VEGA BAJA | 2021-10-31 20:10 | 2021-10-31 21:54 | 10 | 001:44 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B21103100035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2021-10-31 | 1040 | keep | 0 | Oct | 2021 | 0.00070834 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-10-31 20:32 | 2021-11-01 10:50 | 300 | 014:18 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M21103100062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 858 | 2021-10-31 | 257400 | keep | 0 | Oct | 2021 | 0.17531 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-10-31 20:46 | 2021-11-01 08:28 | 140 | 011:42 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M21103100073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 702 | 2021-10-31 | 98280 | keep | 0 | Oct | 2021 | 0.066938 | 9.5353e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 140
HUMACAO | 2021-10-31 21:17 | 2021-11-01 08:48 | 339 | 011:31 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | C21103100081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 691 | 2021-10-31 | 234249 | keep | 0 | Oct | 2021 | 0.15955 | 0.00023089 | Sustained | FALSE | TRUE | Not_TMED_Event | 339
SAN JUAN | 2021-10-31 22:14 | 2021-10-31 22:21 | 300 | 000:07 | P | ERROR HUMANO | DISPARO 1336-06 PERSONAL DE CAROLINA HACIENDO OPERACIONES LLEVA PARTE DE 1303-02 | S21103100000 | New_Event | Human Error | Include | Include | Other | 7 | 2021-10-31 | 2100 | keep | 0 | Oct | 2021 | 0.0014303 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2021-10-31 22:14 | 2021-10-31 22:22 | 2000 | 000:08 | P | ERROR HUMANO | PERSONAL REALIZANDO OPERACIONES | R21103100000 | New_Event | Human Error | Include | Include | Other | 8 | 2021-10-31 | 16000 | keep | 0 | Oct | 2021 | 0.010898 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
SAN JUAN | 2021-10-31 22:14 | 2021-10-31 22:21 | 6481 | 000:07 | T | ERROR HUMANO | DISPARO 1336-06 PERSONAL DE CAROLINA HACIENDO OPERACIONES LLEVA PARTE DE 1303-02 | S21103100000 | New_Event | Human Error | Include | Include | Other | 7 | 2021-10-31 | 45367 | keep | 0 | Oct | 2021 | 0.030899 | 0.0044142 | Sustained | FALSE | FALSE | Not_TMED_Event | 6481
CANOVANAS | 2021-10-31 22:40 | 2021-11-01 10:59 | 100 | 012:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE CON AVE | R21103100217 | New_Event |  |  | Include | Wildlife | 739 | 2021-10-31 | 73900 | keep | 0 | Oct | 2021 | 0.050333 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-10-31 22:48 | 2021-10-31 22:49 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21103100084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-10-31 | 1192 | keep | 0 | Oct | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
FAJARDO | 2021-10-31 23:06 | 2021-11-01 11:28 | 129 | 012:22 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA SE PATRULLO | R21103100218 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 742 | 2021-10-31 | 95718 | keep | 0 | Oct | 2021 | 0.065193 | 8.7861e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 129
VEGA BAJA | 2021-10-31 23:32 | 2021-11-01 10:21 | 40 | 010:49 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | B21103100039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 649 | 2021-10-31 | 25960 | keep | 0 | Oct | 2021 | 0.017681 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-10-31 23:53 | 2021-10-31 23:55 | 1565 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C21103100084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-10-31 | 3130 | keep | 0 | Oct | 2021 | 0.0021318 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
BAYAMON | 2021-11-01 00:43 | 2021-11-01 09:52 | 50 | 009:09 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN C/L SE REEMPLAZO PARARRAYO AVERIADO | B21110100001 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 549 | 2021-11-01 | 27450 | keep | 0 | Nov | 2021 | 0.018696 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-01 00:44 | 2021-11-01 16:13 | 10 | 015:29 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER HACIA TRANSFORMADOR | B21110100002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 929 | 2021-11-01 | 9290 | keep | 0 | Nov | 2021 | 0.0063274 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-11-01 02:12 | 2021-11-01 10:04 | 50 | 007:52 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M21110100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 472 | 2021-11-01 | 23600 | keep | 0 | Nov | 2021 | 0.016074 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-11-01 03:10 | 2021-11-01 09:10 | 40 | 006:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REMPLAZO PORTA FUSIBLES AVERIADO | A21110100001 | New_Event | Cutout Failure | Include | Include | Equipment | 360 | 2021-11-01 | 14400 | keep | 0 | Nov | 2021 | 0.0098078 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-11-01 04:03 | 2021-11-01 04:04 | 539 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21110100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-01 | 539 | keep | 0 | Nov | 2021 | 0.00036711 | 0.00036711 | Momentary | FALSE | FALSE | Not_TMED_Event | 539
HUMACAO | 2021-11-01 04:07 | 2021-11-01 04:08 | 2141 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | C21110100003 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-11-01 | 2141 | keep | 0 | Nov | 2021 | 0.0014582 | 0.0014582 | Momentary | FALSE | FALSE | Not_TMED_Event | 2141
HUMACAO | 2021-11-01 04:08 | 2021-11-01 17:00 | 93 | 012:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21110100004 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 772 | 2021-11-01 | 71796 | keep | 0 | Nov | 2021 | 0.0489 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
BAYAMON | 2021-11-01 04:12 | 2021-11-01 10:15 | 40 | 006:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA. SE REEMPLAZO CAJA QUEMADA | B21110100005 | New_Event | Cutout Failure | Include | Include | Equipment | 363 | 2021-11-01 | 14520 | keep | 0 | Nov | 2021 | 0.0098895 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-11-01 04:13 | 2021-11-01 20:45 | 100 | 016:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN C/L REPARO NEUTRAL PRIMARIO | R21110100003 | New_Event | Wire Down | Include | Include | Equipment | 992 | 2021-11-01 | 99200 | keep | 0 | Nov | 2021 | 0.067565 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-11-01 04:19 | 2021-11-01 10:07 | 20 | 005:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21110100003 | New_Event | Wire Down | Include | Include | Equipment | 348 | 2021-11-01 | 6960 | keep | 0 | Nov | 2021 | 0.0047404 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-11-01 04:24 | 2021-11-01 11:52 | 20 | 007:28 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA REQUIERE DESGANCHE | A21110100002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 448 | 2021-11-01 | 8960 | keep | 0 | Nov | 2021 | 0.0061026 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-11-01 05:31 | 2021-11-01 10:06 | 250 | 004:35 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M21110100008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2021-11-01 | 68750 | keep | 0 | Nov | 2021 | 0.046825 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2021-11-01 06:06 | 2021-11-01 06:07 | 1447 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1112-04 QUE A SU VEZ LLEVA LA CARGA DEL 1419-12 Y 1419-09 | S21110100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-01 | 1447 | keep | 0 | Nov | 2021 | 0.00098555 | 0.00098555 | Momentary | FALSE | FALSE | Not_TMED_Event | 1447
SAN JUAN | 2021-11-01 06:06 | 2021-11-01 06:07 | 266 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1112-04 QUE A SU VEZ LLEVA LA CARGA DEL 1419-12 Y 1419-09 | S21110100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-01 | 266 | keep | 0 | Nov | 2021 | 0.00018117 | 0.00018117 | Momentary | FALSE | FALSE | Not_TMED_Event | 266
SAN JUAN | 2021-11-01 06:06 | 2021-11-01 06:07 | 73 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1112-04 QUE A SU VEZ LLEVA LA CARGA DEL 1419-12 Y 1419-09 | S21110100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-01 | 73 | keep | 0 | Nov | 2021 | 4.972e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
MAYAGÃœEZ | 2021-11-01 06:14 | 2021-11-01 10:00 | 60 | 003:46 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M21110100009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2021-11-01 | 13560 | keep | 0 | Nov | 2021 | 0.0092357 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-11-01 06:33 | 2021-11-01 06:34 | 1026 | 000:01 | T | DESGANCHE | RECIERRE | R21110100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-01 | 1026 | keep | 0 | Nov | 2021 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
SAN JUAN | 2021-11-01 06:34 | 2021-11-01 20:22 | 300 | 013:48 | P | DESCONECTIVO DEFECTUOSO | REMPLAZO 2 VACCUUM SWITCH Y 1 BOLT T | R21110100007 | New_Event | Switch Failure | Include | Include | Equipment | 828 | 2021-11-01 | 248400 | keep | 0 | Nov | 2021 | 0.16918 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2021-11-01 06:34 | 2021-11-01 17:06 | 50 | 010:32 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHO Y REMPLAZO CAJA AVERIADA | R21110100013 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 632 | 2021-11-01 | 31600 | keep | 0 | Nov | 2021 | 0.021523 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-11-01 06:36 | 2021-11-01 06:37 | 1478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21110100004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-01 | 1478 | keep | 0 | Nov | 2021 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
FAJARDO | 2021-11-01 07:17 | 2021-11-01 10:59 | 70 | 003:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE CON AVE | R21110100018 | New_Event |  |  | Include | Wildlife | 222 | 2021-11-01 | 15540 | keep | 0 | Nov | 2021 | 0.010584 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2021-11-01 07:22 | 2021-11-01 11:55 | 75 | 004:33 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | A21110100004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 273 | 2021-11-01 | 20475 | keep | 0 | Nov | 2021 | 0.013945 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
YAUCO | 2021-11-01 07:30 | 2021-11-01 07:31 | 2484 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21110100006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-01 | 2484 | keep | 0 | Nov | 2021 | 0.0016918 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
SAN JUAN | 2021-11-01 08:00 | 2021-11-01 08:01 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21110100020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-01 | 3046 | keep | 0 | Nov | 2021 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
BAYAMON | 2021-11-01 08:04 | 2021-11-01 14:22 | 60 | 006:18 | P | NO SE REPORTO CAUSA | 1 X 150 EN SU 13A | B21110100009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 378 | 2021-11-01 | 22680 | keep | 0 | Nov | 2021 | 0.015447 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-11-01 08:08 | 2021-11-01 16:15 | 15 | 008:07 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR LA MISMA CAPACIDAD EN EL FID 24393851 MARCA EATON NUMERO SERIE 2055105199 VOLTAJES 2400/4160V 120/240V | M21110100025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 487 | 2021-11-01 | 7305 | keep | 0 | Nov | 2021 | 0.0049754 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-11-01 08:17 | 2021-11-01 12:03 | 5 | 003:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21110100014 | New_Event | Bad Weather | Include | Include | Weather | 226 | 2021-11-01 | 1130 | keep | 0 | Nov | 2021 | 0.00076964 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-11-01 08:29 | 2021-11-01 10:55 | 15 | 002:26 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B21110100012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2021-11-01 | 2190 | keep | 0 | Nov | 2021 | 0.0014916 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-11-01 08:31 | 2021-11-01 09:41 | 2 | 001:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE CON AVE | R21111010031 | New_Event |  |  | Include | Wildlife | 70 | 2021-11-01 | 140 | keep | 0 | Nov | 2021 | 9.5353e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
UTUADO | 2021-11-01 09:00 | 2021-11-01 10:57 | 100 | 001:57 | P | ESTRUCTURA AVERIADA | SE REALIZO CAMBIO PRIMARIO A POSTE NUEVO | A21110100015 | New_Event | Defective Pole | Include | Include | Equipment | 117 | 2021-11-01 | 11700 | keep | 0 | Nov | 2021 | 0.0079688 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-11-01 09:08 | 2021-11-01 11:45 | 15 | 002:37 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M21110100037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2021-11-01 | 2355 | keep | 0 | Nov | 2021 | 0.001604 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-11-01 09:12 | 2021-11-01 09:13 | 3896 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR ESTA EN SERVICIO | C21110100025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-01 | 3896 | keep | 0 | Nov | 2021 | 0.0026535 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
BAYAMON | 2021-11-01 09:29 | 2021-11-01 12:19 | 10 | 002:50 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO XMR Y SE REPARO BARRA DE PEDESTAL | B21103100032 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 170 | 2021-11-01 | 1700 | keep | 0 | Nov | 2021 | 0.0011579 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-11-01 09:30 | 2021-11-01 12:22 | 13 | 002:52 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21110100027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2021-11-01 | 2236 | keep | 0 | Nov | 2021 | 0.0015229 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BARRANQUITAS | 2021-11-01 09:37 | 2021-11-01 18:08 | 6 | 008:31 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO | C21110100031 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 511 | 2021-11-01 | 3066 | keep | 0 | Nov | 2021 | 0.0020882 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-11-01 09:58 | 2021-11-01 15:46 | 10 | 005:48 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | S21110100018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 348 | 2021-11-01 | 3480 | keep | 0 | Nov | 2021 | 0.0023702 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-01 10:02 | 2021-11-01 10:49 | 30 | 000:47 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LA LINEA PRIMARIA | A21110100022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 47 | 2021-11-01 | 1410 | keep | 0 | Nov | 2021 | 0.00096034 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-11-01 10:05 | 2021-11-01 17:30 | 38 | 007:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO 2 DISCOS | C21110100036 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 445 | 2021-11-01 | 16910 | keep | 0 | Nov | 2021 | 0.011517 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
HUMACAO | 2021-11-01 10:07 | 2021-11-01 19:46 | 1035 | 009:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO MACHETES PARA REEMPLAZO DE POSTE PRIMARIO CON BANCO DE TRANSFORMADORES IMPACTADO POR VEHICULO | C21110100035 | New_Event |  |  | Include | Wildlife | 579 | 2021-11-01 | 599265 | keep | 0 | Nov | 2021 | 0.40816 | 0.00070493 | Sustained | FALSE | FALSE | Not_TMED_Event | 1035
BARRANQUITAS | 2021-11-01 10:23 | 2021-11-01 12:00 | 23 | 001:37 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25 KVA X 50 KVA | C21110100038 | New_Event | Service Transformer Failure | Include | Include | Equipment | 97 | 2021-11-01 | 2231 | keep | 0 | Nov | 2021 | 0.0015195 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
MAYAGÃœEZ | 2021-11-01 10:36 | 2021-11-01 16:30 | 20 | 005:54 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 37.5 KVA POR LA MISMA CAPACIDAD EN EL FID 24479278 MARCA MOLONEY | M21110100048 | New_Event | Service Transformer Failure | Include | Include | Equipment | 354 | 2021-11-01 | 7080 | keep | 0 | Nov | 2021 | 0.0048222 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-11-01 10:46 | 2021-11-01 12:03 | 12 | 001:17 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50 KVA X 50 KVA CON DERRAME DE ACEITE | C21110100022 | New_Event | Service Transformer Failure | Include | Include | Equipment | 77 | 2021-11-01 | 924 | keep | 0 | Nov | 2021 | 0.00062933 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-11-01 10:48 | 2021-11-01 13:31 | 30 | 002:43 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21110100037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 163 | 2021-11-01 | 4890 | keep | 0 | Nov | 2021 | 0.0033306 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-11-01 10:49 | 2021-11-01 12:55 | 4 | 002:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M21110100049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 126 | 2021-11-01 | 504 | keep | 0 | Nov | 2021 | 0.00034327 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-11-01 10:53 | 2021-11-01 18:19 | 50 | 007:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA RETEZO LINEA Y BAJO LA SECUNDARIA | R21110100041 | New_Event | Wire Down | Include | Include | Equipment | 446 | 2021-11-01 | 22300 | keep | 0 | Nov | 2021 | 0.015188 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-01 10:58 | 2021-11-01 15:00 | 30 | 004:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO BARRA DE PEDESTAL | S21110100001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 242 | 2021-11-01 | 7260 | keep | 0 | Nov | 2021 | 0.0049448 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-11-01 11:18 | 2021-11-01 14:00 | 2 | 002:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR SE REMPLAZO CAJA QUEMADA EN TRANSFORMADOR EN EL FID 24409682 MARCA CHINT 100AMP | M21110100053 | New_Event | Cutout Failure | Include | Include | Equipment | 162 | 2021-11-01 | 324 | keep | 0 | Nov | 2021 | 0.00022067 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2021-11-01 11:30 | 2021-11-01 15:24 | 30 | 003:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA CAMBIO DE LINEA PRIMARIA | A21110100029 | New_Event | Wire Down | Include | Include | Equipment | 234 | 2021-11-01 | 7020 | keep | 0 | Nov | 2021 | 0.0047813 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-11-01 11:42 | 2021-11-01 16:00 | 9 | 004:18 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | C21110100052 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 258 | 2021-11-01 | 2322 | keep | 0 | Nov | 2021 | 0.0015815 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-11-01 12:02 | 2021-11-01 16:29 | 50 | 004:27 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21110100026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 267 | 2021-11-01 | 13350 | keep | 0 | Nov | 2021 | 0.0090926 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-01 12:02 | 2021-11-02 09:28 | 10 | 021:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR IGUANA CRUZO FASE A TIERRA | M21110100059 | New_Event |  |  | Include | Wildlife | 1286 | 2021-11-01 | 12860 | keep | 0 | Nov | 2021 | 0.0087589 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-11-01 12:14 | 2021-11-02 09:51 | 40 | 021:37 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | S21110100029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1297 | 2021-11-01 | 51880 | keep | 0 | Nov | 2021 | 0.035335 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-11-01 12:16 | 2021-11-01 15:34 | 200 | 003:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO DE CORTE DE LINEA | M21110100022 | New_Event | Wire Down | Include | Include | Equipment | 198 | 2021-11-01 | 39600 | keep | 0 | Nov | 2021 | 0.026971 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2021-11-01 12:17 | 2021-11-01 15:20 | 25 | 003:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA REEMPLAZO CAJA QUEMADA | R21110100053 | New_Event | Cutout Failure | Include | Include | Equipment | 183 | 2021-11-01 | 4575 | keep | 0 | Nov | 2021 | 0.003116 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2021-11-01 12:17 | 2021-11-01 14:27 | 10 | 002:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BUSHING Y BAJANTE SECUNDARIO | R21110100052 | New_Event | Secondary Wire Down | Include | Include | Equipment | 130 | 2021-11-01 | 1300 | keep | 0 | Nov | 2021 | 0.00088542 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-11-01 12:23 | 2021-11-02 10:27 | 80 | 022:04 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M21110100063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1324 | 2021-11-01 | 105920 | keep | 0 | Nov | 2021 | 0.072142 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2021-11-01 12:29 | 2021-11-01 18:31 | 14 | 006:02 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR ESCAPE DE 50KVA POR LA MISMA CAPACIDAD EN EL FID 33520355 MARCA GRMCO NUMERO SERIE 82011973285 VOLTAJES 2400/4160V 120/240V CAJA PRIMARIA MARCA CHINT 100AMP | A21110100030 | New_Event | Service Transformer Failure | Include | Include | Equipment | 362 | 2021-11-01 | 5068 | keep | 0 | Nov | 2021 | 0.0034518 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2021-11-01 12:48 | 2021-11-01 14:40 | 300 | 001:52 | P | DESGANCHE | DISPARO DE 1204-01 LLEVA 40% SE SECCIONALIZO BAMBUAS SOBRE LINEA 20% EN SERVICIO | S21110100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2021-11-01 | 33600 | keep | 0 | Nov | 2021 | 0.022885 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
HUMACAO | 2021-11-01 12:55 | 2021-11-01 15:58 | 34 | 003:03 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21110100062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2021-11-01 | 6222 | keep | 0 | Nov | 2021 | 0.0042378 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
VEGA BAJA | 2021-11-01 12:55 | 2021-11-01 14:55 | 10 | 002:00 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA RELOCALIZAR SECUNDARIA A POSTE NUEVO | B21110100048 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 120 | 2021-11-01 | 1200 | keep | 0 | Nov | 2021 | 0.00081731 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-11-01 12:58 | 2021-11-01 14:26 | 400 | 001:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 200 Y 1 X 30 EN CORTE DE LINEA CAMION IMPACTO POSTE | A21110100037 | New_Event |  |  | Include | Wildlife | 88 | 2021-11-01 | 35200 | keep | 0 | Nov | 2021 | 0.023975 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
HUMACAO | 2021-11-01 13:01 | 2021-11-01 16:43 | 1 | 003:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21110100063 | New_Event | Bad Weather | Include | Include | Weather | 222 | 2021-11-01 | 222 | keep | 0 | Nov | 2021 | 0.0001512 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-11-01 13:11 | 2021-11-01 14:49 | 4 | 001:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA LEVANTAR SECUNDARIA | C21110100041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 98 | 2021-11-01 | 392 | keep | 0 | Nov | 2021 | 0.00026699 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2021-11-01 13:15 | 2021-11-01 13:16 | 436 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL 80 PORCIENTO DE LA CARGA POR EL 3015-07 | C21110100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-01 | 436 | keep | 0 | Nov | 2021 | 0.00029696 | 0.00029696 | Momentary | FALSE | FALSE | Not_TMED_Event | 436
HUMACAO | 2021-11-01 13:18 | 2021-11-02 16:31 | 40 | 027:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA QUEMADA | C21110100069 | New_Event | Cutout Failure | Include | Include | Equipment | 1633 | 2021-11-01 | 65320 | keep | 0 | Nov | 2021 | 0.044489 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-11-01 13:21 | 2021-11-01 13:51 | 718 | 000:30 | T | NO SE REPORTO CAUSA | DISPARO SE PATRULLO SE ABRIO N/O CONTRA 1901-05 Y SE CERRO INTERRUPTOR QUEDO EN SERVICIO | S21110100047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 30 | 2021-11-01 | 21540 | keep | 0 | Nov | 2021 | 0.014671 | 0.00048903 | Sustained | FALSE | FALSE | Not_TMED_Event | 718
BAYAMON | 2021-11-01 13:31 | 2021-11-01 13:43 | 1 | 000:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV BAYAMON PUEBLO | B21110100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 12 | 2021-11-01 | 12 | keep | 0 | Nov | 2021 | 8.1731e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-01 13:31 | 2021-11-01 13:43 | 81 | 000:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV BAYAMON PUEBLO | B21110100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 12 | 2021-11-01 | 972 | keep | 0 | Nov | 2021 | 0.00066202 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
BAYAMON | 2021-11-01 13:31 | 2021-11-01 13:43 | 959 | 000:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV BAYAMON PUEBLO | B21110100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 12 | 2021-11-01 | 11508 | keep | 0 | Nov | 2021 | 0.007838 | 0.00065317 | Sustained | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2021-11-01 13:31 | 2021-11-01 13:43 | 1382 | 000:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV BAYAMON PUEBLO | B21110100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 12 | 2021-11-01 | 16584 | keep | 0 | Nov | 2021 | 0.011295 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2021-11-01 13:31 | 2021-11-01 13:43 | 663 | 000:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV BAYAMON PUEBLO | B21110100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 12 | 2021-11-01 | 7956 | keep | 0 | Nov | 2021 | 0.0054188 | 0.00045157 | Sustained | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2021-11-01 13:31 | 2021-11-01 13:43 | 98 | 000:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV BAYAMON PUEBLO | B21110100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 12 | 2021-11-01 | 1176 | keep | 0 | Nov | 2021 | 0.00080097 | 6.6747e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 98
BAYAMON | 2021-11-01 13:31 | 2021-11-01 13:43 | 74 | 000:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV BAYAMON PUEBLO | B21110100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 12 | 2021-11-01 | 888 | keep | 0 | Nov | 2021 | 0.00060481 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
BAYAMON | 2021-11-01 13:31 | 2021-11-01 13:43 | 776 | 000:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV BAYAMON PUEBLO | B21110100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 12 | 2021-11-01 | 9312 | keep | 0 | Nov | 2021 | 0.0063424 | 0.00052853 | Sustained | FALSE | FALSE | Not_TMED_Event | 776
BAYAMON | 2021-11-01 13:31 | 2021-11-01 13:43 | 1514 | 000:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV BAYAMON PUEBLO | B21110100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 12 | 2021-11-01 | 18168 | keep | 0 | Nov | 2021 | 0.012374 | 0.0010312 | Sustained | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2021-11-01 13:31 | 2021-11-01 13:43 | 1105 | 000:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV BAYAMON PUEBLO | B21110100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 12 | 2021-11-01 | 13260 | keep | 0 | Nov | 2021 | 0.0090313 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2021-11-01 13:31 | 2021-11-01 13:58 | 300 | 000:27 | P | NO SE REPORTO CAUSA | SE CERRO MACHETES N/O CON 1330-01 ABRIENDO MACHETES EN URBANIZACION PARKVILLE | S21110100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 27 | 2021-11-01 | 8100 | keep | 0 | Nov | 2021 | 0.0055169 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2021-11-01 13:31 | 2021-11-01 13:43 | 4176 | 000:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV BAYAMON PUEBLO | B21110100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 12 | 2021-11-01 | 50112 | keep | 0 | Nov | 2021 | 0.034131 | 0.0028443 | Sustained | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2021-11-01 13:31 | 2021-11-01 13:43 | 252 | 000:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV BAYAMON PUEBLO | B21110100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 12 | 2021-11-01 | 3024 | keep | 0 | Nov | 2021 | 0.0020596 | 0.00017164 | Sustained | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2021-11-01 13:31 | 2021-11-01 13:43 | 2147 | 000:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV BAYAMON PUEBLO | B21110100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 12 | 2021-11-01 | 25764 | keep | 0 | Nov | 2021 | 0.017548 | 0.0014623 | Sustained | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2021-11-01 13:31 | 2021-11-01 13:43 | 2858 | 000:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV BAYAMON PUEBLO | B21110100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 12 | 2021-11-01 | 34296 | keep | 0 | Nov | 2021 | 0.023359 | 0.0019466 | Sustained | FALSE | FALSE | Not_TMED_Event | 2858
MAYAGÃœEZ | 2021-11-01 13:32 | 2021-11-01 15:20 | 4 | 001:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR LLUVIA Y VIENTO | M21110100072 | New_Event | Bad Weather | Include | Include | Weather | 108 | 2021-11-01 | 432 | keep | 0 | Nov | 2021 | 0.00029423 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2021-11-01 13:40 | 2021-11-01 17:19 | 25 | 003:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21110100070 | New_Event | Bad Weather | Include | Include | Weather | 219 | 2021-11-01 | 5475 | keep | 0 | Nov | 2021 | 0.003729 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2021-11-01 13:42 | 2021-11-01 21:55 | 1 | 008:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN RISER SE REMPLAZO CAJA EN RISER MARCA CHINT 200AMP | M21110100076 | New_Event | Cutout Failure | Include | Include | Equipment | 493 | 2021-11-01 | 493 | keep | 0 | Nov | 2021 | 0.00033578 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-01 13:43 | 2021-11-01 14:04 | 30 | 000:21 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21110100037 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 21 | 2021-11-01 | 630 | keep | 0 | Nov | 2021 | 0.00042909 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2021-11-01 13:51 | 2021-11-01 17:37 | 10 | 003:46 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO 50 KVA X 50 KVA | R21110100061 | New_Event | Service Transformer Failure | Include | Include | Equipment | 226 | 2021-11-01 | 2260 | keep | 0 | Nov | 2021 | 0.0015393 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2021-11-01 13:52 | 2021-11-01 18:32 | 152 | 004:40 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21110100034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2021-11-01 | 42560 | keep | 0 | Nov | 2021 | 0.028987 | 0.00010353 | Sustained | FALSE | FALSE | Not_TMED_Event | 152
CAGUAS | 2021-11-01 13:53 | 2021-11-01 16:38 | 1 | 002:45 | P | OTRAS CAUSAS | 1 NX DE 20 AMP PROBLEMA INTERNO | C21110100073 | New_Event | Other Causes | Include | Include | Other | 165 | 2021-11-01 | 165 | keep | 0 | Nov | 2021 | 0.00011238 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-01 13:58 | 2021-11-01 17:56 | 300 | 003:58 | P | NO SE REPORTO CAUSA | SE CERRO MACHETES N/O CON 1330-01 ABRIENDO MACHETES EN URBANIZACION PARKVILLE | S21110100000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 238 | 2021-11-01 | 71400 | keep | 0 | Nov | 2021 | 0.04863 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-11-01 14:02 | 2021-11-01 20:37 | 10 | 006:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | M21110100079 | New_Event | Secondary Wire Down | Include | Include | Equipment | 395 | 2021-11-01 | 3950 | keep | 0 | Nov | 2021 | 0.0026903 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-11-01 14:03 | 2021-11-01 16:20 | 75 | 002:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA Y VIENTO | M21110100080 | New_Event | Bad Weather | Include | Include | Weather | 137 | 2021-11-01 | 10275 | keep | 0 | Nov | 2021 | 0.0069983 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2021-11-01 14:04 | 2021-11-01 15:47 | 959 | 001:43 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9100 | B21110100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 103 | 2021-11-01 | 98777 | keep | 0 | Nov | 2021 | 0.067277 | 0.00065317 | Sustained | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2021-11-01 14:04 | 2021-11-01 15:47 | 1382 | 001:43 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9100 | B21110100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 103 | 2021-11-01 | 142346 | keep | 0 | Nov | 2021 | 0.096951 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2021-11-01 14:04 | 2021-11-01 15:47 | 663 | 001:43 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9100 | B21110100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 103 | 2021-11-01 | 68289 | keep | 0 | Nov | 2021 | 0.046511 | 0.00045157 | Sustained | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2021-11-01 14:04 | 2021-11-01 15:47 | 1514 | 001:43 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9100 | B21110100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 103 | 2021-11-01 | 155942 | keep | 0 | Nov | 2021 | 0.10621 | 0.0010312 | Sustained | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2021-11-01 14:04 | 2021-11-01 15:47 | 1105 | 001:43 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9100 | B21110100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 103 | 2021-11-01 | 113815 | keep | 0 | Nov | 2021 | 0.077519 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
ARECIBO | 2021-11-01 14:04 | 2021-11-01 17:38 | 8 | 003:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA AVERIADA | A21110100023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 214 | 2021-11-01 | 1712 | keep | 0 | Nov | 2021 | 0.001166 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-11-01 14:04 | 2021-11-01 15:47 | 4176 | 001:43 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9100 | B21110100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 103 | 2021-11-01 | 430128 | keep | 0 | Nov | 2021 | 0.29296 | 0.0028443 | Sustained | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2021-11-01 14:04 | 2021-11-01 15:47 | 252 | 001:43 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9100 | B21110100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 103 | 2021-11-01 | 25956 | keep | 0 | Nov | 2021 | 0.017679 | 0.00017164 | Sustained | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2021-11-01 14:04 | 2021-11-01 15:47 | 2147 | 001:43 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9100 | B21110100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 103 | 2021-11-01 | 221141 | keep | 0 | Nov | 2021 | 0.15062 | 0.0014623 | Sustained | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2021-11-01 14:04 | 2021-11-01 15:47 | 2858 | 001:43 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9100 | B21110100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 103 | 2021-11-01 | 294374 | keep | 0 | Nov | 2021 | 0.2005 | 0.0019466 | Sustained | FALSE | FALSE | Not_TMED_Event | 2858
MAYAGÃœEZ | 2021-11-01 14:05 | 2021-11-01 19:19 | 70 | 005:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21110100081 | New_Event | Bad Weather | Include | Include | Weather | 314 | 2021-11-01 | 21980 | keep | 0 | Nov | 2021 | 0.01497 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
UTUADO | 2021-11-01 14:05 | 2021-11-01 17:04 | 100 | 002:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR LLUVIAS | A21110100043 | New_Event | Bad Weather | Include | Include | Weather | 179 | 2021-11-01 | 17900 | keep | 0 | Nov | 2021 | 0.012192 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-11-01 14:15 | 2021-11-01 15:57 | 12 | 001:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE DE CAJA A TRANSFORMADOR | S21110100065 | New_Event | Wire Down | Include | Include | Equipment | 102 | 2021-11-01 | 1224 | keep | 0 | Nov | 2021 | 0.00083366 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-11-01 14:26 | 2021-11-01 14:43 | 1105 | 000:17 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON RECIERRE EN OFF SE VERIFICO PERSONAL FUERA DE AREA Y SE CERRO INTERRUPTOR | A21110100045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 17 | 2021-11-01 | 18785 | keep | 0 | Nov | 2021 | 0.012794 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
BARRANQUITAS | 2021-11-01 14:29 | 2021-11-01 14:30 | 2635 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 6500 DE BARRANQUITAS A OROCOVIS | C21110100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-01 | 2635 | keep | 0 | Nov | 2021 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2021-11-01 14:29 | 2021-11-01 14:30 | 2280 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 6500 DE BARRANQUITAS A OROCOVIS | C21110100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-01 | 2280 | keep | 0 | Nov | 2021 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2021-11-01 14:29 | 2021-11-01 14:30 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 6500 DE BARRANQUITAS A OROCOVIS | C21110100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-01 | 1617 | keep | 0 | Nov | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
SAN JUAN | 2021-11-01 14:40 | 2021-11-01 15:00 | 300 | 000:20 | P | DESGANCHE | SE DESGANCHE Y SE CERRO MACHETE | S21110100000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 20 | 2021-11-01 | 6000 | keep | 0 | Nov | 2021 | 0.0040866 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-11-01 14:43 | 2021-11-01 18:45 | 400 | 004:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 200 Y 1 X 30 EN CORTE DE LINEA CAMION IMPACTO POSTE | A21110100037 | Partial_restoration |  |  | Include | Wildlife | 242 | 2021-11-01 | 96800 | keep | 0 | Nov | 2021 | 0.06593 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-11-01 14:50 | 2021-11-01 18:10 | 40 | 003:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21110100085 | New_Event | Bad Weather | Include | Include | Weather | 200 | 2021-11-01 | 8000 | keep | 0 | Nov | 2021 | 0.0054488 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2021-11-01 14:54 | 2021-11-01 16:47 | 150 | 001:53 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | A21110100050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2021-11-01 | 16950 | keep | 0 | Nov | 2021 | 0.011545 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2021-11-01 15:17 | 2021-11-01 15:18 | 3041 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE INTERRUPTOR MAL TIEMPO | M21110100090 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-11-01 | 3041 | keep | 0 | Nov | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
SAN JUAN | 2021-11-01 15:22 | 2021-11-01 17:14 | 2000 | 001:52 | P | DESCONECTIVO DEFECTUOSO | REMPLAZO 2 MACHETES 6 AISLADORES Y 1 DISCO QUEMADOS Y CERRO PUENTE | R21110100116 | New_Event | Switch Failure | Include | Include | Equipment | 112 | 2021-11-01 | 224000 | keep | 0 | Nov | 2021 | 0.15257 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
MAYAGÃœEZ | 2021-11-01 15:38 | 2021-11-01 16:05 | 40 | 000:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 1 X 65 1 X 80 EN CORTES DE LINEA MAL TIEMPO | M21110100093 | New_Event | Bad Weather | Include | Include | Weather | 27 | 2021-11-01 | 1080 | keep | 0 | Nov | 2021 | 0.00073558 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-01 15:45 | 2021-11-01 17:48 | 100 | 002:03 | P | SOBRECARGA | SE ABRE CORTE DE LINEA PARA BALANCEAR CARGAS DE FASES | S21110100000 | New_Event | Trip Due To Overload | Include | Include | Other | 123 | 2021-11-01 | 12300 | keep | 0 | Nov | 2021 | 0.0083775 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-11-01 15:48 | 2021-11-01 17:50 | 10 | 002:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 8 EN TRANSFORMADOR SE REPARO PUENTE PRIMARIO | M21110100095 | New_Event | Wire Down | Include | Include | Equipment | 122 | 2021-11-01 | 1220 | keep | 0 | Nov | 2021 | 0.00083094 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-11-01 15:53 | 2021-11-01 20:49 | 40 | 004:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | A21110100059 | New_Event | Bad Weather | Include | Include | Weather | 296 | 2021-11-01 | 11840 | keep | 0 | Nov | 2021 | 0.0080642 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-01 15:59 | 2021-11-02 18:04 | 10 | 026:05 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | S21110100048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1565 | 2021-11-01 | 15650 | keep | 0 | Nov | 2021 | 0.010659 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-11-01 16:01 | 2021-11-01 17:39 | 1 | 001:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21110100093 | New_Event | Bad Weather | Include | Include | Weather | 98 | 2021-11-01 | 98 | keep | 0 | Nov | 2021 | 6.6747e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-11-01 16:05 | 2021-11-01 20:52 | 1444 | 004:47 | T | DESGANCHE | DISPARO DE INTERRUPTOR 6014-02 QUE ESTA LLEVANDO LA CARGA DEL 6014-01 SE RETIRO RAMAS SOBRE TONCAL DEL ALIMENTADOR | M21102900098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 287 | 2021-11-01 | 414428 | keep | 0 | Nov | 2021 | 0.28227 | 0.0009835 | Sustained | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2021-11-01 16:05 | 2021-11-01 20:52 | 3630 | 004:47 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR SE RETIRO RAMAS SOBRE TRONCAL DEL ALIMENTADOR | M21110100098 | Additional_clients | Bad Weather | Include | Include | Weather | 287 | 2021-11-01 | 1041810 | keep | 0 | Nov | 2021 | 0.70957 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-11-01 16:05 | 2021-11-01 16:06 | 2791 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21110100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-01 | 2791 | keep | 0 | Nov | 2021 | 0.0019009 | 0.0019009 | Momentary | FALSE | FALSE | Not_TMED_Event | 2791
ARECIBO | 2021-11-01 16:05 | 2021-11-01 16:06 | 1464 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21110100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-01 | 1464 | keep | 0 | Nov | 2021 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
ARECIBO | 2021-11-01 16:05 | 2021-11-01 16:06 | 759 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21110100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-01 | 759 | keep | 0 | Nov | 2021 | 0.00051695 | 0.00051695 | Momentary | FALSE | FALSE | Not_TMED_Event | 759
ARECIBO | 2021-11-01 16:05 | 2021-11-01 16:06 | 1500 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21110100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-01 | 1500 | keep | 0 | Nov | 2021 | 0.0010216 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
ARECIBO | 2021-11-01 16:05 | 2021-11-01 16:06 | 2132 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21110100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-01 | 2132 | keep | 0 | Nov | 2021 | 0.0014521 | 0.0014521 | Momentary | FALSE | FALSE | Not_TMED_Event | 2132
ARECIBO | 2021-11-01 16:05 | 2021-11-01 16:06 | 2366 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21110100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-01 | 2366 | keep | 0 | Nov | 2021 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
ARECIBO | 2021-11-01 16:05 | 2021-11-01 16:06 | 1976 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21110100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-01 | 1976 | keep | 0 | Nov | 2021 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
ARECIBO | 2021-11-01 16:05 | 2021-11-01 16:06 | 3688 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21110100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-01 | 3688 | keep | 0 | Nov | 2021 | 0.0025119 | 0.0025119 | Momentary | FALSE | FALSE | Not_TMED_Event | 3688
BAYAMON | 2021-11-01 16:05 | 2021-11-01 16:06 | 3070 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPRARO DE LINEA 36100 | B21110100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-01 | 3070 | keep | 0 | Nov | 2021 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2021-11-01 16:05 | 2021-11-01 16:06 | 2735 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPRARO DE LINEA 36100 | B21110100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-01 | 2735 | keep | 0 | Nov | 2021 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2021-11-01 16:05 | 2021-11-01 16:06 | 1070 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPRARO DE LINEA 36100 | B21110100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-01 | 1070 | keep | 0 | Nov | 2021 | 0.00072877 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2021-11-01 16:05 | 2021-11-01 16:06 | 1647 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPRARO DE LINEA 36100 | B21110100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-01 | 1647 | keep | 0 | Nov | 2021 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2021-11-01 16:05 | 2021-11-01 16:06 | 3295 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPRARO DE LINEA 36100 | B21110100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-01 | 3295 | keep | 0 | Nov | 2021 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2021-11-01 16:05 | 2021-11-01 16:06 | 1180 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPRARO DE LINEA 36100 | B21110100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-01 | 1180 | keep | 0 | Nov | 2021 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2021-11-01 16:05 | 2021-11-01 16:06 | 320 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPRARO DE LINEA 36100 | B21110100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-01 | 320 | keep | 0 | Nov | 2021 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2021-11-01 16:05 | 2021-11-01 16:06 | 2234 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPRARO DE LINEA 36100 | B21110100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-01 | 2234 | keep | 0 | Nov | 2021 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
ARECIBO | 2021-11-01 16:16 | 2021-11-01 16:19 | 2791 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-01 | 8373 | keep | 0 | Nov | 2021 | 0.0057028 | 0.0019009 | Momentary | FALSE | FALSE | Not_TMED_Event | 2791
ARECIBO | 2021-11-01 16:16 | 2021-11-01 16:19 | 1464 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-01 | 4392 | keep | 0 | Nov | 2021 | 0.0029914 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
ARECIBO | 2021-11-01 16:16 | 2021-11-01 16:19 | 759 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-01 | 2277 | keep | 0 | Nov | 2021 | 0.0015509 | 0.00051695 | Momentary | FALSE | FALSE | Not_TMED_Event | 759
ARECIBO | 2021-11-01 16:16 | 2021-11-01 16:19 | 1500 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-01 | 4500 | keep | 0 | Nov | 2021 | 0.0030649 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
ARECIBO | 2021-11-01 16:16 | 2021-11-01 16:19 | 2132 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-01 | 6396 | keep | 0 | Nov | 2021 | 0.0043563 | 0.0014521 | Momentary | FALSE | FALSE | Not_TMED_Event | 2132
ARECIBO | 2021-11-01 16:16 | 2021-11-01 16:19 | 2366 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-01 | 7098 | keep | 0 | Nov | 2021 | 0.0048344 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
ARECIBO | 2021-11-01 16:16 | 2021-11-01 16:19 | 1976 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-01 | 5928 | keep | 0 | Nov | 2021 | 0.0040375 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
ARECIBO | 2021-11-01 16:16 | 2021-11-01 16:19 | 3688 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-01 | 11064 | keep | 0 | Nov | 2021 | 0.0075356 | 0.0025119 | Momentary | FALSE | FALSE | Not_TMED_Event | 3688
BAYAMON | 2021-11-01 16:16 | 2021-11-01 16:19 | 3070 | 000:03 | S | LINEA DE TRANSMISION 115KV | DSIPARO DE LINEA 36100 | B21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-01 | 9210 | keep | 0 | Nov | 2021 | 0.0062729 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2021-11-01 16:16 | 2021-11-01 16:19 | 2735 | 000:03 | S | LINEA DE TRANSMISION 115KV | DSIPARO DE LINEA 36100 | B21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-01 | 8205 | keep | 0 | Nov | 2021 | 0.0055884 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2021-11-01 16:16 | 2021-11-01 16:19 | 1070 | 000:03 | S | LINEA DE TRANSMISION 115KV | DSIPARO DE LINEA 36100 | B21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-01 | 3210 | keep | 0 | Nov | 2021 | 0.0021863 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2021-11-01 16:16 | 2021-11-01 16:19 | 1647 | 000:03 | S | LINEA DE TRANSMISION 115KV | DSIPARO DE LINEA 36100 | B21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-01 | 4941 | keep | 0 | Nov | 2021 | 0.0033653 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2021-11-01 16:16 | 2021-11-01 16:19 | 3295 | 000:03 | S | LINEA DE TRANSMISION 115KV | DSIPARO DE LINEA 36100 | B21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-01 | 9885 | keep | 0 | Nov | 2021 | 0.0067326 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2021-11-01 16:16 | 2021-11-01 16:19 | 1180 | 000:03 | S | LINEA DE TRANSMISION 115KV | DSIPARO DE LINEA 36100 | B21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-01 | 3540 | keep | 0 | Nov | 2021 | 0.0024111 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2021-11-01 16:16 | 2021-11-01 16:19 | 320 | 000:03 | S | LINEA DE TRANSMISION 115KV | DSIPARO DE LINEA 36100 | B21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-01 | 960 | keep | 0 | Nov | 2021 | 0.00065385 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2021-11-01 16:16 | 2021-11-01 16:19 | 2234 | 000:03 | S | LINEA DE TRANSMISION 115KV | DSIPARO DE LINEA 36100 | B21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-01 | 6702 | keep | 0 | Nov | 2021 | 0.0045647 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
ARECIBO | 2021-11-01 16:22 | 2021-11-01 21:52 | 2791 | 005:30 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 330 | 2021-11-01 | 921030 | keep | 0 | Nov | 2021 | 0.62731 | 0.0019009 | Sustained | FALSE | FALSE | Not_TMED_Event | 2791
ARECIBO | 2021-11-01 16:22 | 2021-11-01 21:52 | 1464 | 005:30 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 330 | 2021-11-01 | 483120 | keep | 0 | Nov | 2021 | 0.32905 | 0.00099712 | Sustained | FALSE | FALSE | Not_TMED_Event | 1464
ARECIBO | 2021-11-01 16:22 | 2021-11-01 21:52 | 759 | 005:30 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 330 | 2021-11-01 | 250470 | keep | 0 | Nov | 2021 | 0.17059 | 0.00051695 | Sustained | FALSE | FALSE | Not_TMED_Event | 759
ARECIBO | 2021-11-01 16:22 | 2021-11-01 21:52 | 1500 | 005:30 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 330 | 2021-11-01 | 495000 | keep | 0 | Nov | 2021 | 0.33714 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
ARECIBO | 2021-11-01 16:22 | 2021-11-01 21:52 | 2132 | 005:30 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 330 | 2021-11-01 | 703560 | keep | 0 | Nov | 2021 | 0.47919 | 0.0014521 | Sustained | FALSE | FALSE | Not_TMED_Event | 2132
ARECIBO | 2021-11-01 16:22 | 2021-11-01 21:52 | 2366 | 005:30 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 330 | 2021-11-01 | 780780 | keep | 0 | Nov | 2021 | 0.53179 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
ARECIBO | 2021-11-01 16:22 | 2021-11-01 21:52 | 1976 | 005:30 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 330 | 2021-11-01 | 652080 | keep | 0 | Nov | 2021 | 0.44413 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
ARECIBO | 2021-11-01 16:22 | 2021-11-01 21:52 | 3688 | 005:30 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 330 | 2021-11-01 | 1217040 | keep | 0 | Nov | 2021 | 0.82892 | 0.0025119 | Sustained | FALSE | FALSE | Not_TMED_Event | 3688
BAYAMON | 2021-11-01 16:22 | 2021-11-01 20:03 | 3070 | 003:41 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 221 | 2021-11-01 | 678470 | keep | 0 | Nov | 2021 | 0.4621 | 0.002091 | Sustained | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2021-11-01 16:22 | 2021-11-01 20:03 | 2735 | 003:41 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 221 | 2021-11-01 | 604435 | keep | 0 | Nov | 2021 | 0.41168 | 0.0018628 | Sustained | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2021-11-01 16:22 | 2021-11-01 20:03 | 1070 | 003:41 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 221 | 2021-11-01 | 236470 | keep | 0 | Nov | 2021 | 0.16106 | 0.00072877 | Sustained | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2021-11-01 16:22 | 2021-11-01 20:03 | 1647 | 003:41 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 221 | 2021-11-01 | 363987 | keep | 0 | Nov | 2021 | 0.24791 | 0.0011218 | Sustained | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2021-11-01 16:22 | 2021-11-01 20:03 | 3295 | 003:41 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 221 | 2021-11-01 | 728195 | keep | 0 | Nov | 2021 | 0.49597 | 0.0022442 | Sustained | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2021-11-01 16:22 | 2021-11-01 20:03 | 1180 | 003:41 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 221 | 2021-11-01 | 260780 | keep | 0 | Nov | 2021 | 0.17762 | 0.00080369 | Sustained | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2021-11-01 16:22 | 2021-11-01 20:03 | 320 | 003:41 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 221 | 2021-11-01 | 70720 | keep | 0 | Nov | 2021 | 0.048167 | 0.00021795 | Sustained | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2021-11-01 16:22 | 2021-11-01 20:03 | 2234 | 003:41 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21110100000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 221 | 2021-11-01 | 493714 | keep | 0 | Nov | 2021 | 0.33627 | 0.0015216 | Sustained | FALSE | FALSE | Not_TMED_Event | 2234
CANOVANAS | 2021-11-01 17:01 | 2021-11-01 18:55 | 100 | 001:54 | P | DESGANCHE | 1 X 100 EN C/L | R21110100113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2021-11-01 | 11400 | keep | 0 | Nov | 2021 | 0.0077645 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2021-11-01 17:06 | 2021-11-01 18:30 | 2 | 001:24 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR POR DESGANCHE | P21110100048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2021-11-01 | 168 | keep | 0 | Nov | 2021 | 0.00011442 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2021-11-01 17:31 | 2021-11-02 11:50 | 1 | 018:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 20 EN RISER CRUCE CON RATA | C21110100100 | New_Event |  |  | Include | Wildlife | 1099 | 2021-11-01 | 1099 | keep | 0 | Nov | 2021 | 0.00074852 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-11-01 17:54 | 2021-11-02 16:57 | 40 | 023:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21110100200 | New_Event | Bad Weather | Include | Include | Weather | 1383 | 2021-11-01 | 55320 | keep | 0 | Nov | 2021 | 0.037678 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-11-01 17:54 | 2021-11-01 22:44 | 10 | 004:50 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA REQUIERE DESGANCHE | M21110100200 | New_Event | Vegetation Contact | Include | Include | Vegetation | 290 | 2021-11-01 | 2900 | keep | 0 | Nov | 2021 | 0.0019752 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-01 17:56 | 2021-11-01 17:58 | 320 | 000:02 | P | NO SE REPORTO CAUSA | SE CERRO MACHETES EN URBANIZACION PARKVILLE NO SE ENCONTRO CAUSA | B21110100000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-01 | 640 | keep | 0 | Nov | 2021 | 0.0004359 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-11-01 18:00 | 2021-11-01 22:35 | 250 | 004:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA QUEMADA EN EL FID 33682458 MARCA DE LA CAJA HUBBELL DE 200AMP | A21110100220 | New_Event | Cutout Failure | Include | Include | Equipment | 275 | 2021-11-01 | 68750 | keep | 0 | Nov | 2021 | 0.046825 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2021-11-01 18:04 | 2021-11-02 12:15 | 12 | 018:11 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO PM-T-50 DE 100 KVA | R21110100128 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1091 | 2021-11-01 | 13092 | keep | 0 | Nov | 2021 | 0.0089169 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-11-01 18:10 | 2021-11-02 15:52 | 5 | 021:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21110100103 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1302 | 2021-11-01 | 6510 | keep | 0 | Nov | 2021 | 0.0044339 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2021-11-01 18:10 | 2021-11-01 18:11 | 1475 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21110100075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-01 | 1475 | keep | 0 | Nov | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
MAYAGÃœEZ | 2021-11-01 18:12 | 2021-11-01 23:27 | 70 | 005:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y VIENTO | M21110100213 | New_Event | Bad Weather | Include | Include | Weather | 315 | 2021-11-01 | 22050 | keep | 0 | Nov | 2021 | 0.015018 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
FAJARDO | 2021-11-01 18:13 | 2021-11-01 19:17 | 40 | 001:04 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN C/L REMPLAZO AISLADOR | R21110100131 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 64 | 2021-11-01 | 2560 | keep | 0 | Nov | 2021 | 0.0017436 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2021-11-01 18:15 | 2021-11-01 18:17 | 860 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO REALIZA OPERACION DE RECIERRE SE COLOCO RR EN OFF Y SE REALIZO PRUEBA QUEDANDO EN SERVICIO | P21110100055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-01 | 1720 | keep | 0 | Nov | 2021 | 0.0011715 | 0.00058574 | Momentary | FALSE | FALSE | Not_TMED_Event | 860
YAUCO | 2021-11-01 18:28 | 2021-11-02 09:08 | 50 | 014:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA CAUSADO POR DESCARGAS ELECTRICAS | P21110100060 | New_Event | Bad Weather | Include | Include | Weather | 880 | 2021-11-01 | 44000 | keep | 0 | Nov | 2021 | 0.029968 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-11-01 18:29 | 2021-11-02 13:30 | 25 | 019:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON BAJANTES SECUNDARIOS EN TRANSFORMADOR | M21110100224 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1141 | 2021-11-01 | 28525 | keep | 0 | Nov | 2021 | 0.019428 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-11-01 18:33 | 2021-11-01 21:04 | 20 | 002:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA Y VIENTO | M21110100226 | New_Event | Bad Weather | Include | Include | Weather | 151 | 2021-11-01 | 3020 | keep | 0 | Nov | 2021 | 0.0020569 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2021-11-01 18:40 | 2021-11-01 20:25 | 200 | 001:45 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO NO FUNDIO FUSIBLE SE ABRIO CORTE DE LINEA PARA REMPLAZARLO | P21000100065 | New_Event | Defective Pole | Include | Include | Equipment | 105 | 2021-11-01 | 21000 | keep | 0 | Nov | 2021 | 0.014303 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2021-11-01 18:54 | 2021-11-01 19:32 | 6 | 000:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21110100078 | New_Event | Secondary Wire Down | Include | Include | Equipment | 38 | 2021-11-01 | 228 | keep | 0 | Nov | 2021 | 0.00015529 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-11-01 18:56 | 2021-11-01 22:34 | 30 | 003:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B21110100459 | New_Event | Cutout Failure | Include | Include | Equipment | 218 | 2021-11-01 | 6540 | keep | 0 | Nov | 2021 | 0.0044544 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-11-01 18:57 | 2021-11-01 20:08 | 179 | 001:11 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21110100104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2021-11-01 | 12709 | keep | 0 | Nov | 2021 | 0.008656 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
CAGUAS | 2021-11-01 18:57 | 2021-11-01 19:32 | 242 | 000:35 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C21110100117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 35 | 2021-11-01 | 8470 | keep | 0 | Nov | 2021 | 0.0057689 | 0.00016483 | Sustained | FALSE | FALSE | Not_TMED_Event | 242
BAYAMON | 2021-11-01 19:26 | 2021-11-02 11:09 | 12 | 015:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE CERRO PUERTE ABIERTO EN SECUNDARIA Y DESGANCHE | S21110100094 | New_Event | Secondary Wire Down | Include | Include | Equipment | 943 | 2021-11-01 | 11316 | keep | 0 | Nov | 2021 | 0.0077073 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-11-01 19:36 | 2021-11-02 10:24 | 50 | 014:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN PROVISIONAL AEREO AVE CRUZO FASES | P21110100070 | New_Event |  |  | Include | Wildlife | 888 | 2021-11-01 | 44400 | keep | 0 | Nov | 2021 | 0.030241 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-01 19:40 | 2021-11-02 09:37 | 19 | 013:57 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S21110100095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 837 | 2021-11-01 | 15903 | keep | 0 | Nov | 2021 | 0.010831 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2021-11-01 19:47 | 2021-11-01 21:44 | 10 | 001:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21110100089 | New_Event | Secondary Wire Down | Include | Include | Equipment | 117 | 2021-11-01 | 1170 | keep | 0 | Nov | 2021 | 0.00079688 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-01 19:50 | 2021-11-02 10:32 | 27 | 014:42 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B21110100488 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 882 | 2021-11-01 | 23814 | keep | 0 | Nov | 2021 | 0.01622 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
CAGUAS | 2021-11-01 20:04 | 2021-11-02 12:47 | 40 | 016:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | C21110100123 | New_Event | Wire Down | Include | Include | Equipment | 1003 | 2021-11-01 | 40120 | keep | 0 | Nov | 2021 | 0.027326 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2021-11-01 20:10 | 2021-11-01 20:11 | 10 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO NO FUNDIO FUSIBLE | P21110100043 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-01 | 10 | keep | 0 | Nov | 2021 | 6.811e-06 | 6.811e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-01 20:48 | 2021-11-02 08:52 | 15 | 012:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21110100302 | New_Event | Bad Weather | Include | Include | Weather | 724 | 2021-11-01 | 10860 | keep | 0 | Nov | 2021 | 0.0073967 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-11-01 20:52 | 2021-11-02 09:48 | 47 | 012:56 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21110100006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 776 | 2021-11-01 | 36472 | keep | 0 | Nov | 2021 | 0.024841 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
BAYAMON | 2021-11-01 20:56 | 2021-11-02 11:10 | 27 | 014:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA | B21110100501 | New_Event | Cutout Failure | Include | Include | Equipment | 854 | 2021-11-01 | 23058 | keep | 0 | Nov | 2021 | 0.015705 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
MAYAGÃœEZ | 2021-11-01 20:56 | 2021-11-02 11:05 | 40 | 014:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA MARCA HUBBELL 200AMP | M21110100270 | New_Event | Cutout Failure | Include | Include | Equipment | 849 | 2021-11-01 | 33960 | keep | 0 | Nov | 2021 | 0.02313 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-01 21:48 | 2021-11-01 21:51 | 3070 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21110100000 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-01 | 9210 | keep | 0 | Nov | 2021 | 0.0062729 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-01 21:48 | 2021-11-01 21:51 | 2735 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21110100000 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-01 | 8205 | keep | 0 | Nov | 2021 | 0.0055884 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-01 21:48 | 2021-11-01 21:51 | 1070 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21110100000 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-01 | 3210 | keep | 0 | Nov | 2021 | 0.0021863 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-01 21:48 | 2021-11-01 21:51 | 1647 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21110100000 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-01 | 4941 | keep | 0 | Nov | 2021 | 0.0033653 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-01 21:48 | 2021-11-01 21:51 | 3295 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21110100000 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-01 | 9885 | keep | 0 | Nov | 2021 | 0.0067326 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-01 21:48 | 2021-11-01 21:51 | 1180 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21110100000 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-01 | 3540 | keep | 0 | Nov | 2021 | 0.0024111 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-01 21:48 | 2021-11-01 21:51 | 320 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21110100000 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-01 | 960 | keep | 0 | Nov | 2021 | 0.00065385 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-01 21:48 | 2021-11-01 21:51 | 2234 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21110100000 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-01 | 6702 | keep | 0 | Nov | 2021 | 0.0045647 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-01 21:54 | 2021-11-02 09:39 | 419 | 011:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | RISER IMPACTADO HAY MACHETE AVERIADO SE ABRIO INTERRUPTOR PARA REPARAR | R21110100147 | New_Event |  |  | Include | Wildlife | 705 | 2021-11-01 | 295395 | keep | 0 | Nov | 2021 | 0.20119 | 0.00028538 | Sustained | FALSE | FALSE | Not_TMED_Event | 419
MAYAGÃœEZ | 2021-11-01 22:16 | 2021-11-02 11:11 | 1 | 012:55 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA REQUIERE DESGANCHE | M21110100278 | New_Event | Vegetation Contact | Include | Include | Vegetation | 775 | 2021-11-01 | 775 | keep | 0 | Nov | 2021 | 0.00052785 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-11-01 22:28 | 2021-11-02 10:33 | 3 | 012:05 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 EN CORTE DE LINEA SE REEMPLAZO AISLADOR ROTO | R21110100157 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 725 | 2021-11-01 | 2175 | keep | 0 | Nov | 2021 | 0.0014814 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-11-01 23:03 | 2021-11-02 09:50 | 10 | 010:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA EN TRANSFORMADOR MARCA CHANCE 100AMP | M21110100280 | New_Event | Cutout Failure | Include | Include | Equipment | 647 | 2021-11-01 | 6470 | keep | 0 | Nov | 2021 | 0.0044067 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-11-01 23:06 | 2021-11-02 11:07 | 120 | 012:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO BAJANTE ZAFADO | C21110100127 | New_Event | Wire Down | Include | Include | Equipment | 721 | 2021-11-01 | 86520 | keep | 0 | Nov | 2021 | 0.058928 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
PONCE | 2021-11-01 23:26 | 2021-11-01 23:27 | 1478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21110100074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-01 | 1478 | keep | 0 | Nov | 2021 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
BAYAMON | 2021-11-02 00:46 | 2021-11-02 17:16 | 12 | 016:30 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR DESGANCHE SECUNDARIO | S21110200001 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 990 | 2021-11-02 | 11880 | keep | 0 | Nov | 2021 | 0.0080914 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-11-02 01:32 | 2021-11-02 10:06 | 100 | 008:34 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21110200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 514 | 2021-11-02 | 51400 | keep | 0 | Nov | 2021 | 0.035008 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2021-11-02 02:22 | 2021-11-02 10:25 | 8 | 008:03 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | R21110200003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 483 | 2021-11-02 | 3864 | keep | 0 | Nov | 2021 | 0.0026318 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-11-02 02:57 | 2021-11-02 12:40 | 40 | 009:43 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21110200004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 583 | 2021-11-02 | 23320 | keep | 0 | Nov | 2021 | 0.015883 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-11-02 03:41 | 2021-11-02 12:00 | 30 | 008:19 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M21110200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 499 | 2021-11-02 | 14970 | keep | 0 | Nov | 2021 | 0.010196 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-11-02 04:07 | 2021-11-02 04:08 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21110200002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 3458 | keep | 0 | Nov | 2021 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
BAYAMON | 2021-11-02 05:00 | 2021-11-02 10:13 | 52 | 005:13 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA 99% DE LA CARGA SE ENCUENTRA POR EL 1907-03 | S21110200002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 313 | 2021-11-02 | 16276 | keep | 0 | Nov | 2021 | 0.011086 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
ARECIBO | 2021-11-02 05:04 | 2021-11-02 05:05 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21110200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 308 | keep | 0 | Nov | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
SAN JUAN | 2021-11-02 05:45 | 2021-11-02 11:36 | 50 | 005:51 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | R21110200007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 351 | 2021-11-02 | 17550 | keep | 0 | Nov | 2021 | 0.011953 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2021-11-02 07:30 | 2021-11-02 07:51 | 12 | 000:21 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | R21110200009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 21 | 2021-11-02 | 252 | keep | 0 | Nov | 2021 | 0.00017164 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-11-02 07:40 | 2021-11-02 16:16 | 30 | 008:36 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21110200004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 516 | 2021-11-02 | 15480 | keep | 0 | Nov | 2021 | 0.010543 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2021-11-02 07:42 | 2021-11-02 14:56 | 30 | 007:14 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN C/L REMPLAZO AISLADOR | C21110200004 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 434 | 2021-11-02 | 13020 | keep | 0 | Nov | 2021 | 0.0088679 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-11-02 07:50 | 2021-11-03 15:41 | 150 | 031:51 | P | CABLE SOTERRADO AVERIADO | SE REPARO AVERIA DE SU-8 A T-20 Y A T-11 | S21110200005 | New_Event | UG Cable Fault | Include | Include | Equipment | 1911 | 2021-11-02 | 286650 | keep | 0 | Nov | 2021 | 0.19524 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-11-02 08:02 | 2021-11-02 19:39 | 7 | 011:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | M21110200007 | New_Event | Bad Weather | Include | Include | Weather | 697 | 2021-11-02 | 4879 | keep | 0 | Nov | 2021 | 0.0033231 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-11-02 08:03 | 2021-11-02 11:00 | 1 | 002:57 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21110200004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2021-11-02 | 177 | keep | 0 | Nov | 2021 | 0.00012055 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-02 08:05 | 2021-11-02 17:17 | 9 | 009:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | R21110200013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 552 | 2021-11-02 | 4968 | keep | 0 | Nov | 2021 | 0.0033837 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2021-11-02 08:23 | 2021-11-02 10:55 | 35 | 002:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO BAJANTE ZAFADO DE LINEA A CAJA DE CORTE DE LINEA | A21110200007 | New_Event | Wire Down | Include | Include | Equipment | 152 | 2021-11-02 | 5320 | keep | 0 | Nov | 2021 | 0.0036234 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2021-11-02 08:32 | 2021-11-02 08:38 | 400 | 000:06 | P | LINEA DE TRANSMISION 115KV | DISPARO L-36200 INFORMO EL SUPERVISOR JORGE L RIVERA DE LA COMPAÃ‘IA DRC BAMBUA CAYO SOBRE LINEA 20% DE LA CARGA ESTA POR EL 1303-02 | S21110200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-11-02 | 2400 | keep | 0 | Nov | 2021 | 0.0016346 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2021-11-02 08:32 | 2021-11-02 08:50 | 1681 | 000:18 | T | LINEA DE TRANSMISION 115KV | DISPARO L-36200 INFORMO SUPERVISOR JORGE L RIVERA DE LA COMPAÃ‘IA DRC BAMBUA CAYO SOBRE LINEA CARGA POR EL 1303-04 | S21110200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 18 | 2021-11-02 | 30258 | keep | 0 | Nov | 2021 | 0.020609 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-11-02 08:32 | 2021-11-02 08:38 | 2435 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 INFORMO SUPERVISOR JORGE L RIVERA DE LA COMPAÃ‘IA DRC BAMBUA CAYO SOBRE LINEA LLEVA EL 20% DEL 1204-02 | S21110200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-11-02 | 14610 | keep | 0 | Nov | 2021 | 0.0099508 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2021-11-02 08:32 | 2021-11-02 08:50 | 726 | 000:18 | T | LINEA DE TRANSMISION 115KV | DISPARO L-36200 INFORMO SUPERVISOR JORGE L RIVERA DE LA COMPAÃ‘IA DRC BAMBUA CAYO SOBRE LINEA LLEVA 1346-04 | S21110200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 18 | 2021-11-02 | 13068 | keep | 0 | Nov | 2021 | 0.0089006 | 0.00049448 | Sustained | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-11-02 08:32 | 2021-11-02 08:38 | 225 | 000:06 | T | LINEA DE TRANSMISION 115KV | DISPARO L-36200 INFORMO SUPERVISOR JORGE L RIVERA DE LA COMPAÃ‘IA DRC BAMBUA CAYO SOBRE LINEA CARGA POR EL 1303-05 | S21110200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-11-02 | 1350 | keep | 0 | Nov | 2021 | 0.00091948 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-11-02 08:32 | 2021-11-02 08:38 | 870 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 INFORMO SUPERVISOR JORGE L RIVERA DE LA COMPAÃ‘IA DRC BAMBUA CAYO SOBRE LINEA LLEVA EL 1303-04 | S21110200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-11-02 | 5220 | keep | 0 | Nov | 2021 | 0.0035553 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2021-11-02 08:32 | 2021-11-02 08:50 | 3932 | 000:18 | T | LINEA DE TRANSMISION 115KV | DISPARO L-36200 INFORMO SUPERVISOR JORGE L RIVERA DE LA COMPAÃ‘IA DRC BAMBUA CAYO SOBRE LINEA CARGA POR EL 1303-03 | S21110200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 18 | 2021-11-02 | 70776 | keep | 0 | Nov | 2021 | 0.048205 | 0.0026781 | Sustained | FALSE | FALSE | Not_TMED_Event | 3932
SAN JUAN | 2021-11-02 08:32 | 2021-11-02 08:38 | 225 | 000:06 | T | LINEA DE TRANSMISION 115KV | DISPARO L-36200 INFORMO SUPERVISOR JORGE L RIVERA DE LA COMPAÃ‘IA DRC BAMBUA CAYO SOBRE LINEA CARGA POR EL 1303-04 | S21110200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-11-02 | 1350 | keep | 0 | Nov | 2021 | 0.00091948 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
CAGUAS | 2021-11-02 08:32 | 2021-11-02 16:18 | 1 | 007:46 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER NO CAUSA | C21110200010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 466 | 2021-11-02 | 466 | keep | 0 | Nov | 2021 | 0.00031739 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-11-02 08:34 | 2021-11-02 17:11 | 10 | 008:37 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZAR 2 POSTES SECUNDARIOS | B21110200010 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 517 | 2021-11-02 | 5170 | keep | 0 | Nov | 2021 | 0.0035213 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-11-02 08:36 | 2021-11-02 10:54 | 10 | 002:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21110200002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 138 | 2021-11-02 | 1380 | keep | 0 | Nov | 2021 | 0.00093991 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-11-02 08:37 | 2021-11-02 15:50 | 20 | 007:13 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE DE 35 PIES PARTIDO | M21110200011 | New_Event | Defective Pole | Include | Include | Equipment | 433 | 2021-11-02 | 8660 | keep | 0 | Nov | 2021 | 0.0058983 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-11-02 08:46 | 2021-11-02 14:23 | 1 | 005:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN RISER | R21110200017 | New_Event | Cutout Failure | Include | Include | Equipment | 337 | 2021-11-02 | 337 | keep | 0 | Nov | 2021 | 0.00022953 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-11-02 08:47 | 2021-11-02 09:46 | 12 | 000:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B21103100016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 59 | 2021-11-02 | 708 | keep | 0 | Nov | 2021 | 0.00048222 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-11-02 09:03 | 2021-11-02 09:04 | 732 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21110200011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 732 | keep | 0 | Nov | 2021 | 0.00049856 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
YAUCO | 2021-11-02 09:04 | 2021-11-02 12:08 | 50 | 003:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA CAUSADO POR FUERTES LLUVIAS | P21110200010 | New_Event | Bad Weather | Include | Include | Weather | 184 | 2021-11-02 | 9200 | keep | 0 | Nov | 2021 | 0.0062661 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-11-02 09:07 | 2021-11-02 18:24 | 50 | 009:17 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PRIMARIO DE HORMIGON EN MALAS CONDICIONES | R21110200022 | New_Event | Defective Pole | Include | Include | Equipment | 557 | 2021-11-02 | 27850 | keep | 0 | Nov | 2021 | 0.018969 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-11-02 09:07 | 2021-11-02 15:30 | 1 | 006:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA EN MONTURA AAA NO FUNDIO FUSIBLE | P21110200012 | New_Event | Cutout Failure | Include | Include | Equipment | 383 | 2021-11-02 | 383 | keep | 0 | Nov | 2021 | 0.00026086 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-11-02 09:16 | 2021-11-02 12:25 | 25 | 003:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21110200012 | New_Event | Bad Weather | Include | Include | Weather | 189 | 2021-11-02 | 4725 | keep | 0 | Nov | 2021 | 0.0032182 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2021-11-02 09:30 | 2021-11-02 11:11 | 15 | 001:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21110100066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 101 | 2021-11-02 | 1515 | keep | 0 | Nov | 2021 | 0.0010319 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-11-02 09:39 | 2021-11-02 11:55 | 1259 | 002:16 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO INTERRUPTOR PARA REEMPLAZO DE MACHETE AVERIADO Y REPARAR TUBO DE RISER | R21110200025 | Additional_clients |  |  | Include | Wildlife | 136 | 2021-11-02 | 171224 | keep | 0 | Nov | 2021 | 0.11662 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-11-02 09:42 | 2021-11-02 16:55 | 8 | 007:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA Y SE CERRO PUENTE PRIMARIO | A21110200000 | New_Event | Wire Down | Include | Include | Equipment | 433 | 2021-11-02 | 3464 | keep | 0 | Nov | 2021 | 0.0023593 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-11-02 09:55 | 2021-11-02 18:14 | 5 | 008:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21110200026 | New_Event | Bad Weather | Include | Include | Weather | 499 | 2021-11-02 | 2495 | keep | 0 | Nov | 2021 | 0.0016993 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2021-11-02 10:11 | 2021-11-02 10:19 | 6 | 000:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21110200017 | New_Event | Bad Weather | Include | Include | Weather | 8 | 2021-11-02 | 48 | keep | 0 | Nov | 2021 | 3.2693e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2021-11-02 10:12 | 2021-11-02 11:59 | 3 | 001:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO DE LINEA A CAJA DE TRANSFORMADOR | A21110200018 | New_Event | Wire Down | Include | Include | Equipment | 107 | 2021-11-02 | 321 | keep | 0 | Nov | 2021 | 0.00021863 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2021-11-02 10:13 | 2021-11-02 14:30 | 47 | 004:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | R21110200028 | New_Event |  |  | Include | Wildlife | 257 | 2021-11-02 | 12079 | keep | 0 | Nov | 2021 | 0.008227 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
PONCE | 2021-11-02 10:18 | 2021-11-02 14:30 | 15 | 004:12 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 15KVA A 4.16KV AVERIADO | P21110200013 | New_Event | Service Transformer Failure | Include | Include | Equipment | 252 | 2021-11-02 | 3780 | keep | 0 | Nov | 2021 | 0.0025745 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-11-02 10:18 | 2021-11-02 17:11 | 50 | 006:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21110200029 | New_Event | Bad Weather | Include | Include | Weather | 413 | 2021-11-02 | 20650 | keep | 0 | Nov | 2021 | 0.014065 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2021-11-02 10:24 | 2021-11-02 11:32 | 10 | 001:08 | P | TRANSFORMADOR AVERIADO | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA REGULAR VOLTAJE EN PLACAS INTERNAS TRANSFORMADOR NO REGULA Y LO CAMBIARAN MAS ADELANTE | P21110200014 | New_Event | Service Transformer Failure | Include | Include | Equipment | 68 | 2021-11-02 | 680 | keep | 0 | Nov | 2021 | 0.00046314 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-11-02 10:27 | 2021-11-02 14:49 | 8 | 004:22 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR QUEMADO 15KVA X 25 KVA | C21110200032 | New_Event | Service Transformer Failure | Include | Include | Equipment | 262 | 2021-11-02 | 2096 | keep | 0 | Nov | 2021 | 0.0014276 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-11-02 10:29 | 2021-11-02 15:39 | 5 | 005:10 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | R21110200034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 310 | 2021-11-02 | 1550 | keep | 0 | Nov | 2021 | 0.0010557 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-11-02 10:38 | 2021-11-02 16:40 | 70 | 006:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA DE 200AMP | A21110200019 | New_Event | Cutout Failure | Include | Include | Equipment | 362 | 2021-11-02 | 25340 | keep | 0 | Nov | 2021 | 0.017259 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2021-11-02 10:41 | 2021-11-02 19:11 | 100 | 008:30 | P | OTRAS CAUSAS | 1 X 100 EN RISER PROBLEMA INTERNO EN CONDOMINIO LLEVA EL 1911-07 | S21110200042 | New_Event | Other Causes | Include | Include | Other | 510 | 2021-11-02 | 51000 | keep | 0 | Nov | 2021 | 0.034736 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-11-02 10:41 | 2021-11-02 19:11 | 577 | 008:30 | P | OTRAS CAUSAS | 1 X 100 EN RISER PROBLEMA INTERNO EN CONDOMINIO CARGA POR EL 1529-12 | S21110200042 | New_Event | Other Causes | Include | Include | Other | 510 | 2021-11-02 | 294270 | keep | 0 | Nov | 2021 | 0.20043 | 0.00039299 | Sustained | FALSE | FALSE | Not_TMED_Event | 577
BAYAMON | 2021-11-02 10:49 | 2021-11-02 14:50 | 10 | 004:01 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 50 KVA POR 50 KVA | B21110200028 | New_Event | Service Transformer Failure | Include | Include | Equipment | 241 | 2021-11-02 | 2410 | keep | 0 | Nov | 2021 | 0.0016414 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-11-02 10:49 | 2021-11-02 13:57 | 11 | 003:08 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R21110200037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2021-11-02 | 2068 | keep | 0 | Nov | 2021 | 0.0014085 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
GUAYAMA | 2021-11-02 10:53 | 2021-11-02 15:30 | 100 | 004:37 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21110200016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 277 | 2021-11-02 | 27700 | keep | 0 | Nov | 2021 | 0.018866 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2021-11-02 10:53 | 2021-11-02 19:30 | 67 | 008:37 | P | ESTRUCTURA AVERIADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO | P21110200013 | New_Event | Defective Pole | Include | Include | Equipment | 517 | 2021-11-02 | 34639 | keep | 0 | Nov | 2021 | 0.023592 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
MAYAGÃœEZ | 2021-11-02 11:04 | 2021-11-03 12:35 | 1 | 025:31 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 75KVA POR LA MISMA CAPACIDAD EN EL FID 23609578 MARCA MOLONEY NUMERO SERIE 202966-5 VOLTAJE 13200V 120/240V | M21110200034 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1531 | 2021-11-02 | 1531 | keep | 0 | Nov | 2021 | 0.0010428 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-11-02 11:09 | 2021-11-02 17:12 | 1 | 006:03 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21110200035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 363 | 2021-11-02 | 363 | keep | 0 | Nov | 2021 | 0.00024724 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-11-02 11:28 | 2021-11-02 19:15 | 5 | 007:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | M21110200040 | New_Event | Cutout Failure | Include | Include | Equipment | 467 | 2021-11-02 | 2335 | keep | 0 | Nov | 2021 | 0.0015904 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-11-02 11:35 | 2021-11-02 12:40 | 16 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA CON EL EVENTO 457 DEL DIA 01 DE NOVIEMBRE | B21110100457 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2021-11-02 | 1040 | keep | 0 | Nov | 2021 | 0.00070834 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
YAUCO | 2021-11-02 11:42 | 2021-11-03 12:12 | 96 | 024:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA LINEA PRIMARIA ARRIADA | P21110200026 | New_Event | Wire Down | Include | Include | Equipment | 1470 | 2021-11-02 | 141120 | keep | 0 | Nov | 2021 | 0.096116 | 6.5385e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 96
SAN JUAN | 2021-11-02 11:50 | 2021-11-02 13:54 | 12 | 002:04 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA Y DESGANCHE LLEVA EL 1422-03 Y EL 90% DEL 1422-02 | S21110200049 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 124 | 2021-11-02 | 1488 | keep | 0 | Nov | 2021 | 0.0010135 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-11-02 11:52 | 2021-11-02 14:05 | 5 | 002:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21110200041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 133 | 2021-11-02 | 665 | keep | 0 | Nov | 2021 | 0.00045293 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-11-02 12:14 | 2021-11-02 16:53 | 15 | 004:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO BAJANTE DE TRANSFORMADOR | A21110200025 | New_Event | Wire Down | Include | Include | Equipment | 279 | 2021-11-02 | 4185 | keep | 0 | Nov | 2021 | 0.0028504 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-11-02 12:15 | 2021-11-02 13:51 | 1716 | 001:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO ALIMENTADOR SE VERIFICO PERSONAL DESGANCHANDO Y FUERA SE PROBO Y QUEDO FUERA SE ABRIO MACHETE Y SE SECCIONALIZO 40% EN SERVICIO | S21110200055 | New_Event |  |  | Include | Wildlife | 96 | 2021-11-02 | 164736 | keep | 0 | Nov | 2021 | 0.1122 | 0.0011688 | Sustained | FALSE | FALSE | Not_TMED_Event | 1716
PONCE | 2021-11-02 12:19 | 2021-11-02 13:44 | 293 | 001:25 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7900 | P21110200031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2021-11-02 | 24905 | keep | 0 | Nov | 2021 | 0.016963 | 0.00019956 | Sustained | FALSE | FALSE | Not_TMED_Event | 293
PONCE | 2021-11-02 12:19 | 2021-11-02 13:44 | 253 | 001:25 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7900 | P21110200031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2021-11-02 | 21505 | keep | 0 | Nov | 2021 | 0.014647 | 0.00017232 | Sustained | FALSE | FALSE | Not_TMED_Event | 253
PONCE | 2021-11-02 12:19 | 2021-11-02 13:44 | 900 | 001:25 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7900 | P21110200031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2021-11-02 | 76500 | keep | 0 | Nov | 2021 | 0.052104 | 0.00061299 | Sustained | FALSE | FALSE | Not_TMED_Event | 900
PONCE | 2021-11-02 12:19 | 2021-11-02 13:44 | 1615 | 001:25 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7900 | P21110200031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2021-11-02 | 137275 | keep | 0 | Nov | 2021 | 0.093497 | 0.0011 | Sustained | FALSE | FALSE | Not_TMED_Event | 1615
PONCE | 2021-11-02 12:19 | 2021-11-02 13:44 | 3 | 001:25 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7900 | P21110200031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2021-11-02 | 255 | keep | 0 | Nov | 2021 | 0.00017368 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2021-11-02 12:34 | 2021-11-02 15:41 | 40 | 003:07 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21110200045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2021-11-02 | 7480 | keep | 0 | Nov | 2021 | 0.0050946 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2021-11-02 12:38 | 2021-11-02 13:23 | 4 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONECTORES SECUNDARIOS | A21110200027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2021-11-02 | 180 | keep | 0 | Nov | 2021 | 0.0001226 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-11-02 12:58 | 2021-11-02 20:22 | 50 | 007:24 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | M21110200048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 444 | 2021-11-02 | 22200 | keep | 0 | Nov | 2021 | 0.01512 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-11-02 13:13 | 2021-11-02 14:05 | 13 | 000:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE | R21110200045 | New_Event | Cutout Failure | Include | Include | Equipment | 52 | 2021-11-02 | 676 | keep | 0 | Nov | 2021 | 0.00046042 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2021-11-02 13:17 | 2021-11-02 16:34 | 10 | 003:17 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21110200050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2021-11-02 | 1970 | keep | 0 | Nov | 2021 | 0.0013418 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-11-02 13:20 | 2021-11-02 18:23 | 1 | 005:03 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER NO CAUSA | C21110200050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 303 | 2021-11-02 | 303 | keep | 0 | Nov | 2021 | 0.00020637 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-02 13:39 | 2021-11-02 15:56 | 50 | 002:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA | S21110200075 | New_Event | Cutout Failure | Include | Include | Equipment | 137 | 2021-11-02 | 6850 | keep | 0 | Nov | 2021 | 0.0046655 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-11-02 13:46 | 2021-11-03 18:08 | 15 | 028:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE | C21110200054 | New_Event | Cutout Failure | Include | Include | Equipment | 1702 | 2021-11-02 | 25530 | keep | 0 | Nov | 2021 | 0.017388 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-11-02 13:47 | 2021-11-02 16:34 | 1 | 002:47 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 140 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21110200054 | New_Event | Bad Weather | Include | Include | Weather | 167 | 2021-11-02 | 167 | keep | 0 | Nov | 2021 | 0.00011374 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-02 13:51 | 2021-11-02 14:41 | 500 | 000:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO PARA RETIRAR CHANGO CRUZANDO MACHETE EN LA CARR 844 FRENTE A GALERIO PACIFICO | S21110200055 | Partial_restoration |  |  | Include | Wildlife | 50 | 2021-11-02 | 25000 | keep | 0 | Nov | 2021 | 0.017027 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-11-02 14:40 | 2021-11-02 14:41 | 25 | 000:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA QUEMADA | P21110200019 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-11-02 | 25 | keep | 0 | Nov | 2021 | 1.7027e-05 | 1.7027e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-11-02 14:41 | 2021-11-02 15:07 | 1780 | 000:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE CERRO MACHETE 80% EN SERVICIO | S21110200055 | Additional_clients |  |  | Include | Wildlife | 26 | 2021-11-02 | 46280 | keep | 0 | Nov | 2021 | 0.031521 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2021-11-02 14:54 | 2021-11-02 16:55 | 10 | 002:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR CRUCE POR CHANGO | R21110200052 | New_Event |  |  | Include | Wildlife | 121 | 2021-11-02 | 1210 | keep | 0 | Nov | 2021 | 0.00082413 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2021-11-02 15:10 | 2021-11-02 16:20 | 100 | 001:10 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21110200058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2021-11-02 | 7000 | keep | 0 | Nov | 2021 | 0.0047677 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-02 15:22 | 2021-11-02 15:55 | 12 | 000:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21110200040 | New_Event | Bad Weather | Include | Include | Weather | 33 | 2021-11-02 | 396 | keep | 0 | Nov | 2021 | 0.00026971 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-11-02 15:37 | 2021-11-02 19:21 | 1 | 003:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | C21110200063 | New_Event |  |  | Include | Wildlife | 224 | 2021-11-02 | 224 | keep | 0 | Nov | 2021 | 0.00015257 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-02 15:51 | 2021-11-02 15:52 | 3 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21110200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 3 | keep | 0 | Nov | 2021 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-11-02 16:09 | 2021-11-02 18:00 | 30 | 001:51 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO ENREDADERAS | M21110200085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2021-11-02 | 3330 | keep | 0 | Nov | 2021 | 0.002268 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-11-02 16:10 | 2021-11-02 16:13 | 3800 | 000:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO | S21110200000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 3 | 2021-11-02 | 11400 | keep | 0 | Nov | 2021 | 0.0077645 | 0.0025882 | Momentary | FALSE | FALSE | Not_TMED_Event | 3800
SAN JUAN | 2021-11-02 16:13 | 2021-11-02 16:40 | 3800 | 000:27 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO | S21110200000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 27 | 2021-11-02 | 102600 | keep | 0 | Nov | 2021 | 0.06988 | 0.0025882 | Sustained | FALSE | FALSE | Not_TMED_Event | 3800
SAN JUAN | 2021-11-02 16:40 | 2021-11-02 19:06 | 180 | 002:26 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRE MACHETE PARA REMPLAZAR AISLADOR PARTIDO | S21110200114 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 146 | 2021-11-02 | 26280 | keep | 0 | Nov | 2021 | 0.017899 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-11-02 16:49 | 2021-11-02 16:50 | 1922 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO | C21110200071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 1922 | keep | 0 | Nov | 2021 | 0.0013091 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
YAUCO | 2021-11-02 16:51 | 2021-11-03 10:43 | 103 | 017:52 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21110200074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1072 | 2021-11-02 | 110416 | keep | 0 | Nov | 2021 | 0.075204 | 7.0153e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 103
ARECIBO | 2021-11-02 16:53 | 2021-11-02 20:14 | 7 | 003:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21110200044 | New_Event | Bad Weather | Include | Include | Weather | 201 | 2021-11-02 | 1407 | keep | 0 | Nov | 2021 | 0.0009583 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-11-02 16:58 | 2021-11-02 20:32 | 180 | 003:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA | S21110200116 | New_Event | Cutout Failure | Include | Include | Equipment | 214 | 2021-11-02 | 38520 | keep | 0 | Nov | 2021 | 0.026236 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
MAYAGÃœEZ | 2021-11-02 17:08 | 2021-11-02 18:03 | 4 | 000:55 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21110200096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2021-11-02 | 220 | keep | 0 | Nov | 2021 | 0.00014984 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2021-11-02 17:16 | 2021-11-03 11:26 | 96 | 018:10 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO FLAMBOYAN DE LA LINEA | C21110200074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1090 | 2021-11-02 | 104640 | keep | 0 | Nov | 2021 | 0.07127 | 6.5385e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 96
UTUADO | 2021-11-02 17:20 | 2021-11-02 18:50 | 7 | 001:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21110200046 | New_Event | Bad Weather | Include | Include | Weather | 90 | 2021-11-02 | 630 | keep | 0 | Nov | 2021 | 0.00042909 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2021-11-02 17:21 | 2021-11-03 15:03 | 30 | 021:42 | P | DESGANCHE | 1 X 30 EN C/L | R21110200054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1302 | 2021-11-02 | 39060 | keep | 0 | Nov | 2021 | 0.026604 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-11-02 17:33 | 2021-11-02 19:05 | 10 | 001:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO TRANSFORMADOR PARA REPARAR TUBERIA DE ACUEDUCTOS AVERIADA DURANTE EXCAVACION | S21110200120 | New_Event |  |  | Include | Wildlife | 92 | 2021-11-02 | 920 | keep | 0 | Nov | 2021 | 0.00062661 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-02 18:01 | 2021-11-02 19:40 | 60 | 001:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO | A21110200049 | New_Event | Wire Down | Include | Include | Equipment | 99 | 2021-11-02 | 5940 | keep | 0 | Nov | 2021 | 0.0040457 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-11-02 18:28 | 2021-11-02 20:05 | 280 | 001:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21110200052 | New_Event | Bad Weather | Include | Include | Weather | 97 | 2021-11-02 | 27160 | keep | 0 | Nov | 2021 | 0.018499 | 0.00019071 | Sustained | FALSE | FALSE | Not_TMED_Event | 280
BAYAMON | 2021-11-02 18:50 | 2021-11-02 22:58 | 20 | 004:08 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER LLEVA EL 1911-07 | S21110200130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 248 | 2021-11-02 | 4960 | keep | 0 | Nov | 2021 | 0.0033782 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-11-02 18:56 | 2021-11-02 19:00 | 761 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO LLEVA 1421-01 | S21110200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-11-02 | 3044 | keep | 0 | Nov | 2021 | 0.0020733 | 0.00051831 | Momentary | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2021-11-02 18:56 | 2021-11-02 19:00 | 1498 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO CARGA POR EL 1310-04 | S21110200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-11-02 | 5992 | keep | 0 | Nov | 2021 | 0.0040811 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
VEGA BAJA | 2021-11-02 18:57 | 2021-11-03 19:47 | 10 | 024:50 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 37.5 KVA | B21110200057 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1490 | 2021-11-02 | 14900 | keep | 0 | Nov | 2021 | 0.010148 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-11-02 18:58 | 2021-11-02 18:59 | 1862 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3100 DE CANOVANAS TC A BARRAZA | R21110200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-02 | 1862 | keep | 0 | Nov | 2021 | 0.0012682 | 0.0012682 | Momentary | FALSE | FALSE | Not_TMED_Event | 1862
SAN JUAN | 2021-11-02 18:58 | 2021-11-02 18:59 | 1613 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3100 DE CANOVANAS TC A BARRAZA | R21110200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-02 | 1613 | keep | 0 | Nov | 2021 | 0.0010986 | 0.0010986 | Momentary | FALSE | FALSE | Not_TMED_Event | 1613
SAN JUAN | 2021-11-02 18:58 | 2021-11-02 18:59 | 1448 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3100 DE CANOVANAS TC A BARRAZA | R21110200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-02 | 1448 | keep | 0 | Nov | 2021 | 0.00098623 | 0.00098623 | Momentary | FALSE | FALSE | Not_TMED_Event | 1448
MAYAGÃœEZ | 2021-11-02 19:01 | 2021-11-02 20:24 | 80 | 001:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21110200102 | New_Event | Bad Weather | Include | Include | Weather | 83 | 2021-11-02 | 6640 | keep | 0 | Nov | 2021 | 0.0045225 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2021-11-02 19:02 | 2021-11-03 14:46 | 7 | 019:44 | P | PARARRAYOS DEFECTUOSO | 1 X 15 EN TRANSFORMADOR ELIMINO PARARRAYO | R21110200059 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1184 | 2021-11-02 | 8288 | keep | 0 | Nov | 2021 | 0.0056449 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-11-02 19:07 | 2021-11-02 20:43 | 40 | 001:36 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA LLEVA EL 1720-08 | S21110200141 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2021-11-02 | 3840 | keep | 0 | Nov | 2021 | 0.0026154 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-02 19:07 | 2021-11-02 20:43 | 1 | 001:36 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA CARGA POR EL 1709-02 | B21110200141 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2021-11-02 | 96 | keep | 0 | Nov | 2021 | 6.5385e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-02 19:10 | 2021-11-02 19:11 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1206-02 | S21110200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 641 | keep | 0 | Nov | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-11-02 19:10 | 2021-11-02 19:11 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR EL 1206-01 | S21110200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 733 | keep | 0 | Nov | 2021 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2021-11-02 19:11 | 2021-11-02 19:12 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1206-02 | S21110200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 641 | keep | 0 | Nov | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-11-02 19:11 | 2021-11-02 19:12 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR EL 1206-01 | S21110200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 733 | keep | 0 | Nov | 2021 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2021-11-02 19:14 | 2021-11-02 19:15 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1206-02 | S21110200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 641 | keep | 0 | Nov | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-11-02 19:14 | 2021-11-02 19:15 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR EL 1206-01 | S21110200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 733 | keep | 0 | Nov | 2021 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2021-11-02 19:20 | 2021-11-02 19:22 | 225 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO CARGA POR EL 1303-05 | S21110200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-02 | 450 | keep | 0 | Nov | 2021 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-11-02 19:20 | 2021-11-02 19:22 | 870 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO LLEVA 1303-04 | S21110200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-02 | 1740 | keep | 0 | Nov | 2021 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
VEGA BAJA | 2021-11-02 19:23 | 2021-11-02 19:24 | 31 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA | B21110200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 31 | keep | 0 | Nov | 2021 | 2.1114e-05 | 2.1114e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 31
BAYAMON | 2021-11-02 19:28 | 2021-11-03 09:31 | 20 | 014:03 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21110200060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 843 | 2021-11-02 | 16860 | keep | 0 | Nov | 2021 | 0.011483 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-11-02 19:49 | 2021-11-02 23:16 | 150 | 003:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA PUNTO CALIENTE EN CONECTOR DE LINEA | A21110200059 | New_Event | Wire Down | Include | Include | Equipment | 207 | 2021-11-02 | 31050 | keep | 0 | Nov | 2021 | 0.021148 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2021-11-02 20:02 | 2021-11-02 20:03 | 478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA PARTE 1705 03 | B21110200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 478 | keep | 0 | Nov | 2021 | 0.00032556 | 0.00032556 | Momentary | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2021-11-02 20:02 | 2021-11-02 20:03 | 850 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR PARTE POR 1705 01 | B21110200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 850 | keep | 0 | Nov | 2021 | 0.00057893 | 0.00057893 | Momentary | FALSE | FALSE | Not_TMED_Event | 850
SAN JUAN | 2021-11-02 20:03 | 2021-11-02 20:04 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1206-02 | S21110200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 641 | keep | 0 | Nov | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-11-02 20:03 | 2021-11-02 20:04 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR EL 1206-01 | S21110200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 733 | keep | 0 | Nov | 2021 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
BAYAMON | 2021-11-02 20:03 | 2021-11-02 20:04 | 478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA PARTE 1705 03 | B21110200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 478 | keep | 0 | Nov | 2021 | 0.00032556 | 0.00032556 | Momentary | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2021-11-02 20:03 | 2021-11-02 20:04 | 850 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR PARTE POR 1705 01 | B21110200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 850 | keep | 0 | Nov | 2021 | 0.00057893 | 0.00057893 | Momentary | FALSE | FALSE | Not_TMED_Event | 850
BAYAMON | 2021-11-02 20:03 | 2021-11-02 20:05 | 130 | 000:02 | P | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 ALIMENTADOR PARTE DE SU CARGA POR 1717 04 | B21110200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-02 | 260 | keep | 0 | Nov | 2021 | 0.00017708 | 8.8542e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 130
BAYAMON | 2021-11-02 20:03 | 2021-11-02 20:05 | 4533 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 | B21110200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-02 | 9066 | keep | 0 | Nov | 2021 | 0.0061748 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
BAYAMON | 2021-11-02 20:03 | 2021-11-02 20:05 | 911 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 | B21110200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-02 | 1822 | keep | 0 | Nov | 2021 | 0.001241 | 0.00062048 | Momentary | FALSE | FALSE | Not_TMED_Event | 911
BAYAMON | 2021-11-02 20:03 | 2021-11-02 20:05 | 4431 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 ALIMENTADOR 1717 04 LLEVA PARTE 1716 02 | B21110200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-02 | 8862 | keep | 0 | Nov | 2021 | 0.0060359 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
BAYAMON | 2021-11-02 20:03 | 2021-11-02 20:05 | 1362 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 | B21110200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-02 | 2724 | keep | 0 | Nov | 2021 | 0.0018553 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
BAYAMON | 2021-11-02 20:03 | 2021-11-02 20:05 | 341 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 ALIMENTADOR 1717 04 LLEVA PARTE 1716 02 | B21110200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-02 | 682 | keep | 0 | Nov | 2021 | 0.00046451 | 0.00023225 | Momentary | FALSE | FALSE | Not_TMED_Event | 341
SAN JUAN | 2021-11-02 20:13 | 2021-11-02 21:20 | 1681 | 001:07 | T | DESGANCHE | DISPARO NO RECERRO SE PATRULLO SE RETIRO RAMA SOBRE LINEA SALIDA INTERUPTOR SE CERRO QUEDO EN SERVICIO CARGA POR EL 1303-04 | S21110200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2021-11-02 | 112627 | keep | 0 | Nov | 2021 | 0.07671 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-11-02 20:13 | 2021-11-02 20:14 | 726 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL QUEDO EN SERVICIO LLEVA 1346-04 | S21110200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 726 | keep | 0 | Nov | 2021 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-11-02 20:13 | 2021-11-02 20:14 | 3932 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL QUEDO EN SERVICIO CARGA POR EL 1303-03 | S21110200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 3932 | keep | 0 | Nov | 2021 | 0.0026781 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
SAN JUAN | 2021-11-02 20:13 | 2021-11-02 21:20 | 225 | 001:07 | T | DESGANCHE | DISPARO NO RECERRO SE PATRULLO SE RETIRO RAMA SOBRE LINEA EN SALIDA DE INTERUPTOR SE CERRO QUEDO EN SERVICIO CARGA POR EL 1303-04 | S21110200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2021-11-02 | 15075 | keep | 0 | Nov | 2021 | 0.010268 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
AGUADILLA | 2021-11-02 20:31 | 2021-11-03 09:58 | 15 | 013:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA CRUZADA POR CAMION QUE LA IMPACTO | M21110200112 | New_Event |  |  | Include | Wildlife | 807 | 2021-11-02 | 12105 | keep | 0 | Nov | 2021 | 0.0082447 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-11-02 20:31 | 2021-11-02 20:32 | 5042 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | A21110200061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 5042 | keep | 0 | Nov | 2021 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
ARECIBO | 2021-11-02 20:35 | 2021-11-02 20:36 | 5042 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | A21110200062 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 5042 | keep | 0 | Nov | 2021 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
CANOVANAS | 2021-11-02 20:42 | 2021-11-03 12:39 | 80 | 015:57 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21110200061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 957 | 2021-11-02 | 76560 | keep | 0 | Nov | 2021 | 0.052145 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-11-02 21:14 | 2021-11-03 09:16 | 40 | 012:02 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21110200077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 722 | 2021-11-02 | 28880 | keep | 0 | Nov | 2021 | 0.01967 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-11-02 21:19 | 2021-11-02 21:20 | 2777 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | A21110200067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 2777 | keep | 0 | Nov | 2021 | 0.0018914 | 0.0018914 | Momentary | FALSE | FALSE | Not_TMED_Event | 2777
VEGA BAJA | 2021-11-02 21:22 | 2021-11-03 14:48 | 20 | 017:26 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21110200078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1046 | 2021-11-02 | 20920 | keep | 0 | Nov | 2021 | 0.014249 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-11-02 21:41 | 2021-11-03 11:04 | 70 | 013:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA AVERIADA DE 100 AMP. MARCA CHINT Y SE REALIZO DESGANCHE | A21110200068 | New_Event | Cutout Failure | Include | Include | Equipment | 803 | 2021-11-02 | 56210 | keep | 0 | Nov | 2021 | 0.038284 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2021-11-02 22:07 | 2021-11-03 12:20 | 40 | 014:13 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21110200082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 853 | 2021-11-02 | 34120 | keep | 0 | Nov | 2021 | 0.023239 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-11-02 22:08 | 2021-11-03 09:02 | 64 | 010:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21110200086 | New_Event | Bad Weather | Include | Include | Weather | 654 | 2021-11-02 | 41856 | keep | 0 | Nov | 2021 | 0.028508 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
SAN JUAN | 2021-11-02 22:29 | 2021-11-02 22:30 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA EL 1206-02 | S21110200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 641 | keep | 0 | Nov | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-11-02 22:29 | 2021-11-02 22:30 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR EL 1206-01 | S21110200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 733 | keep | 0 | Nov | 2021 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
AGUADILLA | 2021-11-02 22:44 | 2021-11-03 16:45 | 20 | 018:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR Y SE AJUSTO VOLTAJE SECUNDARIO A TRANSFORMADOR | M21110200116 | New_Event | Wire Down | Include | Include | Equipment | 1081 | 2021-11-02 | 21620 | keep | 0 | Nov | 2021 | 0.014725 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2021-11-02 23:14 | 2021-11-03 11:52 | 20 | 012:38 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21110200072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 758 | 2021-11-02 | 15160 | keep | 0 | Nov | 2021 | 0.010325 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-11-02 23:24 | 2021-11-02 23:25 | 1500 | 000:01 | P | NO SE REPORTO CAUSA | INTERRUPTOR RECERRO Y LLEVA EL 40% DEL 9002-03 | B21110200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 1500 | keep | 0 | Nov | 2021 | 0.0010216 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
HUMACAO | 2021-11-02 23:34 | 2021-11-03 12:12 | 247 | 012:38 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO AISLADOR ROTO | C21110200088 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 758 | 2021-11-02 | 187226 | keep | 0 | Nov | 2021 | 0.12752 | 0.00016823 | Sustained | FALSE | FALSE | Not_TMED_Event | 247
MAYAGÃœEZ | 2021-11-02 23:34 | 2021-11-10 18:24 | 15 | 186:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA AVERIADA | M21110200009 | New_Event | Secondary Wire Down | Include | Include | Equipment | 11210 | 2021-11-02 | 168150 | keep | 0 | Nov | 2021 | 0.11453 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2021-11-02 23:40 | 2021-11-03 10:20 | 30 | 010:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA QUEMADA | R21110200079 | New_Event | Cutout Failure | Include | Include | Equipment | 640 | 2021-11-02 | 19200 | keep | 0 | Nov | 2021 | 0.013077 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-11-02 23:49 | 2021-11-03 12:13 | 11 | 012:24 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN RISER @ T-46 BUSHING AVERIADO EN T-46 | R21100200080 | New_Event | Service Transformer Failure | Include | Include | Equipment | 744 | 2021-11-02 | 8184 | keep | 0 | Nov | 2021 | 0.0055741 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
HUMACAO | 2021-11-02 23:53 | 2021-11-02 23:54 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21110200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-02 | 2354 | keep | 0 | Nov | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
SAN JUAN | 2021-11-02 23:57 | 2021-11-03 01:03 | 1447 | 001:06 | T | NO SE REPORTO CAUSA | INTERRUPTOR DISPARO Y SE CERRO POR CONTROL LLEVA EL 1419-09 Y EL 1419-12 | S21110200285 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 66 | 2021-11-02 | 95502 | keep | 0 | Nov | 2021 | 0.065046 | 0.00098555 | Sustained | FALSE | FALSE | Not_TMED_Event | 1447
SAN JUAN | 2021-11-02 23:57 | 2021-11-03 01:03 | 266 | 001:06 | T | NO SE REPORTO CAUSA | INTERRUPTOR DISPARO Y SE CERRO POR CONTROL CARGA TRANSFERIDA AL 1112-04 | S21110200258 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 66 | 2021-11-02 | 17556 | keep | 0 | Nov | 2021 | 0.011957 | 0.00018117 | Sustained | FALSE | FALSE | Not_TMED_Event | 266
SAN JUAN | 2021-11-02 23:57 | 2021-11-03 01:03 | 73 | 001:06 | T | NO SE REPORTO CAUSA | INTERRUPTOR DISPARO Y SE CERRO POR CONTROL CARGA TRANSFERIDA AL 1112-04 | S21110300258 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 66 | 2021-11-02 | 4818 | keep | 0 | Nov | 2021 | 0.0032815 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
AGUADILLA | 2021-11-03 00:13 | 2021-11-03 00:14 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21110300001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-03 | 1192 | keep | 0 | Nov | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
VEGA BAJA | 2021-11-03 00:18 | 2021-11-03 00:19 | 3000 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21110300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-03 | 3000 | keep | 0 | Nov | 2021 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
SAN JUAN | 2021-11-03 00:40 | 2021-11-03 12:03 | 25 | 011:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO CONDUCTOR A CAJA | S21110300030 | New_Event | Wire Down | Include | Include | Equipment | 683 | 2021-11-03 | 17075 | keep | 0 | Nov | 2021 | 0.01163 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2021-11-03 01:02 | 2021-11-03 12:49 | 40 | 011:47 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO CAUSA | R21110300003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 707 | 2021-11-03 | 28280 | keep | 0 | Nov | 2021 | 0.019261 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-11-03 01:21 | 2021-11-03 10:43 | 180 | 009:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA QUEMADA | R21110300006 | New_Event | Cutout Failure | Include | Include | Equipment | 562 | 2021-11-03 | 101160 | keep | 0 | Nov | 2021 | 0.0689 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
SAN JUAN | 2021-11-03 02:47 | 2021-11-03 09:51 | 15 | 007:04 | P | NO SE REPORTO CAUSA | 1 X 10 EN RISER | S21110300048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 424 | 2021-11-03 | 6360 | keep | 0 | Nov | 2021 | 0.0043318 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-11-03 02:55 | 2021-11-03 17:49 | 19 | 014:54 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN RISER SE DEJO FUERA EL T-3 POR AVERIA SOTERRADA DEL T-2 AL T-3 | C21110300006 | New_Event | UG Cable Fault | Include | Include | Equipment | 894 | 2021-11-03 | 16986 | keep | 0 | Nov | 2021 | 0.011569 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
HUMACAO | 2021-11-03 03:06 | 2021-11-03 03:07 | 1835 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21110300013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-03 | 1835 | keep | 0 | Nov | 2021 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
CAGUAS | 2021-11-03 03:50 | 2021-11-03 09:50 | 257 | 006:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | C21110300009 | New_Event | Cutout Failure | Include | Include | Equipment | 360 | 2021-11-03 | 92520 | keep | 0 | Nov | 2021 | 0.063015 | 0.00017504 | Sustained | FALSE | FALSE | Not_TMED_Event | 257
MAYAGÃœEZ | 2021-11-03 03:51 | 2021-11-03 11:10 | 20 | 007:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M21110300002 | New_Event | Bad Weather | Include | Include | Weather | 439 | 2021-11-03 | 8780 | keep | 0 | Nov | 2021 | 0.00598 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-11-03 04:41 | 2021-11-03 19:48 | 300 | 015:07 | P | DESCONECTIVO DEFECTUOSO | REMPLAZO 3 MACHETES Y BAJANTES PRIMARIOS | R21110300017 | New_Event | Switch Failure | Include | Include | Equipment | 907 | 2021-11-03 | 272100 | keep | 0 | Nov | 2021 | 0.18533 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-11-03 04:49 | 2021-11-03 11:09 | 10 | 006:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21110300004 | New_Event | Bad Weather | Include | Include | Weather | 380 | 2021-11-03 | 3800 | keep | 0 | Nov | 2021 | 0.0025882 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-03 04:50 | 2021-11-03 09:01 | 40 | 004:11 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21110300005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 251 | 2021-11-03 | 10040 | keep | 0 | Nov | 2021 | 0.0068382 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-11-03 05:41 | 2021-11-03 05:42 | 2608 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21110300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-03 | 2608 | keep | 0 | Nov | 2021 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
SAN JUAN | 2021-11-03 06:04 | 2021-11-03 06:07 | 225 | 000:03 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL CARGA TRANSFERIDA AL 1303-05 | S21110300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-11-03 | 675 | keep | 0 | Nov | 2021 | 0.00045974 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-11-03 06:04 | 2021-11-03 06:07 | 870 | 000:03 | T | DESGANCHE | SE CERRO POR SCADA | S21110300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-11-03 | 2610 | keep | 0 | Nov | 2021 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
AGUADILLA | 2021-11-03 06:16 | 2021-11-03 10:49 | 200 | 004:33 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | M21110300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 273 | 2021-11-03 | 54600 | keep | 0 | Nov | 2021 | 0.037188 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2021-11-03 06:42 | 2021-11-03 10:40 | 30 | 003:58 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21110300003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2021-11-03 | 7140 | keep | 0 | Nov | 2021 | 0.004863 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2021-11-03 06:49 | 2021-11-03 11:17 | 1124 | 004:28 | T | NO SE REPORTO CAUSA | SE CERRO INTERRUPTOR EN SUBESTACION SIN RTU NO SE REPORTO CAUSA | R21110300046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 268 | 2021-11-03 | 301232 | keep | 0 | Nov | 2021 | 0.20517 | 0.00076555 | Sustained | FALSE | FALSE | Not_TMED_Event | 1124
BAYAMON | 2021-11-03 07:06 | 2021-11-03 07:07 | 1533 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA CARGA 1709-05 | S21110300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-03 | 1533 | keep | 0 | Nov | 2021 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
BAYAMON | 2021-11-03 07:06 | 2021-11-03 07:07 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPCION LLEVA CARGA POR 1709 03 | B21110300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-03 | 2364 | keep | 0 | Nov | 2021 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
BAYAMON | 2021-11-03 07:07 | 2021-11-03 11:52 | 1 | 004:45 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21110300057 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 285 | 2021-11-03 | 285 | keep | 0 | Nov | 2021 | 0.00019411 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-11-03 07:07 | 2021-11-03 10:34 | 113 | 003:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21110300028 | New_Event | Bad Weather | Include | Include | Weather | 207 | 2021-11-03 | 23391 | keep | 0 | Nov | 2021 | 0.015932 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
BARRANQUITAS | 2021-11-03 07:07 | 2021-11-03 10:13 | 35 | 003:06 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO | C21110300017 | New_Event | Bad Weather | Include | Include | Weather | 186 | 2021-11-03 | 6510 | keep | 0 | Nov | 2021 | 0.0044339 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2021-11-03 07:09 | 2021-11-03 11:14 | 20 | 004:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE RETIRO AVE | B21110300011 | New_Event |  |  | Include | Wildlife | 245 | 2021-11-03 | 4900 | keep | 0 | Nov | 2021 | 0.0033374 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-11-03 07:12 | 2021-11-03 07:13 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA A TRAVES DEL 1206-03 | S21110300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-03 | 10211 | keep | 0 | Nov | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-11-03 07:12 | 2021-11-03 07:13 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 1204-5 | S21110300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-03 | 4133 | keep | 0 | Nov | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
PONCE | 2021-11-03 07:14 | 2021-11-03 07:15 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21110300008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-03 | 2113 | keep | 0 | Nov | 2021 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
UTUADO | 2021-11-03 07:59 | 2021-11-03 10:47 | 40 | 002:48 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO ENREDADERA DEL POSTE | A21110300005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2021-11-03 | 6720 | keep | 0 | Nov | 2021 | 0.004577 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-03 08:05 | 2021-11-03 10:24 | 1 | 002:19 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | B21110300019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 139 | 2021-11-03 | 139 | keep | 0 | Nov | 2021 | 9.4672e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-03 08:21 | 2021-11-03 13:49 | 30 | 005:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE LEVANTO ALMBRE PRIMARIO SE REALIZO DESGANCHE Y SE REMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | B21110300024 | New_Event | Wire Down | Include | Include | Equipment | 328 | 2021-11-03 | 9840 | keep | 0 | Nov | 2021 | 0.006702 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-11-03 08:29 | 2021-11-03 08:30 | 271 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21110300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-03 | 271 | keep | 0 | Nov | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
SAN JUAN | 2021-11-03 08:44 | 2021-11-03 12:52 | 20 | 004:08 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L | S21110300056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 248 | 2021-11-03 | 4960 | keep | 0 | Nov | 2021 | 0.0033782 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-11-03 08:53 | 2021-11-03 14:45 | 42 | 005:52 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21110300023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 352 | 2021-11-03 | 14784 | keep | 0 | Nov | 2021 | 0.010069 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
MAYAGÃœEZ | 2021-11-03 08:56 | 2021-11-03 08:57 | 637 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE PROBO Y QUEDO EN SERVICIO LLEVA LA CARGA DEL 6703-03 | M21110300020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-03 | 637 | keep | 0 | Nov | 2021 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
MAYAGÃœEZ | 2021-11-03 08:56 | 2021-11-03 08:57 | 1491 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 6703-02 QUE ESTA LLEVANDO LA CARGA DEL 6702-03 SE PROBO Y QUEDO EN SERVICIO | M21110300020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-03 | 1491 | keep | 0 | Nov | 2021 | 0.0010155 | 0.0010155 | Momentary | FALSE | FALSE | Not_TMED_Event | 1491
CAGUAS | 2021-11-03 09:04 | 2021-11-03 10:56 | 12 | 001:52 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR NO SE LE PUDO BAJAR TAP SE PASO LA CARGA A OTRO CERCANO | C21110300026 | New_Event | Service Transformer Failure | Include | Include | Equipment | 112 | 2021-11-03 | 1344 | keep | 0 | Nov | 2021 | 0.00091539 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-11-03 09:11 | 2021-11-03 11:03 | 6 | 001:52 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR REQUIERE DESGANCHE | A21110300009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2021-11-03 | 672 | keep | 0 | Nov | 2021 | 0.0004577 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-11-03 09:20 | 2021-11-03 09:25 | 6244 | 000:05 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S21110300065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-11-03 | 31220 | keep | 0 | Nov | 2021 | 0.021264 | 0.0042528 | Momentary | FALSE | FALSE | Not_TMED_Event | 6244
CANOVANAS | 2021-11-03 09:46 | 2021-11-03 15:05 | 10 | 005:19 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | R21110300085 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 319 | 2021-11-03 | 3190 | keep | 0 | Nov | 2021 | 0.0021727 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-11-03 09:56 | 2021-11-03 20:44 | 10 | 010:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR TOMAS Y SECUNDARIAS | B21110300028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 648 | 2021-11-03 | 6480 | keep | 0 | Nov | 2021 | 0.0044135 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-11-03 10:04 | 2021-11-03 13:01 | 761 | 002:57 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CONDUCTOR AISLADOR Y SE REMPLAZO CAJA LLEVA EL 1421-01 | S21110300000 | New_Event | Wire Down | Include | Include | Equipment | 177 | 2021-11-03 | 134697 | keep | 0 | Nov | 2021 | 0.091742 | 0.00051831 | Sustained | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2021-11-03 10:04 | 2021-11-03 13:01 | 1498 | 002:57 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CONDUCTOR AISLADOR Y SE REMPLAZO CAJA CARGA TRANSFERIDA AL 1310-04 | S21110300071 | New_Event | Wire Down | Include | Include | Equipment | 177 | 2021-11-03 | 265146 | keep | 0 | Nov | 2021 | 0.18059 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
ARECIBO | 2021-11-03 10:05 | 2021-11-04 10:55 | 8 | 024:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA DE TRANSFORMADOR AVERIADA EN EL FID 33984466 MARCA CHINT 100AMP | A21110300061 | New_Event | Cutout Failure | Include | Include | Equipment | 1490 | 2021-11-03 | 11920 | keep | 0 | Nov | 2021 | 0.0081187 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-11-03 10:06 | 2021-11-03 17:30 | 1 | 007:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN RISER MAL TIEMPO | C21110300030 | New_Event | Bad Weather | Include | Include | Weather | 444 | 2021-11-03 | 444 | keep | 0 | Nov | 2021 | 0.00030241 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-11-03 10:10 | 2021-11-03 10:36 | 33 | 000:26 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C21110200082 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 26 | 2021-11-03 | 858 | keep | 0 | Nov | 2021 | 0.00058438 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
HUMACAO | 2021-11-03 10:15 | 2021-11-03 10:16 | 1467 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR | C21110300032 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-11-03 | 1467 | keep | 0 | Nov | 2021 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
HUMACAO | 2021-11-03 10:16 | 2021-11-03 16:38 | 260 | 006:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | C21110300054 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 382 | 2021-11-03 | 99320 | keep | 0 | Nov | 2021 | 0.067646 | 0.00017708 | Sustained | FALSE | FALSE | Not_TMED_Event | 260
BAYAMON | 2021-11-03 10:17 | 2021-11-03 10:18 | 34 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7500 | S21110300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-03 | 34 | keep | 0 | Nov | 2021 | 2.3157e-05 | 2.3157e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 34
BAYAMON | 2021-11-03 10:17 | 2021-11-03 10:18 | 19 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7500 | S21110300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-03 | 19 | keep | 0 | Nov | 2021 | 1.2941e-05 | 1.2941e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2021-11-03 10:17 | 2021-11-03 10:18 | 514 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7500 | S21110300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-03 | 514 | keep | 0 | Nov | 2021 | 0.00035008 | 0.00035008 | Momentary | FALSE | FALSE | Not_TMED_Event | 514
BAYAMON | 2021-11-03 10:17 | 2021-11-03 10:18 | 752 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7500 | S21110300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-03 | 752 | keep | 0 | Nov | 2021 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
BAYAMON | 2021-11-03 10:23 | 2021-11-03 10:24 | 681 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7500 | S21110300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-03 | 681 | keep | 0 | Nov | 2021 | 0.00046383 | 0.00046383 | Momentary | FALSE | FALSE | Not_TMED_Event | 681
BAYAMON | 2021-11-03 10:23 | 2021-11-03 10:24 | 68 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7500 | S21110300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-03 | 68 | keep | 0 | Nov | 2021 | 4.6314e-05 | 4.6314e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 68
AGUADILLA | 2021-11-03 10:25 | 2021-11-03 11:20 | 80 | 000:55 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA DE EMERGENCIA PARA SECCIONALIZAR POSTE PRIMARIO PARTIDO | M21110300046 | New_Event | Defective Pole | Include | Include | Equipment | 55 | 2021-11-03 | 4400 | keep | 0 | Nov | 2021 | 0.0029968 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-11-03 10:26 | 2021-11-03 16:56 | 5 | 006:30 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 50KVA POR LA MISMA CAPACIDAD EN FID 17289196 MARCA HOWARD INDUSTRIES NUMERO SERIE 1255420518 VOLTAJES 7620/13200V 120/240V | M21110300044 | New_Event | Service Transformer Failure | Include | Include | Equipment | 390 | 2021-11-03 | 1950 | keep | 0 | Nov | 2021 | 0.0013281 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-11-03 10:27 | 2021-11-03 10:28 | 6197 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR PORTAFUSIBLE AVERIADO | C21110300037 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-11-03 | 6197 | keep | 0 | Nov | 2021 | 0.0042207 | 0.0042207 | Momentary | FALSE | FALSE | Not_TMED_Event | 6197
CAGUAS | 2021-11-03 10:28 | 2021-11-03 12:24 | 32 | 001:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | C21110300004 | New_Event | Cutout Failure | Include | Include | Equipment | 116 | 2021-11-03 | 3712 | keep | 0 | Nov | 2021 | 0.0025282 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
CAGUAS | 2021-11-03 10:28 | 2021-11-03 12:24 | 65 | 001:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA REMPLAZO PORTAFUSIBLE | C21110300042 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 116 | 2021-11-03 | 7540 | keep | 0 | Nov | 2021 | 0.0051355 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2021-11-03 10:28 | 2021-11-03 11:28 | 13 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C21110200085 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2021-11-03 | 780 | keep | 0 | Nov | 2021 | 0.00053125 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
HUMACAO | 2021-11-03 10:34 | 2021-11-03 13:44 | 1 | 003:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR CHANGO | C21110300038 | New_Event |  |  | Include | Wildlife | 190 | 2021-11-03 | 190 | keep | 0 | Nov | 2021 | 0.00012941 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-11-03 11:20 | 2021-11-03 22:12 | 20 | 010:52 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO DE MADERA DE 45' POR UNO IGUAL Y SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR LA MISMA CAPACIDAD EN EL FID 31229403 MARCA HOWARD INDUSTRIES NUMERO DE SERIE 1597941221 VOLTAJES 2400/4160V 120/240V | M21110300046 | Partial_restoration | Defective Pole | Include | Include | Equipment | 652 | 2021-11-03 | 13040 | keep | 0 | Nov | 2021 | 0.0088815 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-11-03 11:22 | 2021-11-03 14:17 | 237 | 002:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | C21110300048 | New_Event | Bad Weather | Include | Include | Weather | 175 | 2021-11-03 | 41475 | keep | 0 | Nov | 2021 | 0.028248 | 0.00016142 | Sustained | FALSE | FALSE | Not_TMED_Event | 237
CAGUAS | 2021-11-03 11:24 | 2021-11-04 12:20 | 6 | 024:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO SECUNDARIA ABIERTA | C21110300049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1496 | 2021-11-03 | 8976 | keep | 0 | Nov | 2021 | 0.0061135 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-11-03 11:40 | 2021-11-03 11:42 | 850 | 000:02 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE CERRO POR SCADA CARGA EL 95% POR EL 1119-04 | S21110300000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 2 | 2021-11-03 | 1700 | keep | 0 | Nov | 2021 | 0.0011579 | 0.00057893 | Momentary | FALSE | FALSE | Not_TMED_Event | 850
BAYAMON | 2021-11-03 11:40 | 2021-11-03 11:42 | 2720 | 000:02 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE CERRO POR SCADA LLEVA EL 95% DEL 1115-05 | S21110300000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 2 | 2021-11-03 | 5440 | keep | 0 | Nov | 2021 | 0.0037052 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
BAYAMON | 2021-11-03 11:42 | 2021-11-03 20:44 | 100 | 009:02 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACION MH-5A @ MH-5B | S21110300097 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 542 | 2021-11-03 | 54200 | keep | 0 | Nov | 2021 | 0.036915 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-11-03 11:42 | 2021-11-03 16:25 | 11 | 004:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 8 EN TRANSFORMADOR SE SECCIONALIZO TOMA IMPACTADA COLUMNA PARTIDA | C21110300053 | New_Event |  |  | Include | Wildlife | 283 | 2021-11-03 | 3113 | keep | 0 | Nov | 2021 | 0.0021203 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
GUAYAMA | 2021-11-03 11:43 | 2021-11-03 15:22 | 15 | 003:39 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO DE TRANSFORMADOR 50 KVA A 2400 VOLTIOS QUEMADO POR TRANSFORMADOR DE IGUAL CAPACIDAD | P21110300021 | New_Event | Service Transformer Failure | Include | Include | Equipment | 219 | 2021-11-03 | 3285 | keep | 0 | Nov | 2021 | 0.0022374 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-11-03 11:49 | 2021-11-03 13:55 | 8 | 002:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | R21110300098 | New_Event | Secondary Wire Down | Include | Include | Equipment | 126 | 2021-11-03 | 1008 | keep | 0 | Nov | 2021 | 0.00068654 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-11-03 11:59 | 2021-11-03 13:24 | 870 | 001:25 | T | BREAKER DEFECTUOSO O NO OPERA | INTERRUPTOR CON PROBLEMAS SE TRANSFIRIO POR B/I AL 1303-04 | S21110300000 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 85 | 2021-11-03 | 73950 | keep | 0 | Nov | 2021 | 0.050367 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
GUAYAMA | 2021-11-03 12:01 | 2021-11-03 12:24 | 45 | 000:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 40 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P21110300023 | New_Event |  |  | Include | Wildlife | 23 | 2021-11-03 | 1035 | keep | 0 | Nov | 2021 | 0.00070493 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2021-11-03 12:02 | 2021-11-03 12:30 | 20 | 000:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA EN MONTURA DE TRANSFORMADOR | M21110300064 | New_Event | Cutout Failure | Include | Include | Equipment | 28 | 2021-11-03 | 560 | keep | 0 | Nov | 2021 | 0.00038141 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-11-03 12:05 | 2021-11-03 13:35 | 20 | 001:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M21110300066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2021-11-03 | 1800 | keep | 0 | Nov | 2021 | 0.001226 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-11-03 12:23 | 2021-11-03 13:04 | 5 | 000:41 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA NO CAUSA | R21110300102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 41 | 2021-11-03 | 205 | keep | 0 | Nov | 2021 | 0.00013962 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-11-03 12:41 | 2021-11-03 12:47 | 726 | 000:06 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA 1346-04 | S21110300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2021-11-03 | 4356 | keep | 0 | Nov | 2021 | 0.0029669 | 0.00049448 | Sustained | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-11-03 12:41 | 2021-11-03 12:47 | 3932 | 000:06 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA TRANSFERIDA AL 1303-03 | S21110300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2021-11-03 | 23592 | keep | 0 | Nov | 2021 | 0.016068 | 0.0026781 | Sustained | FALSE | FALSE | Not_TMED_Event | 3932
BAYAMON | 2021-11-03 12:46 | 2021-11-03 18:32 | 10 | 005:46 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21110300046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 346 | 2021-11-03 | 3460 | keep | 0 | Nov | 2021 | 0.0023566 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2021-11-03 12:46 | 2021-11-03 14:51 | 152 | 002:05 | P | DESGANCHE | 1 X 50 Y 1 X 65 EN CORTES DE LINEAS CRUCE DE FASE PRIMARIA POR RAMA | P21110300028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2021-11-03 | 19000 | keep | 0 | Nov | 2021 | 0.012941 | 0.00010353 | Sustained | FALSE | FALSE | Not_TMED_Event | 152
MAYAGÃœEZ | 2021-11-03 12:46 | 2021-11-03 14:32 | 6 | 001:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REEMPLAZO LINEA SECUNDARIA | M21110200057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 106 | 2021-11-03 | 636 | keep | 0 | Nov | 2021 | 0.00043318 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-11-03 13:11 | 2021-11-03 13:12 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21110300032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-03 | 2113 | keep | 0 | Nov | 2021 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
AGUADILLA | 2021-11-03 13:49 | 2021-11-03 13:50 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21110300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-03 | 1827 | keep | 0 | Nov | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
CANOVANAS | 2021-11-03 13:50 | 2021-11-03 16:58 | 40 | 003:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 C/L Y 1 X 15 XMR DESGANCHO Y FIJO LINEA ZAFADA POR POR POSTE IMPACTADO | R21110300119 | New_Event |  |  | Include | Wildlife | 188 | 2021-11-03 | 7520 | keep | 0 | Nov | 2021 | 0.0051218 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-11-03 13:50 | 2021-11-03 18:16 | 40 | 004:26 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE Y SE DESPEGO BAJANTE DE CRUCETA | C21110300072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2021-11-03 | 10640 | keep | 0 | Nov | 2021 | 0.0072469 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-11-03 13:50 | 2021-11-03 15:35 | 4 | 001:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA AVERIADA EN TRANSFORMADOR EN EL FID 23625155 MARCA CHINT 100AMP | M21110300084 | New_Event | Cutout Failure | Include | Include | Equipment | 105 | 2021-11-03 | 420 | keep | 0 | Nov | 2021 | 0.00028606 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-11-03 13:50 | 2021-11-03 16:02 | 40 | 002:12 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M21110300033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2021-11-03 | 5280 | keep | 0 | Nov | 2021 | 0.0035962 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2021-11-03 13:52 | 2021-11-03 13:54 | 1089 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3000 DE JUNCOS A RIO BLANCO | C21110300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-03 | 2178 | keep | 0 | Nov | 2021 | 0.0014834 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2021-11-03 13:52 | 2021-11-03 13:54 | 3896 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3000 DE JUNCOS A RIO BLANCO | C21110300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-03 | 7792 | keep | 0 | Nov | 2021 | 0.0053071 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2021-11-03 13:52 | 2021-11-03 13:54 | 1467 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3000 DE JUNCOS A RIO BLANCO | C21110300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-03 | 2934 | keep | 0 | Nov | 2021 | 0.0019983 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
HUMACAO | 2021-11-03 13:53 | 2021-11-03 16:12 | 11 | 002:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA Y TENSOR | C21110200081 | New_Event | Secondary Wire Down | Include | Include | Equipment | 139 | 2021-11-03 | 1529 | keep | 0 | Nov | 2021 | 0.0010414 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
VEGA BAJA | 2021-11-03 13:55 | 2021-11-04 01:16 | 300 | 011:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REMPLAZO POSTE IMPACTADO POR VEHICULO | B21110300053 | New_Event |  |  | Include | Wildlife | 681 | 2021-11-03 | 204300 | keep | 0 | Nov | 2021 | 0.13915 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2021-11-03 14:02 | 2021-11-03 14:59 | 1681 | 000:57 | T | DESGANCHE | DISPARO 1303-04 LLEVANDO CARGA 1303-05,1303-01 Y 1346-06 POR MAL TIEMPO | S21110300128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2021-11-03 | 95817 | keep | 0 | Nov | 2021 | 0.065261 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-11-03 14:02 | 2021-11-03 14:45 | 225 | 000:43 | T | DESGANCHE | DISPARO LLEVANDO CARGA 1303-5,1303-1 Y 1346-6 MAL TIEMPO | S21110300128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 43 | 2021-11-03 | 9675 | keep | 0 | Nov | 2021 | 0.0065896 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-11-03 14:02 | 2021-11-03 14:45 | 225 | 000:43 | T | DESGANCHE | DISPARO DE 1303-04 LLEVANDO CARGA 1303-5,1303-1 Y 1346-6 MAL TIEMPO | S21110300128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 43 | 2021-11-03 | 9675 | keep | 0 | Nov | 2021 | 0.0065896 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-11-03 14:02 | 2021-11-03 14:59 | 1598 | 000:57 | T | DESGANCHE | DISPARO DE 1303-04 LLEVANDO CARGA 1303-05,1303-01 Y 1346-06 MAL TIEMPO | S21110300128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2021-11-03 | 91086 | keep | 0 | Nov | 2021 | 0.062038 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2021-11-03 14:06 | 2021-11-03 14:07 | 859 | 000:01 | P | LINEA DE TRANSMISION 115KV | DISPARO L-36200 CARGA EL 20% POR EL 1303-02 | S21110300128 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-03 | 859 | keep | 0 | Nov | 2021 | 0.00058506 | 0.00058506 | Momentary | FALSE | FALSE | Not_TMED_Event | 859
SAN JUAN | 2021-11-03 14:06 | 2021-11-03 14:07 | 108 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 | S21110300128 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-03 | 108 | keep | 0 | Nov | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
SAN JUAN | 2021-11-03 14:06 | 2021-11-03 14:07 | 1368 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 | S21110300128 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-03 | 1368 | keep | 0 | Nov | 2021 | 0.00093174 | 0.00093174 | Momentary | FALSE | FALSE | Not_TMED_Event | 1368
SAN JUAN | 2021-11-03 14:06 | 2021-11-03 14:07 | 2064 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 | S21110300128 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-03 | 2064 | keep | 0 | Nov | 2021 | 0.0014058 | 0.0014058 | Momentary | FALSE | FALSE | Not_TMED_Event | 2064
SAN JUAN | 2021-11-03 14:06 | 2021-11-03 14:07 | 2435 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 | S21110300128 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-03 | 2435 | keep | 0 | Nov | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2021-11-03 14:06 | 2021-11-03 14:07 | 726 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 LLEVA CARGA 1346-4 | S21110300128 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-03 | 726 | keep | 0 | Nov | 2021 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-11-03 14:06 | 2021-11-03 14:07 | 726 | 000:01 | T | LINEA DE TRANSMISION 115KV | DISPARO L-36200 LLEVA CARGA 1346-4 | S21110300128 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-03 | 726 | keep | 0 | Nov | 2021 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
MAYAGÃœEZ | 2021-11-03 14:06 | 2021-11-03 16:07 | 90 | 002:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA AVERIADA EN CONVERTIDOR EN EL FID 1000942304 MARCA HUBBELL 200AMP | M21110300088 | New_Event | Cutout Failure | Include | Include | Equipment | 121 | 2021-11-03 | 10890 | keep | 0 | Nov | 2021 | 0.0074171 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2021-11-03 14:09 | 2021-11-04 11:52 | 75 | 021:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN C/L, 2 X 80 EN C/L Y SE REMPLAZO CAJA | S21110300133 | New_Event | Cutout Failure | Include | Include | Equipment | 1303 | 2021-11-03 | 97725 | keep | 0 | Nov | 2021 | 0.06656 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2021-11-03 14:16 | 2021-11-03 14:17 | 2402 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR LLEVA CARGA 1720 08 | S21110300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-03 | 2402 | keep | 0 | Nov | 2021 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2021-11-03 14:16 | 2021-11-03 14:17 | 1 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR 1709 02 | S21110300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-03 | 1 | keep | 0 | Nov | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-03 14:17 | 2021-11-03 18:53 | 40 | 004:36 | P | DESGANCHE | 2 X 140 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21110300185 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 276 | 2021-11-03 | 11040 | keep | 0 | Nov | 2021 | 0.0075193 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-11-03 14:25 | 2021-11-03 14:31 | 6 | 000:06 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 10 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21110300034 | New_Event | Bad Weather | Include | Include | Weather | 6 | 2021-11-03 | 36 | keep | 0 | Nov | 2021 | 2.4519e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-11-03 14:28 | 2021-11-03 14:29 | 1588 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA CARGA 1711 05 | B21110300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-03 | 1588 | keep | 0 | Nov | 2021 | 0.0010816 | 0.0010816 | Momentary | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2021-11-03 14:28 | 2021-11-03 14:29 | 1976 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR 1711 01 | B21110300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-03 | 1976 | keep | 0 | Nov | 2021 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
CAGUAS | 2021-11-03 14:32 | 2021-11-03 15:21 | 3 | 000:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA TOTAL PARA CERRAR PUENTE DE LINEA A LINEA | C21110300077 | New_Event | Wire Down | Include | Include | Equipment | 49 | 2021-11-03 | 147 | keep | 0 | Nov | 2021 | 0.00010012 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-11-03 14:40 | 2021-11-03 14:43 | 573 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA CARGA DE 1704 05 | B21110300060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-03 | 1719 | keep | 0 | Nov | 2021 | 0.0011708 | 0.00039027 | Momentary | FALSE | FALSE | Not_TMED_Event | 573
BAYAMON | 2021-11-03 14:40 | 2021-11-03 14:43 | 1313 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR 1704 04 | B21110300060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-03 | 3939 | keep | 0 | Nov | 2021 | 0.0026828 | 0.00089428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1313
BAYAMON | 2021-11-03 14:40 | 2021-11-03 16:24 | 1139 | 001:44 | T | NO SE REPORTO CAUSA | SE CERRO INTERRUPTOR ABRIENDO MACHETES DE AMARRE CON 1709-03 | S2110300169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2021-11-03 | 118456 | keep | 0 | Nov | 2021 | 0.08068 | 0.00077577 | Sustained | FALSE | FALSE | Not_TMED_Event | 1139
MAYAGÃœEZ | 2021-11-03 14:50 | 2021-11-04 15:00 | 100 | 024:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21110300103 | New_Event | Bad Weather | Include | Include | Weather | 1450 | 2021-11-03 | 145000 | keep | 0 | Nov | 2021 | 0.098759 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-03 14:52 | 2021-11-03 16:36 | 10 | 001:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21110300038 | New_Event | Bad Weather | Include | Include | Weather | 104 | 2021-11-03 | 1040 | keep | 0 | Nov | 2021 | 0.00070834 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-11-03 14:54 | 2021-11-03 15:50 | 870 | 000:56 | T | DESGANCHE | SE RETIRO BAMBUAS SOBRE LINEA LLEVA 1303-04 | S21110300128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2021-11-03 | 48720 | keep | 0 | Nov | 2021 | 0.033183 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2021-11-03 14:57 | 2021-11-03 14:58 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1206-2 | S21110300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-03 | 641 | keep | 0 | Nov | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-11-03 14:57 | 2021-11-03 14:58 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1206-2 | S21110300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-03 | 733 | keep | 0 | Nov | 2021 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
MAYAGÃœEZ | 2021-11-03 14:57 | 2021-11-03 17:04 | 15 | 002:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21110300104 | New_Event | Bad Weather | Include | Include | Weather | 127 | 2021-11-03 | 1905 | keep | 0 | Nov | 2021 | 0.0012975 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-11-03 15:02 | 2021-11-03 15:03 | 225 | 000:01 | T | DESGANCHE | DISPARO LLEVANDO CARGA 1303-5,1303-1 Y 1346-6 MAL TIEMPO | S21110300128 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-03 | 225 | keep | 0 | Nov | 2021 | 0.00015325 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-11-03 15:03 | 2021-11-03 19:27 | 50 | 004:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21110300105 | New_Event | Bad Weather | Include | Include | Weather | 264 | 2021-11-03 | 13200 | keep | 0 | Nov | 2021 | 0.0089905 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-11-03 15:03 | 2021-11-03 16:53 | 300 | 001:50 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO INTERRUPTOR PARA PODER SECCIONALIZAR AVERIA DE POSTE PARTIDO POR IMPACTO DE VEHICULO SE REMPLAZO EL POSTE | B21110300000 | New_Event |  |  | Include | Wildlife | 110 | 2021-11-03 | 33000 | keep | 0 | Nov | 2021 | 0.022476 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2021-11-03 15:07 | 2021-11-04 11:38 | 20 | 020:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA | S21110300186 | New_Event | Cutout Failure | Include | Include | Equipment | 1231 | 2021-11-03 | 24620 | keep | 0 | Nov | 2021 | 0.016769 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-11-03 15:11 | 2021-11-03 15:12 | 4291 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO | S21110300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-03 | 4291 | keep | 0 | Nov | 2021 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
BAYAMON | 2021-11-03 15:16 | 2021-11-03 18:31 | 40 | 003:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REMPLAZARON 2 AISLADORES | B21110300067 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 195 | 2021-11-03 | 7800 | keep | 0 | Nov | 2021 | 0.0053125 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-11-03 15:19 | 2021-11-03 15:21 | 859 | 000:02 | P | NO SE REPORTO CAUSA | RECERRO CARGA EL 20% POR EL 1303-02 | S21110300207 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-03 | 1718 | keep | 0 | Nov | 2021 | 0.0011701 | 0.00058506 | Momentary | FALSE | FALSE | Not_TMED_Event | 859
SAN JUAN | 2021-11-03 15:19 | 2021-11-03 15:21 | 2435 | 000:02 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 20% 1204-2 | S21110300207 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-03 | 4870 | keep | 0 | Nov | 2021 | 0.0033169 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-11-03 15:21 | 2021-11-03 17:15 | 40 | 001:54 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21110300068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 114 | 2021-11-03 | 4560 | keep | 0 | Nov | 2021 | 0.0031058 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2021-11-03 15:36 | 2021-11-03 17:16 | 35 | 001:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P21110300052 | New_Event |  |  | Include | Wildlife | 100 | 2021-11-03 | 3500 | keep | 0 | Nov | 2021 | 0.0023838 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-11-03 15:36 | 2021-11-03 17:46 | 30 | 002:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21110300078 | New_Event | Bad Weather | Include | Include | Weather | 130 | 2021-11-03 | 3900 | keep | 0 | Nov | 2021 | 0.0026563 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2021-11-03 15:42 | 2021-11-03 16:00 | 60 | 000:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P21110300053 | New_Event |  |  | Include | Wildlife | 18 | 2021-11-03 | 1080 | keep | 0 | Nov | 2021 | 0.00073558 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2021-11-03 15:55 | 2021-11-03 19:33 | 11 | 003:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN XMR REPARO CONEXION EN NEUTRAL PRIMARIO HACIA XMR | R21110300132 | New_Event | Wire Down | Include | Include | Equipment | 218 | 2021-11-03 | 2398 | keep | 0 | Nov | 2021 | 0.0016333 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2021-11-03 16:10 | 2021-11-03 18:15 | 20 | 002:05 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21110300075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 125 | 2021-11-03 | 2500 | keep | 0 | Nov | 2021 | 0.0017027 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-11-03 16:10 | 2021-11-03 17:41 | 30 | 001:31 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA LA CARGA ESTABA TRANSFERIDA AL 8404-04 | B21110300076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 91 | 2021-11-03 | 2730 | keep | 0 | Nov | 2021 | 0.0018594 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2021-11-03 16:10 | 2021-11-03 17:41 | 30 | 001:31 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21110300076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 91 | 2021-11-03 | 2730 | keep | 0 | Nov | 2021 | 0.0018594 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2021-11-03 16:18 | 2021-11-03 17:50 | 8 | 001:32 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25 KVA X 25 KVA | C21110300097 | New_Event | Service Transformer Failure | Include | Include | Equipment | 92 | 2021-11-03 | 736 | keep | 0 | Nov | 2021 | 0.00050129 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-11-03 16:24 | 2021-11-03 17:35 | 600 | 001:11 | T | NO SE REPORTO CAUSA | SE CERRO MACHETES DE AMARRE CON 1909-07 NO SE ENCONTRO CAUSA CARGA POR EL 1909-07 | S2110300169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 71 | 2021-11-03 | 42600 | keep | 0 | Nov | 2021 | 0.029015 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2021-11-03 16:28 | 2021-11-03 16:57 | 1681 | 000:29 | T | DESGANCHE | DISPARO SE DIO UN GOI PARA SECCIONALIZAR TRAMO CAMINO LOS GUANOS PARA REALIZAR DESGANCHE DE BAMBUAS SOBRE LINEA 90% EN SERVICIO LLEVA 1346-06 | S21110300266 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 29 | 2021-11-03 | 48749 | keep | 0 | Nov | 2021 | 0.033203 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-03 16:28 | 2021-11-03 16:57 | 1598 | 000:29 | T | DESGANCHE | DISPARO SE DIO UN GOI PARA SECCIONALIZAR TRAMO CAMINO LOS GUANOS PARA REALIZAR DESGANCHE BAMBUAS SOBRE LINEA 90% EN SERVICIO LLEVA 1346-06 | S21110300266 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 29 | 2021-11-03 | 46342 | keep | 0 | Nov | 2021 | 0.031563 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-11-03 16:44 | 2021-11-03 16:45 | 1307 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR CRUCE POR CHANGO Y CAJA PRIMARIA AVERIADA | C21110300102 | New_Event |  |  | Include | Wildlife | 1 | 2021-11-03 | 1307 | keep | 0 | Nov | 2021 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
CAGUAS | 2021-11-03 16:45 | 2021-11-03 19:35 | 162 | 002:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR CHANGO Y SE REEMPLAZO CAJA PRIMARIA QUEMADA | C21110300104 | 1st_after_momentary |  |  | Include | Wildlife | 170 | 2021-11-03 | 27540 | keep | 0 | Nov | 2021 | 0.018757 | 0.00011034 | Sustained | FALSE | FALSE | Not_TMED_Event | 162
BAYAMON | 2021-11-03 16:51 | 2021-11-03 21:41 | 30 | 004:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN RISER SE REMPLAZO CAJA PRIMARIA EN RISER | B21110300062 | New_Event | Cutout Failure | Include | Include | Equipment | 290 | 2021-11-03 | 8700 | keep | 0 | Nov | 2021 | 0.0059255 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-11-03 16:53 | 2021-11-03 18:52 | 150 | 001:59 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21110300105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2021-11-03 | 17850 | keep | 0 | Nov | 2021 | 0.012158 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2021-11-03 16:57 | 2021-11-03 21:00 | 200 | 004:03 | P | DESGANCHE | SE DESGANCHO Y SE CERRO MACHETES 100% EN SERVICIO | S21110300266 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 243 | 2021-11-03 | 48600 | keep | 0 | Nov | 2021 | 0.033101 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-11-03 17:07 | 2021-11-03 19:43 | 6 | 002:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO BANCO DE TRANSFORMADORES PARA REPARAR CONEXIONES SECUNDARIAS | B21110200049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 156 | 2021-11-03 | 936 | keep | 0 | Nov | 2021 | 0.00063751 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-11-03 17:17 | 2021-11-04 09:40 | 11 | 016:23 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR | C21110300108 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 983 | 2021-11-03 | 10813 | keep | 0 | Nov | 2021 | 0.0073647 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2021-11-03 17:49 | 2021-11-03 17:50 | 225 | 000:01 | T | DESGANCHE | DISPARO SE RETIRO BAMBUAS SOBRE LINEA CAMINO LUCIANO VAZQUEZ LLEVA 1303-4 | S21110300128 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-03 | 225 | keep | 0 | Nov | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
CAGUAS | 2021-11-03 17:49 | 2021-11-04 14:16 | 20 | 020:27 | P | CABLE SOTERRADO AVERIADO | CERRO EN T - 3 HACIA T - 4 AVERIA DEL T- 2 HACIA EL T - 3 | C21110300006 | New_Event | UG Cable Fault | Include | Include | Equipment | 1227 | 2021-11-03 | 24540 | keep | 0 | Nov | 2021 | 0.016714 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-11-03 18:13 | 2021-11-03 20:46 | 39 | 002:33 | P | DESGANCHE | 1 X 20 EN RISER SE RETIRO ENREDADERA | C21110300115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2021-11-03 | 5967 | keep | 0 | Nov | 2021 | 0.0040641 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
MAYAGÃœEZ | 2021-11-03 18:14 | 2021-11-05 14:28 | 5 | 044:14 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25KVA POR TRANSFORMADOR DE 15KVA AVERIADO MARCA COOPER POWER NUMERO SERIE 2055098970 VOLTAJE 4160V 120/240V EVENTO DEL DIA 3 | M21110300132 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2654 | 2021-11-03 | 13270 | keep | 0 | Nov | 2021 | 0.0090381 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-11-03 18:34 | 2021-11-03 21:15 | 200 | 002:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | S21110300331 | New_Event | Wire Down | Include | Include | Equipment | 161 | 2021-11-03 | 32200 | keep | 0 | Nov | 2021 | 0.021931 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2021-11-03 18:37 | 2021-11-03 22:35 | 150 | 003:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 100 EN CORTE DE LINEA SE SECCIONALIZO LINEA PRIMARIA ROTA Y SE REMPLAZO UNA CAJA PRIMARIA QUEMADA EN EL FID 1001258208 MARCA CHINT 100AMP | A21110300047 | New_Event | Wire Down | Include | Include | Equipment | 238 | 2021-11-03 | 35700 | keep | 0 | Nov | 2021 | 0.024315 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2021-11-03 18:54 | 2021-11-03 22:21 | 100 | 003:27 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21110200335 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2021-11-03 | 20700 | keep | 0 | Nov | 2021 | 0.014099 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2021-11-03 19:14 | 2021-11-04 11:30 | 18 | 016:16 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | C21110300118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 976 | 2021-11-03 | 17568 | keep | 0 | Nov | 2021 | 0.011965 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2021-11-03 20:10 | 2021-11-03 22:10 | 60 | 002:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PORTA FUSIBLE | B21110300108 | New_Event | Cutout Failure | Include | Include | Equipment | 120 | 2021-11-03 | 7200 | keep | 0 | Nov | 2021 | 0.0049039 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2021-11-03 21:09 | 2021-11-04 11:17 | 1 | 014:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CONECTO BAJANTE SAFADO A RISER | P21110300070 | New_Event | Wire Down | Include | Include | Equipment | 848 | 2021-11-03 | 848 | keep | 0 | Nov | 2021 | 0.00057757 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-03 21:21 | 2021-11-03 22:48 | 1447 | 001:27 | T | NO SE REPORTO CAUSA | INTERRUPTOR DISPARO Y SE CERRO POR CONTROL LLEVA EL 1419-09 Y EL 1419-12 | S21110300353 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2021-11-03 | 125889 | keep | 0 | Nov | 2021 | 0.085742 | 0.00098555 | Sustained | FALSE | FALSE | Not_TMED_Event | 1447
SAN JUAN | 2021-11-03 21:21 | 2021-11-03 22:48 | 266 | 001:27 | T | NO SE REPORTO CAUSA | INTERRUPTOR DISPARO Y SE CERRO POR CONTROL CARGA POR EL 1112-04 | S21110300353 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2021-11-03 | 23142 | keep | 0 | Nov | 2021 | 0.015762 | 0.00018117 | Sustained | FALSE | FALSE | Not_TMED_Event | 266
SAN JUAN | 2021-11-03 21:21 | 2021-11-03 22:48 | 73 | 001:27 | T | NO SE REPORTO CAUSA | INTERRUPTOR DISPARO Y SE CERRO POR CONTROL CARGAA TRANSFERIDA AL 1112-04 | S21110300353 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2021-11-03 | 6351 | keep | 0 | Nov | 2021 | 0.0043256 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
CANOVANAS | 2021-11-03 21:21 | 2021-11-04 10:36 | 262 | 013:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 Y 1 X 30 EN CORTES DE LINEA Y 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | R21110400001 | New_Event | Cutout Failure | Include | Include | Equipment | 795 | 2021-11-03 | 208290 | keep | 0 | Nov | 2021 | 0.14187 | 0.00017845 | Sustained | FALSE | FALSE | Not_TMED_Event | 262
CAGUAS | 2021-11-03 21:27 | 2021-11-04 08:39 | 11 | 011:12 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | C21110300124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 672 | 2021-11-03 | 7392 | keep | 0 | Nov | 2021 | 0.0050347 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2021-11-03 22:29 | 2021-11-04 14:36 | 40 | 016:07 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21110300117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 967 | 2021-11-03 | 38680 | keep | 0 | Nov | 2021 | 0.026345 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-11-03 22:36 | 2021-11-04 11:58 | 67 | 013:22 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 140 EN CORTE DE LINEA SE REEMPLAZO AISLADOR Y SE FIJO CONDUCTOR PRIMARIO | R21110300145 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 802 | 2021-11-03 | 53734 | keep | 0 | Nov | 2021 | 0.036598 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
MAYAGÃœEZ | 2021-11-03 22:56 | 2021-11-04 10:30 | 35 | 011:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21110300163 | New_Event | Bad Weather | Include | Include | Weather | 694 | 2021-11-03 | 24290 | keep | 0 | Nov | 2021 | 0.016544 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2021-11-03 23:16 | 2021-11-04 17:25 | 200 | 018:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA | A21110300060 | New_Event | Wire Down | Include | Include | Equipment | 1089 | 2021-11-03 | 217800 | keep | 0 | Nov | 2021 | 0.14834 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-11-03 23:30 | 2021-11-04 11:34 | 3 | 012:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21110300164 | New_Event | Bad Weather | Include | Include | Weather | 724 | 2021-11-03 | 2172 | keep | 0 | Nov | 2021 | 0.0014793 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2021-11-03 23:55 | 2021-11-04 12:46 | 50 | 012:51 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE REPORTA CAUSA | P21110300072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 771 | 2021-11-03 | 38550 | keep | 0 | Nov | 2021 | 0.026256 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-11-04 00:07 | 2021-11-04 00:46 | 300 | 000:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO INTERRUPTOR PARA CERRAR PUENTES ABIERTO Y PODER NORMALIZAR CARGAS | B21110400000 | New_Event |  |  | Include | Wildlife | 39 | 2021-11-04 | 11700 | keep | 0 | Nov | 2021 | 0.0079688 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2021-11-04 00:19 | 2021-11-04 04:59 | 1802 | 004:40 | T | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO INTERRUPTOR POR CONTROL | S21110500003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2021-11-04 | 504560 | keep | 0 | Nov | 2021 | 0.34365 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
BAYAMON | 2021-11-04 00:46 | 2021-11-04 00:47 | 2402 | 000:01 | T | DESGANCHE | RECERRO | S21110400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-04 | 2402 | keep | 0 | Nov | 2021 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2021-11-04 00:47 | 2021-11-04 12:11 | 200 | 011:24 | P | DESGANCHE | 2 X 100 EN C/L SE REALIZO DESGANCHE SE REMPLAZO PARARRAYOS Y AISLADORES | S21110400001 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 684 | 2021-11-04 | 136800 | keep | 0 | Nov | 2021 | 0.093174 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-11-04 00:50 | 2021-11-04 14:49 | 20 | 013:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21110400001 | New_Event | Bad Weather | Include | Include | Weather | 839 | 2021-11-04 | 16780 | keep | 0 | Nov | 2021 | 0.011429 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-11-04 01:51 | 2021-11-04 01:54 | 36 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL CARGA TRANSFERIDA AL 1620-04 | S21110400002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-04 | 108 | keep | 0 | Nov | 2021 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-11-04 01:51 | 2021-11-04 01:54 | 172 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL, LLEVA LA CARGA 1620-01 | S21110400002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-04 | 516 | keep | 0 | Nov | 2021 | 0.00035145 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
BAYAMON | 2021-11-04 02:18 | 2021-11-04 15:51 | 15 | 013:33 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21110400004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 813 | 2021-11-04 | 12195 | keep | 0 | Nov | 2021 | 0.008306 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-11-04 02:24 | 2021-11-04 13:35 | 80 | 011:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21110400002 | New_Event | Bad Weather | Include | Include | Weather | 671 | 2021-11-04 | 53680 | keep | 0 | Nov | 2021 | 0.036561 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2021-11-04 02:36 | 2021-11-04 02:37 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21110400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-04 | 308 | keep | 0 | Nov | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
CAGUAS | 2021-11-04 03:07 | 2021-11-04 03:08 | 2302 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C21110400014 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-04 | 2302 | keep | 0 | Nov | 2021 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
CAGUAS | 2021-11-04 03:08 | 2021-11-04 17:56 | 1583 | 014:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTO CONDUCTOR | C21110400022 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 888 | 2021-11-04 | 1405704 | keep | 0 | Nov | 2021 | 0.95742 | 0.0010782 | Sustained | FALSE | FALSE | Not_TMED_Event | 1583
CAGUAS | 2021-11-04 03:27 | 2021-11-04 13:40 | 60 | 010:13 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C21110400006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 613 | 2021-11-04 | 36780 | keep | 0 | Nov | 2021 | 0.025051 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2021-11-04 03:31 | 2021-11-04 03:32 | 436 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO | C21110400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-04 | 436 | keep | 0 | Nov | 2021 | 0.00029696 | 0.00029696 | Momentary | FALSE | FALSE | Not_TMED_Event | 436
CAGUAS | 2021-11-04 04:07 | 2021-11-04 09:50 | 90 | 005:43 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA Y 1 X 40 EN RISER NO CAUSA | C21110400007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 343 | 2021-11-04 | 30870 | keep | 0 | Nov | 2021 | 0.021025 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2021-11-04 04:18 | 2021-11-04 09:57 | 18 | 005:39 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21110300144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 339 | 2021-11-04 | 6102 | keep | 0 | Nov | 2021 | 0.004156 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
MAYAGÃœEZ | 2021-11-04 05:00 | 2021-11-04 16:32 | 200 | 011:32 | P | PARARRAYOS DEFECTUOSO | 1 X 140 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21110400005 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 692 | 2021-11-04 | 138400 | keep | 0 | Nov | 2021 | 0.094264 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-11-04 05:43 | 2021-11-04 15:18 | 60 | 009:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO PORTA FUSIBLE | S21110400007 | New_Event | Cutout Failure | Include | Include | Equipment | 575 | 2021-11-04 | 34500 | keep | 0 | Nov | 2021 | 0.023498 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-11-04 06:06 | 2021-11-04 13:49 | 49 | 007:43 | P | DESGANCHE | 2 X 50 EN C/L SE REALIZO DESGANCHE | S21110400009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 463 | 2021-11-04 | 22687 | keep | 0 | Nov | 2021 | 0.015452 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
HUMACAO | 2021-11-04 06:06 | 2021-11-04 11:34 | 45 | 005:28 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21110400016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 328 | 2021-11-04 | 14760 | keep | 0 | Nov | 2021 | 0.010053 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2021-11-04 06:29 | 2021-11-04 09:32 | 110 | 003:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA REMPLAZO CAJA PRIMARIA QUEMADA | C21110400020 | New_Event | Cutout Failure | Include | Include | Equipment | 183 | 2021-11-04 | 20130 | keep | 0 | Nov | 2021 | 0.01371 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
MAYAGÃœEZ | 2021-11-04 06:30 | 2021-11-04 17:54 | 3 | 011:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | M21110400008 | New_Event | Bad Weather | Include | Include | Weather | 684 | 2021-11-04 | 2052 | keep | 0 | Nov | 2021 | 0.0013976 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2021-11-04 06:38 | 2021-11-04 09:56 | 75 | 003:18 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C21110400024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 198 | 2021-11-04 | 14850 | keep | 0 | Nov | 2021 | 0.010114 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2021-11-04 06:55 | 2021-11-04 06:57 | 1116 | 000:02 | T | PROTECCION DEFECTUOSA | RECIERRE | C21110400030 | New_Event | Protection Miscoordination | Include | Include | Other | 2 | 2021-11-04 | 2232 | keep | 0 | Nov | 2021 | 0.0015202 | 0.0007601 | Momentary | FALSE | FALSE | Not_TMED_Event | 1116
FAJARDO | 2021-11-04 06:56 | 2021-11-04 10:44 | 23 | 003:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR RATON | R21110400005 | New_Event |  |  | Include | Wildlife | 228 | 2021-11-04 | 5244 | keep | 0 | Nov | 2021 | 0.0035717 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
CAGUAS | 2021-11-04 06:57 | 2021-11-04 15:08 | 50 | 008:11 | P | PROTECCION DEFECTUOSA | 1 X 100 EN CORTE DE LINEA POR CARGA FUSIBLE DE MENOR CAPACIDAD | C21110400038 | 1st_after_momentary | Protection Miscoordination | Include | Include | Other | 491 | 2021-11-04 | 24550 | keep | 0 | Nov | 2021 | 0.016721 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-11-04 07:00 | 2021-11-04 13:37 | 11 | 006:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR CRUCE POR AVE | C21110400031 | New_Event |  |  | Include | Wildlife | 397 | 2021-11-04 | 4367 | keep | 0 | Nov | 2021 | 0.0029743 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
PONCE | 2021-11-04 07:02 | 2021-11-04 15:10 | 50 | 008:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | P21110400003 | New_Event |  |  | Include | Wildlife | 488 | 2021-11-04 | 24400 | keep | 0 | Nov | 2021 | 0.016619 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-04 07:05 | 2021-11-04 15:19 | 1 | 008:14 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S21110400011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 494 | 2021-11-04 | 494 | keep | 0 | Nov | 2021 | 0.00033646 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2021-11-04 07:11 | 2021-11-04 10:58 | 50 | 003:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA POR AVE CRUZAR FASES | P21110400004 | New_Event |  |  | Include | Wildlife | 227 | 2021-11-04 | 11350 | keep | 0 | Nov | 2021 | 0.0077304 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-04 07:17 | 2021-11-04 12:00 | 30 | 004:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21110400018 | New_Event | Bad Weather | Include | Include | Weather | 283 | 2021-11-04 | 8490 | keep | 0 | Nov | 2021 | 0.0057825 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-11-04 07:41 | 2021-11-04 12:11 | 60 | 004:30 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B21110400010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 270 | 2021-11-04 | 16200 | keep | 0 | Nov | 2021 | 0.011034 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-11-04 07:44 | 2021-11-04 16:39 | 100 | 008:55 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21104000020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 535 | 2021-11-04 | 53500 | keep | 0 | Nov | 2021 | 0.036439 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-11-04 07:56 | 2021-11-04 13:31 | 12 | 005:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 25 EN TRANSFORMADOR SE REPARO SECUNDARIA | B21110400012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 335 | 2021-11-04 | 4020 | keep | 0 | Nov | 2021 | 0.002738 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2021-11-04 08:12 | 2021-11-04 11:32 | 50 | 003:20 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B21110400015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 200 | 2021-11-04 | 10000 | keep | 0 | Nov | 2021 | 0.006811 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-04 08:52 | 2021-11-04 20:52 | 10 | 012:00 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5 KVA | S21110400059 | New_Event | Service Transformer Failure | Include | Include | Equipment | 720 | 2021-11-04 | 7200 | keep | 0 | Nov | 2021 | 0.0049039 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-04 08:52 | 2021-11-04 20:52 | 15 | 012:00 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5KVA POR IGUAL CAPACIDAD | S21110400046 | New_Event | Service Transformer Failure | Include | Include | Equipment | 720 | 2021-11-04 | 10800 | keep | 0 | Nov | 2021 | 0.0073558 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-11-04 08:57 | 2021-11-04 08:58 | 1467 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21110400060 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-11-04 | 1467 | keep | 0 | Nov | 2021 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
HUMACAO | 2021-11-04 08:58 | 2021-11-04 13:56 | 1 | 004:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN RISER REEMPLAZARON CAJA PRIMARIA QUEMADA | C21110400083 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 298 | 2021-11-04 | 298 | keep | 0 | Nov | 2021 | 0.00020297 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-11-04 09:00 | 2021-11-04 16:21 | 50 | 007:21 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21110400027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 441 | 2021-11-04 | 22050 | keep | 0 | Nov | 2021 | 0.015018 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2021-11-04 09:15 | 2021-11-04 17:24 | 100 | 008:09 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA ENDEREZAR POSTE Y REALIZAR DESGANCHE | A21110400003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 489 | 2021-11-04 | 48900 | keep | 0 | Nov | 2021 | 0.033306 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2021-11-04 09:16 | 2021-11-04 17:00 | 50 | 007:44 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21110400008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 464 | 2021-11-04 | 23200 | keep | 0 | Nov | 2021 | 0.015801 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-04 09:18 | 2021-11-04 10:44 | 1 | 001:26 | P | DESGANCHE | 2 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | M21110400035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2021-11-04 | 86 | keep | 0 | Nov | 2021 | 5.8574e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-04 09:32 | 2021-11-04 09:33 | 641 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37900 | S21110400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-04 | 641 | keep | 0 | Nov | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-11-04 09:32 | 2021-11-04 09:33 | 733 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37900 | S21110400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-04 | 733 | keep | 0 | Nov | 2021 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2021-11-04 09:32 | 2021-11-04 09:33 | 4133 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37900 | S21110400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-04 | 4133 | keep | 0 | Nov | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-11-04 09:32 | 2021-11-04 09:33 | 1799 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37900 | S21110400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-04 | 1799 | keep | 0 | Nov | 2021 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
CAGUAS | 2021-11-04 09:32 | 2021-11-04 12:04 | 70 | 002:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA | C21110400020 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 152 | 2021-11-04 | 10640 | keep | 0 | Nov | 2021 | 0.0072469 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-04 09:34 | 2021-11-04 09:35 | 4291 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE L-37900 | S21110400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-04 | 4291 | keep | 0 | Nov | 2021 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
SAN JUAN | 2021-11-04 09:34 | 2021-11-04 09:35 | 1381 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE L-37900 | S21110400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-04 | 1381 | keep | 0 | Nov | 2021 | 0.00094059 | 0.00094059 | Momentary | FALSE | FALSE | Not_TMED_Event | 1381
BAYAMON | 2021-11-04 09:34 | 2021-11-04 19:14 | 10 | 009:40 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA Y 1 X 65 EN RISER SE REALIZO DESGANCHE | B21110400094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 580 | 2021-11-04 | 5800 | keep | 0 | Nov | 2021 | 0.0039504 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-11-04 09:37 | 2021-11-04 11:32 | 45 | 001:55 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21110400066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2021-11-04 | 5175 | keep | 0 | Nov | 2021 | 0.0035247 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2021-11-04 09:43 | 2021-11-04 17:10 | 2 | 007:27 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21110300032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 447 | 2021-11-04 | 894 | keep | 0 | Nov | 2021 | 0.0006089 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2021-11-04 09:50 | 2021-11-04 11:30 | 15 | 001:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | M21110300042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 100 | 2021-11-04 | 1500 | keep | 0 | Nov | 2021 | 0.0010216 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-11-04 09:54 | 2021-11-04 12:30 | 36 | 002:36 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21110400027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 156 | 2021-11-04 | 5616 | keep | 0 | Nov | 2021 | 0.003825 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CAGUAS | 2021-11-04 10:08 | 2021-11-04 16:34 | 1 | 006:26 | P | OTRAS CAUSAS | 1 X 10 EN XMR PROA | C21110400071 | New_Event | Other Causes | Include | Include | Other | 386 | 2021-11-04 | 386 | keep | 0 | Nov | 2021 | 0.0002629 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-11-04 10:30 | 2021-11-04 14:00 | 1 | 003:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21110400015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 210 | 2021-11-04 | 210 | keep | 0 | Nov | 2021 | 0.00014303 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-04 10:46 | 2021-11-04 14:36 | 15 | 003:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21110400046 | New_Event | Secondary Wire Down | Include | Include | Equipment | 230 | 2021-11-04 | 3450 | keep | 0 | Nov | 2021 | 0.0023498 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-11-04 11:01 | 2021-11-04 11:02 | 776 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | B21110400000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2021-11-04 | 776 | keep | 0 | Nov | 2021 | 0.00052853 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
VEGA BAJA | 2021-11-04 11:02 | 2021-11-04 17:31 | 300 | 006:29 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO | B21110400044 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 389 | 2021-11-04 | 116700 | keep | 0 | Nov | 2021 | 0.079484 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
HUMACAO | 2021-11-04 11:04 | 2021-11-04 13:19 | 1 | 002:15 | P | NO SE REPORTO CAUSA | 1 X 20 EN BANCO DE TRANSFORMADOR | C21110400077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 135 | 2021-11-04 | 135 | keep | 0 | Nov | 2021 | 9.1948e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-04 11:06 | 2021-11-04 17:31 | 15 | 006:25 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21110400042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 385 | 2021-11-04 | 5775 | keep | 0 | Nov | 2021 | 0.0039333 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-11-04 11:08 | 2021-11-04 12:25 | 200 | 001:17 | P | SOBRECARGA | 3 X 200 EN CORTE DE LINEA POR SOBRECARGA | P21110400016 | New_Event | Trip Due To Overload | Include | Include | Other | 77 | 2021-11-04 | 15400 | keep | 0 | Nov | 2021 | 0.010489 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-11-04 11:12 | 2021-11-04 22:59 | 25 | 011:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21110400052 | New_Event | Bad Weather | Include | Include | Weather | 707 | 2021-11-04 | 17675 | keep | 0 | Nov | 2021 | 0.012038 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2021-11-04 11:20 | 2021-11-04 15:20 | 6 | 004:00 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA X 50 KVA | R21110400016 | New_Event | Service Transformer Failure | Include | Include | Equipment | 240 | 2021-11-04 | 1440 | keep | 0 | Nov | 2021 | 0.00098078 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2021-11-04 11:28 | 2021-11-04 13:50 | 5 | 002:22 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO ENCONTRO CAUSA | R21110400017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 142 | 2021-11-04 | 710 | keep | 0 | Nov | 2021 | 0.00048358 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-11-04 11:33 | 2021-11-04 13:34 | 1222 | 002:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21110400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 121 | 2021-11-04 | 147862 | keep | 0 | Nov | 2021 | 0.10071 | 0.0008323 | Sustained | FALSE | FALSE | Not_TMED_Event | 1222
ARECIBO | 2021-11-04 11:33 | 2021-11-04 13:34 | 2756 | 002:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21110400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 121 | 2021-11-04 | 333476 | keep | 0 | Nov | 2021 | 0.22713 | 0.0018771 | Sustained | FALSE | FALSE | Not_TMED_Event | 2756
ARECIBO | 2021-11-04 11:33 | 2021-11-04 13:34 | 2833 | 002:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21110400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 121 | 2021-11-04 | 342793 | keep | 0 | Nov | 2021 | 0.23347 | 0.0019295 | Sustained | FALSE | FALSE | Not_TMED_Event | 2833
ARECIBO | 2021-11-04 11:33 | 2021-11-04 13:34 | 1218 | 002:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21110400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 121 | 2021-11-04 | 147378 | keep | 0 | Nov | 2021 | 0.10038 | 0.00082957 | Sustained | FALSE | FALSE | Not_TMED_Event | 1218
ARECIBO | 2021-11-04 11:33 | 2021-11-04 13:34 | 1345 | 002:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21110400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 121 | 2021-11-04 | 162745 | keep | 0 | Nov | 2021 | 0.11084 | 0.00091607 | Sustained | FALSE | FALSE | Not_TMED_Event | 1345
ARECIBO | 2021-11-04 11:33 | 2021-11-04 13:34 | 1265 | 002:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21110400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 121 | 2021-11-04 | 153065 | keep | 0 | Nov | 2021 | 0.10425 | 0.00086159 | Sustained | FALSE | FALSE | Not_TMED_Event | 1265
ARECIBO | 2021-11-04 11:33 | 2021-11-04 13:34 | 2071 | 002:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21110400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 121 | 2021-11-04 | 250591 | keep | 0 | Nov | 2021 | 0.17068 | 0.0014105 | Sustained | FALSE | FALSE | Not_TMED_Event | 2071
ARECIBO | 2021-11-04 11:33 | 2021-11-04 13:34 | 760 | 002:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21110400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 121 | 2021-11-04 | 91960 | keep | 0 | Nov | 2021 | 0.062634 | 0.00051763 | Sustained | FALSE | FALSE | Not_TMED_Event | 760
ARECIBO | 2021-11-04 11:33 | 2021-11-04 13:34 | 509 | 002:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21110400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 121 | 2021-11-04 | 61589 | keep | 0 | Nov | 2021 | 0.041948 | 0.00034668 | Sustained | FALSE | FALSE | Not_TMED_Event | 509
ARECIBO | 2021-11-04 11:33 | 2021-11-04 13:34 | 2620 | 002:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21110400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 121 | 2021-11-04 | 317020 | keep | 0 | Nov | 2021 | 0.21592 | 0.0017845 | Sustained | FALSE | FALSE | Not_TMED_Event | 2620
ARECIBO | 2021-11-04 11:33 | 2021-11-04 13:34 | 1916 | 002:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21110400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 121 | 2021-11-04 | 231836 | keep | 0 | Nov | 2021 | 0.1579 | 0.001305 | Sustained | FALSE | FALSE | Not_TMED_Event | 1916
GUAYAMA | 2021-11-04 11:48 | 2021-11-04 11:49 | 1565 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21110400024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-04 | 1565 | keep | 0 | Nov | 2021 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
MAYAGÃœEZ | 2021-11-04 12:18 | 2021-11-04 13:43 | 3147 | 001:25 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO LINEA PRIMARIA PARTIDA SE CERRO INTERRUPTOR | M21110400062 | New_Event | Wire Down | Include | Include | Equipment | 85 | 2021-11-04 | 267495 | keep | 0 | Nov | 2021 | 0.18219 | 0.0021434 | Sustained | FALSE | FALSE | Not_TMED_Event | 3147
CAGUAS | 2021-11-04 12:36 | 2021-11-04 19:55 | 1568 | 007:19 | P | ESTRUCTURA AVERIADA | 3 X 80 EN C/L REMPLAZO POSTE PARTIDO | C21110400086 | New_Event | Defective Pole | Include | Include | Equipment | 439 | 2021-11-04 | 688352 | keep | 0 | Nov | 2021 | 0.46883 | 0.001068 | Sustained | FALSE | FALSE | Not_TMED_Event | 1568
YAUCO | 2021-11-04 13:11 | 2021-11-04 13:13 | 1924 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 POR SOBRECARGA | P21110400045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-04 | 3848 | keep | 0 | Nov | 2021 | 0.0026209 | 0.0013104 | Momentary | FALSE | FALSE | Not_TMED_Event | 1924
YAUCO | 2021-11-04 13:11 | 2021-11-04 13:13 | 968 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 POR SOBRECARGA | P21110400045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-04 | 1936 | keep | 0 | Nov | 2021 | 0.0013186 | 0.0006593 | Momentary | FALSE | FALSE | Not_TMED_Event | 968
YAUCO | 2021-11-04 13:11 | 2021-11-04 13:13 | 680 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21110400045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-04 | 1360 | keep | 0 | Nov | 2021 | 0.00092629 | 0.00046314 | Momentary | FALSE | FALSE | Not_TMED_Event | 680
YAUCO | 2021-11-04 13:11 | 2021-11-04 13:13 | 2246 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21110400045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-04 | 4492 | keep | 0 | Nov | 2021 | 0.0030595 | 0.0015297 | Momentary | FALSE | FALSE | Not_TMED_Event | 2246
YAUCO | 2021-11-04 13:11 | 2021-11-04 13:13 | 2011 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21110400045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-04 | 4022 | keep | 0 | Nov | 2021 | 0.0027394 | 0.0013697 | Momentary | FALSE | FALSE | Not_TMED_Event | 2011
YAUCO | 2021-11-04 13:11 | 2021-11-04 13:13 | 339 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21110400045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-04 | 678 | keep | 0 | Nov | 2021 | 0.00046178 | 0.00023089 | Momentary | FALSE | FALSE | Not_TMED_Event | 339
YAUCO | 2021-11-04 13:11 | 2021-11-04 13:13 | 2470 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21110400045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-04 | 4940 | keep | 0 | Nov | 2021 | 0.0033646 | 0.0016823 | Momentary | FALSE | FALSE | Not_TMED_Event | 2470
YAUCO | 2021-11-04 13:11 | 2021-11-04 13:13 | 1182 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21110400045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-04 | 2364 | keep | 0 | Nov | 2021 | 0.0016101 | 0.00080505 | Momentary | FALSE | FALSE | Not_TMED_Event | 1182
YAUCO | 2021-11-04 13:11 | 2021-11-04 13:13 | 2340 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21110400045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-04 | 4680 | keep | 0 | Nov | 2021 | 0.0031875 | 0.0015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 2340
YAUCO | 2021-11-04 13:11 | 2021-11-04 13:13 | 1637 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21110400045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-04 | 3274 | keep | 0 | Nov | 2021 | 0.0022299 | 0.001115 | Momentary | FALSE | FALSE | Not_TMED_Event | 1637
YAUCO | 2021-11-04 13:11 | 2021-11-04 13:13 | 1475 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21110400045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-04 | 2950 | keep | 0 | Nov | 2021 | 0.0020092 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
YAUCO | 2021-11-04 13:11 | 2021-11-04 13:13 | 661 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21110400045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-04 | 1322 | keep | 0 | Nov | 2021 | 0.00090041 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
YAUCO | 2021-11-04 13:11 | 2021-11-04 13:13 | 1569 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21110400045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-04 | 3138 | keep | 0 | Nov | 2021 | 0.0021373 | 0.0010686 | Momentary | FALSE | FALSE | Not_TMED_Event | 1569
YAUCO | 2021-11-04 13:11 | 2021-11-04 13:13 | 2309 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21110400045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-04 | 4618 | keep | 0 | Nov | 2021 | 0.0031453 | 0.0015726 | Momentary | FALSE | FALSE | Not_TMED_Event | 2309
YAUCO | 2021-11-04 13:11 | 2021-11-04 13:13 | 2179 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21110400045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-04 | 4358 | keep | 0 | Nov | 2021 | 0.0029682 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
YAUCO | 2021-11-04 13:11 | 2021-11-04 13:13 | 2440 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21110400045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-04 | 4880 | keep | 0 | Nov | 2021 | 0.0033237 | 0.0016619 | Momentary | FALSE | FALSE | Not_TMED_Event | 2440
YAUCO | 2021-11-04 13:11 | 2021-11-04 13:13 | 1352 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21110400045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-04 | 2704 | keep | 0 | Nov | 2021 | 0.0018417 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
YAUCO | 2021-11-04 13:11 | 2021-11-04 13:13 | 3973 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21110400045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-04 | 7946 | keep | 0 | Nov | 2021 | 0.005412 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2021-11-04 13:11 | 2021-11-04 13:13 | 2484 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21110400045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-04 | 4968 | keep | 0 | Nov | 2021 | 0.0033837 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
MAYAGÃœEZ | 2021-11-04 13:11 | 2021-11-04 15:05 | 281 | 001:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21110400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2021-11-04 | 32034 | keep | 0 | Nov | 2021 | 0.021818 | 0.00019139 | Sustained | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2021-11-04 13:11 | 2021-11-04 15:05 | 1252 | 001:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21110400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2021-11-04 | 142728 | keep | 0 | Nov | 2021 | 0.097211 | 0.00085273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2021-11-04 13:11 | 2021-11-04 15:05 | 595 | 001:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21110400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2021-11-04 | 67830 | keep | 0 | Nov | 2021 | 0.046199 | 0.00040525 | Sustained | FALSE | FALSE | Not_TMED_Event | 595
MAYAGÃœEZ | 2021-11-04 13:11 | 2021-11-04 15:05 | 51 | 001:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21110400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2021-11-04 | 5814 | keep | 0 | Nov | 2021 | 0.0039599 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2021-11-04 13:11 | 2021-11-04 15:05 | 721 | 001:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21110400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2021-11-04 | 82194 | keep | 0 | Nov | 2021 | 0.055982 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2021-11-04 13:11 | 2021-11-04 15:05 | 1382 | 001:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | A21110400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2021-11-04 | 157548 | keep | 0 | Nov | 2021 | 0.10731 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2021-11-04 13:11 | 2021-11-04 15:05 | 654 | 001:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A21110400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2021-11-04 | 74556 | keep | 0 | Nov | 2021 | 0.05078 | 0.00044544 | Sustained | FALSE | FALSE | Not_TMED_Event | 654
BAYAMON | 2021-11-04 13:18 | 2021-11-04 18:53 | 15 | 005:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21110400073 | New_Event | Secondary Wire Down | Include | Include | Equipment | 335 | 2021-11-04 | 5025 | keep | 0 | Nov | 2021 | 0.0034225 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-11-04 13:20 | 2021-11-04 18:09 | 10 | 004:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21110400165 | New_Event | Secondary Wire Down | Include | Include | Equipment | 289 | 2021-11-04 | 2890 | keep | 0 | Nov | 2021 | 0.0019684 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-04 13:34 | 2021-11-04 17:00 | 50 | 003:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | A21110400194 | New_Event | Wire Down | Include | Include | Equipment | 206 | 2021-11-04 | 10300 | keep | 0 | Nov | 2021 | 0.0070153 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-11-04 13:43 | 2021-11-04 14:52 | 5 | 001:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 80 EN RISER SE REEMPLAZO CAJA PRIMARIA | R21110400021 | New_Event | Cutout Failure | Include | Include | Equipment | 69 | 2021-11-04 | 345 | keep | 0 | Nov | 2021 | 0.00023498 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-11-04 13:43 | 2021-11-04 16:58 | 70 | 003:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA Y SE CERRO PUENTE | M21110400064 | Partial_restoration | Wire Down | Include | Include | Equipment | 195 | 2021-11-04 | 13650 | keep | 0 | Nov | 2021 | 0.009297 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-11-04 13:47 | 2021-11-05 12:00 | 1 | 022:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA DE TRANSFORMADOR AVERIADA EN EL FID 12571778 MARCA HUBBELL 100AMP Y SE REMPLAZO CRUCETA PARTIDA | M21110400091 | New_Event | Cutout Failure | Include | Include | Equipment | 1333 | 2021-11-04 | 1333 | keep | 0 | Nov | 2021 | 0.0009079 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-11-04 13:51 | 2021-11-04 17:13 | 1 | 003:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REMPLAZO TOMA QUEMADA | C21110400102 | New_Event | Secondary Wire Down | Include | Include | Equipment | 202 | 2021-11-04 | 202 | keep | 0 | Nov | 2021 | 0.00013758 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-11-04 13:52 | 2021-11-04 18:30 | 1345 | 004:38 | S | AISLADOR ROTO, PARTIDO O SAFADO | SE RETIRO CARGA A PETICION DEL TOC PARA REMPLAZAR AISLADORES 38 KV AVERIADOS EN EL TRANSFORMADOR | A21110400190 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 278 | 2021-11-04 | 373910 | keep | 0 | Nov | 2021 | 0.25467 | 0.00091607 | Sustained | FALSE | FALSE | Not_TMED_Event | 1345
ARECIBO | 2021-11-04 13:52 | 2021-11-04 18:30 | 1265 | 004:38 | S | AISLADOR ROTO, PARTIDO O SAFADO | SE RETIRO CARGA A PETICION DEL TOC PARA REMPLAZAR AISLADORES 38 KV AVERIADOS EN EL TRANSFORMADOR | A21110400190 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 278 | 2021-11-04 | 351670 | keep | 0 | Nov | 2021 | 0.23952 | 0.00086159 | Sustained | FALSE | FALSE | Not_TMED_Event | 1265
ARECIBO | 2021-11-04 13:52 | 2021-11-04 18:30 | 2071 | 004:38 | S | AISLADOR ROTO, PARTIDO O SAFADO | SE RETIRO CARGA A PETICION DEL TOC PARA REMPLAZAR AISLADORES 38 KV AVERIADOS EN EL TRANSFORMADOR | A21110400190 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 278 | 2021-11-04 | 575738 | keep | 0 | Nov | 2021 | 0.39213 | 0.0014105 | Sustained | FALSE | FALSE | Not_TMED_Event | 2071
ARECIBO | 2021-11-04 13:52 | 2021-11-04 18:30 | 760 | 004:38 | S | AISLADOR ROTO, PARTIDO O SAFADO | SE RETIRO CARGA A PETICION DEL TOC PARA REMPLAZAR AISLADORES 38 KV AVERIADOS EN EL TRANSFORMADOR | A21110400190 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 278 | 2021-11-04 | 211280 | keep | 0 | Nov | 2021 | 0.1439 | 0.00051763 | Sustained | FALSE | FALSE | Not_TMED_Event | 760
AGUADILLA | 2021-11-04 14:03 | 2021-11-04 16:48 | 12 | 002:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | M21110400098 | New_Event | Bad Weather | Include | Include | Weather | 165 | 2021-11-04 | 1980 | keep | 0 | Nov | 2021 | 0.0013486 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-11-04 14:05 | 2021-11-04 14:06 | 641 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | S21110400000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-04 | 641 | keep | 0 | Nov | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-11-04 14:05 | 2021-11-04 14:06 | 733 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO CARGA TRANSFERIDA AL 1206-01 | S21110400000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-04 | 733 | keep | 0 | Nov | 2021 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2021-11-04 14:06 | 2021-11-04 16:28 | 341 | 002:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA | S21110400064 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 142 | 2021-11-04 | 48422 | keep | 0 | Nov | 2021 | 0.03298 | 0.00023225 | Sustained | FALSE | FALSE | Not_TMED_Event | 341
FAJARDO | 2021-11-04 14:28 | 2021-11-04 15:21 | 14 | 000:53 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | R21110400022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 53 | 2021-11-04 | 742 | keep | 0 | Nov | 2021 | 0.00050537 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2021-11-04 14:44 | 2021-11-04 17:56 | 50 | 003:12 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21110400110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2021-11-04 | 9600 | keep | 0 | Nov | 2021 | 0.0065385 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-11-04 14:55 | 2021-11-05 09:20 | 40 | 018:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21110400113 | New_Event | Bad Weather | Include | Include | Weather | 1105 | 2021-11-04 | 44200 | keep | 0 | Nov | 2021 | 0.030104 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-11-04 14:58 | 2021-11-04 19:54 | 50 | 004:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21110400154 | New_Event | Bad Weather | Include | Include | Weather | 296 | 2021-11-04 | 14800 | keep | 0 | Nov | 2021 | 0.01008 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-04 14:58 | 2021-11-04 20:06 | 40 | 005:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21104000114 | New_Event | Bad Weather | Include | Include | Weather | 308 | 2021-11-04 | 12320 | keep | 0 | Nov | 2021 | 0.0083911 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-11-04 15:00 | 2021-11-04 18:28 | 90 | 003:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR CHANGO | R21110400025 | New_Event |  |  | Include | Wildlife | 208 | 2021-11-04 | 18720 | keep | 0 | Nov | 2021 | 0.01275 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2021-11-04 15:11 | 2021-11-04 17:09 | 30 | 001:58 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21110400089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2021-11-04 | 3540 | keep | 0 | Nov | 2021 | 0.0024111 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2021-11-04 15:26 | 2021-11-05 09:30 | 100 | 018:04 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21110400121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1084 | 2021-11-04 | 108400 | keep | 0 | Nov | 2021 | 0.073831 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-11-04 15:35 | 2021-11-04 18:37 | 40 | 003:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CRUCE POR REPTIL | C21110400115 | New_Event |  |  | Include | Wildlife | 182 | 2021-11-04 | 7280 | keep | 0 | Nov | 2021 | 0.0049584 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-11-04 16:00 | 2021-11-05 10:42 | 30 | 018:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA VEHICULO IMPACTO POSTE | A21110400211 | New_Event |  |  | Include | Wildlife | 1122 | 2021-11-04 | 33660 | keep | 0 | Nov | 2021 | 0.022926 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-11-04 16:07 | 2021-11-04 16:42 | 17 | 000:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO C/L PARA REPARAR NEUTRAL PRIMARIO Y RETEZAR LINEAS | C21110400123 | New_Event | Wire Down | Include | Include | Equipment | 35 | 2021-11-04 | 595 | keep | 0 | Nov | 2021 | 0.00040525 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
SAN JUAN | 2021-11-04 16:11 | 2021-11-04 16:12 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21110400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-04 | 870 | keep | 0 | Nov | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
VEGA BAJA | 2021-11-04 16:24 | 2021-11-04 19:22 | 50 | 002:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE DESCRUZO LINEAS | B21110400094 | New_Event | Wire Down | Include | Include | Equipment | 178 | 2021-11-04 | 8900 | keep | 0 | Nov | 2021 | 0.0060617 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-11-04 16:25 | 2021-11-04 16:55 | 5 | 000:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE POR AVE | C21110400130 | New_Event |  |  | Include | Wildlife | 30 | 2021-11-04 | 150 | keep | 0 | Nov | 2021 | 0.00010216 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2021-11-04 16:28 | 2021-11-04 20:21 | 45 | 003:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | R21110400030 | New_Event | Bad Weather | Include | Include | Weather | 233 | 2021-11-04 | 10485 | keep | 0 | Nov | 2021 | 0.0071413 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
YAUCO | 2021-11-04 17:11 | 2021-11-04 19:34 | 10 | 002:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | P21110400083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 143 | 2021-11-04 | 1430 | keep | 0 | Nov | 2021 | 0.00097397 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-11-04 17:16 | 2021-11-04 21:09 | 15 | 003:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21110400105 | New_Event | Secondary Wire Down | Include | Include | Equipment | 233 | 2021-11-04 | 3495 | keep | 0 | Nov | 2021 | 0.0023804 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-11-04 17:20 | 2021-11-04 17:40 | 4161 | 000:20 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO SE VERIFICO PERSONAL FUERA | C21110400000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 20 | 2021-11-04 | 83220 | keep | 0 | Nov | 2021 | 0.056681 | 0.002834 | Sustained | FALSE | FALSE | Not_TMED_Event | 4161
BAYAMON | 2021-11-04 17:28 | 2021-11-04 17:30 | 3597 | 000:02 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 50% DEL 9405-05 | B21110400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-04 | 7194 | keep | 0 | Nov | 2021 | 0.0048998 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2021-11-04 17:28 | 2021-11-04 17:30 | 1300 | 000:02 | P | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 50% TRANSFERIDO AL 1719-15 | B21110400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-04 | 2600 | keep | 0 | Nov | 2021 | 0.0017708 | 0.00088542 | Momentary | FALSE | FALSE | Not_TMED_Event | 1300
HUMACAO | 2021-11-04 17:40 | 2021-11-04 20:54 | 40 | 003:14 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN C/L REMPLAZO AISLADOR | C21110400157 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 194 | 2021-11-04 | 7760 | keep | 0 | Nov | 2021 | 0.0052853 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-11-04 17:48 | 2021-11-05 11:32 | 171 | 017:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE DESGANCHO Y REEMPLAZARON CAJA PRIMARIA | C21110400151 | New_Event | Cutout Failure | Include | Include | Equipment | 1064 | 2021-11-04 | 181944 | keep | 0 | Nov | 2021 | 0.12392 | 0.00011647 | Sustained | FALSE | FALSE | Not_TMED_Event | 171
HUMACAO | 2021-11-04 18:22 | 2021-11-05 10:16 | 12 | 015:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE CERRO PUENTE DE CAJA A LINEA | C21110400158 | New_Event | Wire Down | Include | Include | Equipment | 954 | 2021-11-04 | 11448 | keep | 0 | Nov | 2021 | 0.0077972 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-11-04 18:35 | 2021-11-04 20:12 | 30 | 001:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN RISER Y 1 X 80 EN SU POR DESCARGAS ELECTRICAS | M21110400160 | New_Event | Bad Weather | Include | Include | Weather | 97 | 2021-11-04 | 2910 | keep | 0 | Nov | 2021 | 0.001982 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-11-04 18:46 | 2021-11-05 10:05 | 40 | 015:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21110400164 | New_Event | Bad Weather | Include | Include | Weather | 919 | 2021-11-04 | 36760 | keep | 0 | Nov | 2021 | 0.025037 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-11-04 18:49 | 2021-11-04 22:03 | 75 | 003:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21110400123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2021-11-04 | 14550 | keep | 0 | Nov | 2021 | 0.0099099 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2021-11-04 19:04 | 2021-11-05 12:25 | 15 | 017:21 | P | NO SE REPORTO CAUSA | 1 X 25 EN XMR | S21110400103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1041 | 2021-11-04 | 15615 | keep | 0 | Nov | 2021 | 0.010635 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-11-04 19:15 | 2021-11-04 20:45 | 10 | 001:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZO BARRA PEDESTAL | B21110400115 | New_Event | Secondary Wire Down | Include | Include | Equipment | 90 | 2021-11-04 | 900 | keep | 0 | Nov | 2021 | 0.00061299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-11-04 19:32 | 2021-11-04 23:24 | 1 | 003:52 | P | PARARRAYOS DEFECTUOSO | 3 X 100 EN C/L REMPLAZO 3 PARARRAYOS | R21110400038 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 232 | 2021-11-04 | 232 | keep | 0 | Nov | 2021 | 0.00015801 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-11-04 20:06 | 2021-11-05 11:24 | 240 | 015:18 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA DESGANCHE | C21110400176 | New_Event | Vegetation Contact | Include | Include | Vegetation | 918 | 2021-11-04 | 220320 | keep | 0 | Nov | 2021 | 0.15006 | 0.00016346 | Sustained | FALSE | FALSE | Not_TMED_Event | 240
ARECIBO | 2021-11-04 20:06 | 2021-11-04 23:10 | 100 | 003:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21110400231 | New_Event | Bad Weather | Include | Include | Weather | 184 | 2021-11-04 | 18400 | keep | 0 | Nov | 2021 | 0.012532 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2021-11-04 20:45 | 2021-11-04 22:27 | 75 | 001:42 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 40 EN CORTE DE LINEA | B21110400137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 102 | 2021-11-04 | 7650 | keep | 0 | Nov | 2021 | 0.0052104 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2021-11-04 20:49 | 2021-11-05 10:33 | 44 | 013:44 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | C21110400181 | New_Event | Vegetation Contact | Include | Include | Vegetation | 824 | 2021-11-04 | 36256 | keep | 0 | Nov | 2021 | 0.024694 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
CAGUAS | 2021-11-04 21:26 | 2021-11-05 09:29 | 66 | 012:03 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21110400183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 723 | 2021-11-04 | 47718 | keep | 0 | Nov | 2021 | 0.032501 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
CAGUAS | 2021-11-04 21:29 | 2021-11-05 12:22 | 2 | 014:53 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN TRANSFORMADOR SE RETIRO ENREDADERA | C21110400184 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 893 | 2021-11-04 | 1786 | keep | 0 | Nov | 2021 | 0.0012164 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2021-11-04 21:31 | 2021-11-04 23:23 | 100 | 001:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 30 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO ABIERTO | M21110400170 | New_Event | Wire Down | Include | Include | Equipment | 112 | 2021-11-04 | 11200 | keep | 0 | Nov | 2021 | 0.0076283 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2021-11-04 22:02 | 2021-11-05 10:29 | 60 | 012:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | R21110400042 | New_Event |  |  | Include | Wildlife | 747 | 2021-11-04 | 44820 | keep | 0 | Nov | 2021 | 0.030527 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-11-04 22:03 | 2021-11-05 17:29 | 4 | 019:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21110400173 | New_Event | Bad Weather | Include | Include | Weather | 1166 | 2021-11-04 | 4664 | keep | 0 | Nov | 2021 | 0.0031766 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2021-11-04 22:55 | 2021-11-04 22:57 | 2126 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA | C21110400192 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-04 | 4252 | keep | 0 | Nov | 2021 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
CANOVANAS | 2021-11-04 23:03 | 2021-11-05 09:51 | 140 | 010:48 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | R21110400050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 648 | 2021-11-04 | 90720 | keep | 0 | Nov | 2021 | 0.061789 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
SAN JUAN | 2021-11-05 00:19 | 2021-11-05 05:21 | 550 | 005:02 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETES N/O 30% DE LA CARGA A TRAVES DEL 1529-15 | S21110500003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 302 | 2021-11-05 | 166100 | keep | 0 | Nov | 2021 | 0.11313 | 0.0003746 | Sustained | FALSE | FALSE | Not_TMED_Event | 550
CAGUAS | 2021-11-05 01:48 | 2021-11-05 13:55 | 491 | 012:07 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA MAL TIEMPO | C21110500007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 727 | 2021-11-05 | 356957 | keep | 0 | Nov | 2021 | 0.24312 | 0.00033442 | Sustained | FALSE | FALSE | Not_TMED_Event | 491
HUMACAO | 2021-11-05 02:09 | 2021-11-05 02:10 | 2126 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | C21110500008 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-11-05 | 2126 | keep | 0 | Nov | 2021 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2021-11-05 02:10 | 2021-11-05 10:52 | 221 | 008:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21110500030 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 522 | 2021-11-05 | 115362 | keep | 0 | Nov | 2021 | 0.078573 | 0.00015052 | Sustained | FALSE | FALSE | Not_TMED_Event | 221
BAYAMON | 2021-11-05 02:22 | 2021-11-05 09:45 | 100 | 007:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN DOS C/L Y SE REMPLAZO CAJA PRIMARIA | B21110500030 | New_Event | Cutout Failure | Include | Include | Equipment | 443 | 2021-11-05 | 44300 | keep | 0 | Nov | 2021 | 0.030173 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-11-05 02:25 | 2021-11-05 13:07 | 55 | 010:42 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE DESGANCHO | C21110500009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 642 | 2021-11-05 | 35310 | keep | 0 | Nov | 2021 | 0.024049 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
MAYAGÃœEZ | 2021-11-05 03:56 | 2021-11-05 16:09 | 5 | 012:13 | P | PARARRAYOS DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO DOS PARARRAYOS AVERIADOS | M21110500001 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 733 | 2021-11-05 | 3665 | keep | 0 | Nov | 2021 | 0.0024962 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2021-11-05 04:52 | 2021-11-05 04:53 | 2708 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21110500005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-05 | 2708 | keep | 0 | Nov | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2021-11-05 04:53 | 2021-11-05 12:30 | 60 | 007:37 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | R21110500014 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 457 | 2021-11-05 | 27420 | keep | 0 | Nov | 2021 | 0.018676 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2021-11-05 04:53 | 2021-11-05 10:46 | 210 | 005:53 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 65 EN CORTES DE LINEAS | R21110500015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 353 | 2021-11-05 | 74130 | keep | 0 | Nov | 2021 | 0.05049 | 0.00014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 210
GUAYAMA | 2021-11-05 05:21 | 2021-11-05 11:43 | 50 | 006:22 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21110500003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 382 | 2021-11-05 | 19100 | keep | 0 | Nov | 2021 | 0.013009 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-11-05 05:36 | 2021-11-05 05:37 | 1342 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21110500022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-05 | 1342 | keep | 0 | Nov | 2021 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
HUMACAO | 2021-11-05 06:18 | 2021-11-05 06:19 | 3902 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C21110500026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-05 | 3902 | keep | 0 | Nov | 2021 | 0.0026576 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
HUMACAO | 2021-11-05 06:24 | 2021-11-05 12:06 | 417 | 005:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21110500029 | New_Event | Bad Weather | Include | Include | Weather | 342 | 2021-11-05 | 142614 | keep | 0 | Nov | 2021 | 0.097134 | 0.00028402 | Sustained | FALSE | FALSE | Not_TMED_Event | 417
BAYAMON | 2021-11-05 07:04 | 2021-11-05 11:22 | 50 | 004:18 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L SE REMPLAZO AISLADOR PARTIDO | B21110500005 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 258 | 2021-11-05 | 12900 | keep | 0 | Nov | 2021 | 0.0087861 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-11-05 07:28 | 2021-11-05 15:30 | 3 | 008:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A LINEA | R21110500012 | New_Event | Wire Down | Include | Include | Equipment | 482 | 2021-11-05 | 1446 | keep | 0 | Nov | 2021 | 0.00098486 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-11-05 07:46 | 2021-11-05 18:10 | 20 | 010:24 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21110500004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 624 | 2021-11-05 | 12480 | keep | 0 | Nov | 2021 | 0.0085001 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-11-05 07:49 | 2021-11-05 11:14 | 35 | 003:25 | P | DESGANCHE | 1 X 25 Y 1 X 20 EN CORTES DE LINEAS | R21110500013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2021-11-05 | 7175 | keep | 0 | Nov | 2021 | 0.0048869 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2021-11-05 07:53 | 2021-11-05 09:36 | 19 | 001:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21110500052 | New_Event | Bad Weather | Include | Include | Weather | 103 | 2021-11-05 | 1957 | keep | 0 | Nov | 2021 | 0.0013329 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
PONCE | 2021-11-05 08:24 | 2021-11-05 11:17 | 87 | 002:53 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P21110500009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2021-11-05 | 15051 | keep | 0 | Nov | 2021 | 0.010251 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
CAGUAS | 2021-11-05 08:26 | 2021-11-05 10:19 | 1261 | 001:53 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO INTERRUPTOR QUEDO FUERA SE SECCIONALIZO AISLADOR ROTO CERRADO POR CONTROL | C21110500060 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 113 | 2021-11-05 | 142493 | keep | 0 | Nov | 2021 | 0.097051 | 0.00085886 | Sustained | FALSE | FALSE | Not_TMED_Event | 1261
VEGA BAJA | 2021-11-05 08:34 | 2021-11-05 17:50 | 50 | 009:16 | P | HERRAJE ROTO O PODRIDO | 1 X 80 Y 1 X 50 EN CORTE DE LINEA SE ELIMINO CRUCETA PARTIDA | B21110500012 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 556 | 2021-11-05 | 27800 | keep | 0 | Nov | 2021 | 0.018934 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-05 08:37 | 2021-11-05 13:35 | 6 | 004:58 | P | PARARRAYOS DEFECTUOSO | 1 X 20 EN RISER SE REMPLAZO PARARRAYOS DEFECTUOSO | M21110500014 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 298 | 2021-11-05 | 1788 | keep | 0 | Nov | 2021 | 0.0012178 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-11-05 08:38 | 2021-11-05 14:38 | 80 | 006:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21110500062 | New_Event | Bad Weather | Include | Include | Weather | 360 | 2021-11-05 | 28800 | keep | 0 | Nov | 2021 | 0.019616 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2021-11-05 08:39 | 2021-11-05 14:30 | 45 | 005:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21110500014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 351 | 2021-11-05 | 15795 | keep | 0 | Nov | 2021 | 0.010758 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
VEGA BAJA | 2021-11-05 09:00 | 2021-11-05 10:30 | 6 | 001:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR Y SE REMPLAZO CAJA | B21110500015 | New_Event | Cutout Failure | Include | Include | Equipment | 90 | 2021-11-05 | 540 | keep | 0 | Nov | 2021 | 0.00036779 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-11-05 09:10 | 2021-11-05 15:44 | 1 | 006:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | M21110500018 | New_Event | Bad Weather | Include | Include | Weather | 394 | 2021-11-05 | 394 | keep | 0 | Nov | 2021 | 0.00026835 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-11-05 09:18 | 2021-11-05 10:04 | 30 | 000:46 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS Y ENRREDADERA SOBRE LAS LINEAS | A21110500012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 46 | 2021-11-05 | 1380 | keep | 0 | Nov | 2021 | 0.00093991 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-11-05 09:28 | 2021-11-05 09:29 | 1494 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA | A21110500013 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-05 | 1494 | keep | 0 | Nov | 2021 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
ARECIBO | 2021-11-05 09:29 | 2021-11-05 14:28 | 200 | 004:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 Y 1 X 200 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | A21110500018 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 299 | 2021-11-05 | 59800 | keep | 0 | Nov | 2021 | 0.04073 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2021-11-05 09:40 | 2021-11-05 10:59 | 17 | 001:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRE CAJA EN TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA POR CAMION | P21110500007 | New_Event |  |  | Include | Wildlife | 79 | 2021-11-05 | 1343 | keep | 0 | Nov | 2021 | 0.00091471 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
UTUADO | 2021-11-05 09:40 | 2021-11-05 18:18 | 200 | 008:38 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE | A21110500010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 518 | 2021-11-05 | 103600 | keep | 0 | Nov | 2021 | 0.070561 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-11-05 09:45 | 2021-11-05 14:29 | 12 | 004:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | SS2111050004 | New_Event | Secondary Wire Down | Include | Include | Equipment | 284 | 2021-11-05 | 3408 | keep | 0 | Nov | 2021 | 0.0023212 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-11-05 09:55 | 2021-11-05 10:46 | 7 | 000:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21110500005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 51 | 2021-11-05 | 357 | keep | 0 | Nov | 2021 | 0.00024315 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2021-11-05 10:11 | 2021-11-05 17:35 | 50 | 007:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO A TRANSFORMADOR | M21110500027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 444 | 2021-11-05 | 22200 | keep | 0 | Nov | 2021 | 0.01512 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-11-05 10:17 | 2021-11-05 12:39 | 9 | 002:22 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA REEMPLAZAR 2 BARRAS EN PEDESTAL | C21110500078 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 142 | 2021-11-05 | 1278 | keep | 0 | Nov | 2021 | 0.00087044 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2021-11-05 10:19 | 2021-11-05 13:09 | 1179 | 002:50 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR ROTO Y SE CERRO MACHETES | C21110500075 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 170 | 2021-11-05 | 200430 | keep | 0 | Nov | 2021 | 0.13651 | 0.00080301 | Sustained | FALSE | FALSE | Not_TMED_Event | 1179
PONCE | 2021-11-05 10:20 | 2021-11-06 08:18 | 12 | 021:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | P21110500002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1318 | 2021-11-05 | 15816 | keep | 0 | Nov | 2021 | 0.010772 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-11-05 10:27 | 2021-11-05 10:28 | 2391 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S21110500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-05 | 2391 | keep | 0 | Nov | 2021 | 0.0016285 | 0.0016285 | Momentary | FALSE | FALSE | Not_TMED_Event | 2391
PONCE | 2021-11-05 10:27 | 2021-11-05 12:29 | 50 | 002:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21110500029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2021-11-05 | 6100 | keep | 0 | Nov | 2021 | 0.0041547 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2021-11-05 10:30 | 2021-11-05 15:15 | 12 | 004:45 | P | ESTRUCTURA AVERIADA | POSTE PRIMARIO PARTIDO SE ABRE CAJA EN TRANSFORMADOR PARA RELOCALIZARLO EN POSTE EXISTENTE | P21110500026 | New_Event | Defective Pole | Include | Include | Equipment | 285 | 2021-11-05 | 3420 | keep | 0 | Nov | 2021 | 0.0023293 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-11-05 10:34 | 2021-11-05 10:37 | 5290 | 000:03 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA EL 1336-09 | S21110500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-05 | 15870 | keep | 0 | Nov | 2021 | 0.010809 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2021-11-05 10:34 | 2021-11-05 10:37 | 207 | 000:03 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1336-08 | S21110500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-05 | 621 | keep | 0 | Nov | 2021 | 0.00042296 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
CAGUAS | 2021-11-05 10:34 | 2021-11-05 12:18 | 21 | 001:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21110500079 | New_Event | Bad Weather | Include | Include | Weather | 104 | 2021-11-05 | 2184 | keep | 0 | Nov | 2021 | 0.0014875 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
MAYAGÃœEZ | 2021-11-05 10:37 | 2021-11-05 15:11 | 100 | 004:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | M21110500023 | New_Event | Wire Down | Include | Include | Equipment | 274 | 2021-11-05 | 27400 | keep | 0 | Nov | 2021 | 0.018662 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-11-05 10:38 | 2021-11-05 10:39 | 570 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21110500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-05 | 570 | keep | 0 | Nov | 2021 | 0.00038822 | 0.00038822 | Momentary | FALSE | FALSE | Not_TMED_Event | 570
HUMACAO | 2021-11-05 10:42 | 2021-11-05 17:26 | 12 | 006:44 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA | C21110500080 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 404 | 2021-11-05 | 4848 | keep | 0 | Nov | 2021 | 0.003302 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-11-05 10:50 | 2021-11-05 16:00 | 2 | 005:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | VIA LIBRE D2021-00467 DESENERGIZAR PM 10 PARA ALAMBRAR TOMAS SECUNDARIAS | M21110500026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 310 | 2021-11-05 | 620 | keep | 0 | Nov | 2021 | 0.00042228 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2021-11-05 10:52 | 2021-11-05 14:12 | 1 | 003:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | R21110500024 | New_Event | Wire Down | Include | Include | Equipment | 200 | 2021-11-05 | 200 | keep | 0 | Nov | 2021 | 0.00013622 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-11-05 10:55 | 2021-11-06 15:00 | 8 | 028:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO DIFERENTES CASOS EL MISMO EVENTO | A21110500034 | New_Event | Wire Down | Include | Include | Equipment | 1685 | 2021-11-05 | 13480 | keep | 0 | Nov | 2021 | 0.0091812 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-11-05 10:55 | 2021-11-05 17:04 | 30 | 006:09 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PARTIDO DE 45' METAL CLASE III EN EL FID 22689943 Y SE CERRO CORTE DE LINEA | A21110500034 | New_Event | Defective Pole | Include | Include | Equipment | 369 | 2021-11-05 | 11070 | keep | 0 | Nov | 2021 | 0.0075397 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-11-05 11:00 | 2021-11-05 11:52 | 10 | 000:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | A21110500032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 52 | 2021-11-05 | 520 | keep | 0 | Nov | 2021 | 0.00035417 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-11-05 11:08 | 2021-11-05 12:34 | 6 | 001:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21110500017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 86 | 2021-11-05 | 516 | keep | 0 | Nov | 2021 | 0.00035145 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2021-11-05 11:25 | 2021-11-05 18:10 | 6 | 006:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARARON VARIOS TRAMOS DE SECUNDARIAS EN MALAS CONDICIONES | A21110500036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 405 | 2021-11-05 | 2430 | keep | 0 | Nov | 2021 | 0.0016551 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-11-05 11:29 | 2021-11-05 14:16 | 20 | 002:47 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTE DE LINEA MAL TIEMPO | R21110500028 | New_Event | Bad Weather | Include | Include | Weather | 167 | 2021-11-05 | 3340 | keep | 0 | Nov | 2021 | 0.0022749 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2021-11-05 11:33 | 2021-11-05 11:34 | 569 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21110500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-05 | 569 | keep | 0 | Nov | 2021 | 0.00038754 | 0.00038754 | Momentary | FALSE | FALSE | Not_TMED_Event | 569
AGUADILLA | 2021-11-05 11:33 | 2021-11-05 11:34 | 1245 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21110500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-05 | 1245 | keep | 0 | Nov | 2021 | 0.00084796 | 0.00084796 | Momentary | FALSE | FALSE | Not_TMED_Event | 1245
AGUADILLA | 2021-11-05 11:33 | 2021-11-05 11:34 | 1155 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21110500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-05 | 1155 | keep | 0 | Nov | 2021 | 0.00078667 | 0.00078667 | Momentary | FALSE | FALSE | Not_TMED_Event | 1155
AGUADILLA | 2021-11-05 11:33 | 2021-11-05 11:34 | 867 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21110500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-05 | 867 | keep | 0 | Nov | 2021 | 0.00059051 | 0.00059051 | Momentary | FALSE | FALSE | Not_TMED_Event | 867
AGUADILLA | 2021-11-05 11:33 | 2021-11-05 11:34 | 257 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21110500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-05 | 257 | keep | 0 | Nov | 2021 | 0.00017504 | 0.00017504 | Momentary | FALSE | FALSE | Not_TMED_Event | 257
AGUADILLA | 2021-11-05 11:33 | 2021-11-05 11:34 | 1336 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21110500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-05 | 1336 | keep | 0 | Nov | 2021 | 0.00090994 | 0.00090994 | Momentary | FALSE | FALSE | Not_TMED_Event | 1336
AGUADILLA | 2021-11-05 11:33 | 2021-11-05 11:34 | 3315 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21110500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-05 | 3315 | keep | 0 | Nov | 2021 | 0.0022578 | 0.0022578 | Momentary | FALSE | FALSE | Not_TMED_Event | 3315
AGUADILLA | 2021-11-05 11:33 | 2021-11-05 11:34 | 1718 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21110500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-05 | 1718 | keep | 0 | Nov | 2021 | 0.0011701 | 0.0011701 | Momentary | FALSE | FALSE | Not_TMED_Event | 1718
SAN JUAN | 2021-11-05 11:48 | 2021-11-05 14:18 | 1 | 002:30 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21110500072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 150 | 2021-11-05 | 150 | keep | 0 | Nov | 2021 | 0.00010216 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-05 11:52 | 2021-11-05 15:00 | 30 | 003:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA | S21110500074 | New_Event | Wire Down | Include | Include | Equipment | 188 | 2021-11-05 | 5640 | keep | 0 | Nov | 2021 | 0.0038414 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-11-05 12:04 | 2021-11-05 20:20 | 50 | 008:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21110500037 | New_Event | Bad Weather | Include | Include | Weather | 496 | 2021-11-05 | 24800 | keep | 0 | Nov | 2021 | 0.016891 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2021-11-05 12:09 | 2021-11-05 16:19 | 32 | 004:10 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA DE QUENEPA DE LA LINEA | R21110500033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 250 | 2021-11-05 | 8000 | keep | 0 | Nov | 2021 | 0.0054488 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
HUMACAO | 2021-11-05 12:15 | 2021-11-05 12:16 | 2450 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 12600 DE HUMACAO TC A VERDEMAR | C21110500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-05 | 2450 | keep | 0 | Nov | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2021-11-05 12:15 | 2021-11-05 12:16 | 640 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 12600 DE HUMACAO TC A VERDEMAR | C21110500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-05 | 640 | keep | 0 | Nov | 2021 | 0.0004359 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
MAYAGÃœEZ | 2021-11-05 12:28 | 2021-11-05 18:15 | 15 | 005:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE DESCRUZO LINEA ELIMINANDO LINEA INOPERANTE | M21110500042 | New_Event | Wire Down | Include | Include | Equipment | 347 | 2021-11-05 | 5205 | keep | 0 | Nov | 2021 | 0.0035451 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-11-05 12:33 | 2021-11-05 16:03 | 40 | 003:30 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21110500038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 210 | 2021-11-05 | 8400 | keep | 0 | Nov | 2021 | 0.0057212 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-11-05 12:44 | 2021-11-05 16:48 | 55 | 004:04 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALZIO DESGANCHE | C21110500096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 244 | 2021-11-05 | 13420 | keep | 0 | Nov | 2021 | 0.0091403 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CAGUAS | 2021-11-05 12:57 | 2021-11-05 15:05 | 54 | 002:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN RISER CRUCE POR GLOBO | C21110500098 | New_Event |  |  | Include | Wildlife | 128 | 2021-11-05 | 6912 | keep | 0 | Nov | 2021 | 0.0047077 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
SAN JUAN | 2021-11-05 13:03 | 2021-11-06 12:30 | 30 | 023:27 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO | S21110500079 | New_Event | Switch Failure | Include | Include | Equipment | 1407 | 2021-11-05 | 42210 | keep | 0 | Nov | 2021 | 0.028749 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-11-05 13:31 | 2021-11-05 18:23 | 15 | 004:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR TRANSFORMADOR PARA REPARAR SECUNDARIA | S21110500082 | New_Event | Secondary Wire Down | Include | Include | Equipment | 292 | 2021-11-05 | 4380 | keep | 0 | Nov | 2021 | 0.0029832 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-11-05 13:34 | 2021-11-05 13:43 | 1 | 000:09 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21110500045 | New_Event | Bad Weather | Include | Include | Weather | 9 | 2021-11-05 | 9 | keep | 0 | Nov | 2021 | 6.1299e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-11-05 13:38 | 2021-11-05 16:48 | 36 | 003:10 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21110500106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2021-11-05 | 6840 | keep | 0 | Nov | 2021 | 0.0046587 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
HUMACAO | 2021-11-05 13:53 | 2021-11-05 17:56 | 55 | 004:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21110500108 | New_Event | Bad Weather | Include | Include | Weather | 243 | 2021-11-05 | 13365 | keep | 0 | Nov | 2021 | 0.0091028 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
HUMACAO | 2021-11-05 13:53 | 2021-11-05 13:54 | 3420 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C21110500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-05 | 3420 | keep | 0 | Nov | 2021 | 0.0023293 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
CAGUAS | 2021-11-05 14:06 | 2021-11-05 14:55 | 10 | 000:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZO DE BARRA EN PEDESTAL | C21110500109 | New_Event | Secondary Wire Down | Include | Include | Equipment | 49 | 2021-11-05 | 490 | keep | 0 | Nov | 2021 | 0.00033374 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-05 14:11 | 2021-11-05 16:01 | 10 | 001:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BARRAS DE PEDESTAL | B21110500049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 110 | 2021-11-05 | 1100 | keep | 0 | Nov | 2021 | 0.0007492 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-11-05 14:12 | 2021-11-05 16:55 | 494 | 002:43 | T | BREAKER DEFECTUOSO O NO OPERA | BREAKER 5005-05 CON BOBINA DE CLOSE QUEMADA SE PASA CARGA A 5005-04 | P21110500046 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 163 | 2021-11-05 | 80522 | keep | 0 | Nov | 2021 | 0.054843 | 0.00033646 | Sustained | FALSE | FALSE | Not_TMED_Event | 494
BAYAMON | 2021-11-05 14:24 | 2021-11-05 17:02 | 50 | 002:38 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21110500053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 158 | 2021-11-05 | 7900 | keep | 0 | Nov | 2021 | 0.0053807 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-05 14:27 | 2021-11-06 10:04 | 60 | 019:37 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21110500054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1177 | 2021-11-05 | 70620 | keep | 0 | Nov | 2021 | 0.048099 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-11-05 14:28 | 2021-11-05 16:46 | 5 | 002:18 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA RETEZAR LINEA SECUNDARIA Y SE REALIZO DESGANCHE | A21110500047 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 138 | 2021-11-05 | 690 | keep | 0 | Nov | 2021 | 0.00046996 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-11-05 14:28 | 2021-11-05 14:32 | 1494 | 000:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR POR PERSONAL CERRANDO CORTE DE LINEA | A21110500053 | New_Event | Wire Down | Include | Include | Equipment | 4 | 2021-11-05 | 5976 | keep | 0 | Nov | 2021 | 0.0040702 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
UTUADO | 2021-11-05 14:32 | 2021-11-05 16:09 | 40 | 001:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21110500055 | New_Event | Bad Weather | Include | Include | Weather | 97 | 2021-11-05 | 3880 | keep | 0 | Nov | 2021 | 0.0026427 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-11-05 14:32 | 2021-11-05 16:50 | 200 | 002:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 Y 1 X 200 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | A21110500018 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 138 | 2021-11-05 | 27600 | keep | 0 | Nov | 2021 | 0.018798 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2021-11-05 14:35 | 2021-11-06 13:06 | 6 | 022:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO NEUTRAL SECUNDARIO | C21110500112 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1351 | 2021-11-05 | 8106 | keep | 0 | Nov | 2021 | 0.005521 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2021-11-05 14:47 | 2021-11-05 17:29 | 24 | 002:42 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | P21110500048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 162 | 2021-11-05 | 3888 | keep | 0 | Nov | 2021 | 0.0026481 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
ARECIBO | 2021-11-05 14:50 | 2021-11-05 16:49 | 2132 | 001:59 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR POR LINEA ARREADA | A21110500000 | New_Event | Wire Down | Include | Include | Equipment | 119 | 2021-11-05 | 253708 | keep | 0 | Nov | 2021 | 0.1728 | 0.0014521 | Sustained | FALSE | FALSE | Not_TMED_Event | 2132
MAYAGÃœEZ | 2021-11-05 14:58 | 2021-11-05 18:20 | 51 | 003:22 | T | DESGANCHE | DISPARO DE INTERRUPTOR 7902-03 QUE ESTA LLEVANDO LA CARGA DEL 7902-02 SE RETIRO ARBOL SOBRE LINEA PRIMARIA | M21110500051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2021-11-05 | 10302 | keep | 0 | Nov | 2021 | 0.0070166 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2021-11-05 14:58 | 2021-11-05 18:20 | 721 | 003:22 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE RETIRO ARBOL SOBRE LINEA PRIMARIA | M21110500051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2021-11-05 | 145642 | keep | 0 | Nov | 2021 | 0.099196 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
SAN JUAN | 2021-11-05 15:00 | 2021-11-05 18:23 | 12 | 003:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA RELOCALIZAR SECUNDARIA | S21110500074 | New_Event | Secondary Wire Down | Include | Include | Equipment | 203 | 2021-11-05 | 2436 | keep | 0 | Nov | 2021 | 0.0016591 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-11-05 15:11 | 2021-11-06 09:30 | 60 | 018:19 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P21110500052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1099 | 2021-11-05 | 65940 | keep | 0 | Nov | 2021 | 0.044911 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-11-05 15:21 | 2021-11-06 17:02 | 15 | 025:41 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21110500054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1541 | 2021-11-05 | 23115 | keep | 0 | Nov | 2021 | 0.015744 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-11-05 15:25 | 2021-11-05 16:13 | 14 | 000:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA RELOCALIZAR SECUNDARIA | C21110500120 | New_Event | Secondary Wire Down | Include | Include | Equipment | 48 | 2021-11-05 | 672 | keep | 0 | Nov | 2021 | 0.0004577 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2021-11-05 15:40 | 2021-11-05 17:55 | 3 | 002:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR SE DESGANCHO Y REEMPLAZO PORTAFUSIBLE | R21110500044 | New_Event | Cutout Failure | Include | Include | Equipment | 135 | 2021-11-05 | 405 | keep | 0 | Nov | 2021 | 0.00027584 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2021-11-05 15:41 | 2021-11-05 16:58 | 1879 | 001:17 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE BORRARON BANDERAS CERRADO POR CONTROL | C21110500122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 77 | 2021-11-05 | 144683 | keep | 0 | Nov | 2021 | 0.098543 | 0.0012798 | Sustained | FALSE | FALSE | Not_TMED_Event | 1879
MAYAGÃœEZ | 2021-11-05 15:42 | 2021-11-05 17:53 | 100 | 002:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21110500055 | New_Event | Bad Weather | Include | Include | Weather | 131 | 2021-11-05 | 13100 | keep | 0 | Nov | 2021 | 0.0089224 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-11-05 15:52 | 2021-11-05 19:27 | 15 | 003:35 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50KVA CON PROBLEMAS DE VOLTAJE | S21110500092 | New_Event | Service Transformer Failure | Include | Include | Equipment | 215 | 2021-11-05 | 3225 | keep | 0 | Nov | 2021 | 0.0021965 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2021-11-05 16:08 | 2021-11-05 17:09 | 2 | 001:01 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 15KVA POR 25KVA EN EL FID 33678097 MARCA GRUCO NUMERO SERIE 12112156891 | A21110500080 | New_Event | Service Transformer Failure | Include | Include | Equipment | 61 | 2021-11-05 | 122 | keep | 0 | Nov | 2021 | 8.3094e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2021-11-05 16:10 | 2021-11-06 19:35 | 40 | 027:25 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21110600077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1645 | 2021-11-05 | 65800 | keep | 0 | Nov | 2021 | 0.044816 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-05 16:23 | 2021-11-05 18:28 | 30 | 002:05 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | B21110500065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2021-11-05 | 3750 | keep | 0 | Nov | 2021 | 0.0025541 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-11-05 16:29 | 2021-11-05 21:13 | 15 | 004:44 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21110500066 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 284 | 2021-11-05 | 4260 | keep | 0 | Nov | 2021 | 0.0029015 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-11-05 16:49 | 2021-11-05 19:35 | 300 | 002:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE RETEZO LINEA ARREADA | A21110500079 | Partial_restoration | Wire Down | Include | Include | Equipment | 166 | 2021-11-05 | 49800 | keep | 0 | Nov | 2021 | 0.033919 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-05 16:54 | 2021-11-05 16:55 | 590 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21110500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-05 | 590 | keep | 0 | Nov | 2021 | 0.00040185 | 0.00040185 | Momentary | FALSE | FALSE | Not_TMED_Event | 590
PONCE | 2021-11-05 16:55 | 2021-11-06 06:45 | 68 | 013:50 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21110500062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 830 | 2021-11-05 | 56440 | keep | 0 | Nov | 2021 | 0.038441 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
ARECIBO | 2021-11-05 17:17 | 2021-11-06 08:52 | 8 | 015:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21110500089 | New_Event | Bad Weather | Include | Include | Weather | 935 | 2021-11-05 | 7480 | keep | 0 | Nov | 2021 | 0.0050946 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-11-05 17:38 | 2021-11-06 08:44 | 10 | 015:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21110500094 | New_Event | Bad Weather | Include | Include | Weather | 906 | 2021-11-05 | 9060 | keep | 0 | Nov | 2021 | 0.0061707 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-11-05 17:39 | 2021-11-05 17:49 | 3420 | 000:10 | S | MAL TIEMPO/RAYOS/WET ASH | DISPARO INTERRUPTOR 0010 MUCHA LLUVIA EN EL AREA | C21110500000 | New_Event | Bad Weather | Include | Include | Weather | 10 | 2021-11-05 | 34200 | keep | 0 | Nov | 2021 | 0.023293 | 0.0023293 | Sustained | FALSE | FALSE | Not_TMED_Event | 3420
HUMACAO | 2021-11-05 17:39 | 2021-11-05 17:49 | 4 | 000:10 | S | MAL TIEMPO/RAYOS/WET ASH | DISPARO INTERRUPTOR 0010 MUCHA LLUVIA EN EL AREA | C21110500000 | New_Event | Bad Weather | Include | Include | Weather | 10 | 2021-11-05 | 40 | keep | 0 | Nov | 2021 | 2.7244e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2021-11-05 17:39 | 2021-11-05 17:49 | 3 | 000:10 | S | MAL TIEMPO/RAYOS/WET ASH | DISPARO INTERRUPTOR 0010 MUCHA LLUVIA EN EL AREA | C21110500000 | New_Event | Bad Weather | Include | Include | Weather | 10 | 2021-11-05 | 30 | keep | 0 | Nov | 2021 | 2.0433e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2021-11-05 17:39 | 2021-11-06 07:13 | 12 | 013:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA | C21110600134 | New_Event | Secondary Wire Down | Include | Include | Equipment | 814 | 2021-11-05 | 9768 | keep | 0 | Nov | 2021 | 0.0066529 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-11-05 17:53 | 2021-11-06 08:18 | 5 | 014:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | C21110500140 | New_Event | Secondary Wire Down | Include | Include | Equipment | 865 | 2021-11-05 | 4325 | keep | 0 | Nov | 2021 | 0.0029457 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2021-11-05 18:00 | 2021-11-05 18:50 | 1 | 000:50 | P | NO SE REPORTO CAUSA | SE CERRO CAJA ABIERTA EN TRANSFORMADOR NO TENIAN FUSIBLE FUNDIDO | M21110500069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 50 | 2021-11-05 | 50 | keep | 0 | Nov | 2021 | 3.4055e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-05 18:06 | 2021-11-06 10:17 | 6 | 016:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21110500068 | New_Event | Secondary Wire Down | Include | Include | Equipment | 971 | 2021-11-05 | 5826 | keep | 0 | Nov | 2021 | 0.0039681 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2021-11-05 18:10 | 2021-11-05 18:11 | 4188 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R21110500050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-05 | 4188 | keep | 0 | Nov | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CAGUAS | 2021-11-05 18:12 | 2021-11-06 11:02 | 30 | 016:50 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | C21110500142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1010 | 2021-11-05 | 30300 | keep | 0 | Nov | 2021 | 0.020637 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-11-05 18:15 | 2021-11-05 20:25 | 88 | 002:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21110500144 | New_Event | Bad Weather | Include | Include | Weather | 130 | 2021-11-05 | 11440 | keep | 0 | Nov | 2021 | 0.0077917 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
VEGA BAJA | 2021-11-05 18:31 | 2021-11-05 20:11 | 15 | 001:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 25KVA CON PROBLEMAS DE VOLTAJE | B21110500070 | New_Event | Service Transformer Failure | Include | Include | Equipment | 100 | 2021-11-05 | 1500 | keep | 0 | Nov | 2021 | 0.0010216 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-11-05 18:58 | 2021-11-06 12:58 | 51 | 018:00 | T | DESGANCHE | SE RETIRO PALMA SOBRE LINEAS PRIMARIAS Y SE CERRO AMARRE CON 7902-03 | M21110500071 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1080 | 2021-11-05 | 55080 | keep | 0 | Nov | 2021 | 0.037515 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-11-05 18:58 | 2021-11-05 22:00 | 721 | 003:02 | T | DESGANCHE | SE ABRIO EL AMARRE ENTRE LOS ALIMENTADORES 7902-2 Y 7902-03 YA QUE ESTOS MACHETES ESTAN QUEMADOS Y SE CERRO EL INTERRUPTOR 7902-03 | M21110500076 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 182 | 2021-11-05 | 131222 | keep | 0 | Nov | 2021 | 0.089375 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-11-05 19:02 | 2021-11-06 09:14 | 60 | 014:12 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21110500077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 852 | 2021-11-05 | 51120 | keep | 0 | Nov | 2021 | 0.034818 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2021-11-05 19:05 | 2021-11-05 19:06 | 1922 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C21110500146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-05 | 1922 | keep | 0 | Nov | 2021 | 0.0013091 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
HUMACAO | 2021-11-05 19:25 | 2021-11-05 20:51 | 3420 | 001:26 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DEL 0010 SE RETIRO AVE DEL PARARRAYO DE LA BAJA DEL TRANSFORMADOR | C21110500000 | New_Event |  |  | Include | Wildlife | 86 | 2021-11-05 | 294120 | keep | 0 | Nov | 2021 | 0.20032 | 0.0023293 | Sustained | FALSE | FALSE | Not_TMED_Event | 3420
HUMACAO | 2021-11-05 19:25 | 2021-11-05 20:51 | 4 | 001:26 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DEL 0010 SE RETIRO AVE DEL PARARRAYO DE LA BAJA DEL TRANSFORMADOR | C21110500000 | New_Event |  |  | Include | Wildlife | 86 | 2021-11-05 | 344 | keep | 0 | Nov | 2021 | 0.0002343 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2021-11-05 19:25 | 2021-11-05 20:51 | 3 | 001:26 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DEL 0010 SE RETIRO AVE DEL PARARRAYO DE LA BAJA DEL TRANSFORMADOR | C21110500000 | New_Event |  |  | Include | Wildlife | 86 | 2021-11-05 | 258 | keep | 0 | Nov | 2021 | 0.00017572 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-11-05 19:31 | 2021-11-06 14:29 | 5 | 018:58 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR SE DESGANCHO SE REPARO SECUNDARIA | B21110500072 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1138 | 2021-11-05 | 5690 | keep | 0 | Nov | 2021 | 0.0038754 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2021-11-05 20:06 | 2021-11-06 08:18 | 45 | 012:12 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21110500159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 732 | 2021-11-05 | 32940 | keep | 0 | Nov | 2021 | 0.022435 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
PONCE | 2021-11-05 20:34 | 2021-11-06 09:40 | 282 | 013:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA QUEMADA | P21110500072 | New_Event | Cutout Failure | Include | Include | Equipment | 786 | 2021-11-05 | 221652 | keep | 0 | Nov | 2021 | 0.15097 | 0.00019207 | Sustained | FALSE | FALSE | Not_TMED_Event | 282
CAGUAS | 2021-11-05 21:00 | 2021-11-05 21:01 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | C21070300168 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-05 | 2203 | keep | 0 | Nov | 2021 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
FAJARDO | 2021-11-05 21:55 | 2021-11-06 09:58 | 70 | 012:03 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | R21110500055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 723 | 2021-11-05 | 50610 | keep | 0 | Nov | 2021 | 0.03447 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2021-11-05 22:29 | 2021-11-06 08:18 | 10 | 009:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | C21110500172 | New_Event |  |  | Include | Wildlife | 589 | 2021-11-05 | 5890 | keep | 0 | Nov | 2021 | 0.0040117 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-05 22:44 | 2021-11-06 15:33 | 66 | 016:49 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO Y SE NORMALIZO LA CARGA | B21110500085 | New_Event | Defective Pole | Include | Include | Equipment | 1009 | 2021-11-05 | 66594 | keep | 0 | Nov | 2021 | 0.045357 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
BARRANQUITAS | 2021-11-05 22:56 | 2021-11-06 12:49 | 50 | 013:53 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C21110500074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 833 | 2021-11-05 | 41650 | keep | 0 | Nov | 2021 | 0.028368 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-11-05 22:58 | 2021-11-06 09:57 | 50 | 010:59 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B21110500091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 659 | 2021-11-05 | 32950 | keep | 0 | Nov | 2021 | 0.022442 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-05 23:28 | 2021-11-06 09:06 | 30 | 009:38 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21110500085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 578 | 2021-11-05 | 17340 | keep | 0 | Nov | 2021 | 0.01181 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2021-11-06 00:20 | 2021-11-06 01:00 | 5 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR CONEXIONES EN PEDESTAL SECUNDARIO | M21110500082 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2021-11-06 | 200 | keep | 0 | Nov | 2021 | 0.00013622 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-11-06 02:16 | 2021-11-06 09:03 | 20 | 006:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B21110600003 | New_Event | Cutout Failure | Include | Include | Equipment | 407 | 2021-11-06 | 8140 | keep | 0 | Nov | 2021 | 0.0055441 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-11-06 02:45 | 2021-11-06 08:18 | 50 | 005:33 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L CARGA DE 1909-09 POR 1907-03 | S21110600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 333 | 2021-11-06 | 16650 | keep | 0 | Nov | 2021 | 0.01134 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-11-06 03:16 | 2021-11-06 08:18 | 90 | 005:02 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C21110600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 302 | 2021-11-06 | 27180 | keep | 0 | Nov | 2021 | 0.018512 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2021-11-06 04:47 | 2021-11-06 08:49 | 60 | 004:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21100600004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2021-11-06 | 14520 | keep | 0 | Nov | 2021 | 0.0098895 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2021-11-06 04:47 | 2021-11-06 08:18 | 40 | 003:31 | P | DESGANCHE | 1 X 65 EN C/L | C21110600186 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2021-11-06 | 8440 | keep | 0 | Nov | 2021 | 0.0057484 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-06 04:53 | 2021-11-06 18:34 | 35 | 013:41 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21110600003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 821 | 2021-11-06 | 28735 | keep | 0 | Nov | 2021 | 0.019571 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
GUAYAMA | 2021-11-06 06:04 | 2021-11-06 15:06 | 10 | 009:02 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE BUSHING SECUNDARIO DE TRANSFORMADOR POR LINEA SECUNDARIA AVERIADA | P21110600001 | New_Event | Service Transformer Failure | Include | Include | Equipment | 542 | 2021-11-06 | 5420 | keep | 0 | Nov | 2021 | 0.0036915 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-11-06 06:06 | 2021-11-06 06:07 | 1979 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21110600004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-06 | 1979 | keep | 0 | Nov | 2021 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
CANOVANAS | 2021-11-06 06:10 | 2021-11-06 06:11 | 1648 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | R21110600006 | New_Event |  |  | Include | Wildlife | 1 | 2021-11-06 | 1648 | keep | 0 | Nov | 2021 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2021-11-06 06:11 | 2021-11-06 08:18 | 125 | 002:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 Y 1 X 50 EN CORTES DE LINEAS CRUCE POR AVE | R21110600007 | 1st_after_momentary |  |  | Include | Wildlife | 127 | 2021-11-06 | 15875 | keep | 0 | Nov | 2021 | 0.010812 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
HUMACAO | 2021-11-06 06:13 | 2021-11-06 09:33 | 75 | 003:20 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C21110600011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 200 | 2021-11-06 | 15000 | keep | 0 | Nov | 2021 | 0.010216 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2021-11-06 06:35 | 2021-11-06 06:36 | 651 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21110600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-06 | 651 | keep | 0 | Nov | 2021 | 0.00044339 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
SAN JUAN | 2021-11-06 06:39 | 2021-11-06 06:41 | 837 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1401-07 | S21110600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-06 | 1674 | keep | 0 | Nov | 2021 | 0.0011402 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2021-11-06 06:39 | 2021-11-06 06:41 | 908 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA EL 1401-06 | S21110600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-06 | 1816 | keep | 0 | Nov | 2021 | 0.0012369 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
BARRANQUITAS | 2021-11-06 06:42 | 2021-11-06 06:43 | 2635 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21110600000 | New_Event |  |  | Include | Wildlife | 1 | 2021-11-06 | 2635 | keep | 0 | Nov | 2021 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2021-11-06 06:43 | 2021-11-06 08:18 | 125 | 001:35 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C21110600013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 95 | 2021-11-06 | 11875 | keep | 0 | Nov | 2021 | 0.008088 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2021-11-06 07:12 | 2021-11-06 08:18 | 50 | 001:06 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21110600014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2021-11-06 | 3300 | keep | 0 | Nov | 2021 | 0.0022476 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-11-06 07:13 | 2021-11-06 07:14 | 1702 | 000:01 | T | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | RECIERRE | C21110600000 | Additional_clients | Secondary Wire Down | Include | Include | Equipment | 1 | 2021-11-06 | 1702 | keep | 0 | Nov | 2021 | 0.0011592 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-11-06 07:14 | 2021-11-06 11:12 | 80 | 003:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 Y 1 X 50 EN CORTES DE LINEAS CRUCE POR AVE | C21110600023 | New_Event |  |  | Include | Wildlife | 238 | 2021-11-06 | 19040 | keep | 0 | Nov | 2021 | 0.012968 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2021-11-06 07:14 | 2021-11-06 17:18 | 12 | 010:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA | C21110600134 | 1st_after_momentary | Secondary Wire Down | Include | Include | Equipment | 604 | 2021-11-06 | 7248 | keep | 0 | Nov | 2021 | 0.0049366 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-11-06 07:25 | 2021-11-07 10:05 | 30 | 026:40 | P | DESGANCHE | 1 X 30 EN C/L | C21110600016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1600 | 2021-11-06 | 48000 | keep | 0 | Nov | 2021 | 0.032693 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2021-11-06 07:32 | 2021-11-06 14:17 | 15 | 006:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABREN PUENTES PRIMARIOS PARA REMPLAZO DE 6 CAJAS PRIMARIAS DE 100 AMP EN TRES TRANSFORMADORES DISTINTOS | P21110600003 | New_Event | Cutout Failure | Include | Include | Equipment | 405 | 2021-11-06 | 6075 | keep | 0 | Nov | 2021 | 0.0041377 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-11-06 07:37 | 2021-11-06 07:38 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1206-03 | S21110600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-06 | 10211 | keep | 0 | Nov | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-11-06 07:37 | 2021-11-06 07:38 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVANDO EL 1204-05 | S21110600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-06 | 4133 | keep | 0 | Nov | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-11-06 07:38 | 2021-11-06 10:09 | 1 | 002:31 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | S21110600024 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 151 | 2021-11-06 | 151 | keep | 0 | Nov | 2021 | 0.00010285 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-11-06 08:05 | 2021-11-06 17:32 | 40 | 009:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21110600027 | New_Event |  |  | Include | Wildlife | 567 | 2021-11-06 | 22680 | keep | 0 | Nov | 2021 | 0.015447 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-11-06 08:08 | 2021-11-06 15:36 | 20 | 007:28 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE SECUNDARIO | S21110600010 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 448 | 2021-11-06 | 8960 | keep | 0 | Nov | 2021 | 0.0061026 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-11-06 08:14 | 2021-11-06 11:54 | 50 | 003:40 | P | DESGANCHE | 1 X 55 EN C/L SE REALIZO DESGANCHE | B21110600020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2021-11-06 | 11000 | keep | 0 | Nov | 2021 | 0.007492 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2021-11-06 08:18 | 2021-11-06 14:07 | 45 | 005:49 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21110500159 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 349 | 2021-11-06 | 15705 | keep | 0 | Nov | 2021 | 0.010697 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-11-06 08:25 | 2021-11-06 14:31 | 90 | 006:06 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C21110600002 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 366 | 2021-11-06 | 32940 | keep | 0 | Nov | 2021 | 0.022435 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-11-06 08:25 | 2021-11-06 10:59 | 10 | 002:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | C21110500172 | Partial_restoration |  |  | Include | Wildlife | 154 | 2021-11-06 | 1540 | keep | 0 | Nov | 2021 | 0.0010489 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-11-06 08:25 | 2021-11-06 08:49 | 1017 | 000:24 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV DE CIDRA POR AVERIA DE OVERHEAD ROTO EN LINEA 3800 CIDRA @ CAYEY TC | C21110600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 24 | 2021-11-06 | 24408 | keep | 0 | Nov | 2021 | 0.016624 | 0.00069267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1017
CAGUAS | 2021-11-06 08:25 | 2021-11-06 08:49 | 2770 | 000:24 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV DE CIDRA POR AVERIA DE OVERHEAD ROTO EN LINEA 3800 CIDRA @ CAYEY TC | C21110600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 24 | 2021-11-06 | 66480 | keep | 0 | Nov | 2021 | 0.045279 | 0.0018866 | Sustained | FALSE | FALSE | Not_TMED_Event | 2770
CAGUAS | 2021-11-06 08:25 | 2021-11-06 08:49 | 1854 | 000:24 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV DE CIDRA POR AVERIA DE OVERHEAD ROTO EN LINEA 3800 CIDRA @ CAYEY TC | C21110600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 24 | 2021-11-06 | 44496 | keep | 0 | Nov | 2021 | 0.030306 | 0.0012628 | Sustained | FALSE | FALSE | Not_TMED_Event | 1854
CAGUAS | 2021-11-06 08:25 | 2021-11-06 08:49 | 2859 | 000:24 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV DE CIDRA POR AVERIA DE OVERHEAD ROTO EN LINEA 3800 CIDRA @ CAYEY TC | C21110600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 24 | 2021-11-06 | 68616 | keep | 0 | Nov | 2021 | 0.046734 | 0.0019473 | Sustained | FALSE | FALSE | Not_TMED_Event | 2859
BARRANQUITAS | 2021-11-06 08:25 | 2021-11-07 09:40 | 40 | 025:15 | P | DESGANCHE | 1 X 65 EN C/L | C21110600186 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1515 | 2021-11-06 | 60600 | keep | 0 | Nov | 2021 | 0.041274 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-11-06 08:25 | 2021-11-06 14:44 | 125 | 006:19 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C21110600013 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 379 | 2021-11-06 | 47375 | keep | 0 | Nov | 2021 | 0.032267 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-11-06 08:26 | 2021-11-06 16:22 | 5 | 007:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | C21110500140 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 476 | 2021-11-06 | 2380 | keep | 0 | Nov | 2021 | 0.001621 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-11-06 08:26 | 2021-11-06 11:55 | 50 | 003:29 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21110600014 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 209 | 2021-11-06 | 10450 | keep | 0 | Nov | 2021 | 0.0071174 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-06 08:30 | 2021-11-06 09:46 | 50 | 001:16 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L CARGA DE 1909-09 POR 1907-03 | S21110600002 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 76 | 2021-11-06 | 3800 | keep | 0 | Nov | 2021 | 0.0025882 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-11-06 08:32 | 2021-11-07 10:44 | 60 | 026:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21110600055 | New_Event | Bad Weather | Include | Include | Weather | 1572 | 2021-11-06 | 94320 | keep | 0 | Nov | 2021 | 0.064241 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2021-11-06 08:55 | 2021-11-06 10:47 | 12 | 001:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REMPARAR PUENTES SECUNDARIOS | P21110500002 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 112 | 2021-11-06 | 1344 | keep | 0 | Nov | 2021 | 0.00091539 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-11-06 09:04 | 2021-11-06 10:35 | 125 | 001:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 Y 1 X 50 EN CORTES DE LINEAS CRUCE POR AVE | R21110600007 | Partial_restoration |  |  | Include | Wildlife | 91 | 2021-11-06 | 11375 | keep | 0 | Nov | 2021 | 0.0077475 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-11-06 09:15 | 2021-11-06 15:30 | 1 | 006:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | M21110600024 | New_Event | Bad Weather | Include | Include | Weather | 375 | 2021-11-06 | 375 | keep | 0 | Nov | 2021 | 0.00025541 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-06 09:41 | 2021-11-06 20:05 | 35 | 010:24 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21110600042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 624 | 2021-11-06 | 21840 | keep | 0 | Nov | 2021 | 0.014875 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2021-11-06 09:43 | 2021-11-06 09:52 | 60 | 000:09 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21110600030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2021-11-06 | 540 | keep | 0 | Nov | 2021 | 0.00036779 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-11-06 09:45 | 2021-11-06 11:45 | 65 | 002:00 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO Y CRUCETA | B21110500005 | New_Event | Defective Pole | Include | Include | Equipment | 120 | 2021-11-06 | 7800 | keep | 0 | Nov | 2021 | 0.0053125 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
ARECIBO | 2021-11-06 09:52 | 2021-11-06 09:53 | 2791 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A21110600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-06 | 2791 | keep | 0 | Nov | 2021 | 0.0019009 | 0.0019009 | Momentary | FALSE | FALSE | Not_TMED_Event | 2791
ARECIBO | 2021-11-06 09:52 | 2021-11-06 09:53 | 1464 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A21110600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-06 | 1464 | keep | 0 | Nov | 2021 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
ARECIBO | 2021-11-06 09:52 | 2021-11-06 09:53 | 759 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A21110600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-06 | 759 | keep | 0 | Nov | 2021 | 0.00051695 | 0.00051695 | Momentary | FALSE | FALSE | Not_TMED_Event | 759
ARECIBO | 2021-11-06 09:52 | 2021-11-06 09:53 | 1500 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A21110600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-06 | 1500 | keep | 0 | Nov | 2021 | 0.0010216 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
ARECIBO | 2021-11-06 09:52 | 2021-11-06 09:53 | 2132 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A21110600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-06 | 2132 | keep | 0 | Nov | 2021 | 0.0014521 | 0.0014521 | Momentary | FALSE | FALSE | Not_TMED_Event | 2132
ARECIBO | 2021-11-06 09:52 | 2021-11-06 09:53 | 2366 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A21110600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-06 | 2366 | keep | 0 | Nov | 2021 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
ARECIBO | 2021-11-06 09:52 | 2021-11-06 09:53 | 1976 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A21110600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-06 | 1976 | keep | 0 | Nov | 2021 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
ARECIBO | 2021-11-06 09:52 | 2021-11-06 09:53 | 3688 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A21110600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-06 | 3688 | keep | 0 | Nov | 2021 | 0.0025119 | 0.0025119 | Momentary | FALSE | FALSE | Not_TMED_Event | 3688
BAYAMON | 2021-11-06 09:52 | 2021-11-06 09:54 | 3070 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21110600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-06 | 6140 | keep | 0 | Nov | 2021 | 0.0041819 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2021-11-06 09:52 | 2021-11-06 09:54 | 2735 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21110600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-06 | 5470 | keep | 0 | Nov | 2021 | 0.0037256 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2021-11-06 09:52 | 2021-11-06 09:54 | 1070 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21110600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-06 | 2140 | keep | 0 | Nov | 2021 | 0.0014575 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2021-11-06 09:52 | 2021-11-06 09:54 | 1647 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21110600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-06 | 3294 | keep | 0 | Nov | 2021 | 0.0022435 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2021-11-06 09:52 | 2021-11-06 09:54 | 3295 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21110600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-06 | 6590 | keep | 0 | Nov | 2021 | 0.0044884 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2021-11-06 09:52 | 2021-11-06 09:54 | 1180 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21110600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-06 | 2360 | keep | 0 | Nov | 2021 | 0.0016074 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2021-11-06 09:52 | 2021-11-06 09:54 | 320 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21110600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-06 | 640 | keep | 0 | Nov | 2021 | 0.0004359 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2021-11-06 09:52 | 2021-11-06 09:54 | 2234 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21110600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-06 | 4468 | keep | 0 | Nov | 2021 | 0.0030431 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2021-11-06 09:54 | 2021-11-06 15:29 | 60 | 005:35 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21110600030 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 335 | 2021-11-06 | 20100 | keep | 0 | Nov | 2021 | 0.01369 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-06 10:03 | 2021-11-06 12:40 | 30 | 002:37 | P | NO SE REPORTO CAUSA | 1 X 140 EN RISER | S21110600043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 157 | 2021-11-06 | 4710 | keep | 0 | Nov | 2021 | 0.003208 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-11-06 10:15 | 2021-11-06 11:30 | 10 | 001:15 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | A21110600027 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 75 | 2021-11-06 | 750 | keep | 0 | Nov | 2021 | 0.00051082 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-06 10:15 | 2021-11-06 11:30 | 5 | 001:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21110600025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 75 | 2021-11-06 | 375 | keep | 0 | Nov | 2021 | 0.00025541 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-11-06 10:45 | 2021-11-06 12:08 | 1 | 001:23 | P | OTRAS CAUSAS | 1 X 25 EN BANCO DE TRANSFORMADOR EQUIPO DE MEDICION AVERIADO | C21110600156 | New_Event | Other Causes | Include | Include | Other | 83 | 2021-11-06 | 83 | keep | 0 | Nov | 2021 | 5.6531e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-06 11:14 | 2021-11-06 14:20 | 12 | 003:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21110500049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 186 | 2021-11-06 | 2232 | keep | 0 | Nov | 2021 | 0.0015202 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-11-06 11:17 | 2021-11-06 12:52 | 12 | 001:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21110600053 | New_Event | Secondary Wire Down | Include | Include | Equipment | 95 | 2021-11-06 | 1140 | keep | 0 | Nov | 2021 | 0.00077645 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-11-06 11:32 | 2021-11-06 18:00 | 100 | 006:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA VEHICULO CRUZO LINEAS | M21110600034 | New_Event |  |  | Include | Wildlife | 388 | 2021-11-06 | 38800 | keep | 0 | Nov | 2021 | 0.026427 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-06 11:33 | 2021-11-06 16:06 | 10 | 004:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21110600031 | New_Event | Bad Weather | Include | Include | Weather | 273 | 2021-11-06 | 2730 | keep | 0 | Nov | 2021 | 0.0018594 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-06 11:40 | 2021-11-06 12:36 | 5 | 000:56 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B21110600041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 56 | 2021-11-06 | 280 | keep | 0 | Nov | 2021 | 0.00019071 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-11-06 11:41 | 2021-11-06 12:18 | 15 | 000:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21110500081 | New_Event | Secondary Wire Down | Include | Include | Equipment | 37 | 2021-11-06 | 555 | keep | 0 | Nov | 2021 | 0.00037801 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-11-06 11:56 | 2021-11-06 11:57 | 1843 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21110600165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-06 | 1843 | keep | 0 | Nov | 2021 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
CAGUAS | 2021-11-06 12:09 | 2021-11-07 10:25 | 30 | 022:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN C/L BAJANTE PARARRAYO CRUZADO | C21110600169 | New_Event | Wire Down | Include | Include | Equipment | 1336 | 2021-11-06 | 40080 | keep | 0 | Nov | 2021 | 0.027298 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2021-11-06 12:18 | 2021-11-06 14:09 | 2216 | 001:51 | T | NO SE REPORTO CAUSA | DISPARO SE PATRULLO NO SE REPORTO CONDICION Y SE CERRO POR SCADA | B21110600044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 111 | 2021-11-06 | 245976 | keep | 0 | Nov | 2021 | 0.16753 | 0.0015093 | Sustained | FALSE | FALSE | Not_TMED_Event | 2216
SAN JUAN | 2021-11-06 12:37 | 2021-11-06 16:55 | 15 | 004:18 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5KVA POR 25KVA | S21110600059 | New_Event | Service Transformer Failure | Include | Include | Equipment | 258 | 2021-11-06 | 3870 | keep | 0 | Nov | 2021 | 0.0026358 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-11-06 12:47 | 2021-11-06 12:50 | 1 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21110600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-06 | 3 | keep | 0 | Nov | 2021 | 2.0433e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-11-06 12:55 | 2021-11-06 12:58 | 721 | 000:03 | T | DESGANCHE | SE ABRIO INTERRUPTOR PARA CERRAR AMARRE CON 7902-02 | M21110600040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-11-06 | 2163 | keep | 0 | Nov | 2021 | 0.0014732 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
PONCE | 2021-11-06 13:04 | 2021-11-06 14:25 | 10 | 001:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE TRANSFORMADOR PARA REMPLAZO DE HOT CLAMP | P21110600094 | New_Event | Wire Down | Include | Include | Equipment | 81 | 2021-11-06 | 810 | keep | 0 | Nov | 2021 | 0.00055169 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-11-06 13:04 | 2021-11-06 15:34 | 68 | 002:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21110600095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2021-11-06 | 10200 | keep | 0 | Nov | 2021 | 0.0069472 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
AGUADILLA | 2021-11-06 13:12 | 2021-11-06 13:13 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21110600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-06 | 3041 | keep | 0 | Nov | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
MAYAGÃœEZ | 2021-11-06 13:14 | 2021-11-07 13:25 | 300 | 024:11 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS DE ARBOL SOBRE LAS LINEAS | M21110600068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1451 | 2021-11-06 | 435300 | keep | 0 | Nov | 2021 | 0.29648 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-11-06 13:22 | 2021-11-07 09:30 | 68 | 020:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21110600045 | New_Event | Bad Weather | Include | Include | Weather | 1208 | 2021-11-06 | 82144 | keep | 0 | Nov | 2021 | 0.055948 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
ARECIBO | 2021-11-06 13:22 | 2021-11-06 17:26 | 20 | 004:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21110600036 | New_Event | Bad Weather | Include | Include | Weather | 244 | 2021-11-06 | 4880 | keep | 0 | Nov | 2021 | 0.0033237 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-11-06 13:34 | 2021-11-06 16:19 | 6 | 002:45 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR CARGA DEL 1720-07 POR EL 1709-01 | S21110600063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 165 | 2021-11-06 | 990 | keep | 0 | Nov | 2021 | 0.00067428 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2021-11-06 13:53 | 2021-11-06 13:54 | 390 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21110600047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-06 | 390 | keep | 0 | Nov | 2021 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
CANOVANAS | 2021-11-06 14:16 | 2021-11-06 17:18 | 45 | 003:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | R21110600096 | New_Event |  |  | Include | Wildlife | 182 | 2021-11-06 | 8190 | keep | 0 | Nov | 2021 | 0.0055782 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2021-11-06 14:19 | 2021-11-06 18:19 | 62 | 004:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 40 EN C/L SE REMPLAZARON 3 CAJAS PRIMARIAS | B21110500052 | New_Event | Cutout Failure | Include | Include | Equipment | 240 | 2021-11-06 | 14880 | keep | 0 | Nov | 2021 | 0.010135 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
CAGUAS | 2021-11-06 14:28 | 2021-11-07 15:54 | 1 | 025:26 | P | DESGANCHE | 2 X 50 EN C/L | C21110600177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1526 | 2021-11-06 | 1526 | keep | 0 | Nov | 2021 | 0.0010394 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-06 14:37 | 2021-11-06 20:17 | 314 | 005:40 | P | CABLE SOTERRADO AVERIADO | SE ABRIO EN SU-18 Y SE REPARO NEUTRAL SOTERRADO AVERIADO | S21110500085 | New_Event | UG Cable Fault | Include | Include | Equipment | 340 | 2021-11-06 | 106760 | keep | 0 | Nov | 2021 | 0.072714 | 0.00021386 | Sustained | FALSE | FALSE | Not_TMED_Event | 314
CAGUAS | 2021-11-06 14:52 | 2021-11-06 15:34 | 35 | 000:42 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL SOBRE LINEA Y RETEZAR LINEA PRIMARIA | C21110600111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 42 | 2021-11-06 | 1470 | keep | 0 | Nov | 2021 | 0.0010012 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2021-11-06 15:37 | 2021-11-06 16:44 | 10 | 001:07 | P | NO SE REPORTO CAUSA | 2 X 10 EN TRANSFORMADOR | B21110600066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 67 | 2021-11-06 | 670 | keep | 0 | Nov | 2021 | 0.00045633 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-06 15:52 | 2021-11-06 18:02 | 30 | 002:10 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA CARGA POR EL 1709-01 | B21110600072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2021-11-06 | 3900 | keep | 0 | Nov | 2021 | 0.0026563 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-11-06 16:03 | 2021-11-06 19:17 | 9 | 003:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA ABIERTA | R21110600099 | New_Event | Secondary Wire Down | Include | Include | Equipment | 194 | 2021-11-06 | 1746 | keep | 0 | Nov | 2021 | 0.0011892 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-11-06 16:10 | 2021-11-06 18:51 | 30 | 002:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN C/L SE REPARO NEUTRAL CRUZADO | B21110600074 | New_Event | Wire Down | Include | Include | Equipment | 161 | 2021-11-06 | 4830 | keep | 0 | Nov | 2021 | 0.0032897 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-11-06 16:18 | 2021-11-06 17:28 | 6 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA CARGA DE 1909-09 POR EL 1907-03 | S21110600058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2021-11-06 | 420 | keep | 0 | Nov | 2021 | 0.00028606 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2021-11-06 16:37 | 2021-11-07 12:38 | 1 | 020:01 | P | OTRAS CAUSAS | SE FIJÃ“ TRANSFORMADOR ZAFADO Y SE CERRÃ“ CAJA NO FUNDIÃ“ EL FUSIBLE | M21110600065 | New_Event | Other Causes | Include | Include | Other | 1201 | 2021-11-06 | 1201 | keep | 0 | Nov | 2021 | 0.000818 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-06 16:40 | 2021-11-06 17:34 | 35 | 000:54 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21110600076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 54 | 2021-11-06 | 1890 | keep | 0 | Nov | 2021 | 0.0012873 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2021-11-06 16:55 | 2021-11-06 17:24 | 20 | 000:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | A21110600041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 29 | 2021-11-06 | 580 | keep | 0 | Nov | 2021 | 0.00039504 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-11-06 17:35 | 2021-11-06 18:48 | 10 | 001:13 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 37.5 KVA X 37.5 KVA | A21110600048 | New_Event | Service Transformer Failure | Include | Include | Equipment | 73 | 2021-11-06 | 730 | keep | 0 | Nov | 2021 | 0.0004972 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-11-06 17:44 | 2021-11-07 15:20 | 150 | 021:36 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M21110600072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1296 | 2021-11-06 | 194400 | keep | 0 | Nov | 2021 | 0.1324 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2021-11-06 17:46 | 2021-11-07 12:22 | 2 | 018:36 | P | PARARRAYOS DEFECTUOSO | 1 X 8 EN TRANSFORMADOR SE REMPLAZO PARARRAYOS DEFECTUOSO | A21110600049 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1116 | 2021-11-06 | 2232 | keep | 0 | Nov | 2021 | 0.0015202 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2021-11-06 17:49 | 2021-11-07 10:25 | 7 | 016:36 | P | NO SE REPORTO CAUSA | 1 X 15 EN CORTE DE LINEA | B21110600082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 996 | 2021-11-06 | 6972 | keep | 0 | Nov | 2021 | 0.0047486 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2021-11-06 17:55 | 2021-11-08 10:38 | 20 | 040:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO C/L PARA REPARAR NEUTRAL PRIMARIO | C21110600184 | New_Event | Wire Down | Include | Include | Equipment | 2443 | 2021-11-06 | 48860 | keep | 0 | Nov | 2021 | 0.033278 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-11-06 18:44 | 2021-11-07 11:08 | 50 | 016:24 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHO Y CERRO PUENTE | C21110600186 | New_Event | Vegetation Contact | Include | Include | Vegetation | 984 | 2021-11-06 | 49200 | keep | 0 | Nov | 2021 | 0.03351 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-06 18:50 | 2021-11-07 10:40 | 40 | 015:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA CRUZADA | M21110600079 | New_Event | Wire Down | Include | Include | Equipment | 950 | 2021-11-06 | 38000 | keep | 0 | Nov | 2021 | 0.025882 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-11-06 19:19 | 2021-11-06 20:34 | 1 | 001:15 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21110600085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 75 | 2021-11-06 | 75 | keep | 0 | Nov | 2021 | 5.1082e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-11-06 20:08 | 2021-11-07 00:01 | 1 | 003:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO DE LINEA A CAJA DE CORTE DE LINEA | A21110600052 | New_Event | Wire Down | Include | Include | Equipment | 233 | 2021-11-06 | 233 | keep | 0 | Nov | 2021 | 0.0001587 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-11-06 20:59 | 2021-11-07 08:23 | 15 | 011:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21110600084 | New_Event | Bad Weather | Include | Include | Weather | 684 | 2021-11-06 | 10260 | keep | 0 | Nov | 2021 | 0.006988 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-11-06 21:45 | 2021-11-06 23:40 | 50 | 001:55 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21110600089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2021-11-06 | 5750 | keep | 0 | Nov | 2021 | 0.0039163 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-11-07 01:07 | 2021-11-07 01:08 | 5042 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR CULEBRA CRUZO CAJA DE TRANSFORMADOR | A21110700001 | New_Event |  |  | Include | Wildlife | 1 | 2021-11-07 | 5042 | keep | 0 | Nov | 2021 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
ARECIBO | 2021-11-07 01:08 | 2021-11-07 10:30 | 12 | 009:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR SE RETIRO CULEBRA SOBRE CAJA DE TRANSFORMADOR | A21110700006 | 1st_after_momentary |  |  | Include | Wildlife | 562 | 2021-11-07 | 6744 | keep | 0 | Nov | 2021 | 0.0045933 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-11-07 01:44 | 2021-11-07 03:43 | 1514 | 001:59 | T | DESGANCHE | DISPARO DE INTERRUPTOR. SE ABRIO MACHETES Y SE CERRO POR SCADA. SE CONTINUA PATRULLANDO 30% EN SERVICIO | B21110700001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2021-11-07 | 180166 | keep | 0 | Nov | 2021 | 0.12271 | 0.0010312 | Sustained | FALSE | FALSE | Not_TMED_Event | 1514
MAYAGÃœEZ | 2021-11-07 01:52 | 2021-11-07 10:29 | 100 | 008:37 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21110700004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 517 | 2021-11-07 | 51700 | keep | 0 | Nov | 2021 | 0.035213 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-11-07 02:39 | 2021-11-07 02:40 | 550 | 000:01 | P | DESGANCHE | RECIERRE DE INTERRUPTOR 1529-15.LLEVA EL 30% DE LA CARGA DEL 1346-02. | S21110700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-07 | 550 | keep | 0 | Nov | 2021 | 0.0003746 | 0.0003746 | Momentary | FALSE | FALSE | Not_TMED_Event | 550
BAYAMON | 2021-11-07 02:39 | 2021-11-07 02:40 | 1802 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR. ADEMAS LLEVA EL 30% DE LA CARGA DEL 1346-02. | S21110700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-07 | 1802 | keep | 0 | Nov | 2021 | 0.0012273 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
BAYAMON | 2021-11-07 02:40 | 2021-11-07 13:08 | 96 | 010:28 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | S21110700003 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 628 | 2021-11-07 | 60288 | keep | 0 | Nov | 2021 | 0.041062 | 6.5385e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 96
CAGUAS | 2021-11-07 02:41 | 2021-11-08 09:34 | 11 | 030:53 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | C21110700002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1853 | 2021-11-07 | 20383 | keep | 0 | Nov | 2021 | 0.013883 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2021-11-07 03:11 | 2021-11-07 03:12 | 1192 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR PUENTES PRIMARIOS ROTOS | M21110700005 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-07 | 1192 | keep | 0 | Nov | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2021-11-07 03:12 | 2021-11-07 11:45 | 500 | 008:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 140 EN CORTE DE LINEA SE REPARO PUENTES PRIMARIOS | M21110700027 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 513 | 2021-11-07 | 256500 | keep | 0 | Nov | 2021 | 0.1747 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2021-11-07 03:43 | 2021-11-07 09:58 | 1057 | 006:15 | P | DESGANCHE | SE REALIZO DESGANCHE Y AL REALIZAR OPERACIONES PARA NORMALIZAR DISPARO NUEVAMENTE | B21110700007 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 375 | 2021-11-07 | 396375 | keep | 0 | Nov | 2021 | 0.26997 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-11-07 05:25 | 2021-11-07 05:26 | 2280 | 000:01 | T | ESTRUCTURA AVERIADA | RECIERRE CARGAS POR EL 9902-03 | C21110700000 | New_Event | Defective Pole | Include | Include | Equipment | 1 | 2021-11-07 | 2280 | keep | 0 | Nov | 2021 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2021-11-07 05:25 | 2021-11-07 05:26 | 1617 | 000:01 | T | ESTRUCTURA AVERIADA | RECIERRE LLEVA LA CARGA DEL 9902-02 | C21110700000 | New_Event | Defective Pole | Include | Include | Equipment | 1 | 2021-11-07 | 1617 | keep | 0 | Nov | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
BARRANQUITAS | 2021-11-07 05:26 | 2021-11-07 14:44 | 197 | 009:18 | P | ESTRUCTURA AVERIADA | ABRIO C/L PARA REMPLAZAR POSTE PRIMARIO PARTIDO | C21110700023 | 1st_after_momentary | Defective Pole | Include | Include | Equipment | 558 | 2021-11-07 | 109926 | keep | 0 | Nov | 2021 | 0.07487 | 0.00013418 | Sustained | FALSE | FALSE | Not_TMED_Event | 197
SAN JUAN | 2021-11-07 05:35 | 2021-11-07 10:20 | 20 | 004:45 | P | NO SE REPORTO CAUSA | 1 X 25 EN SU-2A @ T-7 | R21110700002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 285 | 2021-11-07 | 5700 | keep | 0 | Nov | 2021 | 0.0038822 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-11-07 06:08 | 2021-11-07 10:43 | 50 | 004:35 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C21110700004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 275 | 2021-11-07 | 13750 | keep | 0 | Nov | 2021 | 0.0093651 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-11-07 07:05 | 2021-11-07 12:32 | 100 | 005:27 | P | DESGANCHE | 1 X 140 EN C/L | C21110700005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 327 | 2021-11-07 | 32700 | keep | 0 | Nov | 2021 | 0.022272 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2021-11-07 07:18 | 2021-11-07 07:19 | 625 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21110700003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-07 | 625 | keep | 0 | Nov | 2021 | 0.00042568 | 0.00042568 | Momentary | FALSE | FALSE | Not_TMED_Event | 625
ARECIBO | 2021-11-07 07:36 | 2021-11-07 07:37 | 2697 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21110700002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-07 | 2697 | keep | 0 | Nov | 2021 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
HUMACAO | 2021-11-07 08:09 | 2021-11-07 14:07 | 5 | 005:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN XMR MAL TIEMPO | C21110700007 | New_Event | Bad Weather | Include | Include | Weather | 358 | 2021-11-07 | 1790 | keep | 0 | Nov | 2021 | 0.0012192 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2021-11-07 08:10 | 2021-11-07 15:41 | 40 | 007:31 | P | DESGANCHE | 1 X 15 Y 1 X 20 EN C/L | R21110700005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 451 | 2021-11-07 | 18040 | keep | 0 | Nov | 2021 | 0.012287 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2021-11-07 08:18 | 2021-11-07 10:23 | 350 | 002:05 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P21110700002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 125 | 2021-11-07 | 43750 | keep | 0 | Nov | 2021 | 0.029798 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
BAYAMON | 2021-11-07 08:19 | 2021-11-07 10:23 | 50 | 002:04 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21110700013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 124 | 2021-11-07 | 6200 | keep | 0 | Nov | 2021 | 0.0042228 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-11-07 08:21 | 2021-11-07 08:22 | 1979 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21110700003 | New_Event |  |  | Include | Wildlife | 1 | 2021-11-07 | 1979 | keep | 0 | Nov | 2021 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2021-11-07 08:22 | 2021-11-07 16:19 | 65 | 007:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | P21110700040 | 1st_after_momentary |  |  | Include | Wildlife | 477 | 2021-11-07 | 31005 | keep | 0 | Nov | 2021 | 0.021117 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2021-11-07 08:24 | 2021-11-07 11:19 | 50 | 002:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L CRUCE POR AVE | C21110700010 | New_Event |  |  | Include | Wildlife | 175 | 2021-11-07 | 8750 | keep | 0 | Nov | 2021 | 0.0059596 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-11-07 08:42 | 2021-11-07 13:25 | 2524 | 004:43 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR SUBESTACION SIN RTU SE REEMPLAZO CAJA PRIMARIA QUEMADA EN SALIDA DEL INTERRUPTOR Y PARARRAYO AVERIADO | R21110700009 | New_Event | Cutout Failure | Include | Include | Equipment | 283 | 2021-11-07 | 714292 | keep | 0 | Nov | 2021 | 0.4865 | 0.0017191 | Sustained | FALSE | FALSE | Not_TMED_Event | 2524
BAYAMON | 2021-11-07 08:43 | 2021-11-07 11:24 | 80 | 002:41 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21110700009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 161 | 2021-11-07 | 12880 | keep | 0 | Nov | 2021 | 0.0087725 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2021-11-07 08:48 | 2021-11-07 11:03 | 9 | 002:15 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | A21110700005 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 135 | 2021-11-07 | 1215 | keep | 0 | Nov | 2021 | 0.00082753 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2021-11-07 08:56 | 2021-11-07 15:55 | 65 | 006:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | P21110700007 | New_Event |  |  | Include | Wildlife | 419 | 2021-11-07 | 27235 | keep | 0 | Nov | 2021 | 0.01855 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2021-11-07 09:07 | 2021-11-07 09:08 | 1342 | 000:01 | T | DESGANCHE | RECIERRE | C21110700018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-07 | 1342 | keep | 0 | Nov | 2021 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
CAGUAS | 2021-11-07 09:08 | 2021-11-07 15:50 | 50 | 006:42 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21110700019 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 402 | 2021-11-07 | 20100 | keep | 0 | Nov | 2021 | 0.01369 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2021-11-07 09:12 | 2021-11-07 10:54 | 12 | 001:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE DE PARARRAYO POR AVE | P21110700010 | New_Event |  |  | Include | Wildlife | 102 | 2021-11-07 | 1224 | keep | 0 | Nov | 2021 | 0.00083366 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-11-07 09:27 | 2021-11-07 14:57 | 12 | 005:30 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR DE 25KVA POR IGUAL CAPACIDAD | S21110700012 | New_Event | Service Transformer Failure | Include | Include | Equipment | 330 | 2021-11-07 | 3960 | keep | 0 | Nov | 2021 | 0.0026971 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2021-11-07 09:41 | 2021-11-07 09:42 | 661 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21110700012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-07 | 661 | keep | 0 | Nov | 2021 | 0.0004502 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
YAUCO | 2021-11-07 09:42 | 2021-11-07 13:52 | 30 | 004:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21110700016 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 250 | 2021-11-07 | 7500 | keep | 0 | Nov | 2021 | 0.0051082 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-11-07 09:58 | 2021-11-07 09:59 | 1514 | 000:01 | T | DESGANCHE | SE REALIZO DESGANCHE Y AL REALIZAR OPERACIONES PARA NORMALIZAR DISPARO NUEVAMENTE Y SE CERRO POR SCADA | B21110700007 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-07 | 1514 | keep | 0 | Nov | 2021 | 0.0010312 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-07 09:59 | 2021-11-07 11:20 | 1057 | 001:21 | P | DESGANCHE | SE REALIZO DESGANCHE Y AL REALIZAR OPERACIONES PARA NORMALIZAR DISPARO NUEVAMENTE | B21110700007 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 81 | 2021-11-07 | 85617 | keep | 0 | Nov | 2021 | 0.058313 | 0.00071992 | Sustained | FALSE | FALSE | Not_TMED_Event | 1057
YAUCO | 2021-11-07 10:26 | 2021-11-07 12:08 | 400 | 001:42 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P21110700014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 102 | 2021-11-07 | 40800 | keep | 0 | Nov | 2021 | 0.027789 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
CAGUAS | 2021-11-07 11:09 | 2021-11-07 17:10 | 40 | 006:01 | P | DESGANCHE | 1 X 40 EN C/L | C21110700020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 361 | 2021-11-07 | 14440 | keep | 0 | Nov | 2021 | 0.009835 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-07 11:20 | 2021-11-07 11:21 | 1514 | 000:01 | T | DESGANCHE | SE REALIZO DESGANCHE Y AL REALIZAR OPERACIONES PARA NORMALIZAR DISPARO NUEVAMENTE Y SE CERRO POR SCADA | B21110700007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-07 | 1514 | keep | 0 | Nov | 2021 | 0.0010312 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2021-11-07 11:21 | 2021-11-07 12:10 | 1057 | 000:49 | P | DESGANCHE | SE REALIZO DESGANCHE SE LLEVO LINEA ZAFADA A SU SITIO Y SE CERRO MACHETES | B21110700007 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 49 | 2021-11-07 | 51793 | keep | 0 | Nov | 2021 | 0.035276 | 0.00071992 | Sustained | FALSE | FALSE | Not_TMED_Event | 1057
CANOVANAS | 2021-11-07 11:22 | 2021-11-07 13:40 | 50 | 002:18 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA NO CAUSA | R21110700040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 138 | 2021-11-07 | 6900 | keep | 0 | Nov | 2021 | 0.0046996 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-11-07 11:33 | 2021-11-07 19:09 | 4 | 007:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR BARRAS DE PEDESTAL | C21110700024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 456 | 2021-11-07 | 1824 | keep | 0 | Nov | 2021 | 0.0012423 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-11-07 11:34 | 2021-11-07 14:48 | 12 | 003:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BARRA EN PEDESTAL | S21110700021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 194 | 2021-11-07 | 2328 | keep | 0 | Nov | 2021 | 0.0015856 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2021-11-07 11:49 | 2021-11-07 12:56 | 200 | 001:07 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21110700011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2021-11-07 | 13400 | keep | 0 | Nov | 2021 | 0.0091267 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
GUAYAMA | 2021-11-07 12:17 | 2021-11-07 14:20 | 15 | 002:03 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE REPORTO LA CAUSA | P21110700023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 123 | 2021-11-07 | 1845 | keep | 0 | Nov | 2021 | 0.0012566 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-11-07 12:22 | 2021-11-07 16:05 | 1 | 003:43 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA POR DESGANCHE | A21110700015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 223 | 2021-11-07 | 223 | keep | 0 | Nov | 2021 | 0.00015188 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-11-07 12:35 | 2021-11-07 12:53 | 12 | 000:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A21110600013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 18 | 2021-11-07 | 216 | keep | 0 | Nov | 2021 | 0.00014712 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-11-07 12:46 | 2021-11-07 13:22 | 12 | 000:36 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S21110700025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 36 | 2021-11-07 | 432 | keep | 0 | Nov | 2021 | 0.00029423 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-11-07 12:53 | 2021-11-07 12:54 | 51 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR 7902-03 EL CUAL LLEVA LA CARGA DEL 7902-02 NO SE REPORTO CAUSA | M21110700065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-07 | 51 | keep | 0 | Nov | 2021 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2021-11-07 12:53 | 2021-11-07 12:54 | 721 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 7902-02 | M21110700065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-07 | 721 | keep | 0 | Nov | 2021 | 0.00049107 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
MAYAGÃœEZ | 2021-11-07 12:55 | 2021-11-07 12:57 | 51 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR 7902-03 EL CUAL LLEVA LA CARGA DEL 7902-02 NO SE REPORTÃ“ CAUSA SE CERRÃ“ POR SCADA | M21110700066 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-07 | 102 | keep | 0 | Nov | 2021 | 6.9472e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2021-11-07 12:55 | 2021-11-07 12:57 | 721 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 7902-02 SE CERRÃ“ POR SCADA | M21110700066 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-07 | 1442 | keep | 0 | Nov | 2021 | 0.00098214 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
CANOVANAS | 2021-11-07 13:14 | 2021-11-07 15:17 | 45 | 002:03 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/ L NO CAUSA | R21110700056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 123 | 2021-11-07 | 5535 | keep | 0 | Nov | 2021 | 0.0037699 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
GUAYAMA | 2021-11-07 13:21 | 2021-11-07 17:33 | 464 | 004:12 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR POR AVERIA SOTERRADA EN TRONCAL DEL ALIMENTADOR SE TRANSFIERE EL 70% DE LA CARGA AL 4003-02 | P21110700027 | New_Event | UG Cable Fault | Include | Include | Equipment | 252 | 2021-11-07 | 116928 | keep | 0 | Nov | 2021 | 0.079639 | 0.00031603 | Sustained | FALSE | FALSE | Not_TMED_Event | 464
SAN JUAN | 2021-11-07 13:25 | 2021-11-07 13:28 | 1500 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO NO RECERRO 1336-08 SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA CARGA 1336-9 Y 30% 1204-4 | S21110700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-07 | 4500 | keep | 0 | Nov | 2021 | 0.0030649 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2021-11-07 13:25 | 2021-11-07 13:28 | 5290 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA CARGA 1336-9 Y 30% 1204-4 | S21110700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-07 | 15870 | keep | 0 | Nov | 2021 | 0.010809 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2021-11-07 13:25 | 2021-11-07 13:28 | 207 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO 1336-8 SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA CARGA 1336-9 Y 30% 1204-4 | S21110700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-07 | 621 | keep | 0 | Nov | 2021 | 0.00042296 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
CAGUAS | 2021-11-07 13:38 | 2021-11-07 15:01 | 7 | 001:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21110500160 | New_Event | Secondary Wire Down | Include | Include | Equipment | 83 | 2021-11-07 | 581 | keep | 0 | Nov | 2021 | 0.00039572 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2021-11-07 14:24 | 2021-11-07 14:25 | 1397 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21110700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-07 | 1397 | keep | 0 | Nov | 2021 | 0.00095149 | 0.00095149 | Momentary | FALSE | FALSE | Not_TMED_Event | 1397
VEGA BAJA | 2021-11-07 14:31 | 2021-11-07 15:40 | 180 | 001:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES PARA LLEVAR LINEA SAFADA A SU SITIO | B21110700069 | New_Event | Wire Down | Include | Include | Equipment | 69 | 2021-11-07 | 12420 | keep | 0 | Nov | 2021 | 0.0084592 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
BARRANQUITAS | 2021-11-07 14:35 | 2021-11-07 16:38 | 45 | 002:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE POR GLOBO | C21110700032 | New_Event |  |  | Include | Wildlife | 123 | 2021-11-07 | 5535 | keep | 0 | Nov | 2021 | 0.0037699 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2021-11-07 14:54 | 2021-11-07 14:55 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21110700063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-07 | 3046 | keep | 0 | Nov | 2021 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2021-11-07 14:55 | 2021-11-07 17:42 | 200 | 002:47 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 80 EN C/L NO CAUSA | R21110700064 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 167 | 2021-11-07 | 33400 | keep | 0 | Nov | 2021 | 0.022749 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-11-07 15:14 | 2021-11-07 15:15 | 320 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | B21110700025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-07 | 320 | keep | 0 | Nov | 2021 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
AGUADILLA | 2021-11-07 15:20 | 2021-11-07 18:38 | 10 | 003:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CAJAS DE TRANSFORMADOR PARA RETEZAR LINEA PRIMARIA | M21110700077 | New_Event | Wire Down | Include | Include | Equipment | 198 | 2021-11-07 | 1980 | keep | 0 | Nov | 2021 | 0.0013486 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-11-07 15:35 | 2021-11-07 15:48 | 15 | 000:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFDORMADOR PARA REPARAR BAJANTE SECUNDARIO | M21110700073 | New_Event | Secondary Wire Down | Include | Include | Equipment | 13 | 2021-11-07 | 195 | keep | 0 | Nov | 2021 | 0.00013281 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-11-07 15:45 | 2021-11-07 15:46 | 551 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21110700034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-07 | 551 | keep | 0 | Nov | 2021 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
SAN JUAN | 2021-11-07 16:23 | 2021-11-08 09:55 | 5 | 017:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | R21110700068 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1052 | 2021-11-07 | 5260 | keep | 0 | Nov | 2021 | 0.0035826 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2021-11-07 16:40 | 2021-11-07 19:06 | 7 | 002:26 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE | R21110700070 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 146 | 2021-11-07 | 1022 | keep | 0 | Nov | 2021 | 0.00069608 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2021-11-07 16:49 | 2021-11-07 18:03 | 1131 | 001:14 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO SE SECCIONALIZO CONDUCTOR EN EL SUELO | C21110700000 | New_Event | Wire Down | Include | Include | Equipment | 74 | 2021-11-07 | 83694 | keep | 0 | Nov | 2021 | 0.057004 | 0.00077032 | Sustained | FALSE | FALSE | Not_TMED_Event | 1131
PONCE | 2021-11-07 16:51 | 2021-11-08 10:37 | 100 | 017:46 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P21110700043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1066 | 2021-11-07 | 106600 | keep | 0 | Nov | 2021 | 0.072605 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2021-11-07 17:14 | 2021-11-07 18:18 | 10 | 001:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES SECUNDARIAS | A21110700023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 64 | 2021-11-07 | 640 | keep | 0 | Nov | 2021 | 0.0004359 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2021-11-07 17:33 | 2021-11-07 17:42 | 4279 | 000:09 | T | OTRAS CAUSAS | DISPARO DE INTERRUPTOR AL TRANSFERIRLE PARTE DE LA CARGA DEL 4006-05 | P21110700046 | New_Event | Other Causes | Include | Include | Other | 9 | 2021-11-07 | 38511 | keep | 0 | Nov | 2021 | 0.02623 | 0.0029144 | Sustained | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2021-11-07 17:33 | 2021-11-07 20:25 | 138 | 002:52 | P | CABLE SOTERRADO AVERIADO | AVERIA SOTERRADA EN TRONCAL DEL ALIMENTADOR SE CONSTRUYO PROVICIONAL AEREO Y SE TRANSFIRIO LA CARGA AL 4006-04 | P21110700052 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 172 | 2021-11-07 | 23736 | keep | 0 | Nov | 2021 | 0.016166 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-11-07 17:44 | 2021-11-07 19:14 | 250 | 001:30 | P | SOBRECARGA | 2 X 200 EN CONVERTIDOR POR SOBRECARGA | A21110700026 | New_Event | Trip Due To Overload | Include | Include | Other | 90 | 2021-11-07 | 22500 | keep | 0 | Nov | 2021 | 0.015325 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
AGUADILLA | 2021-11-07 17:50 | 2021-11-07 18:14 | 6 | 000:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONECTORES SECUNDARIOS | M21110700081 | New_Event | Secondary Wire Down | Include | Include | Equipment | 24 | 2021-11-07 | 144 | keep | 0 | Nov | 2021 | 9.8078e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-11-07 17:53 | 2021-11-08 11:14 | 1 | 017:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE DESGANCHO Y REEMPLAZARON CAJA PRIMARIA EN TRANSFORMADOR | C21110700045 | New_Event | Cutout Failure | Include | Include | Equipment | 1041 | 2021-11-07 | 1041 | keep | 0 | Nov | 2021 | 0.00070902 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-07 17:55 | 2021-11-07 18:42 | 8 | 000:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BARRA PEDESTAL SECUNDARIO | S21110700037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 47 | 2021-11-07 | 376 | keep | 0 | Nov | 2021 | 0.00025609 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2021-11-07 18:03 | 2021-11-07 21:36 | 300 | 003:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO SE SECCIONALIZO CONDUCTOR EN EL SUELO | C21110700000 | Partial_restoration | Wire Down | Include | Include | Equipment | 213 | 2021-11-07 | 63900 | keep | 0 | Nov | 2021 | 0.043522 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-07 18:33 | 2021-11-07 21:56 | 3 | 003:23 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | S21110700043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 203 | 2021-11-07 | 609 | keep | 0 | Nov | 2021 | 0.00041479 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2021-11-07 18:34 | 2021-11-07 20:41 | 50 | 002:07 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | A21110700037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2021-11-07 | 6350 | keep | 0 | Nov | 2021 | 0.004325 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2021-11-07 18:36 | 2021-11-08 07:42 | 20 | 013:06 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | R21110700072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 786 | 2021-11-07 | 15720 | keep | 0 | Nov | 2021 | 0.010707 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-11-07 18:40 | 2021-11-07 21:12 | 15 | 002:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR SE REMPLAZA CAJA | S21110700044 | New_Event | Cutout Failure | Include | Include | Equipment | 152 | 2021-11-07 | 2280 | keep | 0 | Nov | 2021 | 0.0015529 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2021-11-07 19:50 | 2021-11-08 09:45 | 40 | 013:55 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER NO CAUSA | R21110700073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 835 | 2021-11-07 | 33400 | keep | 0 | Nov | 2021 | 0.022749 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2021-11-07 19:51 | 2021-11-08 11:30 | 80 | 015:39 | P | DESGANCHE | 1 X 30 Y 1 X 20 EN C/L DESGANCHO Y RETEZO LINEAS | R21110700074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 939 | 2021-11-07 | 75120 | keep | 0 | Nov | 2021 | 0.051164 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2021-11-07 19:55 | 2021-11-07 21:36 | 50 | 001:41 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | A21110700048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2021-11-07 | 5050 | keep | 0 | Nov | 2021 | 0.0034395 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-11-07 19:58 | 2021-11-07 22:40 | 40 | 002:42 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | A21110700049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2021-11-07 | 6480 | keep | 0 | Nov | 2021 | 0.0044135 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2021-11-07 20:25 | 2021-11-08 15:15 | 1 | 018:50 | P | CABLE SOTERRADO AVERIADO | AVERIA SOTERRADA EN MH-04 | P21110700056 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1130 | 2021-11-07 | 1130 | keep | 0 | Nov | 2021 | 0.00076964 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-11-07 21:18 | 2021-11-08 00:21 | 200 | 003:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO | M21110700097 | New_Event | Wire Down | Include | Include | Equipment | 183 | 2021-11-07 | 36600 | keep | 0 | Nov | 2021 | 0.024928 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2021-11-07 21:36 | 2021-11-07 21:43 | 1131 | 000:07 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y ABRIO BREAKER PARA CERRAR MACHETES | C21110700000 | Additional_clients | Wire Down | Include | Include | Equipment | 7 | 2021-11-07 | 7917 | keep | 0 | Nov | 2021 | 0.0053922 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-11-07 21:57 | 2021-11-08 09:20 | 20 | 011:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21110700105 | New_Event | Bad Weather | Include | Include | Weather | 683 | 2021-11-07 | 13660 | keep | 0 | Nov | 2021 | 0.0093038 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-11-07 22:18 | 2021-11-07 22:56 | 10 | 000:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21110700031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 38 | 2021-11-07 | 380 | keep | 0 | Nov | 2021 | 0.00025882 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-11-07 23:19 | 2021-11-08 09:22 | 100 | 010:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 Y 1 X 40 EN C/L CRUCE POR AVE | R21110700078 | New_Event |  |  | Include | Wildlife | 603 | 2021-11-07 | 60300 | keep | 0 | Nov | 2021 | 0.04107 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-11-07 23:23 | 2021-11-08 11:10 | 6 | 011:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21110700032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 707 | 2021-11-07 | 4242 | keep | 0 | Nov | 2021 | 0.0028892 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2021-11-08 00:15 | 2021-11-08 19:33 | 53 | 019:18 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVISIONAL HACIA T-71 POR TRAMO SOTERRADO AVERIADO | B21110800001 | New_Event | UG Cable Fault | Include | Include | Equipment | 1158 | 2021-11-08 | 61374 | keep | 0 | Nov | 2021 | 0.041802 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
YAUCO | 2021-11-08 01:30 | 2021-11-08 01:31 | 661 | 000:01 | T | NO SE REPORTO CAUSA | RECERRE | P211108000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-08 | 661 | keep | 0 | Nov | 2021 | 0.0004502 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
ARECIBO | 2021-11-08 03:29 | 2021-11-08 11:10 | 200 | 007:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21110800001 | New_Event | Bad Weather | Include | Include | Weather | 461 | 2021-11-08 | 92200 | keep | 0 | Nov | 2021 | 0.062797 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-11-08 06:00 | 2021-11-08 11:17 | 4 | 005:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BARRAS DE PEDESTAL | R21110800001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 317 | 2021-11-08 | 1268 | keep | 0 | Nov | 2021 | 0.00086363 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2021-11-08 06:25 | 2021-11-08 13:56 | 3 | 007:31 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO | C21110800002 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 451 | 2021-11-08 | 1353 | keep | 0 | Nov | 2021 | 0.00092152 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2021-11-08 06:37 | 2021-11-08 12:33 | 1 | 005:56 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO AISLADOR | C21110800003 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 356 | 2021-11-08 | 356 | keep | 0 | Nov | 2021 | 0.00024247 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-11-08 06:55 | 2021-11-08 10:00 | 150 | 003:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21110800010 | New_Event | Bad Weather | Include | Include | Weather | 185 | 2021-11-08 | 27750 | keep | 0 | Nov | 2021 | 0.0189 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-11-08 07:09 | 2021-11-08 13:00 | 60 | 005:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA MAL TIEMPO | M21110800008 | New_Event | Bad Weather | Include | Include | Weather | 351 | 2021-11-08 | 21060 | keep | 0 | Nov | 2021 | 0.014344 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-11-08 07:37 | 2021-11-08 10:00 | 10 | 002:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21110800013 | New_Event | Bad Weather | Include | Include | Weather | 143 | 2021-11-08 | 1430 | keep | 0 | Nov | 2021 | 0.00097397 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-11-08 07:38 | 2021-11-08 10:07 | 5 | 002:29 | P | NO SE REPORTO CAUSA | 1 X 10 RM XMR NO CAUSA | R21110800008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 149 | 2021-11-08 | 745 | keep | 0 | Nov | 2021 | 0.00050742 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-11-08 07:39 | 2021-11-08 09:12 | 1979 | 001:33 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE SUBESTACION | P21110800011 | New_Event |  |  | Include | Wildlife | 93 | 2021-11-08 | 184047 | keep | 0 | Nov | 2021 | 0.12535 | 0.0013479 | Sustained | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2021-11-08 07:39 | 2021-11-08 08:45 | 3114 | 001:06 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE SUBESTACION | P21110800010 | New_Event |  |  | Include | Wildlife | 66 | 2021-11-08 | 205524 | keep | 0 | Nov | 2021 | 0.13998 | 0.0021209 | Sustained | FALSE | FALSE | Not_TMED_Event | 3114
PONCE | 2021-11-08 07:39 | 2021-11-08 10:08 | 5069 | 002:29 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE SUBESTACION NO SE REPORTO LA CAUSA | P21110800027 | New_Event |  |  | Include | Wildlife | 149 | 2021-11-08 | 755281 | keep | 0 | Nov | 2021 | 0.51442 | 0.0034525 | Sustained | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2021-11-08 07:39 | 2021-11-08 08:43 | 2696 | 001:04 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE SUBESTACION | P21110800010 | New_Event |  |  | Include | Wildlife | 64 | 2021-11-08 | 172544 | keep | 0 | Nov | 2021 | 0.11752 | 0.0018362 | Sustained | FALSE | FALSE | Not_TMED_Event | 2696
PONCE | 2021-11-08 07:39 | 2021-11-08 08:43 | 5063 | 001:04 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE SUBESTACION | P21110800010 | New_Event |  |  | Include | Wildlife | 64 | 2021-11-08 | 324032 | keep | 0 | Nov | 2021 | 0.2207 | 0.0034484 | Sustained | FALSE | FALSE | Not_TMED_Event | 5063
ARECIBO | 2021-11-08 07:54 | 2021-11-08 12:25 | 1 | 004:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA ROTA | A21110800017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 271 | 2021-11-08 | 271 | keep | 0 | Nov | 2021 | 0.00018458 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-11-08 08:03 | 2021-11-08 15:18 | 117 | 007:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 Y 1 X 65 EN CORTES DE LINEA CRUCE POR AVE | C21110800006 | New_Event |  |  | Include | Wildlife | 435 | 2021-11-08 | 50895 | keep | 0 | Nov | 2021 | 0.034664 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
CAGUAS | 2021-11-08 08:09 | 2021-11-08 20:12 | 86 | 012:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO AISLADOR ROTO | C21110800008 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 723 | 2021-11-08 | 62178 | keep | 0 | Nov | 2021 | 0.042349 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
GUAYAMA | 2021-11-08 08:11 | 2021-11-08 10:12 | 50 | 002:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | P21110800044 | New_Event |  |  | Include | Wildlife | 121 | 2021-11-08 | 6050 | keep | 0 | Nov | 2021 | 0.0041206 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2021-11-08 08:28 | 2021-11-08 14:50 | 100 | 006:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | A21110800020 | New_Event | Wire Down | Include | Include | Equipment | 382 | 2021-11-08 | 38200 | keep | 0 | Nov | 2021 | 0.026018 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2021-11-08 08:32 | 2021-11-08 09:13 | 1 | 000:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | P21110800060 | New_Event | Bad Weather | Include | Include | Weather | 41 | 2021-11-08 | 41 | keep | 0 | Nov | 2021 | 2.7925e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-11-08 08:32 | 2021-11-08 14:38 | 1 | 006:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | A21110800022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 366 | 2021-11-08 | 366 | keep | 0 | Nov | 2021 | 0.00024928 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-11-08 08:38 | 2021-11-08 12:09 | 40 | 003:31 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO CAUSA | R21110800007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 211 | 2021-11-08 | 8440 | keep | 0 | Nov | 2021 | 0.0057484 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2021-11-08 08:43 | 2021-11-08 08:47 | 100 | 000:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO FASE | P21110800002 | Partial_restoration |  |  | Include | Wildlife | 4 | 2021-11-08 | 400 | keep | 0 | Nov | 2021 | 0.00027244 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-11-08 08:47 | 2021-11-08 11:15 | 100 | 002:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO FASE | P21110800002 | 1st_after_momentary |  |  | Include | Wildlife | 148 | 2021-11-08 | 14800 | keep | 0 | Nov | 2021 | 0.01008 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-08 08:49 | 2021-11-08 15:05 | 1 | 006:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21110800024 | New_Event | Bad Weather | Include | Include | Weather | 376 | 2021-11-08 | 376 | keep | 0 | Nov | 2021 | 0.00025609 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-11-08 08:50 | 2021-11-08 10:36 | 25 | 001:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO NEUTRAL | B21110800011 | New_Event | Wire Down | Include | Include | Equipment | 106 | 2021-11-08 | 2650 | keep | 0 | Nov | 2021 | 0.0018049 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-11-08 09:00 | 2021-11-08 17:43 | 6 | 008:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21110800013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 523 | 2021-11-08 | 3138 | keep | 0 | Nov | 2021 | 0.0021373 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-11-08 09:13 | 2021-11-09 15:02 | 8 | 029:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REMPLAZO CONECTORES EN BAJANTE DEL TRANSFORMADOR | S21110800013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1789 | 2021-11-08 | 14312 | keep | 0 | Nov | 2021 | 0.0097478 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-11-08 09:15 | 2021-11-08 12:16 | 7 | 003:01 | P | ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR Y SE REMPLAZO POSTE PARTIDO | B21110800015 | New_Event | Defective Pole | Include | Include | Equipment | 181 | 2021-11-08 | 1267 | keep | 0 | Nov | 2021 | 0.00086295 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2021-11-08 09:29 | 2021-11-08 10:05 | 3 | 000:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | M21110800016 | New_Event | Cutout Failure | Include | Include | Equipment | 36 | 2021-11-08 | 108 | keep | 0 | Nov | 2021 | 7.3558e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2021-11-08 09:30 | 2021-11-08 10:10 | 22 | 000:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 75 KVA POR UNO DE 75 KVA | A21110800027 | New_Event | Service Transformer Failure | Include | Include | Equipment | 40 | 2021-11-08 | 880 | keep | 0 | Nov | 2021 | 0.00059936 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
AGUADILLA | 2021-11-08 09:42 | 2021-11-08 17:10 | 15 | 007:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA PARTIDA | M21110800017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 448 | 2021-11-08 | 6720 | keep | 0 | Nov | 2021 | 0.004577 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2021-11-08 09:45 | 2021-11-08 12:50 | 4 | 003:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | A21110800032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 185 | 2021-11-08 | 740 | keep | 0 | Nov | 2021 | 0.00050401 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2021-11-08 09:50 | 2021-11-08 10:25 | 10 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES DE LINEAS SECUNDARIAS | A21110800057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2021-11-08 | 350 | keep | 0 | Nov | 2021 | 0.00023838 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-11-08 09:56 | 2021-11-08 18:13 | 1 | 008:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR SECUNDARIA | C21110800026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 497 | 2021-11-08 | 497 | keep | 0 | Nov | 2021 | 0.0003385 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-11-08 10:00 | 2021-11-08 15:55 | 2 | 005:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA RELOCALIZAR LINEA A POSTE NUEVO | A21110800037 | New_Event | Wire Down | Include | Include | Equipment | 355 | 2021-11-08 | 710 | keep | 0 | Nov | 2021 | 0.00048358 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
UTUADO | 2021-11-08 10:00 | 2021-11-08 12:40 | 5 | 002:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21110800036 | New_Event | Bad Weather | Include | Include | Weather | 160 | 2021-11-08 | 800 | keep | 0 | Nov | 2021 | 0.00054488 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-11-08 10:11 | 2021-11-08 10:12 | 2067 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE INTERRUPTOR | M21110800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-08 | 2067 | keep | 0 | Nov | 2021 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
MAYAGÃœEZ | 2021-11-08 10:12 | 2021-11-08 15:35 | 200 | 005:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA | M21110800030 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 323 | 2021-11-08 | 64600 | keep | 0 | Nov | 2021 | 0.043999 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-11-08 10:13 | 2021-11-08 16:23 | 150 | 006:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA RAMAL | B21110800021 | New_Event | Wire Down | Include | Include | Equipment | 370 | 2021-11-08 | 55500 | keep | 0 | Nov | 2021 | 0.037801 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2021-11-08 10:16 | 2021-11-08 12:42 | 1 | 002:26 | P | NO SE REPORTO CAUSA | 3 X 25 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | C21110800027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2021-11-08 | 146 | keep | 0 | Nov | 2021 | 9.944e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-08 10:29 | 2021-11-08 15:09 | 1 | 004:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 20 EN TRANSFORMADOR Y SE REPARO SECUNDARIA | S21110800022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 280 | 2021-11-08 | 280 | keep | 0 | Nov | 2021 | 0.00019071 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2021-11-08 10:29 | 2021-11-08 13:30 | 25 | 003:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA AVE CRUZO FASE | P21110800083 | New_Event |  |  | Include | Wildlife | 181 | 2021-11-08 | 4525 | keep | 0 | Nov | 2021 | 0.003082 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-11-08 10:31 | 2021-11-08 14:26 | 25 | 003:55 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S21110800023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 235 | 2021-11-08 | 5875 | keep | 0 | Nov | 2021 | 0.0040014 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2021-11-08 10:31 | 2021-11-08 10:32 | 4702 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21110800024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-08 | 4702 | keep | 0 | Nov | 2021 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
BARRANQUITAS | 2021-11-08 10:33 | 2021-11-08 13:55 | 8 | 003:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR SECUNDARIA | C21110800025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 202 | 2021-11-08 | 1616 | keep | 0 | Nov | 2021 | 0.0011007 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-11-08 10:38 | 2021-11-08 11:09 | 10 | 000:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR NEUTRAL SECUNDARIO | C21110600190 | New_Event | Secondary Wire Down | Include | Include | Equipment | 31 | 2021-11-08 | 310 | keep | 0 | Nov | 2021 | 0.00021114 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-11-08 10:53 | 2021-11-08 13:01 | 6 | 002:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA RETIRAR CARGA Y LEVANTAR NEUTRAL PRIMARIO | C21110800033 | New_Event | Wire Down | Include | Include | Equipment | 128 | 2021-11-08 | 768 | keep | 0 | Nov | 2021 | 0.00052308 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-11-08 10:54 | 2021-11-08 18:25 | 6 | 007:31 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA X 50 KVA | A21110800043 | New_Event | Service Transformer Failure | Include | Include | Equipment | 451 | 2021-11-08 | 2706 | keep | 0 | Nov | 2021 | 0.001843 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2021-11-08 10:55 | 2021-11-08 13:20 | 3 | 002:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA POR 25 KVA | M21110800033 | New_Event | Service Transformer Failure | Include | Include | Equipment | 145 | 2021-11-08 | 435 | keep | 0 | Nov | 2021 | 0.00029628 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2021-11-08 10:59 | 2021-11-08 11:00 | 3718 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE NO SE REMPLAZO CAJA SE DEJO PARA LUEGO | P21110800085 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-11-08 | 3718 | keep | 0 | Nov | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
PONCE | 2021-11-08 11:00 | 2021-11-08 12:47 | 50 | 001:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CERRO CAJA PRIMARIA EN CORTE DE LINEA | P21110800087 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 107 | 2021-11-08 | 5350 | keep | 0 | Nov | 2021 | 0.0036439 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-11-08 11:00 | 2021-11-08 16:38 | 9 | 005:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | A21110800041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 338 | 2021-11-08 | 3042 | keep | 0 | Nov | 2021 | 0.0020719 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2021-11-08 11:09 | 2021-11-08 15:06 | 242 | 003:57 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | C21110800035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 237 | 2021-11-08 | 57354 | keep | 0 | Nov | 2021 | 0.039064 | 0.00016483 | Sustained | FALSE | FALSE | Not_TMED_Event | 242
CAGUAS | 2021-11-08 11:09 | 2021-11-10 19:18 | 20 | 056:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO C/L PARA REPARAR NEUTRAL PRIMARIO | C21110600184 | Partial_restoration | Wire Down | Include | Include | Equipment | 3369 | 2021-11-08 | 67380 | keep | 0 | Nov | 2021 | 0.045892 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-11-08 11:14 | 2021-11-08 15:29 | 12 | 004:15 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE SECUNDARIO PARTIDO 35 PIES DE METAL | M21110800037 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 255 | 2021-11-08 | 3060 | keep | 0 | Nov | 2021 | 0.0020842 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-11-08 11:18 | 2021-11-08 14:08 | 4 | 002:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BARRAS Y PEDESTAL | R21110800015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 170 | 2021-11-08 | 680 | keep | 0 | Nov | 2021 | 0.00046314 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-11-08 11:28 | 2021-11-08 18:52 | 45 | 007:24 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR 25KVA | B21110800014 | New_Event | Service Transformer Failure | Include | Include | Equipment | 444 | 2021-11-08 | 19980 | keep | 0 | Nov | 2021 | 0.013608 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2021-11-08 11:45 | 2021-11-08 16:26 | 16 | 004:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES SECUNDARIAS | M21110800042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 281 | 2021-11-08 | 4496 | keep | 0 | Nov | 2021 | 0.0030622 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
AGUADILLA | 2021-11-08 11:57 | 2021-11-08 13:00 | 20 | 001:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA PARTIDA | M21110800044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 63 | 2021-11-08 | 1260 | keep | 0 | Nov | 2021 | 0.00085818 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-11-08 12:13 | 2021-11-08 12:54 | 7 | 000:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21110800009 | New_Event | Secondary Wire Down | Include | Include | Equipment | 41 | 2021-11-08 | 287 | keep | 0 | Nov | 2021 | 0.00019547 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-11-08 12:15 | 2021-11-08 13:10 | 6 | 000:55 | P | OTRAS CAUSAS | 1 X 40 EN CORTE DE LINEA DESGASTE DEL FUSIBLE | A21110800058 | New_Event | Other Causes | Include | Include | Other | 55 | 2021-11-08 | 330 | keep | 0 | Nov | 2021 | 0.00022476 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2021-11-08 12:16 | 2021-11-08 16:01 | 100 | 003:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L Y 1 X 80 EN RISER REMPLAZO CAJA AVERIADA | R21110800017 | New_Event | Cutout Failure | Include | Include | Equipment | 225 | 2021-11-08 | 22500 | keep | 0 | Nov | 2021 | 0.015325 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-11-08 12:29 | 2021-11-08 12:59 | 1 | 000:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR CHANGO | C21110800039 | New_Event |  |  | Include | Wildlife | 30 | 2021-11-08 | 30 | keep | 0 | Nov | 2021 | 2.0433e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-11-08 12:30 | 2021-11-09 12:31 | 10 | 024:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | ABRIO XMR PARA REPARAR SECUNDARIA AVERIADA POR PERSONAL DE AAA | C21110800040 | New_Event |  |  | Include | Wildlife | 1441 | 2021-11-08 | 14410 | keep | 0 | Nov | 2021 | 0.0098146 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-11-08 12:31 | 2021-11-08 16:36 | 80 | 004:05 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA REMPLAZO AISLADOR | R21110800020 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 245 | 2021-11-08 | 19600 | keep | 0 | Nov | 2021 | 0.013349 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2021-11-08 12:41 | 2021-11-08 17:33 | 12 | 004:52 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUE NO REGULA DE 37.5KVA A 4.16KV POR UNO DE LA MISMA CAPACIDAD | P21110800092 | New_Event | Service Transformer Failure | Include | Include | Equipment | 292 | 2021-11-08 | 3504 | keep | 0 | Nov | 2021 | 0.0023866 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2021-11-08 12:43 | 2021-11-08 15:17 | 1 | 002:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21110800059 | New_Event | Bad Weather | Include | Include | Weather | 154 | 2021-11-08 | 154 | keep | 0 | Nov | 2021 | 0.00010489 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-11-08 13:20 | 2021-11-08 14:05 | 9 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR 2 CONECTORES DEFECTUOSOS | C21110800046 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2021-11-08 | 405 | keep | 0 | Nov | 2021 | 0.00027584 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-11-08 13:29 | 2021-11-08 14:41 | 9 | 001:12 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR SE DESGANCHO Y SE REPARO SECUNDARIA | B21110800037 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 72 | 2021-11-08 | 648 | keep | 0 | Nov | 2021 | 0.00044135 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2021-11-08 13:50 | 2021-11-08 17:55 | 4 | 004:05 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PRIMARIO MADERA 30' CLASE 3 POR UNO DE METAL 35' CLASE 3 | M21110800062 | New_Event | Defective Pole | Include | Include | Equipment | 245 | 2021-11-08 | 980 | keep | 0 | Nov | 2021 | 0.00066747 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-11-08 13:51 | 2021-11-08 20:31 | 1 | 006:40 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | A21110800064 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 400 | 2021-11-08 | 400 | keep | 0 | Nov | 2021 | 0.00027244 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-08 13:52 | 2021-11-08 18:13 | 1 | 004:21 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER | B21110800038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 261 | 2021-11-08 | 261 | keep | 0 | Nov | 2021 | 0.00017777 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-11-08 13:56 | 2021-11-08 13:57 | 3902 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECERRO INTERRUPTOR PARARRAYO AVERIADO | C21110800049 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-11-08 | 3902 | keep | 0 | Nov | 2021 | 0.0026576 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
HUMACAO | 2021-11-08 13:57 | 2021-11-08 15:19 | 3 | 001:22 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO | C21110800002 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 82 | 2021-11-08 | 246 | keep | 0 | Nov | 2021 | 0.00016755 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2021-11-08 14:00 | 2021-11-08 14:01 | 1067 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | P21110800097 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-08 | 1067 | keep | 0 | Nov | 2021 | 0.00072673 | 0.00072673 | Momentary | FALSE | FALSE | Not_TMED_Event | 1067
PONCE | 2021-11-08 14:01 | 2021-11-08 17:18 | 340 | 003:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR PARA CERRAR PUENTE EN TRONCAL PRIMARIO | P21110800101 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 197 | 2021-11-08 | 66980 | keep | 0 | Nov | 2021 | 0.04562 | 0.00023157 | Sustained | FALSE | FALSE | Not_TMED_Event | 340
YAUCO | 2021-11-08 14:02 | 2021-11-08 15:38 | 15 | 001:36 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE REPORTA CAUSA | P21110800098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2021-11-08 | 1440 | keep | 0 | Nov | 2021 | 0.00098078 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-11-08 14:20 | 2021-11-08 18:06 | 20 | 003:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN TRANSFORMADOR Y SE REALIZO DESGANCHE SECUNDARIO | B21110800039 | New_Event | Cutout Failure | Include | Include | Equipment | 226 | 2021-11-08 | 4520 | keep | 0 | Nov | 2021 | 0.0030786 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-11-08 14:30 | 2021-11-08 14:31 | 2457 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C21110800053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-08 | 2457 | keep | 0 | Nov | 2021 | 0.0016735 | 0.0016735 | Momentary | FALSE | FALSE | Not_TMED_Event | 2457
SAN JUAN | 2021-11-08 14:48 | 2021-11-08 20:21 | 10 | 005:33 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S21110800043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 333 | 2021-11-08 | 3330 | keep | 0 | Nov | 2021 | 0.002268 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-11-08 14:50 | 2021-11-08 19:17 | 12 | 004:27 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA X 37.5 KVA | A21110800020 | New_Event | Service Transformer Failure | Include | Include | Equipment | 267 | 2021-11-08 | 3204 | keep | 0 | Nov | 2021 | 0.0021822 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-11-08 14:52 | 2021-11-08 17:14 | 17 | 002:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR 250 PIES DE 3/2 ALUMINIO | C21110800056 | New_Event | Secondary Wire Down | Include | Include | Equipment | 142 | 2021-11-08 | 2414 | keep | 0 | Nov | 2021 | 0.0016442 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
AGUADILLA | 2021-11-08 15:27 | 2021-11-08 19:29 | 5 | 004:02 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR POR DESGANCHE | M21110800076 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 242 | 2021-11-08 | 1210 | keep | 0 | Nov | 2021 | 0.00082413 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2021-11-08 15:28 | 2021-11-08 17:52 | 40 | 002:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA AVERIADA NO FUNDIO | R21110800035 | New_Event | Cutout Failure | Include | Include | Equipment | 144 | 2021-11-08 | 5760 | keep | 0 | Nov | 2021 | 0.0039231 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2021-11-08 15:49 | 2021-11-08 15:50 | 1293 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO RECERRO SE DIO PRUEBA Y QUEDO EN SERVICIO | P21110800109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-08 | 1293 | keep | 0 | Nov | 2021 | 0.00088066 | 0.00088066 | Momentary | FALSE | FALSE | Not_TMED_Event | 1293
CAGUAS | 2021-11-08 15:54 | 2021-11-08 17:28 | 5 | 001:34 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5 KVA X 37.5 KVA | C21110800060 | New_Event | Service Transformer Failure | Include | Include | Equipment | 94 | 2021-11-08 | 470 | keep | 0 | Nov | 2021 | 0.00032011 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-11-08 16:00 | 2021-11-08 16:37 | 10 | 000:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BARRAS SECUNDARIAS | A21110800066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 37 | 2021-11-08 | 370 | keep | 0 | Nov | 2021 | 0.00025201 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-11-08 16:05 | 2021-11-08 16:37 | 2 | 000:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA PARA REPARAR BAJANTE SECUNDARIO | C21110800061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 32 | 2021-11-08 | 64 | keep | 0 | Nov | 2021 | 4.359e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2021-11-08 16:40 | 2021-11-08 17:25 | 11 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO FUSIBLE DE PM-T-23 PARA REEMPLAZAR BARRA EN PEDESTAL | C21110800063 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2021-11-08 | 495 | keep | 0 | Nov | 2021 | 0.00033714 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2021-11-08 16:40 | 2021-11-08 18:05 | 8 | 001:25 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA POR DESGANCHE | M21110800083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2021-11-08 | 680 | keep | 0 | Nov | 2021 | 0.00046314 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-11-08 16:50 | 2021-11-08 17:11 | 15 | 000:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21110700055 | New_Event | Secondary Wire Down | Include | Include | Equipment | 21 | 2021-11-08 | 315 | keep | 0 | Nov | 2021 | 0.00021455 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-11-08 16:52 | 2021-11-08 21:59 | 10 | 005:07 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR T-116 | B21110800050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 307 | 2021-11-08 | 3070 | keep | 0 | Nov | 2021 | 0.002091 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-11-08 16:57 | 2021-11-08 23:21 | 3420 | 006:24 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DEL 0010 SE RETIRARON AVES MUERTAS Y SE DESCONECTARON 2 PARARRAYOS AVERIADOS EN BARRA DE DISTRIBUCION | C21110800068 | New_Event |  |  | Include | Wildlife | 384 | 2021-11-08 | 1313280 | keep | 0 | Nov | 2021 | 0.89447 | 0.0023293 | Sustained | FALSE | FALSE | Not_TMED_Event | 3420
HUMACAO | 2021-11-08 16:57 | 2021-11-08 23:21 | 4 | 006:24 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DEL 0010 SE RETIRARON AVES MUERTAS Y SE DESCONECTARON 2 PARARRAYOS AVERIADOS EN BARRA DE DISTRIBUCION | C21110800068 | New_Event |  |  | Include | Wildlife | 384 | 2021-11-08 | 1536 | keep | 0 | Nov | 2021 | 0.0010462 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2021-11-08 16:57 | 2021-11-08 23:21 | 3 | 006:24 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DEL 0010 SE RETIRARON AVES MUERTAS Y SE DESCONECTARON 2 PARARRAYOS AVERIADOS EN BARRA DE DISTRIBUCION | C21110800068 | New_Event |  |  | Include | Wildlife | 384 | 2021-11-08 | 1152 | keep | 0 | Nov | 2021 | 0.00078462 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2021-11-08 17:14 | 2021-11-09 16:30 | 7 | 023:16 | P | TRANSFORMADOR AVERIADO | INSTALO XMR DE 25 KVA | C21110800056 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1396 | 2021-11-08 | 9772 | keep | 0 | Nov | 2021 | 0.0066557 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-11-08 17:18 | 2021-11-08 20:59 | 36 | 003:41 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER Y 1 X 25 EN TRANSFORMADOR | B21110800051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 221 | 2021-11-08 | 7956 | keep | 0 | Nov | 2021 | 0.0054188 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
PONCE | 2021-11-08 17:18 | 2021-11-08 17:49 | 1067 | 000:31 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR PARA CERRAR PUENTE PRIMARIO EN TRONCAL DEL ALIMENTADOR | P21110800116 | Additional_clients | Wire Down | Include | Include | Equipment | 31 | 2021-11-08 | 33077 | keep | 0 | Nov | 2021 | 0.022529 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-11-08 17:21 | 2021-11-08 17:22 | 817 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C21110800069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-08 | 817 | keep | 0 | Nov | 2021 | 0.00055645 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
PONCE | 2021-11-08 17:34 | 2021-11-08 20:14 | 150 | 002:40 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21110800119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2021-11-08 | 24000 | keep | 0 | Nov | 2021 | 0.016346 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2021-11-08 17:56 | 2021-11-09 11:12 | 5 | 017:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR CRUCE POR REPTIL | C21110800076 | New_Event |  |  | Include | Wildlife | 1036 | 2021-11-08 | 5180 | keep | 0 | Nov | 2021 | 0.0035281 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-11-08 17:57 | 2021-11-08 17:58 | 742 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 1709-03 LLEVA 1709-5 | S21110800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-08 | 742 | keep | 0 | Nov | 2021 | 0.00050537 | 0.00050537 | Momentary | FALSE | FALSE | Not_TMED_Event | 742
BAYAMON | 2021-11-08 17:57 | 2021-11-08 17:58 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 1709-03 LLEVA 1709-5 | S21110800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-08 | 2364 | keep | 0 | Nov | 2021 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
AGUADILLA | 2021-11-08 17:57 | 2021-11-08 17:58 | 3041 | 000:01 | T | TRANSFORMADOR AVERIADO | RECIERRE DE INTERRUPTOR | M21110800000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1 | 2021-11-08 | 3041 | keep | 0 | Nov | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2021-11-08 17:58 | 2021-11-08 21:10 | 5 | 003:12 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5KVA AVERIADO POR 37.5KVA BUENO | M21110800091 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 192 | 2021-11-08 | 960 | keep | 0 | Nov | 2021 | 0.00065385 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-11-08 18:08 | 2021-11-08 18:42 | 250 | 000:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRE CORTE DE LINEA PARA SACAR CAMION ENRREDADO EN LINEA PRIMARIA | P21110800121 | New_Event |  |  | Include | Wildlife | 34 | 2021-11-08 | 8500 | keep | 0 | Nov | 2021 | 0.0057893 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
ARECIBO | 2021-11-08 18:21 | 2021-11-08 18:22 | 5042 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21110800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-08 | 5042 | keep | 0 | Nov | 2021 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
ARECIBO | 2021-11-08 18:37 | 2021-11-09 13:00 | 13 | 018:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES SECUNDARIAS | A21110800092 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1103 | 2021-11-08 | 14339 | keep | 0 | Nov | 2021 | 0.0097662 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CANOVANAS | 2021-11-08 18:44 | 2021-11-08 21:43 | 25 | 002:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN C/L CRUCE POR AVE | R21110800042 | New_Event |  |  | Include | Wildlife | 179 | 2021-11-08 | 4475 | keep | 0 | Nov | 2021 | 0.0030479 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-11-08 18:55 | 2021-11-08 20:05 | 200 | 001:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | M21110800094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2021-11-08 | 14000 | keep | 0 | Nov | 2021 | 0.0095353 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2021-11-08 19:35 | 2021-11-09 00:09 | 30 | 004:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO Y SE RETIRO GLOBOS ENREDADOS EN LINEA PRIMARIA | A21110800097 | New_Event | Wire Down | Include | Include | Equipment | 274 | 2021-11-08 | 8220 | keep | 0 | Nov | 2021 | 0.0055986 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2021-11-08 19:50 | 2021-11-08 20:08 | 35 | 000:18 | P | DESGANCHE | SE ABRIO CORTE DE LINEA DE EMERGENCIA PARA RETIRAR ARBOL SOBRE LINEA | A21110800099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 18 | 2021-11-08 | 630 | keep | 0 | Nov | 2021 | 0.00042909 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2021-11-08 20:33 | 2021-11-09 00:46 | 70 | 004:13 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | S21110800068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 253 | 2021-11-08 | 17710 | keep | 0 | Nov | 2021 | 0.012062 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-11-08 21:18 | 2021-11-08 21:19 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21110800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-08 | 990 | keep | 0 | Nov | 2021 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
BAYAMON | 2021-11-08 22:36 | 2021-11-09 09:06 | 1 | 010:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA SE RETIRO AVE DE LA CRUCETA | B21110800062 | New_Event |  |  | Include | Wildlife | 630 | 2021-11-08 | 630 | keep | 0 | Nov | 2021 | 0.00042909 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-11-09 00:02 | 2021-11-09 11:45 | 20 | 011:43 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | A21110900001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 703 | 2021-11-09 | 14060 | keep | 0 | Nov | 2021 | 0.0095762 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-11-09 00:57 | 2021-11-09 10:13 | 50 | 009:16 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21110900001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 556 | 2021-11-09 | 27800 | keep | 0 | Nov | 2021 | 0.018934 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-11-09 02:17 | 2021-11-09 20:18 | 40 | 018:01 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REMPLAZO TERMINACION Y EMPALME SOTERRADO | B21110900001 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1081 | 2021-11-09 | 43240 | keep | 0 | Nov | 2021 | 0.029451 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-09 03:38 | 2021-11-09 09:11 | 75 | 005:33 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21110900002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 333 | 2021-11-09 | 24975 | keep | 0 | Nov | 2021 | 0.01701 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2021-11-09 04:20 | 2021-11-09 09:01 | 140 | 004:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN C/L CRUCE POR AVE | C21110900003 | New_Event |  |  | Include | Wildlife | 281 | 2021-11-09 | 39340 | keep | 0 | Nov | 2021 | 0.026794 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
CAGUAS | 2021-11-09 06:19 | 2021-11-09 10:24 | 200 | 004:05 | P | DESGANCHE | 3 X 100 EN CORTE DE LINEA | C21110900012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2021-11-09 | 49000 | keep | 0 | Nov | 2021 | 0.033374 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2021-11-09 07:00 | 2021-11-09 09:30 | 100 | 002:30 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA POR DESGANCHE | A21110900002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2021-11-09 | 15000 | keep | 0 | Nov | 2021 | 0.010216 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-11-09 07:28 | 2021-11-09 09:10 | 50 | 001:42 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO CAUSA | C21110900023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 102 | 2021-11-09 | 5100 | keep | 0 | Nov | 2021 | 0.0034736 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-09 07:31 | 2021-11-09 10:29 | 40 | 002:58 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21110900003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 178 | 2021-11-09 | 7120 | keep | 0 | Nov | 2021 | 0.0048494 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-11-09 07:32 | 2021-11-09 10:42 | 6 | 003:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO Y LINEA SECUNDARIA | C21110900025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 190 | 2021-11-09 | 1140 | keep | 0 | Nov | 2021 | 0.00077645 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-11-09 07:33 | 2021-11-09 12:36 | 4 | 005:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | S21110900005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 303 | 2021-11-09 | 1212 | keep | 0 | Nov | 2021 | 0.00082549 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-11-09 07:33 | 2021-11-09 14:28 | 50 | 006:55 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21110900004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 415 | 2021-11-09 | 20750 | keep | 0 | Nov | 2021 | 0.014133 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-11-09 07:36 | 2021-11-09 07:37 | 2039 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21110900004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-09 | 2039 | keep | 0 | Nov | 2021 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
UTUADO | 2021-11-09 07:44 | 2021-11-09 10:41 | 4 | 002:57 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR POR DESGANCHE | A21110900007 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 177 | 2021-11-09 | 708 | keep | 0 | Nov | 2021 | 0.00048222 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-11-09 07:50 | 2021-11-09 10:52 | 8 | 003:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES EN LINEAS SECUNDARIAS | A21110900008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 182 | 2021-11-09 | 1456 | keep | 0 | Nov | 2021 | 0.00099167 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2021-11-09 07:59 | 2021-11-09 08:00 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21110900005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-09 | 2113 | keep | 0 | Nov | 2021 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
BARRANQUITAS | 2021-11-09 08:00 | 2021-11-09 16:33 | 30 | 008:33 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO CAUSA | C21110900029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 513 | 2021-11-09 | 15390 | keep | 0 | Nov | 2021 | 0.010482 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-11-09 08:01 | 2021-11-09 12:07 | 40 | 004:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CRUCE POR AVE | C21110900030 | New_Event |  |  | Include | Wildlife | 246 | 2021-11-09 | 9840 | keep | 0 | Nov | 2021 | 0.006702 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-09 08:21 | 2021-11-09 08:22 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21110900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-09 | 3941 | keep | 0 | Nov | 2021 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
MAYAGÃœEZ | 2021-11-09 08:26 | 2021-11-09 14:35 | 100 | 006:09 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M21110900007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 369 | 2021-11-09 | 36900 | keep | 0 | Nov | 2021 | 0.025132 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-11-09 08:27 | 2021-11-09 17:29 | 1 | 009:02 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S21110900025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 542 | 2021-11-09 | 542 | keep | 0 | Nov | 2021 | 0.00036915 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-11-09 08:34 | 2021-11-09 14:12 | 8 | 005:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR BARRAS DE PEDESTAL | R21110900002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 338 | 2021-11-09 | 2704 | keep | 0 | Nov | 2021 | 0.0018417 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-11-09 08:41 | 2021-11-09 08:42 | 4664 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE INTERRUPTOR | M21110900018 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-11-09 | 4664 | keep | 0 | Nov | 2021 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
MAYAGÃœEZ | 2021-11-09 08:44 | 2021-11-09 22:52 | 150 | 014:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21110900147 | New_Event | Bad Weather | Include | Include | Weather | 848 | 2021-11-09 | 127200 | keep | 0 | Nov | 2021 | 0.086635 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2021-11-09 08:45 | 2021-11-09 10:26 | 14 | 001:41 | P | NO SE REPORTO CAUSA | 1 X 15 EN PROVISIONAL AEREO NO ENCONTRARON CAUSA | R21110900003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 101 | 2021-11-09 | 1414 | keep | 0 | Nov | 2021 | 0.00096307 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2021-11-09 08:50 | 2021-11-09 09:41 | 1 | 000:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 Y 1 X 30 EN CORTE DE LINEA POR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21110900022 | New_Event | Bad Weather | Include | Include | Weather | 51 | 2021-11-09 | 51 | keep | 0 | Nov | 2021 | 3.4736e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-11-09 09:03 | 2021-11-09 12:03 | 35 | 003:00 | P | ESTRUCTURA AVERIADA | ENDEREZAR POSTE PRIMARIO | A21110900023 | New_Event | Defective Pole | Include | Include | Equipment | 180 | 2021-11-09 | 6300 | keep | 0 | Nov | 2021 | 0.0042909 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-11-09 09:06 | 2021-11-09 12:04 | 80 | 002:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA IGUANA CRUZO FASE A TIERRA | M21110900029 | New_Event |  |  | Include | Wildlife | 178 | 2021-11-09 | 14240 | keep | 0 | Nov | 2021 | 0.0096988 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-11-09 09:15 | 2021-11-09 09:16 | 5062 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R21110900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-09 | 5062 | keep | 0 | Nov | 2021 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
BAYAMON | 2021-11-09 09:17 | 2021-11-09 18:40 | 10 | 009:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 30 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | B21110900007 | New_Event | Cutout Failure | Include | Include | Equipment | 563 | 2021-11-09 | 5630 | keep | 0 | Nov | 2021 | 0.0038346 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-11-09 09:26 | 2021-11-09 11:47 | 9 | 002:21 | P | PARARRAYOS DEFECTUOSO | 1 X 10 EN XMR FIJO CAJA Y REMPLAZO PARARRAYO | C21110900047 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 141 | 2021-11-09 | 1269 | keep | 0 | Nov | 2021 | 0.00086431 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-11-09 09:35 | 2021-11-09 09:38 | 1983 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR Y SE CERRO POR CONTROL ESTA CARGA ESTA POR EL INTERRUPTOR 1801-02 | B21110900008 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2021-11-09 | 5949 | keep | 0 | Nov | 2021 | 0.0040518 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-11-09 09:35 | 2021-11-09 09:38 | 1000 | 000:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR 1801 02 Y SE CERRO POR CONTROL LLEVA CARGA 1711-04 Y PARTE 1717 01 | B21110900008 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2021-11-09 | 3000 | keep | 0 | Nov | 2021 | 0.0020433 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
BAYAMON | 2021-11-09 09:35 | 2021-11-09 09:38 | 186 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO Y SE CERRO POR CONTROL LLEVA CARGA 1711-04 Y PARTE 1717 01 | B21110900008 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2021-11-09 | 558 | keep | 0 | Nov | 2021 | 0.00038005 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
ARECIBO | 2021-11-09 09:38 | 2021-11-09 09:39 | 24 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | A21110900000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-09 | 24 | keep | 0 | Nov | 2021 | 1.6346e-05 | 1.6346e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2021-11-09 09:39 | 2021-11-09 15:08 | 150 | 005:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO EN TRONCAL | B21110900009 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 329 | 2021-11-09 | 49350 | keep | 0 | Nov | 2021 | 0.033612 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2021-11-09 09:39 | 2021-11-09 15:27 | 7 | 005:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | A21110900035 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 348 | 2021-11-09 | 2436 | keep | 0 | Nov | 2021 | 0.0016591 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-11-09 09:40 | 2021-11-09 11:40 | 2 | 002:00 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE DE 35' MADERA | A21110900032 | New_Event | Defective Pole | Include | Include | Equipment | 120 | 2021-11-09 | 240 | keep | 0 | Nov | 2021 | 0.00016346 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2021-11-09 09:42 | 2021-11-09 16:08 | 1 | 006:26 | P | NO SE REPORTO CAUSA | 1 X 80 EN TRANSCLOSURE | B21110900012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 386 | 2021-11-09 | 386 | keep | 0 | Nov | 2021 | 0.0002629 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-11-09 09:45 | 2021-11-09 11:17 | 7 | 001:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR LINEA Y BAJANTE SECUNDARIO | C21110900050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 92 | 2021-11-09 | 644 | keep | 0 | Nov | 2021 | 0.00043863 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-11-09 09:46 | 2021-11-09 13:35 | 10 | 003:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARARON CONEXIONES SECUNDARIAS | A21110900034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 229 | 2021-11-09 | 2290 | keep | 0 | Nov | 2021 | 0.0015597 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-11-09 09:52 | 2021-11-09 13:10 | 55 | 003:18 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHO Y FIJO BAJANTE DE CAJA A XMR | C21110900052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2021-11-09 | 10890 | keep | 0 | Nov | 2021 | 0.0074171 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
VEGA BAJA | 2021-11-09 09:55 | 2021-11-09 18:24 | 1 | 008:29 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21110900016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 509 | 2021-11-09 | 509 | keep | 0 | Nov | 2021 | 0.00034668 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-11-09 10:03 | 2021-11-09 10:45 | 224 | 000:42 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA ABRIR PUENTES Y SECCIONALIZAR POSTE EN MALAS CONDICIONES | R21110900005 | New_Event | Defective Pole | Include | Include | Equipment | 42 | 2021-11-09 | 9408 | keep | 0 | Nov | 2021 | 0.0064077 | 0.00015257 | Sustained | FALSE | FALSE | Not_TMED_Event | 224
BAYAMON | 2021-11-09 10:12 | 2021-11-09 14:21 | 1 | 004:09 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | B21110900024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 249 | 2021-11-09 | 249 | keep | 0 | Nov | 2021 | 0.00016959 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-11-09 10:45 | 2021-11-09 16:43 | 81 | 005:58 | P | ESTRUCTURA AVERIADA | ABRIO C/L PARA REMPLAZAR POSTE EN MAL ESTADO | R21110900007 | Partial_restoration | Defective Pole | Include | Include | Equipment | 358 | 2021-11-09 | 28998 | keep | 0 | Nov | 2021 | 0.01975 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-11-09 10:50 | 2021-11-09 12:26 | 15 | 001:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M21110900047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 96 | 2021-11-09 | 1440 | keep | 0 | Nov | 2021 | 0.00098078 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-11-09 10:53 | 2021-11-09 10:54 | 4702 | 000:01 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL | B21110900038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-09 | 4702 | keep | 0 | Nov | 2021 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2021-11-09 10:57 | 2021-11-09 12:33 | 4702 | 001:36 | T | DESGANCHE | PERSONAL DESGANCHO Y ELIMINO AISLADOR SIN ORDENES DEL OIC | B21110900040 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 96 | 2021-11-09 | 451392 | keep | 0 | Nov | 2021 | 0.30744 | 0.0032025 | Sustained | FALSE | FALSE | Not_TMED_Event | 4702
PONCE | 2021-11-09 10:58 | 2021-11-09 12:20 | 1 | 001:22 | P | NO SE REPORTO CAUSA | 1 X 25 NX EN SU-1C NO SE REPORTO CAUSA | P21110900016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2021-11-09 | 82 | keep | 0 | Nov | 2021 | 5.585e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-11-09 11:07 | 2021-11-09 12:01 | 7 | 000:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21110900015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 54 | 2021-11-09 | 378 | keep | 0 | Nov | 2021 | 0.00025745 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-11-09 11:13 | 2021-11-09 22:10 | 50 | 010:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA Y SE REALIZO DESGANCHE | A21110900042 | New_Event | Wire Down | Include | Include | Equipment | 657 | 2021-11-09 | 32850 | keep | 0 | Nov | 2021 | 0.022374 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2021-11-09 11:15 | 2021-11-09 11:16 | 1131 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21110900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-09 | 1131 | keep | 0 | Nov | 2021 | 0.00077032 | 0.00077032 | Momentary | FALSE | FALSE | Not_TMED_Event | 1131
MAYAGÃœEZ | 2021-11-09 11:19 | 2021-11-09 16:07 | 60 | 004:48 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL SOBRE LINEAS | M21110900054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2021-11-09 | 17280 | keep | 0 | Nov | 2021 | 0.011769 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-11-09 11:31 | 2021-11-11 19:18 | 12 | 055:47 | P | ESTRUCTURA AVERIADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO POSTE PARTIDO | A21110900043 | New_Event | Defective Pole | Include | Include | Equipment | 3347 | 2021-11-09 | 40164 | keep | 0 | Nov | 2021 | 0.027356 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2021-11-09 11:34 | 2021-11-09 13:23 | 65 | 001:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEA | P21110900024 | New_Event |  |  | Include | Wildlife | 109 | 2021-11-09 | 7085 | keep | 0 | Nov | 2021 | 0.0048256 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
ARECIBO | 2021-11-09 11:37 | 2021-11-09 14:33 | 6 | 002:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFOMADOR Y SE REPARO BAJANTE SECUNDARIO | A21110900045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 176 | 2021-11-09 | 1056 | keep | 0 | Nov | 2021 | 0.00071924 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-11-09 11:54 | 2021-11-09 15:01 | 55 | 003:07 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L NO CAUSA | C21110900070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 187 | 2021-11-09 | 10285 | keep | 0 | Nov | 2021 | 0.0070051 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
HUMACAO | 2021-11-09 12:08 | 2021-11-09 16:27 | 20 | 004:19 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | C21110900072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 259 | 2021-11-09 | 5180 | keep | 0 | Nov | 2021 | 0.0035281 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-11-09 12:25 | 2021-11-09 12:38 | 4 | 000:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA LIMPIAR BUSHING SECUNDARIOS | P21110900027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 13 | 2021-11-09 | 52 | keep | 0 | Nov | 2021 | 3.5417e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-11-09 12:30 | 2021-11-09 13:34 | 15 | 001:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M21110800095 | New_Event | Secondary Wire Down | Include | Include | Equipment | 64 | 2021-11-09 | 960 | keep | 0 | Nov | 2021 | 0.00065385 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-11-09 12:58 | 2021-11-09 16:49 | 100 | 003:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN C/L LEVANTO CONDUCTOR | R21110900013 | New_Event | Wire Down | Include | Include | Equipment | 231 | 2021-11-09 | 23100 | keep | 0 | Nov | 2021 | 0.015733 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2021-11-09 13:26 | 2021-11-09 15:52 | 47 | 002:26 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE ABRE CORTE DE LINEA PARA HACER DESGANCHE | P21110900032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2021-11-09 | 6862 | keep | 0 | Nov | 2021 | 0.0046737 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
BAYAMON | 2021-11-09 13:28 | 2021-11-09 21:45 | 26 | 008:17 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L | S21110900035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 497 | 2021-11-09 | 12922 | keep | 0 | Nov | 2021 | 0.0088011 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
VEGA BAJA | 2021-11-09 13:49 | 2021-11-09 16:33 | 10 | 002:44 | P | PARARRAYOS DEFECTUOSO | 1 X 25 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS AVERIADO | B21110900126 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 164 | 2021-11-09 | 1640 | keep | 0 | Nov | 2021 | 0.001117 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-11-09 14:16 | 2021-11-09 17:51 | 7 | 003:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | R21110900017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 215 | 2021-11-09 | 1505 | keep | 0 | Nov | 2021 | 0.001025 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-11-09 14:22 | 2021-11-09 19:30 | 70 | 005:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | M21110900079 | New_Event | Wire Down | Include | Include | Equipment | 308 | 2021-11-09 | 21560 | keep | 0 | Nov | 2021 | 0.014684 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-11-09 14:25 | 2021-11-09 17:10 | 15 | 002:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 40 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO ABIERTO | M21110900080 | New_Event | Wire Down | Include | Include | Equipment | 165 | 2021-11-09 | 2475 | keep | 0 | Nov | 2021 | 0.0016857 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-11-09 14:34 | 2021-11-10 18:26 | 1 | 027:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | BAJANTE ZAFADO SOBRE CRUCETA | A21111090006 | New_Event | Wire Down | Include | Include | Equipment | 1672 | 2021-11-09 | 1672 | keep | 0 | Nov | 2021 | 0.0011388 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-11-09 14:38 | 2021-11-09 18:38 | 25 | 004:00 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHO Y REPARO SECUNDARIA | C21110900083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2021-11-09 | 6000 | keep | 0 | Nov | 2021 | 0.0040866 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-11-09 14:48 | 2021-11-09 21:11 | 25 | 006:23 | P | NO SE REPORTO CAUSA | 2 X 65 EN C/L | S21110900043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 383 | 2021-11-09 | 9575 | keep | 0 | Nov | 2021 | 0.0065215 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-11-09 14:48 | 2021-11-09 20:50 | 1 | 006:02 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S21110900044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 362 | 2021-11-09 | 362 | keep | 0 | Nov | 2021 | 0.00024656 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-11-09 14:51 | 2021-11-09 16:17 | 50 | 001:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN RISE Y 1 X 40 1 X 50 EN C/L CRUCE POR AVE | R21110900020 | New_Event |  |  | Include | Wildlife | 86 | 2021-11-09 | 4300 | keep | 0 | Nov | 2021 | 0.0029287 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-11-09 14:52 | 2021-11-09 17:50 | 7 | 002:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C21110900084 | New_Event | Secondary Wire Down | Include | Include | Equipment | 178 | 2021-11-09 | 1246 | keep | 0 | Nov | 2021 | 0.00084864 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-11-09 15:08 | 2021-11-09 16:03 | 1983 | 000:55 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERUPTOR 1801 02 PARA REPARAR PUENTE ABIERTO EN TRONCAL LLEVA CARGA 1711-04 Y PARTE 1717-01 | B21110900149 | New_Event | Wire Down | Include | Include | Equipment | 55 | 2021-11-09 | 109065 | keep | 0 | Nov | 2021 | 0.074284 | 0.0013506 | Sustained | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-11-09 15:08 | 2021-11-09 16:03 | 1000 | 000:55 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1801-02 PARA REPARAR PUENTE ABIERTO EN TRONCAL LLEVA CARGA 1711 04 Y PARTE 1717 01 | B21110900149 | New_Event | Wire Down | Include | Include | Equipment | 55 | 2021-11-09 | 55000 | keep | 0 | Nov | 2021 | 0.03746 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
BAYAMON | 2021-11-09 15:08 | 2021-11-09 16:03 | 186 | 000:55 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA REPARAR PUENTE ABIERTO EN TRONCAL LLEVA CARGA 1711 04 Y PARTE 1717 01 | B21110900149 | New_Event | Wire Down | Include | Include | Equipment | 55 | 2021-11-09 | 10230 | keep | 0 | Nov | 2021 | 0.0069676 | 0.00012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 186
FAJARDO | 2021-11-09 15:10 | 2021-11-09 17:27 | 20 | 002:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN C/L CAMION HALO LINEAS | R21110900022 | New_Event |  |  | Include | Wildlife | 137 | 2021-11-09 | 2740 | keep | 0 | Nov | 2021 | 0.0018662 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-11-09 15:12 | 2021-11-09 20:48 | 50 | 005:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTO CONDUCTOR NO FUNDIO | C21110900089 | New_Event | Wire Down | Include | Include | Equipment | 336 | 2021-11-09 | 16800 | keep | 0 | Nov | 2021 | 0.011442 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-09 15:27 | 2021-11-09 17:20 | 75 | 001:53 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M21110900097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2021-11-09 | 8475 | keep | 0 | Nov | 2021 | 0.0057723 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2021-11-09 15:42 | 2021-11-09 17:04 | 50 | 001:22 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO CAUSA | C21110900092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2021-11-09 | 4100 | keep | 0 | Nov | 2021 | 0.0027925 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-11-09 15:49 | 2021-11-09 20:46 | 40 | 004:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO C/L PARA REPARAR NEUTRAL PRIMARIO | C21110900094 | New_Event | Wire Down | Include | Include | Equipment | 297 | 2021-11-09 | 11880 | keep | 0 | Nov | 2021 | 0.0080914 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-09 15:50 | 2021-11-09 16:31 | 2 | 000:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REMPLAZO CONECTORES SECUNDARIOS | S21110900016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 41 | 2021-11-09 | 82 | keep | 0 | Nov | 2021 | 5.585e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2021-11-09 16:07 | 2021-11-09 18:31 | 30 | 002:24 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21110900162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2021-11-09 | 4320 | keep | 0 | Nov | 2021 | 0.0029423 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-11-09 16:08 | 2021-11-09 16:09 | 1467 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21110900098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-09 | 1467 | keep | 0 | Nov | 2021 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
BARRANQUITAS | 2021-11-09 16:23 | 2021-11-09 16:24 | 2635 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21110900101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-09 | 2635 | keep | 0 | Nov | 2021 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
PONCE | 2021-11-09 16:42 | 2021-11-09 18:51 | 1 | 002:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN TRANSFORMADOR SE REPARO PUENTE PRIMARIO SAFADO DE CAJA PRIMARIA | P21110900047 | New_Event | Wire Down | Include | Include | Equipment | 129 | 2021-11-09 | 129 | keep | 0 | Nov | 2021 | 8.7861e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-11-09 16:49 | 2021-11-09 20:58 | 80 | 004:09 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHO Y CRUCE POR AVE | C21110900104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 249 | 2021-11-09 | 19920 | keep | 0 | Nov | 2021 | 0.013567 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-11-09 16:56 | 2021-11-09 16:57 | 3597 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR 1719 15 LLEVANDO PARTE CARGA 9405 05 | B21110900000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-11-09 | 3597 | keep | 0 | Nov | 2021 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2021-11-09 16:56 | 2021-11-09 16:57 | 600 | 000:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE ALIMENTADOR 1719-15 LLEVANDO PARTE DE LA CARGA DEL ALIMENTADOR 9405-05 | B21110900000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-11-09 | 600 | keep | 0 | Nov | 2021 | 0.00040866 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
BAYAMON | 2021-11-09 16:56 | 2021-11-09 21:55 | 30 | 004:59 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21110900169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 299 | 2021-11-09 | 8970 | keep | 0 | Nov | 2021 | 0.0061094 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-11-09 16:57 | 2021-11-09 18:26 | 75 | 001:29 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO AISLADOR SE SUBIO ALAMBRE Y SE REMPLAZO PORTAFUSIBLE | B21110900171 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 89 | 2021-11-09 | 6675 | keep | 0 | Nov | 2021 | 0.0045463 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
PONCE | 2021-11-09 17:03 | 2021-11-09 18:08 | 10 | 001:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE TRANSFORMADOR PARA REPARAR PUENTE PRIMARIO DE PARARRAYO CRUZADO | P21110900048 | New_Event | Wire Down | Include | Include | Equipment | 65 | 2021-11-09 | 650 | keep | 0 | Nov | 2021 | 0.00044271 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-11-09 17:17 | 2021-11-09 18:50 | 65 | 001:33 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEAS | M21110900115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2021-11-09 | 6045 | keep | 0 | Nov | 2021 | 0.0041172 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2021-11-09 17:23 | 2021-11-09 17:24 | 2617 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21110900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-09 | 2617 | keep | 0 | Nov | 2021 | 0.0017824 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
MAYAGÃœEZ | 2021-11-09 17:25 | 2021-11-09 19:15 | 100 | 001:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21110900121 | New_Event | Bad Weather | Include | Include | Weather | 110 | 2021-11-09 | 11000 | keep | 0 | Nov | 2021 | 0.007492 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-11-09 17:26 | 2021-11-09 20:09 | 10 | 002:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR Y RELOCALIZAR TOMA SECUNDARIA ABIERTA | S21110800009 | New_Event | Secondary Wire Down | Include | Include | Equipment | 163 | 2021-11-09 | 1630 | keep | 0 | Nov | 2021 | 0.0011102 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-11-09 17:28 | 2021-11-09 17:41 | 14 | 000:13 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE REPORTA CAUSA | P21110900053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2021-11-09 | 182 | keep | 0 | Nov | 2021 | 0.00012396 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2021-11-09 17:32 | 2021-11-09 19:39 | 10 | 002:07 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BARRAS SECUNDARIAS EN PEDESTAL | B21110900172 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 127 | 2021-11-09 | 1270 | keep | 0 | Nov | 2021 | 0.00086499 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-09 17:40 | 2021-11-09 17:41 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21110900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-09 | 3941 | keep | 0 | Nov | 2021 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
MAYAGÃœEZ | 2021-11-09 18:00 | 2021-11-09 20:40 | 4664 | 002:40 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO PUENTES PARA SECCIONALIZAR AISLADORES PARTIDOS | M21110900124 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 160 | 2021-11-09 | 746240 | keep | 0 | Nov | 2021 | 0.50826 | 0.0031766 | Sustained | FALSE | FALSE | Not_TMED_Event | 4664
BAYAMON | 2021-11-09 18:05 | 2021-11-09 18:34 | 10 | 000:29 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BARRA SECUNDARIA EN PEDESTAL | B21110900141 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 29 | 2021-11-09 | 290 | keep | 0 | Nov | 2021 | 0.00019752 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-11-09 18:12 | 2021-11-09 21:08 | 16 | 002:56 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 15 X 15KVA | C21110900105 | New_Event | Service Transformer Failure | Include | Include | Equipment | 176 | 2021-11-09 | 2816 | keep | 0 | Nov | 2021 | 0.001918 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2021-11-09 18:26 | 2021-11-09 18:27 | 3597 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR 1719 15 LLEVANDO PARTE DE LA CARGA 9405 05 | B21110900000 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-11-09 | 3597 | keep | 0 | Nov | 2021 | 0.0024499 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-09 18:26 | 2021-11-09 18:27 | 600 | 000:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE ALIMENTADOR 1719-15 LLEVANDO PARTE DE LA CARGA DEL ALIMENTADOR 9405-05 | B21110900000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-11-09 | 600 | keep | 0 | Nov | 2021 | 0.00040866 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
BAYAMON | 2021-11-09 18:27 | 2021-11-09 20:13 | 75 | 001:46 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO AISLADOR SE SUBIO ALAMBRE Y SE REMPLAZO PORTAFUSIBLE | B21110900171 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 106 | 2021-11-09 | 7950 | keep | 0 | Nov | 2021 | 0.0054147 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
GUAYAMA | 2021-11-09 18:36 | 2021-11-09 21:02 | 50 | 002:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE CAMBIO CAJA PRIMARIA QUEMADA | P21110900054 | New_Event | Cutout Failure | Include | Include | Equipment | 146 | 2021-11-09 | 7300 | keep | 0 | Nov | 2021 | 0.004972 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-11-09 18:38 | 2021-11-10 11:08 | 145 | 016:30 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M21110900145 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 990 | 2021-11-09 | 143550 | keep | 0 | Nov | 2021 | 0.097771 | 9.8759e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 145
AGUADILLA | 2021-11-09 18:38 | 2021-11-10 11:08 | 50 | 016:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21110900145 | New_Event | Bad Weather | Include | Include | Weather | 990 | 2021-11-09 | 49500 | keep | 0 | Nov | 2021 | 0.033714 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-09 18:47 | 2021-11-10 10:27 | 50 | 015:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21110900152 | New_Event | Bad Weather | Include | Include | Weather | 940 | 2021-11-09 | 47000 | keep | 0 | Nov | 2021 | 0.032011 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-09 18:51 | 2021-11-09 18:52 | 2067 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | M21110900000 | New_Event |  |  | Include | Wildlife | 1 | 2021-11-09 | 2067 | keep | 0 | Nov | 2021 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
MAYAGÃœEZ | 2021-11-09 18:52 | 2021-11-10 11:27 | 15 | 016:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M21110900199 | 1st_after_momentary |  |  | Include | Wildlife | 995 | 2021-11-09 | 14925 | keep | 0 | Nov | 2021 | 0.010165 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-11-09 19:14 | 2021-11-09 21:19 | 20 | 002:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | A21110900076 | New_Event | Cutout Failure | Include | Include | Equipment | 125 | 2021-11-09 | 2500 | keep | 0 | Nov | 2021 | 0.0017027 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-11-09 19:14 | 2021-11-09 20:48 | 20 | 001:34 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE SECUNDARIO | A21110900075 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 94 | 2021-11-09 | 1880 | keep | 0 | Nov | 2021 | 0.0012805 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-11-09 19:25 | 2021-11-09 20:34 | 26 | 001:09 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA SE PATRULLO | R21110900029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 69 | 2021-11-09 | 1794 | keep | 0 | Nov | 2021 | 0.0012219 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
PONCE | 2021-11-09 20:30 | 2021-11-09 21:13 | 10 | 000:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE LEVANTO SECUNDARIA | P21110900064 | New_Event | Secondary Wire Down | Include | Include | Equipment | 43 | 2021-11-09 | 430 | keep | 0 | Nov | 2021 | 0.00029287 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-11-09 20:40 | 2021-11-10 13:55 | 15 | 017:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO PUENTES Y SE REEMPLAZO AISLADORES Y CAJA PRIMARIA DEFECTUOSA 100AMP MARCA ABB FID:23551691 | M21110900192 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 1035 | 2021-11-09 | 15525 | keep | 0 | Nov | 2021 | 0.010574 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-09 20:48 | 2021-11-09 22:04 | 40 | 001:16 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21110900063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 76 | 2021-11-09 | 3040 | keep | 0 | Nov | 2021 | 0.0020705 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-11-09 20:50 | 2021-11-09 22:35 | 20 | 001:45 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21110900195 | New_Event | Bad Weather | Include | Include | Weather | 105 | 2021-11-09 | 2100 | keep | 0 | Nov | 2021 | 0.0014303 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-11-09 21:03 | 2021-11-10 10:38 | 15 | 013:35 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | M21110900196 | New_Event | Vegetation Contact | Include | Include | Vegetation | 815 | 2021-11-09 | 12225 | keep | 0 | Nov | 2021 | 0.0083264 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-11-09 21:09 | 2021-11-09 21:10 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21110900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-09 | 1192 | keep | 0 | Nov | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
MAYAGÃœEZ | 2021-11-09 21:11 | 2021-11-10 17:38 | 100 | 020:27 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21110900197 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1227 | 2021-11-09 | 122700 | keep | 0 | Nov | 2021 | 0.08357 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2021-11-09 22:38 | 2021-11-09 22:39 | 5069 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21110900066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-09 | 5069 | keep | 0 | Nov | 2021 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
CAGUAS | 2021-11-09 22:49 | 2021-11-10 11:56 | 17 | 013:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C21110900116 | New_Event | Cutout Failure | Include | Include | Equipment | 787 | 2021-11-09 | 13379 | keep | 0 | Nov | 2021 | 0.0091124 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
SAN JUAN | 2021-11-09 23:31 | 2021-11-10 02:37 | 4481 | 003:06 | T | DESCONECTIVO DEFECTUOSO | SE CERRO INTERRUPTOR ABRIENDO MACHETES EN AVENIDA ITURREGUI CASI MARGINAL BALDORIOTY FRENTE A CHINATOWN | S21110900016 | New_Event | Switch Failure | Include | Include | Equipment | 186 | 2021-11-09 | 833466 | keep | 0 | Nov | 2021 | 0.56767 | 0.003052 | Sustained | FALSE | FALSE | Not_TMED_Event | 4481
MAYAGÃœEZ | 2021-11-09 23:50 | 2021-11-10 23:00 | 50 | 023:10 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21110900009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1390 | 2021-11-09 | 69500 | keep | 0 | Nov | 2021 | 0.047336 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-11-10 00:32 | 2021-11-10 09:35 | 20 | 009:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21111000002 | New_Event | Bad Weather | Include | Include | Weather | 543 | 2021-11-10 | 10860 | keep | 0 | Nov | 2021 | 0.0073967 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-11-10 00:36 | 2021-11-10 10:46 | 200 | 010:10 | P | NO SE REPORTO CAUSA | 1 X 200 EN RISER NO CAUSA | R21111000008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 610 | 2021-11-10 | 122000 | keep | 0 | Nov | 2021 | 0.083094 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-11-10 01:33 | 2021-11-10 03:07 | 8 | 001:34 | P | NO SE REPORTO CAUSA | 1 X 5 EN MONTURA DE TRANSFORMADORES | B21111000002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 94 | 2021-11-10 | 752 | keep | 0 | Nov | 2021 | 0.00051218 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-11-10 01:59 | 2021-11-10 02:01 | 1746 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA | B21111000003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-10 | 3492 | keep | 0 | Nov | 2021 | 0.0023784 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
BAYAMON | 2021-11-10 02:01 | 2021-11-10 09:21 | 50 | 007:20 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU-16 | B21111000001 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 440 | 2021-11-10 | 22000 | keep | 0 | Nov | 2021 | 0.014984 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-10 02:08 | 2021-11-10 02:09 | 3070 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21111100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-10 | 3070 | keep | 0 | Nov | 2021 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
SAN JUAN | 2021-11-10 02:37 | 2021-11-10 04:15 | 2592 | 001:38 | P | DESCONECTIVO DEFECTUOSO | REEMPLAZO MACHETE Y AISLADORES | R21111000016 | New_Event | Switch Failure | Include | Include | Equipment | 98 | 2021-11-10 | 254016 | keep | 0 | Nov | 2021 | 0.17301 | 0.0017654 | Sustained | FALSE | FALSE | Not_TMED_Event | 2592
BAYAMON | 2021-11-10 03:07 | 2021-11-10 03:08 | 2605 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1718-03 LLEVA LA CARGA DEL 1710-05 | B21111000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-10 | 2605 | keep | 0 | Nov | 2021 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2021-11-10 03:07 | 2021-11-10 03:08 | 2605 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1718 03 LLEVA PARTE 1710 05 | B21111000000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-10 | 2605 | keep | 0 | Nov | 2021 | 0.0017743 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-10 03:08 | 2021-11-10 09:30 | 8 | 006:22 | P | NO SE REPORTO CAUSA | 1 X 5 EN MONTURA DE TRANSFORMADORES | B21111000002 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 382 | 2021-11-10 | 3056 | keep | 0 | Nov | 2021 | 0.0020814 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-11-10 04:15 | 2021-11-10 04:16 | 4481 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DE INTERRUPTOR AL REALIZAR OPERACIONES PARA LOCALIZAR POSIBLE AVERIA | S21111000016 | Additional_clients | Switch Failure | Include | Include | Equipment | 1 | 2021-11-10 | 4481 | keep | 0 | Nov | 2021 | 0.003052 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-10 04:16 | 2021-11-10 09:21 | 2592 | 005:05 | P | DESCONECTIVO DEFECTUOSO | REEMPLAZO MACHETE Y AISLADORES | R21111000016 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 305 | 2021-11-10 | 790560 | keep | 0 | Nov | 2021 | 0.53845 | 0.0017654 | Sustained | FALSE | FALSE | Not_TMED_Event | 2592
HUMACAO | 2021-11-10 04:21 | 2021-11-10 04:23 | 2126 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C21111000003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-10 | 4252 | keep | 0 | Nov | 2021 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
CANOVANAS | 2021-11-10 04:30 | 2021-11-10 04:31 | 1124 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | R21111000032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-10 | 1124 | keep | 0 | Nov | 2021 | 0.00076555 | 0.00076555 | Momentary | FALSE | FALSE | Not_TMED_Event | 1124
CAGUAS | 2021-11-10 04:51 | 2021-11-10 04:52 | 1742 | 000:01 | T | DESGANCHE | DISPARO 3015-07 SE CERRO POR CONTROL 3015-07 LLEVANDO PARTE 80% DE CARGA DEL 3103-05 | C21111000005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-10 | 1742 | keep | 0 | Nov | 2021 | 0.0011865 | 0.0011865 | Momentary | FALSE | FALSE | Not_TMED_Event | 1742
CAGUAS | 2021-11-10 04:52 | 2021-11-10 04:53 | 500 | 000:01 | P | DESGANCHE | DISPARO 3015-07 SE CERRO POR CONTROL 3015-07 LLEVANDO PARTE 80% DE CARGA DEL 3103-05 | C21111000005 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-10 | 500 | keep | 0 | Nov | 2021 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
AGUADILLA | 2021-11-10 04:52 | 2021-11-10 12:01 | 30 | 007:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA QUEMADA EN EL FID 31495665 MARCA CHINT DE 100AMP | M21111000001 | New_Event | Cutout Failure | Include | Include | Equipment | 429 | 2021-11-10 | 12870 | keep | 0 | Nov | 2021 | 0.0087657 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-11-10 04:53 | 2021-11-10 06:50 | 1742 | 001:57 | T | DESGANCHE | DISPARO 3015-07 SE CERRO POR CONTROL 3015-07 LLEVANDO PARTE 80% DE CARGA DEL 3103-05 SE RETIRO RAMA DE LA LINEA CERRADO POR CONTROL | C21111000005 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 117 | 2021-11-10 | 203814 | keep | 0 | Nov | 2021 | 0.13882 | 0.0011865 | Sustained | FALSE | FALSE | Not_TMED_Event | 1742
BAYAMON | 2021-11-10 05:22 | 2021-11-10 11:02 | 40 | 005:40 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21111000002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 340 | 2021-11-10 | 13600 | keep | 0 | Nov | 2021 | 0.0092629 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-10 07:37 | 2021-11-10 09:46 | 60 | 002:09 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21111000008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 129 | 2021-11-10 | 7740 | keep | 0 | Nov | 2021 | 0.0052717 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-11-10 07:47 | 2021-11-10 10:00 | 100 | 002:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | A21111000009 | New_Event | Cutout Failure | Include | Include | Equipment | 133 | 2021-11-10 | 13300 | keep | 0 | Nov | 2021 | 0.0090586 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2021-11-10 08:02 | 2021-11-10 08:03 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21111000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-10 | 1310 | keep | 0 | Nov | 2021 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
CANOVANAS | 2021-11-10 08:08 | 2021-11-10 08:09 | 2708 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21111000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-10 | 2708 | keep | 0 | Nov | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
MAYAGÃœEZ | 2021-11-10 08:19 | 2021-11-10 10:37 | 100 | 002:18 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA EL JOURNEYMAN INFORMO QUE NO ENCONTRO CAUSA DE AVERIA | M21111000009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 138 | 2021-11-10 | 13800 | keep | 0 | Nov | 2021 | 0.0093991 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-11-10 08:30 | 2021-11-10 13:19 | 8 | 004:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C21111000024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 289 | 2021-11-10 | 2312 | keep | 0 | Nov | 2021 | 0.0015747 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2021-11-10 08:31 | 2021-11-10 12:16 | 50 | 003:45 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21111000070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2021-11-10 | 11250 | keep | 0 | Nov | 2021 | 0.0076623 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-11-10 08:33 | 2021-11-10 08:34 | 143 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1404-06 CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 80% 1404-07 | S21111000011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-10 | 143 | keep | 0 | Nov | 2021 | 9.7397e-05 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
BAYAMON | 2021-11-10 08:37 | 2021-11-10 11:36 | 30 | 002:59 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN PROVISIONAL AEREO SE REMPLAZO AISLADOR | B21111000016 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 179 | 2021-11-10 | 5370 | keep | 0 | Nov | 2021 | 0.0036575 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-11-10 08:37 | 2021-11-10 10:36 | 8 | 001:59 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S21111000012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 119 | 2021-11-10 | 952 | keep | 0 | Nov | 2021 | 0.0006484 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-11-10 08:39 | 2021-11-10 09:34 | 10 | 000:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BARRAS EN PEDESTAL | B21111000017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 55 | 2021-11-10 | 550 | keep | 0 | Nov | 2021 | 0.0003746 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-10 09:03 | 2021-11-10 10:57 | 60 | 001:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA QUEMADA MARCA CHINT DE 100AMP | A21111000015 | New_Event | Cutout Failure | Include | Include | Equipment | 114 | 2021-11-10 | 6840 | keep | 0 | Nov | 2021 | 0.0046587 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-11-10 09:07 | 2021-11-10 09:35 | 130 | 000:28 | P | LINEA DE TRANSMISION 115KV | 20% DE LA CARGA TRANSFERIDA AL 1717-04 | B21111000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-11-10 | 3640 | keep | 0 | Nov | 2021 | 0.0024792 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
BAYAMON | 2021-11-10 09:07 | 2021-11-10 09:35 | 3533 | 000:28 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 | B21111000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-11-10 | 98924 | keep | 0 | Nov | 2021 | 0.067377 | 0.0024063 | Sustained | FALSE | FALSE | Not_TMED_Event | 3533
BAYAMON | 2021-11-10 09:07 | 2021-11-10 09:35 | 75 | 000:28 | P | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 95% DE ESTA CARGA TRANSFERIDA AL 1713-05 | B21111000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-11-10 | 2100 | keep | 0 | Nov | 2021 | 0.0014303 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2021-11-10 09:07 | 2021-11-10 09:35 | 4431 | 000:28 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 | B21111000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-11-10 | 124068 | keep | 0 | Nov | 2021 | 0.084502 | 0.0030179 | Sustained | FALSE | FALSE | Not_TMED_Event | 4431
BAYAMON | 2021-11-10 09:07 | 2021-11-10 09:35 | 1362 | 000:28 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 | B21111000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-11-10 | 38136 | keep | 0 | Nov | 2021 | 0.025974 | 0.00092765 | Sustained | FALSE | FALSE | Not_TMED_Event | 1362
BAYAMON | 2021-11-10 09:07 | 2021-11-10 09:35 | 341 | 000:28 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 | B21111000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-11-10 | 9548 | keep | 0 | Nov | 2021 | 0.0065031 | 0.00023225 | Sustained | FALSE | FALSE | Not_TMED_Event | 341
MAYAGÃœEZ | 2021-11-10 09:07 | 2021-11-10 16:55 | 10 | 007:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES SECUNDARIAS | M21111000021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 468 | 2021-11-10 | 4680 | keep | 0 | Nov | 2021 | 0.0031875 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-11-10 09:18 | 2021-11-10 16:39 | 1 | 007:21 | P | NO SE REPORTO CAUSA | 2 X 15 EN BANCO DE XMRS NO CAUSA | C21111000027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 441 | 2021-11-10 | 441 | keep | 0 | Nov | 2021 | 0.00030036 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-10 09:21 | 2021-11-10 09:57 | 6481 | 000:36 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR REALIZANDO MANIOBRAS LADO CAROLINA SE COORDINO CON COD CAGUAS Y SE CERRO | S21111000000 | Additional_clients | Switch Failure | Include | Include | Equipment | 36 | 2021-11-10 | 233316 | keep | 0 | Nov | 2021 | 0.15891 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2021-11-10 09:41 | 2021-11-10 11:49 | 40 | 002:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA CONTAMINACION EN CAJA PRIMARIA POR SALITRE | R21111000098 | New_Event | Cutout Failure | Include | Include | Equipment | 128 | 2021-11-10 | 5120 | keep | 0 | Nov | 2021 | 0.0034872 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-11-10 09:47 | 2021-11-10 11:15 | 100 | 001:28 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | R21111000104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 88 | 2021-11-10 | 8800 | keep | 0 | Nov | 2021 | 0.0059936 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-11-10 09:49 | 2021-11-10 12:05 | 12 | 002:16 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M21111000029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2021-11-10 | 1632 | keep | 0 | Nov | 2021 | 0.0011115 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2021-11-10 09:50 | 2021-11-10 12:28 | 55 | 002:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | P21111000007 | New_Event |  |  | Include | Wildlife | 158 | 2021-11-10 | 8690 | keep | 0 | Nov | 2021 | 0.0059187 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
SAN JUAN | 2021-11-10 09:57 | 2021-11-10 10:32 | 2592 | 000:35 | P | DESCONECTIVO DEFECTUOSO | REEMPLAZO MACHETE Y AISLADORES | R21111000016 | Partial_restoration | Switch Failure | Include | Include | Equipment | 35 | 2021-11-10 | 90720 | keep | 0 | Nov | 2021 | 0.061789 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2021-11-10 10:08 | 2021-11-10 11:06 | 6 | 000:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE LINEA A XMR | R21111000126 | New_Event | Wire Down | Include | Include | Equipment | 58 | 2021-11-10 | 348 | keep | 0 | Nov | 2021 | 0.00023702 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-11-10 10:14 | 2021-11-10 13:45 | 35 | 003:31 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21111000013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2021-11-10 | 7385 | keep | 0 | Nov | 2021 | 0.0050299 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2021-11-10 10:27 | 2021-11-10 19:02 | 7 | 008:35 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 37.5 KVA X 37.5 KVA | R21111000128 | New_Event | Service Transformer Failure | Include | Include | Equipment | 515 | 2021-11-10 | 3605 | keep | 0 | Nov | 2021 | 0.0024553 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-11-10 10:32 | 2021-11-10 10:45 | 4481 | 000:13 | T | DESCONECTIVO DEFECTUOSO | DISPARO PERSONAL CAROLINA REALIZANDO MANIOBRAS | S21111000016 | New_Event | Switch Failure | Include | Include | Equipment | 13 | 2021-11-10 | 58253 | keep | 0 | Nov | 2021 | 0.039676 | 0.003052 | Sustained | FALSE | FALSE | Not_TMED_Event | 4481
SAN JUAN | 2021-11-10 10:41 | 2021-11-10 10:42 | 1085 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1404-06 CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 80% 1404-07 | S21111000011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-10 | 1085 | keep | 0 | Nov | 2021 | 0.00073899 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
VEGA BAJA | 2021-11-10 10:43 | 2021-11-10 14:37 | 30 | 003:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21111000080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 234 | 2021-11-10 | 7020 | keep | 0 | Nov | 2021 | 0.0047813 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-11-10 10:45 | 2021-11-10 11:42 | 2592 | 000:57 | P | DESCONECTIVO DEFECTUOSO | REEMPLAZO MACHETE Y AISLADORES | R21111000016 | Partial_restoration | Switch Failure | Include | Include | Equipment | 57 | 2021-11-10 | 147744 | keep | 0 | Nov | 2021 | 0.10063 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2021-11-10 10:45 | 2021-11-10 18:50 | 9 | 008:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR CONEXIONES EN LINEA SECUNDARIA | P21111000025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 485 | 2021-11-10 | 4365 | keep | 0 | Nov | 2021 | 0.002973 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2021-11-10 10:53 | 2021-11-10 20:43 | 40 | 009:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR FUERTES LLUVIAS | M21111000038 | New_Event | Bad Weather | Include | Include | Weather | 590 | 2021-11-10 | 23600 | keep | 0 | Nov | 2021 | 0.016074 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-10 11:00 | 2021-11-10 12:04 | 1 | 001:04 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21111000081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2021-11-10 | 64 | keep | 0 | Nov | 2021 | 4.359e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-11-10 11:00 | 2021-11-10 16:26 | 60 | 005:26 | P | DESGANCHE | 1 X 30 Y 1 X 40 EN C/L DESGANCHO Y RETEZO LINEAS | C21111000038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 326 | 2021-11-10 | 19560 | keep | 0 | Nov | 2021 | 0.013322 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-11-10 11:19 | 2021-11-10 11:20 | 81 | 000:01 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | R21111000033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-10 | 81 | keep | 0 | Nov | 2021 | 5.5169e-05 | 5.5169e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 81
ARECIBO | 2021-11-10 11:30 | 2021-11-10 18:37 | 17 | 007:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | A21110900030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 427 | 2021-11-10 | 7259 | keep | 0 | Nov | 2021 | 0.0049441 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
HUMACAO | 2021-11-10 11:33 | 2021-11-10 16:28 | 6 | 004:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | C21111000042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 295 | 2021-11-10 | 1770 | keep | 0 | Nov | 2021 | 0.0012055 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-11-10 11:33 | 2021-11-10 13:39 | 1650 | 002:06 | T | DESGANCHE | DISPARO DE ALIMENTADOR | P21111000036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2021-11-10 | 207900 | keep | 0 | Nov | 2021 | 0.1416 | 0.0011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 1650
PONCE | 2021-11-10 11:35 | 2021-11-11 10:30 | 40 | 022:55 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU-1 NO SE ENCONTRO CAUSA | P21111000080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1375 | 2021-11-10 | 55000 | keep | 0 | Nov | 2021 | 0.03746 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2021-11-10 11:39 | 2021-11-10 14:50 | 15 | 003:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA PARTIDA | M21111000043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 191 | 2021-11-10 | 2865 | keep | 0 | Nov | 2021 | 0.0019513 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-11-10 11:39 | 2021-11-10 12:17 | 10 | 000:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21111000004 | New_Event | Secondary Wire Down | Include | Include | Equipment | 38 | 2021-11-10 | 380 | keep | 0 | Nov | 2021 | 0.00025882 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-11-10 11:42 | 2021-11-10 11:46 | 4481 | 000:04 | T | DESCONECTIVO DEFECTUOSO | DISPARO PERSONAL CAROLINA REALIZANDO MANIOBRAS SE REMPLAZO AISLACION Y MACHETES CARR.190 KM.0.2 LOS ANGELES | S21111000016 | Additional_clients | Switch Failure | Include | Include | Equipment | 4 | 2021-11-10 | 17924 | keep | 0 | Nov | 2021 | 0.012208 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-10 11:44 | 2021-11-11 13:41 | 10 | 025:57 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 75KV CON ALTO VOLTAJE. NO SE PODIA BAJAR TAPS | B21111000083 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1557 | 2021-11-10 | 15570 | keep | 0 | Nov | 2021 | 0.010605 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-11-10 11:46 | 2021-11-10 12:13 | 2592 | 000:27 | P | DESCONECTIVO DEFECTUOSO | REEMPLAZO MACHETE Y AISLADORES | R21111000016 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 27 | 2021-11-10 | 69984 | keep | 0 | Nov | 2021 | 0.047666 | 0.0017654 | Sustained | FALSE | FALSE | Not_TMED_Event | 2592
CAGUAS | 2021-11-10 11:50 | 2021-11-10 15:25 | 80 | 003:35 | P | DESGANCHE | 1 X 80 EN C/L | C21111000043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2021-11-10 | 17200 | keep | 0 | Nov | 2021 | 0.011715 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2021-11-10 11:50 | 2021-11-10 18:29 | 100 | 006:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO DE LINEA A CAJA DE CORTE DE LINEA | A21111000032 | New_Event | Wire Down | Include | Include | Equipment | 399 | 2021-11-10 | 39900 | keep | 0 | Nov | 2021 | 0.027176 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2021-11-10 11:55 | 2021-11-10 20:30 | 20 | 008:35 | P | DESGANCHE | 1 X 30 EN CONVERTIDOR SE RETIRO RAMA | A21111000033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 515 | 2021-11-10 | 10300 | keep | 0 | Nov | 2021 | 0.0070153 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-11-10 11:56 | 2021-11-10 11:57 | 4390 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 9300 DE JUNCOS A SAN LORENZO | C21111000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-10 | 4390 | keep | 0 | Nov | 2021 | 0.00299 | 0.00299 | Momentary | FALSE | FALSE | Not_TMED_Event | 4390
CAGUAS | 2021-11-10 11:56 | 2021-11-10 11:57 | 2092 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 9300 DE JUNCOS A SAN LORENZO | C21111000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-10 | 2092 | keep | 0 | Nov | 2021 | 0.0014249 | 0.0014249 | Momentary | FALSE | FALSE | Not_TMED_Event | 2092
CAGUAS | 2021-11-10 11:56 | 2021-11-10 11:57 | 540 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 9300 DE JUNCOS A SAN LORENZO | C21111000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-10 | 540 | keep | 0 | Nov | 2021 | 0.00036779 | 0.00036779 | Momentary | FALSE | FALSE | Not_TMED_Event | 540
CAGUAS | 2021-11-10 11:56 | 2021-11-10 11:57 | 131 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 9300 DE JUNCOS A SAN LORENZO | C21111000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-10 | 131 | keep | 0 | Nov | 2021 | 8.9224e-05 | 8.9224e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 131
CAGUAS | 2021-11-10 11:56 | 2021-11-10 11:57 | 2281 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 9300 DE JUNCOS A SAN LORENZO | C21111000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-10 | 2281 | keep | 0 | Nov | 2021 | 0.0015536 | 0.0015536 | Momentary | FALSE | FALSE | Not_TMED_Event | 2281
CAGUAS | 2021-11-10 11:56 | 2021-11-10 11:57 | 1569 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 9300 DE JUNCOS A SAN LORENZO | C21111000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-10 | 1569 | keep | 0 | Nov | 2021 | 0.0010686 | 0.0010686 | Momentary | FALSE | FALSE | Not_TMED_Event | 1569
CAGUAS | 2021-11-10 11:56 | 2021-11-10 11:57 | 2417 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 9300 DE JUNCOS A SAN LORENZO | C21111000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-10 | 2417 | keep | 0 | Nov | 2021 | 0.0016462 | 0.0016462 | Momentary | FALSE | FALSE | Not_TMED_Event | 2417
CAGUAS | 2021-11-10 11:57 | 2021-11-10 13:33 | 17 | 001:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C21110900116 | New_Event | Cutout Failure | Include | Include | Equipment | 96 | 2021-11-10 | 1632 | keep | 0 | Nov | 2021 | 0.0011115 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BARRANQUITAS | 2021-11-10 12:24 | 2021-11-10 14:30 | 6 | 002:06 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 37.5 KVA X 37.5 KVA | C21111000048 | New_Event | Service Transformer Failure | Include | Include | Equipment | 126 | 2021-11-10 | 756 | keep | 0 | Nov | 2021 | 0.00051491 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2021-11-10 12:47 | 2021-11-10 17:27 | 30 | 004:40 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | M21111000046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2021-11-10 | 8400 | keep | 0 | Nov | 2021 | 0.0057212 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-11-10 13:33 | 2021-11-10 14:15 | 10 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21111000082 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2021-11-10 | 420 | keep | 0 | Nov | 2021 | 0.00028606 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-11-10 13:39 | 2021-11-10 16:44 | 57 | 003:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21111000048 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 185 | 2021-11-10 | 10545 | keep | 0 | Nov | 2021 | 0.0071822 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-11-10 14:10 | 2021-11-10 22:19 | 50 | 008:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21111000107 | New_Event | Bad Weather | Include | Include | Weather | 489 | 2021-11-10 | 24450 | keep | 0 | Nov | 2021 | 0.016653 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-10 14:24 | 2021-11-10 15:10 | 75 | 000:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | S21111000065 | New_Event | Cutout Failure | Include | Include | Equipment | 46 | 2021-11-10 | 3450 | keep | 0 | Nov | 2021 | 0.0023498 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CANOVANAS | 2021-11-10 14:33 | 2021-11-10 16:48 | 100 | 002:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L REMPLAZO CAJA QUEMADA | R21111000178 | New_Event | Cutout Failure | Include | Include | Equipment | 135 | 2021-11-10 | 13500 | keep | 0 | Nov | 2021 | 0.0091948 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-10 14:45 | 2021-11-10 17:40 | 15 | 002:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | A21111000049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 175 | 2021-11-10 | 2625 | keep | 0 | Nov | 2021 | 0.0017879 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-11-10 14:49 | 2021-11-10 16:37 | 40 | 001:48 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21111000099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 108 | 2021-11-10 | 4320 | keep | 0 | Nov | 2021 | 0.0029423 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-10 14:59 | 2021-11-10 15:00 | 3438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21111000101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-10 | 3438 | keep | 0 | Nov | 2021 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
ARECIBO | 2021-11-10 15:10 | 2021-11-10 16:10 | 12 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | A21111000024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2021-11-10 | 720 | keep | 0 | Nov | 2021 | 0.00049039 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-11-10 15:15 | 2021-11-11 13:28 | 6 | 022:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR NEUTRAL SECUNDARIO | C21111000059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1333 | 2021-11-10 | 7998 | keep | 0 | Nov | 2021 | 0.0054474 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-11-10 15:20 | 2021-11-10 21:29 | 28 | 006:09 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO PM AVERIADO DE 75 KVA X 100 KVA | A21111000050 | New_Event | Service Transformer Failure | Include | Include | Equipment | 369 | 2021-11-10 | 10332 | keep | 0 | Nov | 2021 | 0.0070371 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
SAN JUAN | 2021-11-10 15:29 | 2021-11-10 22:35 | 5 | 007:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 25 EN CORTE DE LINEA Y 1 X20 EN MONTURA DE TRANSFORMADOR SE REPARO BAJANTE SECUNDARIO EN MONTURA DE TRANSFOMADOR | S21111000072 | New_Event | Secondary Wire Down | Include | Include | Equipment | 426 | 2021-11-10 | 2130 | keep | 0 | Nov | 2021 | 0.0014507 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-11-10 15:31 | 2021-11-10 17:28 | 5 | 001:57 | P | PARARRAYOS DEFECTUOSO | 1 X 20 EN TRANSFORMADOR PARARRAYO SUELTO OCACIONA CRUCE DE FASE A TIERRA | P21111000056 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 117 | 2021-11-10 | 585 | keep | 0 | Nov | 2021 | 0.00039844 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-11-10 15:41 | 2021-11-10 16:22 | 75 | 000:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA PALOMA CRUZO FASE | P21111000058 | New_Event |  |  | Include | Wildlife | 41 | 2021-11-10 | 3075 | keep | 0 | Nov | 2021 | 0.0020944 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2021-11-10 15:58 | 2021-11-10 16:26 | 5 | 000:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C21111000062 | New_Event | Secondary Wire Down | Include | Include | Equipment | 28 | 2021-11-10 | 140 | keep | 0 | Nov | 2021 | 9.5353e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-11-10 16:30 | 2021-11-10 19:36 | 30 | 003:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR FUERTES LLUVIAS | M21111000070 | New_Event | Bad Weather | Include | Include | Weather | 186 | 2021-11-10 | 5580 | keep | 0 | Nov | 2021 | 0.0038005 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-11-10 16:34 | 2021-11-10 17:44 | 30 | 001:10 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21111000057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2021-11-10 | 2100 | keep | 0 | Nov | 2021 | 0.0014303 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-11-10 16:43 | 2021-11-10 18:52 | 50 | 002:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR FUERTES LLUVIAS | M21111000071 | New_Event | Bad Weather | Include | Include | Weather | 129 | 2021-11-10 | 6450 | keep | 0 | Nov | 2021 | 0.0043931 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-11-10 16:51 | 2021-11-10 16:54 | 1483 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1336-08 CARGA 30% POR EL 1336-08 | S21111000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-10 | 4449 | keep | 0 | Nov | 2021 | 0.0030302 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2021-11-10 16:51 | 2021-11-11 16:54 | 1483 | 024:03 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1336-08 LLEVANDO CARGA 1336-09 Y 30% DEL 1204-04 | S21111000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1443 | 2021-11-10 | 2139969 | keep | 0 | Nov | 2021 | 1.4575 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2021-11-10 16:51 | 2021-11-10 16:54 | 207 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1336 08 LLEVANDO CARGA 1336 09 Y PARTE 1204 04 | S21111000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-10 | 621 | keep | 0 | Nov | 2021 | 0.00042296 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
BAYAMON | 2021-11-10 16:55 | 2021-11-10 18:00 | 15 | 001:05 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21111000105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 65 | 2021-11-10 | 975 | keep | 0 | Nov | 2021 | 0.00066407 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-11-10 17:01 | 2021-11-10 18:14 | 24 | 001:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21111000066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 73 | 2021-11-10 | 1752 | keep | 0 | Nov | 2021 | 0.0011933 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
HUMACAO | 2021-11-10 17:18 | 2021-11-11 12:34 | 5 | 019:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR NEUTRAL SECUNDARIO | C21111000066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1156 | 2021-11-10 | 5780 | keep | 0 | Nov | 2021 | 0.0039367 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-11-10 17:18 | 2021-11-10 17:19 | 2067 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21111000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-10 | 2067 | keep | 0 | Nov | 2021 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
MAYAGÃœEZ | 2021-11-10 17:28 | 2021-11-10 19:47 | 80 | 002:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR FUERTES LLUVIAS | M21111000075 | New_Event | Bad Weather | Include | Include | Weather | 139 | 2021-11-10 | 11120 | keep | 0 | Nov | 2021 | 0.0075738 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2021-11-10 17:36 | 2021-11-10 20:24 | 85 | 002:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L CRUCE POR AVE | R21111000181 | New_Event |  |  | Include | Wildlife | 168 | 2021-11-10 | 14280 | keep | 0 | Nov | 2021 | 0.009726 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
AGUADILLA | 2021-11-10 17:52 | 2021-11-10 18:39 | 1 | 000:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA POR FUERTES LLUVIAS | M21111000079 | New_Event | Bad Weather | Include | Include | Weather | 47 | 2021-11-10 | 47 | keep | 0 | Nov | 2021 | 3.2011e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-11-10 18:14 | 2021-11-10 18:15 | 1979 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21111000064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-10 | 1979 | keep | 0 | Nov | 2021 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
BAYAMON | 2021-11-10 18:16 | 2021-11-10 21:43 | 60 | 003:27 | P | DESGANCHE | 1 X 65 Y 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21111000109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2021-11-10 | 12420 | keep | 0 | Nov | 2021 | 0.0084592 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2021-11-10 18:25 | 2021-11-11 10:38 | 40 | 016:13 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO CAUSA | C21111000070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 973 | 2021-11-10 | 38920 | keep | 0 | Nov | 2021 | 0.026508 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-11-10 18:26 | 2021-11-10 18:27 | 3157 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA REPARAR BAJANTE ZAFADO SOBRE CRUCETA | A21111000000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-10 | 3157 | keep | 0 | Nov | 2021 | 0.0021502 | 0.0021502 | Momentary | FALSE | FALSE | Not_TMED_Event | 3157
UTUADO | 2021-11-10 18:29 | 2021-11-10 19:46 | 6 | 001:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA LUEGO DE RAPARADO EL BAJANTE SE ENCONTRO PROBLEMAS EN LA SECUNDARIA | A21111000032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 77 | 2021-11-10 | 462 | keep | 0 | Nov | 2021 | 0.00031467 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-11-10 18:33 | 2021-11-11 14:13 | 10 | 019:40 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21111000066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1180 | 2021-11-10 | 11800 | keep | 0 | Nov | 2021 | 0.0080369 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-10 18:33 | 2021-11-11 15:39 | 2 | 021:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21111000068 | New_Event | Bad Weather | Include | Include | Weather | 1266 | 2021-11-10 | 2532 | keep | 0 | Nov | 2021 | 0.0017245 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
GUAYAMA | 2021-11-10 18:45 | 2021-11-10 19:50 | 12 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR CONEXIONES EN LINEA SECUNDARIA | P21111000067 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2021-11-10 | 780 | keep | 0 | Nov | 2021 | 0.00053125 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-11-10 18:47 | 2021-11-10 19:52 | 12 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21111000107 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2021-11-10 | 780 | keep | 0 | Nov | 2021 | 0.00053125 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-11-10 19:13 | 2021-11-10 21:45 | 50 | 002:32 | P | DESGANCHE | 1 X 50 EN C/L | R21111000184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2021-11-10 | 7600 | keep | 0 | Nov | 2021 | 0.0051763 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-10 19:47 | 2021-11-11 10:05 | 10 | 014:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21111000092 | New_Event | Bad Weather | Include | Include | Weather | 858 | 2021-11-10 | 8580 | keep | 0 | Nov | 2021 | 0.0058438 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-10 20:00 | 2021-11-10 21:33 | 1000 | 001:33 | P | DESCONECTIVO DEFECTUOSO | MACHETE QUEMADO EN SALIDA DE INTERRUPTOR 8504-02 | A21111000074 | New_Event | Switch Failure | Include | Include | Equipment | 93 | 2021-11-10 | 93000 | keep | 0 | Nov | 2021 | 0.063342 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
MAYAGÃœEZ | 2021-11-10 20:42 | 2021-11-10 20:43 | 4381 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21111000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-10 | 4381 | keep | 0 | Nov | 2021 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
AGUADILLA | 2021-11-10 21:13 | 2021-11-11 13:45 | 10 | 016:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 8 EN TRANSFORMADOR SE REPARO LINEAS SECUNDARIAS CRUZADAS | M21111000100 | New_Event | Secondary Wire Down | Include | Include | Equipment | 992 | 2021-11-10 | 9920 | keep | 0 | Nov | 2021 | 0.0067565 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-11-10 21:18 | 2021-11-10 23:14 | 181 | 001:56 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | R21111000185 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2021-11-10 | 20996 | keep | 0 | Nov | 2021 | 0.0143 | 0.00012328 | Sustained | FALSE | FALSE | Not_TMED_Event | 181
GUAYAMA | 2021-11-10 21:21 | 2021-11-11 00:15 | 100 | 002:54 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | P21111000073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2021-11-10 | 17400 | keep | 0 | Nov | 2021 | 0.011851 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-10 21:33 | 2021-11-11 00:22 | 2839 | 002:49 | S | DESCONECTIVO DEFECTUOSO | SE REEMPLAZARON MACHETES DEL BKR 8504-01 Y DEL 8504-02 QUEMADOS | A21111000000 | New_Event | Switch Failure | Include | Include | Equipment | 169 | 2021-11-10 | 479791 | keep | 0 | Nov | 2021 | 0.32678 | 0.0019336 | Sustained | FALSE | FALSE | Not_TMED_Event | 2839
ARECIBO | 2021-11-10 21:33 | 2021-11-11 00:22 | 1160 | 002:49 | S | DESCONECTIVO DEFECTUOSO | SE REEMPLAZARON MACHETES DEL BKR 8504-01 Y DEL 8504-02 QUEMADOS | A21111000000 | Additional_clients | Switch Failure | Include | Include | Equipment | 169 | 2021-11-10 | 196040 | keep | 0 | Nov | 2021 | 0.13352 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-11-10 21:33 | 2021-11-11 00:22 | 1860 | 002:49 | S | DESCONECTIVO DEFECTUOSO | SE REEMPLAZARON MACHETES DEL BKR 8504-01 Y DEL 8504-02 QUEMADOS | A21111000000 | New_Event | Switch Failure | Include | Include | Equipment | 169 | 2021-11-10 | 314340 | keep | 0 | Nov | 2021 | 0.2141 | 0.0012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 1860
ARECIBO | 2021-11-10 21:38 | 2021-11-11 02:28 | 13 | 004:50 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | A21111000062 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 290 | 2021-11-10 | 3770 | keep | 0 | Nov | 2021 | 0.0025677 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
GUAYAMA | 2021-11-10 22:03 | 2021-11-11 11:31 | 171 | 013:28 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | P21111000075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 808 | 2021-11-10 | 138168 | keep | 0 | Nov | 2021 | 0.094106 | 0.00011647 | Sustained | FALSE | FALSE | Not_TMED_Event | 171
CAGUAS | 2021-11-10 22:28 | 2021-11-11 11:47 | 40 | 013:19 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | C21111000075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 799 | 2021-11-10 | 31960 | keep | 0 | Nov | 2021 | 0.021768 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-11-11 02:09 | 2021-11-11 10:35 | 50 | 008:26 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21111100002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 506 | 2021-11-11 | 25300 | keep | 0 | Nov | 2021 | 0.017232 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-11-11 02:28 | 2021-11-11 02:29 | 1541 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13700 | A21111100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-11 | 1541 | keep | 0 | Nov | 2021 | 0.0010496 | 0.0010496 | Momentary | FALSE | FALSE | Not_TMED_Event | 1541
ARECIBO | 2021-11-11 02:28 | 2021-11-11 02:29 | 307 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13700 | A21111100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-11 | 307 | keep | 0 | Nov | 2021 | 0.0002091 | 0.0002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 307
ARECIBO | 2021-11-11 02:28 | 2021-11-11 02:29 | 1277 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13700 | A21111100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-11 | 1277 | keep | 0 | Nov | 2021 | 0.00086976 | 0.00086976 | Momentary | FALSE | FALSE | Not_TMED_Event | 1277
ARECIBO | 2021-11-11 02:28 | 2021-11-11 02:29 | 1644 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13700 | A21111100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-11 | 1644 | keep | 0 | Nov | 2021 | 0.0011197 | 0.0011197 | Momentary | FALSE | FALSE | Not_TMED_Event | 1644
ARECIBO | 2021-11-11 02:28 | 2021-11-11 02:29 | 1831 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13700 | A21111100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-11 | 1831 | keep | 0 | Nov | 2021 | 0.0012471 | 0.0012471 | Momentary | FALSE | FALSE | Not_TMED_Event | 1831
ARECIBO | 2021-11-11 02:29 | 2021-11-12 14:50 | 13 | 036:21 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | A21111100062 | Partial_restoration | Secondary Vegetation | Include | Include | Vegetation | 2181 | 2021-11-11 | 28353 | keep | 0 | Nov | 2021 | 0.019311 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-11-11 03:48 | 2021-11-11 14:34 | 100 | 010:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE REPARO BAJANTE DE CORTE DE LINEA | M21111100002 | New_Event | Wire Down | Include | Include | Equipment | 646 | 2021-11-11 | 64600 | keep | 0 | Nov | 2021 | 0.043999 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-11 04:38 | 2021-11-11 07:21 | 100 | 002:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS ABIERTOS | A21111100001 | New_Event | Wire Down | Include | Include | Equipment | 163 | 2021-11-11 | 16300 | keep | 0 | Nov | 2021 | 0.011102 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-11-11 05:08 | 2021-11-11 11:57 | 80 | 006:49 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE GENERO GOI BY-211111-01 PARA REALIZAR DESGANCHE | B21111100003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 409 | 2021-11-11 | 32720 | keep | 0 | Nov | 2021 | 0.022285 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-11-11 05:29 | 2021-11-11 10:14 | 2466 | 004:45 | T | NO SE REPORTO CAUSA | INTERRUPTOR DISPARO Y SE CERRO POR CONTROL NO HABIA RTU EN LA SUBESTACION | S21111100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 285 | 2021-11-11 | 702810 | keep | 0 | Nov | 2021 | 0.47868 | 0.0016796 | Sustained | FALSE | FALSE | Not_TMED_Event | 2466
HUMACAO | 2021-11-11 05:35 | 2021-11-11 10:12 | 80 | 004:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L REMPLAZO CAJA QUEMADA | C21111100009 | New_Event | Cutout Failure | Include | Include | Equipment | 277 | 2021-11-11 | 22160 | keep | 0 | Nov | 2021 | 0.015093 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2021-11-11 06:16 | 2021-11-11 06:17 | 2468 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21111100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-11 | 2468 | keep | 0 | Nov | 2021 | 0.0016809 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
VEGA BAJA | 2021-11-11 06:27 | 2021-11-11 13:40 | 50 | 007:13 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZARON DOS AISLADORES | B21111100006 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 433 | 2021-11-11 | 21650 | keep | 0 | Nov | 2021 | 0.014746 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-11 06:39 | 2021-11-11 09:02 | 60 | 002:23 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21111100008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 143 | 2021-11-11 | 8580 | keep | 0 | Nov | 2021 | 0.0058438 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2021-11-11 06:43 | 2021-11-11 11:39 | 200 | 004:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 80 EN RISER CRUCE DE FASES PRIMARIAS POR ROHEDOR | P21111100004 | New_Event |  |  | Include | Wildlife | 296 | 2021-11-11 | 59200 | keep | 0 | Nov | 2021 | 0.040321 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-11-11 07:06 | 2021-11-11 07:08 | 1681 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-04 QUE A SU VEZ LA CARGA DE LOS ALIMENTADORES 1303-01 Y 1346-06 SE PROBO POR CONTROL QUEDO EN SERVICIO. 1303-04 NO ESTUVO FUERA PARA ESTE PERIODO YA QUE LA CARGA ESTA TRANSFERIDA A OTRO INTERRUPTOR | S21111100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-11 | 3362 | keep | 0 | Nov | 2021 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-11-11 07:06 | 2021-11-11 07:08 | 225 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 QUE A SU VEZ LLEVA 1303-4 SE PROBO POR CONTROL QUEDO EN SERVICIO | S21111100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-11 | 450 | keep | 0 | Nov | 2021 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-11-11 07:06 | 2021-11-11 07:08 | 870 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 QUE A SU VEZ LLEVA 1303-4 SE PROBO POR CONTROL QUEDO EN SERVICIO | S21111100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-11 | 1740 | keep | 0 | Nov | 2021 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2021-11-11 07:06 | 2021-11-11 07:08 | 1598 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-04 QUE A SU VEZ LA CARGA DE LOS ALIMENTADORES 1303-01 Y 1346-06 SE PROBO POR CONTROL QUEDO EN SERVICIO. 1303-04 NO ESTUVO FUERA PARA ESTE PERIODO YA QUE LA CARGA ESTA TRANSFERIDA A OTRO INTERRUPTOR | S21111100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-11 | 3196 | keep | 0 | Nov | 2021 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2021-11-11 07:08 | 2021-11-11 07:09 | 225 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 QUE A SU VEZ LLEVA 1303-4 SE PROBO POR CONTROL QUEDO EN SERVICIO | S21111100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-11 | 225 | keep | 0 | Nov | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-11-11 07:08 | 2021-11-11 07:09 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 QUE A SU VEZ LLEVA 1303-4 SE PROBO POR CONTROL QUEDO EN SERVICIO | S21111100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-11 | 870 | keep | 0 | Nov | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
MAYAGÃœEZ | 2021-11-11 07:11 | 2021-11-11 10:45 | 50 | 003:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA POR LINEA CRUZADA | M21111100004 | New_Event | Wire Down | Include | Include | Equipment | 214 | 2021-11-11 | 10700 | keep | 0 | Nov | 2021 | 0.0072877 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-11-11 07:13 | 2021-11-11 10:48 | 20 | 003:35 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | R21111100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 215 | 2021-11-11 | 4300 | keep | 0 | Nov | 2021 | 0.0029287 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-11-11 07:21 | 2021-11-11 07:22 | 4607 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR PUENTES PRIMARIOS ABIERTOS | A21111100002 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2021-11-11 | 4607 | keep | 0 | Nov | 2021 | 0.0031378 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-11-11 07:22 | 2021-11-11 12:18 | 100 | 004:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS ABIERTOS | A21111100001 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 296 | 2021-11-11 | 29600 | keep | 0 | Nov | 2021 | 0.02016 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-11-11 07:24 | 2021-11-11 17:23 | 10 | 009:59 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 25KVA AVERIADO SE DESGANCHO Y SE REPARO SECUNDARIA | B21111100011 | New_Event | Service Transformer Failure | Include | Include | Equipment | 599 | 2021-11-11 | 5990 | keep | 0 | Nov | 2021 | 0.0040798 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-11 07:30 | 2021-11-11 10:41 | 80 | 003:11 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21111100012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 191 | 2021-11-11 | 15280 | keep | 0 | Nov | 2021 | 0.010407 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2021-11-11 07:42 | 2021-11-11 12:53 | 10 | 005:11 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR JOURNEYMAN NO ENCONTRO CAUSA | A21111100003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 311 | 2021-11-11 | 3110 | keep | 0 | Nov | 2021 | 0.0021182 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-11 07:46 | 2021-11-11 09:13 | 681 | 001:27 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECCERO 3 VECES PROBO MALO SE DESCRUZO CONDUCTOR Y SE CERRO POR SCADA | S21111010007 | New_Event | Wire Down | Include | Include | Equipment | 87 | 2021-11-11 | 59247 | keep | 0 | Nov | 2021 | 0.040353 | 0.00046383 | Sustained | FALSE | FALSE | Not_TMED_Event | 681
CANOVANAS | 2021-11-11 08:02 | 2021-11-11 10:04 | 20 | 002:02 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | R21111100002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2021-11-11 | 2440 | keep | 0 | Nov | 2021 | 0.0016619 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-11-11 08:31 | 2021-11-11 08:32 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21111100010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-11 | 1097 | keep | 0 | Nov | 2021 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
BAYAMON | 2021-11-11 08:46 | 2021-11-11 14:44 | 6 | 005:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21111100021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 358 | 2021-11-11 | 2148 | keep | 0 | Nov | 2021 | 0.001463 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2021-11-11 08:48 | 2021-11-11 10:52 | 50 | 002:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR GLOBO DE HELIO | P21111100017 | New_Event |  |  | Include | Wildlife | 124 | 2021-11-11 | 6200 | keep | 0 | Nov | 2021 | 0.0042228 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-11 08:56 | 2021-11-11 08:58 | 550 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR Y SE CERRO POR CONTROL 20% DE LA CARGA TRANSFERIDA AL 1717-04 | B21111100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-11 | 1100 | keep | 0 | Nov | 2021 | 0.0007492 | 0.0003746 | Momentary | FALSE | FALSE | Not_TMED_Event | 550
BAYAMON | 2021-11-11 08:56 | 2021-11-11 08:58 | 362 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DEL ALIMENTADOR 1717-04 Y SE CERRO POR CONTROL LLEVA 20% DE LA CARGA DEL 1716-02 | B21111500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-11 | 724 | keep | 0 | Nov | 2021 | 0.00049311 | 0.00024656 | Momentary | FALSE | FALSE | Not_TMED_Event | 362
UTUADO | 2021-11-11 09:24 | 2021-11-11 12:32 | 20 | 003:08 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO AVERIADO DE 40' MADERA POR 45' METAL CLASE 3 EN FID 31546858 | A21111100006 | New_Event | Defective Pole | Include | Include | Equipment | 188 | 2021-11-11 | 3760 | keep | 0 | Nov | 2021 | 0.0025609 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-11-11 09:30 | 2021-11-11 17:09 | 12 | 007:39 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR UNO DE IGUAL CAPACIDAD | B21111100026 | New_Event | Service Transformer Failure | Include | Include | Equipment | 459 | 2021-11-11 | 5508 | keep | 0 | Nov | 2021 | 0.0037515 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-11-11 09:37 | 2021-11-11 17:10 | 60 | 007:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21111100013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 453 | 2021-11-11 | 27180 | keep | 0 | Nov | 2021 | 0.018512 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2021-11-11 09:43 | 2021-11-11 15:38 | 50 | 005:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE RETEZO LINEA ARRIADA | A21111100008 | New_Event | Wire Down | Include | Include | Equipment | 355 | 2021-11-11 | 17750 | keep | 0 | Nov | 2021 | 0.012089 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-11 09:54 | 2021-11-11 17:26 | 8 | 007:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21111100027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 452 | 2021-11-11 | 3616 | keep | 0 | Nov | 2021 | 0.0024628 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2021-11-11 10:05 | 2021-11-11 12:35 | 12 | 002:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR BAJANTES SECUNDARIOS | P21111100024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 150 | 2021-11-11 | 1800 | keep | 0 | Nov | 2021 | 0.001226 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-11-11 10:09 | 2021-11-11 10:10 | 58 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21111100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-11 | 58 | keep | 0 | Nov | 2021 | 3.9504e-05 | 3.9504e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 58
HUMACAO | 2021-11-11 10:12 | 2021-11-11 10:13 | 1593 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21111100000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-11-11 | 1593 | keep | 0 | Nov | 2021 | 0.001085 | 0.001085 | Momentary | FALSE | FALSE | Not_TMED_Event | 1593
HUMACAO | 2021-11-11 10:13 | 2021-11-11 12:15 | 80 | 002:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L REMPLAZO CAJA QUEMADA | C21111100009 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 122 | 2021-11-11 | 9760 | keep | 0 | Nov | 2021 | 0.0066475 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2021-11-11 10:15 | 2021-11-11 14:00 | 300 | 003:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 2 X 80 Y 1 X 65 EN C/L CRUCE POR AVE | C21111100035 | New_Event |  |  | Include | Wildlife | 225 | 2021-11-11 | 67500 | keep | 0 | Nov | 2021 | 0.045974 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BARRANQUITAS | 2021-11-11 10:29 | 2021-11-11 12:33 | 30 | 002:04 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHO Y REMPLAZO PARARRAYO | C21111100037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2021-11-11 | 3720 | keep | 0 | Nov | 2021 | 0.0025337 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-11-11 10:37 | 2021-11-11 10:50 | 627 | 000:13 | S | LINEA DE TRANSMISION 38KV | DISPARO L-8900 | S21111100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 13 | 2021-11-11 | 8151 | keep | 0 | Nov | 2021 | 0.0055516 | 0.00042705 | Sustained | FALSE | FALSE | Not_TMED_Event | 627
SAN JUAN | 2021-11-11 10:37 | 2021-11-11 10:50 | 293 | 000:13 | S | LINEA DE TRANSMISION 38KV | DISPARO L-8900 LLEVA 1421-5 | S21111100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 13 | 2021-11-11 | 3809 | keep | 0 | Nov | 2021 | 0.0025943 | 0.00019956 | Sustained | FALSE | FALSE | Not_TMED_Event | 293
SAN JUAN | 2021-11-11 10:37 | 2021-11-11 10:50 | 761 | 000:13 | S | LINEA DE TRANSMISION 38KV | DISPARO L-8900 LLEVA 1421-1 | S21111100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 13 | 2021-11-11 | 9893 | keep | 0 | Nov | 2021 | 0.0067381 | 0.00051831 | Sustained | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2021-11-11 10:37 | 2021-11-11 10:50 | 451 | 000:13 | S | LINEA DE TRANSMISION 38KV | DISPARO L-8900 | S21111100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 13 | 2021-11-11 | 5863 | keep | 0 | Nov | 2021 | 0.0039933 | 0.00030717 | Sustained | FALSE | FALSE | Not_TMED_Event | 451
SAN JUAN | 2021-11-11 10:37 | 2021-11-11 10:50 | 1498 | 000:13 | T | LINEA DE TRANSMISION 38KV | DISPARO L-8900 CARGA A TRAVES DEL 1310-04 | S21111100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 13 | 2021-11-11 | 19474 | keep | 0 | Nov | 2021 | 0.013264 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
SAN JUAN | 2021-11-11 10:37 | 2021-11-11 10:50 | 766 | 000:13 | T | LINEA DE TRANSMISION 38KV | DISPARO L-8900 CARGA A TRAVES DEL 1310-03 | S21111100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 13 | 2021-11-11 | 9958 | keep | 0 | Nov | 2021 | 0.0067823 | 0.00052172 | Sustained | FALSE | FALSE | Not_TMED_Event | 766
ARECIBO | 2021-11-11 10:44 | 2021-11-11 12:47 | 15 | 002:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A21111100016 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 123 | 2021-11-11 | 1845 | keep | 0 | Nov | 2021 | 0.0012566 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2021-11-11 10:52 | 2021-11-11 14:41 | 3 | 003:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA ROTA | A21111100018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 229 | 2021-11-11 | 687 | keep | 0 | Nov | 2021 | 0.00046791 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2021-11-11 10:54 | 2021-11-11 11:34 | 1 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA CERRAR BAJANTE SECUNDARIO | R21111100008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2021-11-11 | 40 | keep | 0 | Nov | 2021 | 2.7244e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-11-11 10:54 | 2021-11-11 16:21 | 5 | 005:27 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | C21111100041 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 327 | 2021-11-11 | 1635 | keep | 0 | Nov | 2021 | 0.0011136 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-11-11 11:02 | 2021-11-11 11:52 | 10 | 000:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21111100004 | New_Event | Secondary Wire Down | Include | Include | Equipment | 50 | 2021-11-11 | 500 | keep | 0 | Nov | 2021 | 0.00034055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-11-11 11:09 | 2021-11-11 17:19 | 44 | 006:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L REMPLAZO CAJA QUEMADA | C21111100043 | New_Event | Cutout Failure | Include | Include | Equipment | 370 | 2021-11-11 | 16280 | keep | 0 | Nov | 2021 | 0.011088 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
SAN JUAN | 2021-11-11 11:21 | 2021-11-11 11:25 | 829 | 000:04 | P | LINEA DE TRANSMISION 115KV | DISPARO L-37900 60% POR 1206-04 | S21111100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-11-11 | 3316 | keep | 0 | Nov | 2021 | 0.0022585 | 0.00056463 | Momentary | FALSE | FALSE | Not_TMED_Event | 829
SAN JUAN | 2021-11-11 11:21 | 2021-11-11 11:25 | 720 | 000:04 | P | LINEA DE TRANSMISION 115KV | DISPARO L-37900 40% DE LA CARGA POR EL 1206-04 | S21111100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-11-11 | 2880 | keep | 0 | Nov | 2021 | 0.0019616 | 0.00049039 | Momentary | FALSE | FALSE | Not_TMED_Event | 720
SAN JUAN | 2021-11-11 11:21 | 2021-11-11 11:25 | 10211 | 000:04 | T | LINEA DE TRANSMISION 115KV | DISPARO L-37900 CARGA TRAVES DEL 1206-3 | S21111100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-11-11 | 40844 | keep | 0 | Nov | 2021 | 0.027819 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-11-11 11:21 | 2021-11-11 11:25 | 641 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO L-37900 | S21111100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-11-11 | 2564 | keep | 0 | Nov | 2021 | 0.0017463 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-11-11 11:21 | 2021-11-11 11:25 | 733 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO L-37900 CARGA POR EL 1206-01 | S21111100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-11-11 | 2932 | keep | 0 | Nov | 2021 | 0.001997 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2021-11-11 11:21 | 2021-11-11 11:25 | 4133 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO L-37900 LLEVA 1204-5 | S21111100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-11-11 | 16532 | keep | 0 | Nov | 2021 | 0.01126 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-11-11 11:21 | 2021-11-11 11:25 | 1799 | 000:04 | S | LINEA DE TRANSMISION 115KV | DISPARO L-37900 LLEVA 60% DEL 1303-2, 40% DEL 1204-2 Y 60% DEL 1204-3 | S21111100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-11-11 | 7196 | keep | 0 | Nov | 2021 | 0.0049012 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2021-11-11 11:21 | 2021-11-11 11:25 | 500 | 000:04 | P | LINEA DE TRANSMISION 115KV | DISPARO L-37900 60% DE LA CARGA POR 1206-04 | S21111100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-11-11 | 2000 | keep | 0 | Nov | 2021 | 0.0013622 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2021-11-11 11:27 | 2021-11-11 15:00 | 60 | 003:33 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21111100121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 213 | 2021-11-11 | 12780 | keep | 0 | Nov | 2021 | 0.0087044 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2021-11-11 11:35 | 2021-11-12 10:48 | 15 | 023:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO NO FUNDIO FUSIBLE | P21111100095 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1393 | 2021-11-11 | 20895 | keep | 0 | Nov | 2021 | 0.014231 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-11-11 12:07 | 2021-11-11 14:59 | 16 | 002:52 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 25 KVA X 50 KVA | C21111100048 | New_Event | Service Transformer Failure | Include | Include | Equipment | 172 | 2021-11-11 | 2752 | keep | 0 | Nov | 2021 | 0.0018744 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BARRANQUITAS | 2021-11-11 12:10 | 2021-11-11 16:47 | 50 | 004:37 | P | DESGANCHE | 1 X 65 EN C/L | C21111100049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 277 | 2021-11-11 | 13850 | keep | 0 | Nov | 2021 | 0.0094332 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-11-11 12:25 | 2021-11-11 16:56 | 4 | 004:31 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR DE 50 KVA X 50 KVA | C21111100051 | New_Event | Service Transformer Failure | Include | Include | Equipment | 271 | 2021-11-11 | 1084 | keep | 0 | Nov | 2021 | 0.00073831 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-11-11 12:42 | 2021-11-11 12:43 | 1633 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1703-01 LLEVA PARTE DEL 1703-05 | B21111100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-11 | 1633 | keep | 0 | Nov | 2021 | 0.0011122 | 0.0011122 | Momentary | FALSE | FALSE | Not_TMED_Event | 1633
BAYAMON | 2021-11-11 12:42 | 2021-11-11 12:43 | 20 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1703-01 QUE LLEVA PARTE DEL 1703-05 | B21111100049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-11 | 20 | keep | 0 | Nov | 2021 | 1.3622e-05 | 1.3622e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-11-11 12:43 | 2021-11-11 16:30 | 175 | 003:47 | P | DESGANCHE | 2 X 100 EN C/L | R21111100017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2021-11-11 | 39725 | keep | 0 | Nov | 2021 | 0.027057 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
BAYAMON | 2021-11-11 12:43 | 2021-11-11 13:10 | 100 | 000:27 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | B21111100049 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 27 | 2021-11-11 | 2700 | keep | 0 | Nov | 2021 | 0.001839 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-11-11 12:50 | 2021-11-11 13:18 | 627 | 000:28 | S | LINEA DE TRANSMISION 38KV | DISPARO L-8900 | S21111100000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-11-11 | 17556 | keep | 0 | Nov | 2021 | 0.011957 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-11 12:50 | 2021-11-11 13:18 | 293 | 000:28 | S | LINEA DE TRANSMISION 38KV | DISPARO L-8900 LLEVA 1421-5 | S21111100000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-11-11 | 8204 | keep | 0 | Nov | 2021 | 0.0055877 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-11 12:50 | 2021-11-11 13:18 | 761 | 000:28 | S | LINEA DE TRANSMISION 38KV | DISPARO L-8900 LLEVA 1421-1 | S21111100000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-11-11 | 21308 | keep | 0 | Nov | 2021 | 0.014513 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-11 12:50 | 2021-11-11 13:18 | 451 | 000:28 | S | LINEA DE TRANSMISION 38KV | DISPARO L-8900 | S21111100000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-11-11 | 12628 | keep | 0 | Nov | 2021 | 0.0086009 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-11 12:50 | 2021-11-11 13:18 | 1498 | 000:28 | T | LINEA DE TRANSMISION 38KV | DISPARO L-8900 CARGA A TRAVES DEL 1310-04 | S21111100000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-11-11 | 41944 | keep | 0 | Nov | 2021 | 0.028568 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-11 12:50 | 2021-11-11 13:18 | 766 | 000:28 | T | LINEA DE TRANSMISION 38KV | DISPARO L-8900 CARGA A TRAVES DEL 1310-03 | S21111100000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 28 | 2021-11-11 | 21448 | keep | 0 | Nov | 2021 | 0.014608 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-11-11 12:50 | 2021-11-11 12:51 | 2580 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 11100 DE CANOVANAS TC A LAS MERCEDES | R21111100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-11 | 2580 | keep | 0 | Nov | 2021 | 0.0017572 | 0.0017572 | Momentary | FALSE | FALSE | Not_TMED_Event | 2580
CANOVANAS | 2021-11-11 12:50 | 2021-11-11 12:51 | 500 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 11100 DE CANOVANAS TC A LAS MERCEDES | R21111100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-11 | 500 | keep | 0 | Nov | 2021 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
CANOVANAS | 2021-11-11 13:00 | 2021-11-11 15:56 | 30 | 002:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L CRUCE POR GLOBO | R21111100018 | New_Event |  |  | Include | Wildlife | 176 | 2021-11-11 | 5280 | keep | 0 | Nov | 2021 | 0.0035962 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2021-11-11 13:03 | 2021-11-11 17:45 | 50 | 004:42 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | P21111100046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 282 | 2021-11-11 | 14100 | keep | 0 | Nov | 2021 | 0.0096034 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-11 13:10 | 2021-11-11 13:11 | 1633 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL 1703-01 QUE LLEVA PARTE DEL 1703-05 | B21111100000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-11 | 1633 | keep | 0 | Nov | 2021 | 0.0011122 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-11 13:10 | 2021-11-11 13:11 | 20 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1703-01 QUE LLEVA PARTE DEL 1703-05 | B21111100049 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-11 | 20 | keep | 0 | Nov | 2021 | 1.3622e-05 | 1.3622e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-11-11 13:11 | 2021-11-11 14:17 | 100 | 001:06 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | B21111100049 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 66 | 2021-11-11 | 6600 | keep | 0 | Nov | 2021 | 0.0044952 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-11-11 13:15 | 2021-11-11 14:57 | 15 | 001:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR NEUTRAL AVERIADO | M21111100020 | New_Event | Wire Down | Include | Include | Equipment | 102 | 2021-11-11 | 1530 | keep | 0 | Nov | 2021 | 0.0010421 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-11-11 13:18 | 2021-11-11 13:19 | 550 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO | S21111100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-11 | 550 | keep | 0 | Nov | 2021 | 0.0003746 | 0.0003746 | Momentary | FALSE | FALSE | Not_TMED_Event | 550
FAJARDO | 2021-11-11 13:37 | 2021-11-11 13:38 | 1376 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO INTERRUPTOR EN SERVICIO | R21111100020 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-11 | 1376 | keep | 0 | Nov | 2021 | 0.00093719 | 0.00093719 | Momentary | FALSE | FALSE | Not_TMED_Event | 1376
FAJARDO | 2021-11-11 13:38 | 2021-11-11 14:18 | 25 | 000:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR | R21111100028 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 40 | 2021-11-11 | 1000 | keep | 0 | Nov | 2021 | 0.0006811 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2021-11-11 13:40 | 2021-11-11 18:12 | 5 | 004:32 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE SECUNDARIO | A21111100037 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 272 | 2021-11-11 | 1360 | keep | 0 | Nov | 2021 | 0.00092629 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-11-11 13:46 | 2021-11-11 17:20 | 52 | 003:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO PUENTE A CAJA PRIMARIA | S21111100107 | New_Event | Wire Down | Include | Include | Equipment | 214 | 2021-11-11 | 11128 | keep | 0 | Nov | 2021 | 0.0075792 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
BAYAMON | 2021-11-11 13:46 | 2021-11-11 17:20 | 40 | 003:34 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S21111100160 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 214 | 2021-11-11 | 8560 | keep | 0 | Nov | 2021 | 0.0058302 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-11-11 13:47 | 2021-11-11 16:25 | 50 | 002:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE POR AVE | R21111100022 | New_Event |  |  | Include | Wildlife | 158 | 2021-11-11 | 7900 | keep | 0 | Nov | 2021 | 0.0053807 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2021-11-11 13:59 | 2021-11-11 16:26 | 10 | 002:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA NO SE REMPLAZO FUSIBLE | P21111100058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 147 | 2021-11-11 | 1470 | keep | 0 | Nov | 2021 | 0.0010012 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-11-11 14:01 | 2021-11-11 19:52 | 45 | 005:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN C/L LEVANTO CONDUCTOR | C21111100059 | New_Event | Wire Down | Include | Include | Equipment | 351 | 2021-11-11 | 15795 | keep | 0 | Nov | 2021 | 0.010758 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2021-11-11 14:04 | 2021-11-11 16:52 | 50 | 002:48 | P | DESGANCHE | 1 X 50 EN C/L | C21111100061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2021-11-11 | 8400 | keep | 0 | Nov | 2021 | 0.0057212 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-11-11 14:15 | 2021-11-11 17:15 | 7 | 003:00 | P | TRANSFORMADOR AVERIADO | SE ABRIO CORTE DE LINEA PARA REMPLAZAR PT AVERIADO | M21111100026 | New_Event | Service Transformer Failure | Include | Include | Equipment | 180 | 2021-11-11 | 1260 | keep | 0 | Nov | 2021 | 0.00085818 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-11-11 14:17 | 2021-11-11 14:18 | 1633 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21111100000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-11 | 1633 | keep | 0 | Nov | 2021 | 0.0011122 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-11 14:17 | 2021-11-11 14:18 | 20 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1703-01 QUE LLEVA PARTE DEL 1703-05 | B21111100049 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-11 | 20 | keep | 0 | Nov | 2021 | 1.3622e-05 | 1.3622e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-11-11 14:18 | 2021-11-11 17:22 | 100 | 003:04 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | B21111100049 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 184 | 2021-11-11 | 18400 | keep | 0 | Nov | 2021 | 0.012532 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2021-11-11 14:18 | 2021-11-11 14:29 | 1376 | 000:11 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | A PETICION DE ABEL CASTRO SE ABRIO BKR POR CONDUCTOR VIVO EN EL SUELO | R21111100028 | Additional_clients | Wire Down | Include | Include | Equipment | 11 | 2021-11-11 | 15136 | keep | 0 | Nov | 2021 | 0.010309 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-11 14:21 | 2021-11-11 17:46 | 7 | 003:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR DESPEGO CAJA PRIMARIA DEL POSTE | R21111100026 | New_Event | Cutout Failure | Include | Include | Equipment | 205 | 2021-11-11 | 1435 | keep | 0 | Nov | 2021 | 0.00097737 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-11-11 14:21 | 2021-11-11 16:38 | 20 | 002:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 10 EN TRANSFORMADOR SE REPARO BAJANTES SECUNDARIOS QUEMADOS | A21111100041 | New_Event | Wire Down | Include | Include | Equipment | 137 | 2021-11-11 | 2740 | keep | 0 | Nov | 2021 | 0.0018662 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2021-11-11 14:27 | 2021-11-11 16:45 | 25 | 002:18 | P | NO SE REPORTO CAUSA | 2 X 30 EN CORTE DE LINEA NO SE REPORTO CAUSA | P21111100061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 138 | 2021-11-11 | 3450 | keep | 0 | Nov | 2021 | 0.0023498 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2021-11-11 14:29 | 2021-11-11 15:32 | 25 | 001:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR | R21111100028 | Partial_restoration | Wire Down | Include | Include | Equipment | 63 | 2021-11-11 | 1575 | keep | 0 | Nov | 2021 | 0.0010727 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-11 14:30 | 2021-11-11 17:04 | 35 | 002:34 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S21111100167 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 154 | 2021-11-11 | 5390 | keep | 0 | Nov | 2021 | 0.0036711 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2021-11-11 14:30 | 2021-11-11 15:59 | 7 | 001:29 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE POSTE SECUNDARIO PARTIDO | B21111100062 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 89 | 2021-11-11 | 623 | keep | 0 | Nov | 2021 | 0.00042432 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-11-11 14:44 | 2021-11-11 20:52 | 25 | 006:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA | S21111100169 | New_Event | Cutout Failure | Include | Include | Equipment | 368 | 2021-11-11 | 9200 | keep | 0 | Nov | 2021 | 0.0062661 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2021-11-11 14:55 | 2021-11-11 20:21 | 60 | 005:26 | P | DESGANCHE | 1 X 30 Y 1 X 50 EN C/L | C21111100067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 326 | 2021-11-11 | 19560 | keep | 0 | Nov | 2021 | 0.013322 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2021-11-11 14:55 | 2021-11-12 10:56 | 76 | 020:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21111100067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1201 | 2021-11-11 | 91276 | keep | 0 | Nov | 2021 | 0.062168 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
BAYAMON | 2021-11-11 15:05 | 2021-11-11 18:46 | 6 | 003:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21111100071 | New_Event | Secondary Wire Down | Include | Include | Equipment | 221 | 2021-11-11 | 1326 | keep | 0 | Nov | 2021 | 0.00090313 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-11-11 15:11 | 2021-11-11 18:19 | 50 | 003:08 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S21111100171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2021-11-11 | 9400 | keep | 0 | Nov | 2021 | 0.0064023 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-11 15:13 | 2021-11-11 16:30 | 40 | 001:17 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21111100036 | New_Event | Bad Weather | Include | Include | Weather | 77 | 2021-11-11 | 3080 | keep | 0 | Nov | 2021 | 0.0020978 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-11-11 15:14 | 2021-11-11 17:23 | 15 | 002:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZARON CONECTORES SECUNDARIOS | S21111100127 | New_Event | Secondary Wire Down | Include | Include | Equipment | 129 | 2021-11-11 | 1935 | keep | 0 | Nov | 2021 | 0.0013179 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-11-11 15:40 | 2021-11-11 15:59 | 10 | 000:19 | P | NO SE REPORTO CAUSA | 1 X 15 EN CORTE DE LINEA | B21111100066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 19 | 2021-11-11 | 190 | keep | 0 | Nov | 2021 | 0.00012941 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-11-11 15:43 | 2021-11-11 17:30 | 7 | 001:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REMPLAZO CONECTOR QUEMADO EN BAJANTE SECUNDARIO | C21111100074 | New_Event | Secondary Wire Down | Include | Include | Equipment | 107 | 2021-11-11 | 749 | keep | 0 | Nov | 2021 | 0.00051014 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2021-11-11 15:56 | 2021-11-11 19:40 | 60 | 003:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA SE REPORTA MAL TIEMPO RAYOS | B21111100068 | New_Event | Bad Weather | Include | Include | Weather | 224 | 2021-11-11 | 13440 | keep | 0 | Nov | 2021 | 0.0091539 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2021-11-11 16:02 | 2021-11-11 17:59 | 15 | 001:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | P21111100072 | New_Event | Secondary Wire Down | Include | Include | Equipment | 117 | 2021-11-11 | 1755 | keep | 0 | Nov | 2021 | 0.0011953 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-11-11 16:06 | 2021-11-11 16:57 | 6 | 000:51 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR SE DESGANCHO Y SE REPARO SECUNDARIA | S21111100177 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 51 | 2021-11-11 | 306 | keep | 0 | Nov | 2021 | 0.00020842 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-11-11 16:08 | 2021-11-11 17:49 | 80 | 001:41 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REPARO AISLADOR ROTO EN LINEA PRIMARIA | A21111100053 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 101 | 2021-11-11 | 8080 | keep | 0 | Nov | 2021 | 0.0055033 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-11-11 16:15 | 2021-11-11 16:50 | 15 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M21111100030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2021-11-11 | 525 | keep | 0 | Nov | 2021 | 0.00035758 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-11-11 16:31 | 2021-11-11 16:32 | 1879 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO | C21111100079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-11 | 1879 | keep | 0 | Nov | 2021 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
PONCE | 2021-11-11 16:39 | 2021-11-11 17:15 | 80 | 000:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | P21111100079 | New_Event | Bad Weather | Include | Include | Weather | 36 | 2021-11-11 | 2880 | keep | 0 | Nov | 2021 | 0.0019616 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2021-11-11 17:02 | 2021-11-11 20:45 | 12 | 003:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO FUSIBLE DE 15 AMP EN TRANSFORMADOR Y SE REEMPLAZO CAJA QUEMADA EN TRANSFORMADOR | A21111100037 | New_Event | Cutout Failure | Include | Include | Equipment | 223 | 2021-11-11 | 2676 | keep | 0 | Nov | 2021 | 0.0018226 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-11-11 17:03 | 2021-11-11 19:02 | 50 | 001:59 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21111100032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2021-11-11 | 5950 | keep | 0 | Nov | 2021 | 0.0040525 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-11-11 17:12 | 2021-11-11 19:04 | 50 | 001:52 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO CAUSA | R21111100034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2021-11-11 | 5600 | keep | 0 | Nov | 2021 | 0.0038141 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2021-11-11 17:29 | 2021-11-11 17:30 | 1604 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21111100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-11 | 1604 | keep | 0 | Nov | 2021 | 0.0010925 | 0.0010925 | Momentary | FALSE | FALSE | Not_TMED_Event | 1604
BAYAMON | 2021-11-11 17:30 | 2021-11-11 22:00 | 15 | 004:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 30 EN TRANSFORMADOR Y SE REPARO SECUNDARIA CRUZADA | B21111100076 | New_Event | Secondary Wire Down | Include | Include | Equipment | 270 | 2021-11-11 | 4050 | keep | 0 | Nov | 2021 | 0.0027584 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2021-11-11 17:30 | 2021-11-12 09:05 | 58 | 015:35 | P | TRANSFORMADOR AVERIADO | 1 X 50 EN CORTE DE LINEA SE SECCIONALIZO TRANSFORMADOR AVERIADO | C21111000086 | New_Event | Service Transformer Failure | Include | Include | Equipment | 935 | 2021-11-11 | 54230 | keep | 0 | Nov | 2021 | 0.036936 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
SAN JUAN | 2021-11-11 17:37 | 2021-11-11 22:30 | 100 | 004:53 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21111100192 | New_Event | Vegetation Contact | Include | Include | Vegetation | 293 | 2021-11-11 | 29300 | keep | 0 | Nov | 2021 | 0.019956 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-11-11 17:57 | 2021-11-11 17:58 | 3070 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21111100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-11 | 3070 | keep | 0 | Nov | 2021 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2021-11-11 17:59 | 2021-11-11 18:00 | 3070 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21111100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-11 | 3070 | keep | 0 | Nov | 2021 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2021-11-11 18:10 | 2021-11-11 20:14 | 130 | 002:04 | P | NO SE REPORTO CAUSA | 1 X 125 EN SU-3 | B21111100083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 124 | 2021-11-11 | 16120 | keep | 0 | Nov | 2021 | 0.010979 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
BAYAMON | 2021-11-11 18:32 | 2021-11-12 18:35 | 30 | 024:03 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 100 EN RISER DE LA PARALELA SE REMPLAZO UNIDAD SECCIONALIZADORA | S21111100198 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1443 | 2021-11-11 | 43290 | keep | 0 | Nov | 2021 | 0.029485 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-11-11 18:46 | 2021-11-12 10:28 | 60 | 015:42 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21111100095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 942 | 2021-11-11 | 56520 | keep | 0 | Nov | 2021 | 0.038496 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2021-11-11 19:31 | 2021-11-11 21:29 | 40 | 001:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN RISER CRUCE X REPTIL | R21111100038 | New_Event |  |  | Include | Wildlife | 118 | 2021-11-11 | 4720 | keep | 0 | Nov | 2021 | 0.0032148 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2021-11-11 19:40 | 2021-11-12 11:16 | 4 | 015:36 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | A21111100059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 936 | 2021-11-11 | 3744 | keep | 0 | Nov | 2021 | 0.00255 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-11-11 19:47 | 2021-11-11 21:53 | 35 | 002:06 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S21111100210 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2021-11-11 | 4410 | keep | 0 | Nov | 2021 | 0.0030036 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2021-11-11 20:23 | 2021-11-11 22:09 | 10 | 001:46 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21111100093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2021-11-11 | 1060 | keep | 0 | Nov | 2021 | 0.00072196 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-11 21:04 | 2021-11-11 22:23 | 1 | 001:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21111100060 | New_Event | Bad Weather | Include | Include | Weather | 79 | 2021-11-11 | 79 | keep | 0 | Nov | 2021 | 5.3807e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-11-11 21:35 | 2021-11-11 21:36 | 1590 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21111100109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-11 | 1590 | keep | 0 | Nov | 2021 | 0.0010829 | 0.0010829 | Momentary | FALSE | FALSE | Not_TMED_Event | 1590
FAJARDO | 2021-11-11 21:50 | 2021-11-11 22:47 | 95 | 000:57 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | R21111100040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 57 | 2021-11-11 | 5415 | keep | 0 | Nov | 2021 | 0.0036881 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
BAYAMON | 2021-11-11 22:20 | 2021-11-12 09:19 | 15 | 010:59 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B21111100099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 659 | 2021-11-11 | 9885 | keep | 0 | Nov | 2021 | 0.0067326 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-11-11 22:50 | 2021-11-12 14:12 | 30 | 015:22 | P | DESGANCHE | 1 X 30 EN C/L | C21111100114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 922 | 2021-11-11 | 27660 | keep | 0 | Nov | 2021 | 0.018839 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-11-11 23:07 | 2021-11-12 14:23 | 60 | 015:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO BAJANTE DE CORTE DE LINEA | A21111100063 | New_Event | Wire Down | Include | Include | Equipment | 916 | 2021-11-11 | 54960 | keep | 0 | Nov | 2021 | 0.037433 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-11-11 23:22 | 2021-11-12 18:56 | 50 | 019:34 | P | ESTRUCTURA AVERIADA | 1 X 50 Y 1 X 40 EN CORTES DE LINEA DIFERENTES SE REMPLAZO POSTE PARTIDO | M21111100061 | New_Event | Defective Pole | Include | Include | Equipment | 1174 | 2021-11-11 | 58700 | keep | 0 | Nov | 2021 | 0.03998 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-11-11 23:30 | 2021-11-12 10:41 | 75 | 011:11 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21111100101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 671 | 2021-11-11 | 50325 | keep | 0 | Nov | 2021 | 0.034276 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2021-11-11 23:58 | 2021-11-12 15:17 | 45 | 015:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN C/L MAL TIEMPO | C21111100117 | New_Event | Bad Weather | Include | Include | Weather | 919 | 2021-11-11 | 41355 | keep | 0 | Nov | 2021 | 0.028167 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2021-11-12 00:22 | 2021-11-12 10:18 | 5 | 009:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE POR AVE | R21111200001 | New_Event |  |  | Include | Wildlife | 596 | 2021-11-12 | 2980 | keep | 0 | Nov | 2021 | 0.0020297 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2021-11-12 00:26 | 2021-11-12 00:27 | 2708 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21111200002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-12 | 2708 | keep | 0 | Nov | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2021-11-12 00:27 | 2021-11-12 09:40 | 30 | 009:13 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L NO CAUSA | R21111200007 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 553 | 2021-11-12 | 16590 | keep | 0 | Nov | 2021 | 0.011299 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-11-12 00:56 | 2021-11-12 00:57 | 3833 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21111200002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-12 | 3833 | keep | 0 | Nov | 2021 | 0.0026106 | 0.0026106 | Momentary | FALSE | FALSE | Not_TMED_Event | 3833
SAN JUAN | 2021-11-12 01:06 | 2021-11-12 09:22 | 100 | 008:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN C/L MAL TIEMPO | R21111200005 | New_Event | Bad Weather | Include | Include | Weather | 496 | 2021-11-12 | 49600 | keep | 0 | Nov | 2021 | 0.033782 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-11-12 02:49 | 2021-11-12 02:50 | 790 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21111200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-12 | 790 | keep | 0 | Nov | 2021 | 0.00053807 | 0.00053807 | Momentary | FALSE | FALSE | Not_TMED_Event | 790
BAYAMON | 2021-11-12 03:12 | 2021-11-12 09:19 | 40 | 006:07 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21111200001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 367 | 2021-11-12 | 14680 | keep | 0 | Nov | 2021 | 0.0099985 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2021-11-12 03:28 | 2021-11-12 10:37 | 100 | 007:09 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | P21111200003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 429 | 2021-11-12 | 42900 | keep | 0 | Nov | 2021 | 0.029219 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-11-12 03:37 | 2021-11-12 03:38 | 186 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | B21111200000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-12 | 186 | keep | 0 | Nov | 2021 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2021-11-12 03:38 | 2021-11-12 10:25 | 1 | 006:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN RISER SE REPARO BAJANTE DE PT EN TRANSCLOSURE | B21111200005 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 407 | 2021-11-12 | 407 | keep | 0 | Nov | 2021 | 0.00027721 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-11-12 03:52 | 2021-11-12 09:48 | 200 | 005:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L REMPLAZO CAJA AVERIADA | R21111200009 | New_Event | Cutout Failure | Include | Include | Equipment | 356 | 2021-11-12 | 71200 | keep | 0 | Nov | 2021 | 0.048494 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-11-12 04:19 | 2021-11-12 10:45 | 1 | 006:26 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21111200003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 386 | 2021-11-12 | 386 | keep | 0 | Nov | 2021 | 0.0002629 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-12 04:42 | 2021-11-12 10:39 | 50 | 005:57 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE DESGANCHO PALMA | S21111200008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 357 | 2021-11-12 | 17850 | keep | 0 | Nov | 2021 | 0.012158 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-11-12 04:45 | 2021-11-12 06:39 | 1681 | 001:54 | T | DESGANCHE | DISPARO 1303-04 QUE LLEVA 1303-01 SE SECCIONALIZO Y SE CERRO 1303-04 POR SCADA | S21111200009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2021-11-12 | 191634 | keep | 0 | Nov | 2021 | 0.13052 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-11-12 04:45 | 2021-11-12 06:39 | 1598 | 001:54 | T | DESGANCHE | DISPARO 1303-04 QUE LLEVA 1346-06 SE SECCIONALIZO Y SE CERRO 1303-04 POR SCADA | S21111200009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2021-11-12 | 182172 | keep | 0 | Nov | 2021 | 0.12408 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
CAGUAS | 2021-11-12 05:07 | 2021-11-12 05:08 | 1854 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21111200005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-12 | 1854 | keep | 0 | Nov | 2021 | 0.0012628 | 0.0012628 | Momentary | FALSE | FALSE | Not_TMED_Event | 1854
CAGUAS | 2021-11-12 05:20 | 2021-11-12 11:30 | 19 | 006:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21111200007 | New_Event | Bad Weather | Include | Include | Weather | 370 | 2021-11-12 | 7030 | keep | 0 | Nov | 2021 | 0.0047881 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
ARECIBO | 2021-11-12 06:16 | 2021-11-12 09:54 | 6 | 003:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA EN TRANSFORMADOR AVERIADA | A21111200002 | New_Event | Cutout Failure | Include | Include | Equipment | 218 | 2021-11-12 | 1308 | keep | 0 | Nov | 2021 | 0.00089087 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-11-12 06:24 | 2021-11-12 16:36 | 5 | 010:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE POR REPTIL | C21111200013 | New_Event |  |  | Include | Wildlife | 612 | 2021-11-12 | 3060 | keep | 0 | Nov | 2021 | 0.0020842 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-11-12 06:28 | 2021-11-12 14:16 | 20 | 007:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 40 EN C/L REPARO SECUNDARIA | C21111200014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 468 | 2021-11-12 | 9360 | keep | 0 | Nov | 2021 | 0.0063751 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-11-12 06:31 | 2021-11-12 08:57 | 50 | 002:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | A21111200003 | New_Event | Bad Weather | Include | Include | Weather | 146 | 2021-11-12 | 7300 | keep | 0 | Nov | 2021 | 0.004972 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-11-12 06:39 | 2021-11-12 08:38 | 168 | 001:59 | P | DESGANCHE | REALIZO DESGANCHE Y SE CERRO MACHETES | S21111200009 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 119 | 2021-11-12 | 19992 | keep | 0 | Nov | 2021 | 0.013616 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-11-12 06:44 | 2021-11-12 06:45 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | A21111200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-12 | 308 | keep | 0 | Nov | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2021-11-12 07:09 | 2021-11-12 11:14 | 50 | 004:05 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21111200056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2021-11-12 | 12250 | keep | 0 | Nov | 2021 | 0.0083434 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-11-12 07:42 | 2021-11-12 11:38 | 40 | 003:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA NO FUNDIO | R21111200013 | New_Event | Wire Down | Include | Include | Equipment | 236 | 2021-11-12 | 9440 | keep | 0 | Nov | 2021 | 0.0064295 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-11-12 07:50 | 2021-11-12 11:38 | 5 | 003:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C21111200018 | New_Event |  |  | Include | Wildlife | 228 | 2021-11-12 | 1140 | keep | 0 | Nov | 2021 | 0.00077645 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2021-11-12 07:58 | 2021-11-12 12:11 | 60 | 004:13 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LA LINEA | B21111200012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 253 | 2021-11-12 | 15180 | keep | 0 | Nov | 2021 | 0.010339 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2021-11-12 08:04 | 2021-11-12 10:47 | 80 | 002:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE CRUZO LINEAS | P21111200009 | New_Event |  |  | Include | Wildlife | 163 | 2021-11-12 | 13040 | keep | 0 | Nov | 2021 | 0.0088815 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2021-11-12 08:21 | 2021-11-12 10:31 | 10 | 002:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BARRA EN PEDESTAL SECUNDARIO NO FUNDIO FUSIBLE | P21111200015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 130 | 2021-11-12 | 1300 | keep | 0 | Nov | 2021 | 0.00088542 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-12 08:28 | 2021-11-12 09:48 | 30 | 001:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A21111200008 | New_Event | Bad Weather | Include | Include | Weather | 80 | 2021-11-12 | 2400 | keep | 0 | Nov | 2021 | 0.0016346 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2021-11-12 08:48 | 2021-11-12 10:10 | 40 | 001:22 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR Y 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA | A21111200009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 82 | 2021-11-12 | 3280 | keep | 0 | Nov | 2021 | 0.002234 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-12 09:00 | 2021-11-12 17:37 | 25 | 008:37 | P | DESGANCHE | 3 X 100 EN CORTE DE LINEA SE RETIRO RAMA DE PALMA | S21111200072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 517 | 2021-11-12 | 12925 | keep | 0 | Nov | 2021 | 0.0088032 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-11-12 09:00 | 2021-11-12 14:30 | 10 | 005:30 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE POSTE SECUNDARIO AVERIADO | M21111200006 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 330 | 2021-11-12 | 3300 | keep | 0 | Nov | 2021 | 0.0022476 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-11-12 09:03 | 2021-11-12 15:46 | 15 | 006:43 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L NO CAUSA | R21111200020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 403 | 2021-11-12 | 6045 | keep | 0 | Nov | 2021 | 0.0041172 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-11-12 09:04 | 2021-11-12 09:05 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21111200018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-12 | 990 | keep | 0 | Nov | 2021 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
BARRANQUITAS | 2021-11-12 09:05 | 2021-11-12 09:06 | 1604 | 000:01 | T | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | RECIERRE | C21111200000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1 | 2021-11-12 | 1604 | keep | 0 | Nov | 2021 | 0.0010925 | 0.0010925 | Momentary | FALSE | FALSE | Not_TMED_Event | 1604
CANOVANAS | 2021-11-12 09:21 | 2021-11-12 13:05 | 20 | 003:44 | P | DESGANCHE | 1 X 20 EN RISER | R21111200022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2021-11-12 | 4480 | keep | 0 | Nov | 2021 | 0.0030513 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-11-12 09:23 | 2021-11-12 12:18 | 1 | 002:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 40 EN RISER SE REMPLAZO PORTAFUSIBLE | S21111200076 | New_Event | Cutout Failure | Include | Include | Equipment | 175 | 2021-11-12 | 175 | keep | 0 | Nov | 2021 | 0.00011919 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2021-11-12 09:23 | 2021-11-12 12:56 | 65 | 003:33 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21111200022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2021-11-12 | 13845 | keep | 0 | Nov | 2021 | 0.0094298 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2021-11-12 09:25 | 2021-11-12 11:44 | 10 | 002:19 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50KVA CON PROBLEMAS DE VOLTAJE | B21111200009 | New_Event | Service Transformer Failure | Include | Include | Equipment | 139 | 2021-11-12 | 1390 | keep | 0 | Nov | 2021 | 0.00094672 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-12 09:26 | 2021-11-12 11:21 | 1 | 001:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | A21111200013 | New_Event | Cutout Failure | Include | Include | Equipment | 115 | 2021-11-12 | 115 | keep | 0 | Nov | 2021 | 7.8326e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-12 09:34 | 2021-11-12 11:10 | 30 | 001:36 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21111200081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2021-11-12 | 2880 | keep | 0 | Nov | 2021 | 0.0019616 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-11-12 09:39 | 2021-11-12 17:53 | 15 | 008:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M21111200024 | New_Event | Cutout Failure | Include | Include | Equipment | 494 | 2021-11-12 | 7410 | keep | 0 | Nov | 2021 | 0.0050469 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-11-12 09:42 | 2021-11-12 10:20 | 8 | 000:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR CONECTORES EN LA SECUNDARIA | C21111100105 | New_Event | Secondary Wire Down | Include | Include | Equipment | 38 | 2021-11-12 | 304 | keep | 0 | Nov | 2021 | 0.00020705 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-11-12 09:45 | 2021-11-12 12:35 | 30 | 002:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR NEUTRAL PRIMARIO ROTO | M21111200020 | New_Event | Wire Down | Include | Include | Equipment | 170 | 2021-11-12 | 5100 | keep | 0 | Nov | 2021 | 0.0034736 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-11-12 09:51 | 2021-11-12 10:40 | 5 | 000:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR NEUTRAL EN TRANSFORMADOR | M21111200019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 49 | 2021-11-12 | 245 | keep | 0 | Nov | 2021 | 0.00016687 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-11-12 10:00 | 2021-11-12 13:20 | 6 | 003:20 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR SE REPARO SECUNDARIA Y SE DESGANCHO ESTA CARGA DEL 1422-02 ESTA A TRAVES DEL 1418-02 | S21111200084 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 200 | 2021-11-12 | 1200 | keep | 0 | Nov | 2021 | 0.00081731 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-11-12 10:10 | 2021-11-12 11:55 | 50 | 001:45 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21111200024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2021-11-12 | 5250 | keep | 0 | Nov | 2021 | 0.0035758 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2021-11-12 10:10 | 2021-11-12 10:42 | 2635 | 000:32 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 6500 DE BARRANQUITAS A TORO NEGRO | C21111200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 32 | 2021-11-12 | 84320 | keep | 0 | Nov | 2021 | 0.05743 | 0.0017947 | Sustained | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2021-11-12 10:10 | 2021-11-12 10:42 | 2280 | 000:32 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 6500 DE BARRANQUITAS A TORO NEGRO | C21111200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 32 | 2021-11-12 | 72960 | keep | 0 | Nov | 2021 | 0.049693 | 0.0015529 | Sustained | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2021-11-12 10:10 | 2021-11-12 10:42 | 1617 | 000:32 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 6500 DE BARRANQUITAS A TORO NEGRO | C21111200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 32 | 2021-11-12 | 51744 | keep | 0 | Nov | 2021 | 0.035243 | 0.0011013 | Sustained | FALSE | FALSE | Not_TMED_Event | 1617
AGUADILLA | 2021-11-12 10:17 | 2021-11-12 15:03 | 300 | 004:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | BAJANTE DE LINEA A CAJA DE CORTE DE LINEA ZAFADO SE ABRIO CORTE DE LINEA ANTERIOR PARA REPARAR | M21111200031 | New_Event | Wire Down | Include | Include | Equipment | 286 | 2021-11-12 | 85800 | keep | 0 | Nov | 2021 | 0.058438 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2021-11-12 10:18 | 2021-11-12 11:33 | 50 | 001:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE POR AVE | R21111200026 | New_Event |  |  | Include | Wildlife | 75 | 2021-11-12 | 3750 | keep | 0 | Nov | 2021 | 0.0025541 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-12 10:28 | 2021-11-12 12:19 | 200 | 001:51 | P | SOBRECARGA | 1 X 40 EN CORTE DE LINEA EL JOURNEYMAN INFORMO QUE EL FUSIBLE FUNDIO POR SOBRECARGA | M21111200033 | New_Event | Trip Due To Overload | Include | Include | Other | 111 | 2021-11-12 | 22200 | keep | 0 | Nov | 2021 | 0.01512 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2021-11-12 10:35 | 2021-11-12 12:00 | 18 | 001:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES Y CONECTORES SECUNDARIOS | A21111000064 | New_Event | Secondary Wire Down | Include | Include | Equipment | 85 | 2021-11-12 | 1530 | keep | 0 | Nov | 2021 | 0.0010421 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
PONCE | 2021-11-12 10:38 | 2021-11-12 12:09 | 50 | 001:31 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21111200034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2021-11-12 | 4550 | keep | 0 | Nov | 2021 | 0.003099 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-11-12 10:40 | 2021-11-12 15:13 | 45 | 004:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE POR PALOMA | R21111200028 | New_Event |  |  | Include | Wildlife | 273 | 2021-11-12 | 12285 | keep | 0 | Nov | 2021 | 0.0083673 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2021-11-12 10:58 | 2021-11-12 13:12 | 3 | 002:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 5 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA EN TRANSFORMADOR Y SE LEVANTO NEUTRAL PRIMARIO | C21111200066 | New_Event | Cutout Failure | Include | Include | Equipment | 134 | 2021-11-12 | 402 | keep | 0 | Nov | 2021 | 0.0002738 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2021-11-12 11:02 | 2021-11-12 11:51 | 1 | 000:49 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR BARRA EN PEDESTAL | C21111100065 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 49 | 2021-11-12 | 49 | keep | 0 | Nov | 2021 | 3.3374e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-11-12 11:03 | 2021-11-12 12:38 | 10 | 001:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | A21111200020 | New_Event | Bad Weather | Include | Include | Weather | 95 | 2021-11-12 | 950 | keep | 0 | Nov | 2021 | 0.00064704 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-11-12 11:13 | 2021-11-12 13:35 | 4 | 002:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR BARRAS DE PEDESTAL | R21111200032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 142 | 2021-11-12 | 568 | keep | 0 | Nov | 2021 | 0.00038686 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
FAJARDO | 2021-11-12 11:17 | 2021-11-12 13:45 | 7 | 002:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | R21111200033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 148 | 2021-11-12 | 1036 | keep | 0 | Nov | 2021 | 0.00070561 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2021-11-12 11:30 | 2021-11-12 14:28 | 6 | 002:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE POR RATON | C21111200069 | New_Event |  |  | Include | Wildlife | 178 | 2021-11-12 | 1068 | keep | 0 | Nov | 2021 | 0.00072741 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-11-12 11:37 | 2021-11-12 11:39 | 1633 | 000:02 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO Y SE CERRO POR CONTROL | B21111200000 | New_Event |  |  | Include | Wildlife | 2 | 2021-11-12 | 3266 | keep | 0 | Nov | 2021 | 0.0022245 | 0.0011122 | Momentary | FALSE | FALSE | Not_TMED_Event | 1633
BAYAMON | 2021-11-12 11:37 | 2021-11-12 11:39 | 20 | 000:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO 1703-01 QUE LLEVA PARTE DEL 1703-05 | B21111200000 | New_Event |  |  | Include | Wildlife | 2 | 2021-11-12 | 40 | keep | 0 | Nov | 2021 | 2.7244e-05 | 1.3622e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-11-12 11:38 | 2021-11-12 22:19 | 8 | 010:41 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR POSTE SECUNDARIO ROTO | R21111200035 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 641 | 2021-11-12 | 5128 | keep | 0 | Nov | 2021 | 0.0034927 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-11-12 11:48 | 2021-11-12 12:55 | 1633 | 001:07 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO Y SE CERRO POR CONTROL | B21111200000 | 1st_after_momentary |  |  | Include | Wildlife | 67 | 2021-11-12 | 109411 | keep | 0 | Nov | 2021 | 0.074519 | 0.0011122 | Sustained | FALSE | FALSE | Not_TMED_Event | 1633
BAYAMON | 2021-11-12 11:48 | 2021-11-12 12:55 | 20 | 001:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO 1703-01 QUE LLEVA PARTE DEL 1703-05 | B21111200000 | 1st_after_momentary |  |  | Include | Wildlife | 67 | 2021-11-12 | 1340 | keep | 0 | Nov | 2021 | 0.00091267 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-11-12 11:58 | 2021-11-12 14:25 | 50 | 002:27 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 40 EN CORTE DE LINEA | B21111200039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 147 | 2021-11-12 | 7350 | keep | 0 | Nov | 2021 | 0.0050061 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2021-11-12 12:04 | 2021-11-12 14:20 | 2 | 002:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21111200029 | New_Event | Bad Weather | Include | Include | Weather | 136 | 2021-11-12 | 272 | keep | 0 | Nov | 2021 | 0.00018526 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2021-11-12 12:11 | 2021-11-13 13:26 | 13 | 025:15 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO DEL SUB4 A T2 | C21111200073 | New_Event | UG Cable Fault | Include | Include | Equipment | 1515 | 2021-11-12 | 19695 | keep | 0 | Nov | 2021 | 0.013414 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
ARECIBO | 2021-11-12 12:11 | 2021-11-12 14:30 | 100 | 002:19 | P | ESTRUCTURA AVERIADA | 2 X 25 Y 1 X 40 EN CORTE DE LINEA SE ABRIO PUENTES PARA SECCIONALIZAR POSTE PARTIDO | A21111200030 | New_Event | Defective Pole | Include | Include | Equipment | 139 | 2021-11-12 | 13900 | keep | 0 | Nov | 2021 | 0.0094672 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2021-11-12 12:26 | 2021-11-12 15:19 | 80 | 002:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE LINEA A CAJA | R21111200039 | New_Event | Wire Down | Include | Include | Equipment | 173 | 2021-11-12 | 13840 | keep | 0 | Nov | 2021 | 0.0094264 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-11-12 12:29 | 2021-11-12 12:30 | 551 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1204-01 DE LA PORTATIL #22 LLEVA EL 40% DE LA CARGA DEL 1204-03 | S21111200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-12 | 551 | keep | 0 | Nov | 2021 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
FAJARDO | 2021-11-12 12:34 | 2021-11-12 15:04 | 5 | 002:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REMPLAZO PORTAFUSIBLE | R21111200040 | New_Event | Cutout Failure | Include | Include | Equipment | 150 | 2021-11-12 | 750 | keep | 0 | Nov | 2021 | 0.00051082 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-11-12 12:39 | 2021-11-12 12:40 | 643 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21111200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-12 | 643 | keep | 0 | Nov | 2021 | 0.00043794 | 0.00043794 | Momentary | FALSE | FALSE | Not_TMED_Event | 643
BAYAMON | 2021-11-12 12:40 | 2021-11-12 18:09 | 60 | 005:29 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21111200100 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 329 | 2021-11-12 | 19740 | keep | 0 | Nov | 2021 | 0.013445 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2021-11-12 12:49 | 2021-11-12 12:50 | 2635 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO INTERRUPTOR EN SERVICIO | C21111200076 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-11-12 | 2635 | keep | 0 | Nov | 2021 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2021-11-12 12:50 | 2021-11-12 17:31 | 99 | 004:41 | P | PARARRAYOS DEFECTUOSO | 2 X 100 EN CORTES DE LINEA Y SE REEMPLAZO PARARRAYO | C21111200084 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 281 | 2021-11-12 | 27819 | keep | 0 | Nov | 2021 | 0.018947 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
BARRANQUITAS | 2021-11-12 12:51 | 2021-11-12 12:52 | 1604 | 000:01 | T | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | RECERRO INTERRUPTOR EN SERVICIO | C21111120000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1 | 2021-11-12 | 1604 | keep | 0 | Nov | 2021 | 0.0010925 | 0.0010925 | Momentary | FALSE | FALSE | Not_TMED_Event | 1604
BARRANQUITAS | 2021-11-12 12:52 | 2021-11-12 17:20 | 5 | 004:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN XMR REPARO SECUNDARIA | C21111200086 | 1st_after_momentary | Secondary Wire Down | Include | Include | Equipment | 268 | 2021-11-12 | 1340 | keep | 0 | Nov | 2021 | 0.00091267 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-11-12 12:58 | 2021-11-12 15:32 | 50 | 002:34 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21111200051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2021-11-12 | 7700 | keep | 0 | Nov | 2021 | 0.0052444 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-12 13:15 | 2021-11-12 22:12 | 20 | 008:57 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21111200046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 537 | 2021-11-12 | 10740 | keep | 0 | Nov | 2021 | 0.007315 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-11-12 13:21 | 2021-11-12 14:11 | 30 | 000:50 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S21111200104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 50 | 2021-11-12 | 1500 | keep | 0 | Nov | 2021 | 0.0010216 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-11-12 13:59 | 2021-11-12 17:27 | 25 | 003:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | M21111200049 | New_Event |  |  | Include | Wildlife | 208 | 2021-11-12 | 5200 | keep | 0 | Nov | 2021 | 0.0035417 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2021-11-12 14:09 | 2021-11-12 17:58 | 12 | 003:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C21111200088 | New_Event | Secondary Wire Down | Include | Include | Equipment | 229 | 2021-11-12 | 2748 | keep | 0 | Nov | 2021 | 0.0018717 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-11-12 14:11 | 2021-11-12 14:27 | 51 | 000:16 | T | NO SE REPORTO CAUSA | CARGA POR 7902-03 | M21111200050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 16 | 2021-11-12 | 816 | keep | 0 | Nov | 2021 | 0.00055577 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2021-11-12 14:11 | 2021-11-12 14:27 | 721 | 000:16 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR RECIERRE EN OFF SE VERIFICO PERSONAL FUERA DE LAS LINEAS Y SE CERRO INTERRUPTOR LLEVA LA CARGA DEL 7902-02 | M21111200050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 16 | 2021-11-12 | 11536 | keep | 0 | Nov | 2021 | 0.0078571 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
BAYAMON | 2021-11-12 14:13 | 2021-11-12 14:14 | 1633 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO Y SE CERRO POR CONTROL | B21111200000 | Partial_restoration |  |  | Include | Wildlife | 1 | 2021-11-12 | 1633 | keep | 0 | Nov | 2021 | 0.0011122 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-12 14:13 | 2021-11-12 14:14 | 20 | 000:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO 1703-01 QUE LLEVA PARTE DEL 1703-05 | B21111200000 | Partial_restoration |  |  | Include | Wildlife | 1 | 2021-11-12 | 20 | keep | 0 | Nov | 2021 | 1.3622e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-11-12 14:16 | 2021-11-12 16:53 | 15 | 002:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21111100097 | New_Event | Secondary Wire Down | Include | Include | Equipment | 157 | 2021-11-12 | 2355 | keep | 0 | Nov | 2021 | 0.001604 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-11-12 14:21 | 2021-11-12 15:21 | 75 | 001:00 | P | ESTRUCTURA AVERIADA | SE SECCIONALIZO POSTE PARTIDO | B21111200047 | New_Event | Defective Pole | Include | Include | Equipment | 60 | 2021-11-12 | 4500 | keep | 0 | Nov | 2021 | 0.0030649 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2021-11-12 14:30 | 2021-11-12 16:11 | 200 | 001:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO CORTE DE LINEA PARA REPARAR TENSOR ZAFADO PEGANDO CON LINEA PRIMARIA | M21111200051 | New_Event |  |  | Include | Wildlife | 101 | 2021-11-12 | 20200 | keep | 0 | Nov | 2021 | 0.013758 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2021-11-12 14:30 | 2021-11-12 18:45 | 10 | 004:15 | P | ESTRUCTURA AVERIADA | SE PASO TRANSFORMADOR A POSTE NUEVO Y SE CERRO PUENTES | A21111200030 | Partial_restoration | Defective Pole | Include | Include | Equipment | 255 | 2021-11-12 | 2550 | keep | 0 | Nov | 2021 | 0.0017368 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-11-12 14:30 | 2021-11-12 16:13 | 1 | 001:43 | P | OTRAS CAUSAS | 3 X 50 EN CORTE DE LINEA PROBLEMA INTERNO CLIENTE REMPLAZO TRANSFORMADOR PRIVADO AVERIADO | A21111200043 | New_Event | Other Causes | Include | Include | Other | 103 | 2021-11-12 | 103 | keep | 0 | Nov | 2021 | 7.0153e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-12 14:46 | 2021-11-12 14:47 | 400 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1401-08 Y SE CERRO POR SCADA LLEVA PARTE DEL 1303-02 | S21111200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-12 | 400 | keep | 0 | Nov | 2021 | 0.00027244 | 0.00027244 | Momentary | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2021-11-12 14:46 | 2021-11-12 14:47 | 922 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1401-08 Y SE CERRO POR SCADA LLEVA 1346-05 | S21111200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-12 | 922 | keep | 0 | Nov | 2021 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-11-12 14:46 | 2021-11-12 14:47 | 300 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1401-08 Y SE CERRO POR SCADA LLEVA PARTE DEL 1348-08 | S21111200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-12 | 300 | keep | 0 | Nov | 2021 | 0.00020433 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2021-11-12 14:46 | 2021-11-12 14:47 | 135 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1401-08 Y SE CERRO POR SCADA LLEVA 1346-05 PARTE DE 1348-08 Y PARTE DEL 1303-02 | S21111200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-12 | 135 | keep | 0 | Nov | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
BAYAMON | 2021-11-12 14:48 | 2021-11-12 14:59 | 3798 | 000:11 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR PRIMARIO EN EL SUELO | B21111200063 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 11 | 2021-11-12 | 41778 | keep | 0 | Nov | 2021 | 0.028455 | 0.0025868 | Sustained | FALSE | FALSE | Not_TMED_Event | 3798
BAYAMON | 2021-11-12 14:49 | 2021-11-12 16:54 | 1633 | 002:05 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR. SE SECCIONALIZO CONDUCTOR CRUZADO CON TENSOR | B21111200000 | 1st_after_momentary |  |  | Include | Wildlife | 125 | 2021-11-12 | 204125 | keep | 0 | Nov | 2021 | 0.13903 | 0.0011122 | Sustained | FALSE | FALSE | Not_TMED_Event | 1633
BAYAMON | 2021-11-12 14:49 | 2021-11-12 16:54 | 20 | 002:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO 1703-01 QUE LLEVA PARTE DEL 1703-05 | B21111200000 | 1st_after_momentary |  |  | Include | Wildlife | 125 | 2021-11-12 | 2500 | keep | 0 | Nov | 2021 | 0.0017027 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-11-12 14:49 | 2021-11-12 18:54 | 300 | 004:05 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE LEVANTO CONDUCTOR Y SE REEMPLAZO AISLADOR | B21111200050 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 245 | 2021-11-12 | 73500 | keep | 0 | Nov | 2021 | 0.050061 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
GUAYAMA | 2021-11-12 14:51 | 2021-11-12 15:27 | 80 | 000:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE CAMBIO CAJA PRIMARIA QUEMADA | P21111200049 | New_Event | Cutout Failure | Include | Include | Equipment | 36 | 2021-11-12 | 2880 | keep | 0 | Nov | 2021 | 0.0019616 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-11-12 14:53 | 2021-11-12 17:11 | 1 | 002:18 | P | OTRAS CAUSAS | 3 X 5 EN TRANSFORMADOR PROBLEMA DE CLIENTE | M21111200053 | New_Event | Other Causes | Include | Include | Other | 138 | 2021-11-12 | 138 | keep | 0 | Nov | 2021 | 9.3991e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-12 14:59 | 2021-11-12 18:54 | 300 | 003:55 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y SE LEVANTO CONDUCTOR AL ALCANCE DE LA MANO | B21111200050 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 235 | 2021-11-12 | 70500 | keep | 0 | Nov | 2021 | 0.048017 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-11-12 15:03 | 2021-11-12 15:40 | 7 | 000:37 | P | SECUNDARIA/DESGANCHE | ABRIO XMR PARA DESGANCHAR Y REPARAR NEUTRALES | C21111100063 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 37 | 2021-11-12 | 259 | keep | 0 | Nov | 2021 | 0.0001764 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2021-11-12 15:03 | 2021-11-12 16:39 | 1250 | 001:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA SE CERRO CORTE DE LINEA | M21111200031 | Additional_clients | Wire Down | Include | Include | Equipment | 96 | 2021-11-12 | 120000 | keep | 0 | Nov | 2021 | 0.081731 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-12 15:14 | 2021-11-12 16:50 | 6 | 001:36 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21111200115 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 96 | 2021-11-12 | 576 | keep | 0 | Nov | 2021 | 0.00039231 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2021-11-12 15:21 | 2021-11-12 20:49 | 30 | 005:28 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO | B21111200047 | Partial_restoration | Defective Pole | Include | Include | Equipment | 328 | 2021-11-12 | 9840 | keep | 0 | Nov | 2021 | 0.006702 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-12 15:36 | 2021-11-12 17:01 | 30 | 001:25 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | B21111200078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 85 | 2021-11-12 | 2550 | keep | 0 | Nov | 2021 | 0.0017368 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-11-12 15:49 | 2021-11-12 19:13 | 65 | 003:24 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L SE REEMPLAZO AISLADOR | C21111200097 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 204 | 2021-11-12 | 13260 | keep | 0 | Nov | 2021 | 0.0090313 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2021-11-12 15:58 | 2021-11-12 17:42 | 100 | 001:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA CIVILES DESGANCHANDO EN SUS PATIOS OCASIONARON LA INTERRUPCION | S21111200120 | New_Event |  |  | Include | Wildlife | 104 | 2021-11-12 | 10400 | keep | 0 | Nov | 2021 | 0.0070834 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-11-12 15:58 | 2021-11-12 18:21 | 60 | 002:23 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | S21111200121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 143 | 2021-11-12 | 8580 | keep | 0 | Nov | 2021 | 0.0058438 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2021-11-12 15:58 | 2021-11-12 17:45 | 85 | 001:47 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | R21111200043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 107 | 2021-11-12 | 9095 | keep | 0 | Nov | 2021 | 0.0061946 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
YAUCO | 2021-11-12 16:06 | 2021-11-12 17:38 | 100 | 001:32 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P21111200052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2021-11-12 | 9200 | keep | 0 | Nov | 2021 | 0.0062661 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-11-12 16:45 | 2021-11-12 20:18 | 40 | 003:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21111200069 | New_Event | Wire Down | Include | Include | Equipment | 213 | 2021-11-12 | 8520 | keep | 0 | Nov | 2021 | 0.0058029 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-11-12 16:51 | 2021-11-12 18:41 | 40 | 001:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CRUCE POR REPTIL | R21111200046 | New_Event |  |  | Include | Wildlife | 110 | 2021-11-12 | 4400 | keep | 0 | Nov | 2021 | 0.0029968 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-12 16:54 | 2021-11-12 18:40 | 1600 | 001:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | GOI BY-211112-01 SE REPARO CONDUCTOR CRUZADO CON TENSOR | B21111200000 | Partial_restoration |  |  | Include | Wildlife | 106 | 2021-11-12 | 169600 | keep | 0 | Nov | 2021 | 0.11551 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-12 17:04 | 2021-11-12 22:40 | 15 | 005:36 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5KVA POR IGUAL CAPACIDAD | S21111200129 | New_Event | Service Transformer Failure | Include | Include | Equipment | 336 | 2021-11-12 | 5040 | keep | 0 | Nov | 2021 | 0.0034327 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-11-12 17:10 | 2021-11-12 17:11 | 400 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1336-06 Y SE CERRO POR SCADA LLEVA PARTE DEL 1303-02 | S21111200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-12 | 400 | keep | 0 | Nov | 2021 | 0.00027244 | 0.00027244 | Momentary | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2021-11-12 17:10 | 2021-11-12 17:11 | 6481 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1336-06 Y SE CERRO POR SCADA LLEVA PARTE DEL 1303-02 | S21111200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-12 | 6481 | keep | 0 | Nov | 2021 | 0.0044142 | 0.0044142 | Momentary | FALSE | FALSE | Not_TMED_Event | 6481
SAN JUAN | 2021-11-12 17:13 | 2021-11-12 20:09 | 1 | 002:56 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | S21111200130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2021-11-12 | 176 | keep | 0 | Nov | 2021 | 0.00011987 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-11-12 17:34 | 2021-11-13 11:59 | 10 | 018:25 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 50KVA A 4.16KV POR UNO DE LA MISMA CAPACIDAD | P21111200058 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1105 | 2021-11-12 | 11050 | keep | 0 | Nov | 2021 | 0.0075261 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2021-11-12 17:39 | 2021-11-13 09:25 | 120 | 015:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | P21111200059 | New_Event | Wire Down | Include | Include | Equipment | 946 | 2021-11-12 | 113520 | keep | 0 | Nov | 2021 | 0.077318 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2021-11-12 17:50 | 2021-11-12 18:49 | 30 | 000:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA | B21111200078 | New_Event | Wire Down | Include | Include | Equipment | 59 | 2021-11-12 | 1770 | keep | 0 | Nov | 2021 | 0.0012055 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2021-11-12 18:16 | 2021-11-13 12:04 | 100 | 017:48 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21111200116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1068 | 2021-11-12 | 106800 | keep | 0 | Nov | 2021 | 0.072741 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2021-11-12 18:30 | 2021-11-13 09:17 | 3 | 014:47 | P | DESGANCHE | 1 X 8 EN TRANSFORMADOR | C21111200118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 887 | 2021-11-12 | 2661 | keep | 0 | Nov | 2021 | 0.0018124 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-11-12 18:38 | 2021-11-13 11:03 | 25 | 016:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L SE REMPLAZO AISLADOR Y SE REMPLAZO CAJA | S21111200138 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 985 | 2021-11-12 | 24625 | keep | 0 | Nov | 2021 | 0.016772 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2021-11-12 18:51 | 2021-11-12 18:52 | 1648 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21111200052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-12 | 1648 | keep | 0 | Nov | 2021 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
ARECIBO | 2021-11-12 19:25 | 2021-11-12 19:26 | 2888 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA SE CERRO POR SCADA | A21111200053 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-11-12 | 2888 | keep | 0 | Nov | 2021 | 0.001967 | 0.001967 | Momentary | FALSE | FALSE | Not_TMED_Event | 2888
ARECIBO | 2021-11-12 19:26 | 2021-11-12 22:44 | 50 | 003:18 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21111200059 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 198 | 2021-11-12 | 9900 | keep | 0 | Nov | 2021 | 0.0067428 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-11-12 19:43 | 2021-11-13 12:16 | 10 | 016:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21111200056 | New_Event | Wire Down | Include | Include | Equipment | 993 | 2021-11-12 | 9930 | keep | 0 | Nov | 2021 | 0.0067633 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-11-12 20:18 | 2021-11-13 17:53 | 36 | 021:35 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25 X 37.5KVA | C21111200132 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1295 | 2021-11-12 | 46620 | keep | 0 | Nov | 2021 | 0.031753 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
HUMACAO | 2021-11-12 20:26 | 2021-11-13 01:51 | 2354 | 005:25 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR ROTO Y CERRO INTELLIRUPTER 2603-7B ABIERTO LLEVANDO LA CARGA DEL 2604-01 | C21111200134 | New_Event | Wire Down | Include | Include | Equipment | 325 | 2021-11-12 | 765050 | keep | 0 | Nov | 2021 | 0.52107 | 0.0016033 | Sustained | FALSE | FALSE | Not_TMED_Event | 2354
HUMACAO | 2021-11-12 20:26 | 2021-11-13 10:15 | 99 | 013:49 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21111200136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 829 | 2021-11-12 | 82071 | keep | 0 | Nov | 2021 | 0.055898 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
VEGA BAJA | 2021-11-12 20:49 | 2021-11-13 07:08 | 776 | 010:19 | T | SOBRECARGA | DISPARO POR LOCKOUT DE TRANSFORMADOR 9001-00. SE LE TRANSFIRIO EL PARTE AL 9003-06 | B21111200093 | New_Event | Trip Due To Overload | Include | Include | Other | 619 | 2021-11-12 | 480344 | keep | 0 | Nov | 2021 | 0.32716 | 0.00052853 | Sustained | FALSE | FALSE | Not_TMED_Event | 776
VEGA BAJA | 2021-11-12 20:49 | 2021-11-13 00:38 | 2216 | 003:49 | T | SOBRECARGA | DISPARO POR LOCKOUT DE TRANSFORMADOR 9001-00. SE LE TRANSFIRIO EL 85% DE SU CARGA AL 9002-03 | B21111200093 | New_Event | Trip Due To Overload | Include | Include | Other | 229 | 2021-11-12 | 507464 | keep | 0 | Nov | 2021 | 0.34563 | 0.0015093 | Sustained | FALSE | FALSE | Not_TMED_Event | 2216
VEGA BAJA | 2021-11-12 20:49 | 2021-11-12 23:51 | 2610 | 003:02 | T | SOBRECARGA | DISPARO POR LOCKOUT DE TRANSFORMADOR 9001-00. SE LE DEVOLVIO LA CARGA AL 9003-00 | B21111200093 | New_Event | Trip Due To Overload | Include | Include | Other | 182 | 2021-11-12 | 475020 | keep | 0 | Nov | 2021 | 0.32353 | 0.0017777 | Sustained | FALSE | FALSE | Not_TMED_Event | 2610
VEGA BAJA | 2021-11-12 20:49 | 2021-11-12 23:51 | 3076 | 003:02 | T | SOBRECARGA | DISPARO POR LOCKOUT DE TRANSFORMADOR 9001-00. SE LE DEVOLVIO LA CARGA AL 9003-00 | B21111200093 | New_Event | Trip Due To Overload | Include | Include | Other | 182 | 2021-11-12 | 559832 | keep | 0 | Nov | 2021 | 0.3813 | 0.002095 | Sustained | FALSE | FALSE | Not_TMED_Event | 3076
UTUADO | 2021-11-12 21:26 | 2021-11-13 12:13 | 50 | 014:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA PARTIDA SE ABRIO CORTE DE LINEA PARA REPARAR | A21111200061 | New_Event | Wire Down | Include | Include | Equipment | 887 | 2021-11-12 | 44350 | keep | 0 | Nov | 2021 | 0.030207 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-12 22:16 | 2021-11-13 16:34 | 40 | 018:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA NO FUNDIO FUSIBLES | M21111200076 | New_Event | Wire Down | Include | Include | Equipment | 1098 | 2021-11-12 | 43920 | keep | 0 | Nov | 2021 | 0.029914 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-11-12 22:35 | 2021-11-13 14:06 | 70 | 015:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21111200063 | New_Event | Bad Weather | Include | Include | Weather | 931 | 2021-11-12 | 65170 | keep | 0 | Nov | 2021 | 0.044387 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-11-12 23:01 | 2021-11-12 23:58 | 100 | 000:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M11112000080 | New_Event | Bad Weather | Include | Include | Weather | 57 | 2021-11-12 | 5700 | keep | 0 | Nov | 2021 | 0.0038822 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2021-11-13 00:14 | 2021-11-13 08:26 | 6 | 008:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA QUEMADA | R21111300002 | New_Event | Cutout Failure | Include | Include | Equipment | 492 | 2021-11-13 | 2952 | keep | 0 | Nov | 2021 | 0.0020106 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-11-13 00:20 | 2021-11-13 19:59 | 100 | 019:39 | P | CABLE SOTERRADO AVERIADO | AVERIA DEL SU5 AL T16 SE CONSTRUYO AEREO PROVISIONAL DE AEREO EXISTENTE AL T16 | C21111300003 | New_Event | UG Cable Fault | Include | Include | Equipment | 1179 | 2021-11-13 | 117900 | keep | 0 | Nov | 2021 | 0.080301 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-11-13 00:24 | 2021-11-13 08:51 | 100 | 008:27 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA SE PATRULLO | C21111300004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 507 | 2021-11-13 | 50700 | keep | 0 | Nov | 2021 | 0.034532 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-11-13 00:31 | 2021-11-13 10:21 | 80 | 009:50 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21111300001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 590 | 2021-11-13 | 47200 | keep | 0 | Nov | 2021 | 0.032148 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2021-11-13 00:38 | 2021-11-13 06:05 | 1116 | 005:27 | P | SOBRECARGA | CULMINARON LAS PRUEBAS DE TTR AL TRANSFORMADOR 9001-00 Y SE NORMALIZO LAS CARGAS | B21111300000 | Partial_restoration | Trip Due To Overload | Include | Include | Other | 327 | 2021-11-13 | 364932 | keep | 0 | Nov | 2021 | 0.24855 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-13 01:19 | 2021-11-13 11:19 | 4 | 010:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE | R21111300003 | New_Event | Wire Down | Include | Include | Equipment | 600 | 2021-11-13 | 2400 | keep | 0 | Nov | 2021 | 0.0016346 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2021-11-13 02:13 | 2021-11-13 09:57 | 100 | 007:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIAS | C21111300008 | New_Event | Bad Weather | Include | Include | Weather | 464 | 2021-11-13 | 46400 | keep | 0 | Nov | 2021 | 0.031603 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-11-13 03:00 | 2021-11-13 13:23 | 60 | 010:23 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21111300009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 623 | 2021-11-13 | 37380 | keep | 0 | Nov | 2021 | 0.025459 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2021-11-13 03:49 | 2021-11-13 13:03 | 30 | 009:14 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21111300011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 554 | 2021-11-13 | 16620 | keep | 0 | Nov | 2021 | 0.01132 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-11-13 04:08 | 2021-11-13 18:35 | 9 | 014:27 | P | DESGANCHE | 2 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21111300098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 867 | 2021-11-13 | 7803 | keep | 0 | Nov | 2021 | 0.0053146 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2021-11-13 04:37 | 2021-11-13 11:42 | 325 | 007:05 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR. SE REMPLAZO AISLACION Y SE CERRO POR SCADA | B21111300013 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 425 | 2021-11-13 | 138125 | keep | 0 | Nov | 2021 | 0.094076 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2021-11-13 05:04 | 2021-11-13 09:26 | 35 | 004:22 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S21111300005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 262 | 2021-11-13 | 9170 | keep | 0 | Nov | 2021 | 0.0062456 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2021-11-13 05:06 | 2021-11-13 08:59 | 44 | 003:53 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21111300011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2021-11-13 | 10252 | keep | 0 | Nov | 2021 | 0.0069826 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
VEGA BAJA | 2021-11-13 05:27 | 2021-11-13 15:03 | 50 | 009:36 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B21111300015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 576 | 2021-11-13 | 28800 | keep | 0 | Nov | 2021 | 0.019616 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-13 05:28 | 2021-11-13 11:22 | 50 | 005:54 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21111300007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 354 | 2021-11-13 | 17700 | keep | 0 | Nov | 2021 | 0.012055 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-11-13 05:48 | 2021-11-13 11:54 | 90 | 006:06 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO | C21111300014 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 366 | 2021-11-13 | 32940 | keep | 0 | Nov | 2021 | 0.022435 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CAGUAS | 2021-11-13 06:04 | 2021-11-13 13:35 | 90 | 007:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE LEVANTO CONDUCTOR DEL SUELO | C21111300016 | New_Event | Wire Down | Include | Include | Equipment | 451 | 2021-11-13 | 40590 | keep | 0 | Nov | 2021 | 0.027646 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
UTUADO | 2021-11-13 06:05 | 2021-11-13 09:47 | 80 | 003:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA Y VIENTO | A21111300001 | New_Event | Bad Weather | Include | Include | Weather | 222 | 2021-11-13 | 17760 | keep | 0 | Nov | 2021 | 0.012096 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2021-11-13 06:05 | 2021-11-13 06:06 | 1100 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 9002-03 QUE LLEVA A SU VEZ EL 50% DEL 9001-02 | B21111300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-13 | 1100 | keep | 0 | Nov | 2021 | 0.0007492 | 0.0007492 | Momentary | FALSE | FALSE | Not_TMED_Event | 1100
VEGA BAJA | 2021-11-13 06:05 | 2021-11-13 06:06 | 3332 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 9002-03 QUE LLEVA A SU VEZ EL 50% DEL 9001-02 | B21111300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-13 | 3332 | keep | 0 | Nov | 2021 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
VEGA BAJA | 2021-11-13 06:06 | 2021-11-13 16:12 | 1116 | 010:06 | P | SOBRECARGA | CULMINARON LAS PRUEBAS DE TTR AL TRANSFORMADOR 9001-00 Y SE NORMALIZO LAS CARGAS | B21111300000 | Partial_restoration | Trip Due To Overload | Include | Include | Other | 606 | 2021-11-13 | 676296 | keep | 0 | Nov | 2021 | 0.46062 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-11-13 06:56 | 2021-11-13 10:57 | 70 | 004:01 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C21111300023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 241 | 2021-11-13 | 16870 | keep | 0 | Nov | 2021 | 0.01149 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2021-11-13 06:59 | 2021-11-13 07:00 | 3941 | 000:01 | T | DESGANCHE | RECERRO | B21111300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-13 | 3941 | keep | 0 | Nov | 2021 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
BAYAMON | 2021-11-13 07:00 | 2021-11-13 09:24 | 50 | 002:24 | P | DESGANCHE | 1 X 30 SE DESGANCHO EN RISER | B21111300035 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 144 | 2021-11-13 | 7200 | keep | 0 | Nov | 2021 | 0.0049039 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-11-13 07:08 | 2021-11-13 16:24 | 600 | 009:16 | P | SOBRECARGA | DISPARO POR LOCKOUT DE TRANSFORMADOR 9001-00.CULMINARON LAS PRUEBAS DE TTR AL TRANSFORMADOR Y SE NORMALIZO LAS CARGAS | B21111200093 | New_Event | Trip Due To Overload | Include | Include | Other | 556 | 2021-11-13 | 333600 | keep | 0 | Nov | 2021 | 0.22721 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
CAGUAS | 2021-11-13 07:11 | 2021-11-13 07:12 | 1261 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21111300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-13 | 1261 | keep | 0 | Nov | 2021 | 0.00085886 | 0.00085886 | Momentary | FALSE | FALSE | Not_TMED_Event | 1261
CANOVANAS | 2021-11-13 07:21 | 2021-11-13 12:04 | 70 | 004:43 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21111300005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2021-11-13 | 19810 | keep | 0 | Nov | 2021 | 0.013493 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2021-11-13 07:23 | 2021-11-13 12:36 | 100 | 005:13 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P21111300032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 313 | 2021-11-13 | 31300 | keep | 0 | Nov | 2021 | 0.021318 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-13 07:23 | 2021-11-13 09:13 | 7 | 001:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21111300002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 110 | 2021-11-13 | 770 | keep | 0 | Nov | 2021 | 0.00052444 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-11-13 07:37 | 2021-11-13 07:38 | 4431 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21111300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-13 | 4431 | keep | 0 | Nov | 2021 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
ARECIBO | 2021-11-13 07:48 | 2021-11-13 18:30 | 10 | 010:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21111300003 | New_Event | Bad Weather | Include | Include | Weather | 642 | 2021-11-13 | 6420 | keep | 0 | Nov | 2021 | 0.0043726 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2021-11-13 07:56 | 2021-11-13 07:57 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P211113000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-13 | 2100 | keep | 0 | Nov | 2021 | 0.0014303 | 0.0014303 | Momentary | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2021-11-13 07:56 | 2021-11-13 07:57 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P211113000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-13 | 922 | keep | 0 | Nov | 2021 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2021-11-13 07:56 | 2021-11-13 07:57 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P211113000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-13 | 1676 | keep | 0 | Nov | 2021 | 0.0011415 | 0.0011415 | Momentary | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2021-11-13 07:56 | 2021-11-13 07:57 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P211113000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-13 | 2844 | keep | 0 | Nov | 2021 | 0.001937 | 0.001937 | Momentary | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2021-11-13 07:56 | 2021-11-13 07:57 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P211113000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-13 | 2775 | keep | 0 | Nov | 2021 | 0.00189 | 0.00189 | Momentary | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2021-11-13 07:56 | 2021-11-13 07:57 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P211113000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-13 | 1457 | keep | 0 | Nov | 2021 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2021-11-13 07:56 | 2021-11-13 07:57 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P211113000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-13 | 1086 | keep | 0 | Nov | 2021 | 0.00073967 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2021-11-13 07:56 | 2021-11-13 07:57 | 2134 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P211113000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-13 | 2134 | keep | 0 | Nov | 2021 | 0.0014535 | 0.0014535 | Momentary | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2021-11-13 07:56 | 2021-11-13 07:57 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P211113000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-13 | 1464 | keep | 0 | Nov | 2021 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2021-11-13 07:56 | 2021-11-13 07:57 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P211113000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-13 | 1833 | keep | 0 | Nov | 2021 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2021-11-13 07:56 | 2021-11-13 07:57 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P211113000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-13 | 1565 | keep | 0 | Nov | 2021 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2021-11-13 07:56 | 2021-11-13 07:57 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P211113000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-13 | 977 | keep | 0 | Nov | 2021 | 0.00066543 | 0.00066543 | Momentary | FALSE | FALSE | Not_TMED_Event | 977
ARECIBO | 2021-11-13 08:04 | 2021-11-13 17:17 | 10 | 009:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR Y SE REMPLAZO CAJA PRIMARIA AVERIADA | A21111300006 | New_Event | Cutout Failure | Include | Include | Equipment | 553 | 2021-11-13 | 5530 | keep | 0 | Nov | 2021 | 0.0037665 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-11-13 08:05 | 2021-11-13 08:08 | 3718 | 000:03 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S21111300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-13 | 11154 | keep | 0 | Nov | 2021 | 0.0075969 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
YAUCO | 2021-11-13 08:09 | 2021-11-13 08:10 | 1475 | 000:01 | T | DESGANCHE | RECIERRE | P211113000XX | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-13 | 1475 | keep | 0 | Nov | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
BAYAMON | 2021-11-13 08:10 | 2021-11-13 08:11 | 3708 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21111300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-13 | 3708 | keep | 0 | Nov | 2021 | 0.0025255 | 0.0025255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3708
CAGUAS | 2021-11-13 08:10 | 2021-11-13 14:20 | 40 | 006:10 | P | DESGANCHE | 1 X 50 Y DESGANCHE DE BAMBUAS | C21111300032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 370 | 2021-11-13 | 14800 | keep | 0 | Nov | 2021 | 0.01008 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2021-11-13 08:10 | 2021-11-13 10:50 | 50 | 002:40 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21111300036 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 160 | 2021-11-13 | 8000 | keep | 0 | Nov | 2021 | 0.0054488 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-11-13 08:13 | 2021-11-13 13:23 | 4 | 005:10 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CERRARON ORDENES | R21111300007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 310 | 2021-11-13 | 1240 | keep | 0 | Nov | 2021 | 0.00084456 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-11-13 08:18 | 2021-11-13 09:44 | 20 | 001:26 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | S21111300014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 86 | 2021-11-13 | 1720 | keep | 0 | Nov | 2021 | 0.0011715 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-11-13 08:47 | 2021-11-13 20:41 | 60 | 011:54 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R21111300008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 714 | 2021-11-13 | 42840 | keep | 0 | Nov | 2021 | 0.029178 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-11-13 08:51 | 2021-11-13 10:42 | 15 | 001:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21111200065 | New_Event | Secondary Wire Down | Include | Include | Equipment | 111 | 2021-11-13 | 1665 | keep | 0 | Nov | 2021 | 0.001134 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-11-13 09:00 | 2021-11-13 12:27 | 25 | 003:27 | P | CABLE SOTERRADO AVERIADO | SE ABRIO RISER DE SOTERRADO PARA QUE AAA REPARARA AVERIA | S21111300018 | New_Event | UG Cable Fault | Include | Include | Equipment | 207 | 2021-11-13 | 5175 | keep | 0 | Nov | 2021 | 0.0035247 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-11-13 09:04 | 2021-11-13 10:54 | 60 | 001:50 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA Y 1 X 40 EN PROVISIONAL AEREO | B21111300056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 110 | 2021-11-13 | 6600 | keep | 0 | Nov | 2021 | 0.0044952 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-11-13 09:18 | 2021-11-14 09:10 | 25 | 023:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA AVE CRUZO LINEAS SE REMPLAZO PORTAFUSIBLES | A21111300002 | New_Event |  |  | Include | Wildlife | 1432 | 2021-11-13 | 35800 | keep | 0 | Nov | 2021 | 0.024383 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2021-11-13 09:19 | 2021-11-14 11:09 | 15 | 025:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA RETEZO LINEAS | C21111300041 | New_Event | Wire Down | Include | Include | Equipment | 1550 | 2021-11-13 | 23250 | keep | 0 | Nov | 2021 | 0.015835 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-11-13 09:20 | 2021-11-13 09:44 | 1 | 000:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO CONEXIONES SECUNDARIAS | M21111200026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 24 | 2021-11-13 | 24 | keep | 0 | Nov | 2021 | 1.6346e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-13 09:24 | 2021-11-13 09:25 | 3941 | 000:01 | T | DESGANCHE | RECERRO | B21111300000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-13 | 3941 | keep | 0 | Nov | 2021 | 0.0026842 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-13 09:25 | 2021-11-13 11:17 | 50 | 001:52 | P | DESGANCHE | 1 X 30 SE DESGANCHO EN RISER | B21111300035 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 112 | 2021-11-13 | 5600 | keep | 0 | Nov | 2021 | 0.0038141 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2021-11-13 09:32 | 2021-11-13 15:15 | 57 | 005:43 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21111300042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 343 | 2021-11-13 | 19551 | keep | 0 | Nov | 2021 | 0.013316 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
PONCE | 2021-11-13 09:34 | 2021-11-13 16:35 | 145 | 007:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO ABIERTO | P21111300039 | New_Event | Wire Down | Include | Include | Equipment | 421 | 2021-11-13 | 61045 | keep | 0 | Nov | 2021 | 0.041577 | 9.8759e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 145
ARECIBO | 2021-11-13 09:37 | 2021-11-13 14:33 | 100 | 004:56 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21111300016 | New_Event | Bad Weather | Include | Include | Weather | 296 | 2021-11-13 | 29600 | keep | 0 | Nov | 2021 | 0.02016 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2021-11-13 09:50 | 2021-11-13 11:17 | 70 | 001:27 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21111300010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2021-11-13 | 6090 | keep | 0 | Nov | 2021 | 0.0041479 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2021-11-13 10:17 | 2021-11-13 15:12 | 36 | 004:55 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RELIZO DESGANCHE | B21111300071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 295 | 2021-11-13 | 10620 | keep | 0 | Nov | 2021 | 0.0072332 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
BAYAMON | 2021-11-13 10:18 | 2021-11-13 13:54 | 100 | 003:36 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE CARGA DE 1720-07 TRANSFERIDA AL 1709-01 | B21111300072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 216 | 2021-11-13 | 21600 | keep | 0 | Nov | 2021 | 0.014712 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-13 10:23 | 2021-11-14 08:52 | 1 | 022:29 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | A21111300018 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1349 | 2021-11-13 | 1349 | keep | 0 | Nov | 2021 | 0.0009188 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-11-13 10:43 | 2021-11-13 16:51 | 39 | 006:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | C21111300048 | New_Event |  |  | Include | Wildlife | 368 | 2021-11-13 | 14352 | keep | 0 | Nov | 2021 | 0.0097751 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
AGUADILLA | 2021-11-13 10:44 | 2021-11-13 18:46 | 20 | 008:02 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA POR UNO DE 37.5 KVA | M21111300008 | New_Event | Service Transformer Failure | Include | Include | Equipment | 482 | 2021-11-13 | 9640 | keep | 0 | Nov | 2021 | 0.0065658 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-11-13 11:06 | 2021-11-13 11:09 | 1615 | 0:03 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL | S21111300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-11-13 | 4845 | keep | 0 | Nov | 2021 | 0.0032999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
SAN JUAN | 2021-11-13 11:09 | 2021-11-13 15:39 | 100 | 004:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21111300014 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 270 | 2021-11-13 | 27000 | keep | 0 | Nov | 2021 | 0.01839 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-11-13 11:27 | 2021-11-13 11:56 | 1 | 000:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE CON AVE | C21111300058 | New_Event |  |  | Include | Wildlife | 29 | 2021-11-13 | 29 | keep | 0 | Nov | 2021 | 1.9752e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-11-13 11:28 | 2021-11-13 17:58 | 30 | 006:30 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO CORTE DE LINEA | B21111300083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 390 | 2021-11-13 | 11700 | keep | 0 | Nov | 2021 | 0.0079688 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2021-11-13 11:32 | 2021-11-13 11:33 | 4132 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21111300047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-13 | 4132 | keep | 0 | Nov | 2021 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2021-11-13 11:33 | 2021-11-13 18:00 | 1 | 006:27 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | P21111300071 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 387 | 2021-11-13 | 387 | keep | 0 | Nov | 2021 | 0.00026358 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-11-13 11:47 | 2021-11-13 12:42 | 4 | 000:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO CONEXIONES SECUNDARIAS | M21111100015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 55 | 2021-11-13 | 220 | keep | 0 | Nov | 2021 | 0.00014984 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-11-13 11:50 | 2021-11-13 11:51 | 2107 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR LINEA PRIMARIA ARRIADA | A21111300020 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-13 | 2107 | keep | 0 | Nov | 2021 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
ARECIBO | 2021-11-13 11:51 | 2021-11-13 15:50 | 1750 | 003:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES PARA REPARAR LINEA ARRIADA | A21111300043 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 239 | 2021-11-13 | 418250 | keep | 0 | Nov | 2021 | 0.28487 | 0.0011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 1750
PONCE | 2021-11-13 12:03 | 2021-11-13 12:58 | 70 | 000:55 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21111300049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2021-11-13 | 3850 | keep | 0 | Nov | 2021 | 0.0026222 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2021-11-13 12:08 | 2021-11-13 17:03 | 1 | 004:55 | P | OTRAS CAUSAS | 2 X 15 EN BANCO DE TRANSFORMADOR PROBLEMA DEL CLIENTE | C21111300059 | New_Event | Other Causes | Include | Include | Other | 295 | 2021-11-13 | 295 | keep | 0 | Nov | 2021 | 0.00020092 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-11-13 12:13 | 2021-11-13 15:44 | 400 | 003:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA SE CERRO CORTE DE LINEA | A21111200061 | Additional_clients | Wire Down | Include | Include | Equipment | 211 | 2021-11-13 | 84400 | keep | 0 | Nov | 2021 | 0.057484 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2021-11-13 12:17 | 2021-11-13 16:55 | 2 | 004:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO EN BANCO DE TRANSFORMADORES | R21111300015 | New_Event | Wire Down | Include | Include | Equipment | 278 | 2021-11-13 | 556 | keep | 0 | Nov | 2021 | 0.00037869 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2021-11-13 12:29 | 2021-11-13 19:22 | 50 | 006:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21111300026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 413 | 2021-11-13 | 20650 | keep | 0 | Nov | 2021 | 0.014065 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-11-13 12:53 | 2021-11-13 17:01 | 300 | 004:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE LEVANTO CONDUCTOR DEL SUELO | C21111300062 | New_Event | Wire Down | Include | Include | Equipment | 248 | 2021-11-13 | 74400 | keep | 0 | Nov | 2021 | 0.050674 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
HUMACAO | 2021-11-13 12:56 | 2021-11-13 15:00 | 1 | 002:04 | P | OTRAS CAUSAS | 2 X 20 EN BANCO DE TRANSFORMADORES PROBLEMA DEL CLIENTE | C21111300064 | New_Event | Other Causes | Include | Include | Other | 124 | 2021-11-13 | 124 | keep | 0 | Nov | 2021 | 8.4456e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-13 12:59 | 2021-11-14 11:51 | 10 | 022:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO 200 PIES SECUNDARIA Y SE REALIZO DESGANCHE | S21111300038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1372 | 2021-11-13 | 13720 | keep | 0 | Nov | 2021 | 0.0093446 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-13 13:03 | 2021-11-14 11:43 | 10 | 022:40 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S2111300039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1360 | 2021-11-13 | 13600 | keep | 0 | Nov | 2021 | 0.0092629 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-11-13 13:10 | 2021-11-13 16:48 | 92 | 003:38 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C21111300068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 218 | 2021-11-13 | 20056 | keep | 0 | Nov | 2021 | 0.01366 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
PONCE | 2021-11-13 13:13 | 2021-11-13 13:14 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21111300055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-13 | 527 | keep | 0 | Nov | 2021 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
UTUADO | 2021-11-13 13:18 | 2021-11-13 17:46 | 4 | 004:28 | P | PARARRAYOS DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PARARRAYOS DEFECTUOSO | A21111300030 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 268 | 2021-11-13 | 1072 | keep | 0 | Nov | 2021 | 0.00073013 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-11-13 13:27 | 2021-11-13 13:28 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 1206-01 LLEVA LA CARGA DEL 1206-02 | S21111300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-13 | 641 | keep | 0 | Nov | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-11-13 13:27 | 2021-11-13 13:28 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 1206-01 CARGA POR EL 1206-01 | S21111300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-13 | 733 | keep | 0 | Nov | 2021 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
PONCE | 2021-11-13 13:38 | 2021-11-13 15:04 | 50 | 001:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA Y 1 X 5 EN TRANSFORMADOR SE REEMPLAZO UNA CAJA PRIMARIA EN CORTE DE LINEA Y UNA EN TRANSFORMADOR | P21111300059 | New_Event | Cutout Failure | Include | Include | Equipment | 86 | 2021-11-13 | 4300 | keep | 0 | Nov | 2021 | 0.0029287 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-11-13 13:40 | 2021-11-13 14:34 | 10 | 000:54 | P | SECUNDARIA/DESGANCHE | SE ABRE TRANSFORMADOR PARA REALIZAR DESGANCHE SECUNDARIO | P21111300058 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 54 | 2021-11-13 | 540 | keep | 0 | Nov | 2021 | 0.00036779 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-13 14:05 | 2021-11-14 20:00 | 60 | 029:55 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE | B21111400127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1795 | 2021-11-13 | 107700 | keep | 0 | Nov | 2021 | 0.073354 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-11-13 14:08 | 2021-11-13 15:14 | 6 | 001:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21111200069 | New_Event | Secondary Wire Down | Include | Include | Equipment | 66 | 2021-11-13 | 396 | keep | 0 | Nov | 2021 | 0.00026971 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-11-13 14:18 | 2021-11-13 14:19 | 1117 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR 6404-02 EL CUAL LLEVA LA CARGA DEL 6404-01 NO SE REPORTO CAUSA | M21111300016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-13 | 1117 | keep | 0 | Nov | 2021 | 0.00076078 | 0.00076078 | Momentary | FALSE | FALSE | Not_TMED_Event | 1117
MAYAGÃœEZ | 2021-11-13 14:18 | 2021-11-13 14:19 | 1671 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO RECERRO LLEVA LA CARGA DEL 6404-01 NO SE REPORTO CAUSA SE CERRO POR SCADA | M21111300016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-13 | 1671 | keep | 0 | Nov | 2021 | 0.0011381 | 0.0011381 | Momentary | FALSE | FALSE | Not_TMED_Event | 1671
MAYAGÃœEZ | 2021-11-13 14:18 | 2021-11-13 14:19 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR 6404-04 EL CUAL LLEVA LA CARGA DEL 6404-03 NO SE REPORTO CAUSA | M21111300017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-13 | 527 | keep | 0 | Nov | 2021 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
MAYAGÃœEZ | 2021-11-13 14:18 | 2021-11-13 14:19 | 671 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6404-03 | M21111300017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-13 | 671 | keep | 0 | Nov | 2021 | 0.00045702 | 0.00045702 | Momentary | FALSE | FALSE | Not_TMED_Event | 671
CAGUAS | 2021-11-13 14:29 | 2021-11-14 12:52 | 50 | 022:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN C/L MAL TIEMPO | C21111300080 | New_Event | Bad Weather | Include | Include | Weather | 1343 | 2021-11-13 | 67150 | keep | 0 | Nov | 2021 | 0.045736 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-13 14:29 | 2021-11-15 15:09 | 1 | 048:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 30 EN CORTE DE LINEA LINEA PRIMARIA ROTA SE REALIZO DESGANCHE RELACION DEL EVENTO M21111300013 (NOTA: DICE EN BITACORA SE DEJA PENDIENTE PARA LUNES NECESITA DESGANCHE) | M21111500075 | New_Event | Wire Down | Include | Include | Equipment | 2920 | 2021-11-13 | 2920 | keep | 0 | Nov | 2021 | 0.0019888 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-11-13 14:30 | 2021-11-13 14:31 | 1017 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C21111300081 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-13 | 1017 | keep | 0 | Nov | 2021 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
CAGUAS | 2021-11-13 14:31 | 2021-11-13 14:56 | 200 | 000:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CONDUCTOR EN EL SUELO | C21111300085 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 25 | 2021-11-13 | 5000 | keep | 0 | Nov | 2021 | 0.0034055 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-11-13 14:45 | 2021-11-13 17:35 | 4 | 002:50 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21111300025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2021-11-13 | 680 | keep | 0 | Nov | 2021 | 0.00046314 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2021-11-13 14:49 | 2021-11-13 14:52 | 2580 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11100 | R21111300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-13 | 7740 | keep | 0 | Nov | 2021 | 0.0052717 | 0.0017572 | Momentary | FALSE | FALSE | Not_TMED_Event | 2580
CANOVANAS | 2021-11-13 14:49 | 2021-11-13 14:52 | 500 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11100 | R21111300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-13 | 1500 | keep | 0 | Nov | 2021 | 0.0010216 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
ARECIBO | 2021-11-13 14:49 | 2021-11-14 13:07 | 8 | 022:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21111300037 | New_Event | Bad Weather | Include | Include | Weather | 1338 | 2021-11-13 | 10704 | keep | 0 | Nov | 2021 | 0.0072904 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-11-13 14:52 | 2021-11-13 22:58 | 150 | 008:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | M21111300028 | New_Event | Wire Down | Include | Include | Equipment | 486 | 2021-11-13 | 72900 | keep | 0 | Nov | 2021 | 0.049652 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-11-13 14:52 | 2021-11-13 18:54 | 80 | 004:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR ROTO EN TRONCAL DEL ALIMENTADOR | M21111300078 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 242 | 2021-11-13 | 19360 | keep | 0 | Nov | 2021 | 0.013186 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2021-11-13 14:56 | 2021-11-13 17:35 | 1017 | 002:39 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA RETIRAR PELIGRO DE CONDUCTOR DEL SUELO | C21111300085 | Additional_clients | Wire Down | Include | Include | Equipment | 159 | 2021-11-13 | 161703 | keep | 0 | Nov | 2021 | 0.11014 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2021-11-13 15:17 | 2021-11-13 15:51 | 4 | 000:34 | P | HERRAJE ROTO O PODRIDO | SE REEMPLAZO HOT CLAMP PODRIDO | R21111300021 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 34 | 2021-11-13 | 136 | keep | 0 | Nov | 2021 | 9.2629e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-11-13 15:31 | 2021-11-13 18:55 | 60 | 003:24 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21111300046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 204 | 2021-11-13 | 12240 | keep | 0 | Nov | 2021 | 0.0083366 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-11-13 15:34 | 2021-11-13 20:00 | 100 | 004:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21111300046 | New_Event | Wire Down | Include | Include | Equipment | 266 | 2021-11-13 | 26600 | keep | 0 | Nov | 2021 | 0.018117 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-11-13 16:08 | 2021-11-13 17:40 | 36 | 001:32 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C21111300092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 92 | 2021-11-13 | 3312 | keep | 0 | Nov | 2021 | 0.0022558 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
PONCE | 2021-11-13 16:08 | 2021-11-13 16:50 | 8 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P21111300069 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2021-11-13 | 336 | keep | 0 | Nov | 2021 | 0.00022885 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2021-11-13 16:14 | 2021-11-13 16:40 | 12 | 000:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REMPLAZAR CONEXIONES EN LINEA SECUNDARIA | P21111300070 | New_Event | Secondary Wire Down | Include | Include | Equipment | 26 | 2021-11-13 | 312 | keep | 0 | Nov | 2021 | 0.0002125 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-11-13 16:23 | 2021-11-14 09:17 | 5 | 016:54 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | C21111300096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1014 | 2021-11-13 | 5070 | keep | 0 | Nov | 2021 | 0.0034532 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2021-11-13 16:24 | 2021-11-13 16:38 | 100 | 000:14 | P | SOBRECARGA | DISPARO POR LOCKOUT DE TRANSFORMADOR 9001-00.CULMINARON LAS PRUEBAS DE TTR AL TRANSFORMADOR Y SE NORMALIZO LAS CARGAS | B21111200093 | New_Event | Trip Due To Overload | Include | Include | Other | 14 | 2021-11-13 | 1400 | keep | 0 | Nov | 2021 | 0.00095353 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-11-13 16:51 | 2021-11-14 13:04 | 100 | 020:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO LINEA PRIMARIA PARTIDA SE CERRO CORTE DE LINEA | M21111300063 | New_Event | Wire Down | Include | Include | Equipment | 1213 | 2021-11-13 | 121300 | keep | 0 | Nov | 2021 | 0.082617 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-11-13 16:56 | 2021-11-14 09:31 | 40 | 016:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA | M21111300064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 995 | 2021-11-13 | 39800 | keep | 0 | Nov | 2021 | 0.027108 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2021-11-13 16:58 | 2021-11-13 18:04 | 5 | 001:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REMPLAZAR CONEXIONES EN LINEA SECUNDARIA | P21111300072 | New_Event | Secondary Wire Down | Include | Include | Equipment | 66 | 2021-11-13 | 330 | keep | 0 | Nov | 2021 | 0.00022476 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-11-13 17:08 | 2021-11-14 12:03 | 80 | 018:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE POR AVE | C21113000103 | New_Event |  |  | Include | Wildlife | 1135 | 2021-11-13 | 90800 | keep | 0 | Nov | 2021 | 0.061843 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2021-11-13 17:12 | 2021-11-14 12:10 | 8 | 018:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C21111300104 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1138 | 2021-11-13 | 9104 | keep | 0 | Nov | 2021 | 0.0062007 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-11-13 17:29 | 2021-11-13 17:30 | 128 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 3009-02 LLEVANDO LAS CARGAS DEL 3009-03 Y 3009-04 | C21111300106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-13 | 128 | keep | 0 | Nov | 2021 | 8.718e-05 | 8.718e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 128
CAGUAS | 2021-11-13 17:29 | 2021-11-13 17:30 | 273 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 3009-02 LLEVANDO LAS CARGAS DEL 3009-03 Y 3009-04 | C21111300106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-13 | 273 | keep | 0 | Nov | 2021 | 0.00018594 | 0.00018594 | Momentary | FALSE | FALSE | Not_TMED_Event | 273
CAGUAS | 2021-11-13 17:29 | 2021-11-13 17:30 | 1772 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 3009-02 LLEVANDO LAS CARGAS DEL 3009-03 Y 3009-04 | C21111300106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-13 | 1772 | keep | 0 | Nov | 2021 | 0.0012069 | 0.0012069 | Momentary | FALSE | FALSE | Not_TMED_Event | 1772
CAGUAS | 2021-11-13 17:30 | 2021-11-13 18:13 | 50 | 000:43 | P | NO SE REPORTO CAUSA | 1 X 140 Y 1 X 100 EN CORTES DE LINEA | C21111300108 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 43 | 2021-11-13 | 2150 | keep | 0 | Nov | 2021 | 0.0014644 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-11-13 17:35 | 2021-11-13 19:24 | 200 | 001:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR DEL SUELO | C21111300085 | Partial_restoration | Wire Down | Include | Include | Equipment | 109 | 2021-11-13 | 21800 | keep | 0 | Nov | 2021 | 0.014848 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-11-13 18:05 | 2021-11-14 15:20 | 50 | 021:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN C/L SE REEMPLAZARON DISCOS ROTOS | C21111300116 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1275 | 2021-11-13 | 63750 | keep | 0 | Nov | 2021 | 0.04342 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-11-13 18:10 | 2021-11-13 18:11 | 4188 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21111300027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-13 | 4188 | keep | 0 | Nov | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
VEGA BAJA | 2021-11-13 18:14 | 2021-11-14 15:26 | 500 | 021:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO A MACHETE Y SE NORMALIZO LA CATGA | B21111300055 | New_Event | Wire Down | Include | Include | Equipment | 1272 | 2021-11-13 | 636000 | keep | 0 | Nov | 2021 | 0.43318 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CANOVANAS | 2021-11-13 18:16 | 2021-11-13 20:58 | 15 | 002:42 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | R21113000028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 162 | 2021-11-13 | 2430 | keep | 0 | Nov | 2021 | 0.0016551 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-11-13 18:26 | 2021-11-15 10:50 | 6 | 040:24 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 37.5 KVA X 37.5 KVA | A21111300056 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2424 | 2021-11-13 | 14544 | keep | 0 | Nov | 2021 | 0.0099059 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-11-13 19:26 | 2021-11-14 10:15 | 75 | 014:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA DE 100 AMP | M21111300104 | New_Event | Cutout Failure | Include | Include | Equipment | 889 | 2021-11-13 | 66675 | keep | 0 | Nov | 2021 | 0.045412 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2021-11-13 19:30 | 2021-11-13 19:31 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21111300106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-13 | 3458 | keep | 0 | Nov | 2021 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
ARECIBO | 2021-11-13 19:35 | 2021-11-14 08:39 | 75 | 013:04 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21111300064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 784 | 2021-11-13 | 58800 | keep | 0 | Nov | 2021 | 0.040048 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2021-11-13 19:38 | 2021-11-13 19:40 | 2126 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C21111300124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-13 | 4252 | keep | 0 | Nov | 2021 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
CAGUAS | 2021-11-13 20:00 | 2021-11-13 20:18 | 1922 | 000:18 | T | NO SE REPORTO CAUSA | DISPARO SE VERIFICO PERSONAL FUERA | C21111300130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 18 | 2021-11-13 | 34596 | keep | 0 | Nov | 2021 | 0.023563 | 0.0013091 | Sustained | FALSE | FALSE | Not_TMED_Event | 1922
HUMACAO | 2021-11-13 20:49 | 2021-11-13 20:52 | 1891 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5300 | C21113000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-13 | 5673 | keep | 0 | Nov | 2021 | 0.0038639 | 0.001288 | Momentary | FALSE | FALSE | Not_TMED_Event | 1891
HUMACAO | 2021-11-13 20:49 | 2021-11-13 20:52 | 1250 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5300 | C21113000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-13 | 3750 | keep | 0 | Nov | 2021 | 0.0025541 | 0.00085137 | Momentary | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2021-11-13 20:49 | 2021-11-13 20:52 | 2141 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5300 | C21113000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-13 | 6423 | keep | 0 | Nov | 2021 | 0.0043747 | 0.0014582 | Momentary | FALSE | FALSE | Not_TMED_Event | 2141
HUMACAO | 2021-11-13 20:49 | 2021-11-13 20:52 | 1827 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5300 | C21113000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-13 | 5481 | keep | 0 | Nov | 2021 | 0.0037331 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
CANOVANAS | 2021-11-13 21:17 | 2021-11-13 22:35 | 35 | 001:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ABIERTO EN SALIDA DE CAJA PRIMARIA | R21111300031 | New_Event | Wire Down | Include | Include | Equipment | 78 | 2021-11-13 | 2730 | keep | 0 | Nov | 2021 | 0.0018594 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2021-11-13 21:29 | 2021-11-14 20:05 | 295 | 022:36 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZARON DISCOS QUEMADOS A CONSECUENCIA DE AVERIA EN LA LINEA 5200 | C21111400166 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1356 | 2021-11-13 | 400020 | keep | 0 | Nov | 2021 | 0.27245 | 0.00020092 | Sustained | FALSE | FALSE | Not_TMED_Event | 295
ARECIBO | 2021-11-13 22:10 | 2021-11-13 23:20 | 20 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A21111300035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2021-11-13 | 1400 | keep | 0 | Nov | 2021 | 0.00095353 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-11-13 22:37 | 2021-11-14 11:30 | 20 | 012:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN RISER POR MAL TIEMPO | P21111300077 | New_Event | Bad Weather | Include | Include | Weather | 773 | 2021-11-13 | 15460 | keep | 0 | Nov | 2021 | 0.01053 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-11-14 00:55 | 2021-11-14 00:56 | 2608 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21111400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 2608 | keep | 0 | Nov | 2021 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
BAYAMON | 2021-11-14 00:57 | 2021-11-14 11:01 | 20 | 010:04 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21111400001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 604 | 2021-11-14 | 12080 | keep | 0 | Nov | 2021 | 0.0082276 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-11-14 01:15 | 2021-11-14 01:16 | 1983 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1801-02 QUE A SU VEZ LLEVA LA CARGA DEL 1711-04 | B21111400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 1983 | keep | 0 | Nov | 2021 | 0.0013506 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-11-14 01:15 | 2021-11-14 01:16 | 186 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1801-02 QUE A SU VEZ LLEVA LA CARGA DEL 1711-04 | B21111400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 186 | keep | 0 | Nov | 2021 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
SAN JUAN | 2021-11-14 01:32 | 2021-11-14 01:33 | 1681 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-04 QUE A SU VEZ LA CARGA DE LOS ALIMENTADORES 1303-1 Y 1346-06 SE PROBO POR CONTROL QUEDO EN SERVICIO. 1303-4 NO ESTUBO FUERA PARA ESTE PERIODO YA QUE LA CARGA ESTA TRANSFERIDA A OTRO INTERRUPTOR | S21111400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 1681 | keep | 0 | Nov | 2021 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-11-14 01:32 | 2021-11-14 01:33 | 259 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21111400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 259 | keep | 0 | Nov | 2021 | 0.0001764 | 0.0001764 | Momentary | FALSE | FALSE | Not_TMED_Event | 259
SAN JUAN | 2021-11-14 01:32 | 2021-11-14 01:33 | 1598 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-04 QUE A SU VEZ LA CARGA DE LOS ALIMENTADORES 1303-1 Y 1346-06 SE PROBO POR CONTROL QUEDO EN SERVICIO. 1303-4 NO ESTUBO FUERA PARA ESTE PERIODO YA QUE LA CARGA ESTA TRANSFERIDA A OTRO INTERRUPTOR | S21111400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 1598 | keep | 0 | Nov | 2021 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
CANOVANAS | 2021-11-14 02:25 | 2021-11-14 11:40 | 40 | 009:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | R21111400002 | New_Event |  |  | Include | Wildlife | 555 | 2021-11-14 | 22200 | keep | 0 | Nov | 2021 | 0.01512 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-11-14 02:29 | 2021-11-14 09:39 | 40 | 007:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 Y 1 X 15 EN C/L MAL TIEMPO | R21111400003 | New_Event | Bad Weather | Include | Include | Weather | 430 | 2021-11-14 | 17200 | keep | 0 | Nov | 2021 | 0.011715 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2021-11-14 03:47 | 2021-11-14 03:48 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21111400005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 1192 | keep | 0 | Nov | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
BAYAMON | 2021-11-14 04:24 | 2021-11-14 10:01 | 200 | 005:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 100 EN RISER HACIA SU-3. SE REPARO PUENTE PRIMARIO DE LINEA A CAJA EN RISER A CAUSA DE VEHICULO IMPACTO POSTE Y PARTIO 3 POSTES CONSECUENTES | B21114000005 | New_Event |  |  | Include | Wildlife | 337 | 2021-11-14 | 67400 | keep | 0 | Nov | 2021 | 0.045906 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2021-11-14 04:24 | 2021-11-14 12:15 | 50 | 007:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L MAL TIEMPO | C21111400002 | New_Event | Bad Weather | Include | Include | Weather | 471 | 2021-11-14 | 23550 | keep | 0 | Nov | 2021 | 0.01604 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-14 04:34 | 2021-11-14 12:43 | 10 | 008:09 | P | ESTRUCTURA AVERIADA | POSTE PARTIDO. SE RELOCALIZO LINEA PRIMARIA A OTRO POSTE CON TRANSFORMADOR | B21111400010 | New_Event | Defective Pole | Include | Include | Equipment | 489 | 2021-11-14 | 4890 | keep | 0 | Nov | 2021 | 0.0033306 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-11-14 04:41 | 2021-11-14 04:42 | 128 | 000:01 | T | DESGANCHE | RECIERRE 3009-02 LLEVANDO LA CARGA DEL 3009-03 Y 3009-04 | C21111400004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-14 | 128 | keep | 0 | Nov | 2021 | 8.718e-05 | 8.718e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 128
CAGUAS | 2021-11-14 04:41 | 2021-11-14 04:42 | 273 | 000:01 | T | DESGANCHE | RECIERRE 3009-02 LLEVANDO LA CARGA DEL 3009-03 Y 3009-04 | C21111400004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-14 | 273 | keep | 0 | Nov | 2021 | 0.00018594 | 0.00018594 | Momentary | FALSE | FALSE | Not_TMED_Event | 273
CAGUAS | 2021-11-14 04:41 | 2021-11-14 04:42 | 1772 | 000:01 | T | DESGANCHE | RECIERRE 3009-02 LLEVANDO LA CARGA DEL 3009-03 Y 3009-04 | C21111400004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-14 | 1772 | keep | 0 | Nov | 2021 | 0.0012069 | 0.0012069 | Momentary | FALSE | FALSE | Not_TMED_Event | 1772
CAGUAS | 2021-11-14 04:42 | 2021-11-14 10:36 | 100 | 005:54 | P | DESGANCHE | 1 X 100 EN C/L | C21111400005 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 354 | 2021-11-14 | 35400 | keep | 0 | Nov | 2021 | 0.024111 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-11-14 06:08 | 2021-11-14 06:09 | 1339 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21111400009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 1339 | keep | 0 | Nov | 2021 | 0.00091199 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
MAYAGÃœEZ | 2021-11-14 06:08 | 2021-11-14 19:05 | 470 | 012:57 | T | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO SALIDA SOTERRADA AVERIADA DEL INTERRUPTOR 6601-02 Y SE PASO LA CARGA AL 6601-03 | M21111400042 | New_Event | UG Cable Fault | Include | Include | Equipment | 777 | 2021-11-14 | 365190 | keep | 0 | Nov | 2021 | 0.24873 | 0.00032011 | Sustained | FALSE | FALSE | Not_TMED_Event | 470
BAYAMON | 2021-11-14 06:23 | 2021-11-14 12:49 | 20 | 006:26 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21111400026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 386 | 2021-11-14 | 7720 | keep | 0 | Nov | 2021 | 0.0052581 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-11-14 07:17 | 2021-11-14 07:18 | 1984 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO LLEVA CARGA 1911-7 SE PROBO POR CONTROL QUEDO EN SERVICIO | S21111400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 1984 | keep | 0 | Nov | 2021 | 0.0013513 | 0.0013513 | Momentary | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2021-11-14 07:17 | 2021-11-14 07:18 | 577 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1529-12 | S21111400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 577 | keep | 0 | Nov | 2021 | 0.00039299 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
CAGUAS | 2021-11-14 07:37 | 2021-11-14 12:55 | 9 | 005:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C21111400018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 318 | 2021-11-14 | 2862 | keep | 0 | Nov | 2021 | 0.0019493 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
HUMACAO | 2021-11-14 07:38 | 2021-11-14 11:18 | 200 | 003:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 Y 1 X 80 EN C/L | C21111400019 | New_Event | Bad Weather | Include | Include | Weather | 220 | 2021-11-14 | 44000 | keep | 0 | Nov | 2021 | 0.029968 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-11-14 08:02 | 2021-11-14 10:17 | 4 | 002:15 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21111400018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2021-11-14 | 540 | keep | 0 | Nov | 2021 | 0.00036779 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
FAJARDO | 2021-11-14 08:07 | 2021-11-14 12:00 | 40 | 003:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21111400005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2021-11-14 | 9320 | keep | 0 | Nov | 2021 | 0.0063478 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2021-11-14 08:31 | 2021-11-14 15:05 | 100 | 006:34 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR | C21111400025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 394 | 2021-11-14 | 39400 | keep | 0 | Nov | 2021 | 0.026835 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2021-11-14 08:32 | 2021-11-14 08:33 | 4188 | 000:01 | T | OTRAS CAUSAS | RECIERRE | R21111400010 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-11-14 | 4188 | keep | 0 | Nov | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
PONCE | 2021-11-14 08:34 | 2021-11-14 13:05 | 80 | 004:31 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA POR DESGANCHE | P21111400006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 271 | 2021-11-14 | 21680 | keep | 0 | Nov | 2021 | 0.014766 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2021-11-14 08:51 | 2021-11-14 08:52 | 4188 | 000:01 | T | OTRAS CAUSAS | RECIERRE | R21111400010 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-11-14 | 4188 | keep | 0 | Nov | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2021-11-14 09:08 | 2021-11-14 10:05 | 4188 | 000:57 | T | OTRAS CAUSAS | SE SECCIONALIZO PARARRAYOS AVERIADOS EN SUBESTACION PRIVADA | R21111400010 | 1st_after_momentary | Other Causes | Include | Include | Other | 57 | 2021-11-14 | 238716 | keep | 0 | Nov | 2021 | 0.16259 | 0.0028524 | Sustained | FALSE | FALSE | Not_TMED_Event | 4188
ARECIBO | 2021-11-14 09:10 | 2021-11-14 09:11 | 1227 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DEL INTERRUPTOR | A21111400001 | Additional_clients |  |  | Include | Wildlife | 1 | 2021-11-14 | 1227 | keep | 0 | Nov | 2021 | 0.0008357 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-11-14 09:11 | 2021-11-14 14:40 | 25 | 005:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA AVE CRUZO LINEAS SE REMPLAZO PORTAFUSIBLES | A21111300002 | 1st_after_momentary |  |  | Include | Wildlife | 329 | 2021-11-14 | 8225 | keep | 0 | Nov | 2021 | 0.005602 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-11-14 09:15 | 2021-11-15 15:47 | 4 | 030:32 | P | ESTRUCTURA AVERIADA | REEMPLAZO DE POSTE PARTIDO | S21111400025 | New_Event | Defective Pole | Include | Include | Equipment | 1832 | 2021-11-14 | 7328 | keep | 0 | Nov | 2021 | 0.0049911 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2021-11-14 09:25 | 2021-11-14 09:45 | 2 | 000:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | A21111300057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 20 | 2021-11-14 | 40 | keep | 0 | Nov | 2021 | 2.7244e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2021-11-14 09:46 | 2021-11-14 13:43 | 8 | 003:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN XMR REPARO SECUNDARIA | C21111400033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 237 | 2021-11-14 | 1896 | keep | 0 | Nov | 2021 | 0.0012914 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-11-14 10:01 | 2021-11-15 01:37 | 180 | 015:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE INSTALARON TRES POSTES PARTIDOS IMPACTADOS POR UN AUTO Y SE REESTABLECIO SERVICIO | B21111400065 | New_Event |  |  | Include | Wildlife | 936 | 2021-11-14 | 168480 | keep | 0 | Nov | 2021 | 0.11475 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
CANOVANAS | 2021-11-14 10:05 | 2021-11-14 10:54 | 836 | 000:49 | P | OTRAS CAUSAS | SE SECCIONALIZO PARARRAYOS AVERIADOS EN SUBESTACION PRIVADA Y CERRO MACHETES | R21111400010 | New_Event | Other Causes | Include | Include | Other | 49 | 2021-11-14 | 40964 | keep | 0 | Nov | 2021 | 0.0279 | 0.0005694 | Sustained | FALSE | FALSE | Not_TMED_Event | 836
BAYAMON | 2021-11-14 10:18 | 2021-11-14 14:15 | 150 | 003:57 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | S21111400007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 237 | 2021-11-14 | 35550 | keep | 0 | Nov | 2021 | 0.024213 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-11-14 10:19 | 2021-11-14 12:36 | 80 | 002:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | M21111400032 | New_Event | Wire Down | Include | Include | Equipment | 137 | 2021-11-14 | 10960 | keep | 0 | Nov | 2021 | 0.0074648 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2021-11-14 10:23 | 2021-11-14 11:53 | 11 | 001:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR RATA CRUZO FASE | P21111400016 | New_Event |  |  | Include | Wildlife | 90 | 2021-11-14 | 990 | keep | 0 | Nov | 2021 | 0.00067428 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2021-11-14 10:24 | 2021-11-14 14:20 | 25 | 003:56 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU-11 Y 1 X 20 EN CORTE DE LINEA | B21111400056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 236 | 2021-11-14 | 5900 | keep | 0 | Nov | 2021 | 0.0040185 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2021-11-14 10:42 | 2021-11-14 11:56 | 50 | 001:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | P21111400022 | New_Event |  |  | Include | Wildlife | 74 | 2021-11-14 | 3700 | keep | 0 | Nov | 2021 | 0.0025201 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-11-14 10:58 | 2021-11-14 10:59 | 351 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21111400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 351 | keep | 0 | Nov | 2021 | 0.00023906 | 0.00023906 | Momentary | FALSE | FALSE | Not_TMED_Event | 351
SAN JUAN | 2021-11-14 11:17 | 2021-11-14 13:09 | 12 | 001:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA Y REMPLAZO TOMA Y DESGANCHE | S21111400000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 112 | 2021-11-14 | 1344 | keep | 0 | Nov | 2021 | 0.00091539 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-11-14 11:28 | 2021-11-14 16:33 | 45 | 005:05 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR AVERIADO | P21111400029 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 305 | 2021-11-14 | 13725 | keep | 0 | Nov | 2021 | 0.009348 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2021-11-14 11:32 | 2021-11-14 11:33 | 2190 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M21111400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-14 | 2190 | keep | 0 | Nov | 2021 | 0.0014916 | 0.0014916 | Momentary | FALSE | FALSE | Not_TMED_Event | 2190
MAYAGÃœEZ | 2021-11-14 11:33 | 2021-11-15 12:00 | 100 | 024:27 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO ENREDADERA SOBRE LA LINEA | M21111400105 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1467 | 2021-11-14 | 146700 | keep | 0 | Nov | 2021 | 0.099917 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-11-14 11:37 | 2021-11-14 15:19 | 100 | 003:42 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21111400039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2021-11-14 | 22200 | keep | 0 | Nov | 2021 | 0.01512 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-11-14 11:49 | 2021-11-14 11:57 | 1339 | 000:08 | T | CABLE SOTERRADO AVERIADO | SE ABRIO INTERRUPTOR PARAR CERRAR AMARRE CON 6601-02 PROBO MALO POR SALIDA SOTERRADA AVERIADA EN ALIM 6601-02 | M21111400042 | New_Event | UG Cable Fault | Include | Include | Equipment | 8 | 2021-11-14 | 10712 | keep | 0 | Nov | 2021 | 0.0072959 | 0.00091199 | Sustained | FALSE | FALSE | Not_TMED_Event | 1339
MAYAGÃœEZ | 2021-11-14 12:17 | 2021-11-14 12:22 | 2483 | 000:05 | T | CABLE SOTERRADO AVERIADO | SE ABRIO INTERRUPTOR PARAR CERRAR AMARRE CON 6601-02 PROBO MALO POR SALIDA SOTERRADA AVERIADA EN ALIM 6601-02 | M21111400000 | New_Event | UG Cable Fault | Include | Include | Equipment | 5 | 2021-11-14 | 12415 | keep | 0 | Nov | 2021 | 0.0084558 | 0.0016912 | Momentary | FALSE | FALSE | Not_TMED_Event | 2483
BAYAMON | 2021-11-14 12:28 | 2021-11-14 17:52 | 15 | 005:24 | P | NO SE REPORTO CAUSA | 2 X 15 EN TRANSFORMADOR | S21111400011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 324 | 2021-11-14 | 4860 | keep | 0 | Nov | 2021 | 0.0033101 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-11-14 12:33 | 2021-11-14 12:34 | 150 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1801-05 LLEVANDO PARTE 1801-01 | B21111400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 150 | keep | 0 | Nov | 2021 | 0.00010216 | 0.00010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2021-11-14 12:33 | 2021-11-14 12:34 | 112 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1801-05 LLEVANDO PARTE 1801-01 | B21111400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 112 | keep | 0 | Nov | 2021 | 7.6283e-05 | 7.6283e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 112
VEGA BAJA | 2021-11-14 12:45 | 2021-11-14 17:39 | 150 | 004:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | B21111400064 | New_Event | Wire Down | Include | Include | Equipment | 294 | 2021-11-14 | 44100 | keep | 0 | Nov | 2021 | 0.030036 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-11-14 12:47 | 2021-11-14 14:07 | 100 | 001:20 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21111400052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2021-11-14 | 8000 | keep | 0 | Nov | 2021 | 0.0054488 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2021-11-14 13:09 | 2021-11-14 18:49 | 80 | 005:40 | P | DESGANCHE | 2 X 45 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21111400039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 340 | 2021-11-14 | 27200 | keep | 0 | Nov | 2021 | 0.018526 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2021-11-14 13:10 | 2021-11-14 13:33 | 7 | 000:23 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | R21111400033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 23 | 2021-11-14 | 161 | keep | 0 | Nov | 2021 | 0.00010966 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-11-14 13:18 | 2021-11-14 15:50 | 60 | 002:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES QUEMADO | A21111400009 | New_Event | Cutout Failure | Include | Include | Equipment | 152 | 2021-11-14 | 9120 | keep | 0 | Nov | 2021 | 0.0062116 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-11-14 13:32 | 2021-11-14 18:23 | 150 | 004:51 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 80 EN CORTE DE LINEA | S21111400013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 291 | 2021-11-14 | 43650 | keep | 0 | Nov | 2021 | 0.02973 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2021-11-14 14:00 | 2021-11-14 18:13 | 85 | 004:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P21111400041 | New_Event |  |  | Include | Wildlife | 253 | 2021-11-14 | 21505 | keep | 0 | Nov | 2021 | 0.014647 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
FAJARDO | 2021-11-14 14:01 | 2021-11-14 19:00 | 45 | 004:59 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | R21111400034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 299 | 2021-11-14 | 13455 | keep | 0 | Nov | 2021 | 0.0091641 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2021-11-14 14:03 | 2021-11-14 16:20 | 80 | 002:17 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21111400014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 137 | 2021-11-14 | 10960 | keep | 0 | Nov | 2021 | 0.0074648 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2021-11-14 14:27 | 2021-11-14 16:02 | 6 | 001:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIAS | C21111400046 | New_Event | Bad Weather | Include | Include | Weather | 95 | 2021-11-14 | 570 | keep | 0 | Nov | 2021 | 0.00038822 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-11-14 14:30 | 2021-11-14 14:57 | 14 | 000:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21111300060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 27 | 2021-11-14 | 378 | keep | 0 | Nov | 2021 | 0.00025745 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2021-11-14 14:32 | 2021-11-14 14:55 | 1339 | 000:23 | T | CABLE SOTERRADO AVERIADO | SE ABRIO INTERRUPTOR PARAR CERRAR AMARRE 6601-01 Y 6601-02 PROBO MALO POR SALIDA SOTERRADA AVERIADA EN ALIM 6601-02 | M21111400067 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 23 | 2021-11-14 | 30797 | keep | 0 | Nov | 2021 | 0.020976 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-14 14:33 | 2021-11-14 14:35 | 600 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1346-05 UN 100% Y PARTE DE LA CARGA DEL 1303-02 Y 1348-08 | S21111400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-14 | 1200 | keep | 0 | Nov | 2021 | 0.00081731 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2021-11-14 14:33 | 2021-11-14 14:35 | 922 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1346-05 UN 100% Y PARTE DE LA CARGA DEL 1303-02 Y 1348-08 | S21111400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-14 | 1844 | keep | 0 | Nov | 2021 | 0.0012559 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-11-14 14:33 | 2021-11-14 14:35 | 500 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1346-05 UN 100% Y PARTE DE LA CARGA DEL 1303-02 Y 1348-08 | S21111400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-14 | 1000 | keep | 0 | Nov | 2021 | 0.0006811 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2021-11-14 14:33 | 2021-11-14 14:35 | 135 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1346-05 UN 100% Y PARTE DE LA CARGA DEL 1303-02 Y 1348-08 | S21111400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-14 | 270 | keep | 0 | Nov | 2021 | 0.0001839 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
BAYAMON | 2021-11-14 14:43 | 2021-11-14 17:31 | 50 | 002:48 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21111400068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 168 | 2021-11-14 | 8400 | keep | 0 | Nov | 2021 | 0.0057212 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-11-14 14:43 | 2021-11-14 15:13 | 2216 | 000:30 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR SEGURIDAD Y DAR DESPEJE DE LINEA VIVA PARA PODER TRABAJAR UN PUENTE ABIERTO EN EL 9002-03 CON EL EVENTO B21111400064 | B21111400000 | New_Event | Wire Down | Include | Include | Equipment | 30 | 2021-11-14 | 66480 | keep | 0 | Nov | 2021 | 0.045279 | 0.0015093 | Sustained | FALSE | FALSE | Not_TMED_Event | 2216
SAN JUAN | 2021-11-14 15:01 | 2021-11-14 15:03 | 600 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1346-05 UN 100% Y PARTE DE LA CARGA DEL 1303-02 Y 1348-08 | S21111400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-14 | 1200 | keep | 0 | Nov | 2021 | 0.00081731 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2021-11-14 15:01 | 2021-11-14 15:03 | 922 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1346-05 UN 100% Y PARTE DE LA CARGA DEL 1303-02 Y 1348-08 | S21111400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-14 | 1844 | keep | 0 | Nov | 2021 | 0.0012559 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-11-14 15:01 | 2021-11-14 15:03 | 500 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1346-05 UN 100% Y PARTE DE LA CARGA DEL 1303-02 Y 1348-08 | S21111400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-14 | 1000 | keep | 0 | Nov | 2021 | 0.0006811 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2021-11-14 15:01 | 2021-11-14 15:03 | 135 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1346-05 UN 100% Y PARTE DE LA CARGA DEL 1303-02 Y 1348-08 | S21111400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-14 | 270 | keep | 0 | Nov | 2021 | 0.0001839 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
AGUADILLA | 2021-11-14 15:05 | 2021-11-14 16:35 | 18 | 001:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEAS SUCUNDARIAS AVERIADAS | M21111300070 | New_Event | Secondary Wire Down | Include | Include | Equipment | 90 | 2021-11-14 | 1620 | keep | 0 | Nov | 2021 | 0.0011034 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2021-11-14 15:09 | 2021-11-14 15:10 | 1420 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1530-6 | S21111400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 1420 | keep | 0 | Nov | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-11-14 15:09 | 2021-11-14 15:10 | 437 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1526-2 | S21111400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 437 | keep | 0 | Nov | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
CAGUAS | 2021-11-14 15:25 | 2021-11-14 17:14 | 3 | 001:49 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR | C21111400049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2021-11-14 | 327 | keep | 0 | Nov | 2021 | 0.00022272 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-11-14 15:27 | 2021-11-14 15:28 | 3957 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21111400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 3957 | keep | 0 | Nov | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
BAYAMON | 2021-11-14 15:31 | 2021-11-14 15:32 | 1420 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1530-6 | S21111400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 1420 | keep | 0 | Nov | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-11-14 15:31 | 2021-11-14 15:32 | 437 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1526-2 | S21111400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 437 | keep | 0 | Nov | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2021-11-14 15:36 | 2021-11-14 15:37 | 858 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1708-03 Y SE CERRO POR SCADA LLEVA 50% DEL 1708-02 | B21111400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 858 | keep | 0 | Nov | 2021 | 0.00058438 | 0.00058438 | Momentary | FALSE | FALSE | Not_TMED_Event | 858
BAYAMON | 2021-11-14 15:36 | 2021-11-14 15:37 | 1498 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1708-03 Y SE CERRO POR SCADA LLEVA 50% DEL 1708-02 | B21111400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 1498 | keep | 0 | Nov | 2021 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
HUMACAO | 2021-11-14 15:44 | 2021-11-14 19:12 | 80 | 003:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO DISCO ROTOS | C21111400051 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 208 | 2021-11-14 | 16640 | keep | 0 | Nov | 2021 | 0.011333 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-11-14 15:52 | 2021-11-14 15:53 | 3957 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21111400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 3957 | keep | 0 | Nov | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
MAYAGÃœEZ | 2021-11-14 15:53 | 2021-11-14 20:58 | 100 | 005:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M21111400079 | New_Event | Cutout Failure | Include | Include | Equipment | 305 | 2021-11-14 | 30500 | keep | 0 | Nov | 2021 | 0.020773 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-11-14 16:00 | 2021-11-14 19:28 | 7 | 003:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIO | B21111400089 | New_Event | Secondary Wire Down | Include | Include | Equipment | 208 | 2021-11-14 | 1456 | keep | 0 | Nov | 2021 | 0.00099167 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-11-14 16:25 | 2021-11-15 11:23 | 40 | 018:58 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO AISLADOR | S21111400028 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1138 | 2021-11-14 | 45520 | keep | 0 | Nov | 2021 | 0.031003 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2021-11-14 16:25 | 2021-11-14 17:26 | 15 | 001:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE DE LINEA SE REMPLAZARON DOS CAJAS AVERIADAS | P21111400043 | New_Event | Cutout Failure | Include | Include | Equipment | 61 | 2021-11-14 | 915 | keep | 0 | Nov | 2021 | 0.0006232 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-11-14 16:30 | 2021-11-14 16:40 | 20 | 000:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS CRUZADAS | M21111400077 | New_Event | Secondary Wire Down | Include | Include | Equipment | 10 | 2021-11-14 | 200 | keep | 0 | Nov | 2021 | 0.00013622 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-11-14 16:33 | 2021-11-14 18:16 | 150 | 001:43 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CONVERTIDOR SE REMPLAZO AISLADOR PARTIDO Y SE DESGANCHO | B21111400100 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 103 | 2021-11-14 | 15450 | keep | 0 | Nov | 2021 | 0.010523 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2021-11-14 16:48 | 2021-11-14 16:49 | 1648 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21111400045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 1648 | keep | 0 | Nov | 2021 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2021-11-14 16:49 | 2021-11-14 22:03 | 115 | 005:14 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 80 EN CORTES DE LINEAS | R21111400047 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 314 | 2021-11-14 | 36110 | keep | 0 | Nov | 2021 | 0.024594 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
VEGA BAJA | 2021-11-14 16:56 | 2021-11-14 21:40 | 6 | 004:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21111400106 | New_Event | Secondary Wire Down | Include | Include | Equipment | 284 | 2021-11-14 | 1704 | keep | 0 | Nov | 2021 | 0.0011606 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-11-14 17:00 | 2021-11-14 20:40 | 8 | 003:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 10 EN TRANSFORMADOR SE REMPLAZO CAJAS DEL TRANSFORMADOR AVERIADAS | A21111400014 | New_Event | Cutout Failure | Include | Include | Equipment | 220 | 2021-11-14 | 1760 | keep | 0 | Nov | 2021 | 0.0011987 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-11-14 17:22 | 2021-11-14 19:30 | 35 | 002:08 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21111400109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 128 | 2021-11-14 | 4480 | keep | 0 | Nov | 2021 | 0.0030513 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-11-14 17:30 | 2021-11-14 17:31 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21111400090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 990 | keep | 0 | Nov | 2021 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
ARECIBO | 2021-11-14 17:45 | 2021-11-14 18:27 | 8 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A21111300059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2021-11-14 | 336 | keep | 0 | Nov | 2021 | 0.00022885 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-11-14 17:51 | 2021-11-14 17:52 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21111400095 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 990 | keep | 0 | Nov | 2021 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
ARECIBO | 2021-11-14 18:05 | 2021-11-14 18:20 | 9 | 000:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21111400013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 15 | 2021-11-14 | 135 | keep | 0 | Nov | 2021 | 9.1948e-05 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-11-14 18:10 | 2021-11-14 20:23 | 7 | 002:13 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21111400114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 133 | 2021-11-14 | 931 | keep | 0 | Nov | 2021 | 0.0006341 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2021-11-14 18:14 | 2021-11-14 19:38 | 40 | 001:24 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21111400060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2021-11-14 | 3360 | keep | 0 | Nov | 2021 | 0.0022885 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2021-11-14 18:14 | 2021-11-15 11:44 | 50 | 017:30 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA NO SE REPORTO LA CAUSA | P21111400045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1050 | 2021-11-14 | 52500 | keep | 0 | Nov | 2021 | 0.035758 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-11-14 18:17 | 2021-11-14 22:17 | 262 | 004:00 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 A 38KV | S21111400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 240 | 2021-11-14 | 62880 | keep | 0 | Nov | 2021 | 0.042827 | 0.00017845 | Sustained | FALSE | FALSE | Not_TMED_Event | 262
SAN JUAN | 2021-11-14 18:17 | 2021-11-14 22:17 | 296 | 004:00 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 A 38KV | S21111400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 240 | 2021-11-14 | 71040 | keep | 0 | Nov | 2021 | 0.048385 | 0.0002016 | Sustained | FALSE | FALSE | Not_TMED_Event | 296
SAN JUAN | 2021-11-14 18:17 | 2021-11-14 22:17 | 79 | 004:00 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 A 38KV | S21111400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 240 | 2021-11-14 | 18960 | keep | 0 | Nov | 2021 | 0.012914 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
SAN JUAN | 2021-11-14 18:17 | 2021-11-14 22:17 | 1129 | 004:00 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 A 38KV | S21111400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 240 | 2021-11-14 | 270960 | keep | 0 | Nov | 2021 | 0.18455 | 0.00076896 | Sustained | FALSE | FALSE | Not_TMED_Event | 1129
SAN JUAN | 2021-11-14 18:17 | 2021-11-14 22:17 | 1573 | 004:00 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 A 38KV | S21111400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 240 | 2021-11-14 | 377520 | keep | 0 | Nov | 2021 | 0.25713 | 0.0010714 | Sustained | FALSE | FALSE | Not_TMED_Event | 1573
ARECIBO | 2021-11-14 18:21 | 2021-11-14 18:22 | 2107 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21111400016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 2107 | keep | 0 | Nov | 2021 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
ARECIBO | 2021-11-14 18:30 | 2021-11-14 19:34 | 35 | 001:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21111400017 | New_Event | Bad Weather | Include | Include | Weather | 64 | 2021-11-14 | 2240 | keep | 0 | Nov | 2021 | 0.0015257 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2021-11-14 18:35 | 2021-11-15 17:03 | 5 | 022:28 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21111400117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1348 | 2021-11-14 | 6740 | keep | 0 | Nov | 2021 | 0.0045906 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-11-14 18:35 | 2021-11-14 18:36 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21111400099 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 990 | keep | 0 | Nov | 2021 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
MAYAGÃœEZ | 2021-11-14 18:54 | 2021-11-14 19:05 | 2483 | 000:11 | T | CABLE SOTERRADO AVERIADO | SE ABRIO INTERRUPTOR PARAR CERRAR AMARRE CON 6601-02 POR SALIDA SOTERRADA AVERIADA EN ALIM 6601-02 | M21111400000 | New_Event | UG Cable Fault | Include | Include | Equipment | 11 | 2021-11-14 | 27313 | keep | 0 | Nov | 2021 | 0.018603 | 0.0016912 | Sustained | FALSE | FALSE | Not_TMED_Event | 2483
MAYAGÃœEZ | 2021-11-14 19:05 | 2021-11-15 17:38 | 6 | 022:33 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO CORTE DE LINEA PROVISIONAL Y SE CERRO MACHETES PARA ENERGIZAR CLIENTES QUE QUEDARON FUERA POR AVERIA CABLE SOTERRADO | M21111400105 | New_Event | UG Cable Fault | Include | Include | Equipment | 1353 | 2021-11-14 | 8118 | keep | 0 | Nov | 2021 | 0.0055291 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-11-14 19:11 | 2021-11-15 10:00 | 16 | 014:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO A CAJA EN CORTE DE LINEA | P21111400047 | New_Event | Wire Down | Include | Include | Equipment | 889 | 2021-11-14 | 14224 | keep | 0 | Nov | 2021 | 0.0096879 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
FAJARDO | 2021-11-14 19:14 | 2021-11-14 19:15 | 3003 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21111400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 3003 | keep | 0 | Nov | 2021 | 0.0020453 | 0.0020453 | Momentary | FALSE | FALSE | Not_TMED_Event | 3003
PONCE | 2021-11-14 19:20 | 2021-11-15 11:11 | 25 | 015:51 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA POR DESGANCHE | P21111400049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 951 | 2021-11-14 | 23775 | keep | 0 | Nov | 2021 | 0.016193 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-11-14 19:45 | 2021-11-14 19:46 | 418 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1013-13 SE CERRO POR CONTROL Y QUEDO EN SERVICIO LLEVA PARTE DE LA CARGA DEL 1014-16 | S21111400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 418 | keep | 0 | Nov | 2021 | 0.0002847 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
BAYAMON | 2021-11-14 19:45 | 2021-11-14 19:46 | 80 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1013-13 SE CERRO POR CONTROL Y QUEDO EN SERVICIO LLEVA PARTE DE LA CARGA DEL 1014-16 | S21111400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 80 | keep | 0 | Nov | 2021 | 5.4488e-05 | 5.4488e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2021-11-14 20:16 | 2021-11-14 20:17 | 181 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21111400075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-14 | 181 | keep | 0 | Nov | 2021 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
BAYAMON | 2021-11-14 20:48 | 2021-11-15 09:55 | 80 | 013:07 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21111400074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 787 | 2021-11-14 | 62960 | keep | 0 | Nov | 2021 | 0.042882 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-11-14 21:24 | 2021-11-15 10:13 | 300 | 012:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO LINEA A CAJA EN CORTE DE LINEA | S21111400080 | New_Event | Wire Down | Include | Include | Equipment | 769 | 2021-11-14 | 230700 | keep | 0 | Nov | 2021 | 0.15713 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
ARECIBO | 2021-11-14 21:40 | 2021-11-14 22:50 | 10 | 001:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21111400024 | New_Event | Bad Weather | Include | Include | Weather | 70 | 2021-11-14 | 700 | keep | 0 | Nov | 2021 | 0.00047677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-11-14 21:43 | 2021-11-15 10:31 | 80 | 012:48 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21111400118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 768 | 2021-11-14 | 61440 | keep | 0 | Nov | 2021 | 0.041847 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2021-11-14 21:54 | 2021-11-15 10:42 | 12 | 012:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA LEVANTAR SECUNDARIA | C21111400077 | New_Event | Secondary Wire Down | Include | Include | Equipment | 768 | 2021-11-14 | 9216 | keep | 0 | Nov | 2021 | 0.006277 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-11-14 23:18 | 2021-11-15 13:32 | 10 | 014:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE REPARO SECUNDARIA | S21111400107 | New_Event | Secondary Wire Down | Include | Include | Equipment | 854 | 2021-11-14 | 8540 | keep | 0 | Nov | 2021 | 0.0058166 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-11-15 00:03 | 2021-11-15 11:51 | 102 | 011:48 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21111500001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 708 | 2021-11-15 | 72216 | keep | 0 | Nov | 2021 | 0.049186 | 6.9472e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 102
FAJARDO | 2021-11-15 00:15 | 2021-11-15 10:05 | 40 | 009:50 | P | DESGANCHE | 1 X 25 EN C/L | R21111500001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 590 | 2021-11-15 | 23600 | keep | 0 | Nov | 2021 | 0.016074 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2021-11-15 01:16 | 2021-11-15 01:17 | 1475 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21111500002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-15 | 1475 | keep | 0 | Nov | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
YAUCO | 2021-11-15 01:17 | 2021-11-15 08:33 | 84 | 007:16 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA POR DESGANCHE | P21111500004 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 436 | 2021-11-15 | 36624 | keep | 0 | Nov | 2021 | 0.024944 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
MAYAGÃœEZ | 2021-11-15 03:33 | 2021-11-15 03:34 | 4381 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21111500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-15 | 4381 | keep | 0 | Nov | 2021 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
CAGUAS | 2021-11-15 03:50 | 2021-11-15 12:45 | 45 | 008:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE POR REPTIL | C21111500001 | New_Event |  |  | Include | Wildlife | 535 | 2021-11-15 | 24075 | keep | 0 | Nov | 2021 | 0.016397 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2021-11-15 04:00 | 2021-11-15 11:45 | 50 | 007:45 | P | DESGANCHE | 1 X 50 EN C/L | C21111500002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 465 | 2021-11-15 | 23250 | keep | 0 | Nov | 2021 | 0.015835 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-11-15 05:06 | 2021-11-15 14:28 | 10 | 009:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REMPLAZO BAJANTE DE LINEA PRIMARIA A CAJA EN TRANSFORMADOR | P21111500003 | New_Event | Wire Down | Include | Include | Equipment | 562 | 2021-11-15 | 5620 | keep | 0 | Nov | 2021 | 0.0038278 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-15 06:16 | 2021-11-15 12:06 | 50 | 005:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN C/L. SE LEVANTO CONDUCTOR | B21111500003 | New_Event | Wire Down | Include | Include | Equipment | 350 | 2021-11-15 | 17500 | keep | 0 | Nov | 2021 | 0.011919 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-11-15 06:28 | 2021-11-15 14:49 | 6 | 008:21 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR QUEMADO DE 50 KVA X 50 KVA | C21111500005 | New_Event | Service Transformer Failure | Include | Include | Equipment | 501 | 2021-11-15 | 3006 | keep | 0 | Nov | 2021 | 0.0020474 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-11-15 06:29 | 2021-11-15 07:09 | 1588 | 000:40 | S | PROTECCION DEFECTUOSA | DISPARO DE INTERRUPTORES DE LA ALTA POR BACKUP AL NO OPERAR LA PROTECCION DEL 1711-02. LLEVA EL 1711-03 | B21111500008 | New_Event | Protection Miscoordination | Include | Include | Other | 40 | 2021-11-15 | 63520 | keep | 0 | Nov | 2021 | 0.043263 | 0.0010816 | Sustained | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2021-11-15 06:29 | 2021-11-15 06:31 | 1812 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21111500008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-15 | 3624 | keep | 0 | Nov | 2021 | 0.0024683 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
HUMACAO | 2021-11-15 06:35 | 2021-11-15 06:36 | 3701 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21111500007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-15 | 3701 | keep | 0 | Nov | 2021 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
HUMACAO | 2021-11-15 06:36 | 2021-11-15 10:16 | 195 | 003:40 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L NO CAUSA | C21111500009 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 220 | 2021-11-15 | 42900 | keep | 0 | Nov | 2021 | 0.029219 | 0.00013281 | Sustained | FALSE | FALSE | Not_TMED_Event | 195
BAYAMON | 2021-11-15 06:45 | 2021-11-15 07:09 | 723 | 000:24 | S | PROTECCION DEFECTUOSA | DISPARO DE INTERRUPTORES DE LA ALTA POR BACKUP AL NO OPERAR LA PROTECCION DEL 1711-02. SE TRANSFIRIO AL 1716-03 | B21111500008 | New_Event | Protection Miscoordination | Include | Include | Other | 24 | 2021-11-15 | 17352 | keep | 0 | Nov | 2021 | 0.011818 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2021-11-15 06:45 | 2021-11-15 07:09 | 13 | 000:24 | S | PROTECCION DEFECTUOSA | DISPARO DE INTERRUPTORES DE LA ALTA POR BACKUP AL NO OPERAR LA PROTECCION DEL 1711-02. CARGA POR 1711-01. | B21111500008 | New_Event | Protection Miscoordination | Include | Include | Other | 24 | 2021-11-15 | 312 | keep | 0 | Nov | 2021 | 0.0002125 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2021-11-15 06:45 | 2021-11-15 07:09 | 1976 | 000:24 | S | PROTECCION DEFECTUOSA | DISPARO DE INTERRUPTORES DE LA ALTA POR BACKUP AL NO OPERAR LA PROTECCION DEL 1711-02.SE TRANSFIRIO AL 1529-12 | B21111500008 | New_Event | Protection Miscoordination | Include | Include | Other | 24 | 2021-11-15 | 47424 | keep | 0 | Nov | 2021 | 0.0323 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
MAYAGÃœEZ | 2021-11-15 06:46 | 2021-11-15 13:47 | 1 | 007:01 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21111500006 | New_Event | Bad Weather | Include | Include | Weather | 421 | 2021-11-15 | 421 | keep | 0 | Nov | 2021 | 0.00028674 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-11-15 06:51 | 2021-11-15 10:16 | 20 | 003:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | A21111500002 | New_Event |  |  | Include | Wildlife | 205 | 2021-11-15 | 4100 | keep | 0 | Nov | 2021 | 0.0027925 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-11-15 07:00 | 2021-11-15 15:22 | 7 | 008:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C21111500011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 502 | 2021-11-15 | 3514 | keep | 0 | Nov | 2021 | 0.0023934 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-11-15 07:02 | 2021-11-15 23:58 | 150 | 016:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA | B21111500025 | New_Event | Wire Down | Include | Include | Equipment | 1016 | 2021-11-15 | 152400 | keep | 0 | Nov | 2021 | 0.1038 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2021-11-15 07:22 | 2021-11-15 08:47 | 2216 | 001:25 | T | DESGANCHE | DISPARO DE INTERRUPTOR. SE RETIRO RAMA SOBRE ALIMENTADOR Y SE CERRO POR SCADA | B21111500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2021-11-15 | 188360 | keep | 0 | Nov | 2021 | 0.12829 | 0.0015093 | Sustained | FALSE | FALSE | Not_TMED_Event | 2216
MAYAGÃœEZ | 2021-11-15 07:26 | 2021-11-15 17:18 | 70 | 009:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA Y SE CERRO PUENTES PRIMARIOS | M21111500008 | New_Event | Wire Down | Include | Include | Equipment | 592 | 2021-11-15 | 41440 | keep | 0 | Nov | 2021 | 0.028225 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-11-15 07:34 | 2021-11-15 11:30 | 50 | 003:56 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21111500010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 236 | 2021-11-15 | 11800 | keep | 0 | Nov | 2021 | 0.0080369 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2021-11-15 07:43 | 2021-11-15 07:44 | 1839 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5400 | R21111500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-15 | 1839 | keep | 0 | Nov | 2021 | 0.0012525 | 0.0012525 | Momentary | FALSE | FALSE | Not_TMED_Event | 1839
FAJARDO | 2021-11-15 07:43 | 2021-11-15 07:44 | 1778 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5400 | R21111500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-15 | 1778 | keep | 0 | Nov | 2021 | 0.001211 | 0.001211 | Momentary | FALSE | FALSE | Not_TMED_Event | 1778
FAJARDO | 2021-11-15 07:43 | 2021-11-15 07:44 | 1376 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5400 | R21111500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-15 | 1376 | keep | 0 | Nov | 2021 | 0.00093719 | 0.00093719 | Momentary | FALSE | FALSE | Not_TMED_Event | 1376
FAJARDO | 2021-11-15 07:43 | 2021-11-15 07:44 | 293 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5400 | R21111500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-15 | 293 | keep | 0 | Nov | 2021 | 0.00019956 | 0.00019956 | Momentary | FALSE | FALSE | Not_TMED_Event | 293
FAJARDO | 2021-11-15 07:43 | 2021-11-15 07:44 | 1215 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5400 | R21111500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-15 | 1215 | keep | 0 | Nov | 2021 | 0.00082753 | 0.00082753 | Momentary | FALSE | FALSE | Not_TMED_Event | 1215
PONCE | 2021-11-15 07:54 | 2021-11-15 09:03 | 45 | 001:09 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21111500014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 69 | 2021-11-15 | 3105 | keep | 0 | Nov | 2021 | 0.0021148 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2021-11-15 07:55 | 2021-11-15 10:12 | 2 | 002:17 | P | SECUNDARIA/DESGANCHE | 2 X 10 EN XMR DESGANCHO | R21111500005 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 137 | 2021-11-15 | 274 | keep | 0 | Nov | 2021 | 0.00018662 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2021-11-15 07:59 | 2021-11-15 11:35 | 50 | 003:36 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21111500050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 216 | 2021-11-15 | 10800 | keep | 0 | Nov | 2021 | 0.0073558 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-11-15 08:06 | 2021-11-15 12:59 | 50 | 004:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE POR AVE | C21111500021 | New_Event |  |  | Include | Wildlife | 293 | 2021-11-15 | 14650 | keep | 0 | Nov | 2021 | 0.009978 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2021-11-15 08:06 | 2021-11-15 10:43 | 85 | 002:37 | P | DESGANCHE | 2 X 50 EN C/L | C21111500020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2021-11-15 | 13345 | keep | 0 | Nov | 2021 | 0.0090892 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
CAGUAS | 2021-11-15 08:07 | 2021-11-15 10:11 | 5 | 002:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE POR AVE | C21111500022 | New_Event |  |  | Include | Wildlife | 124 | 2021-11-15 | 620 | keep | 0 | Nov | 2021 | 0.00042228 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-11-15 08:12 | 2021-11-15 10:10 | 40 | 001:58 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P21111500015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2021-11-15 | 4720 | keep | 0 | Nov | 2021 | 0.0032148 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-11-15 08:30 | 2021-11-15 08:31 | 3332 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO | B21111500000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-11-15 | 3332 | keep | 0 | Nov | 2021 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
VEGA BAJA | 2021-11-15 08:31 | 2021-11-15 13:47 | 500 | 005:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZARON CAJAS AVERIADAS Y SE NORMALIZO CARGA | B21111500000 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 316 | 2021-11-15 | 158000 | keep | 0 | Nov | 2021 | 0.10761 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
MAYAGÃœEZ | 2021-11-15 08:34 | 2021-11-15 16:00 | 200 | 007:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21111500018 | New_Event | Bad Weather | Include | Include | Weather | 446 | 2021-11-15 | 89200 | keep | 0 | Nov | 2021 | 0.060754 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-11-15 08:37 | 2021-11-15 12:41 | 40 | 004:04 | P | DESGANCHE | 1 X 65 EN C/L. SE REALIZO DESGANCHE | B21111500062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 244 | 2021-11-15 | 9760 | keep | 0 | Nov | 2021 | 0.0066475 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2021-11-15 08:40 | 2021-11-15 15:33 | 5 | 006:53 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21111500018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 413 | 2021-11-15 | 2065 | keep | 0 | Nov | 2021 | 0.0014065 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2021-11-15 08:44 | 2021-11-15 19:56 | 20 | 011:12 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21111500065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 672 | 2021-11-15 | 13440 | keep | 0 | Nov | 2021 | 0.0091539 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2021-11-15 08:47 | 2021-11-15 09:15 | 25 | 000:28 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | R21111500008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 28 | 2021-11-15 | 700 | keep | 0 | Nov | 2021 | 0.00047677 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2021-11-15 08:52 | 2021-11-15 12:01 | 80 | 003:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN SU-1 AVE CRUZO FASE | P21111500020 | New_Event |  |  | Include | Wildlife | 189 | 2021-11-15 | 15120 | keep | 0 | Nov | 2021 | 0.010298 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2021-11-15 09:07 | 2021-11-15 13:43 | 1 | 004:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CHANGO CRUZO LINEA | B21111500077 | New_Event |  |  | Include | Wildlife | 276 | 2021-11-15 | 276 | keep | 0 | Nov | 2021 | 0.00018798 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-11-15 09:15 | 2021-11-15 12:45 | 20 | 003:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | A21111500014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 210 | 2021-11-15 | 4200 | keep | 0 | Nov | 2021 | 0.0028606 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2021-11-15 09:16 | 2021-11-15 09:17 | 40 | 000:01 | P | DESGANCHE | 1 X 40 EN C/L | C21111500004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-15 | 40 | keep | 0 | Nov | 2021 | 2.7244e-05 | 2.7244e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-15 09:22 | 2021-11-15 10:33 | 10 | 001:11 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21111500083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 71 | 2021-11-15 | 710 | keep | 0 | Nov | 2021 | 0.00048358 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-15 09:25 | 2021-11-15 14:28 | 10 | 005:03 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZAR POSTE SECUNDARIO PARTIDO | A21111500015 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 303 | 2021-11-15 | 3030 | keep | 0 | Nov | 2021 | 0.0020637 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-11-15 09:29 | 2021-11-15 15:52 | 7 | 006:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO CAJAS Y PARARRAYOS EN BANCO DE XMRS | C21111500042 | New_Event | Cutout Failure | Include | Include | Equipment | 383 | 2021-11-15 | 2681 | keep | 0 | Nov | 2021 | 0.001826 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2021-11-15 09:35 | 2021-11-15 11:54 | 4 | 002:19 | P | OTRAS CAUSAS | 1 X 50 Y 2 X 65 EN C/L C/T AVERIADO | C21111500044 | New_Event | Other Causes | Include | Include | Other | 139 | 2021-11-15 | 556 | keep | 0 | Nov | 2021 | 0.00037869 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-11-15 09:35 | 2021-11-15 12:06 | 60 | 002:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 30 EN CORTE DE LINEA SE RETEZARON LINEAS PRIMARIAS ARRIADAS | M21111500029 | New_Event | Wire Down | Include | Include | Equipment | 151 | 2021-11-15 | 9060 | keep | 0 | Nov | 2021 | 0.0061707 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2021-11-15 09:40 | 2021-11-15 18:35 | 3 | 008:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA SE CERRO CORTE DE LINEA | A21111500003 | New_Event | Wire Down | Include | Include | Equipment | 535 | 2021-11-15 | 1605 | keep | 0 | Nov | 2021 | 0.0010932 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2021-11-15 09:43 | 2021-11-15 11:34 | 2201 | 001:51 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6900 OVERHEAD DE LINEA 6900 PARTIDO SOBRE LINEA DE DISTRIBUCION | A21111500016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 111 | 2021-11-15 | 244311 | keep | 0 | Nov | 2021 | 0.1664 | 0.0014991 | Sustained | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2021-11-15 09:43 | 2021-11-15 11:34 | 1986 | 001:51 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6900 OVERHEAD DE LINEA 6900 PARTIDO SOBRE LINEA DE DISTRIBUCION | A21111500016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 111 | 2021-11-15 | 220446 | keep | 0 | Nov | 2021 | 0.15014 | 0.0013527 | Sustained | FALSE | FALSE | Not_TMED_Event | 1986
ARECIBO | 2021-11-15 09:43 | 2021-11-15 11:34 | 199 | 001:51 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6900 OVERHEAD DE LINEA 6900 PARTIDO SOBRE LINEA DE DISTRIBUCION | A21111500016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 111 | 2021-11-15 | 22089 | keep | 0 | Nov | 2021 | 0.015045 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2021-11-15 09:43 | 2021-11-15 11:34 | 24 | 001:51 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6900 OVERHEAD DE LINEA 6900 PARTIDO SOBRE LINEA DE DISTRIBUCION | A21111500016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 111 | 2021-11-15 | 2664 | keep | 0 | Nov | 2021 | 0.0018144 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
PONCE | 2021-11-15 09:46 | 2021-11-15 17:17 | 5 | 007:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR LINEA SECUNDARIA AVERIADA | P21111500023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 451 | 2021-11-15 | 2255 | keep | 0 | Nov | 2021 | 0.0015359 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-11-15 09:46 | 2021-11-15 12:21 | 10 | 002:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21111500031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 155 | 2021-11-15 | 1550 | keep | 0 | Nov | 2021 | 0.0010557 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-15 09:54 | 2021-11-15 19:14 | 25 | 009:20 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE MASIVO | B21111500089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 560 | 2021-11-15 | 14000 | keep | 0 | Nov | 2021 | 0.0095353 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-11-15 10:18 | 2021-11-15 10:19 | 1597 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21111500044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-15 | 1597 | keep | 0 | Nov | 2021 | 0.0010877 | 0.0010877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1597
PONCE | 2021-11-15 10:23 | 2021-11-15 11:40 | 30 | 001:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO A CAJA EN CORTE DE LINEA | P21111500026 | New_Event | Wire Down | Include | Include | Equipment | 77 | 2021-11-15 | 2310 | keep | 0 | Nov | 2021 | 0.0015733 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-11-15 10:26 | 2021-11-15 10:38 | 4 | 000:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C21111500000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 12 | 2021-11-15 | 48 | keep | 0 | Nov | 2021 | 3.2693e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-11-15 10:33 | 2021-11-15 15:00 | 50 | 004:27 | P | DESGANCHE | 3 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21111500049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 267 | 2021-11-15 | 13350 | keep | 0 | Nov | 2021 | 0.0090926 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-11-15 10:50 | 2021-11-15 13:30 | 40 | 002:40 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZO DE POSTE PRIMARIO PARTIDO | A21111500043 | New_Event | Defective Pole | Include | Include | Equipment | 160 | 2021-11-15 | 6400 | keep | 0 | Nov | 2021 | 0.004359 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-11-15 11:00 | 2021-11-15 15:08 | 40 | 004:08 | P | ESTRUCTURA AVERIADA | ABRIO C/L PARA REEMPLAZAR POSTE PARTIDO | C21111500054 | New_Event | Defective Pole | Include | Include | Equipment | 248 | 2021-11-15 | 9920 | keep | 0 | Nov | 2021 | 0.0067565 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-15 11:15 | 2021-11-15 12:46 | 3 | 001:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B21111200045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 91 | 2021-11-15 | 273 | keep | 0 | Nov | 2021 | 0.00018594 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2021-11-15 11:23 | 2021-11-16 10:28 | 6 | 023:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C21111500056 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1385 | 2021-11-15 | 8310 | keep | 0 | Nov | 2021 | 0.0056599 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-11-15 11:26 | 2021-11-15 11:28 | 1984 | 000:02 | T | DESCONECTIVO DEFECTUOSO | EN OPERACIONES DE TRANSFERENCIA DEL 1711-05 Y 1911-07 QUE A SU VEZ ESTA POR EL 1529-12, DISPARO 1529-12 Y SE CERRO NUEVAMENTE QUEDANDO EN SERVICIO. LLEVANDO 1911-07 | S21111500000 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2021-11-15 | 3968 | keep | 0 | Nov | 2021 | 0.0027026 | 0.0013513 | Momentary | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2021-11-15 11:26 | 2021-11-15 11:28 | 577 | 000:02 | T | DESCONECTIVO DEFECTUOSO | CARGA POR EL 1529-12. EN OPERACIONES DEL 1711-05 CONTRA EL 1911-07 QUE A SU VEZ ESTA POR EL 1529-12, DISPARO EL 1529-12 LLEVANDO LA CARGA DEL 1911-07 Y SE CERRO NUEVAMENTE. | S21111500000 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2021-11-15 | 1154 | keep | 0 | Nov | 2021 | 0.00078598 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
BAYAMON | 2021-11-15 11:28 | 2021-11-15 16:46 | 300 | 005:18 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO MACHETES Y SE REMPLAZARON LLEVA EL 1911-07 | S21111500083 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 318 | 2021-11-15 | 95400 | keep | 0 | Nov | 2021 | 0.064977 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2021-11-15 11:28 | 2021-11-15 16:46 | 300 | 005:18 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO MACHETES DEL 1529-12 QUE LLEVA 1911-07 PARA REMPLAZAR 2 MACHETES | S21111500083 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 318 | 2021-11-15 | 95400 | keep | 0 | Nov | 2021 | 0.064977 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
PONCE | 2021-11-15 11:29 | 2021-11-15 13:32 | 1 | 002:03 | P | NO SE REPORTO CAUSA | 1 X 30 EN MONTURA TRIFASICA NO SE REPORTO LA CAUSA | P21111500031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 123 | 2021-11-15 | 123 | keep | 0 | Nov | 2021 | 8.3775e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-11-15 11:30 | 2021-11-15 12:02 | 10 | 000:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A21111500011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 32 | 2021-11-15 | 320 | keep | 0 | Nov | 2021 | 0.00021795 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-15 11:34 | 2021-11-15 11:51 | 1986 | 000:17 | T | LINEA DE TRANSMISION 38KV | CARGA POR 8013-04 | A21111500016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2021-11-15 | 33762 | keep | 0 | Nov | 2021 | 0.022995 | 0.0013527 | Sustained | FALSE | FALSE | Not_TMED_Event | 1986
ARECIBO | 2021-11-15 11:34 | 2021-11-15 11:51 | 24 | 000:17 | T | LINEA DE TRANSMISION 38KV | SE RETIRO OVERHEAD DE LINEA 6900 SOBRE LINEAS PRIMARIAS SE CERRO INTERRUPTOR LLEVA LA CARGA DEL 8013-02 | A21111500016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2021-11-15 | 408 | keep | 0 | Nov | 2021 | 0.00027789 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2021-11-15 11:36 | 2021-11-15 17:56 | 12 | 006:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES | B21111500105 | New_Event | Cutout Failure | Include | Include | Equipment | 380 | 2021-11-15 | 4560 | keep | 0 | Nov | 2021 | 0.0031058 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-11-15 11:39 | 2021-11-15 14:12 | 10 | 002:33 | P | SECUNDARIA/ESTRUCTURA AVERIADA | REEMPLAZO POSTE SECUNDARIO | C21111500057 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 153 | 2021-11-15 | 1530 | keep | 0 | Nov | 2021 | 0.0010421 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-11-15 11:54 | 2021-11-15 19:56 | 1 | 008:02 | P | OTRAS CAUSAS | 1 X 20 EN XMR REEMPLAZO EQUIPO DE MEDICION | C21111500044 | New_Event | Other Causes | Include | Include | Other | 482 | 2021-11-15 | 482 | keep | 0 | Nov | 2021 | 0.00032829 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2021-11-15 11:55 | 2021-11-15 12:43 | 10 | 000:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA AVERIADA | P21111500032 | New_Event | Cutout Failure | Include | Include | Equipment | 48 | 2021-11-15 | 480 | keep | 0 | Nov | 2021 | 0.00032693 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-15 12:06 | 2021-11-15 17:00 | 50 | 004:54 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRE CORTE DE LINEA PARA REMPLAZAR AISLADOR | S21111500050 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 294 | 2021-11-15 | 14700 | keep | 0 | Nov | 2021 | 0.010012 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-11-15 12:09 | 2021-11-15 15:24 | 5 | 003:15 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA DESGANCHE | S21111500500 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 195 | 2021-11-15 | 975 | keep | 0 | Nov | 2021 | 0.00066407 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-11-15 12:15 | 2021-11-15 16:21 | 32 | 004:06 | P | DESGANCHE | 1 X 40 EN C/L | C21111500060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2021-11-15 | 7872 | keep | 0 | Nov | 2021 | 0.0053616 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
ARECIBO | 2021-11-15 12:22 | 2021-11-15 12:23 | 1986 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | CARGA POR 8013-04 BAJANTE DE LINEA A CAJA DE RISER ABIERTO | A21111500070 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-15 | 1986 | keep | 0 | Nov | 2021 | 0.0013527 | 0.0013527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1986
ARECIBO | 2021-11-15 12:22 | 2021-11-15 12:23 | 24 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DEL INTERRUPTOR LLEVA LA CARGA DEL 8013-02 BAJANTE DE LINEA A CAJA DE RISER ABIERTO EN ALIM 8013-02 | A21111500070 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-15 | 24 | keep | 0 | Nov | 2021 | 1.6346e-05 | 1.6346e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 24
ARECIBO | 2021-11-15 12:23 | 2021-11-15 20:38 | 1 | 008:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE LINEA PRIMARIA A RISER UN SOLO CLIENTE | A21111500119 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 495 | 2021-11-15 | 495 | keep | 0 | Nov | 2021 | 0.00033714 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-11-15 12:24 | 2021-11-15 18:54 | 40 | 006:30 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN C/L SE REEMPLAZO AISLADOR | C21111500061 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 390 | 2021-11-15 | 15600 | keep | 0 | Nov | 2021 | 0.010625 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2021-11-15 12:28 | 2021-11-15 13:24 | 6 | 000:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | R21111500017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 56 | 2021-11-15 | 336 | keep | 0 | Nov | 2021 | 0.00022885 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-11-15 12:30 | 2021-11-15 12:33 | 850 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1303-02 LLEVANDO 20% 1204-02 | S21111500059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-15 | 2550 | keep | 0 | Nov | 2021 | 0.0017368 | 0.00057893 | Momentary | FALSE | FALSE | Not_TMED_Event | 850
SAN JUAN | 2021-11-15 12:30 | 2021-11-15 12:33 | 2435 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1303-02 LLEVANDO 20% 1204-02 | S21111500059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-15 | 7305 | keep | 0 | Nov | 2021 | 0.0049754 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
UTUADO | 2021-11-15 12:30 | 2021-11-15 12:46 | 12 | 000:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR CONECTORES SECUNDARIOS | A21111400020 | New_Event | Secondary Wire Down | Include | Include | Equipment | 16 | 2021-11-15 | 192 | keep | 0 | Nov | 2021 | 0.00013077 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-11-15 12:33 | 2021-11-15 19:27 | 80 | 006:54 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21111500197 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 414 | 2021-11-15 | 33120 | keep | 0 | Nov | 2021 | 0.022558 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2021-11-15 12:40 | 2021-11-15 12:42 | 3420 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C21111500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-15 | 6840 | keep | 0 | Nov | 2021 | 0.0046587 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
BARRANQUITAS | 2021-11-15 12:42 | 2021-11-15 17:24 | 50 | 004:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L MAL TIEMPO | C21111500065 | New_Event | Bad Weather | Include | Include | Weather | 282 | 2021-11-15 | 14100 | keep | 0 | Nov | 2021 | 0.0096034 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2021-11-15 12:51 | 2021-11-15 16:01 | 25 | 003:10 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | A21111500074 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 190 | 2021-11-15 | 4750 | keep | 0 | Nov | 2021 | 0.0032352 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-11-15 12:54 | 2021-11-15 15:13 | 3 | 002:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21111500064 | New_Event | Bad Weather | Include | Include | Weather | 139 | 2021-11-15 | 417 | keep | 0 | Nov | 2021 | 0.00028402 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-11-15 12:57 | 2021-11-16 19:47 | 100 | 030:50 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE | S21111500223 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1850 | 2021-11-15 | 185000 | keep | 0 | Nov | 2021 | 0.126 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-11-15 13:00 | 2021-11-15 15:02 | 829 | 002:02 | P | DESGANCHE | DISPARO DE INTERRUPTOR 1206-04 QUE A SU VEZ LLEVA 60% DEL 1204-3 | S21111500070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2021-11-15 | 101138 | keep | 0 | Nov | 2021 | 0.068885 | 0.00056463 | Sustained | FALSE | FALSE | Not_TMED_Event | 829
SAN JUAN | 2021-11-15 13:00 | 2021-11-15 15:02 | 1978 | 002:02 | P | DESGANCHE | DISPARO CON R/R OFF PARTE POR 1206-4 BAMBUAS SOBRE LINEA | S21111500070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2021-11-15 | 241316 | keep | 0 | Nov | 2021 | 0.16436 | 0.0013472 | Sustained | FALSE | FALSE | Not_TMED_Event | 1978
SAN JUAN | 2021-11-15 13:00 | 2021-11-15 15:02 | 1799 | 002:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1206-04 QUE A SU VEZ LLEVA EL 40% 1204-04 Y 60% DEL 1204-3. SE REPORTA AVERIA POR BAMBUAS SOBRE LINEA | S21111500070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2021-11-15 | 219478 | keep | 0 | Nov | 2021 | 0.14949 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2021-11-15 13:02 | 2021-11-15 13:05 | 290 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1335-05 LLEVANDO 40% 1301-02 | S21111500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-15 | 870 | keep | 0 | Nov | 2021 | 0.00059255 | 0.00019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 290
SAN JUAN | 2021-11-15 13:02 | 2021-11-15 13:05 | 314 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1335-05 LLEVANDO 40% 1301-02 | S21111500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-15 | 942 | keep | 0 | Nov | 2021 | 0.00064159 | 0.00021386 | Momentary | FALSE | FALSE | Not_TMED_Event | 314
SAN JUAN | 2021-11-15 13:05 | 2021-11-15 13:08 | 1681 | 000:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-04 LLEVANDO CARGA 1303-01 Y 1346-06. CARGA DE 1303-04 POR 1303-05 | S21111500077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-11-15 | 5043 | keep | 0 | Nov | 2021 | 0.0034348 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-11-15 13:05 | 2021-11-15 13:08 | 1598 | 000:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-04 LLEVANDO CARGA 1303-01 Y 1346-06. CARGA DE 1303-04 POR 1303-05 | S21111500077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-11-15 | 4794 | keep | 0 | Nov | 2021 | 0.0032652 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2021-11-15 13:08 | 2021-11-15 14:15 | 200 | 001:07 | P | DESGANCHE | SE RETIRO BAMBUAS SOBRE LINEA Y SE CERRO MACHETE CAMINO LOS GUANOS 100% EN SERVICIO SU CARGA POR 1303-4 | S21111500077 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 67 | 2021-11-15 | 13400 | keep | 0 | Nov | 2021 | 0.0091267 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-11-15 13:43 | 2021-11-15 14:36 | 36 | 000:53 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21111500123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 53 | 2021-11-15 | 1908 | keep | 0 | Nov | 2021 | 0.0012995 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
VEGA BAJA | 2021-11-15 13:43 | 2021-11-15 16:00 | 1 | 002:17 | P | NO SE REPORTO CAUSA | 2 X 65 EN RISER | B21111500123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 137 | 2021-11-15 | 137 | keep | 0 | Nov | 2021 | 9.331e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-11-15 13:44 | 2021-11-15 13:45 | 2720 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR | A21111500082 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-11-15 | 2720 | keep | 0 | Nov | 2021 | 0.0018526 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
ARECIBO | 2021-11-15 13:45 | 2021-11-15 17:09 | 60 | 003:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21111500093 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 204 | 2021-11-15 | 12240 | keep | 0 | Nov | 2021 | 0.0083366 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2021-11-15 13:47 | 2021-11-15 14:10 | 3332 | 000:23 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO INTERRUPTOR POR EMERGENCIA PARA SECCIONALIZAR CAJAS AVERIADAS POR CAERSE | B21111500000 | New_Event | Cutout Failure | Include | Include | Equipment | 23 | 2021-11-15 | 76636 | keep | 0 | Nov | 2021 | 0.052196 | 0.0022694 | Sustained | FALSE | FALSE | Not_TMED_Event | 3332
FAJARDO | 2021-11-15 14:01 | 2021-11-15 16:03 | 100 | 002:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | R21111500022 | New_Event | Cutout Failure | Include | Include | Equipment | 122 | 2021-11-15 | 12200 | keep | 0 | Nov | 2021 | 0.0083094 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2021-11-15 14:09 | 2021-11-15 14:10 | 2708 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | R21111500026 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-11-15 | 2708 | keep | 0 | Nov | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2021-11-15 14:10 | 2021-11-15 16:05 | 100 | 001:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIAS | R21111500027 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 115 | 2021-11-15 | 11500 | keep | 0 | Nov | 2021 | 0.0078326 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-11-15 14:10 | 2021-11-15 14:14 | 3701 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV EN RIO BLANCO | C21111500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2021-11-15 | 14804 | keep | 0 | Nov | 2021 | 0.010083 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
HUMACAO | 2021-11-15 14:10 | 2021-11-15 14:14 | 989 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV EN RIO BLANCO | C21111500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2021-11-15 | 3956 | keep | 0 | Nov | 2021 | 0.0026944 | 0.0006736 | Momentary | FALSE | FALSE | Not_TMED_Event | 989
HUMACAO | 2021-11-15 14:10 | 2021-11-15 14:14 | 1467 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV EN RIO BLANCO | C21111500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2021-11-15 | 5868 | keep | 0 | Nov | 2021 | 0.0039967 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
HUMACAO | 2021-11-15 14:10 | 2021-11-15 14:13 | 1835 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV EN RIO BLANCO | C21111500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-11-15 | 5505 | keep | 0 | Nov | 2021 | 0.0037494 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
HUMACAO | 2021-11-15 14:10 | 2021-11-15 14:13 | 71 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV EN RIO BLANCO | C21111500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-11-15 | 213 | keep | 0 | Nov | 2021 | 0.00014507 | 4.8358e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 71
HUMACAO | 2021-11-15 14:10 | 2021-11-15 14:13 | 1089 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV EN RIO BLANCO | C21111500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-11-15 | 3267 | keep | 0 | Nov | 2021 | 0.0022251 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2021-11-15 14:10 | 2021-11-15 14:13 | 3896 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV EN RIO BLANCO | C21111500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-11-15 | 11688 | keep | 0 | Nov | 2021 | 0.0079606 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2021-11-15 14:10 | 2021-11-15 14:13 | 1467 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE BARRA DE 38 KV | C21111500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-11-15 | 4401 | keep | 0 | Nov | 2021 | 0.0029975 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
ARECIBO | 2021-11-15 14:10 | 2021-11-15 17:04 | 1 | 002:54 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21111500086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2021-11-15 | 174 | keep | 0 | Nov | 2021 | 0.00011851 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-11-15 14:10 | 2021-11-15 17:24 | 500 | 003:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZARON CAJAS AVERIADAS Y SE NORMALIZO CARGA | B21111500000 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 194 | 2021-11-15 | 97000 | keep | 0 | Nov | 2021 | 0.066066 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-11-15 14:11 | 2021-11-16 11:08 | 4 | 020:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN XMR REPARO SECUNDARIA | C21111500073 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1257 | 2021-11-15 | 5028 | keep | 0 | Nov | 2021 | 0.0034245 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2021-11-15 14:12 | 2021-11-15 15:35 | 5 | 001:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | P21111500041 | New_Event | Cutout Failure | Include | Include | Equipment | 83 | 2021-11-15 | 415 | keep | 0 | Nov | 2021 | 0.00028265 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-11-15 14:26 | 2021-11-15 14:44 | 10 | 000:18 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | B21111500002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 18 | 2021-11-15 | 180 | keep | 0 | Nov | 2021 | 0.0001226 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-11-15 14:28 | 2021-11-15 15:06 | 200 | 000:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 65 EN CORTES DE LINEA SE REEMPLAZO CAJA PRIMARIA | R21111500019 | New_Event | Cutout Failure | Include | Include | Equipment | 38 | 2021-11-15 | 7600 | keep | 0 | Nov | 2021 | 0.0051763 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2021-11-15 14:34 | 2021-11-15 18:28 | 50 | 003:54 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE REPORTO CAUSA | P21111500042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 234 | 2021-11-15 | 11700 | keep | 0 | Nov | 2021 | 0.0079688 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-15 15:01 | 2021-11-15 19:25 | 6 | 004:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21111500141 | New_Event | Secondary Wire Down | Include | Include | Equipment | 264 | 2021-11-15 | 1584 | keep | 0 | Nov | 2021 | 0.0010789 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-11-15 15:04 | 2021-11-15 15:05 | 829 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-04 QUE A SU VEZ LLEVA EL 60% DEL 1204-3 | S21111500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-15 | 829 | keep | 0 | Nov | 2021 | 0.00056463 | 0.00056463 | Momentary | FALSE | FALSE | Not_TMED_Event | 829
SAN JUAN | 2021-11-15 15:04 | 2021-11-15 15:05 | 1978 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-04 QUE A SU VEZ LLEVA EL 40% 1204-04 | S21111500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-15 | 1978 | keep | 0 | Nov | 2021 | 0.0013472 | 0.0013472 | Momentary | FALSE | FALSE | Not_TMED_Event | 1978
SAN JUAN | 2021-11-15 15:04 | 2021-11-15 15:05 | 1799 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-04 QUE A SU VEZ LLEVA EL 40% 1204-04 Y 60% DEL 1204-3 | S21111500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-15 | 1799 | keep | 0 | Nov | 2021 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2021-11-15 15:04 | 2021-11-15 15:05 | 200 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 60 AMP CARGA POR EL 1206-04 | S21111500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-15 | 200 | keep | 0 | Nov | 2021 | 0.00013622 | 0.00013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2021-11-15 15:12 | 2021-11-15 16:49 | 30 | 001:37 | P | NO SE REPORTO CAUSA | 1 X 20 RISER | B21111500142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 97 | 2021-11-15 | 2910 | keep | 0 | Nov | 2021 | 0.001982 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2021-11-15 15:14 | 2021-11-16 10:11 | 35 | 018:57 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | B21111500144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1137 | 2021-11-15 | 39795 | keep | 0 | Nov | 2021 | 0.027104 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2021-11-15 15:16 | 2021-11-15 20:12 | 50 | 004:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | A21111500092 | New_Event |  |  | Include | Wildlife | 296 | 2021-11-15 | 14800 | keep | 0 | Nov | 2021 | 0.01008 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-11-15 15:18 | 2021-11-15 15:21 | 36 | 000:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1620-04 QUE A SU VEZ LLEVA LA CARGA DEL 1620-01 | S21111500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-11-15 | 108 | keep | 0 | Nov | 2021 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-11-15 15:18 | 2021-11-15 15:21 | 172 | 000:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1620-04 QUE A SU VEZ LLEVA LA CARGA DEL 1620-01 | S21111500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-11-15 | 516 | keep | 0 | Nov | 2021 | 0.00035145 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
CAGUAS | 2021-11-15 15:18 | 2021-11-16 11:09 | 6 | 019:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C21111500120 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1191 | 2021-11-15 | 7146 | keep | 0 | Nov | 2021 | 0.0048671 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-11-15 15:20 | 2021-11-15 17:22 | 8 | 002:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REEMPLAZAR BAJANTE SECUNDARIO | C21111500122 | New_Event | Secondary Wire Down | Include | Include | Equipment | 122 | 2021-11-15 | 976 | keep | 0 | Nov | 2021 | 0.00066475 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-11-15 15:20 | 2021-11-15 15:35 | 7 | 000:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A21111500076 | New_Event | Secondary Wire Down | Include | Include | Equipment | 15 | 2021-11-15 | 105 | keep | 0 | Nov | 2021 | 7.1515e-05 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-11-15 15:21 | 2021-11-15 17:04 | 30 | 001:43 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REPORTA AVERIA POR DESGANCHE | S21115000175 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 103 | 2021-11-15 | 3090 | keep | 0 | Nov | 2021 | 0.0021046 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-11-15 15:29 | 2021-11-15 15:31 | 1 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2600 | A21111500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-15 | 2 | keep | 0 | Nov | 2021 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-11-15 15:29 | 2021-11-15 15:31 | 2266 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2600 | A21111500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-15 | 4532 | keep | 0 | Nov | 2021 | 0.0030867 | 0.0015434 | Momentary | FALSE | FALSE | Not_TMED_Event | 2266
ARECIBO | 2021-11-15 15:29 | 2021-11-15 15:31 | 1399 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2600 | A21111500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-15 | 2798 | keep | 0 | Nov | 2021 | 0.0019057 | 0.00095285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1399
SAN JUAN | 2021-11-15 15:33 | 2021-11-15 17:04 | 80 | 001:31 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21111500176 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 91 | 2021-11-15 | 7280 | keep | 0 | Nov | 2021 | 0.0049584 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-11-15 15:34 | 2021-11-15 18:09 | 80 | 002:35 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21111500177 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 155 | 2021-11-15 | 12400 | keep | 0 | Nov | 2021 | 0.0084456 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2021-11-15 15:34 | 2021-11-15 17:37 | 65 | 002:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L Y 2 X 50 EN OTRO C/L. SE REMPLAZARON 2 AISLADORES | B21111500147 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 123 | 2021-11-15 | 7995 | keep | 0 | Nov | 2021 | 0.0054454 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2021-11-15 15:38 | 2021-11-16 12:24 | 1 | 020:46 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER Y 1 X 40 EN CORTE DE LINEA | B21111500148 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1246 | 2021-11-15 | 1246 | keep | 0 | Nov | 2021 | 0.00084864 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-15 15:54 | 2021-11-15 15:55 | 959 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21111500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-15 | 959 | keep | 0 | Nov | 2021 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2021-11-15 15:54 | 2021-11-15 15:55 | 1382 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21111500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-15 | 1382 | keep | 0 | Nov | 2021 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2021-11-15 15:54 | 2021-11-15 15:55 | 663 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21111500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-15 | 663 | keep | 0 | Nov | 2021 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2021-11-15 15:54 | 2021-11-15 15:55 | 1514 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21111500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-15 | 1514 | keep | 0 | Nov | 2021 | 0.0010312 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2021-11-15 15:54 | 2021-11-15 15:55 | 1105 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21111500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-15 | 1105 | keep | 0 | Nov | 2021 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2021-11-15 15:54 | 2021-11-15 15:55 | 4176 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21111500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-15 | 4176 | keep | 0 | Nov | 2021 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2021-11-15 15:54 | 2021-11-15 15:55 | 252 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21111500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-15 | 252 | keep | 0 | Nov | 2021 | 0.00017164 | 0.00017164 | Momentary | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2021-11-15 15:54 | 2021-11-15 15:55 | 2147 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21111500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-15 | 2147 | keep | 0 | Nov | 2021 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2021-11-15 15:54 | 2021-11-15 15:55 | 2858 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21111500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-15 | 2858 | keep | 0 | Nov | 2021 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
ARECIBO | 2021-11-15 15:55 | 2021-11-15 18:06 | 10 | 002:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | A21111500096 | New_Event | Secondary Wire Down | Include | Include | Equipment | 131 | 2021-11-15 | 1310 | keep | 0 | Nov | 2021 | 0.00089224 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-11-15 16:17 | 2021-11-15 17:12 | 3 | 000:55 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE REPORTO CAUSA | P21111500056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 55 | 2021-11-15 | 165 | keep | 0 | Nov | 2021 | 0.00011238 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2021-11-15 16:26 | 2021-11-15 17:12 | 2106 | 000:46 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO | R21111500032 | New_Event | Wire Down | Include | Include | Equipment | 46 | 2021-11-15 | 96876 | keep | 0 | Nov | 2021 | 0.065982 | 0.0014344 | Sustained | FALSE | FALSE | Not_TMED_Event | 2106
MAYAGÃœEZ | 2021-11-15 16:29 | 2021-11-15 17:15 | 2 | 000:46 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | M21111500085 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 46 | 2021-11-15 | 92 | keep | 0 | Nov | 2021 | 6.2661e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2021-11-15 16:40 | 2021-11-15 17:42 | 7 | 001:02 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR SE REALIZO DESGANCHE Y SE REPARO SECUNDARIA | B21111500156 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 62 | 2021-11-15 | 434 | keep | 0 | Nov | 2021 | 0.0002956 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-11-15 16:46 | 2021-11-15 17:47 | 800 | 001:01 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO MACHETES DEL 1529-12 QUE LLEVA 1911-07 PARA REMPLAZAR 2 MACHETES | S21111500083 | Additional_clients | Switch Failure | Include | Include | Equipment | 61 | 2021-11-15 | 48800 | keep | 0 | Nov | 2021 | 0.033237 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-15 16:46 | 2021-11-15 17:47 | 277 | 001:01 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO MACHETES DEL 1529-12 QUE LLEVA 1911-07 PARA REMPLAZAR 2 MACHETES | S21111500083 | Partial_restoration | Switch Failure | Include | Include | Equipment | 61 | 2021-11-15 | 16897 | keep | 0 | Nov | 2021 | 0.011508 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2021-11-15 16:56 | 2021-11-15 20:15 | 6 | 003:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR LINEA SECUNDARIA AVERIADA | P21111500058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 199 | 2021-11-15 | 1194 | keep | 0 | Nov | 2021 | 0.00081323 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2021-11-15 17:01 | 2021-11-16 10:23 | 1 | 017:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO BAJANTE SECUNDARIO | C21111500161 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1042 | 2021-11-15 | 1042 | keep | 0 | Nov | 2021 | 0.0007097 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-11-15 17:03 | 2021-11-15 20:45 | 200 | 003:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | A21111500102 | New_Event | Wire Down | Include | Include | Equipment | 222 | 2021-11-15 | 44400 | keep | 0 | Nov | 2021 | 0.030241 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-11-15 17:11 | 2021-11-15 20:07 | 1 | 002:56 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRASFORMADOR | R21111500049 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 176 | 2021-11-15 | 176 | keep | 0 | Nov | 2021 | 0.00011987 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-11-15 17:12 | 2021-11-15 18:39 | 800 | 001:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DESPEGO BAJANTE PEGADO A ESTRUCTURA | R21111500032 | Partial_restoration | Wire Down | Include | Include | Equipment | 87 | 2021-11-15 | 69600 | keep | 0 | Nov | 2021 | 0.047404 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-11-15 17:18 | 2021-11-15 22:12 | 12 | 004:54 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21111500163 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 294 | 2021-11-15 | 3528 | keep | 0 | Nov | 2021 | 0.0024029 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-11-15 17:40 | 2021-11-15 21:44 | 6 | 004:04 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR | R21111500050 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 244 | 2021-11-15 | 1464 | keep | 0 | Nov | 2021 | 0.00099712 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-11-15 17:52 | 2021-11-16 09:55 | 30 | 016:03 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21111500211 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 963 | 2021-11-15 | 28890 | keep | 0 | Nov | 2021 | 0.019677 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-11-15 17:52 | 2021-11-15 18:37 | 40 | 000:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | ABRIO C/L PARA REEMPLAZAR AISLADOR ROTO | C21111500166 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 45 | 2021-11-15 | 1800 | keep | 0 | Nov | 2021 | 0.001226 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-11-15 17:53 | 2021-11-15 17:54 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21111500091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-15 | 3458 | keep | 0 | Nov | 2021 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
HUMACAO | 2021-11-15 18:03 | 2021-11-16 11:11 | 5 | 017:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C21111500168 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1028 | 2021-11-15 | 5140 | keep | 0 | Nov | 2021 | 0.0035008 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2021-11-15 18:06 | 2021-11-15 19:58 | 6 | 001:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA LEVANTAR SECUNDARIA | C21111500141 | New_Event | Secondary Wire Down | Include | Include | Equipment | 112 | 2021-11-15 | 672 | keep | 0 | Nov | 2021 | 0.0004577 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-11-15 18:09 | 2021-11-15 21:57 | 40 | 003:48 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21111500214 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 228 | 2021-11-15 | 9120 | keep | 0 | Nov | 2021 | 0.0062116 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-11-15 18:40 | 2021-11-15 19:10 | 2407 | 000:30 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR BAJANTE DE LINEA A CAJA DE CORTE DE LINEA PEGANDO CON CRUCETA Y POSTE EN LLAMAS | A21111500122 | New_Event | Wire Down | Include | Include | Equipment | 30 | 2021-11-15 | 72210 | keep | 0 | Nov | 2021 | 0.049182 | 0.0016394 | Sustained | FALSE | FALSE | Not_TMED_Event | 2407
CANOVANAS | 2021-11-15 18:57 | 2021-11-16 10:53 | 10 | 015:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR REEMPLAZO CAJA Y PARARRAYO | R21111500062 | New_Event | Cutout Failure | Include | Include | Equipment | 956 | 2021-11-15 | 9560 | keep | 0 | Nov | 2021 | 0.0065113 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-15 19:01 | 2021-11-15 22:57 | 30 | 003:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21111500124 | New_Event | Bad Weather | Include | Include | Weather | 236 | 2021-11-15 | 7080 | keep | 0 | Nov | 2021 | 0.0048222 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-11-15 19:10 | 2021-11-15 21:05 | 1200 | 001:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO Y SE ABRIO INTERRUPTOR PARA CERRAR MACHETES | A21111500128 | Partial_restoration | Wire Down | Include | Include | Equipment | 115 | 2021-11-15 | 138000 | keep | 0 | Nov | 2021 | 0.093991 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-11-15 19:15 | 2021-11-16 09:32 | 100 | 014:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA CAJA PRIMARIA QUEMADA Y FIJAR BAJANTE PRIMARIO A CAJA | P21111500072 | New_Event | Cutout Failure | Include | Include | Equipment | 857 | 2021-11-15 | 85700 | keep | 0 | Nov | 2021 | 0.05837 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-15 19:24 | 2021-11-15 22:16 | 8 | 002:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO DE LINEA A CAJA DE TRANSFORMADOR | A21111500133 | New_Event | Wire Down | Include | Include | Equipment | 172 | 2021-11-15 | 1376 | keep | 0 | Nov | 2021 | 0.00093719 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-11-15 19:35 | 2021-11-15 21:14 | 100 | 001:39 | P | NO SE REPORTO CAUSA | 1 X 80 Y 1 X 65 EN C/L | B21111500176 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2021-11-15 | 9900 | keep | 0 | Nov | 2021 | 0.0067428 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-11-15 19:51 | 2021-11-15 21:28 | 80 | 001:37 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B21111500184 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 97 | 2021-11-15 | 7760 | keep | 0 | Nov | 2021 | 0.0052853 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-11-15 20:14 | 2021-11-16 11:03 | 30 | 014:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO LINEA A CAJA | S21111500227 | New_Event | Wire Down | Include | Include | Equipment | 889 | 2021-11-15 | 26670 | keep | 0 | Nov | 2021 | 0.018165 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2021-11-15 20:17 | 2021-11-15 22:15 | 40 | 001:58 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | R21111500068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2021-11-15 | 4720 | keep | 0 | Nov | 2021 | 0.0032148 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-15 20:33 | 2021-11-15 23:58 | 40 | 003:25 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21111500228 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 205 | 2021-11-15 | 8200 | keep | 0 | Nov | 2021 | 0.005585 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-11-15 20:45 | 2021-11-15 21:40 | 20 | 000:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS AVERIADAS | A21111500085 | New_Event | Secondary Wire Down | Include | Include | Equipment | 55 | 2021-11-15 | 1100 | keep | 0 | Nov | 2021 | 0.0007492 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-11-15 21:04 | 2021-11-15 23:38 | 15 | 002:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE DESGANCHO Y CERRARON BAJANTE DE LINEA A CAJA | R21111500070 | New_Event | Wire Down | Include | Include | Equipment | 154 | 2021-11-15 | 2310 | keep | 0 | Nov | 2021 | 0.0015733 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-11-15 21:05 | 2021-11-15 21:08 | 2407 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR MACHETES | A21111500152 | Additional_clients | Wire Down | Include | Include | Equipment | 3 | 2021-11-15 | 7221 | keep | 0 | Nov | 2021 | 0.0049182 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-11-15 21:06 | 2021-11-16 15:10 | 5 | 018:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M21111500103 | New_Event | Wire Down | Include | Include | Equipment | 1084 | 2021-11-15 | 5420 | keep | 0 | Nov | 2021 | 0.0036915 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-11-15 21:46 | 2021-11-16 09:36 | 40 | 011:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA NO FUNDIO | R21111500071 | New_Event | Wire Down | Include | Include | Equipment | 710 | 2021-11-15 | 28400 | keep | 0 | Nov | 2021 | 0.019343 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-11-15 22:06 | 2021-11-15 22:07 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21111500105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-15 | 3458 | keep | 0 | Nov | 2021 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
VEGA BAJA | 2021-11-15 22:24 | 2021-11-15 22:25 | 652 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21111500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-15 | 652 | keep | 0 | Nov | 2021 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2021-11-15 22:24 | 2021-11-15 22:25 | 1463 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 50% DE SU CARGA ESTA TRANAFERIDO AL 9203-04 | B21111500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-15 | 1463 | keep | 0 | Nov | 2021 | 0.00099644 | 0.00099644 | Momentary | FALSE | FALSE | Not_TMED_Event | 1463
VEGA BAJA | 2021-11-15 22:24 | 2021-11-15 22:25 | 325 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21111500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-15 | 325 | keep | 0 | Nov | 2021 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
MAYAGÃœEZ | 2021-11-15 23:44 | 2021-11-15 23:45 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21111500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-15 | 1097 | keep | 0 | Nov | 2021 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
HUMACAO | 2021-11-16 00:21 | 2021-11-16 11:38 | 500 | 011:17 | P | SOBRECARGA | 3 X 200 3 X 140 Y 2 X 50 EN C/L POR CARGA SE COORDINO FUSIBLES | C21111600001 | New_Event | Trip Due To Overload | Include | Include | Other | 677 | 2021-11-16 | 338500 | keep | 0 | Nov | 2021 | 0.23055 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CAGUAS | 2021-11-16 02:56 | 2021-11-16 02:57 | 2608 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C21111600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-16 | 2608 | keep | 0 | Nov | 2021 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
CAGUAS | 2021-11-16 04:54 | 2021-11-16 10:14 | 8 | 005:20 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO CAUSA | C21111600003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 320 | 2021-11-16 | 2560 | keep | 0 | Nov | 2021 | 0.0017436 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-11-16 05:49 | 2021-11-16 16:35 | 9 | 010:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | M21111600001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 646 | 2021-11-16 | 5814 | keep | 0 | Nov | 2021 | 0.0039599 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2021-11-16 06:14 | 2021-11-16 09:47 | 10 | 003:33 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | A21111600001 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 213 | 2021-11-16 | 2130 | keep | 0 | Nov | 2021 | 0.0014507 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2021-11-16 06:29 | 2021-11-16 16:57 | 10 | 010:28 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21111600001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 628 | 2021-11-16 | 6280 | keep | 0 | Nov | 2021 | 0.0042773 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-11-16 07:07 | 2021-11-16 07:09 | 3718 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR | P211116000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-16 | 7436 | keep | 0 | Nov | 2021 | 0.0050646 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
BAYAMON | 2021-11-16 08:01 | 2021-11-16 13:10 | 40 | 005:09 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 65 EN CORTE DE LINEA SE REPARO TERMINACION EN PROVISIONAL AEREO | B21111600007 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 309 | 2021-11-16 | 12360 | keep | 0 | Nov | 2021 | 0.0084183 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-11-16 08:04 | 2021-11-16 08:06 | 1447 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1112-04 LLEVANDO CARGA 1419-09 Y 1419-12 | S21111600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-16 | 2894 | keep | 0 | Nov | 2021 | 0.0019711 | 0.00098555 | Momentary | FALSE | FALSE | Not_TMED_Event | 1447
SAN JUAN | 2021-11-16 08:04 | 2021-11-16 08:06 | 266 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1112-04 LLEVANDO CARGA 1419-09 Y 1419-12 | S21111600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-16 | 532 | keep | 0 | Nov | 2021 | 0.00036234 | 0.00018117 | Momentary | FALSE | FALSE | Not_TMED_Event | 266
SAN JUAN | 2021-11-16 08:04 | 2021-11-16 08:06 | 73 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1112-04 LLEVANDO CARGA 1419-09 Y 1419-12 | S21111600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-16 | 146 | keep | 0 | Nov | 2021 | 9.944e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
UTUADO | 2021-11-16 08:11 | 2021-11-16 09:53 | 2 | 001:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 20 EN TRANSFORMADOR SE RETIRO TENSOR CRUZANDO LINEAS SECUNDARIAS | A21111600005 | New_Event |  |  | Include | Wildlife | 102 | 2021-11-16 | 204 | keep | 0 | Nov | 2021 | 0.00013894 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2021-11-16 08:27 | 2021-11-16 10:36 | 100 | 002:09 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA INFORMA QUE NO SE DETECTO LA CAUSA | M21111600005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 129 | 2021-11-16 | 12900 | keep | 0 | Nov | 2021 | 0.0087861 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2021-11-16 08:27 | 2021-11-16 11:30 | 1 | 003:03 | P | DESGANCHE | 2 X 20 EN C/L | C21111600015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2021-11-16 | 183 | keep | 0 | Nov | 2021 | 0.00012464 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-16 08:58 | 2021-11-16 08:59 | 222 | 000:01 | T | DESGANCHE | RECERRO 1907-03 LLEVANDO 1909-09 | S21111600016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-16 | 222 | keep | 0 | Nov | 2021 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2021-11-16 08:58 | 2021-11-16 08:59 | 4456 | 000:01 | T | DESGANCHE | RECERRO 1907-03 LLEVANDO 1909-09 | S21111600016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-16 | 4456 | keep | 0 | Nov | 2021 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
BARRANQUITAS | 2021-11-16 09:00 | 2021-11-16 17:22 | 12 | 008:22 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR AVERIADO DE 25 KVA X 50 KVA | C21111600020 | New_Event | Service Transformer Failure | Include | Include | Equipment | 502 | 2021-11-16 | 6024 | keep | 0 | Nov | 2021 | 0.0041029 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-11-16 09:07 | 2021-11-16 09:08 | 222 | 000:01 | T | DESGANCHE | DISPARO 1907-03 LLEVANDO 1909-09 | S21111600016 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-16 | 222 | keep | 0 | Nov | 2021 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2021-11-16 09:07 | 2021-11-16 09:08 | 4456 | 000:01 | T | DESGANCHE | DISPARO 1907-03 LLEVANDO 1909-09 | S21111600016 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-16 | 4456 | keep | 0 | Nov | 2021 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
BAYAMON | 2021-11-16 09:14 | 2021-11-16 09:39 | 222 | 000:25 | T | DESGANCHE | DISPARO 1907-03 LLEVANDO EL 1909-09. SE ABRIO EN MH-1 MARTINEZ NADAL ENTRE 1907-03 Y 1909-09 | S21111600016 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 25 | 2021-11-16 | 5550 | keep | 0 | Nov | 2021 | 0.0037801 | 0.0001512 | Sustained | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2021-11-16 09:14 | 2021-11-16 13:35 | 4456 | 004:21 | T | DESGANCHE | SE SECCIONALIZO ARBOL SOBRE LINEAS Y ABEJAS ABRIENDO MACHETES CARR 177 HACIA AVENIDA ESMERALDA | S21111600016 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 261 | 2021-11-16 | 1163016 | keep | 0 | Nov | 2021 | 0.79212 | 0.003035 | Sustained | FALSE | FALSE | Not_TMED_Event | 4456
AGUADILLA | 2021-11-16 09:19 | 2021-11-16 17:35 | 20 | 008:16 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZAR CONECTORES | M21111600016 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 496 | 2021-11-16 | 9920 | keep | 0 | Nov | 2021 | 0.0067565 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-11-16 09:31 | 2021-11-16 10:43 | 10 | 001:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR NEUTRAL EN BAJANTE SECUNDARIO | S21111500231 | New_Event | Secondary Wire Down | Include | Include | Equipment | 72 | 2021-11-16 | 720 | keep | 0 | Nov | 2021 | 0.00049039 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-11-16 09:35 | 2021-11-16 09:36 | 1859 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 9207-08 LLEVANDO LA CARGA 9207-09 | B21111600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-16 | 1859 | keep | 0 | Nov | 2021 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2021-11-16 09:35 | 2021-11-16 09:36 | 7 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 9207-08 LLEVANDO LA CARGA DEL 9207-09 | B21111600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-16 | 7 | keep | 0 | Nov | 2021 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-11-16 09:39 | 2021-11-16 11:25 | 80 | 001:46 | P | DESGANCHE | SE SECCIONALIZO Y SE CERRO POR SCADA | S21111600016 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 106 | 2021-11-16 | 8480 | keep | 0 | Nov | 2021 | 0.0057757 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-11-16 09:39 | 2021-11-16 12:19 | 7 | 002:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO BAJANTE SECUNDARIO | C21111600025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 160 | 2021-11-16 | 1120 | keep | 0 | Nov | 2021 | 0.00076283 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2021-11-16 09:40 | 2021-11-16 11:55 | 5 | 002:15 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 15 KVA X 37.5 KVA | A21111600015 | New_Event | Service Transformer Failure | Include | Include | Equipment | 135 | 2021-11-16 | 675 | keep | 0 | Nov | 2021 | 0.00045974 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2021-11-16 10:14 | 2021-11-16 16:49 | 1 | 006:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE POR AVE | C21111600034 | New_Event |  |  | Include | Wildlife | 395 | 2021-11-16 | 395 | keep | 0 | Nov | 2021 | 0.00026903 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-11-16 10:16 | 2021-11-16 16:41 | 10 | 006:25 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R21111600008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 385 | 2021-11-16 | 3850 | keep | 0 | Nov | 2021 | 0.0026222 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-11-16 10:28 | 2021-11-16 18:05 | 30 | 007:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M21111600031 | New_Event | Wire Down | Include | Include | Equipment | 457 | 2021-11-16 | 13710 | keep | 0 | Nov | 2021 | 0.0093378 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2021-11-16 10:29 | 2021-11-16 10:31 | 3296 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C21111600041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-16 | 6592 | keep | 0 | Nov | 2021 | 0.0044898 | 0.0022449 | Momentary | FALSE | FALSE | Not_TMED_Event | 3296
PONCE | 2021-11-16 10:30 | 2021-11-16 18:49 | 70 | 008:19 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR DOS POSTES PRIMARIOS | P21111600010 | New_Event | Defective Pole | Include | Include | Equipment | 499 | 2021-11-16 | 34930 | keep | 0 | Nov | 2021 | 0.023791 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-11-16 10:31 | 2021-11-16 16:09 | 30 | 005:38 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21111600032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 338 | 2021-11-16 | 10140 | keep | 0 | Nov | 2021 | 0.0069063 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-11-16 10:34 | 2021-11-16 12:17 | 10 | 001:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | S21111500223 | New_Event | Secondary Wire Down | Include | Include | Equipment | 103 | 2021-11-16 | 1030 | keep | 0 | Nov | 2021 | 0.00070153 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-16 10:49 | 2021-11-16 20:46 | 50 | 009:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA CORTE DE LINEA | S21111600051 | New_Event | Wire Down | Include | Include | Equipment | 597 | 2021-11-16 | 29850 | keep | 0 | Nov | 2021 | 0.020331 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-16 10:55 | 2021-11-16 12:00 | 100 | 001:05 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | M21111600036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 65 | 2021-11-16 | 6500 | keep | 0 | Nov | 2021 | 0.0044271 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2021-11-16 11:05 | 2021-11-16 12:11 | 10 | 001:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B21111400127 | New_Event | Secondary Wire Down | Include | Include | Equipment | 66 | 2021-11-16 | 660 | keep | 0 | Nov | 2021 | 0.00044952 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-11-16 11:10 | 2021-11-16 11:11 | 4369 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21111600046 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-11-16 | 4369 | keep | 0 | Nov | 2021 | 0.0029757 | 0.0029757 | Momentary | FALSE | FALSE | Not_TMED_Event | 4369
CAGUAS | 2021-11-16 11:11 | 2021-11-16 16:07 | 100 | 004:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L REEMPLAZO PORTAFUSIBLE QUEMADO | C21111600049 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 296 | 2021-11-16 | 29600 | keep | 0 | Nov | 2021 | 0.02016 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-16 11:11 | 2021-11-16 14:14 | 4 | 003:03 | P | ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR Y SE REEMPLAZO POSTE PARTIDO | A21111600028 | New_Event | Defective Pole | Include | Include | Equipment | 183 | 2021-11-16 | 732 | keep | 0 | Nov | 2021 | 0.00049856 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-11-16 11:25 | 2021-11-16 11:26 | 222 | 000:01 | T | DESGANCHE | DISPARO 1907-03 LLEVANDO EL 1909-09. SE ABRIO MACHETES EN CARR 177 MARGINAL LOS FRAILES Y SE CERRO EN MH-1 MARTINEZ NADALPROVOCANDO QUE DISPARARA NUEVAMENTE 1907-03 | S21111600016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-16 | 222 | keep | 0 | Nov | 2021 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BARRANQUITAS | 2021-11-16 11:25 | 2021-11-16 13:32 | 20 | 002:07 | P | DESGANCHE | 1 X 25 EN C/L | C21111600054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2021-11-16 | 2540 | keep | 0 | Nov | 2021 | 0.00173 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-11-16 11:26 | 2021-11-16 12:12 | 30 | 000:46 | P | DESGANCHE | SE SECCIONALIZO Y SE CERRO POR SCADA | S21111600016 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 46 | 2021-11-16 | 1380 | keep | 0 | Nov | 2021 | 0.00093991 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2021-11-16 11:29 | 2021-11-16 11:54 | 331 | 000:25 | P | CABLE SOTERRADO AVERIADO | SE ABRE PROVISIONAL DEL 4006-04 AEREO PARA NORMALIZAR LA CARGA DEL 4006-05 | P21111600008 | New_Event | UG Cable Fault | Include | Include | Equipment | 25 | 2021-11-16 | 8275 | keep | 0 | Nov | 2021 | 0.0056361 | 0.00022544 | Sustained | FALSE | FALSE | Not_TMED_Event | 331
BAYAMON | 2021-11-16 11:31 | 2021-11-16 11:34 | 3708 | 000:03 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO INTERRUPTOR SE CERRO POR SCADA | S21111600070 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 3 | 2021-11-16 | 11124 | keep | 0 | Nov | 2021 | 0.0075765 | 0.0025255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3708
SAN JUAN | 2021-11-16 11:33 | 2021-11-16 11:53 | 4 | 000:20 | P | OTRAS CAUSAS | ABRIO XMR T - 268 PARA PERITO ELECTRICISTA ENCABEZAR TUBERIA | R21111600011 | New_Event | Other Causes | Include | Include | Other | 20 | 2021-11-16 | 80 | keep | 0 | Nov | 2021 | 5.4488e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-11-16 11:34 | 2021-11-16 16:29 | 80 | 004:55 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRE MACHETES Y SE ESTABLECIO GOI PARA REMPLAZAR DISCO | S21111600074 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 295 | 2021-11-16 | 23600 | keep | 0 | Nov | 2021 | 0.016074 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2021-11-16 11:38 | 2021-11-16 12:53 | 5 | 001:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | R21111600012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 75 | 2021-11-16 | 375 | keep | 0 | Nov | 2021 | 0.00025541 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2021-11-16 12:04 | 2021-11-16 13:07 | 1 | 001:03 | P | NO SE REPORTO CAUSA | 1 X 40 C/L Y 1 X 10 XMR NO CAUSA | R21111600015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2021-11-16 | 63 | keep | 0 | Nov | 2021 | 4.2909e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-11-16 12:06 | 2021-11-16 15:17 | 200 | 003:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO CON GOI BY-211116-01 | B21111200037 | New_Event | Wire Down | Include | Include | Equipment | 191 | 2021-11-16 | 38200 | keep | 0 | Nov | 2021 | 0.026018 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-11-16 12:12 | 2021-11-16 12:13 | 222 | 000:01 | T | DESGANCHE | DISPARO 1907-03 LLEVANDO EL 1909-09. SE ABRIO MACHETES EN CARR 177 MARGINAL LOS FRAILES Y SE CERRO EN MH-1 MARTINEZ NADAL PROVOCANDO QUE DISPARARA NUEVAMENTE 1907-03. SE ESCUHO EXPLOSION PERO NO ENCUENTRAN AVERIA | S21111600016 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-16 | 222 | keep | 0 | Nov | 2021 | 0.0001512 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-16 12:13 | 2021-11-16 19:35 | 3 | 007:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | R21111600016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 442 | 2021-11-16 | 1326 | keep | 0 | Nov | 2021 | 0.00090313 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-11-16 12:13 | 2021-11-16 12:31 | 15 | 000:18 | P | DESGANCHE | SE SECCIONALIZO Y SE CERRO POR SCADA | S21111600016 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 18 | 2021-11-16 | 270 | keep | 0 | Nov | 2021 | 0.0001839 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-11-16 12:20 | 2021-11-16 12:47 | 3522 | 000:27 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DOS BOCAS | M21111600036 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 27 | 2021-11-16 | 95094 | keep | 0 | Nov | 2021 | 0.064768 | 0.0023988 | Sustained | FALSE | FALSE | Not_TMED_Event | 3522
MAYAGÃœEZ | 2021-11-16 12:20 | 2021-11-16 12:47 | 1337 | 000:27 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DOS BOCAS | M21111600036 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 27 | 2021-11-16 | 36099 | keep | 0 | Nov | 2021 | 0.024587 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
MAYAGÃœEZ | 2021-11-16 12:20 | 2021-11-16 12:47 | 2825 | 000:27 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DOS BOCAS | M21111600036 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 27 | 2021-11-16 | 76275 | keep | 0 | Nov | 2021 | 0.051951 | 0.0019241 | Sustained | FALSE | FALSE | Not_TMED_Event | 2825
MAYAGÃœEZ | 2021-11-16 12:20 | 2021-11-16 12:47 | 1287 | 000:27 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DOS BOCAS | M21111600036 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 27 | 2021-11-16 | 34749 | keep | 0 | Nov | 2021 | 0.023667 | 0.00087657 | Sustained | FALSE | FALSE | Not_TMED_Event | 1287
ARECIBO | 2021-11-16 12:20 | 2021-11-16 13:53 | 1548 | 001:33 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV ARECIBO SECT | A21111600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 93 | 2021-11-16 | 143964 | keep | 0 | Nov | 2021 | 0.098053 | 0.0010543 | Sustained | FALSE | FALSE | Not_TMED_Event | 1548
ARECIBO | 2021-11-16 12:20 | 2021-11-16 13:53 | 274 | 001:33 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV ARECIBO SECT | A21111600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 93 | 2021-11-16 | 25482 | keep | 0 | Nov | 2021 | 0.017356 | 0.00018662 | Sustained | FALSE | FALSE | Not_TMED_Event | 274
ARECIBO | 2021-11-16 12:20 | 2021-11-16 13:53 | 185 | 001:33 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV ARECIBO SECT | A21111600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 93 | 2021-11-16 | 17205 | keep | 0 | Nov | 2021 | 0.011718 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
ARECIBO | 2021-11-16 12:20 | 2021-11-16 13:53 | 9 | 001:33 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV ARECIBO SECT | A21111600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 93 | 2021-11-16 | 837 | keep | 0 | Nov | 2021 | 0.00057008 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2021-11-16 12:20 | 2021-11-16 12:29 | 1105 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV DOS BOCAS ARECIBO | A21111600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2021-11-16 | 9945 | keep | 0 | Nov | 2021 | 0.0067735 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
ARECIBO | 2021-11-16 12:20 | 2021-11-16 13:53 | 316 | 001:33 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV ARECIBO SECT | A21111600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 93 | 2021-11-16 | 29388 | keep | 0 | Nov | 2021 | 0.020016 | 0.00021523 | Sustained | FALSE | FALSE | Not_TMED_Event | 316
ARECIBO | 2021-11-16 12:20 | 2021-11-16 13:53 | 1227 | 001:33 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV ARECIBO SECT | A21111600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 93 | 2021-11-16 | 114111 | keep | 0 | Nov | 2021 | 0.07772 | 0.0008357 | Sustained | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2021-11-16 12:20 | 2021-11-16 13:53 | 3431 | 001:33 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV ARECIBO SECT | A21111600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 93 | 2021-11-16 | 319083 | keep | 0 | Nov | 2021 | 0.21733 | 0.0023368 | Sustained | FALSE | FALSE | Not_TMED_Event | 3431
UTUADO | 2021-11-16 12:20 | 2021-11-16 12:29 | 1405 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV DOS BOCAS ARECIBO | A21111600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2021-11-16 | 12645 | keep | 0 | Nov | 2021 | 0.0086125 | 0.00095694 | Sustained | FALSE | FALSE | Not_TMED_Event | 1405
UTUADO | 2021-11-16 12:20 | 2021-11-16 12:29 | 669 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV DOS BOCAS ARECIBO | A21111600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2021-11-16 | 6021 | keep | 0 | Nov | 2021 | 0.0041009 | 0.00045565 | Sustained | FALSE | FALSE | Not_TMED_Event | 669
UTUADO | 2021-11-16 12:20 | 2021-11-16 12:29 | 1527 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV DOS BOCAS ARECIBO | A21111600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2021-11-16 | 13743 | keep | 0 | Nov | 2021 | 0.0093603 | 0.00104 | Sustained | FALSE | FALSE | Not_TMED_Event | 1527
UTUADO | 2021-11-16 12:20 | 2021-11-16 12:29 | 1054 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV DOS BOCAS ARECIBO | A21111600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2021-11-16 | 9486 | keep | 0 | Nov | 2021 | 0.0064609 | 0.00071787 | Sustained | FALSE | FALSE | Not_TMED_Event | 1054
UTUADO | 2021-11-16 12:20 | 2021-11-16 12:29 | 932 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV DOS BOCAS ARECIBO | A21111600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2021-11-16 | 8388 | keep | 0 | Nov | 2021 | 0.005713 | 0.00063478 | Sustained | FALSE | FALSE | Not_TMED_Event | 932
UTUADO | 2021-11-16 12:20 | 2021-11-16 12:29 | 1633 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV DOS BOCAS ARECIBO | A21111600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2021-11-16 | 14697 | keep | 0 | Nov | 2021 | 0.01001 | 0.0011122 | Sustained | FALSE | FALSE | Not_TMED_Event | 1633
UTUADO | 2021-11-16 12:20 | 2021-11-16 12:29 | 1624 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV DOS BOCAS ARECIBO | A21111600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2021-11-16 | 14616 | keep | 0 | Nov | 2021 | 0.0099549 | 0.0011061 | Sustained | FALSE | FALSE | Not_TMED_Event | 1624
UTUADO | 2021-11-16 12:20 | 2021-11-16 12:29 | 705 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV DOS BOCAS ARECIBO | A21111600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2021-11-16 | 6345 | keep | 0 | Nov | 2021 | 0.0043216 | 0.00048017 | Sustained | FALSE | FALSE | Not_TMED_Event | 705
UTUADO | 2021-11-16 12:20 | 2021-11-16 12:29 | 1521 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV DOS BOCAS ARECIBO | A21111600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2021-11-16 | 13689 | keep | 0 | Nov | 2021 | 0.0093235 | 0.0010359 | Sustained | FALSE | FALSE | Not_TMED_Event | 1521
UTUADO | 2021-11-16 12:20 | 2021-11-16 12:29 | 882 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV DOS BOCAS ARECIBO | A21111600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2021-11-16 | 7938 | keep | 0 | Nov | 2021 | 0.0054065 | 0.00060073 | Sustained | FALSE | FALSE | Not_TMED_Event | 882
HUMACAO | 2021-11-16 12:29 | 2021-11-16 16:52 | 100 | 004:23 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | C21111600061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2021-11-16 | 26300 | keep | 0 | Nov | 2021 | 0.017913 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2021-11-16 12:30 | 2021-11-16 12:31 | 1475 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P211116000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-16 | 1475 | keep | 0 | Nov | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
BAYAMON | 2021-11-16 12:31 | 2021-11-16 12:32 | 222 | 000:01 | T | DESGANCHE | DISPARO 1907-03 LLEVANDO EL 1909-09. SE ABRIO MACHETES EN CARR 177 MARGINAL LOS FRAILES Y SE CERRO EN MH-1 MARTINEZ NADAL PROVOCANDO QUE DISPARARA NUEVAMENTE 1907-03. OPERACION A PETICION DE FOREMAN Y SUPVR EDWARD ONEILL PARA PODER LOCALIZAR AVERIA | S21111600016 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-16 | 222 | keep | 0 | Nov | 2021 | 0.0001512 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-11-16 12:39 | 2021-11-16 18:48 | 50 | 006:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L | C21111600063 | New_Event | Bad Weather | Include | Include | Weather | 369 | 2021-11-16 | 18450 | keep | 0 | Nov | 2021 | 0.012566 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-11-16 12:42 | 2021-11-16 12:43 | 1712 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO RECERRO LLEVA LA CARGA DEL 5010-04 | P211116000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-16 | 1712 | keep | 0 | Nov | 2021 | 0.001166 | 0.001166 | Momentary | FALSE | FALSE | Not_TMED_Event | 1712
PONCE | 2021-11-16 12:42 | 2021-11-16 12:44 | 7 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 5005-03 CARGA ESTA TRANSFERIDA A ESTE ALIMENTADOR | P211116000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-16 | 14 | keep | 0 | Nov | 2021 | 9.5353e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2021-11-16 12:43 | 2021-11-16 14:04 | 10 | 001:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR CRUCE POR AVE | C21111600065 | New_Event |  |  | Include | Wildlife | 81 | 2021-11-16 | 810 | keep | 0 | Nov | 2021 | 0.00055169 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-11-16 12:46 | 2021-11-16 17:27 | 5 | 004:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR LINEA SECUNDARIA | P21111600020 | New_Event | Secondary Wire Down | Include | Include | Equipment | 281 | 2021-11-16 | 1405 | keep | 0 | Nov | 2021 | 0.00095694 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-11-16 12:46 | 2021-11-16 12:47 | 4381 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | M21111600049 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-11-16 | 4381 | keep | 0 | Nov | 2021 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
MAYAGÃœEZ | 2021-11-16 12:47 | 2021-11-16 21:17 | 150 | 008:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA QUEMADA | M21111600067 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 510 | 2021-11-16 | 76500 | keep | 0 | Nov | 2021 | 0.052104 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2021-11-16 13:08 | 2021-11-16 17:49 | 40 | 004:41 | P | DESGANCHE | 1 X 40 EN C/L | C21111600069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 281 | 2021-11-16 | 11240 | keep | 0 | Nov | 2021 | 0.0076555 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-11-16 13:15 | 2021-11-16 18:41 | 40 | 005:26 | P | DESGANCHE | ABRIO C/L PARA CONTRATISTA DESGANCHAR | C21111600051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 326 | 2021-11-16 | 13040 | keep | 0 | Nov | 2021 | 0.0088815 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2021-11-16 13:19 | 2021-11-16 15:20 | 16 | 002:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | R21111600018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 121 | 2021-11-16 | 1936 | keep | 0 | Nov | 2021 | 0.0013186 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2021-11-16 13:21 | 2021-11-16 18:15 | 20 | 004:54 | P | ESTRUCTURA AVERIADA | ABRIO C/L PARA REEMPLAZAR POSTE PARTIDO | C21111600073 | New_Event | Defective Pole | Include | Include | Equipment | 294 | 2021-11-16 | 5880 | keep | 0 | Nov | 2021 | 0.0040048 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2021-11-16 13:47 | 2021-11-16 16:00 | 15 | 002:13 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5 KVA A 2.4 KV POR TRANSFORMADOR DE MISMA CAPACIDAD | P21111600025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 133 | 2021-11-16 | 1995 | keep | 0 | Nov | 2021 | 0.0013588 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-11-16 14:00 | 2021-11-16 16:01 | 80 | 002:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA POR AVE | A21111600103 | New_Event |  |  | Include | Wildlife | 121 | 2021-11-16 | 9680 | keep | 0 | Nov | 2021 | 0.006593 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-11-16 14:02 | 2021-11-16 20:30 | 107 | 006:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRE CORTE DE LINEA PARA REMPLAZO POSTE POR ACCIDENTE CAMION | S21111600121 | New_Event |  |  | Include | Wildlife | 388 | 2021-11-16 | 41516 | keep | 0 | Nov | 2021 | 0.028276 | 7.2877e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 107
BAYAMON | 2021-11-16 14:02 | 2021-11-16 22:19 | 15 | 008:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21111600121 | New_Event | Secondary Wire Down | Include | Include | Equipment | 497 | 2021-11-16 | 7455 | keep | 0 | Nov | 2021 | 0.0050776 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-11-16 14:21 | 2021-11-16 15:37 | 13 | 001:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21111600017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 76 | 2021-11-16 | 988 | keep | 0 | Nov | 2021 | 0.00067292 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BARRANQUITAS | 2021-11-16 14:33 | 2021-11-16 18:56 | 100 | 004:23 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHO Y REEMPLAZO CAJA QUEMADA | C21111600089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2021-11-16 | 26300 | keep | 0 | Nov | 2021 | 0.017913 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-11-16 14:49 | 2021-11-17 10:11 | 25 | 019:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L REEMPLAZO CAJA AVERIADA | C21111600093 | New_Event | Cutout Failure | Include | Include | Equipment | 1162 | 2021-11-16 | 29050 | keep | 0 | Nov | 2021 | 0.019786 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2021-11-16 15:01 | 2021-11-16 17:41 | 85 | 002:40 | P | DESGANCHE | 2 X 65 EN C/L | C21111600098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2021-11-16 | 13600 | keep | 0 | Nov | 2021 | 0.0092629 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
CAGUAS | 2021-11-16 15:01 | 2021-11-16 16:58 | 50 | 001:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE POR AVE | C21111600097 | New_Event |  |  | Include | Wildlife | 117 | 2021-11-16 | 5850 | keep | 0 | Nov | 2021 | 0.0039844 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-16 15:15 | 2021-11-17 13:06 | 1 | 021:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA EN RISER | S21111600034 | New_Event | Cutout Failure | Include | Include | Equipment | 1311 | 2021-11-16 | 1311 | keep | 0 | Nov | 2021 | 0.00089292 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-11-16 15:17 | 2021-11-16 16:23 | 652 | 001:06 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE PRIMARIO CON GOI BY-211116-01 | B21111600037 | Additional_clients | Wire Down | Include | Include | Equipment | 66 | 2021-11-16 | 43032 | keep | 0 | Nov | 2021 | 0.029309 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-11-16 15:22 | 2021-11-16 15:56 | 15 | 000:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21111600037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 34 | 2021-11-16 | 510 | keep | 0 | Nov | 2021 | 0.00034736 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-11-16 15:29 | 2021-11-16 15:30 | 1648 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21111600024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-16 | 1648 | keep | 0 | Nov | 2021 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
BAYAMON | 2021-11-16 15:44 | 2021-11-16 17:29 | 30 | 001:45 | P | HERRAJE ROTO O PODRIDO | SE ABRIO CORTE DE LINEA PARA LLEVAR A SU LUGAR TRANSFORMADOR QUE SE SALIO DE LOS TORNILLOS QUE LO SUJETAN | B21111600039 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 105 | 2021-11-16 | 3150 | keep | 0 | Nov | 2021 | 0.0021455 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2021-11-16 15:55 | 2021-11-17 19:05 | 8 | 027:10 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO CON TRANSFORMADOR | P21111600031 | New_Event | Defective Pole | Include | Include | Equipment | 1630 | 2021-11-16 | 13040 | keep | 0 | Nov | 2021 | 0.0088815 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2021-11-16 16:04 | 2021-11-16 16:08 | 3718 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CON RR EN OFF SE CONFIRMO PERSONAL FUERA DE LINEAS PRIMARIAS Y SE REALIZO PRUEBA QUEDANDO EL INTERRUPTOR EN SERVICIO | P21111600033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-11-16 | 14872 | keep | 0 | Nov | 2021 | 0.010129 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
CAGUAS | 2021-11-16 16:16 | 2021-11-17 21:17 | 5 | 029:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR XMR PARA REPARAR SECUNDARIA | C21111600113 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1741 | 2021-11-16 | 8705 | keep | 0 | Nov | 2021 | 0.0059289 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-11-16 16:16 | 2021-11-16 22:00 | 50 | 005:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN C/L LEVANTO NEUTRAL PRIMARIO | C21111600113 | New_Event | Wire Down | Include | Include | Equipment | 344 | 2021-11-16 | 17200 | keep | 0 | Nov | 2021 | 0.011715 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-16 16:17 | 2021-11-16 19:41 | 10 | 003:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21111600151 | New_Event | Secondary Wire Down | Include | Include | Equipment | 204 | 2021-11-16 | 2040 | keep | 0 | Nov | 2021 | 0.0013894 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-16 16:22 | 2021-11-16 16:23 | 2107 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21111600113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-16 | 2107 | keep | 0 | Nov | 2021 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
CAGUAS | 2021-11-16 16:26 | 2021-11-16 18:21 | 9 | 001:55 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO 15 KVA X 25 KVA | C21111600119 | New_Event | Service Transformer Failure | Include | Include | Equipment | 115 | 2021-11-16 | 1035 | keep | 0 | Nov | 2021 | 0.00070493 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
YAUCO | 2021-11-16 16:29 | 2021-11-16 17:48 | 100 | 001:19 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE | P21111600035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2021-11-16 | 7900 | keep | 0 | Nov | 2021 | 0.0053807 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-11-16 16:39 | 2021-11-17 10:46 | 8 | 018:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C21111600121 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1087 | 2021-11-16 | 8696 | keep | 0 | Nov | 2021 | 0.0059228 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-11-16 16:45 | 2021-11-16 16:58 | 2 | 000:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE CONECTORES | M21111600065 | New_Event | Secondary Wire Down | Include | Include | Equipment | 13 | 2021-11-16 | 26 | keep | 0 | Nov | 2021 | 1.7708e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2021-11-16 16:48 | 2021-11-16 20:10 | 30 | 003:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA CON GOI BY-211116-03 | B21111600058 | New_Event | Cutout Failure | Include | Include | Equipment | 202 | 2021-11-16 | 6060 | keep | 0 | Nov | 2021 | 0.0041274 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2021-11-16 16:49 | 2021-11-16 17:50 | 20 | 001:01 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE REPORTO CAUSA | P21111600039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 61 | 2021-11-16 | 1220 | keep | 0 | Nov | 2021 | 0.00083094 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-11-16 16:52 | 2021-11-16 20:15 | 130 | 003:23 | P | DESGANCHE | 2 X 65 EN C/L | C21111600125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2021-11-16 | 26390 | keep | 0 | Nov | 2021 | 0.017974 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
ARECIBO | 2021-11-16 17:03 | 2021-11-16 17:50 | 10 | 000:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 8 EN TRANSFORMADOR SE REPARO SECUNDARIA PARTIDA | A21111600116 | New_Event | Secondary Wire Down | Include | Include | Equipment | 47 | 2021-11-16 | 470 | keep | 0 | Nov | 2021 | 0.00032011 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-16 17:06 | 2021-11-16 18:28 | 15 | 001:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21111500170 | New_Event | Secondary Wire Down | Include | Include | Equipment | 82 | 2021-11-16 | 1230 | keep | 0 | Nov | 2021 | 0.00083775 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-11-16 17:18 | 2021-11-16 18:13 | 20 | 000:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO C/L PARA LEVANTAR NEUTRAL PRIMARIO | C21102600117 | New_Event | Wire Down | Include | Include | Equipment | 55 | 2021-11-16 | 1100 | keep | 0 | Nov | 2021 | 0.0007492 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2021-11-16 17:23 | 2021-11-16 19:43 | 500 | 002:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA Y SE CERRO PUENTE PRIMARIO | P21111600046 | New_Event | Wire Down | Include | Include | Equipment | 140 | 2021-11-16 | 70000 | keep | 0 | Nov | 2021 | 0.047677 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
ARECIBO | 2021-11-16 17:27 | 2021-11-16 18:13 | 1 | 000:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | A21111600119 | New_Event | Secondary Wire Down | Include | Include | Equipment | 46 | 2021-11-16 | 46 | keep | 0 | Nov | 2021 | 3.133e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-16 17:29 | 2021-11-16 18:53 | 339 | 001:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 Y 1 X 80 EN CORTE DE LINEA PERSONAL DRC DESGANCHANDO CRUZO FASE | S21111600159 | New_Event |  |  | Include | Wildlife | 84 | 2021-11-16 | 28476 | keep | 0 | Nov | 2021 | 0.019395 | 0.00023089 | Sustained | FALSE | FALSE | Not_TMED_Event | 339
BAYAMON | 2021-11-16 17:55 | 2021-11-16 19:30 | 10 | 001:35 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21111600059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 95 | 2021-11-16 | 950 | keep | 0 | Nov | 2021 | 0.00064704 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-11-16 18:16 | 2021-11-16 18:17 | 1825 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21111600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-16 | 1825 | keep | 0 | Nov | 2021 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
CAGUAS | 2021-11-16 18:35 | 2021-11-17 01:46 | 676 | 007:11 | T | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETES DE BARRA QUEMADOS | C21111600176 | New_Event | Switch Failure | Include | Include | Equipment | 431 | 2021-11-16 | 291356 | keep | 0 | Nov | 2021 | 0.19844 | 0.00046042 | Sustained | FALSE | FALSE | Not_TMED_Event | 676
BAYAMON | 2021-11-16 18:35 | 2021-11-16 21:27 | 40 | 002:52 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 40 EN CORTE DE LINEA | B21111600064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 172 | 2021-11-16 | 6880 | keep | 0 | Nov | 2021 | 0.0046859 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-16 18:42 | 2021-11-16 19:22 | 12 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21111600107 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2021-11-16 | 480 | keep | 0 | Nov | 2021 | 0.00032693 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2021-11-16 19:20 | 2021-11-17 05:13 | 150 | 009:53 | P | DESGANCHE | 3 X 80 EN C/L | C21111600197 | New_Event | Vegetation Contact | Include | Include | Vegetation | 593 | 2021-11-16 | 88950 | keep | 0 | Nov | 2021 | 0.060583 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2021-11-16 19:21 | 2021-11-16 20:08 | 40 | 000:47 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA SE INSPECCIONO | R21111600040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 47 | 2021-11-16 | 1880 | keep | 0 | Nov | 2021 | 0.0012805 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2021-11-16 19:28 | 2021-11-16 21:40 | 150 | 002:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA VEHICULO IMPACTA POSTE PRIMARIO | P21111600064 | New_Event |  |  | Include | Wildlife | 132 | 2021-11-16 | 19800 | keep | 0 | Nov | 2021 | 0.013486 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2021-11-16 19:38 | 2021-11-16 19:40 | 1463 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO 50% POR EL 9203-04 | B21111600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-16 | 2926 | keep | 0 | Nov | 2021 | 0.0019929 | 0.00099644 | Momentary | FALSE | FALSE | Not_TMED_Event | 1463
VEGA BAJA | 2021-11-16 19:38 | 2021-11-16 19:40 | 1570 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA 50% 9202-04 | B21111600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-16 | 3140 | keep | 0 | Nov | 2021 | 0.0021386 | 0.0010693 | Momentary | FALSE | FALSE | Not_TMED_Event | 1570
VEGA BAJA | 2021-11-16 19:41 | 2021-11-16 21:48 | 776 | 002:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV VEGA BAJA TC | B21111600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 127 | 2021-11-16 | 98552 | keep | 0 | Nov | 2021 | 0.067123 | 0.00052853 | Sustained | FALSE | FALSE | Not_TMED_Event | 776
VEGA BAJA | 2021-11-16 19:41 | 2021-11-16 21:48 | 2216 | 002:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV VEGA BAJA TC | B21111600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 127 | 2021-11-16 | 281432 | keep | 0 | Nov | 2021 | 0.19168 | 0.0015093 | Sustained | FALSE | FALSE | Not_TMED_Event | 2216
BARRANQUITAS | 2021-11-16 19:48 | 2021-11-17 13:56 | 40 | 018:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN C/L LEVANTO CONDUCTOR | C21111600212 | New_Event | Wire Down | Include | Include | Equipment | 1088 | 2021-11-16 | 43520 | keep | 0 | Nov | 2021 | 0.029641 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-11-16 19:52 | 2021-11-17 12:06 | 6 | 016:14 | P | DESGANCHE | 1 X 65 EN C/L | C21111600216 | New_Event | Vegetation Contact | Include | Include | Vegetation | 974 | 2021-11-16 | 5844 | keep | 0 | Nov | 2021 | 0.0039803 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2021-11-16 19:53 | 2021-11-17 13:30 | 15 | 017:37 | P | TRANSFORMADOR AVERIADO | 1 X 15 EN TRANSFORMADOR POR ESTAR AVERIADO SE CAMBIO TRANSFORMADOR DE 15KVA A 2.4KV POR UNO DE LA MISMA CAPACIDAD | P21111600038 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1057 | 2021-11-16 | 15855 | keep | 0 | Nov | 2021 | 0.010799 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-11-16 20:10 | 2021-11-16 21:55 | 663 | 001:45 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ESTABLECIO GOI BY-211116-03 PARA REMPLAZO DE CAJA PRIMARIA | B21111600058 | Additional_clients | Cutout Failure | Include | Include | Equipment | 105 | 2021-11-16 | 69615 | keep | 0 | Nov | 2021 | 0.047414 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-11-16 20:12 | 2021-11-17 10:17 | 200 | 014:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21111600142 | New_Event | Bad Weather | Include | Include | Weather | 845 | 2021-11-16 | 169000 | keep | 0 | Nov | 2021 | 0.11511 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2021-11-16 20:13 | 2021-11-17 16:10 | 25 | 019:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA EN TRANSFORMADOR | A21111600143 | New_Event | Cutout Failure | Include | Include | Equipment | 1197 | 2021-11-16 | 29925 | keep | 0 | Nov | 2021 | 0.020382 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-11-16 20:37 | 2021-11-17 12:58 | 10 | 016:21 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR QUEMADO DE 50 KVA X 50 KVA | R21111600048 | New_Event | Service Transformer Failure | Include | Include | Equipment | 981 | 2021-11-16 | 9810 | keep | 0 | Nov | 2021 | 0.0066815 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-16 20:39 | 2021-11-17 09:31 | 40 | 012:52 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21111600212 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 772 | 2021-11-16 | 30880 | keep | 0 | Nov | 2021 | 0.021032 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-11-16 20:56 | 2021-11-16 22:05 | 20 | 001:09 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | M21111600125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 69 | 2021-11-16 | 1380 | keep | 0 | Nov | 2021 | 0.00093991 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2021-11-16 21:00 | 2021-11-17 17:20 | 100 | 020:20 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21111600149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1220 | 2021-11-16 | 122000 | keep | 0 | Nov | 2021 | 0.083094 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2021-11-16 21:15 | 2021-11-16 22:50 | 350 | 001:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO | M21111600133 | New_Event | Wire Down | Include | Include | Equipment | 95 | 2021-11-16 | 33250 | keep | 0 | Nov | 2021 | 0.022646 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
CAGUAS | 2021-11-16 21:53 | 2021-11-17 01:46 | 4369 | 003:53 | T | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETES DE BARRA QUEMADOS DEL 3010-02 | C21111600176 | New_Event | Switch Failure | Include | Include | Equipment | 233 | 2021-11-16 | 1017977 | keep | 0 | Nov | 2021 | 0.69334 | 0.0029757 | Sustained | FALSE | FALSE | Not_TMED_Event | 4369
CAGUAS | 2021-11-16 21:53 | 2021-11-17 01:46 | 1606 | 003:53 | T | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETES DE BARRA QUEMADOS DEL 3010-02 LLEVANDO LA CARGA DEL 3010-04 | C21111600176 | New_Event | Switch Failure | Include | Include | Equipment | 233 | 2021-11-16 | 374198 | keep | 0 | Nov | 2021 | 0.25486 | 0.0010938 | Sustained | FALSE | FALSE | Not_TMED_Event | 1606
CAGUAS | 2021-11-16 21:53 | 2021-11-17 01:46 | 725 | 003:53 | T | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETES DE BARRA QUEMADOS DEL 3010-02 CARGA POR EL 3010-03 | C21111600176 | New_Event | Switch Failure | Include | Include | Equipment | 233 | 2021-11-16 | 168925 | keep | 0 | Nov | 2021 | 0.11505 | 0.00049379 | Sustained | FALSE | FALSE | Not_TMED_Event | 725
MAYAGÃœEZ | 2021-11-16 22:05 | 2021-11-16 23:22 | 100 | 001:17 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M21111600148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2021-11-16 | 7700 | keep | 0 | Nov | 2021 | 0.0052444 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-16 22:16 | 2021-11-17 14:00 | 30 | 015:44 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA POR 50 KVA | A21111600151 | New_Event | Service Transformer Failure | Include | Include | Equipment | 944 | 2021-11-16 | 28320 | keep | 0 | Nov | 2021 | 0.019289 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2021-11-16 22:24 | 2021-11-17 10:56 | 100 | 012:32 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 100 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B21111600211 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 752 | 2021-11-16 | 75200 | keep | 0 | Nov | 2021 | 0.051218 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-11-16 22:45 | 2021-11-16 23:05 | 15 | 000:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21111600156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 20 | 2021-11-16 | 300 | keep | 0 | Nov | 2021 | 0.00020433 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-11-16 23:32 | 2021-11-17 00:25 | 50 | 000:53 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO RAMA | M21111600163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 53 | 2021-11-16 | 2650 | keep | 0 | Nov | 2021 | 0.0018049 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-17 00:02 | 2021-11-17 11:08 | 50 | 011:06 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21111700001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 666 | 2021-11-17 | 33300 | keep | 0 | Nov | 2021 | 0.02268 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-11-17 00:05 | 2021-11-17 15:45 | 60 | 015:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | P21111700005 | New_Event | Cutout Failure | Include | Include | Equipment | 940 | 2021-11-17 | 56400 | keep | 0 | Nov | 2021 | 0.038414 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-11-17 00:22 | 2021-11-17 00:23 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 108 | keep | 0 | Nov | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
PONCE | 2021-11-17 01:00 | 2021-11-17 11:59 | 100 | 010:59 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P21111700006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 659 | 2021-11-17 | 65900 | keep | 0 | Nov | 2021 | 0.044884 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-11-17 01:03 | 2021-11-17 05:16 | 200 | 004:13 | P | DESGANCHE | 2 X 200 EN CORTE DE LINEA SE RETIRO ENREDADERA | M21111700005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 253 | 2021-11-17 | 50600 | keep | 0 | Nov | 2021 | 0.034463 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-11-17 01:50 | 2021-11-17 01:51 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21111700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 108 | keep | 0 | Nov | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
MAYAGÃœEZ | 2021-11-17 02:33 | 2021-11-17 02:34 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 108 | keep | 0 | Nov | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
GUAYAMA | 2021-11-17 04:26 | 2021-11-17 10:36 | 50 | 006:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21111700010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 370 | 2021-11-17 | 18500 | keep | 0 | Nov | 2021 | 0.0126 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-17 04:57 | 2021-11-17 04:58 | 108 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M21111700000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-11-17 | 108 | keep | 0 | Nov | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
MAYAGÃœEZ | 2021-11-17 04:58 | 2021-11-17 15:19 | 60 | 010:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR FUERTES VIENTOS | M21111700198 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 621 | 2021-11-17 | 37260 | keep | 0 | Nov | 2021 | 0.025378 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2021-11-17 05:04 | 2021-11-17 11:03 | 44 | 005:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L REEMPLAZO CAJA QUEMADA | R21111700003 | New_Event | Cutout Failure | Include | Include | Equipment | 359 | 2021-11-17 | 15796 | keep | 0 | Nov | 2021 | 0.010759 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
BAYAMON | 2021-11-17 05:07 | 2021-11-17 10:01 | 40 | 004:54 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21111700004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 294 | 2021-11-17 | 11760 | keep | 0 | Nov | 2021 | 0.0080097 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2021-11-17 05:13 | 2021-11-17 05:14 | 3565 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | C21111700000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-17 | 3565 | keep | 0 | Nov | 2021 | 0.0024281 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-11-17 05:14 | 2021-11-17 17:13 | 150 | 011:59 | P | DESGANCHE | 3 X 80 EN C/L | C21111600197 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 719 | 2021-11-17 | 107850 | keep | 0 | Nov | 2021 | 0.073456 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-11-17 05:16 | 2021-11-17 11:00 | 1444 | 005:44 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERERUPTO POR LINEAS CRUZADAS | M21111700019 | New_Event | Wire Down | Include | Include | Equipment | 344 | 2021-11-17 | 496736 | keep | 0 | Nov | 2021 | 0.33832 | 0.0009835 | Sustained | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2021-11-17 05:16 | 2021-11-17 10:35 | 3630 | 005:19 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR POR LINEA CRUZADAS | M21111700019 | New_Event | Wire Down | Include | Include | Equipment | 319 | 2021-11-17 | 1157970 | keep | 0 | Nov | 2021 | 0.78869 | 0.0024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 3630
PONCE | 2021-11-17 05:23 | 2021-11-17 12:51 | 50 | 007:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P21111700011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 448 | 2021-11-17 | 22400 | keep | 0 | Nov | 2021 | 0.015257 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-11-17 05:25 | 2021-11-17 18:18 | 50 | 012:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21111700024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 773 | 2021-11-17 | 38650 | keep | 0 | Nov | 2021 | 0.026324 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-11-17 05:57 | 2021-11-17 14:40 | 80 | 008:43 | P | DESGANCHE | 1 X 80 EN C/L | C21111700009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 523 | 2021-11-17 | 41840 | keep | 0 | Nov | 2021 | 0.028497 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-11-17 06:46 | 2021-11-17 06:48 | 100 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1401-08 LLEVANDO PARTE 1348-08 100% 1346-05 Y PARTE 1303-02 | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-17 | 200 | keep | 0 | Nov | 2021 | 0.00013622 | 6.811e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-11-17 06:46 | 2021-11-17 06:48 | 922 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1401-08 LLEVANDO PARTE 1348-08 100% 1346-05 Y PARTE 1303-02 | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-17 | 1844 | keep | 0 | Nov | 2021 | 0.0012559 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-11-17 06:46 | 2021-11-17 06:48 | 300 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1401-08 LLEVANDO PARTE 1348-08 100% 1346-05 Y PARTE 1303-02 | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-17 | 600 | keep | 0 | Nov | 2021 | 0.00040866 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2021-11-17 06:46 | 2021-11-17 06:48 | 135 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1401-08 LLEVANDO PARTE 1348-08 100% 1346-05 Y PARTE 1303-02 | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-17 | 270 | keep | 0 | Nov | 2021 | 0.0001839 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
BAYAMON | 2021-11-17 06:51 | 2021-11-17 08:00 | 643 | 001:09 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA SE REALIZO DESGANCHE | S21111700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 69 | 2021-11-17 | 44367 | keep | 0 | Nov | 2021 | 0.030218 | 0.00043794 | Sustained | FALSE | FALSE | Not_TMED_Event | 643
UTUADO | 2021-11-17 06:51 | 2021-11-17 10:07 | 40 | 003:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21111700001 | New_Event | Bad Weather | Include | Include | Weather | 196 | 2021-11-17 | 7840 | keep | 0 | Nov | 2021 | 0.0053398 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-11-17 06:53 | 2021-11-17 06:56 | 225 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 LLEVANDO CARGA 1303-04 SE CERRO POR SCADA | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-17 | 675 | keep | 0 | Nov | 2021 | 0.00045974 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-11-17 06:53 | 2021-11-17 06:56 | 870 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 LLEVANDO CARGA 1303-04 SE CERRO POR SCADA | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-17 | 2610 | keep | 0 | Nov | 2021 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
GUAYAMA | 2021-11-17 06:55 | 2021-11-17 09:31 | 30 | 002:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA POR AVE CRUZAR FASE | P21111700014 | New_Event |  |  | Include | Wildlife | 156 | 2021-11-17 | 4680 | keep | 0 | Nov | 2021 | 0.0031875 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-11-17 07:06 | 2021-11-17 07:07 | 1227 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO LA CAUSA | A21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 1227 | keep | 0 | Nov | 2021 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
UTUADO | 2021-11-17 07:47 | 2021-11-17 10:56 | 10 | 003:09 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR ROTO Y 2 X 15 EN TRANSFORMADOR | A21111700011 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 189 | 2021-11-17 | 1890 | keep | 0 | Nov | 2021 | 0.0012873 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-11-17 07:54 | 2021-11-17 13:17 | 6 | 005:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C21111700025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 323 | 2021-11-17 | 1938 | keep | 0 | Nov | 2021 | 0.00132 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-11-17 08:32 | 2021-11-17 08:33 | 534 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1519-05 LLEVANDO CARGA 1519-01 | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 534 | keep | 0 | Nov | 2021 | 0.0003637 | 0.0003637 | Momentary | FALSE | FALSE | Not_TMED_Event | 534
BAYAMON | 2021-11-17 08:32 | 2021-11-17 08:33 | 558 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1519-05 LLEVANDO CARGA 1519-01 | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 558 | keep | 0 | Nov | 2021 | 0.00038005 | 0.00038005 | Momentary | FALSE | FALSE | Not_TMED_Event | 558
BAYAMON | 2021-11-17 08:33 | 2021-11-17 10:47 | 40 | 002:14 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21111700019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2021-11-17 | 5360 | keep | 0 | Nov | 2021 | 0.0036507 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-17 08:34 | 2021-11-17 08:35 | 534 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1519-05 LLEVANDO CARGA 1519-01 | S21111700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 534 | keep | 0 | Nov | 2021 | 0.0003637 | 0.0003637 | Momentary | FALSE | FALSE | Not_TMED_Event | 534
BAYAMON | 2021-11-17 08:34 | 2021-11-17 08:35 | 558 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1519-05 LLEVANDO CARGA 1519-01 | S21111700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 558 | keep | 0 | Nov | 2021 | 0.00038005 | 0.00038005 | Momentary | FALSE | FALSE | Not_TMED_Event | 558
BAYAMON | 2021-11-17 08:40 | 2021-11-17 14:25 | 100 | 005:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE LEVANTO LINEA | S21111700034 | New_Event | Wire Down | Include | Include | Equipment | 345 | 2021-11-17 | 34500 | keep | 0 | Nov | 2021 | 0.023498 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-11-17 08:44 | 2021-11-17 08:45 | 4381 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 4381 | keep | 0 | Nov | 2021 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
BARRANQUITAS | 2021-11-17 08:50 | 2021-11-17 19:28 | 15 | 010:38 | P | DESGANCHE | 1 X 30 EN C/L | C21111700035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 638 | 2021-11-17 | 9570 | keep | 0 | Nov | 2021 | 0.0065181 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-11-17 08:52 | 2021-11-17 13:55 | 8 | 005:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO FUERTES VIENTOS | A21111700018 | New_Event | Bad Weather | Include | Include | Weather | 303 | 2021-11-17 | 2424 | keep | 0 | Nov | 2021 | 0.001651 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-11-17 08:59 | 2021-11-17 09:55 | 10 | 000:56 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 15KVA AVERIADO X TRANSFORMADOR DE 25 KVA FID 31437730 | A21111700020 | New_Event | Service Transformer Failure | Include | Include | Equipment | 56 | 2021-11-17 | 560 | keep | 0 | Nov | 2021 | 0.00038141 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-11-17 09:04 | 2021-11-17 15:40 | 50 | 006:36 | P | ESTRUCTURA AVERIADA | 3 X 65 EN CORTE DE LINEA CAMBIO DE POSTE PARTIDO | M21111700077 | New_Event | Defective Pole | Include | Include | Equipment | 396 | 2021-11-17 | 19800 | keep | 0 | Nov | 2021 | 0.013486 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-11-17 09:06 | 2021-11-17 18:20 | 45 | 009:14 | P | DESGANCHE | 1 X 65 EN C/L | C21111700041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 554 | 2021-11-17 | 24930 | keep | 0 | Nov | 2021 | 0.01698 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2021-11-17 09:07 | 2021-11-17 13:32 | 24 | 004:25 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZARON DISCOS ROTOS Y MACHETE DE 900 AMP QUEMADO | A21111700021 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 265 | 2021-11-17 | 6360 | keep | 0 | Nov | 2021 | 0.0043318 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2021-11-17 09:15 | 2021-11-17 09:52 | 12 | 000:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | B21111700024 | New_Event | Wire Down | Include | Include | Equipment | 37 | 2021-11-17 | 444 | keep | 0 | Nov | 2021 | 0.00030241 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2021-11-17 09:16 | 2021-11-17 10:54 | 20 | 001:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA FUERTES VIENTOS | P21111700061 | New_Event | Bad Weather | Include | Include | Weather | 98 | 2021-11-17 | 1960 | keep | 0 | Nov | 2021 | 0.0013349 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2021-11-17 09:18 | 2021-11-18 11:18 | 1 | 025:60 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 15 KVA X 15KVA | M21111700084 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1560 | 2021-11-17 | 1560 | keep | 0 | Nov | 2021 | 0.0010625 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-17 09:24 | 2021-11-17 09:25 | 790 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-04 LLEVANDO PARTE 1303-02 40% 1204-04 Y 60% 1204-03 | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 790 | keep | 0 | Nov | 2021 | 0.00053807 | 0.00053807 | Momentary | FALSE | FALSE | Not_TMED_Event | 790
SAN JUAN | 2021-11-17 09:24 | 2021-11-17 09:25 | 1900 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-04 LLEVANDO PARTE 1303-02 40% 1204-04 Y 60% 1204-03 | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 1900 | keep | 0 | Nov | 2021 | 0.0012941 | 0.0012941 | Momentary | FALSE | FALSE | Not_TMED_Event | 1900
SAN JUAN | 2021-11-17 09:24 | 2021-11-17 09:25 | 1799 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-04 LLEVANDO PARTE 1303-02 40% 1204-04 Y 60% 1204-03 | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 1799 | keep | 0 | Nov | 2021 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2021-11-17 09:24 | 2021-11-17 09:25 | 300 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-04 LLEVANDO PARTE 1303-02 40% 1204-04 Y 60% 1204-03 | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 300 | keep | 0 | Nov | 2021 | 0.00020433 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
AGUADILLA | 2021-11-17 09:32 | 2021-11-17 17:20 | 50 | 007:48 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA DESGANCHE MASIVO | M21111700071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 468 | 2021-11-17 | 23400 | keep | 0 | Nov | 2021 | 0.015938 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-11-17 09:49 | 2021-11-17 09:50 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR HIZO 2 OPERACIONES Y QUEDO EN SERVICIO | P21111700039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 2113 | keep | 0 | Nov | 2021 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
CAGUAS | 2021-11-17 09:50 | 2021-11-17 15:23 | 90 | 005:33 | P | PARARRAYOS DEFECTUOSO | 3 X 40 EN C/L REEMPLAZO 3 PARARRAYOS | C21111700051 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 333 | 2021-11-17 | 29970 | keep | 0 | Nov | 2021 | 0.020412 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
HUMACAO | 2021-11-17 09:54 | 2021-11-17 09:55 | 2450 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO | C21111700056 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-11-17 | 2450 | keep | 0 | Nov | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2021-11-17 09:55 | 2021-11-17 16:57 | 100 | 007:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L REEMPLAZO CAJA QUEMADA | C21111700117 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 422 | 2021-11-17 | 42200 | keep | 0 | Nov | 2021 | 0.028742 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2021-11-17 10:07 | 2021-11-17 16:40 | 300 | 006:33 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M21111700095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 393 | 2021-11-17 | 117900 | keep | 0 | Nov | 2021 | 0.080301 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2021-11-17 10:12 | 2021-11-17 10:16 | 1066 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR CONTROL | S21111700048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-11-17 | 4264 | keep | 0 | Nov | 2021 | 0.0029042 | 0.00072605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1066
MAYAGÃœEZ | 2021-11-17 10:12 | 2021-11-17 13:10 | 70 | 002:58 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M21111700097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2021-11-17 | 12460 | keep | 0 | Nov | 2021 | 0.0084864 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2021-11-17 10:15 | 2021-11-17 14:24 | 10 | 004:09 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21111700030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 249 | 2021-11-17 | 2490 | keep | 0 | Nov | 2021 | 0.0016959 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-17 10:17 | 2021-11-17 11:15 | 10 | 000:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21111600103 | New_Event | Secondary Wire Down | Include | Include | Equipment | 58 | 2021-11-17 | 580 | keep | 0 | Nov | 2021 | 0.00039504 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-11-17 10:26 | 2021-11-17 19:20 | 150 | 008:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M21111700100 | New_Event | Wire Down | Include | Include | Equipment | 534 | 2021-11-17 | 80100 | keep | 0 | Nov | 2021 | 0.054556 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2021-11-17 10:27 | 2021-11-17 11:52 | 3200 | 001:25 | P | PARARRAYOS DEFECTUOSO | SECCIONALIZO PARARRAYO Y BAJANTE AVERIADO | C21111700091 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 85 | 2021-11-17 | 272000 | keep | 0 | Nov | 2021 | 0.18526 | 0.0021795 | Sustained | FALSE | FALSE | Not_TMED_Event | 3200
MAYAGÃœEZ | 2021-11-17 10:35 | 2021-11-17 11:35 | 50 | 001:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN CONVERTIDOR POR LINEA CRUZADA | M21111700019 | New_Event | Wire Down | Include | Include | Equipment | 60 | 2021-11-17 | 3000 | keep | 0 | Nov | 2021 | 0.0020433 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-17 10:35 | 2021-11-17 17:05 | 200 | 006:30 | P | DESGANCHE | 2 X 200 EN CORTE DE LINEA SE RETIRO ENREDADERA | M21111700005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 390 | 2021-11-17 | 78000 | keep | 0 | Nov | 2021 | 0.053125 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-11-17 10:42 | 2021-11-17 16:00 | 147 | 005:18 | P | NO SE REPORTO CAUSA | 1 X 100, 1 X 80, Y 1 X 65 EN VARIOS CORTE DE LINEA | S21111700052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 318 | 2021-11-17 | 46746 | keep | 0 | Nov | 2021 | 0.031838 | 0.00010012 | Sustained | FALSE | FALSE | Not_TMED_Event | 147
MAYAGÃœEZ | 2021-11-17 10:54 | 2021-11-17 10:55 | 1889 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 1889 | keep | 0 | Nov | 2021 | 0.0012866 | 0.0012866 | Momentary | FALSE | FALSE | Not_TMED_Event | 1889
YAUCO | 2021-11-17 10:55 | 2021-11-17 11:50 | 1 | 000:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR POR FUERTES LLUVIAS | P21111700046 | New_Event | Bad Weather | Include | Include | Weather | 55 | 2021-11-17 | 55 | keep | 0 | Nov | 2021 | 3.746e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-11-17 11:01 | 2021-11-17 11:02 | 2163 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 18000 | P21111700051 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-17 | 2163 | keep | 0 | Nov | 2021 | 0.0014732 | 0.0014732 | Momentary | FALSE | FALSE | Not_TMED_Event | 2163
PONCE | 2021-11-17 11:01 | 2021-11-17 11:02 | 1340 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 18000 | P21111700051 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-17 | 1340 | keep | 0 | Nov | 2021 | 0.00091267 | 0.00091267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1340
PONCE | 2021-11-17 11:01 | 2021-11-17 11:02 | 2039 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 18000 | P21111700051 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-17 | 2039 | keep | 0 | Nov | 2021 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
PONCE | 2021-11-17 11:01 | 2021-11-17 11:02 | 485 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 18000 | P21111700053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-17 | 485 | keep | 0 | Nov | 2021 | 0.00033033 | 0.00033033 | Momentary | FALSE | FALSE | Not_TMED_Event | 485
PONCE | 2021-11-17 11:01 | 2021-11-17 11:02 | 732 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 18000 | P21111700053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-17 | 732 | keep | 0 | Nov | 2021 | 0.00049856 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
MAYAGÃœEZ | 2021-11-17 11:03 | 2021-11-17 12:45 | 20 | 001:42 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21111700114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2021-11-17 | 2040 | keep | 0 | Nov | 2021 | 0.0013894 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2021-11-17 11:09 | 2021-11-17 19:23 | 150 | 008:14 | P | DESGANCHE | 2 X 80 EN C/L | C21111700119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 494 | 2021-11-17 | 74100 | keep | 0 | Nov | 2021 | 0.050469 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2021-11-17 11:10 | 2021-11-17 17:30 | 150 | 006:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 80 EN CORTE DE LINEA VEHICULO IMPACTA TENSOR DE POSTE PRIMARIO | P21111700054 | New_Event |  |  | Include | Wildlife | 380 | 2021-11-17 | 57000 | keep | 0 | Nov | 2021 | 0.038822 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-11-17 11:11 | 2021-11-17 11:12 | 528 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36700 | M21111700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-17 | 528 | keep | 0 | Nov | 2021 | 0.00035962 | 0.00035962 | Momentary | FALSE | FALSE | Not_TMED_Event | 528
MAYAGÃœEZ | 2021-11-17 11:11 | 2021-11-17 11:12 | 4664 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36700 | M21111700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-17 | 4664 | keep | 0 | Nov | 2021 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
MAYAGÃœEZ | 2021-11-17 11:11 | 2021-11-17 11:12 | 2067 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36700 | M21111700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-17 | 2067 | keep | 0 | Nov | 2021 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
MAYAGÃœEZ | 2021-11-17 11:11 | 2021-11-17 11:12 | 1352 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36700 | M21111700000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-17 | 1352 | keep | 0 | Nov | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
VEGA BAJA | 2021-11-17 11:19 | 2021-11-17 12:26 | 6 | 001:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | B21111700034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 67 | 2021-11-17 | 402 | keep | 0 | Nov | 2021 | 0.0002738 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-11-17 11:22 | 2021-11-17 16:47 | 50 | 005:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE EN CORTE DE LINEA | A21111700051 | New_Event | Wire Down | Include | Include | Equipment | 325 | 2021-11-17 | 16250 | keep | 0 | Nov | 2021 | 0.011068 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-17 11:25 | 2021-11-17 20:42 | 2800 | 009:17 | P | ESTRUCTURA AVERIADA | SE SECCIONALIZO ALIMENTADOR PARA REMPLAZO DE POSTE PRIMARIO | B21111700083 | New_Event | Defective Pole | Include | Include | Equipment | 557 | 2021-11-17 | 1559600 | keep | 0 | Nov | 2021 | 1.0622 | 0.0019071 | Sustained | FALSE | FALSE | Not_TMED_Event | 2800
YAUCO | 2021-11-17 11:26 | 2021-11-17 14:15 | 100 | 002:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA FUERTES VIENTOS | P21111700064 | New_Event | Bad Weather | Include | Include | Weather | 169 | 2021-11-17 | 16900 | keep | 0 | Nov | 2021 | 0.011511 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2021-11-17 11:37 | 2021-11-17 14:34 | 1284 | 002:57 | T | DESGANCHE | SE REALIZO DESGANCHE | B21111700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2021-11-17 | 227268 | keep | 0 | Nov | 2021 | 0.15479 | 0.00087453 | Sustained | FALSE | FALSE | Not_TMED_Event | 1284
CAGUAS | 2021-11-17 11:41 | 2021-11-17 15:23 | 40 | 003:42 | P | ESTRUCTURA AVERIADA | 1 X 40 EN C/L SECCIONALIZO 2 POSTES PARTIDOS | C21111700137 | New_Event | Defective Pole | Include | Include | Equipment | 222 | 2021-11-17 | 8880 | keep | 0 | Nov | 2021 | 0.0060481 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2021-11-17 11:52 | 2021-11-17 12:38 | 585 | 000:46 | P | PARARRAYOS DEFECTUOSO | REEMPLAZO PARARRAYO Y BAJANTE | C21111700091 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 46 | 2021-11-17 | 26910 | keep | 0 | Nov | 2021 | 0.018328 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-11-17 12:02 | 2021-11-17 15:48 | 1 | 003:46 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN RISER POR RAYO | M21111700137 | New_Event | Bad Weather | Include | Include | Weather | 226 | 2021-11-17 | 226 | keep | 0 | Nov | 2021 | 0.00015393 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-11-17 12:05 | 2021-11-17 15:02 | 100 | 002:57 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO DISCO | R21111700032 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 177 | 2021-11-17 | 17700 | keep | 0 | Nov | 2021 | 0.012055 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-11-17 12:09 | 2021-11-17 12:48 | 4000 | 000:39 | P | DESGANCHE | DISPARO DE INTERRUPTOR CON 80% DE SU CARGA POR PORTATIL 22 SE ABRIO MACHETE CARR.844 ESQ. 843 RETIRAR ARBOL SOBRE LINEA | S21111700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 39 | 2021-11-17 | 156000 | keep | 0 | Nov | 2021 | 0.10625 | 0.0027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 4000
BAYAMON | 2021-11-17 12:13 | 2021-11-17 12:14 | 643 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 643 | keep | 0 | Nov | 2021 | 0.00043794 | 0.00043794 | Momentary | FALSE | FALSE | Not_TMED_Event | 643
CANOVANAS | 2021-11-17 12:14 | 2021-11-17 15:26 | 3 | 003:12 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN TRANSFORMADOR | R21111700033 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 192 | 2021-11-17 | 576 | keep | 0 | Nov | 2021 | 0.00039231 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-11-17 12:15 | 2021-11-17 15:18 | 10 | 003:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | S21111700058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 183 | 2021-11-17 | 1830 | keep | 0 | Nov | 2021 | 0.0012464 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-11-17 12:28 | 2021-11-17 15:00 | 60 | 002:32 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 Y 1 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B21111700060 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 152 | 2021-11-17 | 9120 | keep | 0 | Nov | 2021 | 0.0062116 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2021-11-17 12:31 | 2021-11-17 18:38 | 6 | 006:07 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE | C21111700150 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 367 | 2021-11-17 | 2202 | keep | 0 | Nov | 2021 | 0.0014998 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2021-11-17 12:34 | 2021-11-17 13:52 | 10 | 001:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR NEUTRAL SECUNDARIO | P21111700080 | New_Event | Secondary Wire Down | Include | Include | Equipment | 78 | 2021-11-17 | 780 | keep | 0 | Nov | 2021 | 0.00053125 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-11-17 12:36 | 2021-11-17 12:48 | 1 | 000:12 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO SE REPORTA CAUSA | P21111700081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 12 | 2021-11-17 | 12 | keep | 0 | Nov | 2021 | 8.1731e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-11-17 12:40 | 2021-11-17 12:41 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21111700167 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 2203 | keep | 0 | Nov | 2021 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
ARECIBO | 2021-11-17 12:47 | 2021-11-17 15:20 | 20 | 002:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A21111700062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2021-11-17 | 3060 | keep | 0 | Nov | 2021 | 0.0020842 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-11-17 12:48 | 2021-11-17 14:16 | 4000 | 001:28 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETE CARR.844 ESQ. 843 SU CARGA A TRAVES PORTATIL 22 | S21111700000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 88 | 2021-11-17 | 352000 | keep | 0 | Nov | 2021 | 0.23975 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-17 12:54 | 2021-11-17 12:55 | 500 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1118-10 LLEVANDO 20% CARGA 1111-01 | S21111700058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 500 | keep | 0 | Nov | 2021 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2021-11-17 12:54 | 2021-11-17 12:55 | 2782 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1118-10 LLEVANDO 20% CARGA 1111-01 | S21111700058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 2782 | keep | 0 | Nov | 2021 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
MAYAGÃœEZ | 2021-11-17 12:55 | 2021-11-17 16:37 | 20 | 003:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21111700151 | New_Event | Bad Weather | Include | Include | Weather | 222 | 2021-11-17 | 4440 | keep | 0 | Nov | 2021 | 0.0030241 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-11-17 12:55 | 2021-11-17 17:45 | 50 | 004:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO TIERRA DE POSTE ZAFADA CRUZANDO CON FASE | M21111700163 | New_Event | Wire Down | Include | Include | Equipment | 290 | 2021-11-17 | 14500 | keep | 0 | Nov | 2021 | 0.0098759 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-17 13:04 | 2021-11-17 13:05 | 1420 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1530-06 LLEVA CARGA DE 1526-02 | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 1420 | keep | 0 | Nov | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-11-17 13:04 | 2021-11-17 13:05 | 437 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1530-06 LLEVA CARGA DE 1526-02 | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 437 | keep | 0 | Nov | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
CAGUAS | 2021-11-17 13:17 | 2021-11-18 15:33 | 22 | 026:16 | P | CABLE SOTERRADO AVERIADO | CONSTRUYO AEREO PROVICIONAL DEL T12 AL T11 | C21111700158 | New_Event | UG Cable Fault | Include | Include | Equipment | 1576 | 2021-11-17 | 34672 | keep | 0 | Nov | 2021 | 0.023615 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
CAGUAS | 2021-11-17 13:17 | 2021-11-17 17:41 | 40 | 004:24 | P | CABLE SOTERRADO AVERIADO | REEMPLAZO ELBOW CONECTOR EN EL T13 AVERIA DEL T-9 AL T10 | C21111700158 | New_Event | UG Cable Fault | Include | Include | Equipment | 264 | 2021-11-17 | 10560 | keep | 0 | Nov | 2021 | 0.0071924 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2021-11-17 13:18 | 2021-11-17 19:39 | 100 | 006:21 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M21111700173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 381 | 2021-11-17 | 38100 | keep | 0 | Nov | 2021 | 0.02595 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-11-17 13:19 | 2021-11-17 13:20 | 643 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21111700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 643 | keep | 0 | Nov | 2021 | 0.00043794 | 0.00043794 | Momentary | FALSE | FALSE | Not_TMED_Event | 643
HUMACAO | 2021-11-17 13:20 | 2021-11-17 13:21 | 551 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21111700161 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 551 | keep | 0 | Nov | 2021 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
CAGUAS | 2021-11-17 13:20 | 2021-11-17 17:11 | 90 | 003:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN C/L CRUCE POR AVE | C21111700159 | New_Event |  |  | Include | Wildlife | 231 | 2021-11-17 | 20790 | keep | 0 | Nov | 2021 | 0.01416 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
HUMACAO | 2021-11-17 13:21 | 2021-11-17 14:40 | 50 | 001:19 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | C21111700163 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 79 | 2021-11-17 | 3950 | keep | 0 | Nov | 2021 | 0.0026903 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-11-17 13:22 | 2021-11-17 16:12 | 4 | 002:50 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21111700038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2021-11-17 | 680 | keep | 0 | Nov | 2021 | 0.00046314 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-11-17 13:26 | 2021-11-17 15:44 | 3 | 002:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | R21111700039 | New_Event | Bad Weather | Include | Include | Weather | 138 | 2021-11-17 | 414 | keep | 0 | Nov | 2021 | 0.00028197 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-11-17 13:26 | 2021-11-17 17:30 | 100 | 004:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA FUERTE VIENTO | M21111700179 | New_Event | Bad Weather | Include | Include | Weather | 244 | 2021-11-17 | 24400 | keep | 0 | Nov | 2021 | 0.016619 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-11-17 13:37 | 2021-11-17 13:38 | 3902 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21111700171 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 3902 | keep | 0 | Nov | 2021 | 0.0026576 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
UTUADO | 2021-11-17 13:37 | 2021-11-17 18:24 | 60 | 004:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | A21111700066 | New_Event | Bad Weather | Include | Include | Weather | 287 | 2021-11-17 | 17220 | keep | 0 | Nov | 2021 | 0.011728 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-11-17 13:44 | 2021-11-17 18:41 | 50 | 004:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21111700080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 297 | 2021-11-17 | 14850 | keep | 0 | Nov | 2021 | 0.010114 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-17 13:44 | 2021-11-17 17:21 | 1 | 003:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | B21111700097 | New_Event | Wire Down | Include | Include | Equipment | 217 | 2021-11-17 | 217 | keep | 0 | Nov | 2021 | 0.0001478 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-11-17 13:47 | 2021-11-17 17:56 | 200 | 004:09 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21111700189 | New_Event | Vegetation Contact | Include | Include | Vegetation | 249 | 2021-11-17 | 49800 | keep | 0 | Nov | 2021 | 0.033919 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-11-17 13:58 | 2021-11-17 14:00 | 225 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1303-05 | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-17 | 450 | keep | 0 | Nov | 2021 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-11-17 13:58 | 2021-11-17 14:00 | 870 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA EL 1303-04 | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-17 | 1740 | keep | 0 | Nov | 2021 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
MAYAGÃœEZ | 2021-11-17 14:00 | 2021-11-17 20:19 | 35 | 006:19 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M21111700197 | New_Event | Vegetation Contact | Include | Include | Vegetation | 379 | 2021-11-17 | 13265 | keep | 0 | Nov | 2021 | 0.0090347 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2021-11-17 14:05 | 2021-11-17 15:39 | 1 | 001:34 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR MAL TIEMPO FUERTES VIENTOS | A21111700070 | New_Event | Bad Weather | Include | Include | Weather | 94 | 2021-11-17 | 94 | keep | 0 | Nov | 2021 | 6.4023e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-11-17 14:06 | 2021-11-17 16:21 | 5 | 002:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR REEMPLAZO PORTAFUSIBLE | C21111700175 | New_Event | Cutout Failure | Include | Include | Equipment | 135 | 2021-11-17 | 675 | keep | 0 | Nov | 2021 | 0.00045974 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2021-11-17 14:08 | 2021-11-17 16:53 | 40 | 002:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | A21111700071 | New_Event | Bad Weather | Include | Include | Weather | 165 | 2021-11-17 | 6600 | keep | 0 | Nov | 2021 | 0.0044952 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-11-17 14:15 | 2021-11-17 14:16 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1206-03 | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 10211 | keep | 0 | Nov | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-11-17 14:15 | 2021-11-17 14:16 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA EL 1204-05 | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 4133 | keep | 0 | Nov | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-11-17 14:16 | 2021-11-17 14:58 | 40 | 000:42 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21111700037 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 42 | 2021-11-17 | 1680 | keep | 0 | Nov | 2021 | 0.0011442 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-11-17 14:16 | 2021-11-17 16:36 | 10 | 002:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | R21111700044 | New_Event | Cutout Failure | Include | Include | Equipment | 140 | 2021-11-17 | 1400 | keep | 0 | Nov | 2021 | 0.00095353 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-17 14:30 | 2021-11-17 14:31 | 1420 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1530-06 | S21111700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 1420 | keep | 0 | Nov | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-11-17 14:30 | 2021-11-17 14:31 | 437 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA EL 1526-02 | S21111700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 437 | keep | 0 | Nov | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2021-11-17 14:33 | 2021-11-17 15:39 | 15 | 001:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21111700082 | New_Event | Secondary Wire Down | Include | Include | Equipment | 66 | 2021-11-17 | 990 | keep | 0 | Nov | 2021 | 0.00067428 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-11-17 14:36 | 2021-11-17 22:59 | 8 | 008:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR EXCAVADORA CRUZO FASES | M21111700213 | New_Event |  |  | Include | Wildlife | 503 | 2021-11-17 | 4024 | keep | 0 | Nov | 2021 | 0.0027407 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-11-17 14:43 | 2021-11-17 19:19 | 110 | 004:36 | P | DESGANCHE | 2 X 65 EN C/L | C21111700183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 276 | 2021-11-17 | 30360 | keep | 0 | Nov | 2021 | 0.020678 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
FAJARDO | 2021-11-17 14:52 | 2021-11-17 16:11 | 8 | 001:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA DE TRANSFORMADOR | R21111700046 | New_Event | Cutout Failure | Include | Include | Equipment | 79 | 2021-11-17 | 632 | keep | 0 | Nov | 2021 | 0.00043045 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2021-11-17 14:55 | 2021-11-17 18:05 | 80 | 003:10 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21111700105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2021-11-17 | 15200 | keep | 0 | Nov | 2021 | 0.010353 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-11-17 15:00 | 2021-11-17 15:01 | 1420 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1530-06 | S21111700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 1420 | keep | 0 | Nov | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-11-17 15:00 | 2021-11-17 15:01 | 437 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 1526-02 | S21111700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 437 | keep | 0 | Nov | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
ARECIBO | 2021-11-17 15:02 | 2021-11-17 15:03 | 5042 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | A21111700077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 5042 | keep | 0 | Nov | 2021 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
GUAYAMA | 2021-11-17 15:07 | 2021-11-17 16:30 | 10 | 001:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR LINEA SECUNDARIA | P21111700108 | New_Event | Secondary Wire Down | Include | Include | Equipment | 83 | 2021-11-17 | 830 | keep | 0 | Nov | 2021 | 0.00056531 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-11-17 15:08 | 2021-11-17 20:56 | 90 | 005:48 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21111700109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 348 | 2021-11-17 | 31320 | keep | 0 | Nov | 2021 | 0.021332 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2021-11-17 15:11 | 2021-11-17 17:21 | 120 | 002:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | R21111700048 | New_Event |  |  | Include | Wildlife | 130 | 2021-11-17 | 15600 | keep | 0 | Nov | 2021 | 0.010625 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2021-11-17 15:12 | 2021-11-17 15:13 | 150 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 30% POR EL 1529-15 | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 150 | keep | 0 | Nov | 2021 | 0.00010216 | 0.00010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2021-11-17 15:12 | 2021-11-17 15:13 | 1802 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA EL 30% DEL 1346-02 | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 1802 | keep | 0 | Nov | 2021 | 0.0012273 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
SAN JUAN | 2021-11-17 15:14 | 2021-11-17 15:15 | 225 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR EL 1303-05 | S21111700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 225 | keep | 0 | Nov | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-11-17 15:14 | 2021-11-17 15:15 | 870 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA EL 1303-04 | S21111700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 870 | keep | 0 | Nov | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
YAUCO | 2021-11-17 15:15 | 2021-11-17 17:19 | 50 | 002:04 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21111700110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2021-11-17 | 6200 | keep | 0 | Nov | 2021 | 0.0042228 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-17 15:17 | 2021-11-17 16:53 | 1 | 001:36 | P | NO SE REPORTO CAUSA | 1 X 15 EN BANCO DE TRANSFORMADORES | B21111700094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2021-11-17 | 96 | keep | 0 | Nov | 2021 | 6.5385e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-11-17 15:21 | 2021-11-17 17:11 | 23 | 001:50 | T | DESGANCHE | DISPARO INTERRUPTOR CRUCE DE FASE EN TRONCAL PRIMARIO POR RAMA | P21111700112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2021-11-17 | 2530 | keep | 0 | Nov | 2021 | 0.0017232 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
CAGUAS | 2021-11-17 15:23 | 2021-11-17 21:48 | 20 | 006:25 | P | ESTRUCTURA AVERIADA | 1 X 40 EN C/L Y 1 X 20 EN XMR REEMPLAZO POSTES PARTIDOS | C21111700137 | Partial_restoration | Defective Pole | Include | Include | Equipment | 385 | 2021-11-17 | 7700 | keep | 0 | Nov | 2021 | 0.0052444 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-11-17 15:28 | 2021-11-17 16:33 | 6 | 001:05 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO CAUSA | C21111700195 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 65 | 2021-11-17 | 390 | keep | 0 | Nov | 2021 | 0.00026563 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-11-17 15:45 | 2021-11-17 16:29 | 1 | 000:44 | P | PARARRAYOS DEFECTUOSO | FIJO BAJANTE DE LINEA A CAJA Y REEMPLAZO PARARRAYO | C21111700198 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 44 | 2021-11-17 | 44 | keep | 0 | Nov | 2021 | 2.9968e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-11-17 15:47 | 2021-11-17 17:34 | 1 | 001:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 25 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA | M21111700246 | New_Event | Secondary Wire Down | Include | Include | Equipment | 107 | 2021-11-17 | 107 | keep | 0 | Nov | 2021 | 7.2877e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-17 16:02 | 2021-11-17 16:50 | 627 | 000:48 | S | LINEA DE TRANSMISION 38KV | DISPARO L-8900 | S21111700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2021-11-17 | 30096 | keep | 0 | Nov | 2021 | 0.020498 | 0.00042705 | Sustained | FALSE | FALSE | Not_TMED_Event | 627
SAN JUAN | 2021-11-17 16:02 | 2021-11-17 16:50 | 293 | 000:48 | S | LINEA DE TRANSMISION 38KV | DISPARO L-8900 LLEVA 1421-5 | S21111700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2021-11-17 | 14064 | keep | 0 | Nov | 2021 | 0.0095789 | 0.00019956 | Sustained | FALSE | FALSE | Not_TMED_Event | 293
SAN JUAN | 2021-11-17 16:02 | 2021-11-17 16:50 | 761 | 000:48 | S | LINEA DE TRANSMISION 38KV | DISPARO L-8900 LLEVA 1421-1 | S21111700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2021-11-17 | 36528 | keep | 0 | Nov | 2021 | 0.024879 | 0.00051831 | Sustained | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2021-11-17 16:02 | 2021-11-17 16:50 | 451 | 000:48 | S | LINEA DE TRANSMISION 38KV | DISPARO L-8900 | S21111700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2021-11-17 | 21648 | keep | 0 | Nov | 2021 | 0.014744 | 0.00030717 | Sustained | FALSE | FALSE | Not_TMED_Event | 451
SAN JUAN | 2021-11-17 16:02 | 2021-11-17 16:50 | 761 | 000:48 | T | LINEA DE TRANSMISION 38KV | DISPARO L-8900 SU CARGA POR 1310-4 | S21111700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2021-11-17 | 36528 | keep | 0 | Nov | 2021 | 0.024879 | 0.00051831 | Sustained | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2021-11-17 16:02 | 2021-11-17 16:50 | 766 | 000:48 | T | LINEA DE TRANSMISION 38KV | DISPARO L-8900 SU CARGA POR 1310-03 | S21111700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2021-11-17 | 36768 | keep | 0 | Nov | 2021 | 0.025043 | 0.00052172 | Sustained | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2021-11-17 16:04 | 2021-11-17 16:05 | 1420 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1530-6 | S21111700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 1420 | keep | 0 | Nov | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-11-17 16:04 | 2021-11-17 16:05 | 437 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1526-2 | S21111700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 437 | keep | 0 | Nov | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
AGUADILLA | 2021-11-17 16:08 | 2021-11-17 19:50 | 60 | 003:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | M21111700267 | New_Event | Wire Down | Include | Include | Equipment | 222 | 2021-11-17 | 13320 | keep | 0 | Nov | 2021 | 0.0090722 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2021-11-17 16:10 | 2021-11-17 16:36 | 60 | 000:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO FUERTES VIENTOS | A21111700084 | New_Event | Bad Weather | Include | Include | Weather | 26 | 2021-11-17 | 1560 | keep | 0 | Nov | 2021 | 0.0010625 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2021-11-17 16:13 | 2021-11-17 16:22 | 20 | 000:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA FUERTES VIENTOS | P21111700061 | New_Event | Bad Weather | Include | Include | Weather | 9 | 2021-11-17 | 180 | keep | 0 | Nov | 2021 | 0.0001226 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-11-17 16:18 | 2021-11-17 21:08 | 810 | 004:50 | S | LINEA DE TRANSMISION 38KV | SE LE RETIRO LA CARGA A LA SUBESTACION POR PUENTE ABIERTO EN LA LINEA 5600 SE TRANSFIRIO LA CARGA A LA LINEA 9200 | M21111700225 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 290 | 2021-11-17 | 234900 | keep | 0 | Nov | 2021 | 0.15999 | 0.00055169 | Sustained | FALSE | FALSE | Not_TMED_Event | 810
MAYAGÃœEZ | 2021-11-17 16:18 | 2021-11-17 21:08 | 1235 | 004:50 | S | LINEA DE TRANSMISION 38KV | SE LE RETIRO LA CARGA A LA SUBESTACION POR PUENTE ABIERTO EN LA LINEA 5600 SE TRANSFIRIO LA CARGA A LA LINEA 9200 | M21111700225 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 290 | 2021-11-17 | 358150 | keep | 0 | Nov | 2021 | 0.24393 | 0.00084115 | Sustained | FALSE | FALSE | Not_TMED_Event | 1235
MAYAGÃœEZ | 2021-11-17 16:18 | 2021-11-17 21:08 | 93 | 004:50 | S | LINEA DE TRANSMISION 38KV | SE LE RETIRO LA CARGA A LA SUBESTACION POR PUENTE ABIERTO EN LA LINEA 5600 SE TRANSFIRIO LA CARGA A LA LINEA 9200 | M21111700225 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 290 | 2021-11-17 | 26970 | keep | 0 | Nov | 2021 | 0.018369 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
MAYAGÃœEZ | 2021-11-17 16:18 | 2021-11-17 21:08 | 1825 | 004:50 | S | LINEA DE TRANSMISION 38KV | SE LE RETIRO LA CARGA A LA SUBESTACION POR PUENTE ABIERTO EN LA LINEA 5600 SE TRANSFIRIO LA CARGA A LA LINEA 9200 | M21111700225 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 290 | 2021-11-17 | 529250 | keep | 0 | Nov | 2021 | 0.36047 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
MAYAGÃœEZ | 2021-11-17 16:18 | 2021-11-17 21:08 | 3230 | 004:50 | S | LINEA DE TRANSMISION 38KV | SE LE RETIRO LA CARGA A LA SUBESTACION POR PUENTE ABIERTO EN LA LINEA 5600 SE TRANSFIRIO LA CARGA A LA LINEA 9200 | M21111700225 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 290 | 2021-11-17 | 936700 | keep | 0 | Nov | 2021 | 0.63798 | 0.0021999 | Sustained | FALSE | FALSE | Not_TMED_Event | 3230
YAUCO | 2021-11-17 16:29 | 2021-11-17 17:17 | 65 | 000:48 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE REPORTO CAUSA | P21111700122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 48 | 2021-11-17 | 3120 | keep | 0 | Nov | 2021 | 0.002125 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2021-11-17 16:37 | 2021-11-17 16:38 | 888 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M21111700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-17 | 888 | keep | 0 | Nov | 2021 | 0.00060481 | 0.00060481 | Momentary | FALSE | FALSE | Not_TMED_Event | 888
MAYAGÃœEZ | 2021-11-17 16:37 | 2021-11-17 16:38 | 393 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M21111700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-17 | 393 | keep | 0 | Nov | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2021-11-17 16:37 | 2021-11-17 16:38 | 4 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M21111700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-17 | 4 | keep | 0 | Nov | 2021 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-11-17 16:37 | 2021-11-17 16:38 | 372 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M21111700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-17 | 372 | keep | 0 | Nov | 2021 | 0.00025337 | 0.00025337 | Momentary | FALSE | FALSE | Not_TMED_Event | 372
MAYAGÃœEZ | 2021-11-17 16:37 | 2021-11-17 16:38 | 2530 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M21111700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-17 | 2530 | keep | 0 | Nov | 2021 | 0.0017232 | 0.0017232 | Momentary | FALSE | FALSE | Not_TMED_Event | 2530
MAYAGÃœEZ | 2021-11-17 16:37 | 2021-11-17 16:38 | 199 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M21111700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-17 | 199 | keep | 0 | Nov | 2021 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
MAYAGÃœEZ | 2021-11-17 16:37 | 2021-11-17 16:38 | 312 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M21111700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-17 | 312 | keep | 0 | Nov | 2021 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
MAYAGÃœEZ | 2021-11-17 16:37 | 2021-11-17 16:38 | 4641 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M21111700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-17 | 4641 | keep | 0 | Nov | 2021 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2021-11-17 16:38 | 2021-11-17 17:37 | 20 | 000:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21111700151 | Partial_restoration | Bad Weather | Include | Include | Weather | 59 | 2021-11-17 | 1180 | keep | 0 | Nov | 2021 | 0.00080369 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-11-17 16:49 | 2021-11-17 22:55 | 40 | 006:06 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEAS | A21111700086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 366 | 2021-11-17 | 14640 | keep | 0 | Nov | 2021 | 0.0099712 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-11-17 17:08 | 2021-11-17 21:23 | 12 | 004:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE EN TRANSFORMADOR | A21111700089 | New_Event | Wire Down | Include | Include | Equipment | 255 | 2021-11-17 | 3060 | keep | 0 | Nov | 2021 | 0.0020842 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-11-17 17:10 | 2021-11-17 17:11 | 817 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21111700051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 817 | keep | 0 | Nov | 2021 | 0.00055645 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
CANOVANAS | 2021-11-17 17:14 | 2021-11-17 21:16 | 100 | 004:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21111700052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2021-11-17 | 24200 | keep | 0 | Nov | 2021 | 0.016483 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2021-11-17 17:17 | 2021-11-17 20:54 | 50 | 003:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21111700126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2021-11-17 | 10850 | keep | 0 | Nov | 2021 | 0.0073899 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-11-17 17:19 | 2021-11-17 17:28 | 50 | 000:09 | P | NO SE REPORTO CAUSA | 3 X 50 EN CORTE DE LINEA | S21111700061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2021-11-17 | 450 | keep | 0 | Nov | 2021 | 0.00030649 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-11-17 17:21 | 2021-11-17 21:20 | 10 | 003:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21111700109 | New_Event | Secondary Wire Down | Include | Include | Equipment | 239 | 2021-11-17 | 2390 | keep | 0 | Nov | 2021 | 0.0016278 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-17 17:34 | 2021-11-17 17:35 | 5042 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | A21111700091 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 5042 | keep | 0 | Nov | 2021 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
ARECIBO | 2021-11-17 17:36 | 2021-11-17 17:37 | 5042 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | A21111700092 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 5042 | keep | 0 | Nov | 2021 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
BAYAMON | 2021-11-17 18:15 | 2021-11-17 19:50 | 10 | 001:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21111700044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 95 | 2021-11-17 | 950 | keep | 0 | Nov | 2021 | 0.00064704 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-11-17 18:20 | 2021-11-17 19:52 | 40 | 001:32 | P | DESGANCHE | 1 X 50 EN C/L | C21111700222 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2021-11-17 | 3680 | keep | 0 | Nov | 2021 | 0.0025064 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2021-11-17 18:23 | 2021-11-18 10:28 | 90 | 016:05 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN C/L MAL TIEMPO | C21111700225 | New_Event | Bad Weather | Include | Include | Weather | 965 | 2021-11-17 | 86850 | keep | 0 | Nov | 2021 | 0.059153 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2021-11-17 18:30 | 2021-11-17 18:31 | 2174 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 2174 | keep | 0 | Nov | 2021 | 0.0014807 | 0.0014807 | Momentary | FALSE | FALSE | Not_TMED_Event | 2174
AGUADILLA | 2021-11-17 18:33 | 2021-11-17 18:34 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21111700328 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 3041 | keep | 0 | Nov | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2021-11-17 18:36 | 2021-11-17 18:37 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21111700330 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 3041 | keep | 0 | Nov | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2021-11-17 18:38 | 2021-11-17 18:39 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21111700331 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 3041 | keep | 0 | Nov | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
PONCE | 2021-11-17 18:47 | 2021-11-18 12:08 | 32 | 017:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA BAMBUA SOBRE LINEA | P21111700127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1041 | 2021-11-17 | 33312 | keep | 0 | Nov | 2021 | 0.022689 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
CAGUAS | 2021-11-17 18:49 | 2021-11-18 10:15 | 40 | 015:26 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | C21111700229 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 926 | 2021-11-17 | 37040 | keep | 0 | Nov | 2021 | 0.025228 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-17 18:50 | 2021-11-17 20:39 | 40 | 001:49 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21111700118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2021-11-17 | 4360 | keep | 0 | Nov | 2021 | 0.0029696 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2021-11-17 18:54 | 2021-11-17 20:21 | 5 | 001:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 10 EN XMR REPARO BAJANTE PRIMARIO | C21111700230 | New_Event | Wire Down | Include | Include | Equipment | 87 | 2021-11-17 | 435 | keep | 0 | Nov | 2021 | 0.00029628 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2021-11-17 19:23 | 2021-11-18 12:30 | 4 | 017:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21111700107 | New_Event | Bad Weather | Include | Include | Weather | 1027 | 2021-11-17 | 4108 | keep | 0 | Nov | 2021 | 0.0027979 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2021-11-17 19:29 | 2021-11-17 21:39 | 80 | 002:10 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M21111700340 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2021-11-17 | 10400 | keep | 0 | Nov | 2021 | 0.0070834 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-11-17 19:35 | 2021-11-17 20:24 | 1 | 000:49 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21111700123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 49 | 2021-11-17 | 49 | keep | 0 | Nov | 2021 | 3.3374e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-17 19:41 | 2021-11-18 13:03 | 9 | 017:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 10 EN TRANSFORMADOR REPARO NEUTRAL PRIMARIO CRUZADO CON SECUNDARIA | R21111700055 | New_Event | Wire Down | Include | Include | Equipment | 1042 | 2021-11-17 | 9378 | keep | 0 | Nov | 2021 | 0.0063873 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
FAJARDO | 2021-11-17 19:41 | 2021-11-17 23:17 | 16 | 003:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA PARTIDA | R21111700063 | New_Event | Cutout Failure | Include | Include | Equipment | 216 | 2021-11-17 | 3456 | keep | 0 | Nov | 2021 | 0.0023539 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2021-11-17 19:49 | 2021-11-17 23:25 | 70 | 003:36 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M21111700350 | New_Event | Vegetation Contact | Include | Include | Vegetation | 216 | 2021-11-17 | 15120 | keep | 0 | Nov | 2021 | 0.010298 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
GUAYAMA | 2021-11-17 19:59 | 2021-11-17 22:09 | 25 | 002:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | P21111700130 | New_Event | Wire Down | Include | Include | Equipment | 130 | 2021-11-17 | 3250 | keep | 0 | Nov | 2021 | 0.0022136 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2021-11-17 20:05 | 2021-11-17 22:49 | 177 | 002:44 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | R21111700058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2021-11-17 | 29028 | keep | 0 | Nov | 2021 | 0.019771 | 0.00012055 | Sustained | FALSE | FALSE | Not_TMED_Event | 177
MAYAGÃœEZ | 2021-11-17 20:19 | 2021-11-17 22:00 | 30 | 001:41 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21111700357 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2021-11-17 | 3030 | keep | 0 | Nov | 2021 | 0.0020637 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-11-17 20:44 | 2021-11-17 20:47 | 225 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO CON R/R ON LLEVA 1303-05 | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-17 | 675 | keep | 0 | Nov | 2021 | 0.00045974 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-11-17 20:44 | 2021-11-17 20:47 | 870 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO CON R/R ON LLEVA 1303-04 | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-17 | 2610 | keep | 0 | Nov | 2021 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2021-11-17 20:45 | 2021-11-17 21:50 | 500 | 001:05 | P | DESGANCHE | DISPARO PORTATIL 8 SE RETIRO ARBOL CARGA POR EL 1424-08 | S21111700187 | New_Event | Vegetation Contact | Include | Include | Vegetation | 65 | 2021-11-17 | 32500 | keep | 0 | Nov | 2021 | 0.022136 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2021-11-17 20:45 | 2021-11-17 21:50 | 400 | 001:05 | P | DESGANCHE | DISPARO PORTATIL 8 SE RETIRO ARBOL SOBRE LINEA | S21111700187 | New_Event | Vegetation Contact | Include | Include | Vegetation | 65 | 2021-11-17 | 26000 | keep | 0 | Nov | 2021 | 0.017708 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2021-11-17 20:45 | 2021-11-17 21:50 | 1290 | 001:05 | T | DESGANCHE | SECUNDARIO PORTATIL # 8 SE VERIFICO ARBOL SOBRE LINEA | S21111700187 | New_Event | Vegetation Contact | Include | Include | Vegetation | 65 | 2021-11-17 | 83850 | keep | 0 | Nov | 2021 | 0.05711 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
CAGUAS | 2021-11-17 21:16 | 2021-11-18 09:33 | 40 | 012:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE POR AVE | C21111700260 | New_Event |  |  | Include | Wildlife | 737 | 2021-11-17 | 29480 | keep | 0 | Nov | 2021 | 0.020079 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-11-17 21:34 | 2021-11-17 21:35 | 863 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21111700379 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 863 | keep | 0 | Nov | 2021 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
SAN JUAN | 2021-11-17 21:36 | 2021-11-17 21:39 | 137 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S21111700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-17 | 411 | keep | 0 | Nov | 2021 | 0.00027993 | 9.331e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 137
SAN JUAN | 2021-11-17 21:36 | 2021-11-17 21:39 | 457 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3600 | S21111700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-17 | 1371 | keep | 0 | Nov | 2021 | 0.00093378 | 0.00031126 | Momentary | FALSE | FALSE | Not_TMED_Event | 457
SAN JUAN | 2021-11-17 21:36 | 2021-11-17 21:39 | 1225 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21111700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-17 | 3675 | keep | 0 | Nov | 2021 | 0.002503 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2021-11-17 21:36 | 2021-11-17 21:39 | 1452 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21111700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-17 | 4356 | keep | 0 | Nov | 2021 | 0.0029669 | 0.00098895 | Momentary | FALSE | FALSE | Not_TMED_Event | 1452
SAN JUAN | 2021-11-17 21:36 | 2021-11-17 21:39 | 616 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21111700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-17 | 1848 | keep | 0 | Nov | 2021 | 0.0012587 | 0.00041955 | Momentary | FALSE | FALSE | Not_TMED_Event | 616
SAN JUAN | 2021-11-17 21:36 | 2021-11-17 21:39 | 4000 | 000:03 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21111700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-17 | 12000 | keep | 0 | Nov | 2021 | 0.0081731 | 0.0027244 | Momentary | FALSE | FALSE | Not_TMED_Event | 4000
SAN JUAN | 2021-11-17 21:36 | 2021-11-17 21:39 | 600 | 000:03 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21111700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-17 | 1800 | keep | 0 | Nov | 2021 | 0.001226 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2021-11-17 21:36 | 2021-11-17 21:37 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1206-3 | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 10211 | keep | 0 | Nov | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-11-17 21:36 | 2021-11-17 21:37 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1204-05 | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 4133 | keep | 0 | Nov | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
BARRANQUITAS | 2021-11-17 21:41 | 2021-11-18 04:57 | 2635 | 007:16 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6500 DE BARRANQUITAS A TORO NEGRO SE REEMPLAZO PERNO DE DISCO DE 38 KV Y FUSIBLE DE 38 KV | C21111800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 436 | 2021-11-17 | 1148860 | keep | 0 | Nov | 2021 | 0.78248 | 0.0017947 | Sustained | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2021-11-17 21:41 | 2021-11-18 04:57 | 2280 | 007:16 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6500 DE BARRANQUITAS A TORO NEGRO SE REEMPLAZO PERNO DE DISCO DE 38 KV Y FUSIBLE DE 38 KV | C21111800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 436 | 2021-11-17 | 994080 | keep | 0 | Nov | 2021 | 0.67706 | 0.0015529 | Sustained | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2021-11-17 21:41 | 2021-11-18 04:57 | 1617 | 007:16 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6500 DE BARRANQUITAS A TORO NEGRO SE REEMPLAZO PERNO DE DISCO DE 38 KV Y FUSIBLE DE 38 KV | C21111800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 436 | 2021-11-17 | 705012 | keep | 0 | Nov | 2021 | 0.48018 | 0.0011013 | Sustained | FALSE | FALSE | Not_TMED_Event | 1617
BAYAMON | 2021-11-17 21:43 | 2021-11-17 21:46 | 320 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-17 | 960 | keep | 0 | Nov | 2021 | 0.00065385 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
SAN JUAN | 2021-11-17 21:44 | 2021-11-18 08:54 | 30 | 011:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | S21111700262 | New_Event | Cutout Failure | Include | Include | Equipment | 670 | 2021-11-17 | 20100 | keep | 0 | Nov | 2021 | 0.01369 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-11-17 21:45 | 2021-11-17 22:26 | 718 | 000:41 | T | NO SE REPORTO CAUSA | SE ABRIO MACHETE DE AMARRE CONTRA 1901-05 Y SE CERRO POR SCADA | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 41 | 2021-11-17 | 29438 | keep | 0 | Nov | 2021 | 0.02005 | 0.00048903 | Sustained | FALSE | FALSE | Not_TMED_Event | 718
BAYAMON | 2021-11-17 21:45 | 2021-11-17 22:39 | 520 | 000:54 | P | NO SE REPORTO CAUSA | SE SECCIONALIZO Y SE CERRARON MACHETES DE AMARRE CONTRA EL 1330-01 | S21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 54 | 2021-11-17 | 28080 | keep | 0 | Nov | 2021 | 0.019125 | 0.00035417 | Sustained | FALSE | FALSE | Not_TMED_Event | 520
BAYAMON | 2021-11-17 21:53 | 2021-11-17 21:54 | 2617 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21111700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 2617 | keep | 0 | Nov | 2021 | 0.0017824 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
HUMACAO | 2021-11-17 22:12 | 2021-11-18 18:05 | 400 | 019:53 | P | DESGANCHE | ABRIO C/L PARA REALIZAR DESGANCHE | C21111700293 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1193 | 2021-11-17 | 477200 | keep | 0 | Nov | 2021 | 0.32502 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2021-11-17 22:39 | 2021-11-18 00:51 | 150 | 002:12 | P | NO SE REPORTO CAUSA | SE CERRARON MACHETES PREVIAMENTE ABIERTO | S21111700000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 132 | 2021-11-17 | 19800 | keep | 0 | Nov | 2021 | 0.013486 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-11-17 22:39 | 2021-11-18 11:48 | 20 | 013:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21111700116 | New_Event | Bad Weather | Include | Include | Weather | 789 | 2021-11-17 | 15780 | keep | 0 | Nov | 2021 | 0.010748 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-11-17 22:49 | 2021-11-18 11:08 | 100 | 012:19 | P | DESGANCHE | 1 X 100 EN C/L | R21111700066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 739 | 2021-11-17 | 73900 | keep | 0 | Nov | 2021 | 0.050333 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2021-11-17 22:55 | 2021-11-18 10:23 | 202 | 011:28 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | P21111700147 | New_Event | Vegetation Contact | Include | Include | Vegetation | 688 | 2021-11-17 | 138976 | keep | 0 | Nov | 2021 | 0.094656 | 0.00013758 | Sustained | FALSE | FALSE | Not_TMED_Event | 202
CAGUAS | 2021-11-17 23:22 | 2021-11-17 23:23 | 128 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVANDO LA CARGA DEL 3009-03 Y 3009-04 EN SERVICIO | C21111700317 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 128 | keep | 0 | Nov | 2021 | 8.718e-05 | 8.718e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 128
CAGUAS | 2021-11-17 23:22 | 2021-11-17 23:23 | 273 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR CARGA POR EL 3009-02 EN SERVICIO | C21111700317 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 273 | keep | 0 | Nov | 2021 | 0.00018594 | 0.00018594 | Momentary | FALSE | FALSE | Not_TMED_Event | 273
CAGUAS | 2021-11-17 23:22 | 2021-11-17 23:23 | 1772 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR CARGA POR EL 3009-02 EN SERVICIO | C21111700317 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 1772 | keep | 0 | Nov | 2021 | 0.0012069 | 0.0012069 | Momentary | FALSE | FALSE | Not_TMED_Event | 1772
MAYAGÃœEZ | 2021-11-17 23:22 | 2021-11-18 19:03 | 810 | 019:41 | S | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA DE LA SUBESTACION A PETICION DEL TOC PARA REPARAR LINEA 5600 | M21111800000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1181 | 2021-11-17 | 956610 | keep | 0 | Nov | 2021 | 0.65154 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-11-17 23:22 | 2021-11-18 19:03 | 1235 | 019:41 | S | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA DE LA SUBESTACION A PETICION DEL TOC PARA REPARAR LINEA 5600 | M21111800000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1181 | 2021-11-17 | 1458535 | keep | 0 | Nov | 2021 | 0.9934 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-11-17 23:22 | 2021-11-18 19:03 | 93 | 019:41 | S | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA DE LA SUBESTACION A PETICION DEL TOC PARA REPARAR LINEA 5600 | M21111800000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1181 | 2021-11-17 | 109833 | keep | 0 | Nov | 2021 | 0.074807 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-11-17 23:22 | 2021-11-18 19:03 | 1825 | 019:41 | S | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA DE LA SUBESTACION A PETICION DEL TOC PARA REPARAR LINEA 5600 | M21111800000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1181 | 2021-11-17 | 2155325 | keep | 0 | Nov | 2021 | 1.468 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-11-17 23:22 | 2021-11-18 19:03 | 3230 | 019:41 | S | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA DE LA SUBESTACION A PETICION DEL TOC PARA REPARAR LINEA 5600 | M21111800000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1181 | 2021-11-17 | 3814630 | keep | 0 | Nov | 2021 | 2.5981 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2021-11-17 23:24 | 2021-11-17 23:25 | 4279 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21111700152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 4279 | keep | 0 | Nov | 2021 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
ARECIBO | 2021-11-17 23:29 | 2021-11-18 10:06 | 150 | 010:37 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21111700118 | New_Event | Bad Weather | Include | Include | Weather | 637 | 2021-11-17 | 95550 | keep | 0 | Nov | 2021 | 0.065079 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-11-17 23:40 | 2021-11-17 23:41 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21111700443 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-17 | 108 | keep | 0 | Nov | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
BAYAMON | 2021-11-17 23:52 | 2021-11-18 03:44 | 2435 | 003:52 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO AVERIA VEHICULO IMPACTO PALMA Y TUMBO CONDUCTORES SE DESPEGO CONDUCTOR DE CRUCETA Y SE CERRO POR SCADA. LLEVA 1907-05 | S21111700309 | New_Event |  |  | Include | Wildlife | 232 | 2021-11-17 | 564920 | keep | 0 | Nov | 2021 | 0.38476 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-11-17 23:52 | 2021-11-18 03:44 | 2956 | 003:52 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO AVERIA VEHICULO IMPACTO PALMA TUMBO CONDUCTORES, SE DESPEGO CONDUCTOR DE CRUCETA Y SE CERRO POR SCADA. LLEVA 1907-05 | S21111700309 | New_Event |  |  | Include | Wildlife | 232 | 2021-11-17 | 685792 | keep | 0 | Nov | 2021 | 0.46709 | 0.0020133 | Sustained | FALSE | FALSE | Not_TMED_Event | 2956
GUAYAMA | 2021-11-17 23:54 | 2021-11-18 09:05 | 65 | 009:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 40 EN CORTE DE LINEA CARPA ENREDADA EN LINEA PRIMARIA | P21111700153 | New_Event |  |  | Include | Wildlife | 551 | 2021-11-17 | 35815 | keep | 0 | Nov | 2021 | 0.024393 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2021-11-17 23:55 | 2021-11-18 09:34 | 30 | 009:39 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | S21111700312 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 579 | 2021-11-17 | 17370 | keep | 0 | Nov | 2021 | 0.011831 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-11-17 23:59 | 2021-11-18 10:29 | 390 | 010:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L REEMPLAZO CAJA AVERIADA | R21111700076 | New_Event | Cutout Failure | Include | Include | Equipment | 630 | 2021-11-17 | 245700 | keep | 0 | Nov | 2021 | 0.16735 | 0.00026563 | Sustained | FALSE | FALSE | Not_TMED_Event | 390
CANOVANAS | 2021-11-18 00:20 | 2021-11-18 07:21 | 2106 | 007:01 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR NO RTU | R21111800006 | New_Event | UG Cable Fault | Include | Include | Equipment | 421 | 2021-11-18 | 886626 | keep | 0 | Nov | 2021 | 0.60388 | 0.0014344 | Sustained | FALSE | FALSE | Not_TMED_Event | 2106
CAGUAS | 2021-11-18 00:20 | 2021-11-18 00:21 | 166 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C21111800005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-18 | 166 | keep | 0 | Nov | 2021 | 0.00011306 | 0.00011306 | Momentary | FALSE | FALSE | Not_TMED_Event | 166
BAYAMON | 2021-11-18 00:21 | 2021-11-18 00:22 | 7 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA EL 1525-01 | S2111180000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-18 | 7 | keep | 0 | Nov | 2021 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-11-18 00:21 | 2021-11-18 00:22 | 15 | 000:01 | T | NO SE REPORTO CAUSA | RECEIRRE | S21111800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-18 | 15 | keep | 0 | Nov | 2021 | 1.0216e-05 | 1.0216e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-11-18 00:21 | 2021-11-18 00:22 | 771 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1327-09 | S2111180000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-18 | 771 | keep | 0 | Nov | 2021 | 0.00052512 | 0.00052512 | Momentary | FALSE | FALSE | Not_TMED_Event | 771
MAYAGÃœEZ | 2021-11-18 00:25 | 2021-11-18 00:26 | 108 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M21111800000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-11-18 | 108 | keep | 0 | Nov | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
MAYAGÃœEZ | 2021-11-18 00:26 | 2021-11-18 16:38 | 80 | 016:12 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21111800054 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 972 | 2021-11-18 | 77760 | keep | 0 | Nov | 2021 | 0.052962 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-11-18 00:51 | 2021-11-18 01:02 | 718 | 000:11 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA 90% DEL 1901-05 | S21111800000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 11 | 2021-11-18 | 7898 | keep | 0 | Nov | 2021 | 0.0053793 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-18 00:51 | 2021-11-18 01:02 | 520 | 000:11 | P | NO SE REPORTO CAUSA | SE CERRARON MACHETES PREVIAMENTE ABIERTO | S21111700000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 11 | 2021-11-18 | 5720 | keep | 0 | Nov | 2021 | 0.0038959 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-18 00:58 | 2021-11-18 10:17 | 100 | 009:19 | P | DESGANCHE | 3 X 30 Y 1 X 80 EN CORTE DE LINEA ARBOL CRUZO LAS FASES | B21111800021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 559 | 2021-11-18 | 55900 | keep | 0 | Nov | 2021 | 0.038073 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-11-18 01:02 | 2021-11-18 04:15 | 150 | 003:13 | P | NO SE REPORTO CAUSA | SE CERRARON MACHETES PREVIAMENTE ABIERTO | S21111700000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 193 | 2021-11-18 | 28950 | keep | 0 | Nov | 2021 | 0.019718 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-18 01:06 | 2021-11-18 16:55 | 10 | 015:49 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21111800043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 949 | 2021-11-18 | 9490 | keep | 0 | Nov | 2021 | 0.0064636 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-11-18 01:11 | 2021-11-18 13:40 | 55 | 012:29 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21111800009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 749 | 2021-11-18 | 41195 | keep | 0 | Nov | 2021 | 0.028058 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CAGUAS | 2021-11-18 01:38 | 2021-11-18 01:39 | 3005 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C21111800016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-18 | 3005 | keep | 0 | Nov | 2021 | 0.0020467 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
CANOVANAS | 2021-11-18 01:40 | 2021-11-18 09:57 | 10 | 008:17 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | R21111800019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 497 | 2021-11-18 | 4970 | keep | 0 | Nov | 2021 | 0.003385 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-11-18 01:41 | 2021-11-18 10:05 | 50 | 008:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L DESGANCHO Y REEMPLAZO CAJA | C21111800017 | New_Event | Cutout Failure | Include | Include | Equipment | 504 | 2021-11-18 | 25200 | keep | 0 | Nov | 2021 | 0.017164 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-18 02:16 | 2021-11-18 10:43 | 50 | 008:27 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21111800007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 507 | 2021-11-18 | 25350 | keep | 0 | Nov | 2021 | 0.017266 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-11-18 02:30 | 2021-11-18 11:59 | 50 | 009:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE NO FUNDIO | C21111800019 | New_Event | Wire Down | Include | Include | Equipment | 569 | 2021-11-18 | 28450 | keep | 0 | Nov | 2021 | 0.019377 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-18 03:44 | 2021-11-18 13:40 | 200 | 009:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE LEVANTO PRIMARIA QUE SE AVERIO EN ACCIDENTE DE TRANSITO | S21111800084 | Partial_restoration |  |  | Include | Wildlife | 596 | 2021-11-18 | 119200 | keep | 0 | Nov | 2021 | 0.081187 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-11-18 03:53 | 2021-11-18 03:54 | 4188 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R21111800028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-18 | 4188 | keep | 0 | Nov | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
BAYAMON | 2021-11-18 04:29 | 2021-11-18 05:40 | 554 | 001:11 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO Y SE CERRO POR SCADA 30% DE CARGA POR EL 1529-15 | S21111800000 | New_Event | Wire Down | Include | Include | Equipment | 71 | 2021-11-18 | 39334 | keep | 0 | Nov | 2021 | 0.02679 | 0.00037733 | Sustained | FALSE | FALSE | Not_TMED_Event | 554
BAYAMON | 2021-11-18 04:29 | 2021-11-18 05:40 | 1802 | 001:11 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO Y SE CERRO POR SCADA LLEVA EL 30% DEL 1346-02 | S21111800000 | New_Event | Wire Down | Include | Include | Equipment | 71 | 2021-11-18 | 127942 | keep | 0 | Nov | 2021 | 0.087141 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
UTUADO | 2021-11-18 04:38 | 2021-11-18 14:15 | 10 | 009:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21111800003 | New_Event | Bad Weather | Include | Include | Weather | 577 | 2021-11-18 | 5770 | keep | 0 | Nov | 2021 | 0.0039299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-18 04:40 | 2021-11-18 10:47 | 75 | 006:07 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21111800026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 367 | 2021-11-18 | 27525 | keep | 0 | Nov | 2021 | 0.018747 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2021-11-18 05:18 | 2021-11-18 05:19 | 878 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21111800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-18 | 878 | keep | 0 | Nov | 2021 | 0.000598 | 0.000598 | Momentary | FALSE | FALSE | Not_TMED_Event | 878
BAYAMON | 2021-11-18 05:24 | 2021-11-18 08:52 | 40 | 003:28 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21111800095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 208 | 2021-11-18 | 8320 | keep | 0 | Nov | 2021 | 0.0056667 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-18 05:27 | 2021-11-18 08:42 | 30 | 003:15 | P | NO SE REPORTO CAUSA | 1 X 25 EN PROVISIONAL AEREO | B21111800013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 195 | 2021-11-18 | 5850 | keep | 0 | Nov | 2021 | 0.0039844 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2021-11-18 05:28 | 2021-11-18 18:33 | 107 | 013:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE CERRO PUENTE PRIMARIO | P21111800008 | New_Event | Wire Down | Include | Include | Equipment | 785 | 2021-11-18 | 83995 | keep | 0 | Nov | 2021 | 0.057209 | 7.2877e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 107
GUAYAMA | 2021-11-18 05:38 | 2021-11-18 11:18 | 79 | 005:40 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA BAMBUA SOBRE LINEA | P21111800007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 340 | 2021-11-18 | 26860 | keep | 0 | Nov | 2021 | 0.018294 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
BAYAMON | 2021-11-18 05:40 | 2021-11-18 06:59 | 1500 | 001:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETE AVE. DE DIEGO 80% EN SERVICIO | S21111800000 | Partial_restoration | Wire Down | Include | Include | Equipment | 79 | 2021-11-18 | 118500 | keep | 0 | Nov | 2021 | 0.08071 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2021-11-18 05:47 | 2021-11-18 11:02 | 80 | 005:15 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN C/L | R21111700034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 315 | 2021-11-18 | 25200 | keep | 0 | Nov | 2021 | 0.017164 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2021-11-18 06:00 | 2021-11-18 11:26 | 60 | 005:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21111800004 | New_Event | Bad Weather | Include | Include | Weather | 326 | 2021-11-18 | 19560 | keep | 0 | Nov | 2021 | 0.013322 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-11-18 06:09 | 2021-11-18 14:16 | 75 | 008:07 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21111800017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 487 | 2021-11-18 | 36525 | keep | 0 | Nov | 2021 | 0.024877 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2021-11-18 06:09 | 2021-11-18 14:09 | 60 | 008:00 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21111800017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 480 | 2021-11-18 | 28800 | keep | 0 | Nov | 2021 | 0.019616 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2021-11-18 06:13 | 2021-11-18 14:31 | 55 | 008:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN C/L MAL TIEMPO | C21111800035 | New_Event | Bad Weather | Include | Include | Weather | 498 | 2021-11-18 | 27390 | keep | 0 | Nov | 2021 | 0.018655 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CAGUAS | 2021-11-18 06:21 | 2021-11-18 11:28 | 50 | 005:07 | P | DESGANCHE | 1 X 50 EN C/L | C21111800037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 307 | 2021-11-18 | 15350 | keep | 0 | Nov | 2021 | 0.010455 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-11-18 06:21 | 2021-11-18 12:47 | 15 | 006:26 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P21111800010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 386 | 2021-11-18 | 5790 | keep | 0 | Nov | 2021 | 0.0039435 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-11-18 06:23 | 2021-11-18 13:56 | 65 | 007:33 | P | DESGANCHE | 1 X 65 EN C/L Y 1 X 10 EN XMR | C21111800038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 453 | 2021-11-18 | 29445 | keep | 0 | Nov | 2021 | 0.020055 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
YAUCO | 2021-11-18 06:23 | 2021-11-18 12:07 | 44 | 005:44 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P21111800012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 344 | 2021-11-18 | 15136 | keep | 0 | Nov | 2021 | 0.010309 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
BAYAMON | 2021-11-18 06:29 | 2021-11-18 15:01 | 40 | 008:32 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21111800018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 512 | 2021-11-18 | 20480 | keep | 0 | Nov | 2021 | 0.013949 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2021-11-18 06:31 | 2021-11-18 12:03 | 30 | 005:32 | P | DESGANCHE | 1 X 30 EN C/L | C21111800041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 332 | 2021-11-18 | 9960 | keep | 0 | Nov | 2021 | 0.0067837 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-11-18 06:34 | 2021-11-18 09:33 | 60 | 002:59 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21111800020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2021-11-18 | 10740 | keep | 0 | Nov | 2021 | 0.007315 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-11-18 06:35 | 2021-11-18 07:36 | 40 | 001:01 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S21111800108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 61 | 2021-11-18 | 2440 | keep | 0 | Nov | 2021 | 0.0016619 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2021-11-18 06:35 | 2021-11-18 13:48 | 10 | 007:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN XMR MAL TIEMPO | C21111800042 | New_Event | Bad Weather | Include | Include | Weather | 433 | 2021-11-18 | 4330 | keep | 0 | Nov | 2021 | 0.0029491 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-18 06:37 | 2021-11-18 10:35 | 40 | 003:58 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21111800021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2021-11-18 | 9520 | keep | 0 | Nov | 2021 | 0.006484 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2021-11-18 06:40 | 2021-11-18 06:41 | 113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21111800015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-18 | 113 | keep | 0 | Nov | 2021 | 7.6964e-05 | 7.6964e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 113
YAUCO | 2021-11-18 06:42 | 2021-11-18 12:30 | 101 | 005:48 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21111800014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 348 | 2021-11-18 | 35148 | keep | 0 | Nov | 2021 | 0.023939 | 6.8791e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 101
CAGUAS | 2021-11-18 06:43 | 2021-11-18 06:44 | 1709 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21111800048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-18 | 1709 | keep | 0 | Nov | 2021 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
UTUADO | 2021-11-18 06:56 | 2021-11-18 09:56 | 20 | 003:00 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21111800005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2021-11-18 | 3600 | keep | 0 | Nov | 2021 | 0.0024519 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-11-18 06:59 | 2021-11-18 17:41 | 300 | 010:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ENCONTRO PUENTE ABIERTO | S21111800000 | Partial_restoration | Wire Down | Include | Include | Equipment | 642 | 2021-11-18 | 192600 | keep | 0 | Nov | 2021 | 0.13118 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-11-18 07:00 | 2021-11-18 11:20 | 80 | 004:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21111800011 | New_Event | Bad Weather | Include | Include | Weather | 260 | 2021-11-18 | 20800 | keep | 0 | Nov | 2021 | 0.014167 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-11-18 07:02 | 2021-11-18 09:19 | 60 | 002:17 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21111800115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 137 | 2021-11-18 | 8220 | keep | 0 | Nov | 2021 | 0.0055986 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2021-11-18 07:03 | 2021-11-18 09:27 | 30 | 002:24 | P | DESGANCHE | 1 X 30 EN C/L | C21111800054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2021-11-18 | 4320 | keep | 0 | Nov | 2021 | 0.0029423 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2021-11-18 07:04 | 2021-11-18 11:09 | 15 | 004:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN C/L MAL TIEMPO | R21111800045 | New_Event | Bad Weather | Include | Include | Weather | 245 | 2021-11-18 | 3675 | keep | 0 | Nov | 2021 | 0.002503 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-11-18 07:07 | 2021-11-18 11:03 | 40 | 003:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 C/L MAL TIEMPO | C21111800056 | New_Event | Bad Weather | Include | Include | Weather | 236 | 2021-11-18 | 9440 | keep | 0 | Nov | 2021 | 0.0064295 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-11-18 07:21 | 2021-11-18 21:39 | 25 | 014:18 | P | CABLE SOTERRADO AVERIADO | 1 X 15 EN PROVISIONAL AEREO SE CONSTRUYO PROVISIONAL DEL SU-2A3 @ T-2A1 | R21111800071 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 858 | 2021-11-18 | 21450 | keep | 0 | Nov | 2021 | 0.014609 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-18 07:36 | 2021-11-18 07:37 | 10211 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO INTERRUPTOR 1206-03 LLEVANDO CARGA 1204-05 | S21118000000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-11-18 | 10211 | keep | 0 | Nov | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-11-18 07:36 | 2021-11-18 07:37 | 4133 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO INTERRUPTOR 1206-03 LLEVANDO CARGA 1204-05 | S21111800000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-11-18 | 4133 | keep | 0 | Nov | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
BAYAMON | 2021-11-18 07:37 | 2021-11-18 17:08 | 100 | 009:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 2 X 80 Y 2 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA | S21111800125 | New_Event | Cutout Failure | Include | Include | Equipment | 571 | 2021-11-18 | 57100 | keep | 0 | Nov | 2021 | 0.038891 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-11-18 07:37 | 2021-11-18 14:06 | 45 | 006:29 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 80 EN RISER SE REPARO TERMINACION | S21111800200 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 389 | 2021-11-18 | 17505 | keep | 0 | Nov | 2021 | 0.011923 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2021-11-18 07:37 | 2021-11-18 10:47 | 40 | 003:10 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S21111800108 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 190 | 2021-11-18 | 7600 | keep | 0 | Nov | 2021 | 0.0051763 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-11-18 07:38 | 2021-11-18 07:39 | 2368 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO | B21111800000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-11-18 | 2368 | keep | 0 | Nov | 2021 | 0.0016128 | 0.0016128 | Momentary | FALSE | FALSE | Not_TMED_Event | 2368
VEGA BAJA | 2021-11-18 07:39 | 2021-11-18 14:15 | 75 | 006:36 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 Y 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B21111800026 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 396 | 2021-11-18 | 29700 | keep | 0 | Nov | 2021 | 0.020229 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2021-11-18 07:52 | 2021-11-18 20:00 | 250 | 012:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE RETEZARON LINEAS PRIMARIAS MISMO EVENTO CON DOS SITUACIONES DIFERENTES | M21111800014 | New_Event | Wire Down | Include | Include | Equipment | 728 | 2021-11-18 | 182000 | keep | 0 | Nov | 2021 | 0.12396 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
AGUADILLA | 2021-11-18 07:52 | 2021-11-18 23:15 | 15 | 015:23 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 50 KVA X 50 KVA MISMO EVENTO SITUACIONES DIFERENTES | M21111800014 | New_Event | Service Transformer Failure | Include | Include | Equipment | 923 | 2021-11-18 | 13845 | keep | 0 | Nov | 2021 | 0.0094298 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-11-18 07:55 | 2021-11-18 07:56 | 1284 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21111800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-18 | 1284 | keep | 0 | Nov | 2021 | 0.00087453 | 0.00087453 | Momentary | FALSE | FALSE | Not_TMED_Event | 1284
CAGUAS | 2021-11-18 07:59 | 2021-11-19 10:28 | 250 | 026:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE NO FUNDIO | C21111800067 | New_Event | Wire Down | Include | Include | Equipment | 1589 | 2021-11-18 | 397250 | keep | 0 | Nov | 2021 | 0.27057 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2021-11-18 08:00 | 2021-11-18 08:02 | 225 | 000:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-05 LLEVANDO CARGA 1303-04 SE CERRO POR SCADA | S21111800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-11-18 | 450 | keep | 0 | Nov | 2021 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-11-18 08:00 | 2021-11-18 08:02 | 870 | 000:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-05 LLEVANDO CARGA 1303-04 SE CERRO POR SCADA | S21111800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-11-18 | 1740 | keep | 0 | Nov | 2021 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
HUMACAO | 2021-11-18 08:07 | 2021-11-18 15:52 | 30 | 007:45 | P | DESGANCHE | 1 X 30 EN C/L | C21111800070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 465 | 2021-11-18 | 13950 | keep | 0 | Nov | 2021 | 0.0095013 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2021-11-18 08:08 | 2021-11-18 11:00 | 302 | 002:52 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO RAMA DE LINEA PRIMARIA | P21111800029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2021-11-18 | 51944 | keep | 0 | Nov | 2021 | 0.035379 | 0.00020569 | Sustained | FALSE | FALSE | Not_TMED_Event | 302
BAYAMON | 2021-11-18 08:13 | 2021-11-19 17:29 | 8 | 033:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN C/L, SE REEMPLAZO PORTAFUSIBLES Y SE CERRARON DOS PUENTES | S21111800139 | New_Event | Cutout Failure | Include | Include | Equipment | 1996 | 2021-11-18 | 15968 | keep | 0 | Nov | 2021 | 0.010876 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-11-18 08:14 | 2021-11-18 08:16 | 1290 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 LLEVANDO CARGA DE 1336-09 Y 40% 1206-04 | S21111800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-18 | 2580 | keep | 0 | Nov | 2021 | 0.0017572 | 0.00087861 | Momentary | FALSE | FALSE | Not_TMED_Event | 1290
SAN JUAN | 2021-11-18 08:14 | 2021-11-18 08:16 | 5290 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 LLEVANDO CARGA DE 1336-09 Y 30% 1204-04 | S21111800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-18 | 10580 | keep | 0 | Nov | 2021 | 0.007206 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2021-11-18 08:14 | 2021-11-18 08:16 | 207 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 LLEVANDO CARGA DE 1336-09 Y 30% 1204-04 | S21111800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-18 | 414 | keep | 0 | Nov | 2021 | 0.00028197 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
ARECIBO | 2021-11-18 08:35 | 2021-11-18 14:45 | 10 | 006:10 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR LA MISMA CAPACIDAD | A21111800012 | New_Event | Service Transformer Failure | Include | Include | Equipment | 370 | 2021-11-18 | 3700 | keep | 0 | Nov | 2021 | 0.0025201 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-11-18 08:40 | 2021-11-18 12:09 | 100 | 003:29 | P | DESGANCHE | 2 X 80 EN C/L | C21111800076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2021-11-18 | 20900 | keep | 0 | Nov | 2021 | 0.014235 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2021-11-18 08:40 | 2021-11-18 23:50 | 30 | 015:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA PARTIDA SE ABRIO CORTE DE LINEA PARA SECCIONALIZAR ABRIENDO PUENTES | M21111800026 | New_Event | Wire Down | Include | Include | Equipment | 910 | 2021-11-18 | 27300 | keep | 0 | Nov | 2021 | 0.018594 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-11-18 08:41 | 2021-11-18 11:14 | 50 | 002:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21111800013 | New_Event | Bad Weather | Include | Include | Weather | 153 | 2021-11-18 | 7650 | keep | 0 | Nov | 2021 | 0.0052104 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-11-18 08:42 | 2021-11-18 16:21 | 35 | 007:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA | P21111800030 | New_Event | Wire Down | Include | Include | Equipment | 459 | 2021-11-18 | 16065 | keep | 0 | Nov | 2021 | 0.010942 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-11-18 08:43 | 2021-11-18 08:44 | 3458 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR CAJA PRIMARIA QUEMADA | M21111800000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-11-18 | 3458 | keep | 0 | Nov | 2021 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
MAYAGÃœEZ | 2021-11-18 08:44 | 2021-11-18 14:40 | 40 | 005:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | M21111800044 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 356 | 2021-11-18 | 14240 | keep | 0 | Nov | 2021 | 0.0096988 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-11-18 08:50 | 2021-11-18 11:30 | 817 | 002:40 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | REEMPLAZO AISLADOR Y LEVANTO NEUTRAL PRIMARIO | R21111800058 | New_Event | Wire Down | Include | Include | Equipment | 160 | 2021-11-18 | 130720 | keep | 0 | Nov | 2021 | 0.089033 | 0.00055645 | Sustained | FALSE | FALSE | Not_TMED_Event | 817
UTUADO | 2021-11-18 08:52 | 2021-11-18 11:59 | 100 | 003:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEAS PRIMARIAS | A21111800015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2021-11-18 | 18700 | keep | 0 | Nov | 2021 | 0.012736 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-11-18 08:59 | 2021-11-18 17:47 | 50 | 008:48 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21111800149 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 528 | 2021-11-18 | 26400 | keep | 0 | Nov | 2021 | 0.017981 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-11-18 09:01 | 2021-11-18 09:26 | 225 | 000:25 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-05 LLEVANDO CARGA 1303-04 SE CERRO POR SCADA SE REALIZO DESGANCHE | S21111800000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 25 | 2021-11-18 | 5625 | keep | 0 | Nov | 2021 | 0.0038312 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-11-18 09:01 | 2021-11-18 09:26 | 870 | 000:25 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-05 LLEVANDO CARGA 1303-04 SE CERRO POR SCADA SE REALIZO DESGANCHE | S21111800000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 25 | 2021-11-18 | 21750 | keep | 0 | Nov | 2021 | 0.014814 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2021-11-18 09:01 | 2021-11-18 11:25 | 75 | 002:24 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21111800030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2021-11-18 | 10800 | keep | 0 | Nov | 2021 | 0.0073558 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2021-11-18 09:03 | 2021-11-18 12:22 | 5 | 003:19 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA X 37.5 KVA | M21111800037 | New_Event | Service Transformer Failure | Include | Include | Equipment | 199 | 2021-11-18 | 995 | keep | 0 | Nov | 2021 | 0.00067769 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-11-18 09:06 | 2021-11-18 10:38 | 300 | 001:32 | P | DESGANCHE | DISPARO DE INTERRUPTOR 1335-05 LLEVANDO 40% 1301-02 SE REALIZO DESGANCHE Y SE CERRO POR SCADA | S21111800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2021-11-18 | 27600 | keep | 0 | Nov | 2021 | 0.018798 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2021-11-18 09:06 | 2021-11-18 10:38 | 314 | 001:32 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1335-05 LLEVANDO 40% 1301-02 SE REALIZO DESGANCHE Y SE CERRO POR SCADA | S21111800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2021-11-18 | 28888 | keep | 0 | Nov | 2021 | 0.019675 | 0.00021386 | Sustained | FALSE | FALSE | Not_TMED_Event | 314
SAN JUAN | 2021-11-18 09:07 | 2021-11-18 10:41 | 3877 | 001:34 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO PARA REALIZAR DESGANCHE Y SE CERRO POR SCADA | S21111800156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2021-11-18 | 364438 | keep | 0 | Nov | 2021 | 0.24822 | 0.0026406 | Sustained | FALSE | FALSE | Not_TMED_Event | 3877
VEGA BAJA | 2021-11-18 09:15 | 2021-11-18 09:16 | 1526 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO | B21111800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-18 | 1526 | keep | 0 | Nov | 2021 | 0.0010394 | 0.0010394 | Momentary | FALSE | FALSE | Not_TMED_Event | 1526
VEGA BAJA | 2021-11-18 09:16 | 2021-11-18 17:02 | 50 | 007:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE CERRO PUENTE DE LINEA A CAJA | B21111800035 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 466 | 2021-11-18 | 23300 | keep | 0 | Nov | 2021 | 0.01587 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-11-18 09:22 | 2021-11-18 11:59 | 7 | 002:37 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR AVERIADO 25 KVA X 25 KVA | C21111800088 | New_Event | Service Transformer Failure | Include | Include | Equipment | 157 | 2021-11-18 | 1099 | keep | 0 | Nov | 2021 | 0.00074852 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2021-11-18 09:22 | 2021-11-18 17:26 | 50 | 008:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO BAJANTE DE CAJA A XMR | C21111800087 | New_Event | Wire Down | Include | Include | Equipment | 484 | 2021-11-18 | 24200 | keep | 0 | Nov | 2021 | 0.016483 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-11-18 09:29 | 2021-11-18 15:03 | 225 | 005:34 | T | DESGANCHE | DISPARO SE RETIRO BAMBUAS SOBRE LINEA SU CARGA POR 1303-5 Y SE CERRO N/O | S21111800000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 334 | 2021-11-18 | 75150 | keep | 0 | Nov | 2021 | 0.051184 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-18 09:29 | 2021-11-18 12:10 | 870 | 002:41 | T | DESGANCHE | SE RETIRO BAMBUAS SOBRE LINEA CAMINO LOS GUANOS LLEVA CARGA 1303-4 SE ABRIO N/O Y ALAMBRE PRIMARIO EN EL PISO | S21111800000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 161 | 2021-11-18 | 140070 | keep | 0 | Nov | 2021 | 0.095401 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-11-18 09:30 | 2021-11-18 10:57 | 1 | 001:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21111700089 | New_Event | Bad Weather | Include | Include | Weather | 87 | 2021-11-18 | 87 | keep | 0 | Nov | 2021 | 5.9255e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-11-18 09:34 | 2021-11-18 18:00 | 20 | 008:26 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO | A21111800020 | New_Event | Defective Pole | Include | Include | Equipment | 506 | 2021-11-18 | 10120 | keep | 0 | Nov | 2021 | 0.0068927 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-11-18 09:37 | 2021-11-18 20:05 | 80 | 010:28 | P | HERRAJE ROTO O PODRIDO | SE ABRE CORTE DE LINEA PARA REMPLAZO CRUCETA | S21111800183 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 628 | 2021-11-18 | 50240 | keep | 0 | Nov | 2021 | 0.034218 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
YAUCO | 2021-11-18 09:39 | 2021-11-18 12:55 | 15 | 003:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CAMION IMPACTO LINEA SECUNDARIA | P21111800037 | New_Event |  |  | Include | Wildlife | 196 | 2021-11-18 | 2940 | keep | 0 | Nov | 2021 | 0.0020024 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-11-18 09:56 | 2021-11-18 12:11 | 50 | 002:15 | P | DESGANCHE | 1 X 50 EN C/L | C21111800090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2021-11-18 | 6750 | keep | 0 | Nov | 2021 | 0.0045974 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-18 10:10 | 2021-11-18 11:44 | 12 | 001:34 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHE PRIMARIO | B21111800038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2021-11-18 | 1128 | keep | 0 | Nov | 2021 | 0.00076828 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-11-18 10:14 | 2021-11-18 17:23 | 11 | 007:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR REPARO SECUNDARIA | R21111800094 | New_Event | Secondary Wire Down | Include | Include | Equipment | 429 | 2021-11-18 | 4719 | keep | 0 | Nov | 2021 | 0.0032141 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
ARECIBO | 2021-11-18 10:15 | 2021-11-18 12:30 | 2 | 002:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | A21111800027 | New_Event | Wire Down | Include | Include | Equipment | 135 | 2021-11-18 | 270 | keep | 0 | Nov | 2021 | 0.0001839 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
FAJARDO | 2021-11-18 10:16 | 2021-11-18 12:10 | 8 | 001:54 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | R21111800067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 114 | 2021-11-18 | 912 | keep | 0 | Nov | 2021 | 0.00062116 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-11-18 10:18 | 2021-11-18 13:26 | 12 | 003:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21111800028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 188 | 2021-11-18 | 2256 | keep | 0 | Nov | 2021 | 0.0015366 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-11-18 10:25 | 2021-11-18 10:26 | 2179 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | R21111800000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-11-18 | 2179 | keep | 0 | Nov | 2021 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
SAN JUAN | 2021-11-18 10:26 | 2021-11-18 19:00 | 190 | 008:34 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA REEMPLAZO AISLADOR | R21111800101 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 514 | 2021-11-18 | 97660 | keep | 0 | Nov | 2021 | 0.066516 | 0.00012941 | Sustained | FALSE | FALSE | Not_TMED_Event | 190
BAYAMON | 2021-11-18 10:31 | 2021-11-18 10:34 | 641 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1133-04 LLEVANDO CARGA 1105-02 Y 1105-01 SE CERRO POR SCADA | S21111800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-18 | 1923 | keep | 0 | Nov | 2021 | 0.0013097 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
BAYAMON | 2021-11-18 10:31 | 2021-11-18 10:34 | 308 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1133-04 LLEVANDO CARGA 1105-02 Y 1105-01 SE CERRO POR SCADA | S21111800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-18 | 924 | keep | 0 | Nov | 2021 | 0.00062933 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2021-11-18 10:31 | 2021-11-18 10:34 | 333 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1133-04 LLEVANDO CARGA 1105-02 Y 1105-01 SE CERRO POR SCADA | S21111800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-18 | 999 | keep | 0 | Nov | 2021 | 0.00068041 | 0.0002268 | Momentary | FALSE | FALSE | Not_TMED_Event | 333
SAN JUAN | 2021-11-18 10:32 | 2021-11-18 10:33 | 6481 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21111800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-18 | 6481 | keep | 0 | Nov | 2021 | 0.0044142 | 0.0044142 | Momentary | FALSE | FALSE | Not_TMED_Event | 6481
SAN JUAN | 2021-11-18 10:32 | 2021-11-18 11:29 | 6244 | 000:57 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZO DESGANCHE Y SE CERRO POR SCADA | S21111800213 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2021-11-18 | 355908 | keep | 0 | Nov | 2021 | 0.24241 | 0.0042528 | Sustained | FALSE | FALSE | Not_TMED_Event | 6244
UTUADO | 2021-11-18 10:37 | 2021-11-18 11:15 | 50 | 000:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21111800031 | New_Event | Bad Weather | Include | Include | Weather | 38 | 2021-11-18 | 1900 | keep | 0 | Nov | 2021 | 0.0012941 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2021-11-18 10:39 | 2021-11-18 10:42 | 2635 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6500 | C21111800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-18 | 7905 | keep | 0 | Nov | 2021 | 0.0053841 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2021-11-18 10:39 | 2021-11-18 10:42 | 2280 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6500 | C21111800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-18 | 6840 | keep | 0 | Nov | 2021 | 0.0046587 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2021-11-18 10:39 | 2021-11-18 10:42 | 1617 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6500 | C21111800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-18 | 4851 | keep | 0 | Nov | 2021 | 0.003304 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
SAN JUAN | 2021-11-18 10:41 | 2021-11-18 11:55 | 80 | 001:14 | P | DESGANCHE | SE CERRO MACHETES EN CARRETERA 199 HILLSIDE SE REALIZO DESGANCHE | S21111800156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2021-11-18 | 5920 | keep | 0 | Nov | 2021 | 0.0040321 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2021-11-18 10:41 | 2021-11-18 18:27 | 1 | 007:46 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 20 EN C/L MAL TIEMPO | C21111800101 | New_Event | Bad Weather | Include | Include | Weather | 466 | 2021-11-18 | 466 | keep | 0 | Nov | 2021 | 0.00031739 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2021-11-18 10:43 | 2021-11-18 13:34 | 112 | 002:51 | P | DESGANCHE | 1 X 100 1 X 80 EN CORTE DE LINEA SE HIZO DESGANCHE | P21111800043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2021-11-18 | 19152 | keep | 0 | Nov | 2021 | 0.013044 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
ARECIBO | 2021-11-18 10:48 | 2021-11-18 18:01 | 75 | 007:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21111800033 | New_Event | Bad Weather | Include | Include | Weather | 433 | 2021-11-18 | 32475 | keep | 0 | Nov | 2021 | 0.022119 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2021-11-18 10:50 | 2021-11-18 19:22 | 107 | 008:32 | P | ESTRUCTURA AVERIADA | SE ABRE CORTE DE LINEA PARA REMPLAZO POSTE | S2111800130 | New_Event | Defective Pole | Include | Include | Equipment | 512 | 2021-11-18 | 54784 | keep | 0 | Nov | 2021 | 0.037313 | 7.2877e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 107
HUMACAO | 2021-11-18 10:55 | 2021-11-18 16:57 | 10 | 006:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN C/L MAL TIEMPO | C21111800106 | New_Event | Bad Weather | Include | Include | Weather | 362 | 2021-11-18 | 3620 | keep | 0 | Nov | 2021 | 0.0024656 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-11-18 11:04 | 2021-11-18 12:42 | 3 | 001:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CAMION PARTE TOMA SECUNDARIA | P21111800045 | New_Event |  |  | Include | Wildlife | 98 | 2021-11-18 | 294 | keep | 0 | Nov | 2021 | 0.00020024 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-11-18 11:04 | 2021-11-18 17:24 | 20 | 006:20 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | M21111800065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 380 | 2021-11-18 | 7600 | keep | 0 | Nov | 2021 | 0.0051763 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-11-18 11:05 | 2021-11-18 17:08 | 100 | 006:03 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S21111800233 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 363 | 2021-11-18 | 36300 | keep | 0 | Nov | 2021 | 0.024724 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-18 11:12 | 2021-11-18 14:10 | 150 | 002:58 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21111800038 | Partial_restoration | Bad Weather | Include | Include | Weather | 178 | 2021-11-18 | 26700 | keep | 0 | Nov | 2021 | 0.018185 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-18 11:16 | 2021-11-18 11:17 | 325 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21111800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-18 | 325 | keep | 0 | Nov | 2021 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
ARECIBO | 2021-11-18 11:16 | 2021-11-18 16:20 | 600 | 005:04 | P | DESGANCHE | 3 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21111800039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 304 | 2021-11-18 | 182400 | keep | 0 | Nov | 2021 | 0.12423 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
CAGUAS | 2021-11-18 11:29 | 2021-11-18 12:41 | 100 | 001:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN C/L MAL TIEMPO | C21111800118 | New_Event | Bad Weather | Include | Include | Weather | 72 | 2021-11-18 | 7200 | keep | 0 | Nov | 2021 | 0.0049039 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-18 11:30 | 2021-11-18 12:25 | 10 | 000:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21111800011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 55 | 2021-11-18 | 550 | keep | 0 | Nov | 2021 | 0.0003746 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-18 11:42 | 2021-11-18 15:01 | 80 | 003:19 | P | DESGANCHE | 3 X 100 EN CORTE DE LINEA SE RETIRO ARBOL | B21111800050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2021-11-18 | 15920 | keep | 0 | Nov | 2021 | 0.010843 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2021-11-18 11:55 | 2021-11-18 11:56 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO LA CAUSA | M21111800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-18 | 3041 | keep | 0 | Nov | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
HUMACAO | 2021-11-18 11:59 | 2021-11-18 12:03 | 1089 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21111800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-11-18 | 4356 | keep | 0 | Nov | 2021 | 0.0029669 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2021-11-18 11:59 | 2021-11-18 12:03 | 3896 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21111800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-11-18 | 15584 | keep | 0 | Nov | 2021 | 0.010614 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2021-11-18 11:59 | 2021-11-18 12:03 | 1467 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21111800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-11-18 | 5868 | keep | 0 | Nov | 2021 | 0.0039967 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
HUMACAO | 2021-11-18 12:03 | 2021-11-18 13:01 | 50 | 000:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE NO FUNDIO | C21111800019 | New_Event | Wire Down | Include | Include | Equipment | 58 | 2021-11-18 | 2900 | keep | 0 | Nov | 2021 | 0.0019752 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-11-18 12:03 | 2021-11-19 10:42 | 7 | 022:39 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR AVERIADO DE 25 KVA X 25 KVA | C21111800088 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1359 | 2021-11-18 | 9513 | keep | 0 | Nov | 2021 | 0.0064793 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-11-18 12:07 | 2021-11-18 14:18 | 1105 | 002:11 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES PARA SECCIONALIZAR PUENTE PRIMARIO ABIERTO Y SE CERRO EL INTERRUPTOR | A21111800043 | New_Event | Wire Down | Include | Include | Equipment | 131 | 2021-11-18 | 144755 | keep | 0 | Nov | 2021 | 0.098592 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
YAUCO | 2021-11-18 12:21 | 2021-11-18 14:09 | 40 | 001:48 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21111800050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2021-11-18 | 4320 | keep | 0 | Nov | 2021 | 0.0029423 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-11-18 12:30 | 2021-11-18 19:00 | 30 | 006:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRE CORTE DE LINEA PARA RETIRAR CULEBRA | S21111800259 | New_Event |  |  | Include | Wildlife | 390 | 2021-11-18 | 11700 | keep | 0 | Nov | 2021 | 0.0079688 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2021-11-18 12:44 | 2021-11-18 14:11 | 55 | 001:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA | R21111800074 | New_Event | Cutout Failure | Include | Include | Equipment | 87 | 2021-11-18 | 4785 | keep | 0 | Nov | 2021 | 0.003259 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
MAYAGÃœEZ | 2021-11-18 12:53 | 2021-11-18 16:13 | 45 | 003:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21111800077 | New_Event | Bad Weather | Include | Include | Weather | 200 | 2021-11-18 | 9000 | keep | 0 | Nov | 2021 | 0.0061299 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2021-11-18 13:04 | 2021-11-18 13:05 | 5252 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21111800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-18 | 5252 | keep | 0 | Nov | 2021 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
BAYAMON | 2021-11-18 13:04 | 2021-11-18 13:05 | 3438 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21111800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-18 | 3438 | keep | 0 | Nov | 2021 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
CAGUAS | 2021-11-18 13:13 | 2021-11-18 15:39 | 5 | 002:26 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHO | C21111800138 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 146 | 2021-11-18 | 730 | keep | 0 | Nov | 2021 | 0.0004972 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-11-18 13:13 | 2021-11-18 18:16 | 30 | 005:03 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | M21111800080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 303 | 2021-11-18 | 9090 | keep | 0 | Nov | 2021 | 0.0061912 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-11-18 13:15 | 2021-11-18 13:17 | 2126 | 000:02 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO CRUCE POR AVE | C21111800140 | New_Event |  |  | Include | Wildlife | 2 | 2021-11-18 | 4252 | keep | 0 | Nov | 2021 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
BAYAMON | 2021-11-18 13:17 | 2021-11-18 18:45 | 478 | 005:28 | T | DESGANCHE | SE RETIRO PALMA DE LA LINEA LLEVANDO 80% DEL 1705-03 | B21111800058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 328 | 2021-11-18 | 156784 | keep | 0 | Nov | 2021 | 0.10678 | 0.00032556 | Sustained | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2021-11-18 13:17 | 2021-11-18 18:45 | 800 | 005:28 | P | DESGANCHE | 80% DEL ALIMENTADOR TRANSFERIDO AL 1705-01 | B21111800058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 328 | 2021-11-18 | 262400 | keep | 0 | Nov | 2021 | 0.17872 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
HUMACAO | 2021-11-18 13:17 | 2021-11-18 18:20 | 1 | 005:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE POR AVE | C21111800195 | 1st_after_momentary |  |  | Include | Wildlife | 303 | 2021-11-18 | 303 | keep | 0 | Nov | 2021 | 0.00020637 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-11-18 13:33 | 2021-11-18 15:37 | 19 | 002:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21111700048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 124 | 2021-11-18 | 2356 | keep | 0 | Nov | 2021 | 0.0016047 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
CAGUAS | 2021-11-18 13:34 | 2021-11-18 16:31 | 50 | 002:57 | P | DESGANCHE | 1 X 65 EN C/L | C21111800148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2021-11-18 | 8850 | keep | 0 | Nov | 2021 | 0.0060277 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2021-11-18 13:34 | 2021-11-18 21:03 | 50 | 007:29 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L REEMPLAZO 2 DISCOS | C21111800147 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 449 | 2021-11-18 | 22450 | keep | 0 | Nov | 2021 | 0.015291 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-11-18 13:39 | 2021-11-18 18:52 | 76 | 005:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO Y SE CERRO CORTE DE LINEA | P21111800056 | New_Event | Wire Down | Include | Include | Equipment | 313 | 2021-11-18 | 23788 | keep | 0 | Nov | 2021 | 0.016202 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
BAYAMON | 2021-11-18 13:44 | 2021-11-18 13:47 | 1825 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1118-09 LLEVANDO CARGA 1118-08 SE CERRO POR SCADA | S21111800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-18 | 5475 | keep | 0 | Nov | 2021 | 0.003729 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
BAYAMON | 2021-11-18 13:44 | 2021-11-18 13:47 | 4398 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1118-09 LLEVANDO CARGA 1118-08 SE CERRO POR SCADA | S21111800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-18 | 13194 | keep | 0 | Nov | 2021 | 0.0089864 | 0.0029955 | Momentary | FALSE | FALSE | Not_TMED_Event | 4398
ARECIBO | 2021-11-18 14:03 | 2021-11-18 15:58 | 10 | 001:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21111800052 | New_Event | Bad Weather | Include | Include | Weather | 115 | 2021-11-18 | 1150 | keep | 0 | Nov | 2021 | 0.00078326 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-11-18 14:08 | 2021-11-18 15:20 | 65 | 001:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P21111800057 | New_Event |  |  | Include | Wildlife | 72 | 2021-11-18 | 4680 | keep | 0 | Nov | 2021 | 0.0031875 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
VEGA BAJA | 2021-11-18 14:12 | 2021-11-18 18:13 | 40 | 004:01 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B21111800069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 241 | 2021-11-18 | 9640 | keep | 0 | Nov | 2021 | 0.0065658 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-11-18 14:18 | 2021-11-18 17:15 | 718 | 002:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO Y SE CERRO LOS MACHETES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR LA AVERIA | A21111800043 | Partial_restoration | Wire Down | Include | Include | Equipment | 177 | 2021-11-18 | 127086 | keep | 0 | Nov | 2021 | 0.086558 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-11-18 14:19 | 2021-11-18 14:20 | 2446 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21111800058 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-11-18 | 2446 | keep | 0 | Nov | 2021 | 0.001666 | 0.001666 | Momentary | FALSE | FALSE | Not_TMED_Event | 2446
PONCE | 2021-11-18 14:20 | 2021-11-18 17:05 | 80 | 002:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 200 EN CORTE DE LINEA SE REMPLAZO AISLADOR AVERIADO | P21111800070 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 165 | 2021-11-18 | 13200 | keep | 0 | Nov | 2021 | 0.0089905 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-11-18 14:21 | 2021-11-18 14:42 | 1 | 000:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21111800086 | New_Event | Bad Weather | Include | Include | Weather | 21 | 2021-11-18 | 21 | keep | 0 | Nov | 2021 | 1.4303e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-11-18 14:23 | 2021-11-18 15:47 | 7 | 001:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR REPARO HERRAJE DE CAJA | C21111800179 | New_Event | Cutout Failure | Include | Include | Equipment | 84 | 2021-11-18 | 588 | keep | 0 | Nov | 2021 | 0.00040048 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2021-11-18 14:24 | 2021-11-18 20:26 | 40 | 006:02 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21111800071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 362 | 2021-11-18 | 14480 | keep | 0 | Nov | 2021 | 0.0098623 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2021-11-18 14:25 | 2021-11-18 14:46 | 1 | 000:21 | P | NO SE REPORTO CAUSA | 1 X 15 EN RISER @ BANCO TRIFASICO | R21111800083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 21 | 2021-11-18 | 21 | keep | 0 | Nov | 2021 | 1.4303e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-18 14:30 | 2021-11-18 15:55 | 627 | 001:25 | S | LINEA DE TRANSMISION 38KV | DISPARO L-8900 | S21111800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2021-11-18 | 53295 | keep | 0 | Nov | 2021 | 0.036299 | 0.00042705 | Sustained | FALSE | FALSE | Not_TMED_Event | 627
SAN JUAN | 2021-11-18 14:30 | 2021-11-18 15:55 | 293 | 001:25 | S | LINEA DE TRANSMISION 38KV | DISPARO L-8900 LLEVA 1421-5 | S21111800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2021-11-18 | 24905 | keep | 0 | Nov | 2021 | 0.016963 | 0.00019956 | Sustained | FALSE | FALSE | Not_TMED_Event | 293
SAN JUAN | 2021-11-18 14:30 | 2021-11-18 15:55 | 761 | 001:25 | S | LINEA DE TRANSMISION 38KV | DISPARO L-8900 LLEVA 1421-1 | S21111800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2021-11-18 | 64685 | keep | 0 | Nov | 2021 | 0.044057 | 0.00051831 | Sustained | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2021-11-18 14:30 | 2021-11-18 15:55 | 451 | 001:25 | S | LINEA DE TRANSMISION 38KV | DISPARO L-8900 | S21111800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2021-11-18 | 38335 | keep | 0 | Nov | 2021 | 0.02611 | 0.00030717 | Sustained | FALSE | FALSE | Not_TMED_Event | 451
BAYAMON | 2021-11-18 14:30 | 2021-11-18 14:31 | 7 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA EL 1525-01 | S21111800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-18 | 7 | keep | 0 | Nov | 2021 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-11-18 14:30 | 2021-11-18 14:31 | 15 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21111800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-18 | 15 | keep | 0 | Nov | 2021 | 1.0216e-05 | 1.0216e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-11-18 14:30 | 2021-11-18 15:55 | 1498 | 001:25 | T | LINEA DE TRANSMISION 38KV | DISPARO L-8900 SU CARGA POR 1310-4 | S21111800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2021-11-18 | 127330 | keep | 0 | Nov | 2021 | 0.086724 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
SAN JUAN | 2021-11-18 14:30 | 2021-11-18 15:55 | 766 | 001:25 | T | LINEA DE TRANSMISION 38KV | DISPARO L-8900 SU CARGA POR 1310-3 | S21111800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2021-11-18 | 65110 | keep | 0 | Nov | 2021 | 0.044346 | 0.00052172 | Sustained | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2021-11-18 14:30 | 2021-11-18 14:31 | 771 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR EL 1327-09 | S21111800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-18 | 771 | keep | 0 | Nov | 2021 | 0.00052512 | 0.00052512 | Momentary | FALSE | FALSE | Not_TMED_Event | 771
BAYAMON | 2021-11-18 14:31 | 2021-11-18 18:08 | 12 | 003:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA | B21111800074 | New_Event | Wire Down | Include | Include | Equipment | 217 | 2021-11-18 | 2604 | keep | 0 | Nov | 2021 | 0.0017736 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-11-18 14:34 | 2021-11-18 21:24 | 150 | 006:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA VEHICULO IMPACTA POSTE PRIMARIO | P21111800063 | New_Event |  |  | Include | Wildlife | 410 | 2021-11-18 | 61500 | keep | 0 | Nov | 2021 | 0.041887 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2021-11-18 14:34 | 2021-11-18 15:58 | 30 | 001:24 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21111800077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2021-11-18 | 2520 | keep | 0 | Nov | 2021 | 0.0017164 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2021-11-18 14:52 | 2021-11-18 14:53 | 1364 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21111800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-18 | 1364 | keep | 0 | Nov | 2021 | 0.00092901 | 0.00092901 | Momentary | FALSE | FALSE | Not_TMED_Event | 1364
UTUADO | 2021-11-18 14:55 | 2021-11-18 18:43 | 100 | 003:48 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | A21111800067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2021-11-18 | 22800 | keep | 0 | Nov | 2021 | 0.015529 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2021-11-18 15:05 | 2021-11-18 17:22 | 11 | 002:17 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR | R21111800091 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 137 | 2021-11-18 | 1507 | keep | 0 | Nov | 2021 | 0.0010264 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
YAUCO | 2021-11-18 15:10 | 2021-11-18 17:10 | 400 | 002:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE DE LINEA PRIMARIA A CAJA EN CORTE DE LINEA | P21111800072 | New_Event | Wire Down | Include | Include | Equipment | 120 | 2021-11-18 | 48000 | keep | 0 | Nov | 2021 | 0.032693 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
AGUADILLA | 2021-11-18 15:13 | 2021-11-18 19:00 | 70 | 003:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21111800100 | New_Event | Bad Weather | Include | Include | Weather | 227 | 2021-11-18 | 15890 | keep | 0 | Nov | 2021 | 0.010823 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2021-11-18 15:23 | 2021-11-18 15:34 | 2891 | 000:11 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO PERSONAL REALIZANDO OPERACIONES EN TRAMO SIN CARGA DEL 1647-08 CON AISLADOR AVERIADO CORRIENDO PARALELO AL 1646-05 | R21118000095 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 11 | 2021-11-18 | 31801 | keep | 0 | Nov | 2021 | 0.02166 | 0.001969 | Sustained | FALSE | FALSE | Not_TMED_Event | 2891
MAYAGÃœEZ | 2021-11-18 15:25 | 2021-11-18 17:50 | 500 | 002:25 | P | DESGANCHE | 3 X 80 EN CORTE DE LINEA DESGANCHE | M21111800106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 145 | 2021-11-18 | 72500 | keep | 0 | Nov | 2021 | 0.049379 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
ARECIBO | 2021-11-18 15:27 | 2021-11-18 15:28 | 5042 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21111800077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-18 | 5042 | keep | 0 | Nov | 2021 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
BARRANQUITAS | 2021-11-18 15:29 | 2021-11-19 10:49 | 3 | 019:20 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN XMR DESGANCHO | C21111800168 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1160 | 2021-11-18 | 3480 | keep | 0 | Nov | 2021 | 0.0023702 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-11-18 15:31 | 2021-11-18 18:07 | 12 | 002:36 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE POSTE SECUNDARIO | S21111800384 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 156 | 2021-11-18 | 1872 | keep | 0 | Nov | 2021 | 0.001275 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-11-18 15:33 | 2021-11-18 15:41 | 4369 | 000:08 | T | NO SE REPORTO CAUSA | DISPARO SE VERIFICO PERSONAL FUERA | C21111800173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2021-11-18 | 34952 | keep | 0 | Nov | 2021 | 0.023806 | 0.0029757 | Sustained | FALSE | FALSE | Not_TMED_Event | 4369
SAN JUAN | 2021-11-18 15:40 | 2021-11-19 11:15 | 12 | 019:35 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR Y SE REALIZO DESGANCHE SECUNDARIO | S21111800389 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1175 | 2021-11-18 | 14100 | keep | 0 | Nov | 2021 | 0.0096034 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-11-18 15:41 | 2021-11-18 16:34 | 7 | 000:53 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | C21111800163 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 53 | 2021-11-18 | 371 | keep | 0 | Nov | 2021 | 0.00025269 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-11-18 15:41 | 2021-11-18 20:49 | 30 | 005:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21111800110 | New_Event | Bad Weather | Include | Include | Weather | 308 | 2021-11-18 | 9240 | keep | 0 | Nov | 2021 | 0.0062933 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2021-11-18 15:55 | 2021-11-18 20:35 | 40 | 004:40 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21111800083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2021-11-18 | 11200 | keep | 0 | Nov | 2021 | 0.0076283 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-11-18 15:59 | 2021-11-18 18:58 | 50 | 002:59 | P | NO SE REPORTO CAUSA | 1 X 65 EN PROVISIONAL | S21111800397 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 179 | 2021-11-18 | 8950 | keep | 0 | Nov | 2021 | 0.0060958 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-18 16:05 | 2021-11-18 16:06 | 271 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21111800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-18 | 271 | keep | 0 | Nov | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
ARECIBO | 2021-11-18 16:26 | 2021-11-18 16:27 | 1976 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21111800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-18 | 1976 | keep | 0 | Nov | 2021 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
SAN JUAN | 2021-11-18 16:36 | 2021-11-18 20:09 | 70 | 003:33 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21111800100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2021-11-18 | 14910 | keep | 0 | Nov | 2021 | 0.010155 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2021-11-18 16:53 | 2021-11-19 11:25 | 15 | 018:32 | P | SECUNDARIA/DESGANCHE | 1 X 25 EN CORTE DE LINEA Y SE REALIZO DESGANCHE SECUNDARIO | S21111800429 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1112 | 2021-11-18 | 16680 | keep | 0 | Nov | 2021 | 0.011361 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-11-18 17:09 | 2021-11-18 17:42 | 50 | 000:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 40 EN CORTE DE LINEA | S21111800125 | New_Event | Cutout Failure | Include | Include | Equipment | 33 | 2021-11-18 | 1650 | keep | 0 | Nov | 2021 | 0.0011238 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2021-11-18 17:09 | 2021-11-19 14:23 | 40 | 021:14 | P | DESGANCHE | 1 X 40 EN C/L | C21111800192 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1274 | 2021-11-18 | 50960 | keep | 0 | Nov | 2021 | 0.034709 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-18 17:15 | 2021-11-19 17:35 | 12 | 024:20 | P | NO SE REPORTO CAUSA | 2 X 15 EN XMR | S21111800043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1460 | 2021-11-18 | 17520 | keep | 0 | Nov | 2021 | 0.011933 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-11-18 17:17 | 2021-11-19 13:00 | 40 | 019:43 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S21111800038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1183 | 2021-11-18 | 47320 | keep | 0 | Nov | 2021 | 0.032229 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-11-18 17:28 | 2021-11-18 19:03 | 8 | 001:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21111800085 | New_Event | Secondary Wire Down | Include | Include | Equipment | 95 | 2021-11-18 | 760 | keep | 0 | Nov | 2021 | 0.00051763 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-11-18 17:41 | 2021-11-18 18:34 | 400 | 000:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO SALIDA ALIMENTADOR SU CARGA POR 1529-15 | S21111800414 | New_Event | Wire Down | Include | Include | Equipment | 53 | 2021-11-18 | 21200 | keep | 0 | Nov | 2021 | 0.014439 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2021-11-18 17:41 | 2021-11-18 18:34 | 1802 | 000:53 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO SALIDA ALIMENTADOR LLEVA 30% 1346-2 | S21111800414 | New_Event | Wire Down | Include | Include | Equipment | 53 | 2021-11-18 | 95506 | keep | 0 | Nov | 2021 | 0.065049 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
CAGUAS | 2021-11-18 17:41 | 2021-11-18 19:55 | 22 | 002:14 | P | CABLE SOTERRADO AVERIADO | CONSTRUYO AEREO PROVISIONAL DEL T12 AL T11 | C21111700158 | New_Event | UG Cable Fault | Include | Include | Equipment | 134 | 2021-11-18 | 2948 | keep | 0 | Nov | 2021 | 0.0020079 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
ARECIBO | 2021-11-18 17:44 | 2021-11-18 17:47 | 1 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A21111800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-18 | 3 | keep | 0 | Nov | 2021 | 2.0433e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-11-18 17:44 | 2021-11-18 17:47 | 2266 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A21111800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-18 | 6798 | keep | 0 | Nov | 2021 | 0.0046301 | 0.0015434 | Momentary | FALSE | FALSE | Not_TMED_Event | 2266
ARECIBO | 2021-11-18 17:44 | 2021-11-18 17:47 | 1399 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A21111800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-18 | 4197 | keep | 0 | Nov | 2021 | 0.0028586 | 0.00095285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1399
ARECIBO | 2021-11-18 17:48 | 2021-11-18 22:25 | 120 | 004:37 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21111800095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 277 | 2021-11-18 | 33240 | keep | 0 | Nov | 2021 | 0.02264 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2021-11-18 17:48 | 2021-11-18 23:04 | 200 | 005:16 | P | DESGANCHE | 3 X 65 C/L SE REALIZO DESGANCHE Y SE LEVANTO CONDUCTORES | B21111800110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 316 | 2021-11-18 | 63200 | keep | 0 | Nov | 2021 | 0.043045 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2021-11-18 18:12 | 2021-11-18 18:54 | 1 | 000:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN MONTURA TRIFASICA CAJA PRIMARIA DEFECTUOSA | P21118000109 | New_Event | Cutout Failure | Include | Include | Equipment | 42 | 2021-11-18 | 42 | keep | 0 | Nov | 2021 | 2.8606e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-11-18 18:14 | 2021-11-18 21:00 | 200 | 002:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21111800098 | New_Event | Bad Weather | Include | Include | Weather | 166 | 2021-11-18 | 33200 | keep | 0 | Nov | 2021 | 0.022612 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-11-18 18:34 | 2021-11-18 19:16 | 150 | 000:42 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO PARARRAYO Y SE REALIZO BYPASS A CAJA SECAS | S21111800414 | New_Event | Switch Failure | Include | Include | Equipment | 42 | 2021-11-18 | 6300 | keep | 0 | Nov | 2021 | 0.0042909 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2021-11-18 18:48 | 2021-11-19 00:57 | 41 | 006:09 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B21111800118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 369 | 2021-11-18 | 15129 | keep | 0 | Nov | 2021 | 0.010304 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
SAN JUAN | 2021-11-18 19:00 | 2021-11-18 20:25 | 70 | 001:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTE DE LINEA SE RETIRO CULEBRA | S21111800259 | Additional_clients |  |  | Include | Wildlife | 85 | 2021-11-18 | 5950 | keep | 0 | Nov | 2021 | 0.0040525 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-11-18 19:01 | 2021-11-18 20:15 | 10 | 001:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21111800028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 74 | 2021-11-18 | 740 | keep | 0 | Nov | 2021 | 0.00050401 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-11-18 19:13 | 2021-11-18 20:04 | 100 | 000:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21111800149 | New_Event | Bad Weather | Include | Include | Weather | 51 | 2021-11-18 | 5100 | keep | 0 | Nov | 2021 | 0.0034736 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-11-18 19:14 | 2021-11-18 21:05 | 4 | 001:51 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA RELOCALIZAR LINEA SECUNDARIA POR POSTE AVERIADO | M21111800150 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 111 | 2021-11-18 | 444 | keep | 0 | Nov | 2021 | 0.00030241 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-11-18 19:16 | 2021-11-18 19:19 | 400 | 000:03 | P | CABLE SOTERRADO AVERIADO | DISPARO AL CERRAR DE RISER A MH-15 SE DEJO ABIERTO Y TAG PARA MAÃ‘ANA VERIFICAR SOLO HAY 2 CLIENTES FUERA SU CARGA POR 1529-15 | S21111800000 | New_Event | UG Cable Fault | Include | Include | Equipment | 3 | 2021-11-18 | 1200 | keep | 0 | Nov | 2021 | 0.00081731 | 0.00027244 | Momentary | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2021-11-18 19:16 | 2021-11-18 19:19 | 1802 | 000:03 | T | CABLE SOTERRADO AVERIADO | DISPARO AL CERRAR DEL RISER A MH-15 SE BYPASEO CAJAS SECA Y SE REMPLAZO PARARRAYO SE DEJO RISER ABIERTO Y TAG PARA MANANA VERIFICAR 2 CLIENTES FUERA AVE. DE DIEGO A OSO BLANCO LLEVA CARGA 1346-2 30% | S21111800000 | New_Event | UG Cable Fault | Include | Include | Equipment | 3 | 2021-11-18 | 5406 | keep | 0 | Nov | 2021 | 0.003682 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
BAYAMON | 2021-11-18 19:19 | 2021-11-19 16:00 | 2 | 020:41 | P | CABLE SOTERRADO AVERIADO | SE REPARO AVERIA SOTERRADA EN MH-8 CON GOI SJ-211119-01 | S21111800076 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 1241 | 2021-11-18 | 2482 | keep | 0 | Nov | 2021 | 0.0016905 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
FAJARDO | 2021-11-18 19:36 | 2021-11-18 20:03 | 1 | 000:27 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | R21111800112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 27 | 2021-11-18 | 27 | keep | 0 | Nov | 2021 | 1.839e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-11-18 19:36 | 2021-11-18 22:52 | 6 | 003:16 | P | PARARRAYOS DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REMPLAZO PARARRAYOS DEFECTUOSO | M21111800157 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 196 | 2021-11-18 | 1176 | keep | 0 | Nov | 2021 | 0.00080097 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-11-18 19:43 | 2021-11-19 12:19 | 50 | 016:36 | P | DESGANCHE | 1 X 50 EN C/L | C21111800204 | New_Event | Vegetation Contact | Include | Include | Vegetation | 996 | 2021-11-18 | 49800 | keep | 0 | Nov | 2021 | 0.033919 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-11-18 19:46 | 2021-11-19 16:10 | 12 | 020:24 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR AVERIADO DE 75 KVA X 37.5 KVA | C21111800205 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1224 | 2021-11-18 | 14688 | keep | 0 | Nov | 2021 | 0.010004 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-11-18 19:47 | 2021-11-18 20:02 | 100 | 000:15 | P | NO SE REPORTO CAUSA | 1 X 100 EN PARALELA | S21111800475 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2021-11-18 | 1500 | keep | 0 | Nov | 2021 | 0.0010216 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-11-18 19:54 | 2021-11-18 19:56 | 6136 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21111800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-18 | 12272 | keep | 0 | Nov | 2021 | 0.0083584 | 0.0041792 | Momentary | FALSE | FALSE | Not_TMED_Event | 6136
CAGUAS | 2021-11-18 20:09 | 2021-11-18 20:30 | 6 | 000:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR NEUTRAL SECUNDARIO | C21111800102 | New_Event | Secondary Wire Down | Include | Include | Equipment | 21 | 2021-11-18 | 126 | keep | 0 | Nov | 2021 | 8.5818e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-11-18 20:12 | 2021-11-19 18:00 | 10 | 021:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO NEUTRAL ABIERTO | S21111800478 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1308 | 2021-11-18 | 13080 | keep | 0 | Nov | 2021 | 0.0089087 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-11-18 20:23 | 2021-11-18 21:15 | 1 | 000:52 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | R21111800113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 52 | 2021-11-18 | 52 | keep | 0 | Nov | 2021 | 3.5417e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-18 20:57 | 2021-11-19 18:22 | 50 | 021:25 | P | CABLE SOTERRADO AVERIADO | CON GOI BY-211119-01 SE REPARO TRAMO DEL SU-1 @ T-10 | B21111800133 | New_Event | UG Cable Fault | Include | Include | Equipment | 1285 | 2021-11-18 | 64250 | keep | 0 | Nov | 2021 | 0.04376 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-18 21:19 | 2021-11-19 15:15 | 10 | 017:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE IDENTIFICO PUENTE ABIERTO DE LINEA A CAJA DE XMR Y POR SEGURIDAD DEBIDO A PUENTES PEGADOS A CRUCETA SE ABRIO CORTE DE LINEA | S21111800486 | New_Event | Wire Down | Include | Include | Equipment | 1076 | 2021-11-18 | 10760 | keep | 0 | Nov | 2021 | 0.0073286 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-11-18 21:24 | 2021-11-18 22:08 | 45 | 000:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CULEBRA CRUZO LINEAS | M21111800168 | New_Event |  |  | Include | Wildlife | 44 | 2021-11-18 | 1980 | keep | 0 | Nov | 2021 | 0.0013486 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2021-11-18 21:26 | 2021-11-19 10:42 | 100 | 013:16 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21111800169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 796 | 2021-11-18 | 79600 | keep | 0 | Nov | 2021 | 0.054215 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-11-18 22:12 | 2021-11-19 07:42 | 40 | 009:30 | P | DESGANCHE | 1 X 40 EN C/L | C21111800212 | New_Event | Vegetation Contact | Include | Include | Vegetation | 570 | 2021-11-18 | 22800 | keep | 0 | Nov | 2021 | 0.015529 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-11-18 22:12 | 2021-11-19 11:50 | 17 | 013:38 | P | CABLE SOTERRADO AVERIADO | 1 X 40 SMU 20 EN SU-1 SE REPARO CABLE SOTERRADO HACIA T-23 | C21111800180 | New_Event | UG Cable Fault | Include | Include | Equipment | 818 | 2021-11-18 | 13906 | keep | 0 | Nov | 2021 | 0.0094713 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
GUAYAMA | 2021-11-18 22:12 | 2021-11-19 10:17 | 40 | 012:05 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTA CAUSA | P21111800128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 725 | 2021-11-18 | 29000 | keep | 0 | Nov | 2021 | 0.019752 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-18 22:48 | 2021-11-19 11:01 | 50 | 012:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN C/L SE REPARO PRIMARIA ZAFADA | B21111800143 | New_Event | Wire Down | Include | Include | Equipment | 733 | 2021-11-18 | 36650 | keep | 0 | Nov | 2021 | 0.024962 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-11-18 23:50 | 2021-11-19 01:10 | 110 | 001:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO LINEA PRIMARIA PARTIDA ABRIENDO PUENTES Y SE CERRO CORTE DE LINEA | M21111800026 | New_Event | Wire Down | Include | Include | Equipment | 80 | 2021-11-18 | 8800 | keep | 0 | Nov | 2021 | 0.0059936 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
MAYAGÃœEZ | 2021-11-19 00:16 | 2021-11-19 15:31 | 25 | 015:15 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | M21111900002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 915 | 2021-11-19 | 22875 | keep | 0 | Nov | 2021 | 0.01558 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2021-11-19 01:10 | 2021-11-19 17:25 | 60 | 016:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M21111800026 | New_Event | Wire Down | Include | Include | Equipment | 975 | 2021-11-19 | 58500 | keep | 0 | Nov | 2021 | 0.039844 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-11-19 01:16 | 2021-11-19 10:33 | 20 | 009:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 SMU 20 DE 20AMP CRUCE POR RATON | R21111900002 | New_Event |  |  | Include | Wildlife | 557 | 2021-11-19 | 11140 | keep | 0 | Nov | 2021 | 0.0075874 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-11-19 01:38 | 2021-11-19 10:21 | 40 | 008:43 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | R21111900003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 523 | 2021-11-19 | 20920 | keep | 0 | Nov | 2021 | 0.014249 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-11-19 02:10 | 2021-11-19 08:41 | 20 | 006:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PORTA FUSIBLE QUEMADO | A21111900001 | New_Event | Cutout Failure | Include | Include | Equipment | 391 | 2021-11-19 | 7820 | keep | 0 | Nov | 2021 | 0.0053262 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-11-19 03:13 | 2021-11-19 17:29 | 100 | 014:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS ABIERTOS Y SE REMPLAZO 3 CAJAS PRIMARIAS AVERIADAS MARCA HUBBLEE DE 200AMP | M21111900004 | New_Event | Wire Down | Include | Include | Equipment | 856 | 2021-11-19 | 85600 | keep | 0 | Nov | 2021 | 0.058302 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-11-19 03:24 | 2021-11-19 11:26 | 50 | 008:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA Y SE REEMPLAZO CAJA QUEMADA | S21111900011 | New_Event | Cutout Failure | Include | Include | Equipment | 482 | 2021-11-19 | 24100 | keep | 0 | Nov | 2021 | 0.016414 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-11-19 03:35 | 2021-11-19 12:11 | 30 | 008:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN C/L RAYOS | B21111900004 | New_Event | Bad Weather | Include | Include | Weather | 516 | 2021-11-19 | 15480 | keep | 0 | Nov | 2021 | 0.010543 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2021-11-19 04:38 | 2021-11-19 04:39 | 2635 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C21111900002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-19 | 2635 | keep | 0 | Nov | 2021 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
CAGUAS | 2021-11-19 04:45 | 2021-11-19 04:46 | 2178 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C21111900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-19 | 2178 | keep | 0 | Nov | 2021 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
YAUCO | 2021-11-19 05:13 | 2021-11-19 10:18 | 50 | 005:05 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA NO SE REPORTA CAUSA | P21111900002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 305 | 2021-11-19 | 15250 | keep | 0 | Nov | 2021 | 0.010387 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-19 05:28 | 2021-11-19 17:32 | 4 | 012:04 | P | OTRAS CAUSAS | 1 X 15 EN TRANSFORMADOR PROBLEMA DE BASE DE CONTADOR DE CLIENTE CAUSO FUNDIERA EL FUSIBLE | M21111900008 | New_Event | Other Causes | Include | Include | Other | 724 | 2021-11-19 | 2896 | keep | 0 | Nov | 2021 | 0.0019725 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2021-11-19 05:39 | 2021-11-19 05:40 | 640 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C21111900004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-19 | 640 | keep | 0 | Nov | 2021 | 0.0004359 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
MAYAGÃœEZ | 2021-11-19 05:39 | 2021-11-19 18:51 | 150 | 013:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE REPARO LINEA PRIMARIA ROTA | M21111900009 | New_Event | Wire Down | Include | Include | Equipment | 792 | 2021-11-19 | 118800 | keep | 0 | Nov | 2021 | 0.080914 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2021-11-19 05:45 | 2021-11-19 05:46 | 2858 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21111900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-19 | 2858 | keep | 0 | Nov | 2021 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
CANOVANAS | 2021-11-19 06:19 | 2021-11-19 15:15 | 9 | 008:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BARRA EN PEDESTAL AVERIADA | R21111900004 | New_Event | Secondary Wire Down | Include | Include | Equipment | 536 | 2021-11-19 | 4824 | keep | 0 | Nov | 2021 | 0.0032856 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2021-11-19 06:25 | 2021-11-19 08:55 | 60 | 002:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN C/L RAYOS | B21111900011 | New_Event | Bad Weather | Include | Include | Weather | 150 | 2021-11-19 | 9000 | keep | 0 | Nov | 2021 | 0.0061299 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2021-11-19 06:40 | 2021-11-19 21:25 | 7 | 014:45 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR AVERIADO DE 15 KVA X 15 KVA | C21111900044 | New_Event | Service Transformer Failure | Include | Include | Equipment | 885 | 2021-11-19 | 6195 | keep | 0 | Nov | 2021 | 0.0042194 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2021-11-19 06:44 | 2021-11-19 10:30 | 50 | 003:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L REEMPLAZO PORTAFUSIBLE QUEMADO | C21111900008 | New_Event | Cutout Failure | Include | Include | Equipment | 226 | 2021-11-19 | 11300 | keep | 0 | Nov | 2021 | 0.0076964 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-11-19 06:54 | 2021-11-19 12:05 | 40 | 005:11 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21111900011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 311 | 2021-11-19 | 12440 | keep | 0 | Nov | 2021 | 0.0084728 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2021-11-19 07:01 | 2021-11-19 09:34 | 40 | 002:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA POR CARPA CRUZAR FASES | P21111900003 | New_Event |  |  | Include | Wildlife | 153 | 2021-11-19 | 6120 | keep | 0 | Nov | 2021 | 0.0041683 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-11-19 07:32 | 2021-11-19 10:26 | 35 | 002:54 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21111900035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2021-11-19 | 6090 | keep | 0 | Nov | 2021 | 0.0041479 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2021-11-19 07:38 | 2021-11-19 12:11 | 30 | 004:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN C/L SE LLEVO LINEA PARTIDA A SU SITIO | B21111900014 | New_Event | Wire Down | Include | Include | Equipment | 273 | 2021-11-19 | 8190 | keep | 0 | Nov | 2021 | 0.0055782 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-11-19 07:42 | 2021-11-19 07:43 | 1879 | 000:01 | T | DESGANCHE | RECIERRE | C21111900015 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-19 | 1879 | keep | 0 | Nov | 2021 | 0.0012798 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-11-19 07:43 | 2021-11-19 09:18 | 40 | 001:35 | P | DESGANCHE | 1 X 40 EN C/L | C21111800212 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 95 | 2021-11-19 | 3800 | keep | 0 | Nov | 2021 | 0.0025882 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2021-11-19 07:50 | 2021-11-19 10:27 | 50 | 002:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21111900004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2021-11-19 | 7850 | keep | 0 | Nov | 2021 | 0.0053466 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-11-19 07:59 | 2021-11-19 13:41 | 60 | 005:42 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER | B21111900015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 342 | 2021-11-19 | 20520 | keep | 0 | Nov | 2021 | 0.013976 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2021-11-19 08:07 | 2021-11-19 14:07 | 9 | 006:00 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR | R21111900008 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 360 | 2021-11-19 | 3240 | keep | 0 | Nov | 2021 | 0.0022067 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2021-11-19 08:15 | 2021-11-19 18:15 | 10 | 010:00 | P | ESTRUCTURA AVERIADA | SE REEMPALZO POSTE PARTIDO Y SE CERRO PUENTE ABIERTO CON VOLTAJE SIN CARGA | S21111900041 | New_Event | Defective Pole | Include | Include | Equipment | 600 | 2021-11-19 | 6000 | keep | 0 | Nov | 2021 | 0.0040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-11-19 08:24 | 2021-11-19 08:40 | 10 | 000:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES Y BUSHINGS | M21111800146 | New_Event | Secondary Wire Down | Include | Include | Equipment | 16 | 2021-11-19 | 160 | keep | 0 | Nov | 2021 | 0.00010898 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-11-19 08:38 | 2021-11-19 12:18 | 10 | 003:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE CAJA DE TRANSFORMADOR PARA REPARAR SECUNDARIA | P21111900008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 220 | 2021-11-19 | 2200 | keep | 0 | Nov | 2021 | 0.0014984 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-11-19 08:40 | 2021-11-19 12:00 | 128 | 003:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | P21111900009 | New_Event | Wire Down | Include | Include | Equipment | 200 | 2021-11-19 | 25600 | keep | 0 | Nov | 2021 | 0.017436 | 8.718e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 128
HUMACAO | 2021-11-19 08:43 | 2021-11-19 19:41 | 9 | 010:58 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR AVERIADO DE 25 KVA X 25 KVA | C21111900025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 658 | 2021-11-19 | 5922 | keep | 0 | Nov | 2021 | 0.0040334 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-11-19 08:45 | 2021-11-19 09:53 | 60 | 001:08 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA CARGA DEL 1907-05 ESTA POR 1909-08 | S21111900048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 68 | 2021-11-19 | 4080 | keep | 0 | Nov | 2021 | 0.0027789 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-11-19 08:50 | 2021-11-19 15:17 | 3 | 006:27 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR AVERIADO 75 X 75 KVA | S21111900038 | New_Event | Service Transformer Failure | Include | Include | Equipment | 387 | 2021-11-19 | 1161 | keep | 0 | Nov | 2021 | 0.00079075 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-11-19 09:00 | 2021-11-19 14:08 | 180 | 005:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L Y 1 X 80 EN SU-3 REEMPLAZO BASE DE FUSIBLE SMU AVERIADO EN SU-3 | R21111900010 | New_Event | Cutout Failure | Include | Include | Equipment | 308 | 2021-11-19 | 55440 | keep | 0 | Nov | 2021 | 0.03776 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
MAYAGÃœEZ | 2021-11-19 09:12 | 2021-11-19 11:00 | 14 | 001:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21111900026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 108 | 2021-11-19 | 1512 | keep | 0 | Nov | 2021 | 0.0010298 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CAGUAS | 2021-11-19 09:15 | 2021-11-19 09:16 | 1153 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3000 | C21111900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-19 | 1153 | keep | 0 | Nov | 2021 | 0.0007853 | 0.0007853 | Momentary | FALSE | FALSE | Not_TMED_Event | 1153
CAGUAS | 2021-11-19 09:15 | 2021-11-19 09:16 | 1709 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3000 | C21111900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-19 | 1709 | keep | 0 | Nov | 2021 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
CAGUAS | 2021-11-19 09:15 | 2021-11-19 09:16 | 1320 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3000 | C21111900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-19 | 1320 | keep | 0 | Nov | 2021 | 0.00089905 | 0.00089905 | Momentary | FALSE | FALSE | Not_TMED_Event | 1320
BAYAMON | 2021-11-19 09:17 | 2021-11-19 19:40 | 4 | 010:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN RISER. SE LEVANTO CONDUCTOR | S21111900051 | New_Event | Wire Down | Include | Include | Equipment | 623 | 2021-11-19 | 2492 | keep | 0 | Nov | 2021 | 0.0016973 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2021-11-19 09:23 | 2021-11-19 15:29 | 1 | 006:06 | P | NO SE REPORTO CAUSA | 2 X 40 EN RISER NO CAUSA | C21111900032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 366 | 2021-11-19 | 366 | keep | 0 | Nov | 2021 | 0.00024928 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-11-19 09:24 | 2021-11-19 12:10 | 40 | 002:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | M21111900028 | New_Event | Wire Down | Include | Include | Equipment | 166 | 2021-11-19 | 6640 | keep | 0 | Nov | 2021 | 0.0045225 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2021-11-19 09:37 | 2021-11-19 11:41 | 20 | 002:04 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN C/L REEMPLAZO AISLADOR | C21111900034 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 124 | 2021-11-19 | 2480 | keep | 0 | Nov | 2021 | 0.0016891 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-11-19 09:41 | 2021-11-19 16:58 | 5 | 007:17 | P | NO SE REPORTO CAUSA | 1 X 100 EN XMR | S21111900057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 437 | 2021-11-19 | 2185 | keep | 0 | Nov | 2021 | 0.0014882 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-11-19 09:53 | 2021-11-19 11:21 | 1153 | 001:28 | S | LINEA DE TRANSMISION 38KV | PERSONA HIZO CONTACTO CON LA LINEA 3000 | C21111900000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 88 | 2021-11-19 | 101464 | keep | 0 | Nov | 2021 | 0.069107 | 0.0007853 | Sustained | FALSE | FALSE | Not_TMED_Event | 1153
CAGUAS | 2021-11-19 09:53 | 2021-11-19 11:21 | 1709 | 001:28 | S | LINEA DE TRANSMISION 38KV | PERSONA HIZO CONTACTO CON LA LINEA 3000 | C21111900000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 88 | 2021-11-19 | 150392 | keep | 0 | Nov | 2021 | 0.10243 | 0.001164 | Sustained | FALSE | FALSE | Not_TMED_Event | 1709
CAGUAS | 2021-11-19 09:53 | 2021-11-19 11:21 | 1320 | 001:28 | S | LINEA DE TRANSMISION 38KV | PERSONA HIZO CONTACTO CON LA LINEA 3000 | C21111900000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 88 | 2021-11-19 | 116160 | keep | 0 | Nov | 2021 | 0.079116 | 0.00089905 | Sustained | FALSE | FALSE | Not_TMED_Event | 1320
MAYAGÃœEZ | 2021-11-19 09:53 | 2021-11-19 16:37 | 10 | 006:44 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR LA MISMA CAPACIDAD | M21111900030 | New_Event | Service Transformer Failure | Include | Include | Equipment | 404 | 2021-11-19 | 4040 | keep | 0 | Nov | 2021 | 0.0027516 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-11-19 09:54 | 2021-11-19 17:13 | 8 | 007:19 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR, SE REALIZO DESGANCHE SECUNDARIO Y REPARO SECUNDARIA PARTIDA | A21111800100 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 439 | 2021-11-19 | 3512 | keep | 0 | Nov | 2021 | 0.002392 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-11-19 09:57 | 2021-11-19 10:49 | 6 | 000:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21111900064 | New_Event | Secondary Wire Down | Include | Include | Equipment | 52 | 2021-11-19 | 312 | keep | 0 | Nov | 2021 | 0.0002125 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-11-19 09:59 | 2021-11-19 11:09 | 60 | 001:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA ZAFADA | M21111900034 | New_Event | Wire Down | Include | Include | Equipment | 70 | 2021-11-19 | 4200 | keep | 0 | Nov | 2021 | 0.0028606 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-11-19 10:01 | 2021-11-19 20:18 | 200 | 010:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21111900035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 617 | 2021-11-19 | 123400 | keep | 0 | Nov | 2021 | 0.084047 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2021-11-19 10:04 | 2021-11-19 17:35 | 85 | 007:31 | P | DESGANCHE | 2 X 50 EN C/L | C21111900051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 451 | 2021-11-19 | 38335 | keep | 0 | Nov | 2021 | 0.02611 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
BAYAMON | 2021-11-19 10:06 | 2021-11-19 11:20 | 120 | 001:14 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | B21111900025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 74 | 2021-11-19 | 8880 | keep | 0 | Nov | 2021 | 0.0060481 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
UTUADO | 2021-11-19 10:07 | 2021-11-19 11:16 | 5 | 001:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CONECTORES SECUNDARIOS | A21111800008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 69 | 2021-11-19 | 345 | keep | 0 | Nov | 2021 | 0.00023498 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-11-19 10:08 | 2021-11-19 15:47 | 80 | 005:39 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21111900026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 339 | 2021-11-19 | 27120 | keep | 0 | Nov | 2021 | 0.018471 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-11-19 10:08 | 2021-11-19 12:40 | 8 | 002:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | ABRIO XMR PARA REPARAR SECUNDARIA AVERIADA POR CAMION | R21111900016 | New_Event |  |  | Include | Wildlife | 152 | 2021-11-19 | 1216 | keep | 0 | Nov | 2021 | 0.00082821 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-11-19 10:25 | 2021-11-19 15:35 | 10 | 005:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARACIONES SECUNDARIAS | M21111900036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 310 | 2021-11-19 | 3100 | keep | 0 | Nov | 2021 | 0.0021114 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-11-19 10:40 | 2021-11-19 18:54 | 60 | 008:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA FUERTE VIENTO | M21111900037 | New_Event | Bad Weather | Include | Include | Weather | 494 | 2021-11-19 | 29640 | keep | 0 | Nov | 2021 | 0.020188 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-11-19 10:42 | 2021-11-19 14:11 | 200 | 003:29 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M21111900069 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 209 | 2021-11-19 | 41800 | keep | 0 | Nov | 2021 | 0.02847 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-19 10:46 | 2021-11-19 15:45 | 60 | 004:59 | P | NO SE REPORTO CAUSA | 1 X 25 Y 1 X 15 EN CORTE DE LINEA | B21111900033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 299 | 2021-11-19 | 17940 | keep | 0 | Nov | 2021 | 0.012219 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2021-11-19 10:50 | 2021-11-19 12:16 | 10 | 001:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | R21111900019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 86 | 2021-11-19 | 860 | keep | 0 | Nov | 2021 | 0.00058574 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-11-19 11:09 | 2021-11-20 12:19 | 6 | 025:10 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR | C21111900090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1510 | 2021-11-19 | 9060 | keep | 0 | Nov | 2021 | 0.0061707 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-11-19 11:21 | 2021-11-19 12:04 | 12 | 000:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR TRANSFORMADOR PARA REPARAR SECUNDARIA | S21111900050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 43 | 2021-11-19 | 516 | keep | 0 | Nov | 2021 | 0.00035145 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2021-11-19 11:26 | 2021-11-19 16:50 | 45 | 005:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN C/L MAL TIEMPO | C21111900094 | New_Event | Bad Weather | Include | Include | Weather | 324 | 2021-11-19 | 14580 | keep | 0 | Nov | 2021 | 0.0099304 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2021-11-19 11:32 | 2021-11-19 14:24 | 60 | 002:52 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21111900023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2021-11-19 | 10320 | keep | 0 | Nov | 2021 | 0.0070289 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2021-11-19 11:50 | 2021-11-19 11:53 | 4369 | 000:03 | T | CABLE SOTERRADO AVERIADO | DISPARO PERSONAL LOCALIZANDO AVERIA SOTERRADA | C21111900097 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 3 | 2021-11-19 | 13107 | keep | 0 | Nov | 2021 | 0.0089271 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-11-19 11:53 | 2021-11-19 12:12 | 17 | 000:19 | P | CABLE SOTERRADO AVERIADO | 1 X 40 SMU 20 EN SU-1 SE REPARO CABLE SOTERRADO HACIA T-23 | C21111800180 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 19 | 2021-11-19 | 323 | keep | 0 | Nov | 2021 | 0.00021999 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2021-11-19 11:57 | 2021-11-19 11:58 | 6136 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE 1709-01 QUE LLEVA 1720-07 | S21111900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-19 | 6136 | keep | 0 | Nov | 2021 | 0.0041792 | 0.0041792 | Momentary | FALSE | FALSE | Not_TMED_Event | 6136
BAYAMON | 2021-11-19 12:06 | 2021-11-19 14:53 | 50 | 002:47 | P | NO SE REPORTO CAUSA | 2 X 80 EN C/L | S21111900085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 167 | 2021-11-19 | 8350 | keep | 0 | Nov | 2021 | 0.0056871 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-11-19 12:12 | 2021-11-19 12:14 | 4369 | 000:02 | T | CABLE SOTERRADO AVERIADO | DISPARO PERSONAL LOCALIZANDO AVERIA SOTERRADA | C21111900097 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 2 | 2021-11-19 | 8738 | keep | 0 | Nov | 2021 | 0.0059514 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-11-19 12:12 | 2021-11-19 16:30 | 50 | 004:18 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN CORTE DE LINEA SE REEMPLAZO AISLADOR | A21111900018 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 258 | 2021-11-19 | 12900 | keep | 0 | Nov | 2021 | 0.0087861 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-11-19 12:14 | 2021-11-19 21:59 | 17 | 009:45 | P | CABLE SOTERRADO AVERIADO | 1 X 40 SMU 20 EN SU-1 SE REPARO CABLE SOTERRADO HACIA T-23 | C21111800180 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 585 | 2021-11-19 | 9945 | keep | 0 | Nov | 2021 | 0.0067735 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
MAYAGÃœEZ | 2021-11-19 12:15 | 2021-11-19 14:45 | 60 | 002:30 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE RETIRO PARARRAYOS AVERIADO | M21111900051 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 150 | 2021-11-19 | 9000 | keep | 0 | Nov | 2021 | 0.0061299 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2021-11-19 12:21 | 2021-11-19 16:34 | 90 | 004:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN C/L MAL TIEMPO | C21111900106 | New_Event | Bad Weather | Include | Include | Weather | 253 | 2021-11-19 | 22770 | keep | 0 | Nov | 2021 | 0.015509 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
HUMACAO | 2021-11-19 12:22 | 2021-11-19 15:41 | 85 | 003:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 EN C/L REEMPLAZO TIGUERO | C21111900107 | New_Event | Wire Down | Include | Include | Equipment | 199 | 2021-11-19 | 16915 | keep | 0 | Nov | 2021 | 0.011521 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
HUMACAO | 2021-11-19 12:23 | 2021-11-19 18:32 | 14 | 006:09 | P | FUEGO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR POR SEGURIDAD CASA EXPLOTO | C21111900114 | New_Event | Fire | Include | Include | Public | 369 | 2021-11-19 | 5166 | keep | 0 | Nov | 2021 | 0.0035185 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2021-11-19 12:30 | 2021-11-19 13:40 | 50 | 001:10 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S21111900093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 70 | 2021-11-19 | 3500 | keep | 0 | Nov | 2021 | 0.0023838 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-11-19 12:46 | 2021-11-19 16:25 | 40 | 003:39 | P | DESGANCHE | 1 X 40 EN C/L | C21111900113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2021-11-19 | 8760 | keep | 0 | Nov | 2021 | 0.0059664 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-11-19 13:00 | 2021-11-19 13:01 | 225 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1303-05 Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1303-04 | S21111900000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-19 | 225 | keep | 0 | Nov | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-11-19 13:00 | 2021-11-19 13:01 | 870 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1303-05 Y SE CERRO POR SCADA. ADEMAS LLEVA LA CARGA DEL 1303-04 | S21111900000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-19 | 870 | keep | 0 | Nov | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2021-11-19 13:01 | 2021-11-19 16:52 | 200 | 003:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE IDENTIFICO PUENTE ABIERTO EN ALIMENTADOR | S21111900097 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 231 | 2021-11-19 | 46200 | keep | 0 | Nov | 2021 | 0.031467 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-11-19 13:01 | 2021-11-19 16:18 | 40 | 003:17 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA EL JOURNEYMAN INFORMO QUE NO ENCONTRO CAUSA QUE FUNDIERA EL FISIBLE | M21111900054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 197 | 2021-11-19 | 7880 | keep | 0 | Nov | 2021 | 0.005367 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-11-19 13:04 | 2021-11-19 16:49 | 60 | 003:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 1 X 50 EN CORTE DE LINEA SE RETIRO IGUANA | B21111900044 | New_Event |  |  | Include | Wildlife | 225 | 2021-11-19 | 13500 | keep | 0 | Nov | 2021 | 0.0091948 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2021-11-19 13:23 | 2021-11-19 15:16 | 8 | 001:53 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR REQUIERE DESGANCHE | M21111900057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2021-11-19 | 904 | keep | 0 | Nov | 2021 | 0.00061571 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-11-19 13:27 | 2021-11-19 14:16 | 60 | 000:49 | P | NO SE REPORTO CAUSA | 2 X 40 EN RISER | S21111900015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 49 | 2021-11-19 | 2940 | keep | 0 | Nov | 2021 | 0.0020024 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2021-11-19 13:32 | 2021-11-19 16:47 | 9 | 003:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR REEMPLAZO PORTAFUSIBLE | R21111900027 | New_Event | Cutout Failure | Include | Include | Equipment | 195 | 2021-11-19 | 1755 | keep | 0 | Nov | 2021 | 0.0011953 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2021-11-19 13:32 | 2021-11-19 17:23 | 80 | 003:51 | P | SOBRECARGA | 1 X 65 Y 1X15 EN CORTE DE LINEA POR SOBRE CARGA | A21111900025 | New_Event | Trip Due To Overload | Include | Include | Other | 231 | 2021-11-19 | 18480 | keep | 0 | Nov | 2021 | 0.012587 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2021-11-19 13:51 | 2021-11-19 17:00 | 90 | 003:09 | P | NO SE REPORTO CAUSA | 1 X 40 1 X 80 EN SU#4 NO SE ENCONTRO CAUSA | P21111900039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 189 | 2021-11-19 | 17010 | keep | 0 | Nov | 2021 | 0.011585 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2021-11-19 14:19 | 2021-11-19 17:34 | 45 | 003:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA | R21111900029 | New_Event | Cutout Failure | Include | Include | Equipment | 195 | 2021-11-19 | 8775 | keep | 0 | Nov | 2021 | 0.0059766 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
UTUADO | 2021-11-19 14:27 | 2021-11-19 19:29 | 10 | 005:02 | P | ESTRUCTURA AVERIADA | 2 X 15 EN TRANSFORMADOR SE REEMPLAZARON DOS POSTE PARTIDOS | A21111900030 | New_Event | Defective Pole | Include | Include | Equipment | 302 | 2021-11-19 | 3020 | keep | 0 | Nov | 2021 | 0.0020569 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-11-19 14:35 | 2021-11-19 17:30 | 6 | 002:55 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZAR POSTE SECUNDARIO PARTIDO POR POSTE 35' METAL | M21111900059 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 175 | 2021-11-19 | 1050 | keep | 0 | Nov | 2021 | 0.00071515 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-11-19 14:36 | 2021-11-20 10:29 | 4 | 019:53 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR | C21111900132 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1193 | 2021-11-19 | 4772 | keep | 0 | Nov | 2021 | 0.0032502 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-11-19 14:40 | 2021-11-19 14:41 | 4291 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1204-02 LLEVANDO 20% 1303-02 | S21111900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-19 | 4291 | keep | 0 | Nov | 2021 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
SAN JUAN | 2021-11-19 14:40 | 2021-11-19 14:41 | 487 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1204-02 LLEVANDO 20% 1303-02 | S21111900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-19 | 487 | keep | 0 | Nov | 2021 | 0.00033169 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
BARRANQUITAS | 2021-11-19 14:40 | 2021-11-19 14:41 | 3565 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21111900134 | New_Event |  |  | Include | Wildlife | 1 | 2021-11-19 | 3565 | keep | 0 | Nov | 2021 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
BARRANQUITAS | 2021-11-19 14:41 | 2021-11-19 20:20 | 100 | 005:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 80 EN C/L CRUCE POR GLOBO | C21111900136 | 1st_after_momentary |  |  | Include | Wildlife | 339 | 2021-11-19 | 33900 | keep | 0 | Nov | 2021 | 0.023089 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2021-11-19 14:47 | 2021-11-19 17:46 | 41 | 002:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | P21111900043 | New_Event | Bad Weather | Include | Include | Weather | 179 | 2021-11-19 | 7339 | keep | 0 | Nov | 2021 | 0.0049986 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
MAYAGÃœEZ | 2021-11-19 14:52 | 2021-11-19 18:12 | 30 | 003:20 | P | DESGANCHE | 1 X 15 EN DOS TRANSFORMADORES REQUIERE DESGANCHE | M21111900068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2021-11-19 | 6000 | keep | 0 | Nov | 2021 | 0.0040866 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-11-19 15:02 | 2021-11-20 11:01 | 3 | 019:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES | C21111900139 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1199 | 2021-11-19 | 3597 | keep | 0 | Nov | 2021 | 0.0024499 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
YAUCO | 2021-11-19 15:02 | 2021-11-19 18:11 | 65 | 003:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN RISER AVE CRUZO FASE | P21111900044 | New_Event |  |  | Include | Wildlife | 189 | 2021-11-19 | 12285 | keep | 0 | Nov | 2021 | 0.0083673 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
VEGA BAJA | 2021-11-19 15:11 | 2021-11-19 16:18 | 15 | 001:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21111900046 | New_Event | Secondary Wire Down | Include | Include | Equipment | 67 | 2021-11-19 | 1005 | keep | 0 | Nov | 2021 | 0.0006845 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-11-19 15:15 | 2021-11-19 16:25 | 200 | 001:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA POR SEGURIDAD DEBIDO A PUENTES PEGADOS EN CRUCETA Y SE CERRO PUENTE DE LINEA A CAJA DE XMR | S21111800486 | Additional_clients | Wire Down | Include | Include | Equipment | 70 | 2021-11-19 | 14000 | keep | 0 | Nov | 2021 | 0.0095353 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2021-11-19 15:26 | 2021-11-19 17:35 | 50 | 002:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA EN CORTE DE LINEA | P21111900047 | New_Event | Cutout Failure | Include | Include | Equipment | 129 | 2021-11-19 | 6450 | keep | 0 | Nov | 2021 | 0.0043931 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-19 15:33 | 2021-11-19 17:44 | 25 | 002:11 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21111900060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 131 | 2021-11-19 | 3275 | keep | 0 | Nov | 2021 | 0.0022306 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-11-19 15:55 | 2021-11-19 15:56 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21111900080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-19 | 3458 | keep | 0 | Nov | 2021 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
BAYAMON | 2021-11-19 15:57 | 2021-11-19 21:53 | 200 | 005:56 | P | OTRAS CAUSAS | SE ABRIO EN RISER HACIA CLIENTE PARA PODER CAMBIAR BASES DEL CONDOMINIO RITZ POR UNAS MAS ACTUALIZADAS YA QUE NO HAY FUSIBLES PARA LAS MISMAS. INFORMA SUPVR. ALVAREZ QUE INSPECCIONES TIENE CONOCIMIENTO Y SE LE FACTURARAN LOS TRABAJOS AL CONDOMINIO. | S21111900111 | New_Event | Other Causes | Include | Include | Other | 356 | 2021-11-19 | 71200 | keep | 0 | Nov | 2021 | 0.048494 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2021-11-19 15:57 | 2021-11-19 17:04 | 1 | 001:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR REEMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | R21111900031 | New_Event | Cutout Failure | Include | Include | Equipment | 67 | 2021-11-19 | 67 | keep | 0 | Nov | 2021 | 4.5633e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-11-19 16:09 | 2021-11-19 16:35 | 10 | 000:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO T-5 PARA RETIRAR PERRO MUERTO POR CONTACTO CON BARRA DE PEDESTAL Y COLOCAR TAPA DE PEDESTAL EN SU SITIO. | R21111900030 | New_Event |  |  | Include | Wildlife | 26 | 2021-11-19 | 260 | keep | 0 | Nov | 2021 | 0.00017708 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-19 16:32 | 2021-11-19 17:35 | 12 | 001:03 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21111900058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2021-11-19 | 756 | keep | 0 | Nov | 2021 | 0.00051491 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-11-19 16:43 | 2021-11-19 18:35 | 75 | 001:52 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | B21111900066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2021-11-19 | 8400 | keep | 0 | Nov | 2021 | 0.0057212 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2021-11-19 16:52 | 2021-11-19 17:39 | 225 | 000:47 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO EN ALIMENTADOR 1303-05 ABRIENDO MACHETES AFECTANDO 1303-04 EN SU TOTALIDAD POR MEDIO DEL GOI SJ-2111190002A | S21111900097 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 47 | 2021-11-19 | 10575 | keep | 0 | Nov | 2021 | 0.0072026 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-11-19 16:52 | 2021-11-19 17:39 | 400 | 000:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO EN ALIMENTADOR ABRIENDO MACHETES DEL 1303-05 AFECTANDO 1303-04 EN SU TOTALIDAD POR MEDIO DEL GOI SJ-2111190002A | S21111900097 | Additional_clients | Wire Down | Include | Include | Equipment | 47 | 2021-11-19 | 18800 | keep | 0 | Nov | 2021 | 0.012805 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-11-19 16:53 | 2021-11-19 18:28 | 12 | 001:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REEMPLAZAR SECUNDARIA | C21111900186 | New_Event | Secondary Wire Down | Include | Include | Equipment | 95 | 2021-11-19 | 1140 | keep | 0 | Nov | 2021 | 0.00077645 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-11-19 16:59 | 2021-11-20 13:04 | 1 | 020:05 | P | SECUNDARIA/DESGANCHE | SE REALIZO DESGANCHE Y SE REPARO 150 PIES DE LINEA SECUNDARIA | M21111900087 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1205 | 2021-11-19 | 1205 | keep | 0 | Nov | 2021 | 0.00082072 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-19 17:11 | 2021-11-19 19:01 | 40 | 001:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA | B21111900072 | New_Event | Cutout Failure | Include | Include | Equipment | 110 | 2021-11-19 | 4400 | keep | 0 | Nov | 2021 | 0.0029968 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-11-19 17:32 | 2021-11-19 21:02 | 75 | 003:30 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21111900074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 210 | 2021-11-19 | 15750 | keep | 0 | Nov | 2021 | 0.010727 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2021-11-19 17:40 | 2021-11-19 19:24 | 20 | 001:44 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 75KVA CON PROBLEMAS DE VOLTAJE | S21111900049 | New_Event | Service Transformer Failure | Include | Include | Equipment | 104 | 2021-11-19 | 2080 | keep | 0 | Nov | 2021 | 0.0014167 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-11-19 17:46 | 2021-11-19 17:47 | 635 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21111900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-19 | 635 | keep | 0 | Nov | 2021 | 0.0004325 | 0.0004325 | Momentary | FALSE | FALSE | Not_TMED_Event | 635
VEGA BAJA | 2021-11-19 18:15 | 2021-11-19 18:46 | 15 | 000:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21111900070 | New_Event | Secondary Wire Down | Include | Include | Equipment | 31 | 2021-11-19 | 465 | keep | 0 | Nov | 2021 | 0.00031671 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-11-19 18:21 | 2021-11-19 20:07 | 100 | 001:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REALIZO DESGANCHE Y SE LEVANTO CONDUCTOR EN EL SUELO. SE ABRIO MACHETES PARA PODER CERRAR PUENTE ABIERTO. SOLO ESTABA AFECTADO DESDE AYER XMR ALUMBRADO | S21111800474 | New_Event | Wire Down | Include | Include | Equipment | 106 | 2021-11-19 | 10600 | keep | 0 | Nov | 2021 | 0.0072196 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-11-19 18:23 | 2021-11-19 18:25 | 320 | 000:02 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL | B21111900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-11-19 | 640 | keep | 0 | Nov | 2021 | 0.0004359 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2021-11-19 18:25 | 2021-11-19 20:58 | 40 | 002:33 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21111900077 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 153 | 2021-11-19 | 6120 | keep | 0 | Nov | 2021 | 0.0041683 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-11-19 18:30 | 2021-11-19 22:31 | 35 | 004:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA VEHICULO CRUZO LINEAS | A21111900035 | New_Event |  |  | Include | Wildlife | 241 | 2021-11-19 | 8435 | keep | 0 | Nov | 2021 | 0.005745 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2021-11-19 18:36 | 2021-11-19 21:03 | 80 | 002:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE ABRIO PUENTE PARA SECCIONALIZAR AVERIA DE LINEA PARTIDA | A21111900036 | New_Event | Wire Down | Include | Include | Equipment | 147 | 2021-11-19 | 11760 | keep | 0 | Nov | 2021 | 0.0080097 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2021-11-19 18:47 | 2021-11-20 12:40 | 10 | 017:53 | P | PARARRAYOS DEFECTUOSO | 1 X 8 EN TRANSFORMADOR SE REEMPLAZO PARARRAYO | C21111900157 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1073 | 2021-11-19 | 10730 | keep | 0 | Nov | 2021 | 0.0073082 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-11-19 19:30 | 2021-11-19 21:20 | 15 | 001:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21111900098 | New_Event | Secondary Wire Down | Include | Include | Equipment | 110 | 2021-11-19 | 1650 | keep | 0 | Nov | 2021 | 0.0011238 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-11-19 19:33 | 2021-11-20 10:38 | 16 | 015:05 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21111900162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 905 | 2021-11-19 | 14480 | keep | 0 | Nov | 2021 | 0.0098623 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CANOVANAS | 2021-11-19 20:01 | 2021-11-19 23:53 | 1648 | 003:52 | T | DESCONECTIVO DEFECTUOSO | RECERRO INTERRUPTOR 3 VECES QUEDO FUERA SE REEMPLAZO MACHETE QUEMADO Y SE DEJO AREA SECCIONALIZADA CERRADO POR CONTROL | R21111900036 | New_Event | Switch Failure | Include | Include | Equipment | 232 | 2021-11-19 | 382336 | keep | 0 | Nov | 2021 | 0.26041 | 0.0011224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1648
BAYAMON | 2021-11-19 20:10 | 2021-11-20 10:44 | 6 | 014:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21111900087 | New_Event | Secondary Wire Down | Include | Include | Equipment | 874 | 2021-11-19 | 5244 | keep | 0 | Nov | 2021 | 0.0035717 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-11-19 20:12 | 2021-11-20 09:39 | 100 | 013:27 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C21111900165 | New_Event | Vegetation Contact | Include | Include | Vegetation | 807 | 2021-11-19 | 80700 | keep | 0 | Nov | 2021 | 0.054964 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2021-11-19 20:48 | 2021-11-19 20:49 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21111900105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-19 | 1192 | keep | 0 | Nov | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2021-11-19 21:01 | 2021-11-20 18:00 | 1 | 020:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN RISER ROEDOR CRUZO LINEAS | M21111900106 | New_Event |  |  | Include | Wildlife | 1259 | 2021-11-19 | 1259 | keep | 0 | Nov | 2021 | 0.0008575 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-11-19 21:03 | 2021-11-20 17:19 | 100 | 020:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | A21111900036 | Additional_clients | Wire Down | Include | Include | Equipment | 1216 | 2021-11-19 | 121600 | keep | 0 | Nov | 2021 | 0.082821 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-11-19 21:35 | 2021-11-19 22:39 | 8 | 001:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21111900095 | New_Event | Secondary Wire Down | Include | Include | Equipment | 64 | 2021-11-19 | 512 | keep | 0 | Nov | 2021 | 0.00034872 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-11-19 21:35 | 2021-11-19 22:16 | 8 | 000:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21111900045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 41 | 2021-11-19 | 328 | keep | 0 | Nov | 2021 | 0.0002234 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2021-11-19 21:44 | 2021-11-19 21:45 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21111900110 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-19 | 1192 | keep | 0 | Nov | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
CANOVANAS | 2021-11-19 22:06 | 2021-11-19 22:07 | 2039 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R21111900048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-19 | 2039 | keep | 0 | Nov | 2021 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
CANOVANAS | 2021-11-19 22:09 | 2021-11-19 22:11 | 2708 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | R21111900049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-19 | 5416 | keep | 0 | Nov | 2021 | 0.0036888 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
SAN JUAN | 2021-11-19 23:06 | 2021-11-20 08:54 | 40 | 009:48 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER | S21111900156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 588 | 2021-11-19 | 23520 | keep | 0 | Nov | 2021 | 0.016019 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-11-19 23:15 | 2021-11-20 13:04 | 100 | 013:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CONDUCTOR EN EL SUELO | S21111900157 | New_Event | Wire Down | Include | Include | Equipment | 829 | 2021-11-19 | 82900 | keep | 0 | Nov | 2021 | 0.056463 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-11-19 23:18 | 2021-11-19 23:19 | 810 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21111900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-19 | 810 | keep | 0 | Nov | 2021 | 0.00055169 | 0.00055169 | Momentary | FALSE | FALSE | Not_TMED_Event | 810
MAYAGÃœEZ | 2021-11-19 23:18 | 2021-11-19 23:19 | 1235 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21111900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-19 | 1235 | keep | 0 | Nov | 2021 | 0.00084115 | 0.00084115 | Momentary | FALSE | FALSE | Not_TMED_Event | 1235
MAYAGÃœEZ | 2021-11-19 23:18 | 2021-11-19 23:19 | 93 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21111900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-19 | 93 | keep | 0 | Nov | 2021 | 6.3342e-05 | 6.3342e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 93
MAYAGÃœEZ | 2021-11-19 23:18 | 2021-11-19 23:19 | 1825 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21111900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-19 | 1825 | keep | 0 | Nov | 2021 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
MAYAGÃœEZ | 2021-11-19 23:18 | 2021-11-19 23:19 | 3230 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21111900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-19 | 3230 | keep | 0 | Nov | 2021 | 0.0021999 | 0.0021999 | Momentary | FALSE | FALSE | Not_TMED_Event | 3230
BAYAMON | 2021-11-19 23:25 | 2021-11-20 10:33 | 15 | 011:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA EN TRANSFORMADOR | S21111900159 | New_Event | Wire Down | Include | Include | Equipment | 668 | 2021-11-19 | 10020 | keep | 0 | Nov | 2021 | 0.0068246 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-11-19 23:30 | 2021-11-19 23:31 | 2708 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R21111900056 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-19 | 2708 | keep | 0 | Nov | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2021-11-19 23:53 | 2021-11-20 00:30 | 16 | 000:37 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO Y SE DEJO AREA SECCIONALIZADA PARA PATRULLAR EN LA MAÃ‘ANA SE CERRO MACHETES | R21111900036 | Partial_restoration | Switch Failure | Include | Include | Equipment | 37 | 2021-11-19 | 592 | keep | 0 | Nov | 2021 | 0.00040321 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-11-19 23:53 | 2021-11-20 11:33 | 50 | 011:40 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21111900089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 700 | 2021-11-19 | 35000 | keep | 0 | Nov | 2021 | 0.023838 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-11-20 00:30 | 2021-11-20 00:32 | 1648 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR PERSONAL NORMALIZANDO GOI SJ211119-50 SE VERIFICO PERSONAL FUERA CERRADO POR CONTROL | R21112000004 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2021-11-20 | 3296 | keep | 0 | Nov | 2021 | 0.0022449 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2021-11-20 00:32 | 2021-11-20 18:07 | 3 | 017:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO CERRO MACHETES Y NORMALIZO CARGA TRANSFERIDA AL 2402-02 | R21112000055 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1055 | 2021-11-20 | 3165 | keep | 0 | Nov | 2021 | 0.0021557 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2021-11-20 00:32 | 2021-11-20 00:57 | 16 | 000:25 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO Y SE DEJO AREA SECCIONALIZADA PARA PATRULLAR EN LA MAÃ‘ANA SE CERRO MACHETES | R21111900036 | Partial_restoration | Switch Failure | Include | Include | Equipment | 25 | 2021-11-20 | 400 | keep | 0 | Nov | 2021 | 0.00027244 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-11-20 01:42 | 2021-11-20 09:53 | 40 | 008:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS | A21112000002 | New_Event | Wire Down | Include | Include | Equipment | 491 | 2021-11-20 | 19640 | keep | 0 | Nov | 2021 | 0.013377 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-11-20 01:43 | 2021-11-20 01:44 | 2708 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | R21112000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-20 | 2708 | keep | 0 | Nov | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2021-11-20 01:44 | 2021-11-20 09:11 | 100 | 007:27 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R21112000009 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 447 | 2021-11-20 | 44700 | keep | 0 | Nov | 2021 | 0.030445 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2021-11-20 03:59 | 2021-11-20 04:00 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21112000004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-20 | 1192 | keep | 0 | Nov | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
CANOVANAS | 2021-11-20 04:49 | 2021-11-20 12:16 | 100 | 007:27 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21112000010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 447 | 2021-11-20 | 44700 | keep | 0 | Nov | 2021 | 0.030445 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-11-20 05:49 | 2021-11-20 11:47 | 60 | 005:58 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21112000005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 358 | 2021-11-20 | 21480 | keep | 0 | Nov | 2021 | 0.01463 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2021-11-20 05:50 | 2021-11-20 10:55 | 80 | 005:05 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21112000006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 305 | 2021-11-20 | 24400 | keep | 0 | Nov | 2021 | 0.016619 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2021-11-20 06:01 | 2021-11-20 06:02 | 1894 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21112000013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-20 | 1894 | keep | 0 | Nov | 2021 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
CAGUAS | 2021-11-20 06:33 | 2021-11-20 06:34 | 918 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE AVE | C21112000000 | New_Event |  |  | Include | Wildlife | 1 | 2021-11-20 | 918 | keep | 0 | Nov | 2021 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2021-11-20 06:34 | 2021-11-20 12:20 | 3 | 005:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | C21112000034 | New_Event |  |  | Include | Wildlife | 346 | 2021-11-20 | 1038 | keep | 0 | Nov | 2021 | 0.00070698 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-11-20 07:06 | 2021-11-20 07:07 | 3597 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO 1719-15 Y SE CERRO POR SCADA LLEVA 50% DEL 9405-05 | B21112000000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-11-20 | 3597 | keep | 0 | Nov | 2021 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2021-11-20 07:06 | 2021-11-20 07:07 | 1606 | 000:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO 1719-15 Y SE CERRO POR SCADA LLEVA 50% DEL 94-5-05 | B21112000000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-11-20 | 1606 | keep | 0 | Nov | 2021 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
BAYAMON | 2021-11-20 07:07 | 2021-11-20 12:43 | 300 | 005:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 140 EN CORTE DE LINEA SE REMPLAZO 2 CAJAS PRIMARIAS | B21111900000 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 336 | 2021-11-20 | 100800 | keep | 0 | Nov | 2021 | 0.068654 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2021-11-20 07:20 | 2021-11-20 11:38 | 130 | 004:18 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R21112000016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 258 | 2021-11-20 | 33540 | keep | 0 | Nov | 2021 | 0.022844 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
BAYAMON | 2021-11-20 07:29 | 2021-11-20 13:46 | 50 | 006:17 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B21112000021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 377 | 2021-11-20 | 18850 | keep | 0 | Nov | 2021 | 0.012839 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-11-20 07:32 | 2021-11-20 08:14 | 1709 | 000:42 | T | DESGANCHE | DISPARO SE RETIRO BAMBUA SOBRE LINEAS | C21112000011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 42 | 2021-11-20 | 71778 | keep | 0 | Nov | 2021 | 0.048888 | 0.001164 | Sustained | FALSE | FALSE | Not_TMED_Event | 1709
BARRANQUITAS | 2021-11-20 07:32 | 2021-11-20 09:28 | 90 | 001:56 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21112000010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2021-11-20 | 10440 | keep | 0 | Nov | 2021 | 0.0071106 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
ARECIBO | 2021-11-20 07:52 | 2021-11-20 14:45 | 1 | 006:53 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER EL JOURNEYMAN NO ENCONTRO CAUSA PARA EL FUSIBLE FUNDIDO | A21112000011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 413 | 2021-11-20 | 413 | keep | 0 | Nov | 2021 | 0.00028129 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-20 07:58 | 2021-11-20 11:21 | 100 | 003:23 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN PROVISIONAL Y 1 X 30 EN RISER | B21112000026 | New_Event | UG Cable Fault | Include | Include | Equipment | 203 | 2021-11-20 | 20300 | keep | 0 | Nov | 2021 | 0.013826 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-11-20 08:15 | 2021-11-20 18:06 | 1 | 009:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REALIZO DESGANCHE Y SE REPARO LINEA PARTIDA | M21112000009 | New_Event | Wire Down | Include | Include | Equipment | 591 | 2021-11-20 | 591 | keep | 0 | Nov | 2021 | 0.00040253 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2021-11-20 08:17 | 2021-11-20 08:18 | 1945 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21112000004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-20 | 1945 | keep | 0 | Nov | 2021 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
BAYAMON | 2021-11-20 08:20 | 2021-11-20 08:21 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21112000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-20 | 1746 | keep | 0 | Nov | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
BAYAMON | 2021-11-20 08:21 | 2021-11-20 18:55 | 65 | 010:34 | P | NO SE REPORTO CAUSA | 1 X 40 Y 1 X 80 EN C/L | B21112000028 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 634 | 2021-11-20 | 41210 | keep | 0 | Nov | 2021 | 0.028068 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CANOVANAS | 2021-11-20 08:54 | 2021-11-20 08:55 | 4188 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21112000024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-20 | 4188 | keep | 0 | Nov | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
BAYAMON | 2021-11-20 08:58 | 2021-11-20 08:59 | 1533 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 1709-05 | S21112000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-20 | 1533 | keep | 0 | Nov | 2021 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
BAYAMON | 2021-11-20 08:58 | 2021-11-20 08:59 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1709-03 | S21112000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-20 | 2364 | keep | 0 | Nov | 2021 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
BAYAMON | 2021-11-20 09:52 | 2021-11-20 18:56 | 82 | 009:04 | P | DESGANCHE | 2 X 100 EN C/L SE REMPLAZO CAJA Y SE REALIZO DESGANCHE | S21112000009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 544 | 2021-11-20 | 44608 | keep | 0 | Nov | 2021 | 0.030382 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
BAYAMON | 2021-11-20 09:58 | 2021-11-20 10:37 | 6 | 000:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21112000036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 39 | 2021-11-20 | 234 | keep | 0 | Nov | 2021 | 0.00015938 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2021-11-20 10:09 | 2021-11-20 10:22 | 10 | 000:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA AJUSTAR BUSHING SECUNDARIO | P21112000011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 13 | 2021-11-20 | 130 | keep | 0 | Nov | 2021 | 8.8542e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-20 10:15 | 2021-11-20 13:14 | 36 | 002:59 | P | NO SE REPORTO CAUSA | 3 X 20 EN SU-4A | B21112000038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 179 | 2021-11-20 | 6444 | keep | 0 | Nov | 2021 | 0.004389 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
FAJARDO | 2021-11-20 10:23 | 2021-11-20 12:33 | 3 | 002:10 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR | R21112000004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2021-11-20 | 390 | keep | 0 | Nov | 2021 | 0.00026563 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-11-20 10:30 | 2021-11-20 11:26 | 6 | 000:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR TRANSFORMADOR Y SE REPARA SECUNDARIA | B21111900064 | New_Event | Secondary Wire Down | Include | Include | Equipment | 56 | 2021-11-20 | 336 | keep | 0 | Nov | 2021 | 0.00022885 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-11-20 10:32 | 2021-11-20 16:11 | 20 | 005:39 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B21112000040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 339 | 2021-11-20 | 6780 | keep | 0 | Nov | 2021 | 0.0046178 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-11-20 10:45 | 2021-11-20 13:29 | 1 | 002:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN RISER CRUCE CON REPTIL | R21112000031 | New_Event |  |  | Include | Wildlife | 164 | 2021-11-20 | 164 | keep | 0 | Nov | 2021 | 0.0001117 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-11-20 10:45 | 2021-11-20 11:19 | 4 | 000:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO NEUTRAL ABIERTO | C21112000037 | New_Event | Wire Down | Include | Include | Equipment | 34 | 2021-11-20 | 136 | keep | 0 | Nov | 2021 | 9.2629e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-11-20 10:57 | 2021-11-20 12:05 | 1 | 001:08 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN TRANSFORMADOR SE DESGANCHO EN LINEAS SECUNDARIAS Y SE AJUSTO VOLTAJE DE TRANSFORMADOR | M21112000017 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 68 | 2021-11-20 | 68 | keep | 0 | Nov | 2021 | 4.6314e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-20 10:58 | 2021-11-20 16:53 | 1 | 005:55 | P | NO SE REPORTO CAUSA | 1 X 15 EN C/L | B21112000046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 355 | 2021-11-20 | 355 | keep | 0 | Nov | 2021 | 0.00024179 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-20 11:00 | 2021-11-20 11:49 | 8 | 000:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO PM Y SE REPARO BARRAS EN PEDESTAL | B21111900035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 49 | 2021-11-20 | 392 | keep | 0 | Nov | 2021 | 0.00026699 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-11-20 11:04 | 2021-11-20 15:31 | 10 | 004:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZARON BAJANTES QUEMADOS | C21112000032 | New_Event | Wire Down | Include | Include | Equipment | 267 | 2021-11-20 | 2670 | keep | 0 | Nov | 2021 | 0.0018185 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-11-20 11:12 | 2021-11-20 14:03 | 1 | 002:51 | P | OTRAS CAUSAS | 1 X 25 EN RISER PROBLEMA DEL CLIENTE | C21111200040 | New_Event | Other Causes | Include | Include | Other | 171 | 2021-11-20 | 171 | keep | 0 | Nov | 2021 | 0.00011647 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-11-20 11:18 | 2021-11-20 11:19 | 1979 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21112000014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-20 | 1979 | keep | 0 | Nov | 2021 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
BAYAMON | 2021-11-20 11:21 | 2021-11-20 21:11 | 40 | 009:50 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL AEREO HACIA T-36, AVERIA EN T-37 | B21112000053 | New_Event | UG Cable Fault | Include | Include | Equipment | 590 | 2021-11-20 | 23600 | keep | 0 | Nov | 2021 | 0.016074 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2021-11-20 11:23 | 2021-11-20 11:49 | 4 | 000:26 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REEMPLAZARON BARRAS | C21112000042 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 26 | 2021-11-20 | 104 | keep | 0 | Nov | 2021 | 7.0834e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2021-11-20 11:33 | 2021-11-20 15:51 | 64 | 004:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZARON BAJANTES QUEMADOS | R21111200034 | New_Event | Wire Down | Include | Include | Equipment | 258 | 2021-11-20 | 16512 | keep | 0 | Nov | 2021 | 0.011246 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
VEGA BAJA | 2021-11-20 11:48 | 2021-11-20 13:34 | 652 | 001:46 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7800 | B21112000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 106 | 2021-11-20 | 69112 | keep | 0 | Nov | 2021 | 0.047072 | 0.00044407 | Sustained | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2021-11-20 11:48 | 2021-11-20 13:34 | 2704 | 001:46 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7800 | B21112000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 106 | 2021-11-20 | 286624 | keep | 0 | Nov | 2021 | 0.19522 | 0.0018417 | Sustained | FALSE | FALSE | Not_TMED_Event | 2704
CANOVANAS | 2021-11-20 11:55 | 2021-11-20 15:35 | 66 | 003:40 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REMOVIO PARARRAYOS DEFECTUOSO | R21112000036 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 220 | 2021-11-20 | 14520 | keep | 0 | Nov | 2021 | 0.0098895 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
BAYAMON | 2021-11-20 12:10 | 2021-11-20 14:56 | 1 | 002:46 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21112000060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2021-11-20 | 166 | keep | 0 | Nov | 2021 | 0.00011306 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-11-20 12:11 | 2021-11-20 12:50 | 12 | 000:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO TRANSFORMADOR Y RETORNO TRANSFORMADOR A BASE IMPACTADO POR AUTO | C21111500075 | New_Event |  |  | Include | Wildlife | 39 | 2021-11-20 | 468 | keep | 0 | Nov | 2021 | 0.00031875 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-11-20 12:15 | 2021-11-20 12:16 | 11 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21112000018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-20 | 11 | keep | 0 | Nov | 2021 | 7.492e-06 | 7.492e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 11
PONCE | 2021-11-20 12:15 | 2021-11-20 14:30 | 10 | 002:15 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRE TRANSFORMADOR PARA REMPLAZO DE POSTE SECUNDARIO | P21112000019 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 135 | 2021-11-20 | 1350 | keep | 0 | Nov | 2021 | 0.00091948 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-20 12:31 | 2021-11-20 17:42 | 60 | 005:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L AVE | S21112000016 | New_Event |  |  | Include | Wildlife | 311 | 2021-11-20 | 18660 | keep | 0 | Nov | 2021 | 0.012709 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2021-11-20 12:41 | 2021-11-20 14:25 | 20 | 001:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN RISER | A21112000031 | New_Event | Wire Down | Include | Include | Equipment | 104 | 2021-11-20 | 2080 | keep | 0 | Nov | 2021 | 0.0014167 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2021-11-20 12:45 | 2021-11-20 17:54 | 50 | 005:09 | P | HERRAJE ROTO O PODRIDO | SE ABRIO CORTE DE LINEA PARA REEMPLAZAR HOT CLAMP | C21112000050 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 309 | 2021-11-20 | 15450 | keep | 0 | Nov | 2021 | 0.010523 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-11-20 12:53 | 2021-11-20 17:02 | 125 | 004:09 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA EL FOREMAN NO ENCONTRO CAUSA PARA EL FUSIBLE FUNDIDO | A21112000032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 249 | 2021-11-20 | 31125 | keep | 0 | Nov | 2021 | 0.021199 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2021-11-20 13:04 | 2021-11-20 13:57 | 525 | 000:53 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1329-03 LLEVANDO LA CARGA DEL 1329-04 PARA LEVANTAR CONDUCTOR Y DE UNA VEZ REEMPLAZAR MACHETES EN MAL ESTADO | S21112000157 | Additional_clients | Wire Down | Include | Include | Equipment | 53 | 2021-11-20 | 27825 | keep | 0 | Nov | 2021 | 0.018951 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-20 13:04 | 2021-11-20 13:57 | 45 | 000:53 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1329-03 LLEVANDO LA CARGA DEL 1329-04 PARA LEVANTAR CONDUCTOR Y DE UNA VEZ REEMPLAZAR MACHETES EN MAL ESTADO | S21112000157 | New_Event | Wire Down | Include | Include | Equipment | 53 | 2021-11-20 | 2385 | keep | 0 | Nov | 2021 | 0.0016244 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2021-11-20 13:09 | 2021-11-20 16:30 | 15 | 003:21 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE | M21112000020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2021-11-20 | 3015 | keep | 0 | Nov | 2021 | 0.0020535 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-11-20 13:17 | 2021-11-20 15:46 | 100 | 002:29 | P | DESGANCHE | 1 X 50 Y 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21112000021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2021-11-20 | 14900 | keep | 0 | Nov | 2021 | 0.010148 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-11-20 13:36 | 2021-11-20 14:52 | 10 | 001:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S21112000013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 76 | 2021-11-20 | 760 | keep | 0 | Nov | 2021 | 0.00051763 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-20 13:38 | 2021-11-20 16:51 | 16 | 003:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B21112000085 | New_Event | Secondary Wire Down | Include | Include | Equipment | 193 | 2021-11-20 | 3088 | keep | 0 | Nov | 2021 | 0.0021032 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2021-11-20 13:39 | 2021-11-20 15:50 | 25 | 002:11 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B21112000089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 131 | 2021-11-20 | 3275 | keep | 0 | Nov | 2021 | 0.0022306 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-11-20 13:40 | 2021-11-20 18:16 | 40 | 004:36 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REPARO AISLADOR AVERIADO EN VIVO | S21112000023 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 276 | 2021-11-20 | 11040 | keep | 0 | Nov | 2021 | 0.0075193 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2021-11-20 13:51 | 2021-11-20 16:56 | 95 | 003:05 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA RETIRO RAMAS SOBRE LINEAS Y REEMPLAZO CAJA PRIMARIA QUEMADA | R21112000040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2021-11-20 | 17575 | keep | 0 | Nov | 2021 | 0.01197 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
HUMACAO | 2021-11-20 14:01 | 2021-11-20 14:08 | 1089 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21112000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-11-20 | 7623 | keep | 0 | Nov | 2021 | 0.005192 | 0.00074171 | Sustained | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2021-11-20 14:01 | 2021-11-20 14:08 | 3896 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21112000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-11-20 | 27272 | keep | 0 | Nov | 2021 | 0.018575 | 0.0026535 | Sustained | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2021-11-20 14:01 | 2021-11-20 14:08 | 1467 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21112000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-11-20 | 10269 | keep | 0 | Nov | 2021 | 0.0069942 | 0.00099917 | Sustained | FALSE | FALSE | Not_TMED_Event | 1467
AGUADILLA | 2021-11-20 14:13 | 2021-11-20 19:30 | 75 | 005:17 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21112000026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 317 | 2021-11-20 | 23775 | keep | 0 | Nov | 2021 | 0.016193 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2021-11-20 14:18 | 2021-11-20 15:37 | 1089 | 001:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21112000000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 79 | 2021-11-20 | 86031 | keep | 0 | Nov | 2021 | 0.058595 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-11-20 14:18 | 2021-11-20 15:37 | 3896 | 001:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21112000000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 79 | 2021-11-20 | 307784 | keep | 0 | Nov | 2021 | 0.20963 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-11-20 14:18 | 2021-11-20 15:37 | 1467 | 001:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21112000000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 79 | 2021-11-20 | 115893 | keep | 0 | Nov | 2021 | 0.078934 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-11-20 14:20 | 2021-11-20 14:40 | 12 | 000:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P21112000008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 20 | 2021-11-20 | 240 | keep | 0 | Nov | 2021 | 0.00016346 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2021-11-20 14:27 | 2021-11-20 16:14 | 100 | 001:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE RETIRO TENSOR PARTIDO | R21112000042 | New_Event |  |  | Include | Wildlife | 107 | 2021-11-20 | 10700 | keep | 0 | Nov | 2021 | 0.0072877 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2021-11-20 14:57 | 2021-11-20 20:04 | 57 | 005:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ZAFADO EN CORTE DE LINEA | P21112000029 | New_Event | Wire Down | Include | Include | Equipment | 307 | 2021-11-20 | 17499 | keep | 0 | Nov | 2021 | 0.011918 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
CAGUAS | 2021-11-20 15:33 | 2021-11-20 18:01 | 90 | 002:28 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21112000087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2021-11-20 | 13320 | keep | 0 | Nov | 2021 | 0.0090722 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
VEGA BAJA | 2021-11-20 15:35 | 2021-11-20 15:36 | 1859 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 9207-09 | B21112000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-20 | 1859 | keep | 0 | Nov | 2021 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2021-11-20 15:35 | 2021-11-20 15:36 | 7 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 9207-08 | B21112000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-20 | 7 | keep | 0 | Nov | 2021 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2021-11-20 15:41 | 2021-11-20 16:55 | 50 | 001:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R21112000053 | New_Event |  |  | Include | Wildlife | 74 | 2021-11-20 | 3700 | keep | 0 | Nov | 2021 | 0.0025201 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-11-20 15:43 | 2021-11-20 18:10 | 10 | 002:27 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR AVERIADO 75KVA POR 75KVA | S21112000029 | New_Event | Service Transformer Failure | Include | Include | Equipment | 147 | 2021-11-20 | 1470 | keep | 0 | Nov | 2021 | 0.0010012 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-20 16:10 | 2021-11-20 16:33 | 6 | 000:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21111900040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 23 | 2021-11-20 | 138 | keep | 0 | Nov | 2021 | 9.3991e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-11-20 16:15 | 2021-11-20 20:34 | 4 | 004:19 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON BUSHING EN MAL ESTADO Y ESCAPE DE ACEITE DE 37 KVA POR LA MISMA CAPACIDAD Y SE REMPLAZO LINEA SECUNDARIA AVERIADA | A21112000022 | New_Event | Service Transformer Failure | Include | Include | Equipment | 259 | 2021-11-20 | 1036 | keep | 0 | Nov | 2021 | 0.00070561 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-11-20 16:21 | 2021-11-21 09:42 | 60 | 017:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M21112000038 | New_Event | Cutout Failure | Include | Include | Equipment | 1041 | 2021-11-20 | 62460 | keep | 0 | Nov | 2021 | 0.042541 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2021-11-20 16:34 | 2021-11-20 18:55 | 1089 | 002:21 | S | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA A XMR 2803 PARA SECCIONALIZAR PUENTE ABIERTO EN CARR 191 KM 0.5 DE LINEA 3000 JUNCOS @ RIO BLANCO | C21112000122 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 141 | 2021-11-20 | 153549 | keep | 0 | Nov | 2021 | 0.10458 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-11-20 16:34 | 2021-11-20 18:55 | 3896 | 002:21 | S | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA A XMR 2803 PARA SECCIONALIZAR PUENTE ABIERTO EN CARR 191 KM 0.5 DE LINEA 3000 JUNCOS @ RIO BLANCO | C21112000122 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 141 | 2021-11-20 | 549336 | keep | 0 | Nov | 2021 | 0.37415 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-11-20 16:34 | 2021-11-20 18:55 | 1467 | 002:21 | S | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA A XMR 2803 PARA SECCIONALIZAR PUENTE ABIERTO EN CARR 191 KM 0.5 DE LINEA 3000 JUNCOS @ RIO BLANCO | C21112000122 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 141 | 2021-11-20 | 206847 | keep | 0 | Nov | 2021 | 0.14088 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2021-11-20 16:43 | 2021-11-20 17:32 | 1 | 000:49 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA REEMPLAZO PARARRAYO Y CAJA PRIMARIA QUEMADA | R21112000061 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 49 | 2021-11-20 | 49 | keep | 0 | Nov | 2021 | 3.3374e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-11-20 16:50 | 2021-11-20 18:00 | 10 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P21112000025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2021-11-20 | 700 | keep | 0 | Nov | 2021 | 0.00047677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-11-20 17:42 | 2021-11-20 17:55 | 553 | 000:13 | P | NO SE REPORTO CAUSA | DISPARO 1529-15 LLEVANDO 30% DEL 1346-02 Y SE CERRO POR SCADA | S21112000033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2021-11-20 | 7189 | keep | 0 | Nov | 2021 | 0.0048964 | 0.00037665 | Sustained | FALSE | FALSE | Not_TMED_Event | 553
BAYAMON | 2021-11-20 17:42 | 2021-11-20 17:55 | 1802 | 000:13 | T | NO SE REPORTO CAUSA | DISPARO 1529-15 LLEVANDO 30% DEL 1346-02. SE VERIFICO PERSONAL FUERA EN ORDEN 23 | S21112000033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2021-11-20 | 23426 | keep | 0 | Nov | 2021 | 0.015955 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
VEGA BAJA | 2021-11-20 17:50 | 2021-11-20 19:18 | 1 | 001:28 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B21112000099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2021-11-20 | 88 | keep | 0 | Nov | 2021 | 5.9936e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-20 18:10 | 2021-11-20 18:11 | 6481 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21112000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-20 | 6481 | keep | 0 | Nov | 2021 | 0.0044142 | 0.0044142 | Momentary | FALSE | FALSE | Not_TMED_Event | 6481
SAN JUAN | 2021-11-20 18:33 | 2021-11-21 12:10 | 40 | 017:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA Y SE REPARO PUENTE | S21112000052 | New_Event | Wire Down | Include | Include | Equipment | 1057 | 2021-11-20 | 42280 | keep | 0 | Nov | 2021 | 0.028797 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-20 18:39 | 2021-11-21 12:13 | 20 | 017:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA Y SE REEMPLAZO CAJA | S21112000054 | New_Event | Cutout Failure | Include | Include | Equipment | 1054 | 2021-11-20 | 21080 | keep | 0 | Nov | 2021 | 0.014357 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2021-11-20 19:05 | 2021-11-20 19:21 | 15 | 000:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN CORTE DE LINEA REEMPLAZO PORTAFUSIBLE | R21112000065 | New_Event | Cutout Failure | Include | Include | Equipment | 16 | 2021-11-20 | 240 | keep | 0 | Nov | 2021 | 0.00016346 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-11-20 19:24 | 2021-11-21 16:35 | 18 | 021:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO DE CAJA A TRANSFORMADOR | A21112000042 | New_Event | Wire Down | Include | Include | Equipment | 1271 | 2021-11-20 | 22878 | keep | 0 | Nov | 2021 | 0.015582 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
ARECIBO | 2021-11-20 19:42 | 2021-11-20 20:52 | 20 | 001:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR AVE CRUZO FASE A TIERRA | A21112000045 | New_Event |  |  | Include | Wildlife | 70 | 2021-11-20 | 1400 | keep | 0 | Nov | 2021 | 0.00095353 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-11-20 21:01 | 2021-11-20 21:56 | 9 | 000:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21112000032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 55 | 2021-11-20 | 495 | keep | 0 | Nov | 2021 | 0.00033714 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2021-11-20 21:08 | 2021-11-21 12:45 | 100 | 015:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21112000055 | New_Event | Bad Weather | Include | Include | Weather | 937 | 2021-11-20 | 93700 | keep | 0 | Nov | 2021 | 0.063819 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-11-21 00:14 | 2021-11-21 12:30 | 2 | 012:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO HACIA TRANSFORMADOR | C21112100001 | New_Event | Wire Down | Include | Include | Equipment | 736 | 2021-11-21 | 1472 | keep | 0 | Nov | 2021 | 0.0010026 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2021-11-21 01:34 | 2021-11-21 10:07 | 20 | 008:33 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21112100003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 513 | 2021-11-21 | 10260 | keep | 0 | Nov | 2021 | 0.006988 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-11-21 02:25 | 2021-11-21 10:51 | 390 | 008:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 1 X 140 Y 1 X 80 EN CORTES DE LINEA REMPLAZO 2 CAJAS QUEMADAS | R21112100002 | New_Event | Cutout Failure | Include | Include | Equipment | 506 | 2021-11-21 | 197340 | keep | 0 | Nov | 2021 | 0.13441 | 0.00026563 | Sustained | FALSE | FALSE | Not_TMED_Event | 390
BAYAMON | 2021-11-21 03:24 | 2021-11-21 09:13 | 32 | 005:49 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21112100003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 349 | 2021-11-21 | 11168 | keep | 0 | Nov | 2021 | 0.0076065 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
AGUADILLA | 2021-11-21 03:34 | 2021-11-21 10:50 | 50 | 007:16 | P | ESTRUCTURA AVERIADA | 1 X 80 EN CORTE DE LINEA POSTE PARTIDO SE ABRIO PUENTES PARA SECCIONALIZAR | M21112100007 | New_Event | Defective Pole | Include | Include | Equipment | 436 | 2021-11-21 | 21800 | keep | 0 | Nov | 2021 | 0.014848 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-21 03:58 | 2021-11-21 09:34 | 18 | 005:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | B21112100004 | New_Event | Wire Down | Include | Include | Equipment | 336 | 2021-11-21 | 6048 | keep | 0 | Nov | 2021 | 0.0041193 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2021-11-21 04:01 | 2021-11-21 09:35 | 2 | 005:34 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO CAUSA | R21112100006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 334 | 2021-11-21 | 668 | keep | 0 | Nov | 2021 | 0.00045497 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2021-11-21 04:41 | 2021-11-21 04:42 | 5063 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21112100002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-21 | 5063 | keep | 0 | Nov | 2021 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
VEGA BAJA | 2021-11-21 05:38 | 2021-11-21 08:11 | 50 | 002:33 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B21112100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 153 | 2021-11-21 | 7650 | keep | 0 | Nov | 2021 | 0.0052104 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2021-11-21 06:53 | 2021-11-21 14:13 | 50 | 007:20 | P | DESGANCHE | 1 X 25 Y 1 X 20 EN CORTES DE LINEA | R21112100029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 440 | 2021-11-21 | 22000 | keep | 0 | Nov | 2021 | 0.014984 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-21 06:55 | 2021-11-21 09:00 | 50 | 002:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L GUARAGUAO CRUZO LINEAS | S21112100004 | New_Event |  |  | Include | Wildlife | 125 | 2021-11-21 | 6250 | keep | 0 | Nov | 2021 | 0.0042568 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-11-21 07:08 | 2021-11-21 07:09 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21112100004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-21 | 3744 | keep | 0 | Nov | 2021 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
CAGUAS | 2021-11-21 07:21 | 2021-11-21 10:10 | 4 | 002:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE CON AVE | C21112100003 | New_Event |  |  | Include | Wildlife | 169 | 2021-11-21 | 676 | keep | 0 | Nov | 2021 | 0.00046042 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
FAJARDO | 2021-11-21 07:30 | 2021-11-21 13:01 | 50 | 005:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE CON REPTIL | R21112100013 | New_Event |  |  | Include | Wildlife | 331 | 2021-11-21 | 16550 | keep | 0 | Nov | 2021 | 0.011272 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-11-21 07:39 | 2021-11-21 10:39 | 30 | 003:00 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B21112100009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 180 | 2021-11-21 | 5400 | keep | 0 | Nov | 2021 | 0.0036779 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-11-21 07:42 | 2021-11-21 10:25 | 35 | 002:43 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA PRINCIPAL SE SECCIONALIZO ARBOL SOBRE LINEA | A21112100006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2021-11-21 | 5705 | keep | 0 | Nov | 2021 | 0.0038856 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2021-11-21 07:43 | 2021-11-21 10:40 | 3 | 002:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO TOMA | R21112100011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 177 | 2021-11-21 | 531 | keep | 0 | Nov | 2021 | 0.00036166 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-11-21 07:55 | 2021-11-21 07:56 | 716 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DEL 1709-03 PERO 50% DE SU CARGA POR EL 1909-07 PERO LLEVA EL 1709-05 | B21112100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-21 | 716 | keep | 0 | Nov | 2021 | 0.00048766 | 0.00048766 | Momentary | FALSE | FALSE | Not_TMED_Event | 716
BAYAMON | 2021-11-21 07:55 | 2021-11-21 07:56 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1709-03 PERO 50% DE SU CARGA POR EL 1909-07 PERO LLEVA EL 1709-05 | B21112100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-21 | 2364 | keep | 0 | Nov | 2021 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
VEGA BAJA | 2021-11-21 07:56 | 2021-11-21 14:19 | 30 | 006:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | B21112100012 | New_Event | Cutout Failure | Include | Include | Equipment | 383 | 2021-11-21 | 11490 | keep | 0 | Nov | 2021 | 0.0078258 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-11-21 08:12 | 2021-11-21 11:40 | 20 | 003:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA AVE CRUZO LINEAS | M21112100011 | New_Event |  |  | Include | Wildlife | 208 | 2021-11-21 | 4160 | keep | 0 | Nov | 2021 | 0.0028334 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2021-11-21 08:36 | 2021-11-21 14:35 | 6 | 005:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR FUERTES VIENTOS | A21112100012 | New_Event | Bad Weather | Include | Include | Weather | 359 | 2021-11-21 | 2154 | keep | 0 | Nov | 2021 | 0.0014671 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-11-21 08:42 | 2021-11-21 11:12 | 30 | 002:30 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | B21112100016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2021-11-21 | 4500 | keep | 0 | Nov | 2021 | 0.0030649 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-11-21 08:44 | 2021-11-21 11:36 | 50 | 002:52 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21112100091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 172 | 2021-11-21 | 8600 | keep | 0 | Nov | 2021 | 0.0058574 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-11-21 09:08 | 2021-11-21 13:26 | 30 | 004:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L SE REMPLAZO CAJA PRIMARIA Y SE REALIZO DEGANCHE | B21112100017 | New_Event | Cutout Failure | Include | Include | Equipment | 258 | 2021-11-21 | 7740 | keep | 0 | Nov | 2021 | 0.0052717 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-11-21 09:12 | 2021-11-22 15:09 | 10 | 029:57 | P | CABLE SOTERRADO AVERIADO | 1 X 7 EN AEREO PROVISIONAL SE CONSTRUYO AEREO PROVISIONAL DE EXISTENTE A T21 | B21112100018 | New_Event | UG Cable Fault | Include | Include | Equipment | 1797 | 2021-11-21 | 17970 | keep | 0 | Nov | 2021 | 0.012239 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-11-21 09:26 | 2021-11-21 15:10 | 10 | 005:44 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21112100019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 344 | 2021-11-21 | 3440 | keep | 0 | Nov | 2021 | 0.002343 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-11-21 09:37 | 2021-11-21 13:07 | 104 | 003:30 | P | DESGANCHE | 1 X 200 Y 1 X 25 EN CORTES DE LINEA | R21112100025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2021-11-21 | 21840 | keep | 0 | Nov | 2021 | 0.014875 | 7.0834e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 104
UTUADO | 2021-11-21 10:05 | 2021-11-21 10:30 | 5 | 000:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR NEUTRAL PARTIDO | A21112100013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 25 | 2021-11-21 | 125 | keep | 0 | Nov | 2021 | 8.5137e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2021-11-21 10:09 | 2021-11-21 18:57 | 10 | 008:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA DEFECTUOSA | M21112100023 | New_Event | Cutout Failure | Include | Include | Equipment | 528 | 2021-11-21 | 5280 | keep | 0 | Nov | 2021 | 0.0035962 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-11-21 10:14 | 2021-11-21 20:00 | 15 | 009:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21112100024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 586 | 2021-11-21 | 8790 | keep | 0 | Nov | 2021 | 0.0059868 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-11-21 10:25 | 2021-11-21 16:15 | 30 | 005:50 | P | SECUNDARIA/ESTRUCTURA AVERIADA | 1 X 30 EN CORTE DE LINEA SE ABRIO PUENTES PARA SECCIONALIZAR POSTE PARTIDO | A21112100021 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 350 | 2021-11-21 | 10500 | keep | 0 | Nov | 2021 | 0.0071515 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-11-21 10:25 | 2021-11-21 12:46 | 15 | 002:21 | P | DESGANCHE | SE RETIRO ARBOL SOBRE LINEA Y SE CERRO CORTE DE LINEA | A21112100006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2021-11-21 | 2115 | keep | 0 | Nov | 2021 | 0.0014405 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-11-21 10:40 | 2021-11-21 11:00 | 10 | 000:20 | P | PARARRAYOS DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR PARARRAYOS AVERIADO | M21112100026 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 20 | 2021-11-21 | 200 | keep | 0 | Nov | 2021 | 0.00013622 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-11-21 10:50 | 2021-11-21 21:50 | 8 | 011:00 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO SE CERRO PUENTES PRIMARIOS | M21112100007 | New_Event | Defective Pole | Include | Include | Equipment | 660 | 2021-11-21 | 5280 | keep | 0 | Nov | 2021 | 0.0035962 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2021-11-21 10:51 | 2021-11-21 10:58 | 4154 | 000:07 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO SE CERIFICO PERSONAL FUERA | R21112100032 | New_Event | Cutout Failure | Include | Include | Equipment | 7 | 2021-11-21 | 29078 | keep | 0 | Nov | 2021 | 0.019805 | 0.0028293 | Sustained | FALSE | FALSE | Not_TMED_Event | 4154
CANOVANAS | 2021-11-21 10:58 | 2021-11-21 13:36 | 390 | 002:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 1 X 140 Y 1 X 80 EN CORTES DE LINEA REMPLAZO 2 CAJAS QUEMADAS | R21112100002 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 158 | 2021-11-21 | 61620 | keep | 0 | Nov | 2021 | 0.041969 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-11-21 10:58 | 2021-11-21 21:23 | 125 | 010:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 Y 1 X 80 EN CORTES DE LINEA LEVANTO CONDUCTOR | C21112100011 | New_Event | Wire Down | Include | Include | Equipment | 625 | 2021-11-21 | 78125 | keep | 0 | Nov | 2021 | 0.053211 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2021-11-21 11:15 | 2021-11-22 18:40 | 40 | 031:25 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO Y SE REPARO CONDUCTOR | B21112100046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1885 | 2021-11-21 | 75400 | keep | 0 | Nov | 2021 | 0.051355 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-11-21 11:24 | 2021-11-21 11:30 | 100 | 000:06 | P | NO SE REPORTO CAUSA | 2 X 50 EN C/L | B21112100027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2021-11-21 | 600 | keep | 0 | Nov | 2021 | 0.00040866 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-11-21 11:28 | 2021-11-21 14:22 | 80 | 002:54 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA | B21112100029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2021-11-21 | 13920 | keep | 0 | Nov | 2021 | 0.0094808 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2021-11-21 12:18 | 2021-11-21 12:27 | 1945 | 000:09 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR TENIA EL RECIERRE EN OFF PERSONAL COMPAÃ‘IA PRIVADA REALIZABA DESGANCHE | P21112100011 | New_Event |  |  | Include | Wildlife | 9 | 2021-11-21 | 17505 | keep | 0 | Nov | 2021 | 0.011923 | 0.0013247 | Sustained | FALSE | FALSE | Not_TMED_Event | 1945
MAYAGÃœEZ | 2021-11-21 12:30 | 2021-11-21 16:45 | 300 | 004:15 | P | DESGANCHE | 1 X 140 EN CONVERTIDOR SE RETIRO RAMAS SOBRE LAS LINEAS | M21112100032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 255 | 2021-11-21 | 76500 | keep | 0 | Nov | 2021 | 0.052104 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
HUMACAO | 2021-11-21 12:31 | 2021-11-21 14:04 | 20 | 001:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN C/L MAL TIEMPO | C21112100019 | New_Event | Bad Weather | Include | Include | Weather | 93 | 2021-11-21 | 1860 | keep | 0 | Nov | 2021 | 0.0012668 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-11-21 12:51 | 2021-11-21 12:55 | 1712 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR | P21112100013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-11-21 | 6848 | keep | 0 | Nov | 2021 | 0.0046641 | 0.001166 | Momentary | FALSE | FALSE | Not_TMED_Event | 1712
SAN JUAN | 2021-11-21 13:13 | 2021-11-21 14:19 | 30 | 001:06 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S21112100023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 66 | 2021-11-21 | 1980 | keep | 0 | Nov | 2021 | 0.0013486 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-11-21 14:01 | 2021-11-21 15:45 | 100 | 001:44 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER Y 1 SMU 20 DE 80A NO CAUSA | R21112100047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2021-11-21 | 10400 | keep | 0 | Nov | 2021 | 0.0070834 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-11-21 14:08 | 2021-11-21 18:38 | 60 | 004:30 | P | HERRAJE ROTO O PODRIDO | SE ABRIO CORTE DE LINEA PARA REPARAR CRUCETA EN MAL ESTADO Y SE REALIZO DESGANCHE | S21112100026 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 270 | 2021-11-21 | 16200 | keep | 0 | Nov | 2021 | 0.011034 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-11-21 14:21 | 2021-11-21 17:15 | 30 | 002:54 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | A21112100024 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 174 | 2021-11-21 | 5220 | keep | 0 | Nov | 2021 | 0.0035553 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-11-21 14:31 | 2021-11-22 10:36 | 2 | 020:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON 2 CAJAS QUEMADAS | C21112100029 | New_Event | Cutout Failure | Include | Include | Equipment | 1205 | 2021-11-21 | 2410 | keep | 0 | Nov | 2021 | 0.0016414 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2021-11-21 14:49 | 2021-11-21 14:50 | 4291 | 000:01 | T | DESGANCHE | RECERRO 1204-02 LLEVANDO 20% 1303-02 | S21112100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-21 | 4291 | keep | 0 | Nov | 2021 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
SAN JUAN | 2021-11-21 14:49 | 2021-11-21 14:50 | 487 | 000:01 | P | DESGANCHE | RECERRO 1204-02 LLEVANDO 20% 1303-02 | S21112100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-21 | 487 | keep | 0 | Nov | 2021 | 0.00033169 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
SAN JUAN | 2021-11-21 14:50 | 2021-11-21 17:42 | 100 | 002:52 | P | DESGANCHE | 3 X 100 EN C/L SE REALIZO DESGANCHE | S21112100028 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 172 | 2021-11-21 | 17200 | keep | 0 | Nov | 2021 | 0.011715 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-11-21 14:50 | 2021-11-21 19:09 | 4 | 004:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR BARRAS DE PEDESTAL | C21112100031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 259 | 2021-11-21 | 1036 | keep | 0 | Nov | 2021 | 0.00070561 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-11-21 15:07 | 2021-11-21 17:12 | 10 | 002:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | S21112100029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 125 | 2021-11-21 | 1250 | keep | 0 | Nov | 2021 | 0.00085137 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-21 15:17 | 2021-11-21 17:17 | 30 | 002:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B21112100040 | New_Event | Cutout Failure | Include | Include | Equipment | 120 | 2021-11-21 | 3600 | keep | 0 | Nov | 2021 | 0.0024519 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-11-21 15:30 | 2021-11-21 16:50 | 10 | 001:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO TRANSFORMADOR PARA REMPLAZAR TRAMO SECUNDARIO Y REALIZAR DESGANCHE | B21112100032 | New_Event | Wire Down | Include | Include | Equipment | 80 | 2021-11-21 | 800 | keep | 0 | Nov | 2021 | 0.00054488 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-11-21 15:40 | 2021-11-21 15:41 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO | C21112100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-21 | 870 | keep | 0 | Nov | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
ARECIBO | 2021-11-21 15:45 | 2021-11-21 16:13 | 8 | 000:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | A21112100047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 28 | 2021-11-21 | 224 | keep | 0 | Nov | 2021 | 0.00015257 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-11-21 15:53 | 2021-11-21 17:25 | 60 | 001:32 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L Y 1 X 80 EN OTRO C/L | S21112100032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 92 | 2021-11-21 | 5520 | keep | 0 | Nov | 2021 | 0.0037596 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2021-11-21 16:00 | 2021-11-21 17:15 | 10 | 001:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR IGUANA CRUZO FASE | P21112100015 | New_Event |  |  | Include | Wildlife | 75 | 2021-11-21 | 750 | keep | 0 | Nov | 2021 | 0.00051082 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-11-21 16:09 | 2021-11-21 17:01 | 30 | 000:52 | P | DESGANCHE | SE ABRIO CORTE DE LINEA TOTAL PARA REALIZAR DESGANCHE DE ARBOL EN FUEGO POR CONTACTO CON LINEAS | B21112100043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 52 | 2021-11-21 | 1560 | keep | 0 | Nov | 2021 | 0.0010625 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-11-21 16:15 | 2021-11-22 18:55 | 15 | 026:40 | P | SECUNDARIA/ESTRUCTURA AVERIADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO POSTE SECUNDARIO PARTIDO | A21112200033 | Partial_restoration | Secondary Defective Pole | Include | Include | Equipment | 1600 | 2021-11-21 | 24000 | keep | 0 | Nov | 2021 | 0.016346 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-11-21 16:18 | 2021-11-21 18:54 | 100 | 002:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR FUERTES LLUVIAS | M21112100040 | New_Event | Bad Weather | Include | Include | Weather | 156 | 2021-11-21 | 15600 | keep | 0 | Nov | 2021 | 0.010625 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-11-21 16:56 | 2021-11-21 17:53 | 150 | 000:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 Y 1 X 50 EN C/L REMPLAZO CAJA AVERIADA | R21112100061 | New_Event | Cutout Failure | Include | Include | Equipment | 57 | 2021-11-21 | 8550 | keep | 0 | Nov | 2021 | 0.0058234 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2021-11-21 17:02 | 2021-11-21 19:02 | 40 | 002:00 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S21112100037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2021-11-21 | 4800 | keep | 0 | Nov | 2021 | 0.0032693 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-21 17:14 | 2021-11-21 19:23 | 1 | 002:09 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | S21112100039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 129 | 2021-11-21 | 129 | keep | 0 | Nov | 2021 | 8.7861e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-11-21 17:26 | 2021-11-22 17:48 | 10 | 024:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M21112100053 | New_Event | Cutout Failure | Include | Include | Equipment | 1462 | 2021-11-21 | 14620 | keep | 0 | Nov | 2021 | 0.0099576 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-11-21 18:11 | 2021-11-22 10:20 | 60 | 016:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 Y 1 X 25 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A21112100036 | New_Event | Wire Down | Include | Include | Equipment | 969 | 2021-11-21 | 58140 | keep | 0 | Nov | 2021 | 0.039599 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2021-11-21 18:13 | 2021-11-22 11:02 | 3 | 016:49 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR SE INPECCIONO | C21112100035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1009 | 2021-11-21 | 3027 | keep | 0 | Nov | 2021 | 0.0020617 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-11-21 18:22 | 2021-11-21 20:44 | 30 | 002:22 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21112100048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 142 | 2021-11-21 | 4260 | keep | 0 | Nov | 2021 | 0.0029015 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-11-21 18:41 | 2021-11-21 18:42 | 922 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO 1401-08 LLEVANDO LA CARGA DEL 1346-05 | S21112100000 | New_Event |  |  | Include | Wildlife | 1 | 2021-11-21 | 922 | keep | 0 | Nov | 2021 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-11-21 18:41 | 2021-11-21 18:42 | 135 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO 1401-08 LLEVANDO LA CARGA DEL 1346-05 | S21112100000 | New_Event |  |  | Include | Wildlife | 1 | 2021-11-21 | 135 | keep | 0 | Nov | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
VEGA BAJA | 2021-11-21 18:48 | 2021-11-21 20:32 | 10 | 001:44 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21112100050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2021-11-21 | 1040 | keep | 0 | Nov | 2021 | 0.00070834 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-21 18:51 | 2021-11-22 10:10 | 20 | 015:19 | P | DESGANCHE | 1 X 20 C/L SE REALIZO DESGANCHE | B21112100051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 919 | 2021-11-21 | 18380 | keep | 0 | Nov | 2021 | 0.012519 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-11-21 18:56 | 2021-11-21 23:11 | 50 | 004:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B21112100052 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 255 | 2021-11-21 | 12750 | keep | 0 | Nov | 2021 | 0.008684 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-21 18:59 | 2021-11-21 23:50 | 7 | 004:51 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE RETIRO BAMBU SOBRE LAS LINEAS SECUNDARIAS | M21112100059 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 291 | 2021-11-21 | 2037 | keep | 0 | Nov | 2021 | 0.0013874 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2021-11-21 19:01 | 2021-11-22 12:37 | 6 | 017:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR BAJANTE SECUNDARIO | C21112100038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1056 | 2021-11-21 | 6336 | keep | 0 | Nov | 2021 | 0.0043154 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-11-21 19:06 | 2021-11-21 19:07 | 686 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21112100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-21 | 686 | keep | 0 | Nov | 2021 | 0.00046723 | 0.00046723 | Momentary | FALSE | FALSE | Not_TMED_Event | 686
SAN JUAN | 2021-11-21 19:14 | 2021-11-21 19:15 | 1447 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1112-04 LLEVANDO LA CARGA DEL 1419-09 Y 1419-12 | S21112100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-21 | 1447 | keep | 0 | Nov | 2021 | 0.00098555 | 0.00098555 | Momentary | FALSE | FALSE | Not_TMED_Event | 1447
SAN JUAN | 2021-11-21 19:14 | 2021-11-21 19:15 | 266 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1112-04 LLEVANDO LA CARGA DEL 1419-09 Y 1419-12 | S21112100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-21 | 266 | keep | 0 | Nov | 2021 | 0.00018117 | 0.00018117 | Momentary | FALSE | FALSE | Not_TMED_Event | 266
SAN JUAN | 2021-11-21 19:14 | 2021-11-21 19:15 | 73 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1112-04 LLEVANDO LA CARGA DEL 1419-09 Y 1419-12 | S21112100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-21 | 73 | keep | 0 | Nov | 2021 | 4.972e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
AGUADILLA | 2021-11-21 19:16 | 2021-11-22 10:20 | 100 | 015:04 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M21112100060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 904 | 2021-11-21 | 90400 | keep | 0 | Nov | 2021 | 0.061571 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-11-21 19:17 | 2021-11-21 19:18 | 922 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO 1401-08 LLEVANDO LA CARGA DEL 1346-05 | S21112100057 | 1st_after_momentary |  |  | Include | Wildlife | 1 | 2021-11-21 | 922 | keep | 0 | Nov | 2021 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-11-21 19:17 | 2021-11-21 19:18 | 135 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO 1401-08 LLEVANDO LA CARGA DEL 1346-05 | S21112100057 | 1st_after_momentary |  |  | Include | Wildlife | 1 | 2021-11-21 | 135 | keep | 0 | Nov | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2021-11-21 19:19 | 2021-11-21 21:15 | 922 | 001:56 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO 1401-08 LLEVANDO LA CARGA DEL 1346-05. SE RETIRO CULEBRA ENCIMA DE CRUCETA Y SE CERRARON MACHETES DEL 1401-08. | S21112100057 | 1st_after_momentary |  |  | Include | Wildlife | 116 | 2021-11-21 | 106952 | keep | 0 | Nov | 2021 | 0.072845 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-11-21 19:19 | 2021-11-21 20:22 | 135 | 001:03 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO ABRIENDO MACHETES EN CALLE 17 VILLA NEVAREZ | S21112100057 | 1st_after_momentary |  |  | Include | Wildlife | 63 | 2021-11-21 | 8505 | keep | 0 | Nov | 2021 | 0.0057927 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
BAYAMON | 2021-11-21 19:36 | 2021-11-21 19:38 | 2234 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA | B21112100058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-21 | 4468 | keep | 0 | Nov | 2021 | 0.0030431 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
SAN JUAN | 2021-11-21 19:37 | 2021-11-22 00:45 | 1862 | 005:08 | S | DESCONECTIVO DEFECTUOSO | REMPLAZO MACHETE Y ASILADOR QUEMADO Y LEVANTO CONDUCTOR | R21112100082 | New_Event | Switch Failure | Include | Include | Equipment | 308 | 2021-11-21 | 573496 | keep | 0 | Nov | 2021 | 0.39061 | 0.0012682 | Sustained | FALSE | FALSE | Not_TMED_Event | 1862
SAN JUAN | 2021-11-21 19:37 | 2021-11-22 00:45 | 1613 | 005:08 | S | DESCONECTIVO DEFECTUOSO | REMPLAZO MACHETE Y ASILADOR QUEMADO Y LEVANTO CONDUCTOR | R21112100082 | New_Event | Switch Failure | Include | Include | Equipment | 308 | 2021-11-21 | 496804 | keep | 0 | Nov | 2021 | 0.33837 | 0.0010986 | Sustained | FALSE | FALSE | Not_TMED_Event | 1613
SAN JUAN | 2021-11-21 19:37 | 2021-11-22 00:45 | 1448 | 005:08 | S | DESCONECTIVO DEFECTUOSO | REMPLAZO MACHETE Y ASILADOR QUEMADO Y LEVANTO CONDUCTOR | R21112100082 | New_Event | Switch Failure | Include | Include | Equipment | 308 | 2021-11-21 | 445984 | keep | 0 | Nov | 2021 | 0.30376 | 0.00098623 | Sustained | FALSE | FALSE | Not_TMED_Event | 1448
AGUADILLA | 2021-11-21 19:39 | 2021-11-21 19:40 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21112100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-21 | 3041 | keep | 0 | Nov | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
ARECIBO | 2021-11-21 19:42 | 2021-11-22 09:20 | 100 | 013:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 Y 1 X 65 EN CONVERTIDOR MAL TIEMPO DESCARGAS ELECTRICAS | A21112100043 | New_Event | Bad Weather | Include | Include | Weather | 818 | 2021-11-21 | 81800 | keep | 0 | Nov | 2021 | 0.055714 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-21 19:58 | 2021-11-22 14:46 | 1 | 018:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN MONTURA DE TRANSFORMADORES MAL TIEMPO DESCARGAS ELECTRICAS | A21112100042 | New_Event | Bad Weather | Include | Include | Weather | 1128 | 2021-11-21 | 1128 | keep | 0 | Nov | 2021 | 0.00076828 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-21 19:58 | 2021-11-22 09:11 | 150 | 013:13 | P | NO SE REPORTO CAUSA | 1 X 200 EN COVERTIDOR | B21112100064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 793 | 2021-11-21 | 118950 | keep | 0 | Nov | 2021 | 0.081016 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2021-11-21 20:22 | 2021-11-21 21:12 | 50 | 000:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE RETIRO CULEBRA ENCIMA DE CRUCETA Y SE PROCEDE A CERRAR NUEVAMENTE MACHETES | S21112100057 | Partial_restoration |  |  | Include | Wildlife | 50 | 2021-11-21 | 2500 | keep | 0 | Nov | 2021 | 0.0017027 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-11-21 21:04 | 2021-11-22 09:40 | 3 | 012:36 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | A21112100045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 756 | 2021-11-21 | 2268 | keep | 0 | Nov | 2021 | 0.0015447 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-11-21 21:12 | 2021-11-21 21:13 | 790 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21112100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-21 | 790 | keep | 0 | Nov | 2021 | 0.00053807 | 0.00053807 | Momentary | FALSE | FALSE | Not_TMED_Event | 790
SAN JUAN | 2021-11-21 21:12 | 2021-11-21 21:15 | 135 | 000:03 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO 1401-08 EN EL MOMENTO QUE ESTABAN CERRANDO MACHETES CON CARGA DESPUES DE RETIRAR CULEBRA ENCIMA DE CRUCETA. SE CERRO NUEVAMENTE ALIMENTADOR CON MACHETES CERRADOS QUEDANDO EN SERVICIO TOTAL | S21112100057 | Additional_clients |  |  | Include | Wildlife | 3 | 2021-11-21 | 405 | keep | 0 | Nov | 2021 | 0.00027584 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-21 21:36 | 2021-11-22 11:26 | 180 | 013:50 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 80 EN SU-3 Y 1 X 100 EN CORTE DE LINEA REPARO TERMINACION EN PROVISIONAL AEREO Y REEMPLAZO CAJA PRIMARIA | R21112100146 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 830 | 2021-11-21 | 149400 | keep | 0 | Nov | 2021 | 0.10176 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
MAYAGÃœEZ | 2021-11-21 21:38 | 2021-11-22 09:52 | 12 | 012:14 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA | M21112100077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 734 | 2021-11-21 | 8808 | keep | 0 | Nov | 2021 | 0.0059991 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-11-21 21:46 | 2021-11-22 09:27 | 299 | 011:41 | P | NO SE REPORTO CAUSA | 2 X 200 EN CORTES DE LINEA SE PATRULLO | C21112100054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 701 | 2021-11-21 | 209599 | keep | 0 | Nov | 2021 | 0.14276 | 0.00020365 | Sustained | FALSE | FALSE | Not_TMED_Event | 299
VEGA BAJA | 2021-11-21 21:53 | 2021-11-22 10:33 | 50 | 012:40 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B21112100084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 760 | 2021-11-21 | 38000 | keep | 0 | Nov | 2021 | 0.025882 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-11-21 22:04 | 2021-11-22 10:42 | 75 | 012:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A21112100057 | New_Event | Cutout Failure | Include | Include | Equipment | 758 | 2021-11-21 | 56850 | keep | 0 | Nov | 2021 | 0.03872 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2021-11-21 22:14 | 2021-11-22 00:05 | 125 | 001:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A21112100059 | New_Event | Cutout Failure | Include | Include | Equipment | 111 | 2021-11-21 | 13875 | keep | 0 | Nov | 2021 | 0.0094502 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2021-11-21 22:52 | 2021-11-22 09:01 | 207 | 010:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE EN RISER DE SALIDA DEL 1416-05 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1416-02 Y 1416-03. LOS TRABAJOS SE REALIZARON EN VIVO Y SE VIO AFECTADA SOLO UNA FASE DE LOS ALIMENTADORES | S21112100124 | New_Event | Wire Down | Include | Include | Equipment | 609 | 2021-11-21 | 126063 | keep | 0 | Nov | 2021 | 0.085861 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2021-11-21 22:52 | 2021-11-22 09:01 | 56 | 010:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE EN RISER DE SALIDA DEL 1416-05 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1416-02 Y 1416-03. LOS TRABAJOS SE REALIZARON EN VIVO Y SE VIO AFECTADA SOLO UNA FASE DE LOS ALIMENTADORES | S21112100124 | New_Event | Wire Down | Include | Include | Equipment | 609 | 2021-11-21 | 34104 | keep | 0 | Nov | 2021 | 0.023228 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
SAN JUAN | 2021-11-21 22:52 | 2021-11-22 09:01 | 1054 | 010:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE EN RISER DE SALIDA DEL 1416-05 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1416-02 Y 1416-03. LOS TRABAJOS SE REALIZARON EN VIVO Y SE VIO AFECTADA SOLO UNA FASE DE LOS ALIMENTADORES | S21112100124 | New_Event | Wire Down | Include | Include | Equipment | 609 | 2021-11-21 | 641886 | keep | 0 | Nov | 2021 | 0.43719 | 0.00071787 | Sustained | FALSE | FALSE | Not_TMED_Event | 1054
FAJARDO | 2021-11-21 23:04 | 2021-11-22 10:04 | 15 | 011:00 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R21112100152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 660 | 2021-11-21 | 9900 | keep | 0 | Nov | 2021 | 0.0067428 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-11-21 23:19 | 2021-11-21 23:20 | 4664 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21112100080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-21 | 4664 | keep | 0 | Nov | 2021 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
AGUADILLA | 2021-11-21 23:19 | 2021-11-21 23:20 | 574 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21112100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-21 | 574 | keep | 0 | Nov | 2021 | 0.00039095 | 0.00039095 | Momentary | FALSE | FALSE | Not_TMED_Event | 574
AGUADILLA | 2021-11-21 23:19 | 2021-11-21 23:20 | 2493 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21112100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-21 | 2493 | keep | 0 | Nov | 2021 | 0.001698 | 0.001698 | Momentary | FALSE | FALSE | Not_TMED_Event | 2493
AGUADILLA | 2021-11-21 23:19 | 2021-11-21 23:20 | 1415 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21112100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-21 | 1415 | keep | 0 | Nov | 2021 | 0.00096375 | 0.00096375 | Momentary | FALSE | FALSE | Not_TMED_Event | 1415
AGUADILLA | 2021-11-21 23:19 | 2021-11-21 23:20 | 1428 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21112100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-21 | 1428 | keep | 0 | Nov | 2021 | 0.0009726 | 0.0009726 | Momentary | FALSE | FALSE | Not_TMED_Event | 1428
AGUADILLA | 2021-11-21 23:19 | 2021-11-21 23:20 | 1036 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21112100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-21 | 1036 | keep | 0 | Nov | 2021 | 0.00070561 | 0.00070561 | Momentary | FALSE | FALSE | Not_TMED_Event | 1036
AGUADILLA | 2021-11-21 23:19 | 2021-11-21 23:20 | 382 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21112100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-21 | 382 | keep | 0 | Nov | 2021 | 0.00026018 | 0.00026018 | Momentary | FALSE | FALSE | Not_TMED_Event | 382
AGUADILLA | 2021-11-21 23:19 | 2021-11-21 23:20 | 39 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21112100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-21 | 39 | keep | 0 | Nov | 2021 | 2.6563e-05 | 2.6563e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 39
AGUADILLA | 2021-11-21 23:19 | 2021-11-21 23:20 | 2366 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21112100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-21 | 2366 | keep | 0 | Nov | 2021 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
MAYAGÃœEZ | 2021-11-21 23:19 | 2021-11-21 23:20 | 1337 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21112100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-21 | 1337 | keep | 0 | Nov | 2021 | 0.00091062 | 0.00091062 | Momentary | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2021-11-21 23:19 | 2021-11-21 23:20 | 709 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21112100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-21 | 709 | keep | 0 | Nov | 2021 | 0.0004829 | 0.0004829 | Momentary | FALSE | FALSE | Not_TMED_Event | 709
BAYAMON | 2021-11-21 23:23 | 2021-11-22 10:04 | 65 | 010:41 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | S21112100131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 641 | 2021-11-21 | 41665 | keep | 0 | Nov | 2021 | 0.028378 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2021-11-21 23:44 | 2021-11-22 15:42 | 50 | 015:58 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S21112100129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 958 | 2021-11-21 | 47900 | keep | 0 | Nov | 2021 | 0.032624 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-11-22 00:10 | 2021-11-22 00:11 | 1859 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 9207-9 | B21112200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 1859 | keep | 0 | Nov | 2021 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2021-11-22 00:10 | 2021-11-22 00:11 | 7 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 9207-8 | B21112200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 7 | keep | 0 | Nov | 2021 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-11-22 00:28 | 2021-11-22 00:31 | 922 | 000:03 | T | NO SE REPORTO CAUSA | RECERRO QUEDO ABIERTO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1401-8 | S21112200001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-22 | 2766 | keep | 0 | Nov | 2021 | 0.0018839 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-11-22 00:28 | 2021-11-22 00:31 | 135 | 000:03 | T | NO SE REPORTO CAUSA | RECERRO QUEDO ABIERTO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1346-5 | S21112200001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-22 | 405 | keep | 0 | Nov | 2021 | 0.00027584 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2021-11-22 00:31 | 2021-11-22 00:36 | 143 | 000:05 | T | LINEA DE TRANSMISION 115KV | SE ABRE INTERRUPTOR PARA RETIRAR OVERHEAD SOBRE ALIMENTADOR L-38900 Y SE CIERRA YA QUE TRAMO NO SE QUEDO SIN SERVICIO LLEVA 80% DEL 1404-7 A PETICION FRANKIE RAMOS | S21112200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-11-22 | 715 | keep | 0 | Nov | 2021 | 0.00048698 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2021-11-22 00:36 | 2021-11-22 00:37 | 1040 | 000:01 | P | LINEA DE TRANSMISION 115KV | SE ABRE INTERRUPTOR PARA RETIRAR OVERHEAD SOBRE ALIMENTADOR L-38900 Y SE CIERRA YA QUE TRAMO NO SE QUEDO SIN SERVICIO 80% DE SU CARGA POR 1404-6 A PETICION FRANKIE RAMOS | S21112200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-22 | 1040 | keep | 0 | Nov | 2021 | 0.00070834 | 0.00070834 | Momentary | FALSE | FALSE | Not_TMED_Event | 1040
SAN JUAN | 2021-11-22 00:40 | 2021-11-22 00:41 | 317 | 000:01 | P | LINEA DE TRANSMISION 115KV | SE ABRE INTERRUPTOR PARA RETIRAR OVERHEAD SOBRE ALIMENTADOR L-38900 Y SE CIERRA YA QUE TRAMO NO SE QUEDO SIN SERVICIO LLEVA 20% DE SU CARGA A PETICION FRANKIE RAMOS | S21112200000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-22 | 317 | keep | 0 | Nov | 2021 | 0.00021591 | 0.00021591 | Momentary | FALSE | FALSE | Not_TMED_Event | 317
ARECIBO | 2021-11-22 00:55 | 2021-11-22 12:48 | 40 | 011:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN RISER SE REMPLAZO CAJA PRIMARIA AVERIADA | A21112200001 | New_Event | Cutout Failure | Include | Include | Equipment | 713 | 2021-11-22 | 28520 | keep | 0 | Nov | 2021 | 0.019425 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-11-22 01:45 | 2021-11-22 12:20 | 150 | 010:35 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M21112200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 635 | 2021-11-22 | 95250 | keep | 0 | Nov | 2021 | 0.064874 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-11-22 01:45 | 2021-11-26 12:05 | 10 | 106:20 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 37.5 KVA X 50 KVA VERIFICADO EN BITACORA | M21112200001 | New_Event | Service Transformer Failure | Include | Include | Equipment | 6380 | 2021-11-22 | 63800 | keep | 0 | Nov | 2021 | 0.043454 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-22 01:46 | 2021-11-22 01:47 | 438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21112200002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 438 | keep | 0 | Nov | 2021 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
ARECIBO | 2021-11-22 01:51 | 2021-11-22 01:52 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21112200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 308 | keep | 0 | Nov | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
ARECIBO | 2021-11-22 03:22 | 2021-11-22 08:52 | 25 | 005:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | A21112200006 | New_Event |  |  | Include | Wildlife | 330 | 2021-11-22 | 8250 | keep | 0 | Nov | 2021 | 0.005619 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2021-11-22 03:50 | 2021-11-22 15:24 | 100 | 011:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN C/L REMPLAZO CAJA AVERIADA | C21112200003 | New_Event | Cutout Failure | Include | Include | Equipment | 694 | 2021-11-22 | 69400 | keep | 0 | Nov | 2021 | 0.047268 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2021-11-22 04:30 | 2021-11-22 06:25 | 4009 | 001:55 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO SE ENCONTRO CAUSA NO ESTA POR SCADA | P21112200004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2021-11-22 | 461035 | keep | 0 | Nov | 2021 | 0.31401 | 0.0027305 | Sustained | FALSE | FALSE | Not_TMED_Event | 4009
FAJARDO | 2021-11-22 04:52 | 2021-11-22 04:53 | 2722 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21112200004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 2722 | keep | 0 | Nov | 2021 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
FAJARDO | 2021-11-22 04:52 | 2021-11-22 04:53 | 693 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21112200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 693 | keep | 0 | Nov | 2021 | 0.000472 | 0.000472 | Momentary | FALSE | FALSE | Not_TMED_Event | 693
VEGA BAJA | 2021-11-22 06:13 | 2021-11-22 10:17 | 50 | 004:04 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21112200004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 244 | 2021-11-22 | 12200 | keep | 0 | Nov | 2021 | 0.0083094 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-11-22 06:33 | 2021-11-22 09:15 | 1 | 002:42 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21112200042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2021-11-22 | 162 | keep | 0 | Nov | 2021 | 0.00011034 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-11-22 06:52 | 2021-11-22 16:27 | 8 | 009:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR BARRAS DE PEDESTAL | C21112200011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 575 | 2021-11-22 | 4600 | keep | 0 | Nov | 2021 | 0.003133 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2021-11-22 07:24 | 2021-11-22 10:27 | 1 | 003:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | R21112200008 | New_Event | Cutout Failure | Include | Include | Equipment | 183 | 2021-11-22 | 183 | keep | 0 | Nov | 2021 | 0.00012464 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-22 07:27 | 2021-11-22 07:28 | 922 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 QUE A SU VEZ LLEVA LA CARGA DEL 1346-05 | S21112200017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 922 | keep | 0 | Nov | 2021 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-11-22 07:27 | 2021-11-22 07:28 | 135 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 QUE A SU VEZ LLEVA LA CARGA DEL 1346-05 | S21112200017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 135 | keep | 0 | Nov | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2021-11-22 07:29 | 2021-11-22 07:30 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE 1206-03 QUE A SU VEZ LLEVA LA CARGA DEL 1204-05 | S21112200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 10211 | keep | 0 | Nov | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-11-22 07:29 | 2021-11-22 07:30 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE 1206-03 QUE A SU VEZ LLEVA LA CARGA DEL 1204-05 | S21112200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 4133 | keep | 0 | Nov | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-11-22 07:30 | 2021-11-22 14:21 | 40 | 006:51 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S21112200030 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 411 | 2021-11-22 | 16440 | keep | 0 | Nov | 2021 | 0.011197 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-11-22 07:34 | 2021-11-22 07:35 | 1494 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 9101-02 QUE LLEVA LA CARGA DEL 9101-04 | B21112200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 1494 | keep | 0 | Nov | 2021 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
VEGA BAJA | 2021-11-22 07:45 | 2021-11-22 13:52 | 22 | 006:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA Y SE REPARO SECUNDARIA | B21112200015 | New_Event | Cutout Failure | Include | Include | Equipment | 367 | 2021-11-22 | 8074 | keep | 0 | Nov | 2021 | 0.0054992 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
AGUADILLA | 2021-11-22 07:50 | 2021-11-22 07:51 | 390 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21112200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 390 | keep | 0 | Nov | 2021 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
BAYAMON | 2021-11-22 07:51 | 2021-11-22 12:26 | 65 | 004:35 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21112100019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2021-11-22 | 17875 | keep | 0 | Nov | 2021 | 0.012175 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
YAUCO | 2021-11-22 07:51 | 2021-11-22 11:35 | 166 | 003:44 | P | HERRAJE ROTO O PODRIDO | 1 X 80 EN CORTE DE LINEA CRUCETA PARTIDA | P21112200045 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 224 | 2021-11-22 | 37184 | keep | 0 | Nov | 2021 | 0.025326 | 0.00011306 | Sustained | FALSE | FALSE | Not_TMED_Event | 166
BARRANQUITAS | 2021-11-22 08:00 | 2021-11-22 13:29 | 4 | 005:29 | P | PARARRAYOS DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO PARARRAYOS | C21112200017 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 329 | 2021-11-22 | 1316 | keep | 0 | Nov | 2021 | 0.00089632 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-11-22 08:06 | 2021-11-22 08:07 | 2107 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21112200019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 2107 | keep | 0 | Nov | 2021 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
BAYAMON | 2021-11-22 08:29 | 2021-11-22 11:40 | 5 | 003:11 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21112200019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2021-11-22 | 955 | keep | 0 | Nov | 2021 | 0.00065045 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-11-22 08:38 | 2021-11-22 13:42 | 200 | 005:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RETIRO CARGA PARA REPARAR PUENTE ABIERTO | M21112200014 | New_Event | Wire Down | Include | Include | Equipment | 304 | 2021-11-22 | 60800 | keep | 0 | Nov | 2021 | 0.041411 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2021-11-22 08:40 | 2021-11-22 11:10 | 39 | 002:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE CON AVE | C21112200026 | New_Event |  |  | Include | Wildlife | 150 | 2021-11-22 | 5850 | keep | 0 | Nov | 2021 | 0.0039844 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
CAGUAS | 2021-11-22 08:42 | 2021-11-22 12:53 | 1 | 004:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 30 EN CORTE DE LINEA CRUCE CON AVE | C21112200027 | New_Event |  |  | Include | Wildlife | 251 | 2021-11-22 | 251 | keep | 0 | Nov | 2021 | 0.00017095 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-22 08:57 | 2021-11-22 13:17 | 40 | 004:20 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21112200022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 260 | 2021-11-22 | 10400 | keep | 0 | Nov | 2021 | 0.0070834 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-11-22 09:12 | 2021-11-22 16:08 | 10 | 006:56 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | B21112200026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 416 | 2021-11-22 | 4160 | keep | 0 | Nov | 2021 | 0.0028334 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-11-22 09:22 | 2021-11-22 12:37 | 7 | 003:15 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 25 KVA X 25 KVA | C21112200035 | New_Event | Service Transformer Failure | Include | Include | Equipment | 195 | 2021-11-22 | 1365 | keep | 0 | Nov | 2021 | 0.0009297 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
YAUCO | 2021-11-22 09:30 | 2021-11-22 14:13 | 50 | 004:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21112200051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2021-11-22 | 14150 | keep | 0 | Nov | 2021 | 0.0096375 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-11-22 09:35 | 2021-11-22 09:36 | 4369 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 600 | C21112200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-22 | 4369 | keep | 0 | Nov | 2021 | 0.0029757 | 0.0029757 | Momentary | FALSE | FALSE | Not_TMED_Event | 4369
CAGUAS | 2021-11-22 09:35 | 2021-11-22 09:36 | 676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 600 | C21112200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-22 | 676 | keep | 0 | Nov | 2021 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
CAGUAS | 2021-11-22 09:35 | 2021-11-22 09:36 | 1606 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 600 | C21112200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-22 | 1606 | keep | 0 | Nov | 2021 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
CAGUAS | 2021-11-22 09:35 | 2021-11-22 09:36 | 725 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 600 | C21112200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-22 | 725 | keep | 0 | Nov | 2021 | 0.00049379 | 0.00049379 | Momentary | FALSE | FALSE | Not_TMED_Event | 725
FAJARDO | 2021-11-22 09:38 | 2021-11-22 12:09 | 40 | 002:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE SAFADO | R21112200025 | New_Event | Wire Down | Include | Include | Equipment | 151 | 2021-11-22 | 6040 | keep | 0 | Nov | 2021 | 0.0041138 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-22 09:49 | 2021-11-22 14:38 | 10 | 004:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA Y TOMA SE REALIZO DESGANCHE | B21112200003 | New_Event | Secondary Wire Down | Include | Include | Equipment | 289 | 2021-11-22 | 2890 | keep | 0 | Nov | 2021 | 0.0019684 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-22 09:51 | 2021-11-22 09:52 | 573 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1704-04 Y SE CERRO POR SCADA LLEVA 1704-05 | B21112200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 573 | keep | 0 | Nov | 2021 | 0.00039027 | 0.00039027 | Momentary | FALSE | FALSE | Not_TMED_Event | 573
BAYAMON | 2021-11-22 09:51 | 2021-11-22 09:52 | 1313 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1704-04 Y SE CERRO POR SCADA LLEVA 1704-05 | B21112200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 1313 | keep | 0 | Nov | 2021 | 0.00089428 | 0.00089428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1313
MAYAGÃœEZ | 2021-11-22 09:52 | 2021-11-22 09:53 | 2073 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13500 | M21112200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-22 | 2073 | keep | 0 | Nov | 2021 | 0.0014119 | 0.0014119 | Momentary | FALSE | FALSE | Not_TMED_Event | 2073
MAYAGÃœEZ | 2021-11-22 09:52 | 2021-11-22 09:53 | 637 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13500 | M21112200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-22 | 637 | keep | 0 | Nov | 2021 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
MAYAGÃœEZ | 2021-11-22 09:52 | 2021-11-22 09:53 | 1491 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13500 | M21112200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-22 | 1491 | keep | 0 | Nov | 2021 | 0.0010155 | 0.0010155 | Momentary | FALSE | FALSE | Not_TMED_Event | 1491
MAYAGÃœEZ | 2021-11-22 09:52 | 2021-11-22 09:53 | 4892 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13500 | M21112200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-22 | 4892 | keep | 0 | Nov | 2021 | 0.0033319 | 0.0033319 | Momentary | FALSE | FALSE | Not_TMED_Event | 4892
MAYAGÃœEZ | 2021-11-22 09:52 | 2021-11-22 09:53 | 160 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13500 | M21112200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-22 | 160 | keep | 0 | Nov | 2021 | 0.00010898 | 0.00010898 | Momentary | FALSE | FALSE | Not_TMED_Event | 160
MAYAGÃœEZ | 2021-11-22 09:53 | 2021-11-22 10:21 | 12 | 000:28 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA | M21112100077 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 28 | 2021-11-22 | 336 | keep | 0 | Nov | 2021 | 0.00022885 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-11-22 10:01 | 2021-11-22 17:00 | 616 | 006:59 | P | DESGANCHE | D2021-00541 PARA REALIZAR DESGANCHE | C21112200043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 419 | 2021-11-22 | 258104 | keep | 0 | Nov | 2021 | 0.17579 | 0.00041955 | Sustained | FALSE | FALSE | Not_TMED_Event | 616
PONCE | 2021-11-22 10:07 | 2021-11-22 12:10 | 72 | 002:03 | P | DESGANCHE | SE ABRE CORTE DE LINEA PARA REALIZAR DESGANCHE | P21112200055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2021-11-22 | 8856 | keep | 0 | Nov | 2021 | 0.0060318 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
HUMACAO | 2021-11-22 10:10 | 2021-11-22 11:25 | 6 | 001:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO NEUTRAL SULFATADO | C21112200039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 75 | 2021-11-22 | 450 | keep | 0 | Nov | 2021 | 0.00030649 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-11-22 10:10 | 2021-11-22 13:16 | 1 | 003:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO TOMA | C21112200039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 186 | 2021-11-22 | 186 | keep | 0 | Nov | 2021 | 0.00012668 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-11-22 10:10 | 2021-11-22 10:40 | 10 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | A21112100025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2021-11-22 | 300 | keep | 0 | Nov | 2021 | 0.00020433 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-22 10:10 | 2021-11-22 10:11 | 2132 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21112200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 2132 | keep | 0 | Nov | 2021 | 0.0014521 | 0.0014521 | Momentary | FALSE | FALSE | Not_TMED_Event | 2132
CAGUAS | 2021-11-22 10:11 | 2021-11-22 12:44 | 3 | 002:33 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REEMPLAZO BARRA EN PEDESTAL | C21112200007 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 153 | 2021-11-22 | 459 | keep | 0 | Nov | 2021 | 0.00031262 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2021-11-22 10:17 | 2021-11-22 11:57 | 2228 | 001:40 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA ROTA EN EL TRONCAL DEL ALIMENTADOR SU CARGA ESTA A TRAVES DEL 8007-04 | A21112200033 | New_Event | Wire Down | Include | Include | Equipment | 100 | 2021-11-22 | 222800 | keep | 0 | Nov | 2021 | 0.15175 | 0.0015175 | Sustained | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2021-11-22 10:17 | 2021-11-22 11:57 | 438 | 001:40 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO EL INTERRUPTOR PARA REPARAR LINEA ROTA EN EL TRONCAL DEL 8007-03 LA CARGA DEL 8007-03 ESTA A TRAVES DEL 8007-04 | A21112200033 | New_Event | Wire Down | Include | Include | Equipment | 100 | 2021-11-22 | 43800 | keep | 0 | Nov | 2021 | 0.029832 | 0.00029832 | Sustained | FALSE | FALSE | Not_TMED_Event | 438
ARECIBO | 2021-11-22 10:28 | 2021-11-22 15:39 | 75 | 005:11 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21112200037 | New_Event | Bad Weather | Include | Include | Weather | 311 | 2021-11-22 | 23325 | keep | 0 | Nov | 2021 | 0.015887 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
UTUADO | 2021-11-22 10:32 | 2021-11-22 14:30 | 100 | 003:58 | P | ESTRUCTURA AVERIADA | POSTE EN MALAS CONDICIONES SE ABRIO CORTE DE LINEA PARA PASAR TRANSFORMADOR Y LINEAS A POSTE QUE ESTABA DESDE PREPA SIN LOS CAMBIOS EVENTO DE FLUCTUACIONES DE VOLTAJE | A21112200034 | New_Event | Defective Pole | Include | Include | Equipment | 238 | 2021-11-22 | 23800 | keep | 0 | Nov | 2021 | 0.01621 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2021-11-22 10:46 | 2021-11-22 13:50 | 32 | 003:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA PERSONAL COMPAÃ‘IA PRIVADA REALIZANDO DESGANCHE RAMA TOCO LINEA | P21112200061 | New_Event |  |  | Include | Wildlife | 184 | 2021-11-22 | 5888 | keep | 0 | Nov | 2021 | 0.0040103 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
BAYAMON | 2021-11-22 10:49 | 2021-11-22 13:29 | 12 | 002:40 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21112200043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 160 | 2021-11-22 | 1920 | keep | 0 | Nov | 2021 | 0.0013077 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-11-22 10:50 | 2021-11-22 10:51 | 1681 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-01 CARGA TRANSFERIDA AL 1303-04 | S21112200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 1681 | keep | 0 | Nov | 2021 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-11-22 10:50 | 2021-11-22 10:51 | 1598 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1346-06 CARGA TRANSFERIDA AL 1303-04 | S21112200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 1598 | keep | 0 | Nov | 2021 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
VEGA BAJA | 2021-11-22 11:15 | 2021-11-22 17:11 | 30 | 005:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21112200047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 356 | 2021-11-22 | 10680 | keep | 0 | Nov | 2021 | 0.0072741 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-11-22 11:27 | 2021-11-22 16:40 | 50 | 005:13 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21112200035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 313 | 2021-11-22 | 15650 | keep | 0 | Nov | 2021 | 0.010659 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2021-11-22 11:34 | 2021-11-22 20:25 | 6 | 008:51 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21112200052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 531 | 2021-11-22 | 3186 | keep | 0 | Nov | 2021 | 0.00217 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-11-22 11:50 | 2021-11-22 12:16 | 21 | 000:26 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR QUEMADO 37.5KVA X 50KVA | R21112200043 | New_Event | Service Transformer Failure | Include | Include | Equipment | 26 | 2021-11-22 | 546 | keep | 0 | Nov | 2021 | 0.00037188 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BAYAMON | 2021-11-22 12:17 | 2021-11-22 15:00 | 20 | 002:43 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21112200057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 163 | 2021-11-22 | 3260 | keep | 0 | Nov | 2021 | 0.0022204 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-11-22 12:27 | 2021-11-22 16:54 | 15 | 004:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M21112200046 | New_Event | Secondary Wire Down | Include | Include | Equipment | 267 | 2021-11-22 | 4005 | keep | 0 | Nov | 2021 | 0.0027278 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-11-22 12:28 | 2021-11-22 14:51 | 7 | 002:23 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO 25 KVA X 25 KVA | C21112200063 | New_Event | Service Transformer Failure | Include | Include | Equipment | 143 | 2021-11-22 | 1001 | keep | 0 | Nov | 2021 | 0.00068178 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2021-11-22 12:37 | 2021-11-22 12:51 | 3296 | 000:14 | T | TRANSFORMADOR AVERIADO | DISPARO SE VERIFICO PERSONAL FUERA | C21112200000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 14 | 2021-11-22 | 46144 | keep | 0 | Nov | 2021 | 0.031428 | 0.0022449 | Sustained | FALSE | FALSE | Not_TMED_Event | 3296
BAYAMON | 2021-11-22 12:39 | 2021-11-22 15:39 | 10 | 003:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO LINEA A CAJA ENTRANSFORMADOR SE REMPLAZARON PARARRAYOS | B21112200058 | New_Event | Wire Down | Include | Include | Equipment | 180 | 2021-11-22 | 1800 | keep | 0 | Nov | 2021 | 0.001226 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-11-22 12:51 | 2021-11-22 17:42 | 6 | 004:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR BAJANTE SECUNDARIO | C21112100038 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 291 | 2021-11-22 | 1746 | keep | 0 | Nov | 2021 | 0.0011892 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-11-22 12:51 | 2021-11-22 14:32 | 7 | 001:41 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 25 KVA X 25 KVA | C21112200035 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 101 | 2021-11-22 | 707 | keep | 0 | Nov | 2021 | 0.00048153 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2021-11-22 12:55 | 2021-11-22 12:56 | 2484 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21112200068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 2484 | keep | 0 | Nov | 2021 | 0.0016918 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
SAN JUAN | 2021-11-22 12:57 | 2021-11-22 12:58 | 2179 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21112200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 2179 | keep | 0 | Nov | 2021 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
ARECIBO | 2021-11-22 13:11 | 2021-11-22 13:22 | 1 | 000:11 | S | ERROR HUMANO | DISPARO DE LA SUBESTACION POR PERSONAL DE RELES HACIENDO PRUEBAS DE CALIBRACION INFORMADO POR EL CENTRO DE CONTROL DE TRANSMISION DE PONCE | A21112200006 | New_Event | Human Error | Include | Include | Other | 11 | 2021-11-22 | 11 | keep | 0 | Nov | 2021 | 7.492e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-11-22 13:11 | 2021-11-22 13:22 | 4607 | 000:11 | S | ERROR HUMANO | DISPARO DE LA SUBESTACION POR PERSONAL DE RELES HACIENDO PRUEBAS DE CALIBRACION INFORMADO POR EL CENTRO DE CONTROL DE TRANSMISION DE PONCE | A21112200006 | New_Event | Human Error | Include | Include | Other | 11 | 2021-11-22 | 50677 | keep | 0 | Nov | 2021 | 0.034516 | 0.0031378 | Sustained | FALSE | FALSE | Not_TMED_Event | 4607
MAYAGÃœEZ | 2021-11-22 13:22 | 2021-11-22 18:00 | 2 | 004:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M21112200054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 278 | 2021-11-22 | 556 | keep | 0 | Nov | 2021 | 0.00037869 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2021-11-22 13:35 | 2021-11-22 13:37 | 75 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1117-9 QUE LLEVA A LA VEZ LA CARGA DE LOS ALIMENTADORES 1115-04, 1115-03 Y 50% DEL 1115-02 | S21112200057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-22 | 150 | keep | 0 | Nov | 2021 | 0.00010216 | 5.1082e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2021-11-22 13:35 | 2021-11-22 13:37 | 134 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1117-9 QUE LLEVA A LA VEZ LA CARGA DE LOS ALIMENTADORES 1115-04, 1115-03 Y 50% DEL 1115-02 | S21112200057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-22 | 268 | keep | 0 | Nov | 2021 | 0.00018253 | 9.1267e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 134
BAYAMON | 2021-11-22 13:35 | 2021-11-22 13:37 | 114 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1117-9 QUE LLEVA A LA VEZ LA CARGA DE LOS ALIMENTADORES 1115-04, 1115-03 Y 50% DEL 1115-02 | S21112200057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-22 | 228 | keep | 0 | Nov | 2021 | 0.00015529 | 7.7645e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 114
BAYAMON | 2021-11-22 13:35 | 2021-11-22 13:37 | 316 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1117-9 QUE LLEVA A LA VEZ LA CARGA DE LOS ALIMENATADORES 1115-04, 1115-03 Y 50% DEL 1115-02 | S21112200057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-22 | 632 | keep | 0 | Nov | 2021 | 0.00043045 | 0.00021523 | Momentary | FALSE | FALSE | Not_TMED_Event | 316
FAJARDO | 2021-11-22 13:46 | 2021-11-22 15:54 | 60 | 002:08 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | R21112200035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 128 | 2021-11-22 | 7680 | keep | 0 | Nov | 2021 | 0.0052308 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2021-11-22 13:48 | 2021-11-22 13:49 | 2379 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21112200071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 2379 | keep | 0 | Nov | 2021 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
SAN JUAN | 2021-11-22 14:00 | 2021-11-22 18:30 | 10 | 004:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO XMR Y SE CERRO PUENTE DE LINEA A CAJA DE XMR | S21112200055 | New_Event | Wire Down | Include | Include | Equipment | 270 | 2021-11-22 | 2700 | keep | 0 | Nov | 2021 | 0.001839 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-22 14:00 | 2021-11-22 15:10 | 14 | 001:10 | P | OTRAS CAUSAS | SE ABRIO CAJAS DE TRANSFORMADOR PARA RETIRAR LINEAS PRIMARIAS FUERA DE USO | A21112200084 | New_Event | Other Causes | Include | Include | Other | 70 | 2021-11-22 | 980 | keep | 0 | Nov | 2021 | 0.00066747 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2021-11-22 14:26 | 2021-11-22 20:16 | 50 | 005:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA CRUZADA POR TENSOR | A21112200091 | New_Event | Wire Down | Include | Include | Equipment | 350 | 2021-11-22 | 17500 | keep | 0 | Nov | 2021 | 0.011919 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-11-22 14:30 | 2021-11-22 17:57 | 10 | 003:27 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | S21112200057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 207 | 2021-11-22 | 2070 | keep | 0 | Nov | 2021 | 0.0014099 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-11-22 14:30 | 2021-11-22 14:31 | 3420 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21112200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 3420 | keep | 0 | Nov | 2021 | 0.0023293 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
HUMACAO | 2021-11-22 14:45 | 2021-11-22 16:20 | 5 | 001:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE X AVE | C21112200080 | New_Event |  |  | Include | Wildlife | 95 | 2021-11-22 | 475 | keep | 0 | Nov | 2021 | 0.00032352 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-11-22 14:49 | 2021-11-22 15:31 | 10 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE CAJA DE TRANSFORMADOR PARA CAMBIAR BARRA EN PEDESTAL SECUNDARIO | P21112200074 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2021-11-22 | 420 | keep | 0 | Nov | 2021 | 0.00028606 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-22 14:54 | 2021-11-22 16:46 | 30 | 001:52 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21112200063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2021-11-22 | 3360 | keep | 0 | Nov | 2021 | 0.0022885 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-11-22 14:59 | 2021-11-22 16:27 | 25 | 001:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21112200095 | New_Event | Bad Weather | Include | Include | Weather | 88 | 2021-11-22 | 2200 | keep | 0 | Nov | 2021 | 0.0014984 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-11-22 15:06 | 2021-11-22 15:10 | 500 | 000:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO INTERRUPTOR 1907-04 LLEVANDO PARTE DE LA CARGA 1346-03. SE REMPLAZO CAJA PRIMARIA | S21112200064 | New_Event | Cutout Failure | Include | Include | Equipment | 4 | 2021-11-22 | 2000 | keep | 0 | Nov | 2021 | 0.0013622 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2021-11-22 15:06 | 2021-11-22 15:10 | 2466 | 000:04 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO INTERRUPTOR 1907-04 LLEVANDO PARTE DE LA CARGA 1346-03. SE REMPLAZO CAJA PRIMARIA | S21112200064 | New_Event | Cutout Failure | Include | Include | Equipment | 4 | 2021-11-22 | 9864 | keep | 0 | Nov | 2021 | 0.0067183 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
BAYAMON | 2021-11-22 15:10 | 2021-11-22 18:02 | 40 | 002:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA HAY AVERIA SOTERRADA HACIA BOMBAS AAA | S21112200067 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 172 | 2021-11-22 | 6880 | keep | 0 | Nov | 2021 | 0.0046859 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-11-22 15:23 | 2021-11-22 19:14 | 40 | 003:51 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S21112200078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 231 | 2021-11-22 | 9240 | keep | 0 | Nov | 2021 | 0.0062933 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-11-22 15:44 | 2021-11-22 16:28 | 2 | 000:44 | P | TRANSFORMADOR AVERIADO | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BUSHING DE TRANSFORMADOR DEFECTUOSO | R21112200040 | New_Event | Service Transformer Failure | Include | Include | Equipment | 44 | 2021-11-22 | 88 | keep | 0 | Nov | 2021 | 5.9936e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2021-11-22 15:46 | 2021-11-22 18:32 | 30 | 002:46 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR | R21112200041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 166 | 2021-11-22 | 4980 | keep | 0 | Nov | 2021 | 0.0033919 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-11-22 16:08 | 2021-11-22 21:10 | 50 | 005:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | A21112200098 | New_Event |  |  | Include | Wildlife | 302 | 2021-11-22 | 15100 | keep | 0 | Nov | 2021 | 0.010285 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-11-22 16:15 | 2021-11-22 18:44 | 100 | 002:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SECCIONALIZO CONDUCTOR EN EL SUELO | C21112200090 | New_Event | Wire Down | Include | Include | Equipment | 149 | 2021-11-22 | 14900 | keep | 0 | Nov | 2021 | 0.010148 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-22 16:20 | 2021-11-22 17:23 | 6 | 001:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | A21112200095 | New_Event | Secondary Wire Down | Include | Include | Equipment | 63 | 2021-11-22 | 378 | keep | 0 | Nov | 2021 | 0.00025745 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-11-22 16:32 | 2021-11-22 16:33 | 2379 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21112200078 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 2379 | keep | 0 | Nov | 2021 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
YAUCO | 2021-11-22 16:34 | 2021-11-22 16:35 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21112200079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 1352 | keep | 0 | Nov | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
BAYAMON | 2021-11-22 16:37 | 2021-11-22 22:51 | 97 | 006:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA NO FUNDIO FUSIBLE | B21112200069 | New_Event | Cutout Failure | Include | Include | Equipment | 374 | 2021-11-22 | 36278 | keep | 0 | Nov | 2021 | 0.024709 | 6.6066e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 97
HUMACAO | 2021-11-22 16:44 | 2021-11-22 17:33 | 40 | 000:49 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER NO CAUSA | C21112200091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 49 | 2021-11-22 | 1960 | keep | 0 | Nov | 2021 | 0.0013349 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-11-22 16:54 | 2021-11-22 19:34 | 300 | 002:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA AUTO IMPACTO POSTE Y CRUZO LINEAS MOMENTANEAMENTE | A21112200107 | New_Event |  |  | Include | Wildlife | 160 | 2021-11-22 | 48000 | keep | 0 | Nov | 2021 | 0.032693 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
FAJARDO | 2021-11-22 16:57 | 2021-11-22 18:08 | 95 | 001:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA SE REPARO LINEAS CRUZADAS POR CAMION | R21112200042 | New_Event |  |  | Include | Wildlife | 71 | 2021-11-22 | 6745 | keep | 0 | Nov | 2021 | 0.004594 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
ARECIBO | 2021-11-22 17:09 | 2021-11-22 17:10 | 2132 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR LINEA PRIMARIA ENERGIZADA EN EL SUELO | A21112200000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-22 | 2132 | keep | 0 | Nov | 2021 | 0.0014521 | 0.0014521 | Momentary | FALSE | FALSE | Not_TMED_Event | 2132
ARECIBO | 2021-11-22 17:10 | 2021-11-22 19:18 | 200 | 002:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21112200101 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 128 | 2021-11-22 | 25600 | keep | 0 | Nov | 2021 | 0.017436 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2021-11-22 17:29 | 2021-11-22 17:40 | 4702 | 000:11 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B21112200073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 11 | 2021-11-22 | 51722 | keep | 0 | Nov | 2021 | 0.035228 | 0.0032025 | Sustained | FALSE | FALSE | Not_TMED_Event | 4702
CANOVANAS | 2021-11-22 17:32 | 2021-11-22 20:35 | 45 | 003:03 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | R21112200044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 183 | 2021-11-22 | 8235 | keep | 0 | Nov | 2021 | 0.0056088 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
HUMACAO | 2021-11-22 17:38 | 2021-11-23 07:23 | 10 | 013:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA CRUCE CON AVE | C21112200095 | New_Event |  |  | Include | Wildlife | 825 | 2021-11-22 | 8250 | keep | 0 | Nov | 2021 | 0.005619 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-11-22 17:43 | 2021-11-22 19:29 | 5 | 001:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR SECUNDARIA AVERIADA | R21112200043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 106 | 2021-11-22 | 530 | keep | 0 | Nov | 2021 | 0.00036098 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-11-22 17:45 | 2021-11-22 17:51 | 100 | 000:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO CORTE DE LINEA PARA REMPLAZAR AISLADOR ROTO Y CORREGIR LINEA ARRIADA | A21112200111 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 6 | 2021-11-22 | 600 | keep | 0 | Nov | 2021 | 0.00040866 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-22 17:51 | 2021-11-22 17:52 | 1345 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21112200112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 1345 | keep | 0 | Nov | 2021 | 0.00091607 | 0.00091607 | Momentary | FALSE | FALSE | Not_TMED_Event | 1345
ARECIBO | 2021-11-22 17:52 | 2021-11-22 19:00 | 100 | 001:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO CORTE DE LINEA PARA REMPLAZAR AISLADOR ROTO Y CORREGIR LINEA ARRIADA | A21112200111 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 68 | 2021-11-22 | 6800 | keep | 0 | Nov | 2021 | 0.0046314 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-11-22 17:55 | 2021-11-22 19:05 | 100 | 001:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CAJA CORTE EN LINEA PARA CERRAR PUENTE PRIMARIO | P21112200081 | New_Event | Wire Down | Include | Include | Equipment | 70 | 2021-11-22 | 7000 | keep | 0 | Nov | 2021 | 0.0047677 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-11-22 18:02 | 2021-11-22 18:04 | 500 | 000:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO INTERRUPTOR 1907-04 LLEVANDO PARTE DE LA CARGA 1346-03. SE REMPLAZO CAJA PRIMARIA | S21112200084 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 2 | 2021-11-22 | 1000 | keep | 0 | Nov | 2021 | 0.0006811 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2021-11-22 18:02 | 2021-11-22 18:04 | 2466 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO INTERRUPTOR 1907-04 LLEVANDO PARTE DE LA CARGA 1346-03. SE REMPLAZO CAJA PRIMARIA. | S21112200084 | Additional_clients | Cutout Failure | Include | Include | Equipment | 2 | 2021-11-22 | 4932 | keep | 0 | Nov | 2021 | 0.0033592 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-22 18:04 | 2021-11-22 18:44 | 40 | 000:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA HAY AVERIA SOTERRADA HACIA BOMBAS AAA | S21112200067 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 40 | 2021-11-22 | 1600 | keep | 0 | Nov | 2021 | 0.0010898 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-11-22 18:07 | 2021-11-23 14:00 | 50 | 019:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | A21112200118 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1193 | 2021-11-22 | 59650 | keep | 0 | Nov | 2021 | 0.040627 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-11-22 18:27 | 2021-11-22 18:28 | 2450 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO | C21112200096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 2450 | keep | 0 | Nov | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
ARECIBO | 2021-11-22 18:36 | 2021-11-22 21:17 | 3 | 002:41 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA POR UNO DE 37.5 KVA | A21112200129 | New_Event | Service Transformer Failure | Include | Include | Equipment | 161 | 2021-11-22 | 483 | keep | 0 | Nov | 2021 | 0.00032897 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-11-22 18:44 | 2021-11-22 18:46 | 500 | 000:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR 1907-04 LLEVANDO PARTE DE LA CARGA 1346-03. SE REMPLAZO CAJA PRIMARIA | S21112200086 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 2 | 2021-11-22 | 1000 | keep | 0 | Nov | 2021 | 0.0006811 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2021-11-22 18:44 | 2021-11-22 18:46 | 2466 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR 1907-04 LLEVANDO PARTE DE LA CARGA 1346-03. SE REMPLAZO CAJA PRIMARIA | S21112200086 | Additional_clients | Cutout Failure | Include | Include | Equipment | 2 | 2021-11-22 | 4932 | keep | 0 | Nov | 2021 | 0.0033592 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-22 18:46 | 2021-11-22 19:55 | 40 | 001:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA HAY AVERIA SOTERRADA HACIA BOMBAS AAA | S21112200067 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 69 | 2021-11-22 | 2760 | keep | 0 | Nov | 2021 | 0.0018798 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2021-11-22 18:54 | 2021-11-22 20:49 | 55 | 001:55 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | R21112200050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2021-11-22 | 6325 | keep | 0 | Nov | 2021 | 0.0043079 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
BAYAMON | 2021-11-22 18:57 | 2021-11-22 18:59 | 320 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B21112200106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-22 | 640 | keep | 0 | Nov | 2021 | 0.0004359 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2021-11-22 18:59 | 2021-11-22 20:00 | 40 | 001:01 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21112200108 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 61 | 2021-11-22 | 2440 | keep | 0 | Nov | 2021 | 0.0016619 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-11-22 20:43 | 2021-11-22 22:12 | 8 | 001:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21112200136 | New_Event | Bad Weather | Include | Include | Weather | 89 | 2021-11-22 | 712 | keep | 0 | Nov | 2021 | 0.00048494 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2021-11-22 20:48 | 2021-11-23 15:00 | 150 | 018:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | A21112200139 | New_Event | Wire Down | Include | Include | Equipment | 1092 | 2021-11-22 | 163800 | keep | 0 | Nov | 2021 | 0.11156 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2021-11-22 20:48 | 2021-11-22 20:49 | 1859 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9207-08 LLEVANDO CARGA 9207-08 | B21112200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 1859 | keep | 0 | Nov | 2021 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2021-11-22 20:48 | 2021-11-22 20:49 | 7 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9207-08 LLEVANDO CARGA 9207-08 | B21112200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 7 | keep | 0 | Nov | 2021 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-11-22 21:06 | 2021-11-22 21:07 | 200 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21112200101 | Partial_restoration | Wire Down | Include | Include | Equipment | 1 | 2021-11-22 | 200 | keep | 0 | Nov | 2021 | 0.00013622 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-22 21:44 | 2021-11-22 21:45 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B21112200118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 1746 | keep | 0 | Nov | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
VEGA BAJA | 2021-11-22 22:01 | 2021-11-22 22:02 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21112200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-22 | 1310 | keep | 0 | Nov | 2021 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
VEGA BAJA | 2021-11-22 22:10 | 2021-11-23 08:29 | 1 | 010:19 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 40 EN C/L | B21112200119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 619 | 2021-11-22 | 619 | keep | 0 | Nov | 2021 | 0.0004216 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-22 22:34 | 2021-11-22 22:38 | 4431 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO | B21112200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-11-22 | 17724 | keep | 0 | Nov | 2021 | 0.012072 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
HUMACAO | 2021-11-22 23:10 | 2021-11-22 23:12 | 2126 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C21112200109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-22 | 4252 | keep | 0 | Nov | 2021 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2021-11-22 23:44 | 2021-11-23 09:29 | 100 | 009:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REEMPLAZO | C21112200112 | New_Event | Cutout Failure | Include | Include | Equipment | 585 | 2021-11-22 | 58500 | keep | 0 | Nov | 2021 | 0.039844 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-23 00:02 | 2021-11-23 17:50 | 30 | 017:48 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | A21112300001 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1068 | 2021-11-23 | 32040 | keep | 0 | Nov | 2021 | 0.021822 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-11-23 00:41 | 2021-11-23 10:45 | 45 | 010:04 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21112300001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 604 | 2021-11-23 | 27180 | keep | 0 | Nov | 2021 | 0.018512 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2021-11-23 01:25 | 2021-11-23 14:37 | 5 | 013:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA QUEMADA DE TRANSFORMADOR | M21112300003 | New_Event | Cutout Failure | Include | Include | Equipment | 792 | 2021-11-23 | 3960 | keep | 0 | Nov | 2021 | 0.0026971 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-11-23 03:33 | 2021-11-23 03:34 | 449 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21112300001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-23 | 449 | keep | 0 | Nov | 2021 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
CANOVANAS | 2021-11-23 04:22 | 2021-11-23 11:17 | 4 | 006:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | R21112300001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 415 | 2021-11-23 | 1660 | keep | 0 | Nov | 2021 | 0.0011306 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2021-11-23 04:31 | 2021-11-23 17:15 | 11 | 012:44 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA A 2.4KV POR UNO DE LA MISMA CAPACIDAD | P21112300002 | New_Event | Service Transformer Failure | Include | Include | Equipment | 764 | 2021-11-23 | 8404 | keep | 0 | Nov | 2021 | 0.0057239 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2021-11-23 06:12 | 2021-11-23 11:20 | 15 | 005:08 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | S21112300001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 308 | 2021-11-23 | 4620 | keep | 0 | Nov | 2021 | 0.0031467 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-11-23 06:45 | 2021-11-23 06:46 | 2402 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR 1709-02 QUE A SU VEZ LLEVA LA CARGA DEL 1720-08 SE REMPLAZO CAJA PRIMARIA | S21112300000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-11-23 | 2402 | keep | 0 | Nov | 2021 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2021-11-23 06:45 | 2021-11-23 06:46 | 1 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR 1709-02 QUE A SU VEZ LLEVA LA CARGA DEL 1720-08 | S21112300000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-11-23 | 1 | keep | 0 | Nov | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-23 06:46 | 2021-11-23 12:20 | 45 | 005:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 Y 1 X 50 EN CORTE DE LINEAS SE REMPLAZO CAJA PRIMARIA | S21112300004 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 334 | 2021-11-23 | 15030 | keep | 0 | Nov | 2021 | 0.010237 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2021-11-23 06:46 | 2021-11-23 11:31 | 300 | 004:45 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21112300003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 285 | 2021-11-23 | 85500 | keep | 0 | Nov | 2021 | 0.058234 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
HUMACAO | 2021-11-23 06:55 | 2021-11-23 11:12 | 89 | 004:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | C21112300010 | New_Event | Cutout Failure | Include | Include | Equipment | 257 | 2021-11-23 | 22873 | keep | 0 | Nov | 2021 | 0.015579 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
ARECIBO | 2021-11-23 07:17 | 2021-11-23 11:25 | 5 | 004:08 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21112300002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 248 | 2021-11-23 | 1240 | keep | 0 | Nov | 2021 | 0.00084456 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-11-23 07:34 | 2021-11-23 11:00 | 6 | 003:26 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE SECUNDARIO PARTIDO LINEAS SECUNDARIAS | M21112300009 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 206 | 2021-11-23 | 1236 | keep | 0 | Nov | 2021 | 0.00084183 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-11-23 08:56 | 2021-11-23 12:40 | 6 | 003:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR TRANSFORMADOR Y REPARAR SECUNDARIA | B21112300031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 224 | 2021-11-23 | 1344 | keep | 0 | Nov | 2021 | 0.00091539 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2021-11-23 09:01 | 2021-11-23 10:09 | 159 | 001:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA CRUCE CON GLOBOS | R21112300005 | New_Event |  |  | Include | Wildlife | 68 | 2021-11-23 | 10812 | keep | 0 | Nov | 2021 | 0.007364 | 0.00010829 | Sustained | FALSE | FALSE | Not_TMED_Event | 159
CAGUAS | 2021-11-23 09:11 | 2021-11-23 12:34 | 3 | 003:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 15 EN TRANSFORMADOR CRUCE CON AVE | C21112300032 | New_Event |  |  | Include | Wildlife | 203 | 2021-11-23 | 609 | keep | 0 | Nov | 2021 | 0.00041479 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2021-11-23 09:27 | 2021-11-23 09:42 | 3 | 000:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | C21112300007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 15 | 2021-11-23 | 45 | keep | 0 | Nov | 2021 | 3.0649e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-11-23 09:28 | 2021-11-23 16:12 | 10 | 006:44 | P | NO SE REPORTO CAUSA | 1 X 150 EN SU | B21112300015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 404 | 2021-11-23 | 4040 | keep | 0 | Nov | 2021 | 0.0027516 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-11-23 09:28 | 2021-11-23 14:12 | 82 | 004:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE LEVANTO NEUTRAL PRIMARIO | C21112300034 | New_Event | Wire Down | Include | Include | Equipment | 284 | 2021-11-23 | 23288 | keep | 0 | Nov | 2021 | 0.015861 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
BARRANQUITAS | 2021-11-23 09:37 | 2021-11-23 09:38 | 2192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21112300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-23 | 2192 | keep | 0 | Nov | 2021 | 0.001493 | 0.001493 | Momentary | FALSE | FALSE | Not_TMED_Event | 2192
VEGA BAJA | 2021-11-23 09:45 | 2021-11-23 12:49 | 20 | 003:04 | P | DESGANCHE | 1 X 30 EN C/L | B21112300016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2021-11-23 | 3680 | keep | 0 | Nov | 2021 | 0.0025064 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-11-23 09:57 | 2021-11-23 10:27 | 7 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21111900030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2021-11-23 | 210 | keep | 0 | Nov | 2021 | 0.00014303 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-11-23 10:00 | 2021-11-23 12:05 | 3 | 002:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21112300042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 125 | 2021-11-23 | 375 | keep | 0 | Nov | 2021 | 0.00025541 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-11-23 10:06 | 2021-11-23 10:07 | 5062 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21112300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-23 | 5062 | keep | 0 | Nov | 2021 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
SAN JUAN | 2021-11-23 10:18 | 2021-11-23 11:35 | 1000 | 001:17 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SPARE 1204-01 QUE LLEVA EL 40% DEL 1204-03 | S21112300022 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 77 | 2021-11-23 | 77000 | keep | 0 | Nov | 2021 | 0.052444 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
UTUADO | 2021-11-23 10:20 | 2021-11-23 11:50 | 15 | 001:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONECTORES SECUNDARIOS | A21112200055 | New_Event | Secondary Wire Down | Include | Include | Equipment | 90 | 2021-11-23 | 1350 | keep | 0 | Nov | 2021 | 0.00091948 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-11-23 10:26 | 2021-11-23 18:33 | 10 | 008:07 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA POR 25 KVA | A21112300016 | New_Event | Service Transformer Failure | Include | Include | Equipment | 487 | 2021-11-23 | 4870 | keep | 0 | Nov | 2021 | 0.0033169 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-23 10:30 | 2021-11-23 15:34 | 100 | 005:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA LINEAS CRUZADAS | A21112300017 | New_Event | Wire Down | Include | Include | Equipment | 304 | 2021-11-23 | 30400 | keep | 0 | Nov | 2021 | 0.020705 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-11-23 10:32 | 2021-11-23 12:10 | 100 | 001:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | R21112300012 | New_Event |  |  | Include | Wildlife | 98 | 2021-11-23 | 9800 | keep | 0 | Nov | 2021 | 0.0066747 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-23 10:37 | 2021-11-23 13:40 | 3 | 003:03 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | A21112300020 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 183 | 2021-11-23 | 549 | keep | 0 | Nov | 2021 | 0.00037392 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2021-11-23 10:46 | 2021-11-23 10:51 | 2725 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500 | C21112300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-11-23 | 13625 | keep | 0 | Nov | 2021 | 0.0092799 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2021-11-23 10:46 | 2021-11-23 10:51 | 1834 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500 | C21112300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-11-23 | 9170 | keep | 0 | Nov | 2021 | 0.0062456 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2021-11-23 10:46 | 2021-11-23 10:51 | 1437 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500 | C21112300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-11-23 | 7185 | keep | 0 | Nov | 2021 | 0.0048937 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2021-11-23 10:46 | 2021-11-23 10:51 | 2565 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500 | C21112300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-11-23 | 12825 | keep | 0 | Nov | 2021 | 0.008735 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2021-11-23 10:46 | 2021-11-23 10:51 | 3565 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500 | C21112300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-11-23 | 17825 | keep | 0 | Nov | 2021 | 0.012141 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
PONCE | 2021-11-23 10:46 | 2021-11-23 12:31 | 2751 | 001:45 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P21112300014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 105 | 2021-11-23 | 288855 | keep | 0 | Nov | 2021 | 0.19674 | 0.0018737 | Sustained | FALSE | FALSE | Not_TMED_Event | 2751
PONCE | 2021-11-23 10:46 | 2021-11-23 12:31 | 576 | 001:45 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P21112300014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 105 | 2021-11-23 | 60480 | keep | 0 | Nov | 2021 | 0.041193 | 0.00039231 | Sustained | FALSE | FALSE | Not_TMED_Event | 576
PONCE | 2021-11-23 10:46 | 2021-11-23 12:31 | 2584 | 001:45 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P21112300014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 105 | 2021-11-23 | 271320 | keep | 0 | Nov | 2021 | 0.18479 | 0.00176 | Sustained | FALSE | FALSE | Not_TMED_Event | 2584
PONCE | 2021-11-23 10:46 | 2021-11-23 12:31 | 1606 | 001:45 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P21112300014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 105 | 2021-11-23 | 168630 | keep | 0 | Nov | 2021 | 0.11485 | 0.0010938 | Sustained | FALSE | FALSE | Not_TMED_Event | 1606
PONCE | 2021-11-23 10:46 | 2021-11-23 12:31 | 29 | 001:45 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P21112300014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 105 | 2021-11-23 | 3045 | keep | 0 | Nov | 2021 | 0.0020739 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
PONCE | 2021-11-23 10:46 | 2021-11-23 12:31 | 4035 | 001:45 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P21112300014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 105 | 2021-11-23 | 423675 | keep | 0 | Nov | 2021 | 0.28856 | 0.0027482 | Sustained | FALSE | FALSE | Not_TMED_Event | 4035
PONCE | 2021-11-23 10:46 | 2021-11-23 12:31 | 3718 | 001:45 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P21112300014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 105 | 2021-11-23 | 390390 | keep | 0 | Nov | 2021 | 0.26589 | 0.0025323 | Sustained | FALSE | FALSE | Not_TMED_Event | 3718
SAN JUAN | 2021-11-23 10:52 | 2021-11-23 15:46 | 8 | 004:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | REPARO SECUNDARIA Y TOMAS AVERIADAS POR CAMION | R21112300013 | New_Event |  |  | Include | Wildlife | 294 | 2021-11-23 | 2352 | keep | 0 | Nov | 2021 | 0.0016019 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-11-23 10:56 | 2021-11-23 13:12 | 40 | 002:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | R21112300014 | New_Event |  |  | Include | Wildlife | 136 | 2021-11-23 | 5440 | keep | 0 | Nov | 2021 | 0.0037052 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-11-23 10:57 | 2021-11-23 11:54 | 1 | 000:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON 2 CAJAS QUEMADAS | R21112300015 | New_Event | Cutout Failure | Include | Include | Equipment | 57 | 2021-11-23 | 57 | keep | 0 | Nov | 2021 | 3.8822e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-11-23 11:11 | 2021-11-23 11:13 | 676 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5300 | C21112300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-23 | 1352 | keep | 0 | Nov | 2021 | 0.00092084 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
HUMACAO | 2021-11-23 11:11 | 2021-11-23 11:13 | 2873 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5300 | C21112300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-23 | 5746 | keep | 0 | Nov | 2021 | 0.0039136 | 0.0019568 | Momentary | FALSE | FALSE | Not_TMED_Event | 2873
HUMACAO | 2021-11-23 11:11 | 2021-11-23 11:13 | 3902 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5300 | C21112300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-23 | 7804 | keep | 0 | Nov | 2021 | 0.0053153 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
MAYAGÃœEZ | 2021-11-23 11:30 | 2021-11-23 17:44 | 1 | 006:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21112300073 | New_Event | Bad Weather | Include | Include | Weather | 374 | 2021-11-23 | 374 | keep | 0 | Nov | 2021 | 0.00025473 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-23 11:31 | 2021-11-23 14:49 | 80 | 003:18 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21112300037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2021-11-23 | 15840 | keep | 0 | Nov | 2021 | 0.010789 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2021-11-23 11:33 | 2021-11-23 12:22 | 2725 | 000:49 | S | LINEA DE TRANSMISION 38KV | OPERACIONES EN LA LINEA 8500 | C21112300000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 49 | 2021-11-23 | 133525 | keep | 0 | Nov | 2021 | 0.090943 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-11-23 11:33 | 2021-11-23 12:22 | 1834 | 000:49 | S | LINEA DE TRANSMISION 38KV | OPERACIONES EN LA LINEA 8500 | C21112300000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 49 | 2021-11-23 | 89866 | keep | 0 | Nov | 2021 | 0.061207 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-11-23 11:33 | 2021-11-23 12:22 | 1437 | 000:49 | S | LINEA DE TRANSMISION 38KV | OPERACIONES EN LA LINEA 8500 | C21112300000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 49 | 2021-11-23 | 70413 | keep | 0 | Nov | 2021 | 0.047958 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-11-23 11:33 | 2021-11-23 12:31 | 2565 | 000:58 | S | LINEA DE TRANSMISION 38KV | OPERACIONES EN LA LINEA 8500 | C21112300000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 58 | 2021-11-23 | 148770 | keep | 0 | Nov | 2021 | 0.10133 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-11-23 11:33 | 2021-11-23 12:31 | 3565 | 000:58 | S | LINEA DE TRANSMISION 38KV | OPERACIONES EN LA LINEA 8500 | C21112300000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 58 | 2021-11-23 | 206770 | keep | 0 | Nov | 2021 | 0.14083 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-23 11:35 | 2021-11-23 19:11 | 100 | 007:36 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR AVERIADO MEDIANTE GOI SJ-211123-02 | S21112300022 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 456 | 2021-11-23 | 45600 | keep | 0 | Nov | 2021 | 0.031058 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-23 11:47 | 2021-11-23 19:33 | 10 | 007:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 15 EN XMR. SE ABRIO XMR PARA SE REEMPALZO CAJA QUEMADA Y SECUNDARIA | S21112300040 | New_Event | Cutout Failure | Include | Include | Equipment | 466 | 2021-11-23 | 4660 | keep | 0 | Nov | 2021 | 0.0031739 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-11-23 11:55 | 2021-11-23 17:07 | 60 | 005:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA VEHICULO CRUZO LINEA SE RETEZO LINEA PRIMARIA | M21112300080 | New_Event |  |  | Include | Wildlife | 312 | 2021-11-23 | 18720 | keep | 0 | Nov | 2021 | 0.01275 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2021-11-23 11:57 | 2021-11-23 18:43 | 150 | 006:46 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | R21112300024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 406 | 2021-11-23 | 60900 | keep | 0 | Nov | 2021 | 0.041479 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2021-11-23 12:30 | 2021-11-23 12:36 | 726 | 000:06 | T | LINEA DE TRANSMISION 115KV | DISPARO DE INTERRUPTOR 1303-03 QUE LLEVA A SU VEZ LA CARGA DEL 1346-04 | S21112300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-11-23 | 4356 | keep | 0 | Nov | 2021 | 0.0029669 | 0.00049448 | Sustained | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-11-23 12:30 | 2021-11-23 12:36 | 3932 | 000:06 | T | LINEA DE TRANSMISION 115KV | DISPARO DE INTERRUPTOR 1303-03 QUE LLEVA A SU VEZ LA CARGA DEL 1346-04 | S21112300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-11-23 | 23592 | keep | 0 | Nov | 2021 | 0.016068 | 0.0026781 | Sustained | FALSE | FALSE | Not_TMED_Event | 3932
ARECIBO | 2021-11-23 12:37 | 2021-11-23 20:18 | 10 | 007:41 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA POR 50 KVA | A21112300030 | New_Event | Service Transformer Failure | Include | Include | Equipment | 461 | 2021-11-23 | 4610 | keep | 0 | Nov | 2021 | 0.0031399 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-11-23 12:41 | 2021-11-23 16:00 | 200 | 003:19 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | M21112300092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2021-11-23 | 39800 | keep | 0 | Nov | 2021 | 0.027108 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-11-23 12:51 | 2021-11-23 13:56 | 35 | 001:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE ENCONTRO CAJA QUEMADA | S21112300049 | New_Event | Cutout Failure | Include | Include | Equipment | 65 | 2021-11-23 | 2275 | keep | 0 | Nov | 2021 | 0.0015495 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-11-23 12:51 | 2021-11-23 15:28 | 300 | 002:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR FUERTES VIENTOS | M21112300092 | New_Event | Bad Weather | Include | Include | Weather | 157 | 2021-11-23 | 47100 | keep | 0 | Nov | 2021 | 0.03208 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2021-11-23 13:06 | 2021-11-23 13:08 | 2580 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11100 | R21112300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-23 | 5160 | keep | 0 | Nov | 2021 | 0.0035145 | 0.0017572 | Momentary | FALSE | FALSE | Not_TMED_Event | 2580
CANOVANAS | 2021-11-23 13:06 | 2021-11-23 13:08 | 500 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11100 | R21112300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-23 | 1000 | keep | 0 | Nov | 2021 | 0.0006811 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2021-11-23 13:13 | 2021-11-23 17:21 | 1399 | 004:08 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR 1704-02 LLEVANDO CARGA 1704-01 PARA RETIRAR CARGA SUBESTACION 1704 PARA REMPLAZO MOD LINEA 10000 | B21112300032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 248 | 2021-11-23 | 346952 | keep | 0 | Nov | 2021 | 0.23631 | 0.00095285 | Sustained | FALSE | FALSE | Not_TMED_Event | 1399
BAYAMON | 2021-11-23 13:13 | 2021-11-23 17:21 | 302 | 004:08 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR 1704-02 LLEVANDO CARGA 1704-01 PARA RETIRAR CARGA SUBESTACION 1704 PARA REMPLAZO MOD LINEA 10000 | B21112300032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 248 | 2021-11-23 | 74896 | keep | 0 | Nov | 2021 | 0.051011 | 0.00020569 | Sustained | FALSE | FALSE | Not_TMED_Event | 302
BAYAMON | 2021-11-23 13:13 | 2021-11-23 14:05 | 1048 | 000:52 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR 1704-08 PARA RETIRAR CARGA SUBESTACION 1704 PARA REMPLAZO MOD LINEA 10000 SE TRANSFIRIO CARGA AL 1708-04 | B21112300034 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 52 | 2021-11-23 | 54496 | keep | 0 | Nov | 2021 | 0.037117 | 0.00071379 | Sustained | FALSE | FALSE | Not_TMED_Event | 1048
BAYAMON | 2021-11-23 13:13 | 2021-11-23 17:26 | 573 | 004:13 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR 1704-04 LLEVANDO CARGA 1704-05 PARA RETIRAR CARGA SUBESTACION 1704 PARA REMPLAZO MOD LINEA 10000 | B21112300034 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 253 | 2021-11-23 | 144969 | keep | 0 | Nov | 2021 | 0.098738 | 0.00039027 | Sustained | FALSE | FALSE | Not_TMED_Event | 573
BAYAMON | 2021-11-23 13:13 | 2021-11-23 17:26 | 1313 | 004:13 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR 1704-04 LLEVANDO CARGA 1704-05 PARA RETIRAR CARGA SUBESTACION 1704 PARA REMPLAZO MOD LINEA 10000 | B21112300034 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 253 | 2021-11-23 | 332189 | keep | 0 | Nov | 2021 | 0.22625 | 0.00089428 | Sustained | FALSE | FALSE | Not_TMED_Event | 1313
MAYAGÃœEZ | 2021-11-23 13:15 | 2021-11-23 16:10 | 25 | 002:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | M21112300104 | New_Event | Secondary Wire Down | Include | Include | Equipment | 175 | 2021-11-23 | 4375 | keep | 0 | Nov | 2021 | 0.0029798 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-11-23 13:19 | 2021-11-23 16:20 | 1 | 003:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | R21112300030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 181 | 2021-11-23 | 181 | keep | 0 | Nov | 2021 | 0.00012328 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-11-23 13:22 | 2021-11-23 16:24 | 16 | 003:02 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REEMPLAZO DE PEDESTAL Y BARRAS DEL PEDESTAL | C21112300123 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 182 | 2021-11-23 | 2912 | keep | 0 | Nov | 2021 | 0.0019833 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2021-11-23 13:49 | 2021-11-23 13:50 | 726 | 000:01 | T | LINEA DE TRANSMISION 115KV | DISPARO DE INTERRUPTOR 1303-03 QUE LLEVA A SU VEZ LA CARGA DEL 1346-04 | S21112300000 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-23 | 726 | keep | 0 | Nov | 2021 | 0.00049448 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-23 13:49 | 2021-11-23 13:50 | 3932 | 000:01 | T | LINEA DE TRANSMISION 115KV | DISPARO DE INTERRUPTOR 1303-03 QUE LLEVA A SU VEZ LA CARGA DEL 1346-04 | S21112300000 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-23 | 3932 | keep | 0 | Nov | 2021 | 0.0026781 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-23 13:56 | 2021-11-23 15:02 | 50 | 001:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA Y SE REEMPLAZO CAJA | S21112300054 | Additional_clients | Cutout Failure | Include | Include | Equipment | 66 | 2021-11-23 | 3300 | keep | 0 | Nov | 2021 | 0.0022476 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-11-23 14:01 | 2021-11-23 14:02 | 2299 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR EN SERVICIO CRUCE POR AVE | C21112300127 | New_Event |  |  | Include | Wildlife | 1 | 2021-11-23 | 2299 | keep | 0 | Nov | 2021 | 0.0015658 | 0.0015658 | Momentary | FALSE | FALSE | Not_TMED_Event | 2299
HUMACAO | 2021-11-23 14:02 | 2021-11-23 16:04 | 1642 | 002:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR PALOMA | C21112300130 | 1st_after_momentary |  |  | Include | Wildlife | 122 | 2021-11-23 | 200324 | keep | 0 | Nov | 2021 | 0.13644 | 0.0011184 | Sustained | FALSE | FALSE | Not_TMED_Event | 1642
SAN JUAN | 2021-11-23 14:07 | 2021-11-23 14:08 | 726 | 000:01 | T | LINEA DE TRANSMISION 115KV | DISPARO DE INTERRUPTOR 1303-03 QUE LLEVA A SU VEZ LA CARGA DEL 1346-04 | S21112300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-23 | 726 | keep | 0 | Nov | 2021 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-11-23 14:07 | 2021-11-23 14:08 | 3932 | 000:01 | T | LINEA DE TRANSMISION 115KV | DISPARO DE INTERRUPTOR 1303-03 QUE LLEVA A SU VEZ LA CARGA DEL 1346-04 | S21112300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-23 | 3932 | keep | 0 | Nov | 2021 | 0.0026781 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
SAN JUAN | 2021-11-23 14:08 | 2021-11-23 21:06 | 65 | 006:58 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU-2 | S21112300116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 418 | 2021-11-23 | 27170 | keep | 0 | Nov | 2021 | 0.018505 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2021-11-23 14:16 | 2021-11-23 17:13 | 10 | 002:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BARRAS SECUNDARIAS EN PEDESTAL | B21112200098 | New_Event | Secondary Wire Down | Include | Include | Equipment | 177 | 2021-11-23 | 1770 | keep | 0 | Nov | 2021 | 0.0012055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-11-23 14:31 | 2021-11-23 15:02 | 7 | 000:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN TRANSFORMADOR Y BARRA EN PEDESTAL | C21112300101 | New_Event | Cutout Failure | Include | Include | Equipment | 31 | 2021-11-23 | 217 | keep | 0 | Nov | 2021 | 0.0001478 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-11-23 14:45 | 2021-11-23 18:09 | 200 | 003:24 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | M21112300129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2021-11-23 | 40800 | keep | 0 | Nov | 2021 | 0.027789 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-11-23 14:56 | 2021-11-23 18:11 | 10 | 003:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S21112300048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 195 | 2021-11-23 | 1950 | keep | 0 | Nov | 2021 | 0.0013281 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-11-23 15:11 | 2021-11-24 14:52 | 5 | 023:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C21112300134 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1421 | 2021-11-23 | 7105 | keep | 0 | Nov | 2021 | 0.0048392 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-11-23 15:20 | 2021-11-23 16:31 | 11 | 001:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR BAJANTE SECUNDARIO Y REPARAR LA SECUNDARIA | C21112300126 | New_Event | Secondary Wire Down | Include | Include | Equipment | 71 | 2021-11-23 | 781 | keep | 0 | Nov | 2021 | 0.00053194 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2021-11-23 15:20 | 2021-11-23 17:52 | 2 | 002:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA SE REEMPLAZO CAJAS QUEMADAS Y CRUCETA PARTIDA A TRANSFORMADOR | M21112300138 | New_Event | Cutout Failure | Include | Include | Equipment | 152 | 2021-11-23 | 304 | keep | 0 | Nov | 2021 | 0.00020705 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2021-11-23 15:24 | 2021-11-23 15:33 | 2000 | 000:09 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1806-02 LLEVANDO PARTE DE LA CARGA 1717-01 | B21112300057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2021-11-23 | 18000 | keep | 0 | Nov | 2021 | 0.01226 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
BAYAMON | 2021-11-23 15:24 | 2021-11-23 15:33 | 4622 | 000:09 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1806-02 LLEVANDO PARTE DE LA CARGA 1717-01 | B21112300057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2021-11-23 | 41598 | keep | 0 | Nov | 2021 | 0.028332 | 0.003148 | Sustained | FALSE | FALSE | Not_TMED_Event | 4622
ARECIBO | 2021-11-23 15:24 | 2021-11-23 18:40 | 50 | 003:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA FUERTES VIENTOS | A21112300036 | New_Event | Bad Weather | Include | Include | Weather | 196 | 2021-11-23 | 9800 | keep | 0 | Nov | 2021 | 0.0066747 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-11-23 15:30 | 2021-11-23 17:12 | 10 | 001:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | B21112300058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 102 | 2021-11-23 | 1020 | keep | 0 | Nov | 2021 | 0.00069472 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-11-23 15:33 | 2021-11-23 18:40 | 2366 | 003:07 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE RETEZO LINEA PRIMARIA CRUZADA | M21112300143 | New_Event | Wire Down | Include | Include | Equipment | 187 | 2021-11-23 | 442442 | keep | 0 | Nov | 2021 | 0.30135 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
UTUADO | 2021-11-23 15:34 | 2021-11-23 17:10 | 20 | 001:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO | A21112300040 | New_Event | Wire Down | Include | Include | Equipment | 96 | 2021-11-23 | 1920 | keep | 0 | Nov | 2021 | 0.0013077 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-11-23 15:47 | 2021-11-23 17:43 | 315 | 001:56 | T | DESGANCHE | DISPARO INTERRUPTOR SE ELIMINO LINEA VACANTE, PARARRAYO Y ENREDADERA CERRADO POR CONTROL | C21112300141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2021-11-23 | 36540 | keep | 0 | Nov | 2021 | 0.024887 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
PONCE | 2021-11-23 15:49 | 2021-11-23 18:25 | 10 | 002:36 | P | OTRAS CAUSAS | SE ABRIO CAJA EN TRANSFORMADOR PARA DESCONECTAR CONTADOR POR ESTAR LA TOMA DEL CLIENTE AVERIADA | P21112300111 | New_Event | Other Causes | Include | Include | Other | 156 | 2021-11-23 | 1560 | keep | 0 | Nov | 2021 | 0.0010625 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-11-23 16:02 | 2021-11-23 20:12 | 30 | 004:10 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21112300076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 250 | 2021-11-23 | 7500 | keep | 0 | Nov | 2021 | 0.0051082 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-11-23 16:05 | 2021-11-23 20:22 | 50 | 004:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN C/L. SE REEMPLAZO CAJA QUEMADA | S21112300087 | New_Event | Cutout Failure | Include | Include | Equipment | 257 | 2021-11-23 | 12850 | keep | 0 | Nov | 2021 | 0.0087521 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-23 16:09 | 2021-11-23 17:50 | 10 | 001:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONECTORES SECUNDARIOS | B21112300075 | New_Event | Secondary Wire Down | Include | Include | Equipment | 101 | 2021-11-23 | 1010 | keep | 0 | Nov | 2021 | 0.00068791 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-11-23 16:10 | 2021-11-23 16:13 | 3718 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S21112300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-23 | 11154 | keep | 0 | Nov | 2021 | 0.0075969 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
HUMACAO | 2021-11-23 16:11 | 2021-11-23 18:20 | 1 | 002:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | C21112300145 | New_Event | Cutout Failure | Include | Include | Equipment | 129 | 2021-11-23 | 129 | keep | 0 | Nov | 2021 | 8.7861e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-23 16:43 | 2021-11-23 18:02 | 290 | 001:19 | P | LINEA DE TRANSMISION 115KV | SE ABRIO INTERRUPTOR DESPUES DE TRANSFERIR 60% DE SU CARGA Y CARGA TOTAL DEL 1346-04. SOLO SE AFECTO 40% DEL 1303-03 PARA DESGANCHAR BAMBUAS EN LINEA 36200. GOI SJ-211123-03 | S21112300012 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 79 | 2021-11-23 | 22910 | keep | 0 | Nov | 2021 | 0.015604 | 0.00019752 | Sustained | FALSE | FALSE | Not_TMED_Event | 290
MAYAGÃœEZ | 2021-11-23 17:06 | 2021-11-23 17:07 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21112300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-23 | 1617 | keep | 0 | Nov | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-11-23 17:06 | 2021-11-23 17:07 | 1017 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21112300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-23 | 1017 | keep | 0 | Nov | 2021 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-11-23 17:06 | 2021-11-23 17:07 | 828 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21112300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-23 | 828 | keep | 0 | Nov | 2021 | 0.00056395 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
BARRANQUITAS | 2021-11-23 17:07 | 2021-11-23 17:55 | 9 | 000:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21112300134 | New_Event | Secondary Wire Down | Include | Include | Equipment | 48 | 2021-11-23 | 432 | keep | 0 | Nov | 2021 | 0.00029423 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2021-11-23 17:08 | 2021-11-23 18:09 | 50 | 001:01 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S21112300102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 61 | 2021-11-23 | 3050 | keep | 0 | Nov | 2021 | 0.0020773 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-11-23 17:12 | 2021-11-23 19:24 | 30 | 002:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR CAJA PRIMARIA DE TRANSFORMADOR TRASPATIO | B21112300058 | New_Event | Cutout Failure | Include | Include | Equipment | 132 | 2021-11-23 | 3960 | keep | 0 | Nov | 2021 | 0.0026971 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2021-11-23 17:22 | 2021-11-23 17:42 | 1483 | 000:20 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE PATRULLO Y NO SE DETECTO LA CAUSA | M21112300123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2021-11-23 | 29660 | keep | 0 | Nov | 2021 | 0.020201 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
GUAYAMA | 2021-11-23 17:23 | 2021-11-23 20:35 | 80 | 003:12 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE REPORTA CAUSA | P21112300099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 192 | 2021-11-23 | 15360 | keep | 0 | Nov | 2021 | 0.010462 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2021-11-23 17:30 | 2021-11-24 11:25 | 30 | 017:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | RISER HACIA T#3 AVERIADO POR ACTO VANDALICO AL PERFORAR CABLE DEL RISER CON UN CLAVO SE CERRO N/O EN T#4 HACIA T#3 | P21112300105 | New_Event |  |  | Include | Wildlife | 1075 | 2021-11-23 | 32250 | keep | 0 | Nov | 2021 | 0.021965 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-11-23 17:38 | 2021-11-24 14:29 | 40 | 020:51 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L NO CAUSA | C21112300153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1251 | 2021-11-23 | 50040 | keep | 0 | Nov | 2021 | 0.034082 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-11-23 17:43 | 2021-11-23 21:37 | 60 | 003:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA VEHICULO IMPACTO POSTE Y CRUZO LINEAS | A21112300051 | New_Event |  |  | Include | Wildlife | 234 | 2021-11-23 | 14040 | keep | 0 | Nov | 2021 | 0.0095626 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2021-11-23 17:52 | 2021-11-24 11:25 | 35 | 017:33 | P | NO SE REPORTO CAUSA | 1 X 40 EN BOVEDA | P21112300093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1053 | 2021-11-23 | 36855 | keep | 0 | Nov | 2021 | 0.025102 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2021-11-23 18:04 | 2021-11-24 11:25 | 50 | 017:21 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | A21112300052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1041 | 2021-11-23 | 52050 | keep | 0 | Nov | 2021 | 0.035451 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-23 18:24 | 2021-11-24 12:00 | 25 | 017:36 | P | DESGANCHE | 3 X 100 EN C/L SE REALIZO DESGANCHE | S21112300118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1056 | 2021-11-23 | 26400 | keep | 0 | Nov | 2021 | 0.017981 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2021-11-23 18:33 | 2021-11-23 19:08 | 80 | 000:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA FUERTES VIENTOS | A21112300055 | New_Event | Bad Weather | Include | Include | Weather | 35 | 2021-11-23 | 2800 | keep | 0 | Nov | 2021 | 0.0019071 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2021-11-23 18:37 | 2021-11-24 12:45 | 10 | 018:08 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA X 25KVA | A21112300056 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1088 | 2021-11-23 | 10880 | keep | 0 | Nov | 2021 | 0.0074103 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-11-23 19:04 | 2021-11-23 19:25 | 29 | 000:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA RETIRAR LINEA VACANTE SOBRE LINEA VIVA | C21112300162 | New_Event | Wire Down | Include | Include | Equipment | 21 | 2021-11-23 | 609 | keep | 0 | Nov | 2021 | 0.00041479 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
CANOVANAS | 2021-11-23 19:36 | 2021-11-23 22:22 | 6 | 002:46 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE | R21112300059 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 166 | 2021-11-23 | 996 | keep | 0 | Nov | 2021 | 0.00067837 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-11-23 19:42 | 2021-11-24 13:00 | 60 | 017:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA PRIMARIA | S21112300125 | New_Event | Cutout Failure | Include | Include | Equipment | 1038 | 2021-11-23 | 62280 | keep | 0 | Nov | 2021 | 0.042419 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-11-23 19:53 | 2021-11-23 21:44 | 50 | 001:51 | P | DESGANCHE | 1 X 50 EN C/L. SE RETIRO PALMA | S21112300128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2021-11-23 | 5550 | keep | 0 | Nov | 2021 | 0.0037801 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-23 20:20 | 2021-11-24 18:11 | 50 | 021:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA TRASPATIO SE TRABAJO CON GOI BY-211124-01 | B21112300097 | New_Event | Cutout Failure | Include | Include | Equipment | 1311 | 2021-11-23 | 65550 | keep | 0 | Nov | 2021 | 0.044646 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-23 20:39 | 2021-11-24 09:30 | 50 | 012:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | S21112300133 | New_Event | Wire Down | Include | Include | Equipment | 771 | 2021-11-23 | 38550 | keep | 0 | Nov | 2021 | 0.026256 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-11-23 20:51 | 2021-11-24 11:10 | 20 | 014:19 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE ENDEREZO POSTE | B21112300099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 859 | 2021-11-23 | 17180 | keep | 0 | Nov | 2021 | 0.011701 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2021-11-23 21:18 | 2021-11-24 07:45 | 165 | 010:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA PAJARO CRUZO FASE | P21112300011 | New_Event |  |  | Include | Wildlife | 627 | 2021-11-23 | 103455 | keep | 0 | Nov | 2021 | 0.070463 | 0.00011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 165
SAN JUAN | 2021-11-23 22:51 | 2021-11-24 13:14 | 60 | 014:23 | P | NO SE REPORTO CAUSA | 2 X 40 EN RISER | S21112300126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 863 | 2021-11-23 | 51780 | keep | 0 | Nov | 2021 | 0.035267 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-11-23 22:54 | 2021-11-23 22:55 | 179 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21112300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-23 | 179 | keep | 0 | Nov | 2021 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
SAN JUAN | 2021-11-24 01:04 | 2021-11-24 12:17 | 100 | 011:13 | P | NO SE REPORTO CAUSA | 1 X 80 Y 1 X 65 EN C/L | S21112400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 673 | 2021-11-24 | 67300 | keep | 0 | Nov | 2021 | 0.045838 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2021-11-24 06:04 | 2021-11-24 10:42 | 500 | 004:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | M21112400002 | New_Event | Cutout Failure | Include | Include | Equipment | 278 | 2021-11-24 | 139000 | keep | 0 | Nov | 2021 | 0.094672 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2021-11-24 06:09 | 2021-11-24 06:11 | 418 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1013-13 Y SE CERRO POR SCADA LLEVA CARGA DEL 1014-16 | S21112400003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-24 | 836 | keep | 0 | Nov | 2021 | 0.0005694 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
BAYAMON | 2021-11-24 06:09 | 2021-11-24 06:11 | 100 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO 1013-13 Y SE CERRO POR SCADA LLEVA CARGA DEL 1014-16 | S21112400003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-24 | 200 | keep | 0 | Nov | 2021 | 0.00013622 | 6.811e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2021-11-24 06:30 | 2021-11-24 06:31 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21112400009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-24 | 3744 | keep | 0 | Nov | 2021 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
MAYAGÃœEZ | 2021-11-24 06:47 | 2021-11-24 13:05 | 60 | 006:18 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21112400004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 378 | 2021-11-24 | 22680 | keep | 0 | Nov | 2021 | 0.015447 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2021-11-24 06:54 | 2021-11-24 11:45 | 100 | 004:51 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | R21112400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 291 | 2021-11-24 | 29100 | keep | 0 | Nov | 2021 | 0.01982 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-11-24 06:55 | 2021-11-24 06:56 | 2126 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO SE CERRO POR CONTROL | C21112400003 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-24 | 2126 | keep | 0 | Nov | 2021 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2021-11-24 06:56 | 2021-11-24 12:44 | 26 | 005:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO BAJANTE DE CORTE DE LINEA | C21112400013 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 348 | 2021-11-24 | 9048 | keep | 0 | Nov | 2021 | 0.0061626 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
FAJARDO | 2021-11-24 07:27 | 2021-11-24 10:19 | 69 | 002:52 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | R21112400003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 172 | 2021-11-24 | 11868 | keep | 0 | Nov | 2021 | 0.0080832 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
GUAYAMA | 2021-11-24 08:00 | 2021-11-24 11:25 | 128 | 003:25 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCER DE FASE PRIMARIA POR RAMA | P21112400010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2021-11-24 | 26240 | keep | 0 | Nov | 2021 | 0.017872 | 8.718e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 128
MAYAGÃœEZ | 2021-11-24 08:00 | 2021-11-24 10:45 | 20 | 002:45 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21112400006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2021-11-24 | 3300 | keep | 0 | Nov | 2021 | 0.0022476 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-11-24 08:01 | 2021-11-24 11:36 | 6 | 003:35 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C21112400007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 215 | 2021-11-24 | 1290 | keep | 0 | Nov | 2021 | 0.00087861 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2021-11-24 08:05 | 2021-11-24 09:35 | 75 | 001:30 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P21112400008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 90 | 2021-11-24 | 6750 | keep | 0 | Nov | 2021 | 0.0045974 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2021-11-24 08:08 | 2021-11-24 11:38 | 1 | 003:30 | P | NO SE REPORTO CAUSA | 1 X 25 EN BANCO TRANSFORMADORES | B21112400005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 210 | 2021-11-24 | 210 | keep | 0 | Nov | 2021 | 0.00014303 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-24 08:24 | 2021-11-25 13:55 | 30 | 029:31 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21112400008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1771 | 2021-11-24 | 53130 | keep | 0 | Nov | 2021 | 0.036187 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-11-24 08:26 | 2021-11-24 10:42 | 100 | 002:16 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO CAUSA | C21112400008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 136 | 2021-11-24 | 13600 | keep | 0 | Nov | 2021 | 0.0092629 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-11-24 08:34 | 2021-11-24 11:19 | 1 | 002:45 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSCLOSURE CLIENTE | S21112400008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 165 | 2021-11-24 | 165 | keep | 0 | Nov | 2021 | 0.00011238 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-11-24 08:36 | 2021-11-24 08:37 | 3420 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21124000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-24 | 3420 | keep | 0 | Nov | 2021 | 0.0023293 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
HUMACAO | 2021-11-24 08:40 | 2021-11-24 10:49 | 2 | 002:09 | P | OTRAS CAUSAS | 1 X 40 EN RISER PROBLEMA DEL CLIENTE | C21112400009 | New_Event | Other Causes | Include | Include | Other | 129 | 2021-11-24 | 258 | keep | 0 | Nov | 2021 | 0.00017572 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2021-11-24 08:44 | 2021-11-24 14:34 | 30 | 005:50 | P | DESGANCHE | 1 X 30 EN C/L | C21112400010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 350 | 2021-11-24 | 10500 | keep | 0 | Nov | 2021 | 0.0071515 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-11-24 08:47 | 2021-11-24 18:16 | 12 | 009:29 | P | SECUNDARIA/DESGANCHE | SE ABRE MONTURA SE REPARO SECUNDARIA Y DESGANCHE | S21112400010 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 569 | 2021-11-24 | 6828 | keep | 0 | Nov | 2021 | 0.0046505 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-11-24 08:54 | 2021-11-24 08:55 | 2106 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | R21112400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-24 | 2106 | keep | 0 | Nov | 2021 | 0.0014344 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
HUMACAO | 2021-11-24 08:54 | 2021-11-24 11:56 | 20 | 003:02 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR LIQUEANDO DE 75 X 75KVA | C21112400011 | New_Event | Service Transformer Failure | Include | Include | Equipment | 182 | 2021-11-24 | 3640 | keep | 0 | Nov | 2021 | 0.0024792 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-11-24 09:03 | 2021-11-24 09:28 | 10 | 000:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR NEUTRAL SECUNDARIO | B21112300027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 25 | 2021-11-24 | 250 | keep | 0 | Nov | 2021 | 0.00017027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-11-24 09:06 | 2021-11-24 15:17 | 40 | 006:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | M21112400014 | New_Event | Wire Down | Include | Include | Equipment | 371 | 2021-11-24 | 14840 | keep | 0 | Nov | 2021 | 0.010107 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-11-24 09:08 | 2021-11-24 15:23 | 15 | 006:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZO DE 2 BARRAS EN PEDESTAL | R21112400014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 375 | 2021-11-24 | 5625 | keep | 0 | Nov | 2021 | 0.0038312 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-11-24 09:11 | 2021-11-24 15:06 | 1 | 005:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON 2 CAJAS PRIMARIAS EN RISER | S21112400022 | New_Event | Cutout Failure | Include | Include | Equipment | 355 | 2021-11-24 | 355 | keep | 0 | Nov | 2021 | 0.00024179 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-11-24 09:12 | 2021-11-24 16:02 | 4 | 006:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR BARRAS DE PEDESTAL | C21112400012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 410 | 2021-11-24 | 1640 | keep | 0 | Nov | 2021 | 0.001117 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2021-11-24 09:36 | 2021-11-24 09:37 | 485 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL ALIMENTADOR | P21112400018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-24 | 485 | keep | 0 | Nov | 2021 | 0.00033033 | 0.00033033 | Momentary | FALSE | FALSE | Not_TMED_Event | 485
MAYAGÃœEZ | 2021-11-24 09:36 | 2021-11-24 17:44 | 20 | 008:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO BAJANTE DE CORTE DE LINEA | M21112400015 | New_Event | Wire Down | Include | Include | Equipment | 488 | 2021-11-24 | 9760 | keep | 0 | Nov | 2021 | 0.0066475 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-11-24 09:43 | 2021-11-24 18:35 | 60 | 008:52 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN AEREO PROVISIONAL HACIA SU-2L SE CONSTRUYO NUEVO AEREO PROVISIONAL HACIA T-7 | R21112400017 | New_Event | UG Cable Fault | Include | Include | Equipment | 532 | 2021-11-24 | 31920 | keep | 0 | Nov | 2021 | 0.021741 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-11-24 09:45 | 2021-11-24 10:15 | 10 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | A21112400001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2021-11-24 | 300 | keep | 0 | Nov | 2021 | 0.00020433 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-11-24 09:52 | 2021-11-24 19:41 | 30 | 009:49 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21112400018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 589 | 2021-11-24 | 17670 | keep | 0 | Nov | 2021 | 0.012035 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-11-24 10:05 | 2021-11-24 10:51 | 4 | 000:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO VARIAS CONDICIONES EN LA LINEA | C21112400001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 46 | 2021-11-24 | 184 | keep | 0 | Nov | 2021 | 0.00012532 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
GUAYAMA | 2021-11-24 10:08 | 2021-11-24 11:30 | 5 | 001:22 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO DE TRANSFORMADOR DE 50 KVA A 7620 VOLTS CON PERDIDA DE ACEITE POR OTRO IGUAL CAPACIDAD | P21112400020 | New_Event | Service Transformer Failure | Include | Include | Equipment | 82 | 2021-11-24 | 410 | keep | 0 | Nov | 2021 | 0.00027925 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2021-11-24 10:10 | 2021-11-24 11:37 | 53 | 001:27 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR CON DERRAME DE ACEITE DE 50 X 50KVA | C21112400005 | New_Event | Service Transformer Failure | Include | Include | Equipment | 87 | 2021-11-24 | 4611 | keep | 0 | Nov | 2021 | 0.0031405 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
MAYAGÃœEZ | 2021-11-24 10:12 | 2021-11-24 12:15 | 10 | 002:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO NEUTRAL SECUNDARIO PARTIDO | M21112400024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 123 | 2021-11-24 | 1230 | keep | 0 | Nov | 2021 | 0.00083775 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-11-24 10:37 | 2021-11-25 00:20 | 16 | 013:43 | P | ESTRUCTURA AVERIADA | ABRIO CORTE DE LINEA PARA REEMPLAZAR POSTE | R21112400021 | New_Event | Defective Pole | Include | Include | Equipment | 823 | 2021-11-24 | 13168 | keep | 0 | Nov | 2021 | 0.0089687 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
AGUADILLA | 2021-11-24 11:18 | 2021-11-24 15:53 | 10 | 004:35 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 15KVA X 25KVA | M21112400028 | New_Event | Service Transformer Failure | Include | Include | Equipment | 275 | 2021-11-24 | 2750 | keep | 0 | Nov | 2021 | 0.001873 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2021-11-24 11:20 | 2021-11-24 13:06 | 10 | 001:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR PUENTES SECUNDARIOS | P21112400025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 106 | 2021-11-24 | 1060 | keep | 0 | Nov | 2021 | 0.00072196 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-24 11:40 | 2021-11-24 15:24 | 20 | 003:44 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 25 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21112400009 | New_Event | Bad Weather | Include | Include | Weather | 224 | 2021-11-24 | 4480 | keep | 0 | Nov | 2021 | 0.0030513 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-11-24 11:46 | 2021-11-24 18:09 | 1 | 006:23 | P | TRANSFORMADOR AVERIADO | SE AJUSTO BUCHING SECUNDARIO A TRANSFORMADOR | A21112400011 | New_Event | Service Transformer Failure | Include | Include | Equipment | 383 | 2021-11-24 | 383 | keep | 0 | Nov | 2021 | 0.00026086 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-24 12:07 | 2021-11-24 17:04 | 30 | 004:57 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA Y 1 X 25 EN SU 2 | B21112400015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 297 | 2021-11-24 | 8910 | keep | 0 | Nov | 2021 | 0.0060686 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2021-11-24 12:07 | 2021-11-24 17:46 | 6 | 005:39 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 10 KVA X 25 KVA | C21112400020 | New_Event | Service Transformer Failure | Include | Include | Equipment | 339 | 2021-11-24 | 2034 | keep | 0 | Nov | 2021 | 0.0013853 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-11-24 12:14 | 2021-11-24 15:53 | 321 | 003:39 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA DESGANCHE | S21112400048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2021-11-24 | 70299 | keep | 0 | Nov | 2021 | 0.04788 | 0.00021863 | Sustained | FALSE | FALSE | Not_TMED_Event | 321
ARECIBO | 2021-11-24 12:15 | 2021-11-24 16:35 | 5 | 004:20 | P | DESGANCHE | SE REEMPLAZO 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21112400014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 260 | 2021-11-24 | 1300 | keep | 0 | Nov | 2021 | 0.00088542 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2021-11-24 12:25 | 2021-11-24 15:41 | 20 | 003:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 10 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA PARTIDA | M21112400032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 196 | 2021-11-24 | 3920 | keep | 0 | Nov | 2021 | 0.0026699 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-11-24 12:43 | 2021-11-24 12:46 | 3070 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B21112400016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-24 | 9210 | keep | 0 | Nov | 2021 | 0.0062729 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2021-11-24 12:46 | 2021-11-24 17:58 | 60 | 005:12 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | B21112400019 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 312 | 2021-11-24 | 18720 | keep | 0 | Nov | 2021 | 0.01275 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-11-24 13:19 | 2021-11-24 15:02 | 25 | 001:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | S21112400044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 103 | 2021-11-24 | 2575 | keep | 0 | Nov | 2021 | 0.0017538 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-11-24 13:20 | 2021-11-24 14:59 | 12 | 001:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | S21112300106 | New_Event | Secondary Wire Down | Include | Include | Equipment | 99 | 2021-11-24 | 1188 | keep | 0 | Nov | 2021 | 0.00080914 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2021-11-24 13:28 | 2021-11-24 13:44 | 1 | 000:16 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21112400020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 16 | 2021-11-24 | 16 | keep | 0 | Nov | 2021 | 1.0898e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-24 13:30 | 2021-11-24 13:31 | 600 | 000:01 | P | LINEA DE TRANSMISION 115KV | DISPARO L-36200 CRUCETA PARTIDA ENTRE 36265 Y VILLA BETINA SU 20% POR EL 1303-02 | S21112400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-24 | 600 | keep | 0 | Nov | 2021 | 0.00040866 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2021-11-24 13:30 | 2021-11-24 13:31 | 108 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 CRUCETA PARTIDA ENTRE MOD-36265 Y VILLA BETINA | S21112400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-24 | 108 | keep | 0 | Nov | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
SAN JUAN | 2021-11-24 13:30 | 2021-11-24 13:31 | 1368 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 CRUCETA PARTIDA ENTRE MOD-36265 Y VILLA BETINA | S21112400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-24 | 1368 | keep | 0 | Nov | 2021 | 0.00093174 | 0.00093174 | Momentary | FALSE | FALSE | Not_TMED_Event | 1368
SAN JUAN | 2021-11-24 13:30 | 2021-11-24 13:31 | 2064 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 CRUCETA PARTIDA ENTRE MOD-36265 Y VILLA BETINA | S21112400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-24 | 2064 | keep | 0 | Nov | 2021 | 0.0014058 | 0.0014058 | Momentary | FALSE | FALSE | Not_TMED_Event | 2064
SAN JUAN | 2021-11-24 13:30 | 2021-11-24 13:31 | 1681 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 CRUCETA PARTIDA ENTRE 36265 Y VILLA BETINA SU CARGA POR 1303-04 | S21112400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-24 | 1681 | keep | 0 | Nov | 2021 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-11-24 13:30 | 2021-11-24 13:31 | 2435 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 CRUCETA PARTIDA ENTRE 36265 Y VILLA BETINA LLEVA 20% DEL 1204-2 | S21112400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-24 | 2435 | keep | 0 | Nov | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2021-11-24 13:30 | 2021-11-24 13:31 | 726 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 CRUCETA PARTIDA ENTRE 36265 Y VILLA BETINA LLEVA 1346-4 | S21112400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-24 | 726 | keep | 0 | Nov | 2021 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-11-24 13:30 | 2021-11-24 13:31 | 225 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 CRUCETA PARTIDA ENTRE 36265 Y VILLA BETINA LLEVA CARGA 1303-1 Y 1346-6 | S21112400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-24 | 225 | keep | 0 | Nov | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-11-24 13:30 | 2021-11-24 13:31 | 870 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 CRUCETA PARTIDA ENTRE 36265 Y VILLA BETINA | S21112400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-24 | 870 | keep | 0 | Nov | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2021-11-24 13:30 | 2021-11-24 13:31 | 3932 | 000:01 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 CRUCETA PARTIDA ENTRE 36265 Y VILLA BETINA SU CARGA POR 1303-3 | S21112400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-24 | 3932 | keep | 0 | Nov | 2021 | 0.0026781 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
SAN JUAN | 2021-11-24 13:30 | 2021-11-24 13:31 | 1598 | 000:01 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36200 CRUCETA PARTIDA ENTRE 36265 Y VILLA BETINA LLEVA CARGA 1303-1 Y 1346-6 | S21112400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-24 | 1598 | keep | 0 | Nov | 2021 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2021-11-24 13:33 | 2021-11-24 13:39 | 600 | 000:06 | P | LINEA DE TRANSMISION 115KV | DISPARO L-36200 CRUCETA PARTIDA ENTRE MOD-36265 Y VILLA BETINA SU 20% 1303-2 | S21112400000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-11-24 | 3600 | keep | 0 | Nov | 2021 | 0.0024519 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2021-11-24 13:33 | 2021-11-24 14:21 | 108 | 000:48 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 SE ENCONTRO CRUCETA PARTIDA ENTRE MOD 36265 Y VILLA BETINA | S21112400000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 48 | 2021-11-24 | 5184 | keep | 0 | Nov | 2021 | 0.0035308 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
SAN JUAN | 2021-11-24 13:33 | 2021-11-24 14:21 | 1368 | 000:48 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 SE ENCONTRO CRUCETA PARTIDA ENTRE MOD 36265 Y VILLA BETINA | S21112400000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 48 | 2021-11-24 | 65664 | keep | 0 | Nov | 2021 | 0.044723 | 0.00093174 | Sustained | FALSE | FALSE | Not_TMED_Event | 1368
SAN JUAN | 2021-11-24 13:33 | 2021-11-24 14:21 | 2064 | 000:48 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 SE ENCONTRO CRUCETA PARTIDA ENTRE MOD 36265 Y VILLA BETINA | S21112400000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 48 | 2021-11-24 | 99072 | keep | 0 | Nov | 2021 | 0.067477 | 0.0014058 | Sustained | FALSE | FALSE | Not_TMED_Event | 2064
SAN JUAN | 2021-11-24 13:33 | 2021-11-24 13:39 | 1681 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 CRUCETA PARTIDA ENTRE MOD-36265 Y VILLA BETINA | S21112400000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-11-24 | 10086 | keep | 0 | Nov | 2021 | 0.0068695 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-11-24 13:33 | 2021-11-24 13:39 | 2435 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 CRUCETA PARTIDA ENTRE MOD-36265 Y VILLA BETINA LLEVA 20% 1204-2 | S21112400000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-11-24 | 14610 | keep | 0 | Nov | 2021 | 0.0099508 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2021-11-24 13:33 | 2021-11-24 13:39 | 726 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 CRUCETA PARTIDA ENTRE MOD-36265 Y VILLA BETINA LLEVA 1346-4 | S21112400000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-11-24 | 4356 | keep | 0 | Nov | 2021 | 0.0029669 | 0.00049448 | Sustained | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-11-24 13:33 | 2021-11-24 13:39 | 225 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 CRUCETA PARTIDA ENTRE MOD-36265 Y VILLA BETINA LLEVA CARGA 1303-1 Y LLEVA 1346-6 | S21112400000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-11-24 | 1350 | keep | 0 | Nov | 2021 | 0.00091948 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-11-24 13:33 | 2021-11-24 13:39 | 870 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO L-36200 CRUCETA PARTIDA ENTRE MOD-36265 Y VILLA BETINA LLEVA 1303-4 | S21112400000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-11-24 | 5220 | keep | 0 | Nov | 2021 | 0.0035553 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2021-11-24 13:33 | 2021-11-24 13:39 | 3932 | 000:06 | T | LINEA DE TRANSMISION 115KV | DISPARO L-36200 CRUCETA PARTIDA ENTRE MOD-36265 Y VILLA BETINA SU CARGA POR 1303-3 | S21112400000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-11-24 | 23592 | keep | 0 | Nov | 2021 | 0.016068 | 0.0026781 | Sustained | FALSE | FALSE | Not_TMED_Event | 3932
SAN JUAN | 2021-11-24 13:33 | 2021-11-24 13:39 | 1598 | 000:06 | T | LINEA DE TRANSMISION 115KV | DISPARO L-36200 CRUCETA PARTIDA ENTRE MOD-36265 Y VILLA BETINA LLEVA CARGA 1303-1 Y LLEVA 1346-6 | S21112400000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-11-24 | 9588 | keep | 0 | Nov | 2021 | 0.0065303 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
ARECIBO | 2021-11-24 13:49 | 2021-11-24 16:34 | 1 | 002:45 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO RAMAS Y SE REPARO SECUNDARIA | A21112400020 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 165 | 2021-11-24 | 165 | keep | 0 | Nov | 2021 | 0.00011238 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-11-24 13:59 | 2021-11-24 17:31 | 7 | 003:32 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | C21112400029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 212 | 2021-11-24 | 1484 | keep | 0 | Nov | 2021 | 0.0010107 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2021-11-24 14:08 | 2021-11-24 15:46 | 2696 | 001:38 | T | CABLE SOTERRADO AVERIADO | TOMA SOTERRADA AVERIADA HACIA EDIFICIO RAMIREZ | P21112400040 | New_Event | UG Cable Fault | Include | Include | Equipment | 98 | 2021-11-24 | 264208 | keep | 0 | Nov | 2021 | 0.17995 | 0.0018362 | Sustained | FALSE | FALSE | Not_TMED_Event | 2696
SAN JUAN | 2021-11-24 14:29 | 2021-11-24 16:38 | 85 | 002:09 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | S21112400102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2021-11-24 | 10965 | keep | 0 | Nov | 2021 | 0.0074682 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
BAYAMON | 2021-11-24 14:38 | 2021-11-24 16:03 | 10 | 001:25 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA REALIZAR DESGANCHE SECUNDARIO Y REPARAR TOMA | B21112400009 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 85 | 2021-11-24 | 850 | keep | 0 | Nov | 2021 | 0.00057893 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-11-24 14:51 | 2021-11-24 14:52 | 4035 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE ALIMENTADOR PUENTES QUEMADOS EN CONVERTIDOR 13KV A 4 KV | P21112400035 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-24 | 4035 | keep | 0 | Nov | 2021 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
PONCE | 2021-11-24 14:52 | 2021-11-24 14:59 | 1017 | 000:07 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE ALIMENTADOR PUENTES QUEMADOS EN CONVERTIDOR 13KV A 4 KV | P21112400035 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 7 | 2021-11-24 | 7119 | keep | 0 | Nov | 2021 | 0.0048487 | 0.00069267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1017
ARECIBO | 2021-11-24 14:57 | 2021-11-24 19:06 | 9 | 004:09 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50 KVA QUEMADO POR 50 KVA | A21112400027 | New_Event | Service Transformer Failure | Include | Include | Equipment | 249 | 2021-11-24 | 2241 | keep | 0 | Nov | 2021 | 0.0015263 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
FAJARDO | 2021-11-24 14:59 | 2021-11-24 15:48 | 950 | 000:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 200 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | R21112400039 | New_Event | Cutout Failure | Include | Include | Equipment | 49 | 2021-11-24 | 46550 | keep | 0 | Nov | 2021 | 0.031705 | 0.00064704 | Sustained | FALSE | FALSE | Not_TMED_Event | 950
PONCE | 2021-11-24 14:59 | 2021-11-24 15:00 | 4035 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE ALIMENTADOR PUENTE QUEMADO EN CONVERTIDOR | P21112400036 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2021-11-24 | 4035 | keep | 0 | Nov | 2021 | 0.0027482 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-11-24 15:00 | 2021-11-24 15:02 | 1017 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE ALIMENTADOR PUENTES QUEMADOS EN CONVERTIDOR 13KV A 4 KV | P21112400041 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 2 | 2021-11-24 | 2034 | keep | 0 | Nov | 2021 | 0.0013853 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
PONCE | 2021-11-24 15:02 | 2021-11-24 15:03 | 4035 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR BAJANTE PRIMARIO AVERIADO EN ENTRADA DE CONVERTIDOR | P21112400041 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-11-24 | 4035 | keep | 0 | Nov | 2021 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
PONCE | 2021-11-24 15:03 | 2021-11-24 18:30 | 1013 | 003:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CONVERTIDOR DE 13 KV A 4 KV CON BAJANTE PRIMARIO AVERIADO SE TRANSFIERE CARGA A 4502-02 | P21112400074 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 207 | 2021-11-24 | 209691 | keep | 0 | Nov | 2021 | 0.14282 | 0.00068995 | Sustained | FALSE | FALSE | Not_TMED_Event | 1013
BAYAMON | 2021-11-24 15:05 | 2021-11-24 17:30 | 1983 | 002:25 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9600 INTERRUPTOR 1801-02 LLEVA 1711-04 Y PARTE 1717-01 | B21112400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 145 | 2021-11-24 | 287535 | keep | 0 | Nov | 2021 | 0.19584 | 0.0013506 | Sustained | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-11-24 15:05 | 2021-11-24 17:30 | 2000 | 002:25 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9600 INTERRUPTOR 1801-02 LLEVA 1711-04 Y PARTE 1717-01 | B21112400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 145 | 2021-11-24 | 290000 | keep | 0 | Nov | 2021 | 0.19752 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
BAYAMON | 2021-11-24 15:05 | 2021-11-24 17:24 | 966 | 002:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9600 | B21112400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 139 | 2021-11-24 | 134274 | keep | 0 | Nov | 2021 | 0.091453 | 0.00065794 | Sustained | FALSE | FALSE | Not_TMED_Event | 966
BAYAMON | 2021-11-24 15:05 | 2021-11-24 17:30 | 186 | 002:25 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9600 INTERRUPTOR 1801-02 LLEVA 1711-04 Y PARTE 1717-01 | B21112400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 145 | 2021-11-24 | 26970 | keep | 0 | Nov | 2021 | 0.018369 | 0.00012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2021-11-24 15:05 | 2021-11-24 17:26 | 1746 | 002:21 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9600 | B21112400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 141 | 2021-11-24 | 246186 | keep | 0 | Nov | 2021 | 0.16768 | 0.0011892 | Sustained | FALSE | FALSE | Not_TMED_Event | 1746
BAYAMON | 2021-11-24 15:05 | 2021-11-24 17:30 | 112 | 002:25 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9600 | B21112400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 145 | 2021-11-24 | 16240 | keep | 0 | Nov | 2021 | 0.011061 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
BAYAMON | 2021-11-24 15:05 | 2021-11-24 21:33 | 67 | 006:28 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9600 | B21112400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 388 | 2021-11-24 | 25996 | keep | 0 | Nov | 2021 | 0.017706 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2021-11-24 15:05 | 2021-11-24 21:33 | 1587 | 006:28 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9600 | B21112400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 388 | 2021-11-24 | 615756 | keep | 0 | Nov | 2021 | 0.41939 | 0.0010809 | Sustained | FALSE | FALSE | Not_TMED_Event | 1587
BAYAMON | 2021-11-24 15:05 | 2021-11-24 21:33 | 521 | 006:28 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9600 | B21112400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 388 | 2021-11-24 | 202148 | keep | 0 | Nov | 2021 | 0.13768 | 0.00035485 | Sustained | FALSE | FALSE | Not_TMED_Event | 521
BAYAMON | 2021-11-24 15:05 | 2021-11-24 21:33 | 1307 | 006:28 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9600 | B21112400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 388 | 2021-11-24 | 507116 | keep | 0 | Nov | 2021 | 0.34539 | 0.00089019 | Sustained | FALSE | FALSE | Not_TMED_Event | 1307
ARECIBO | 2021-11-24 15:15 | 2021-11-24 18:35 | 20 | 003:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21112400028 | New_Event | Bad Weather | Include | Include | Weather | 200 | 2021-11-24 | 4000 | keep | 0 | Nov | 2021 | 0.0027244 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-11-24 15:18 | 2021-11-24 16:58 | 837 | 001:40 | T | NO SE REPORTO CAUSA | SE ABRIO MACHETE CALLE SERGIO CUEVAS Y SE CERRO N/O POR 1401-7 CALLE SARGENTO MEDINA ESQ. CESAR GONZALEZ 60% EN SERVICIO | S21112400141 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 100 | 2021-11-24 | 83700 | keep | 0 | Nov | 2021 | 0.057008 | 0.00057008 | Sustained | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2021-11-24 15:18 | 2021-11-24 16:26 | 908 | 001:08 | T | NO SE REPORTO CAUSA | SE ABRIO N/O CONTRA 1401-6 CALLE CESAR GONZALEZ ESQ. SARGENTO MEDINA SE CERRO POR CONTROL QUEDO EN SERVICIO 1401-7 | S21112400141 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 68 | 2021-11-24 | 61744 | keep | 0 | Nov | 2021 | 0.042054 | 0.00061843 | Sustained | FALSE | FALSE | Not_TMED_Event | 908
UTUADO | 2021-11-24 15:28 | 2021-11-24 20:25 | 60 | 004:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS PARTIDAS | A21112400029 | New_Event | Wire Down | Include | Include | Equipment | 297 | 2021-11-24 | 17820 | keep | 0 | Nov | 2021 | 0.012137 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-11-24 15:37 | 2021-11-24 16:37 | 30 | 001:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO DESCARGAS ELECTRICAS | A21112400030 | New_Event | Bad Weather | Include | Include | Weather | 60 | 2021-11-24 | 1800 | keep | 0 | Nov | 2021 | 0.001226 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-11-24 15:43 | 2021-11-24 19:43 | 100 | 004:00 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21112400050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2021-11-24 | 24000 | keep | 0 | Nov | 2021 | 0.016346 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2021-11-24 15:46 | 2021-11-24 16:40 | 4 | 000:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFOMADOR PARA REEMPLAZAR CONECTORES EN BAJANTE SECUNDARIO Y REPARAR VARIOS PUNTOS EN SECUNDARIA | R21112400042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 54 | 2021-11-24 | 216 | keep | 0 | Nov | 2021 | 0.00014712 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2021-11-24 15:46 | 2021-11-24 15:53 | 2022 | 000:07 | P | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR POR CABLE PRIMARIO SOTERRADO AVERIADO EDIFICIO RAMIREZ | P21112400050 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 7 | 2021-11-24 | 14154 | keep | 0 | Nov | 2021 | 0.0096402 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-11-24 15:53 | 2021-11-24 15:55 | 2696 | 000:02 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR POR CABLE PRIMARIO SOTERRADO AVERIADO EDIFICIO RAMIREZ | P21112400052 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 2 | 2021-11-24 | 5392 | keep | 0 | Nov | 2021 | 0.0036725 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-11-24 15:55 | 2021-11-24 17:12 | 674 | 001:17 | P | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR POR CABLE PRIMARIO SOTERRADO AVERIADO EDIFICIO RAMIREZ | P21112400057 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 77 | 2021-11-24 | 51898 | keep | 0 | Nov | 2021 | 0.035347 | 0.00045906 | Sustained | FALSE | FALSE | Not_TMED_Event | 674
FAJARDO | 2021-11-24 15:58 | 2021-11-24 17:23 | 17 | 001:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZO DE BARRA EN PEDESTAL | R21112400044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 85 | 2021-11-24 | 1445 | keep | 0 | Nov | 2021 | 0.00098418 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2021-11-24 16:11 | 2021-11-24 19:22 | 30 | 003:11 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21112400115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 191 | 2021-11-24 | 5730 | keep | 0 | Nov | 2021 | 0.0039027 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-11-24 16:22 | 2021-11-24 19:08 | 80 | 002:46 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21112400054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2021-11-24 | 13280 | keep | 0 | Nov | 2021 | 0.0090449 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2021-11-24 16:33 | 2021-11-24 17:29 | 1 | 000:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN BANCO DE TRANSFORMADORES SE REEMPLAZO PORTAFUSIBLE | R21112400046 | New_Event | Cutout Failure | Include | Include | Equipment | 56 | 2021-11-24 | 56 | keep | 0 | Nov | 2021 | 3.8141e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2021-11-24 16:53 | 2021-11-24 18:32 | 2280 | 001:39 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO SE SECCIONALIZO CONDUCTOR EN EL SUELO CARGAS POR EL 9902-03 | C21112400036 | New_Event | Wire Down | Include | Include | Equipment | 99 | 2021-11-24 | 225720 | keep | 0 | Nov | 2021 | 0.15374 | 0.0015529 | Sustained | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2021-11-24 16:53 | 2021-11-24 18:32 | 1617 | 001:39 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO LLEVA LA CARGA DEL 9902-02 | C21112400036 | New_Event | Wire Down | Include | Include | Equipment | 99 | 2021-11-24 | 160083 | keep | 0 | Nov | 2021 | 0.10903 | 0.0011013 | Sustained | FALSE | FALSE | Not_TMED_Event | 1617
SAN JUAN | 2021-11-24 16:58 | 2021-11-24 18:22 | 206 | 001:24 | P | NO SE REPORTO CAUSA | SE CERRO MACHETE A SU-3 100% EN SERVICIO SU CARGA POR 1401-7 | S21112400141 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 84 | 2021-11-24 | 17304 | keep | 0 | Nov | 2021 | 0.011786 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-24 17:06 | 2021-11-24 17:46 | 25 | 000:40 | P | NO SE REPORTO CAUSA | 1 X 30 EN TRANSFORMADOR | S21112400165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 40 | 2021-11-24 | 1000 | keep | 0 | Nov | 2021 | 0.0006811 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-11-24 17:10 | 2021-11-24 21:12 | 40 | 004:02 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | S21112400167 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 242 | 2021-11-24 | 9680 | keep | 0 | Nov | 2021 | 0.006593 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-11-24 17:10 | 2021-11-24 18:46 | 5 | 001:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA PARTIDA | A21112400034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 96 | 2021-11-24 | 480 | keep | 0 | Nov | 2021 | 0.00032693 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-11-24 17:13 | 2021-11-24 18:07 | 28 | 000:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIA | R21112400016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 54 | 2021-11-24 | 1512 | keep | 0 | Nov | 2021 | 0.0010298 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
BAYAMON | 2021-11-24 17:16 | 2021-11-24 21:00 | 534 | 003:44 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA SAN FERNANDO SE REMONTO LOCKOUT Y SE PROBO QUEDO EN SERVICIO | S21112400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 224 | 2021-11-24 | 119616 | keep | 0 | Nov | 2021 | 0.08147 | 0.0003637 | Sustained | FALSE | FALSE | Not_TMED_Event | 534
BAYAMON | 2021-11-24 17:16 | 2021-11-24 21:00 | 790 | 003:44 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA SAN FERNANDO SE REMONTO LOCKOUT Y SE PROBO QUEDO EN SERVICIO | S21112400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 224 | 2021-11-24 | 176960 | keep | 0 | Nov | 2021 | 0.12053 | 0.00053807 | Sustained | FALSE | FALSE | Not_TMED_Event | 790
BAYAMON | 2021-11-24 17:16 | 2021-11-24 21:00 | 40 | 003:44 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA SAN FERNANDO SE REMONTO LOCKOUT Y SE PROBO QUEDO EN SERVICIO 80% DE SU CARGA POR 1910-1 | S21112400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 224 | 2021-11-24 | 8960 | keep | 0 | Nov | 2021 | 0.0061026 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-24 17:16 | 2021-11-24 21:00 | 433 | 003:44 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA SAN FERNANDO SE REMONTO LOCKOUT Y SE PROBO QUEDO EN SERVICIO | S21112400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 224 | 2021-11-24 | 96992 | keep | 0 | Nov | 2021 | 0.066061 | 0.00029491 | Sustained | FALSE | FALSE | Not_TMED_Event | 433
BAYAMON | 2021-11-24 17:16 | 2021-11-24 21:00 | 558 | 003:44 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA SAN FERNANDO SE REMONTO LOCKOUT Y SE PROBO QUEDO EN SERVICIO LLEVA CARGA DEL 1519-1 | S21112400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 224 | 2021-11-24 | 124992 | keep | 0 | Nov | 2021 | 0.085131 | 0.00038005 | Sustained | FALSE | FALSE | Not_TMED_Event | 558
BAYAMON | 2021-11-24 17:16 | 2021-11-24 21:00 | 271 | 003:44 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA SAN FERNANDO SE REMONTO LOCKOUT Y SE PROBO BARRA | S21112400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 224 | 2021-11-24 | 60704 | keep | 0 | Nov | 2021 | 0.041345 | 0.00018458 | Sustained | FALSE | FALSE | Not_TMED_Event | 271
SAN JUAN | 2021-11-24 17:19 | 2021-11-24 17:20 | 3957 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21112400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-24 | 3957 | keep | 0 | Nov | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
YAUCO | 2021-11-24 17:23 | 2021-11-25 09:57 | 19 | 016:34 | P | DESGANCHE | 1 X 30 EN TRANSFORMADOR POR DESGANCHE | P21112400075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 994 | 2021-11-24 | 18886 | keep | 0 | Nov | 2021 | 0.012863 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
PONCE | 2021-11-24 17:29 | 2021-11-24 17:34 | 1922 | 000:05 | S | LINEA DE TRANSMISION 38KV | SE ABRE LINEA 4800 PARA CERRAR GOAB | P21112400087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-11-24 | 9610 | keep | 0 | Nov | 2021 | 0.0065453 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
PONCE | 2021-11-24 17:29 | 2021-11-24 17:34 | 2235 | 000:05 | S | LINEA DE TRANSMISION 38KV | SE ABRE LINEA 4800 PARA CERRAR GOAB | P21112400087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-11-24 | 11175 | keep | 0 | Nov | 2021 | 0.0076112 | 0.0015222 | Momentary | FALSE | FALSE | Not_TMED_Event | 2235
PONCE | 2021-11-24 17:29 | 2021-11-24 17:34 | 713 | 000:05 | S | LINEA DE TRANSMISION 38KV | SE ABRE LINEA 4800 PARA CERRAR GOAB | P21112400087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-11-24 | 3565 | keep | 0 | Nov | 2021 | 0.0024281 | 0.00048562 | Momentary | FALSE | FALSE | Not_TMED_Event | 713
PONCE | 2021-11-24 17:29 | 2021-11-24 17:34 | 1067 | 000:05 | S | LINEA DE TRANSMISION 38KV | SE ABRE LINEA 4800 PARA CERRAR GOAB | P21112400087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-11-24 | 5335 | keep | 0 | Nov | 2021 | 0.0036336 | 0.00072673 | Momentary | FALSE | FALSE | Not_TMED_Event | 1067
PONCE | 2021-11-24 17:29 | 2021-11-24 17:34 | 1293 | 000:05 | S | LINEA DE TRANSMISION 38KV | SE ABRE LINEA 4800 PARA CERRAR GOAB | P21112400086 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-11-24 | 6465 | keep | 0 | Nov | 2021 | 0.0044033 | 0.00088066 | Momentary | FALSE | FALSE | Not_TMED_Event | 1293
PONCE | 2021-11-24 17:29 | 2021-11-24 17:34 | 426 | 000:05 | S | LINEA DE TRANSMISION 38KV | SE ABRE LINEA 4800 PARA CERRAR GOAB | P21112400086 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-11-24 | 2130 | keep | 0 | Nov | 2021 | 0.0014507 | 0.00029015 | Momentary | FALSE | FALSE | Not_TMED_Event | 426
PONCE | 2021-11-24 17:29 | 2021-11-24 17:34 | 1556 | 000:05 | S | LINEA DE TRANSMISION 38KV | SE ABRE LINEA 4800 PARA CERRAR GOAB | P21112400086 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-11-24 | 7780 | keep | 0 | Nov | 2021 | 0.0052989 | 0.0010598 | Momentary | FALSE | FALSE | Not_TMED_Event | 1556
PONCE | 2021-11-24 17:30 | 2021-11-24 17:55 | 10 | 000:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR PUENTES SECUNDARIOS | P21112400054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 25 | 2021-11-24 | 250 | keep | 0 | Nov | 2021 | 0.00017027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-24 17:58 | 2021-11-24 18:13 | 10 | 000:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BARRAS SECUNDARIAS EN PEDESTAL | B21112400177 | New_Event | Secondary Wire Down | Include | Include | Equipment | 15 | 2021-11-24 | 150 | keep | 0 | Nov | 2021 | 0.00010216 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-11-24 18:28 | 2021-11-24 22:18 | 18 | 003:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON LINEAS SECUNDARIAS PARTIDAS | M21112400059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 230 | 2021-11-24 | 4140 | keep | 0 | Nov | 2021 | 0.0028197 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BARRANQUITAS | 2021-11-24 18:32 | 2021-11-24 20:52 | 2280 | 002:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR | C21112400036 | Partial_restoration | Wire Down | Include | Include | Equipment | 140 | 2021-11-24 | 319200 | keep | 0 | Nov | 2021 | 0.21741 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-24 18:37 | 2021-11-24 20:17 | 724 | 001:40 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21112400247 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 100 | 2021-11-24 | 72400 | keep | 0 | Nov | 2021 | 0.049311 | 0.00049311 | Sustained | FALSE | FALSE | Not_TMED_Event | 724
CAGUAS | 2021-11-24 18:53 | 2021-11-25 09:14 | 80 | 014:21 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21112400051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 861 | 2021-11-24 | 68880 | keep | 0 | Nov | 2021 | 0.046914 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-11-24 21:14 | 2021-11-25 10:27 | 35 | 013:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO PUENTE A CAJA | S21112400308 | New_Event | Wire Down | Include | Include | Equipment | 793 | 2021-11-24 | 27755 | keep | 0 | Nov | 2021 | 0.018904 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2021-11-24 21:20 | 2021-11-25 10:07 | 50 | 012:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO PUENTE A CAJA PRIMARIA | S21112400310 | New_Event | Wire Down | Include | Include | Equipment | 767 | 2021-11-24 | 38350 | keep | 0 | Nov | 2021 | 0.02612 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-24 21:24 | 2021-11-25 11:45 | 40 | 014:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | S21112400311 | New_Event | Cutout Failure | Include | Include | Equipment | 861 | 2021-11-24 | 34440 | keep | 0 | Nov | 2021 | 0.023457 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-24 21:28 | 2021-11-25 13:27 | 10 | 015:59 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR | S21112400313 | New_Event | Vegetation Contact | Include | Include | Vegetation | 959 | 2021-11-24 | 9590 | keep | 0 | Nov | 2021 | 0.0065317 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-11-24 21:36 | 2021-11-25 10:07 | 40 | 012:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA LEVANTAR LINEA PRIMARIA DEL PISO | P21112400130 | New_Event | Wire Down | Include | Include | Equipment | 751 | 2021-11-24 | 30040 | keep | 0 | Nov | 2021 | 0.02046 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-24 21:37 | 2021-11-24 22:32 | 40 | 000:55 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21112400317 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 55 | 2021-11-24 | 2200 | keep | 0 | Nov | 2021 | 0.0014984 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2021-11-24 21:50 | 2021-11-25 08:04 | 80 | 010:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | P21112400132 | New_Event | Cutout Failure | Include | Include | Equipment | 614 | 2021-11-24 | 49120 | keep | 0 | Nov | 2021 | 0.033455 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2021-11-24 22:10 | 2021-11-25 10:27 | 500 | 012:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | GOI=CG-211125-01, SE ABRIO MACHETES PARA SECCIONALIZAR Y REPARAR PUENTE ABIERTO | C21112400063 | New_Event | Wire Down | Include | Include | Equipment | 737 | 2021-11-24 | 368500 | keep | 0 | Nov | 2021 | 0.25098 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CAGUAS | 2021-11-24 22:18 | 2021-11-24 22:19 | 1590 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21112400071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-24 | 1590 | keep | 0 | Nov | 2021 | 0.0010829 | 0.0010829 | Momentary | FALSE | FALSE | Not_TMED_Event | 1590
MAYAGÃœEZ | 2021-11-24 23:44 | 2021-11-26 12:17 | 5 | 036:33 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO SE CERRO CORTE DE LINEA VERIFICADO EN BITACORA | M21112600023 | New_Event | Defective Pole | Include | Include | Equipment | 2193 | 2021-11-24 | 10965 | keep | 0 | Nov | 2021 | 0.0074682 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-11-25 01:06 | 2021-11-25 01:07 | 1097 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M21112500000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-11-25 | 1097 | keep | 0 | Nov | 2021 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
MAYAGÃœEZ | 2021-11-25 01:07 | 2021-11-25 10:59 | 150 | 009:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA LLUVIA Y VIENTO | M21112500004 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 592 | 2021-11-25 | 88800 | keep | 0 | Nov | 2021 | 0.060481 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2021-11-25 02:36 | 2021-11-25 08:24 | 1 | 005:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21112500001 | New_Event | Bad Weather | Include | Include | Weather | 348 | 2021-11-25 | 348 | keep | 0 | Nov | 2021 | 0.00023702 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-11-25 02:51 | 2021-11-25 08:40 | 20 | 005:49 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21112500006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 349 | 2021-11-25 | 6980 | keep | 0 | Nov | 2021 | 0.004754 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-11-25 02:57 | 2021-11-25 10:15 | 80 | 007:18 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | A21112500002 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 438 | 2021-11-25 | 35040 | keep | 0 | Nov | 2021 | 0.023866 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2021-11-25 03:25 | 2021-11-25 03:27 | 1565 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C21112500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-25 | 3130 | keep | 0 | Nov | 2021 | 0.0021318 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
BAYAMON | 2021-11-25 03:28 | 2021-11-25 08:07 | 40 | 004:39 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21112500008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 279 | 2021-11-25 | 11160 | keep | 0 | Nov | 2021 | 0.007601 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-11-25 06:37 | 2021-11-25 09:19 | 30 | 002:42 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21112500015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 162 | 2021-11-25 | 4860 | keep | 0 | Nov | 2021 | 0.0033101 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-11-25 06:45 | 2021-11-25 08:51 | 80 | 002:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21112500014 | New_Event | Bad Weather | Include | Include | Weather | 126 | 2021-11-25 | 10080 | keep | 0 | Nov | 2021 | 0.0068654 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-11-25 07:11 | 2021-11-25 10:08 | 10 | 002:57 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE SECUNDARIO Y SE REPARO SECUNDARIA | B21112500021 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 177 | 2021-11-25 | 1770 | keep | 0 | Nov | 2021 | 0.0012055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-11-25 07:19 | 2021-11-25 13:07 | 2126 | 005:48 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE RISER CRUZANDO FASE EN CARR 3 KM 81 FTE PALMA REAL Y SECCIONALIZO MENSAJERO DE SPACER SOBRE PUENTE EN CARR 3 FTE URB. BUXO | C21112500020 | New_Event | Wire Down | Include | Include | Equipment | 348 | 2021-11-25 | 739848 | keep | 0 | Nov | 2021 | 0.50391 | 0.001448 | Sustained | FALSE | FALSE | Not_TMED_Event | 2126
ARECIBO | 2021-11-25 07:27 | 2021-11-25 08:18 | 2720 | 000:51 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR SE SECCIONALIZO LINEA PRIMARIA ROTA | A21112500007 | New_Event | Wire Down | Include | Include | Equipment | 51 | 2021-11-25 | 138720 | keep | 0 | Nov | 2021 | 0.094482 | 0.0018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 2720
ARECIBO | 2021-11-25 07:27 | 2021-11-25 07:28 | 3431 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR POR LINEAS CRUZADAS CON EL 8010-02 | A21112500008 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-25 | 3431 | keep | 0 | Nov | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
VEGA BAJA | 2021-11-25 07:27 | 2021-11-25 22:29 | 28 | 015:02 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21112500023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 902 | 2021-11-25 | 25256 | keep | 0 | Nov | 2021 | 0.017202 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
ARECIBO | 2021-11-25 07:28 | 2021-11-25 12:15 | 50 | 004:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO DEL 8010-02 SOBRE 8015-09 | A21112500008 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 287 | 2021-11-25 | 14350 | keep | 0 | Nov | 2021 | 0.0097737 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-11-25 07:31 | 2021-11-25 11:57 | 1 | 004:26 | P | NO SE REPORTO CAUSA | 2 X 50 EN RISER EL JOURNEYMAN NO ENCONTRO CAUSA | M21112500010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 266 | 2021-11-25 | 266 | keep | 0 | Nov | 2021 | 0.00018117 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-25 07:32 | 2021-11-25 07:34 | 225 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1303-05 | S21112500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-25 | 450 | keep | 0 | Nov | 2021 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-11-25 07:32 | 2021-11-25 07:34 | 870 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA 1303-04 | S21112500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-25 | 1740 | keep | 0 | Nov | 2021 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2021-11-25 07:33 | 2021-11-25 10:12 | 20 | 002:39 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21112500025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 159 | 2021-11-25 | 3180 | keep | 0 | Nov | 2021 | 0.0021659 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2021-11-25 07:48 | 2021-11-25 09:36 | 65 | 001:48 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO | C21112500029 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 108 | 2021-11-25 | 7020 | keep | 0 | Nov | 2021 | 0.0047813 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2021-11-25 07:58 | 2021-11-25 13:14 | 30 | 005:16 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21112500006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 316 | 2021-11-25 | 9480 | keep | 0 | Nov | 2021 | 0.0064568 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-11-25 07:59 | 2021-11-25 11:30 | 90 | 003:31 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO CAUSA | C21112500032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 211 | 2021-11-25 | 18990 | keep | 0 | Nov | 2021 | 0.012934 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2021-11-25 08:01 | 2021-11-25 10:48 | 10 | 002:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | R21112500005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 167 | 2021-11-25 | 1670 | keep | 0 | Nov | 2021 | 0.0011374 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-11-25 08:10 | 2021-11-25 08:47 | 1234 | 000:37 | T | DESGANCHE | SE RETIRO RAMAS DE ARBOL CRUZANDO FASES EN CARR 940 KM 3.3 FTE. PLAZA FAJARDO MALL | R21112500007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 37 | 2021-11-25 | 45658 | keep | 0 | Nov | 2021 | 0.031097 | 0.00084047 | Sustained | FALSE | FALSE | Not_TMED_Event | 1234
ARECIBO | 2021-11-25 08:18 | 2021-11-25 12:15 | 400 | 003:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO Y SE CERRO MACHETES | A21112500007 | Partial_restoration | Wire Down | Include | Include | Equipment | 237 | 2021-11-25 | 94800 | keep | 0 | Nov | 2021 | 0.064568 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-25 08:22 | 2021-11-25 08:23 | 922 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1401-08 | S21112500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 922 | keep | 0 | Nov | 2021 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-11-25 08:22 | 2021-11-25 08:23 | 135 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA 1346-05 | S21112500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 135 | keep | 0 | Nov | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
PONCE | 2021-11-25 08:22 | 2021-11-25 15:23 | 1 | 007:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO EN TRANSFORMADOR | P21112500006 | New_Event | Wire Down | Include | Include | Equipment | 421 | 2021-11-25 | 421 | keep | 0 | Nov | 2021 | 0.00028674 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-11-25 08:22 | 2021-11-25 08:23 | 4664 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M21112500016 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-11-25 | 4664 | keep | 0 | Nov | 2021 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
MAYAGÃœEZ | 2021-11-25 08:23 | 2021-11-25 10:40 | 200 | 002:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA LLUVIA Y VIENTO | M21112500017 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 137 | 2021-11-25 | 27400 | keep | 0 | Nov | 2021 | 0.018662 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2021-11-25 08:47 | 2021-11-25 09:32 | 180 | 000:45 | P | DESGANCHE | 2 X 100 Y 1 X 50 EN CORTES DE LINEAS | R21112500004 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 45 | 2021-11-25 | 8100 | keep | 0 | Nov | 2021 | 0.0055169 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-25 08:48 | 2021-11-25 08:49 | 614 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 SABANA LLANA @ SAN ANTON | R21112500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-25 | 614 | keep | 0 | Nov | 2021 | 0.00041819 | 0.00041819 | Momentary | FALSE | FALSE | Not_TMED_Event | 614
SAN JUAN | 2021-11-25 08:48 | 2021-11-25 08:49 | 770 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 SABANA LLANA @ SAN ANTON | S21112500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-25 | 770 | keep | 0 | Nov | 2021 | 0.00052444 | 0.00052444 | Momentary | FALSE | FALSE | Not_TMED_Event | 770
SAN JUAN | 2021-11-25 08:48 | 2021-11-25 08:49 | 1271 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 SABANA LLANA @ SAN ANTON | S21112500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-25 | 1271 | keep | 0 | Nov | 2021 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
SAN JUAN | 2021-11-25 08:48 | 2021-11-25 08:49 | 247 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 SABANA LLANA @ SAN ANTON | R21112500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-25 | 247 | keep | 0 | Nov | 2021 | 0.00016823 | 0.00016823 | Momentary | FALSE | FALSE | Not_TMED_Event | 247
BAYAMON | 2021-11-25 08:48 | 2021-11-25 13:11 | 30 | 004:23 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21112500036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2021-11-25 | 7890 | keep | 0 | Nov | 2021 | 0.0053738 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-11-25 09:00 | 2021-11-25 09:16 | 8 | 000:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21112400060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 16 | 2021-11-25 | 128 | keep | 0 | Nov | 2021 | 8.718e-05 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-11-25 09:01 | 2021-11-25 09:57 | 40 | 000:56 | P | DESGANCHE | 1 X 80 Y 1 X 40 EN CORTES DE LINEAS | B21112500038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2021-11-25 | 2240 | keep | 0 | Nov | 2021 | 0.0015257 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-11-25 09:02 | 2021-11-25 09:46 | 1 | 000:44 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21112500033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 44 | 2021-11-25 | 44 | keep | 0 | Nov | 2021 | 2.9968e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-11-25 09:06 | 2021-11-25 12:12 | 25 | 003:06 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | M21112500022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2021-11-25 | 4650 | keep | 0 | Nov | 2021 | 0.0031671 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2021-11-25 09:08 | 2021-11-25 09:09 | 3025 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 2906-02 LLEVANDO LA CARGA DEL 2604-02 Y 2604-03 | C21112500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 3025 | keep | 0 | Nov | 2021 | 0.0020603 | 0.0020603 | Momentary | FALSE | FALSE | Not_TMED_Event | 3025
HUMACAO | 2021-11-25 09:08 | 2021-11-25 09:09 | 1593 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 2906-02 LLEVANDO LA CARGA DEL 2604-02 Y 2604-03 | C21112500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 1593 | keep | 0 | Nov | 2021 | 0.001085 | 0.001085 | Momentary | FALSE | FALSE | Not_TMED_Event | 1593
HUMACAO | 2021-11-25 09:08 | 2021-11-25 09:09 | 3420 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 2906-02 LLEVANDO LA CARGA DEL 2604-02 Y 2604-03 | C21112500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 3420 | keep | 0 | Nov | 2021 | 0.0023293 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
HUMACAO | 2021-11-25 09:11 | 2021-11-25 09:12 | 3025 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 2906-02 LLEVANDO LA CARGA DEL 2604-02 Y 2604-03 | C21112500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 3025 | keep | 0 | Nov | 2021 | 0.0020603 | 0.0020603 | Momentary | FALSE | FALSE | Not_TMED_Event | 3025
HUMACAO | 2021-11-25 09:11 | 2021-11-25 09:12 | 1593 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 2906-02 LLEVANDO LA CARGA DEL 2604-02 Y 2604-03 | C21112500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 1593 | keep | 0 | Nov | 2021 | 0.001085 | 0.001085 | Momentary | FALSE | FALSE | Not_TMED_Event | 1593
HUMACAO | 2021-11-25 09:11 | 2021-11-25 09:12 | 3420 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 2906-02 LLEVANDO LA CARGA DEL 2604-02 Y 2604-03 | C21112500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 3420 | keep | 0 | Nov | 2021 | 0.0023293 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
HUMACAO | 2021-11-25 09:18 | 2021-11-25 09:19 | 3025 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 2906-02 LLEVANDO LA CARGA DEL 2604-02 Y 2604-03 | C21112500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 3025 | keep | 0 | Nov | 2021 | 0.0020603 | 0.0020603 | Momentary | FALSE | FALSE | Not_TMED_Event | 3025
HUMACAO | 2021-11-25 09:18 | 2021-11-25 09:19 | 1593 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 2906-02 LLEVANDO LA CARGA DEL 2604-02 Y 2604-03 | C21112500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 1593 | keep | 0 | Nov | 2021 | 0.001085 | 0.001085 | Momentary | FALSE | FALSE | Not_TMED_Event | 1593
HUMACAO | 2021-11-25 09:18 | 2021-11-25 09:19 | 3420 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 2906-02 LLEVANDO LA CARGA DEL 2604-02 Y 2604-03 | C21112500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 3420 | keep | 0 | Nov | 2021 | 0.0023293 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
BAYAMON | 2021-11-25 09:20 | 2021-11-25 12:04 | 10 | 002:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA | B21112500042 | New_Event | Cutout Failure | Include | Include | Equipment | 164 | 2021-11-25 | 1640 | keep | 0 | Nov | 2021 | 0.001117 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-11-25 09:24 | 2021-11-25 10:54 | 11 | 001:30 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R21112500034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 90 | 2021-11-25 | 990 | keep | 0 | Nov | 2021 | 0.00067428 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BARRANQUITAS | 2021-11-25 09:36 | 2021-11-25 09:37 | 2635 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | C21112500067 | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-11-25 | 2635 | keep | 0 | Nov | 2021 | 0.0017947 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-11-25 09:37 | 2021-11-25 15:39 | 65 | 006:02 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO | C21112500029 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 362 | 2021-11-25 | 23530 | keep | 0 | Nov | 2021 | 0.016026 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2021-11-25 09:38 | 2021-11-25 13:19 | 15 | 003:41 | P | NO SE REPORTO CAUSA | 1 X 10 EN C/L | S21112500022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 221 | 2021-11-25 | 3315 | keep | 0 | Nov | 2021 | 0.0022578 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-11-25 09:43 | 2021-11-25 12:16 | 1 | 002:33 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA REEMPLAZO AISLADOR ROTO | C21112500069 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 153 | 2021-11-25 | 153 | keep | 0 | Nov | 2021 | 0.00010421 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-11-25 09:43 | 2021-11-25 09:44 | 637 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M21112500023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-25 | 637 | keep | 0 | Nov | 2021 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
MAYAGÃœEZ | 2021-11-25 09:44 | 2021-11-25 15:26 | 80 | 005:42 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21112500025 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 342 | 2021-11-25 | 27360 | keep | 0 | Nov | 2021 | 0.018635 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2021-11-25 09:57 | 2021-11-25 11:27 | 4027 | 001:30 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE RETIRO ARBOL CRUZANDO TRONCAL Y SE CERRO POR SCADA | B21112500044 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 90 | 2021-11-25 | 362430 | keep | 0 | Nov | 2021 | 0.24685 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2021-11-25 09:58 | 2021-11-25 13:42 | 14 | 003:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P21112500015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 224 | 2021-11-25 | 3136 | keep | 0 | Nov | 2021 | 0.0021359 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2021-11-25 09:58 | 2021-11-25 14:04 | 10 | 004:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A21112500029 | New_Event | Wire Down | Include | Include | Equipment | 246 | 2021-11-25 | 2460 | keep | 0 | Nov | 2021 | 0.0016755 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-11-25 09:58 | 2021-11-25 09:59 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21112500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 1310 | keep | 0 | Nov | 2021 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
VEGA BAJA | 2021-11-25 09:59 | 2021-11-25 10:00 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9202-02 LLEVANDO PARTE DE LA CARGA 9202-03 | B21112500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 308 | keep | 0 | Nov | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2021-11-25 09:59 | 2021-11-25 10:00 | 500 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9202-02 LLEVANDO PARTE DE LA CARGA 9202-03 | B21112500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 500 | keep | 0 | Nov | 2021 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2021-11-25 10:01 | 2021-11-25 10:54 | 50 | 000:53 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S21112500022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 53 | 2021-11-25 | 2650 | keep | 0 | Nov | 2021 | 0.0018049 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-11-25 10:07 | 2021-11-25 12:12 | 100 | 002:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA LEVANTAR LINEA PRIMARIA DEL PISO | P21112500013 | Additional_clients | Wire Down | Include | Include | Equipment | 125 | 2021-11-25 | 12500 | keep | 0 | Nov | 2021 | 0.0085137 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-11-25 10:15 | 2021-11-25 12:20 | 10 | 002:05 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON PROBLEMAS DE VOLTAJE DE 25 KVA X 37.5 KVA | A21112500032 | New_Event | Service Transformer Failure | Include | Include | Equipment | 125 | 2021-11-25 | 1250 | keep | 0 | Nov | 2021 | 0.00085137 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-25 10:25 | 2021-11-25 16:00 | 60 | 005:35 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21112500035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 335 | 2021-11-25 | 20100 | keep | 0 | Nov | 2021 | 0.01369 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-11-25 10:33 | 2021-11-25 15:05 | 30 | 004:32 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21112500037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 272 | 2021-11-25 | 8160 | keep | 0 | Nov | 2021 | 0.0055577 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-11-25 10:36 | 2021-11-25 14:49 | 40 | 004:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR FUERTES VIENTOS | M21112500028 | New_Event | Bad Weather | Include | Include | Weather | 253 | 2021-11-25 | 10120 | keep | 0 | Nov | 2021 | 0.0068927 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-11-25 10:43 | 2021-11-25 10:44 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9202-02 LLEVANDO PARTE DE LA CARGA 9202-03 | B21112500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 308 | keep | 0 | Nov | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2021-11-25 10:43 | 2021-11-25 10:44 | 500 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9202-02 LLEVANDO PARTE DE LA CARGA 9202-03 | B21112500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 500 | keep | 0 | Nov | 2021 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
BARRANQUITAS | 2021-11-25 10:45 | 2021-11-25 10:46 | 2280 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 9902-03 LLEVANDO LA CARGA DEL 9902-02 | C21112500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 2280 | keep | 0 | Nov | 2021 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2021-11-25 10:45 | 2021-11-25 10:46 | 1617 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 9902-03 LLEVANDO LA CARGA DEL 9902-02 | C21112500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 1617 | keep | 0 | Nov | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
VEGA BAJA | 2021-11-25 10:46 | 2021-11-25 10:47 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9202-02 LLEVANDO PARTE DE LA CARGA 9202-03 | B21112500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 308 | keep | 0 | Nov | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2021-11-25 10:46 | 2021-11-25 10:47 | 500 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9202-02 LLEVANDO PARTE DE LA CARGA 9202-03 | B21112500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 500 | keep | 0 | Nov | 2021 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
VEGA BAJA | 2021-11-25 10:47 | 2021-11-25 10:48 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9202-02 LLEVANDO PARTE DE LA CARGA 9202-03 | B21112500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 308 | keep | 0 | Nov | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2021-11-25 10:47 | 2021-11-25 10:48 | 500 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9202-02 LLEVANDO PARTE DE LA CARGA 9202-03 | B21112500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 500 | keep | 0 | Nov | 2021 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
CANOVANAS | 2021-11-25 10:48 | 2021-11-25 11:02 | 2580 | 000:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11100 | R21112500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2021-11-25 | 36120 | keep | 0 | Nov | 2021 | 0.024601 | 0.0017572 | Sustained | FALSE | FALSE | Not_TMED_Event | 2580
CANOVANAS | 2021-11-25 10:48 | 2021-11-25 11:02 | 500 | 000:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11100 | R21112500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2021-11-25 | 7000 | keep | 0 | Nov | 2021 | 0.0047677 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
VEGA BAJA | 2021-11-25 10:51 | 2021-11-25 15:00 | 308 | 004:09 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 9202-02 LLEVANDO PARTE DE LA CARGA 9202-03 SE PATRULLO Y NO SE ENCONTRO CAUSA SE CERRO POR SCADA | B21112500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 249 | 2021-11-25 | 76692 | keep | 0 | Nov | 2021 | 0.052235 | 0.00020978 | Sustained | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2021-11-25 11:01 | 2021-11-25 11:02 | 290 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21112500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 290 | keep | 0 | Nov | 2021 | 0.00019752 | 0.00019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 290
GUAYAMA | 2021-11-25 11:03 | 2021-11-25 13:15 | 50 | 002:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P21112500023 | New_Event | Bad Weather | Include | Include | Weather | 132 | 2021-11-25 | 6600 | keep | 0 | Nov | 2021 | 0.0044952 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-25 11:08 | 2021-11-25 14:49 | 100 | 003:41 | P | DESGANCHE | 1 X 100 1 X 65 Y 1 X 80 EN CORTE DE LINEA | S21112500033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2021-11-25 | 22100 | keep | 0 | Nov | 2021 | 0.015052 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-25 11:14 | 2021-11-25 16:56 | 30 | 005:42 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21112500044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 342 | 2021-11-25 | 10260 | keep | 0 | Nov | 2021 | 0.006988 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-11-25 11:19 | 2021-11-25 12:22 | 10 | 001:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BARRA AVERIADA EN PEDESTAL | C21112400083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 63 | 2021-11-25 | 630 | keep | 0 | Nov | 2021 | 0.00042909 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-11-25 11:20 | 2021-11-25 16:08 | 1 | 004:48 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | B21112500060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 288 | 2021-11-25 | 288 | keep | 0 | Nov | 2021 | 0.00019616 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-11-25 11:21 | 2021-11-25 17:41 | 509 | 006:20 | P | LINEA DE TRANSMISION 38KV | SE ABRIO TRANSFORMADOR PARA REPARAR FASE DE LINEA 3100 SOBRE LA DISTRIBUCION | R21112500047 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 380 | 2021-11-25 | 193420 | keep | 0 | Nov | 2021 | 0.13174 | 0.00034668 | Sustained | FALSE | FALSE | Not_TMED_Event | 509
VEGA BAJA | 2021-11-25 11:24 | 2021-11-25 15:12 | 20 | 003:48 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21112500063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2021-11-25 | 4560 | keep | 0 | Nov | 2021 | 0.0031058 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-11-25 11:27 | 2021-11-25 14:30 | 100 | 003:03 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21112500030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2021-11-25 | 18300 | keep | 0 | Nov | 2021 | 0.012464 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-25 11:27 | 2021-11-25 12:20 | 50 | 000:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21112500046 | New_Event | Bad Weather | Include | Include | Weather | 53 | 2021-11-25 | 2650 | keep | 0 | Nov | 2021 | 0.0018049 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-11-25 11:27 | 2021-11-25 11:43 | 40 | 000:16 | P | DESGANCHE | 1 X 80 Y 1 X 40 EN CORTES DE LINEAS | B21112500038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 16 | 2021-11-25 | 640 | keep | 0 | Nov | 2021 | 0.0004359 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-11-25 11:28 | 2021-11-25 11:29 | 2106 | 000:01 | T | CABLE SOTERRADO AVERIADO | DISPARO | R21112500000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2021-11-25 | 2106 | keep | 0 | Nov | 2021 | 0.0014344 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
CANOVANAS | 2021-11-25 11:33 | 2021-11-25 11:34 | 2106 | 000:01 | T | CABLE SOTERRADO AVERIADO | DISPARO | R21112500000 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 1 | 2021-11-25 | 2106 | keep | 0 | Nov | 2021 | 0.0014344 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
HUMACAO | 2021-11-25 11:33 | 2021-11-25 11:35 | 1089 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C21112500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-25 | 2178 | keep | 0 | Nov | 2021 | 0.0014834 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2021-11-25 11:33 | 2021-11-25 11:35 | 3896 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C21112500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-25 | 7792 | keep | 0 | Nov | 2021 | 0.0053071 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2021-11-25 11:33 | 2021-11-25 11:35 | 1467 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C21112500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-25 | 2934 | keep | 0 | Nov | 2021 | 0.0019983 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
CAGUAS | 2021-11-25 11:33 | 2021-11-25 13:49 | 436 | 002:16 | P | DESGANCHE | RETIRARON BAMBUAS SOBRE LINEAS Y CERRO INTERRUPTOR, PARTE DE LA CARGA POR EL 3015-07 | C21112500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2021-11-25 | 59296 | keep | 0 | Nov | 2021 | 0.040386 | 0.00029696 | Sustained | FALSE | FALSE | Not_TMED_Event | 436
HUMACAO | 2021-11-25 11:36 | 2021-11-25 12:16 | 1089 | 000:40 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C21112500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 40 | 2021-11-25 | 43560 | keep | 0 | Nov | 2021 | 0.029669 | 0.00074171 | Sustained | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2021-11-25 11:36 | 2021-11-25 12:16 | 3896 | 000:40 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C21112500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 40 | 2021-11-25 | 155840 | keep | 0 | Nov | 2021 | 0.10614 | 0.0026535 | Sustained | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2021-11-25 11:36 | 2021-11-25 12:16 | 1467 | 000:40 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C21112500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 40 | 2021-11-25 | 58680 | keep | 0 | Nov | 2021 | 0.039967 | 0.00099917 | Sustained | FALSE | FALSE | Not_TMED_Event | 1467
CAGUAS | 2021-11-25 11:36 | 2021-11-25 12:47 | 1342 | 001:11 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SECCIONALIZARON CONDUCTOR SAFADO SOBRE HERRAJE | C21112500079 | New_Event | Wire Down | Include | Include | Equipment | 71 | 2021-11-25 | 95282 | keep | 0 | Nov | 2021 | 0.064896 | 0.00091403 | Sustained | FALSE | FALSE | Not_TMED_Event | 1342
BAYAMON | 2021-11-25 11:41 | 2021-11-25 13:07 | 35 | 001:26 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA | S21112500040 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 86 | 2021-11-25 | 3010 | keep | 0 | Nov | 2021 | 0.0020501 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2021-11-25 11:48 | 2021-11-25 16:03 | 25 | 004:15 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21112500047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 255 | 2021-11-25 | 6375 | keep | 0 | Nov | 2021 | 0.004342 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2021-11-25 11:50 | 2021-11-25 16:35 | 57 | 004:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 Y 2 X 30 EN CORTES DE LINEA MAL TIEMPO | C21112500104 | New_Event | Bad Weather | Include | Include | Weather | 285 | 2021-11-25 | 16245 | keep | 0 | Nov | 2021 | 0.011064 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
SAN JUAN | 2021-11-25 11:55 | 2021-11-25 16:20 | 80 | 004:25 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S21112500044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 265 | 2021-11-25 | 21200 | keep | 0 | Nov | 2021 | 0.014439 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-11-25 11:57 | 2021-11-25 18:33 | 30 | 006:36 | P | DESGANCHE | 2 X 65 Y 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21112500109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 396 | 2021-11-25 | 11880 | keep | 0 | Nov | 2021 | 0.0080914 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2021-11-25 11:58 | 2021-11-25 13:22 | 40 | 001:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | P21112500032 | New_Event | Bad Weather | Include | Include | Weather | 84 | 2021-11-25 | 3360 | keep | 0 | Nov | 2021 | 0.0022885 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-11-25 12:01 | 2021-11-25 13:15 | 60 | 001:14 | P | LINEA DE TRANSMISION 38KV | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE DE EMERGENCIA EN LINEA 2200 | B21112500066 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 74 | 2021-11-25 | 4440 | keep | 0 | Nov | 2021 | 0.0030241 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2021-11-25 12:08 | 2021-11-25 14:29 | 20 | 002:21 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21112500069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 141 | 2021-11-25 | 2820 | keep | 0 | Nov | 2021 | 0.0019207 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-11-25 12:13 | 2021-11-25 12:50 | 20 | 000:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA EN TRANSFORMADOR MARCA CHINT 100AMP | M21112500032 | New_Event | Cutout Failure | Include | Include | Equipment | 37 | 2021-11-25 | 740 | keep | 0 | Nov | 2021 | 0.00050401 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-11-25 12:18 | 2021-11-25 15:36 | 1089 | 003:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A PUEBLITO DEL RIO SE REEMPLAZO AISLADOR ROTO DE 38 KV | C21112500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 198 | 2021-11-25 | 215622 | keep | 0 | Nov | 2021 | 0.14686 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-11-25 12:18 | 2021-11-25 15:36 | 3896 | 003:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A PUEBLITO DEL RIO SE REEMPLAZO AISLADOR ROTO DE 38 KV | C21112500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 198 | 2021-11-25 | 771408 | keep | 0 | Nov | 2021 | 0.5254 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-11-25 12:18 | 2021-11-25 15:36 | 1467 | 003:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A PUEBLITO DEL RIO SE REEMPLAZO AISLADOR ROTO DE 38 KV | C21112500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 198 | 2021-11-25 | 290466 | keep | 0 | Nov | 2021 | 0.19784 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-11-25 12:34 | 2021-11-25 13:38 | 60 | 001:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21112500134 | New_Event | Bad Weather | Include | Include | Weather | 64 | 2021-11-25 | 3840 | keep | 0 | Nov | 2021 | 0.0026154 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2021-11-25 12:34 | 2021-11-26 10:59 | 50 | 022:25 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21112500133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1345 | 2021-11-25 | 67250 | keep | 0 | Nov | 2021 | 0.045804 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2021-11-25 12:36 | 2021-11-25 15:24 | 13 | 002:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA FUERTE LLUVIA | P21112500037 | New_Event | Bad Weather | Include | Include | Weather | 168 | 2021-11-25 | 2184 | keep | 0 | Nov | 2021 | 0.0014875 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BARRANQUITAS | 2021-11-25 12:42 | 2021-11-25 15:13 | 110 | 002:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE SECCIONALIZO CONDUCTOR PRIMARIO EN EL SUELO | C21112500139 | New_Event | Wire Down | Include | Include | Equipment | 151 | 2021-11-25 | 16610 | keep | 0 | Nov | 2021 | 0.011313 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
UTUADO | 2021-11-25 12:43 | 2021-11-25 19:06 | 80 | 006:23 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21112500058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 383 | 2021-11-25 | 30640 | keep | 0 | Nov | 2021 | 0.020869 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2021-11-25 12:47 | 2021-11-25 14:54 | 500 | 002:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DESGANCHO PALMA, SE FIJO CONDUCTOR AL AISLADOR Y SE REPARO NEUTRAL PRIMARIO | C21112500079 | Partial_restoration | Wire Down | Include | Include | Equipment | 127 | 2021-11-25 | 63500 | keep | 0 | Nov | 2021 | 0.04325 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-11-25 12:58 | 2021-11-25 16:40 | 55 | 003:42 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA FUERTE BRISA | P21112500044 | New_Event | Bad Weather | Include | Include | Weather | 222 | 2021-11-25 | 12210 | keep | 0 | Nov | 2021 | 0.0083162 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
HUMACAO | 2021-11-25 13:07 | 2021-11-25 16:50 | 1115 | 003:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO CONDUCTOR AL AISLADOR SE CERRO MACHETES | C21112500020 | New_Event | Wire Down | Include | Include | Equipment | 223 | 2021-11-25 | 248645 | keep | 0 | Nov | 2021 | 0.16935 | 0.00075942 | Sustained | FALSE | FALSE | Not_TMED_Event | 1115
CANOVANAS | 2021-11-25 13:12 | 2021-11-25 13:13 | 2106 | 000:01 | T | CABLE SOTERRADO AVERIADO | DISPARO | R21112500000 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 1 | 2021-11-25 | 2106 | keep | 0 | Nov | 2021 | 0.0014344 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
MAYAGÃœEZ | 2021-11-25 13:15 | 2021-11-25 17:25 | 80 | 004:10 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M21112500037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 250 | 2021-11-25 | 20000 | keep | 0 | Nov | 2021 | 0.013622 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2021-11-25 13:16 | 2021-11-25 15:31 | 500 | 002:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21112500039 | New_Event | Bad Weather | Include | Include | Weather | 135 | 2021-11-25 | 67500 | keep | 0 | Nov | 2021 | 0.045974 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
PONCE | 2021-11-25 13:20 | 2021-11-25 14:01 | 2113 | 000:41 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ELIMINO PUENTE DE PARARRAYO SOBRE CRUCETA Y SE PUSO INTERRUPTOR EN SERVICIO | P21112500048 | New_Event | Wire Down | Include | Include | Equipment | 41 | 2021-11-25 | 86633 | keep | 0 | Nov | 2021 | 0.059005 | 0.0014392 | Sustained | FALSE | FALSE | Not_TMED_Event | 2113
ARECIBO | 2021-11-25 13:40 | 2021-11-25 15:59 | 100 | 002:19 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21112500052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2021-11-25 | 13900 | keep | 0 | Nov | 2021 | 0.0094672 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2021-11-25 13:44 | 2021-11-25 14:40 | 50 | 000:56 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTES DE LINEA | R21112500063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 56 | 2021-11-25 | 2800 | keep | 0 | Nov | 2021 | 0.0019071 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-25 13:49 | 2021-11-25 14:15 | 10 | 000:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | P21112500012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 26 | 2021-11-25 | 260 | keep | 0 | Nov | 2021 | 0.00017708 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-11-25 13:53 | 2021-11-25 15:54 | 2566 | 002:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO SE ABRIO SU-17 A MH-24 SE CERRO POR CONTROL 20% EN SERVICIO | S21112500049 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 121 | 2021-11-25 | 310486 | keep | 0 | Nov | 2021 | 0.21147 | 0.0017477 | Sustained | FALSE | FALSE | Not_TMED_Event | 2566
BAYAMON | 2021-11-25 13:53 | 2021-11-25 18:09 | 40 | 004:16 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | CAJAS SECAS EN MH-33 AVERIADA AVE. PONCE DE LEON | S21112500049 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 256 | 2021-11-25 | 10240 | keep | 0 | Nov | 2021 | 0.0069744 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-11-25 13:58 | 2021-11-25 15:34 | 2106 | 001:36 | T | CABLE SOTERRADO AVERIADO | DISPARO SE SECCIONALIZO EL ALIMENTADOR | R21112500071 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 96 | 2021-11-25 | 202176 | keep | 0 | Nov | 2021 | 0.1377 | 0.0014344 | Sustained | FALSE | FALSE | Not_TMED_Event | 2106
CAGUAS | 2021-11-25 13:59 | 2021-11-26 10:17 | 11 | 020:18 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR REPARO SECUNDARIA Y DESGANCHO RAMA | C21112500176 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1218 | 2021-11-25 | 13398 | keep | 0 | Nov | 2021 | 0.0091253 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2021-11-25 14:04 | 2021-11-25 15:43 | 7 | 001:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BAJANTE SECUNDARIO | R21112500066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 99 | 2021-11-25 | 693 | keep | 0 | Nov | 2021 | 0.000472 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2021-11-25 14:06 | 2021-11-25 16:09 | 17 | 002:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA FUERTE LLUVIA | P21112500055 | New_Event | Bad Weather | Include | Include | Weather | 123 | 2021-11-25 | 2091 | keep | 0 | Nov | 2021 | 0.0014242 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
MAYAGÃœEZ | 2021-11-25 14:34 | 2021-11-25 17:39 | 50 | 003:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21112500058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2021-11-25 | 9250 | keep | 0 | Nov | 2021 | 0.0063001 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-11-25 14:41 | 2021-11-26 21:20 | 5 | 030:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS VERIFICADO EN BITACORA | A21112500063 | New_Event | Bad Weather | Include | Include | Weather | 1839 | 2021-11-25 | 9195 | keep | 0 | Nov | 2021 | 0.0062627 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-11-25 14:47 | 2021-11-25 14:48 | 1478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21112500057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 1478 | keep | 0 | Nov | 2021 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
CAGUAS | 2021-11-25 14:53 | 2021-11-25 16:35 | 50 | 001:42 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21112500189 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2021-11-25 | 5100 | keep | 0 | Nov | 2021 | 0.0034736 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2021-11-25 15:13 | 2021-11-25 19:13 | 70 | 004:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO SE CERRO FUSIBLES | C21112500139 | Partial_restoration | Wire Down | Include | Include | Equipment | 240 | 2021-11-25 | 16800 | keep | 0 | Nov | 2021 | 0.011442 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-11-25 15:17 | 2021-11-25 15:31 | 1 | 000:14 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | A21112500055 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 14 | 2021-11-25 | 14 | keep | 0 | Nov | 2021 | 9.5353e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-25 15:34 | 2021-11-25 16:22 | 10 | 000:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21112500078 | New_Event | Secondary Wire Down | Include | Include | Equipment | 48 | 2021-11-25 | 480 | keep | 0 | Nov | 2021 | 0.00032693 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-11-25 15:34 | 2021-11-25 16:39 | 500 | 001:05 | P | CABLE SOTERRADO AVERIADO | SE CERRARON MACHETES | R21112500071 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 65 | 2021-11-25 | 32500 | keep | 0 | Nov | 2021 | 0.022136 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-11-25 15:39 | 2021-11-25 20:02 | 1067 | 004:23 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | TRES TRAMOS DE LINEA PRIMARIA EN EL PISO | P21112500065 | New_Event | Wire Down | Include | Include | Equipment | 263 | 2021-11-25 | 280621 | keep | 0 | Nov | 2021 | 0.19113 | 0.00072673 | Sustained | FALSE | FALSE | Not_TMED_Event | 1067
SAN JUAN | 2021-11-25 15:53 | 2021-11-25 18:15 | 10 | 002:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | R21112500089 | New_Event | Secondary Wire Down | Include | Include | Equipment | 142 | 2021-11-25 | 1420 | keep | 0 | Nov | 2021 | 0.00096716 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-11-25 15:54 | 2021-11-25 15:57 | 2000 | 000:03 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO SE ABRIO SU-17 A MH-24 SE CERRO POR CONTROL 20% EN SERVICIO | S21112500049 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 3 | 2021-11-25 | 6000 | keep | 0 | Nov | 2021 | 0.0040866 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-11-25 15:55 | 2021-11-25 16:16 | 42 | 000:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21112400039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 21 | 2021-11-25 | 882 | keep | 0 | Nov | 2021 | 0.00060073 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
SAN JUAN | 2021-11-25 15:57 | 2021-11-25 16:00 | 2566 | 000:03 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO AL CERRAR SU-17 20% EN SERVICIO | S21112500049 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 3 | 2021-11-25 | 7698 | keep | 0 | Nov | 2021 | 0.0052431 | 0.0017477 | Momentary | FALSE | FALSE | Not_TMED_Event | 2566
SAN JUAN | 2021-11-25 16:00 | 2021-11-25 17:28 | 2000 | 001:28 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO AL CERRAR SU-17 20% EN SERVICIO | S21112500049 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 88 | 2021-11-25 | 176000 | keep | 0 | Nov | 2021 | 0.11987 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
VEGA BAJA | 2021-11-25 16:05 | 2021-11-25 16:06 | 500 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 9202-02 LLEVANDO PARTE DE LA CARGA 9202-03 SE PATRULLO Y NO SE ENCONTRO CAUSA SE CERRO POR SCADA | B21112500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 500 | keep | 0 | Nov | 2021 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
PONCE | 2021-11-25 16:12 | 2021-11-25 17:17 | 12 | 001:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA FUERTE LLUVIA | P21112500068 | New_Event | Bad Weather | Include | Include | Weather | 65 | 2021-11-25 | 780 | keep | 0 | Nov | 2021 | 0.00053125 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2021-11-25 16:19 | 2021-11-25 22:22 | 100 | 006:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO Y SE REMPLAZO PORTAFUSIBLES EN CORTE DE LINEA | M21112500056 | New_Event | Wire Down | Include | Include | Equipment | 363 | 2021-11-25 | 36300 | keep | 0 | Nov | 2021 | 0.024724 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2021-11-25 16:26 | 2021-11-25 16:27 | 2580 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11100 | R21112500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-25 | 2580 | keep | 0 | Nov | 2021 | 0.0017572 | 0.0017572 | Momentary | FALSE | FALSE | Not_TMED_Event | 2580
CANOVANAS | 2021-11-25 16:26 | 2021-11-25 16:27 | 500 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11100 | R21112500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-25 | 500 | keep | 0 | Nov | 2021 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
CANOVANAS | 2021-11-25 16:28 | 2021-11-25 18:11 | 2580 | 001:43 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11100 | R21112500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 103 | 2021-11-25 | 265740 | keep | 0 | Nov | 2021 | 0.18099 | 0.0017572 | Sustained | FALSE | FALSE | Not_TMED_Event | 2580
CANOVANAS | 2021-11-25 16:28 | 2021-11-25 18:11 | 500 | 001:43 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11100 | R21112500000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 103 | 2021-11-25 | 51500 | keep | 0 | Nov | 2021 | 0.035076 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CANOVANAS | 2021-11-25 16:39 | 2021-11-25 17:55 | 2106 | 001:16 | T | CABLE SOTERRADO AVERIADO | DISPARO | R21112500096 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 76 | 2021-11-25 | 160056 | keep | 0 | Nov | 2021 | 0.10901 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-11-25 16:46 | 2021-11-25 20:17 | 19 | 003:31 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5 KVA X 37.5 KVA | C21112500210 | New_Event | Service Transformer Failure | Include | Include | Equipment | 211 | 2021-11-25 | 4009 | keep | 0 | Nov | 2021 | 0.0027305 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
HUMACAO | 2021-11-25 16:50 | 2021-11-25 17:39 | 2 | 000:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA Y 1 X 20 EN RISER MAL TIEMPO | C21112500210 | New_Event | Bad Weather | Include | Include | Weather | 49 | 2021-11-25 | 98 | keep | 0 | Nov | 2021 | 6.6747e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
GUAYAMA | 2021-11-25 17:24 | 2021-11-25 20:54 | 80 | 003:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA FUERTE LLUVIA | P21112500070 | New_Event | Bad Weather | Include | Include | Weather | 210 | 2021-11-25 | 16800 | keep | 0 | Nov | 2021 | 0.011442 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-11-25 17:25 | 2021-11-26 02:30 | 107 | 009:05 | S | BREAKER DEFECTUOSO O NO OPERA | SE TRANSFIRIO 6702-2 AL 6702-1 POR AUXILIARES DE BARRA Y UN BUSHING QUEMADO Y SE TRANSFIRIO EL 6702-3 AL 6702-4 POR TENER TODOS LOS BUSHING QUEMADOS | M21112500095 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 545 | 2021-11-25 | 58315 | keep | 0 | Nov | 2021 | 0.039718 | 7.2877e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 107
MAYAGÃœEZ | 2021-11-25 17:25 | 2021-11-26 02:30 | 1666 | 009:05 | S | BREAKER DEFECTUOSO O NO OPERA | SE TRANSFIRIO 6702-2 AL 6702-1 POR AUXILIARES DE BARRA Y UN BUSHING QUEMADO Y SE TRANSFIRIO EL 6702-3 AL 6702-4 POR TENER TODOS LOS BUSHING QUEMADOS | M21112500095 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 545 | 2021-11-25 | 907970 | keep | 0 | Nov | 2021 | 0.61841 | 0.0011347 | Sustained | FALSE | FALSE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2021-11-25 17:25 | 2021-11-26 02:30 | 4387 | 009:05 | S | BREAKER DEFECTUOSO O NO OPERA | SE TRANSFIRIO 6702-2 AL 6702-1 POR AUXILIARES DE BARRA Y UN BUSHING QUEMADO Y SE TRANSFIRIO EL 6702-3 AL 6702-4 POR TENER TODOS LOS BUSHING QUEMADOS | M21112500095 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 545 | 2021-11-25 | 2390915 | keep | 0 | Nov | 2021 | 1.6284 | 0.002988 | Sustained | FALSE | FALSE | Not_TMED_Event | 4387
SAN JUAN | 2021-11-25 17:28 | 2021-11-25 17:29 | 2566 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRE INTERRUPTOR PARA CERRAR SU-12 A SU-7 50% EN SERVICIO | S21112500049 | Additional_clients | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-11-25 | 2566 | keep | 0 | Nov | 2021 | 0.0017477 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-25 17:29 | 2021-11-25 17:54 | 1250 | 000:25 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRE INTERRUPTOR PARA CERRAR SU-12 A SU-7 50% EN SERVICIO | S21112500049 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 25 | 2021-11-25 | 31250 | keep | 0 | Nov | 2021 | 0.021284 | 0.00085137 | Sustained | FALSE | FALSE | Not_TMED_Event | 1250
SAN JUAN | 2021-11-25 17:54 | 2021-11-25 17:57 | 2566 | 000:03 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO AL CERRAR SU-7 A MH-3 | S21112500049 | Additional_clients | UG - Broken Splice / Terminal | Include | Include | Equipment | 3 | 2021-11-25 | 7698 | keep | 0 | Nov | 2021 | 0.0052431 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-25 17:57 | 2021-11-25 18:09 | 2309 | 000:12 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE CERRO MH-7 A SU-26 90% DEL 1111-1 Y 5 % DEL 1115-5 | S21112500049 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 12 | 2021-11-25 | 27708 | keep | 0 | Nov | 2021 | 0.018872 | 0.0015726 | Sustained | FALSE | FALSE | Not_TMED_Event | 2309
BAYAMON | 2021-11-25 17:57 | 2021-11-25 18:09 | 436 | 000:12 | P | DESCONECTIVO DEFECTUOSO | SE CERRO MH-7 A SU-26 EL 5% ESTA POR EL 1111-01 | S21112500049 | New_Event | Switch Failure | Include | Include | Equipment | 12 | 2021-11-25 | 5232 | keep | 0 | Nov | 2021 | 0.0035635 | 0.00029696 | Sustained | FALSE | FALSE | Not_TMED_Event | 436
CANOVANAS | 2021-11-25 18:00 | 2021-11-25 18:04 | 2106 | 000:04 | T | CABLE SOTERRADO AVERIADO | DISPARO PERSONAL REALIZANDO OPERACIONES PARA LOCALIZAR AVERIA | R21112500096 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 4 | 2021-11-25 | 8424 | keep | 0 | Nov | 2021 | 0.0057375 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-25 18:01 | 2021-11-25 18:02 | 6244 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO | S21112500066 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2021-11-25 | 6244 | keep | 0 | Nov | 2021 | 0.0042528 | 0.0042528 | Momentary | FALSE | FALSE | Not_TMED_Event | 6244
SAN JUAN | 2021-11-25 18:04 | 2021-11-25 18:05 | 6244 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO | S21112500068 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-11-25 | 6244 | keep | 0 | Nov | 2021 | 0.0042528 | 0.0042528 | Momentary | FALSE | FALSE | Not_TMED_Event | 6244
CANOVANAS | 2021-11-25 18:04 | 2021-11-26 12:18 | 80 | 018:14 | P | CABLE SOTERRADO AVERIADO | SECCIONALIZARON AVERIA DEL SU-4 @ SU-5, SU-26 @ SU-5 Y SE CERRO N/O RISER @ SU-33 | R21112500096 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 1094 | 2021-11-25 | 87520 | keep | 0 | Nov | 2021 | 0.059609 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-11-25 18:05 | 2021-11-26 16:09 | 200 | 022:04 | P | DESCONECTIVO DEFECTUOSO | REEMPLAZO DE MACHETE QUEMADO EN SU-26 | S21112500109 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1324 | 2021-11-25 | 264800 | keep | 0 | Nov | 2021 | 0.18035 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-11-25 18:11 | 2021-11-25 22:07 | 100 | 003:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 SMU 20 DE 100A Y 1 SMU 20 DE 25A EN LOS SU D Y 1A CRUCE POR RATA | R21112500130 | New_Event |  |  | Include | Wildlife | 236 | 2021-11-25 | 23600 | keep | 0 | Nov | 2021 | 0.016074 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-11-25 18:28 | 2021-11-25 18:29 | 2566 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO AL CERRAR MH-3 AL MH-11 | S21112500049 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-11-25 | 2566 | keep | 0 | Nov | 2021 | 0.0017477 | 0.0017477 | Momentary | FALSE | FALSE | Not_TMED_Event | 2566
CAGUAS | 2021-11-25 18:28 | 2021-11-26 11:47 | 75 | 017:19 | P | DESGANCHE | 1 X 40 Y 1 X 30 EN CORTES DE LINEAS | C21112500218 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1039 | 2021-11-25 | 77925 | keep | 0 | Nov | 2021 | 0.053074 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2021-11-25 18:29 | 2021-11-25 18:44 | 246 | 000:15 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE CERRO MH-3 A MH-11 SE DEJO CAJAS SECAS EN MH-33 AVERIADA PARA INSPECCIONAR 99% EN SERVICIO | S21112500049 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 15 | 2021-11-25 | 3690 | keep | 0 | Nov | 2021 | 0.0025132 | 0.00016755 | Sustained | FALSE | FALSE | Not_TMED_Event | 246
SAN JUAN | 2021-11-25 18:33 | 2021-11-26 09:36 | 20 | 015:03 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S21112500075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 903 | 2021-11-25 | 18060 | keep | 0 | Nov | 2021 | 0.012301 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-11-25 18:44 | 2021-11-26 11:30 | 246 | 016:46 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REPARO CAJAS SECAS EN MH-33 | S21112500049 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 1006 | 2021-11-25 | 247476 | keep | 0 | Nov | 2021 | 0.16855 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-11-25 18:56 | 2021-11-25 21:50 | 60 | 002:54 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 Y 1 X 25 EN CORTES DE LINEA SE REEMPLAZO AISLADOR | R21112500140 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 174 | 2021-11-25 | 10440 | keep | 0 | Nov | 2021 | 0.0071106 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-11-25 18:57 | 2021-11-25 18:59 | 826 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF 95% POR 1119-4 SE PROBO POR CONTROL QUEDO EN SERVICIO | S21112500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-25 | 1652 | keep | 0 | Nov | 2021 | 0.0011252 | 0.00056258 | Momentary | FALSE | FALSE | Not_TMED_Event | 826
BAYAMON | 2021-11-25 18:57 | 2021-11-25 18:59 | 862 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SU CARGA POR 1119-4 SE PROBO POR CONTROL QUEDO EN SERVICIO | S21112500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-25 | 1724 | keep | 0 | Nov | 2021 | 0.0011742 | 0.0005871 | Momentary | FALSE | FALSE | Not_TMED_Event | 862
BAYAMON | 2021-11-25 18:57 | 2021-11-25 18:59 | 2720 | 000:02 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO CON R/R OFF LLEVA 95% 1115-5 Y 99% DEL 1119-2 SE PROBO POR CONTROL QUEDO EN SERVICIO | S21112500000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 2 | 2021-11-25 | 5440 | keep | 0 | Nov | 2021 | 0.0037052 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
BARRANQUITAS | 2021-11-25 18:58 | 2021-11-26 10:33 | 30 | 015:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ABIERTO EN SALIDA DE CAJA PRIMARIA | C21112500223 | New_Event | Wire Down | Include | Include | Equipment | 935 | 2021-11-25 | 28050 | keep | 0 | Nov | 2021 | 0.019105 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-11-25 18:59 | 2021-11-26 16:12 | 161 | 021:13 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REALIZARON TERMINACIONES EN SU-10 Y SE REEMPLAZARON MACHETES | S21112500113 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 1273 | 2021-11-25 | 204953 | keep | 0 | Nov | 2021 | 0.13959 | 0.00010966 | Sustained | FALSE | FALSE | Not_TMED_Event | 161
VEGA BAJA | 2021-11-25 19:09 | 2021-11-25 22:25 | 50 | 003:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | B21112500091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2021-11-25 | 9800 | keep | 0 | Nov | 2021 | 0.0066747 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-11-25 19:35 | 2021-11-26 03:35 | 20 | 008:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR REEMPLAZO AISLADOR | R21112500143 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 480 | 2021-11-25 | 9600 | keep | 0 | Nov | 2021 | 0.0065385 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-11-25 19:56 | 2021-11-25 20:16 | 1588 | 000:20 | S | PROTECCION DEFECTUOSA | DISPARO INTERRUPTORES 0006 Y 0004 DE BARRA DE TRANSMISION 115KV | B21112500000 | New_Event | Protection Miscoordination | Include | Include | Other | 20 | 2021-11-25 | 31760 | keep | 0 | Nov | 2021 | 0.021632 | 0.0010816 | Sustained | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2021-11-25 19:56 | 2021-11-25 20:16 | 723 | 000:20 | S | PROTECCION DEFECTUOSA | DISPARO INTERRUPTORES 0006 Y 0004 DE BARRA DE TRANSMISION 115KV | B21112500000 | New_Event | Protection Miscoordination | Include | Include | Other | 20 | 2021-11-25 | 14460 | keep | 0 | Nov | 2021 | 0.0098486 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2021-11-25 19:56 | 2021-11-25 20:16 | 13 | 000:20 | S | PROTECCION DEFECTUOSA | DISPARO INTERRUPTORES 0006 Y 0004 DE BARRA DE TRANSMISION 115KV | B21112500000 | New_Event | Protection Miscoordination | Include | Include | Other | 20 | 2021-11-25 | 260 | keep | 0 | Nov | 2021 | 0.00017708 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2021-11-25 19:56 | 2021-11-25 20:16 | 1976 | 000:20 | S | PROTECCION DEFECTUOSA | DISPARO INTERRUPTORES 0006 Y 0004 DE BARRA DE TRANSMISION 115KV | B21112500000 | New_Event | Protection Miscoordination | Include | Include | Other | 20 | 2021-11-25 | 39520 | keep | 0 | Nov | 2021 | 0.026917 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2021-11-25 19:56 | 2021-11-25 20:00 | 1812 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B21112500092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-11-25 | 7248 | keep | 0 | Nov | 2021 | 0.0049366 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
SAN JUAN | 2021-11-25 19:59 | 2021-11-25 20:02 | 250 | 000:03 | P | NO SE REPORTO CAUSA | RECERRO QUEDO ABIERTO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1437-3 | S21112500092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-25 | 750 | keep | 0 | Nov | 2021 | 0.00051082 | 0.00017027 | Momentary | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2021-11-25 19:59 | 2021-11-25 20:02 | 1699 | 000:03 | T | NO SE REPORTO CAUSA | RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA PARTE DEL 1301-2 | S21112500092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-11-25 | 5097 | keep | 0 | Nov | 2021 | 0.0034715 | 0.0011572 | Momentary | FALSE | FALSE | Not_TMED_Event | 1699
VEGA BAJA | 2021-11-25 20:19 | 2021-11-25 20:20 | 325 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21112500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 325 | keep | 0 | Nov | 2021 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
CAGUAS | 2021-11-25 20:36 | 2021-11-26 09:57 | 95 | 013:21 | P | NO SE REPORTO CAUSA | 2 X 40 EN CORTE DE LINEA | C21112500229 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 801 | 2021-11-25 | 76095 | keep | 0 | Nov | 2021 | 0.051828 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
BARRANQUITAS | 2021-11-25 20:41 | 2021-11-26 10:23 | 85 | 013:42 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | C21112500230 | New_Event | Vegetation Contact | Include | Include | Vegetation | 822 | 2021-11-25 | 69870 | keep | 0 | Nov | 2021 | 0.047588 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
BAYAMON | 2021-11-25 20:51 | 2021-11-26 10:48 | 52 | 013:57 | P | DESGANCHE | 2 X 100 C/L DESGANCHE | S21112500098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 837 | 2021-11-25 | 43524 | keep | 0 | Nov | 2021 | 0.029644 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
BAYAMON | 2021-11-25 21:03 | 2021-11-25 21:04 | 520 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 20% DE SU CARGA TRANSFERIDA AL 1717-04 | B21112500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 520 | keep | 0 | Nov | 2021 | 0.00035417 | 0.00035417 | Momentary | FALSE | FALSE | Not_TMED_Event | 520
VEGA BAJA | 2021-11-25 21:45 | 2021-11-26 13:05 | 27 | 015:20 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21112500130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 920 | 2021-11-25 | 24840 | keep | 0 | Nov | 2021 | 0.016918 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
ARECIBO | 2021-11-25 21:48 | 2021-11-26 19:30 | 5 | 021:42 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50 KVA QUEMADO X 50 KVA | A21112500062 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1302 | 2021-11-25 | 6510 | keep | 0 | Nov | 2021 | 0.0044339 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-11-25 22:16 | 2021-11-26 13:30 | 60 | 015:14 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA POR DESGANCHE | P21112500097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 914 | 2021-11-25 | 54840 | keep | 0 | Nov | 2021 | 0.037351 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2021-11-25 22:22 | 2021-11-25 22:23 | 2039 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21112500155 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-25 | 2039 | keep | 0 | Nov | 2021 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
SAN JUAN | 2021-11-25 22:38 | 2021-11-26 10:36 | 50 | 011:58 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21112500114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 718 | 2021-11-25 | 35900 | keep | 0 | Nov | 2021 | 0.024451 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-11-25 22:50 | 2021-11-26 11:05 | 40 | 012:15 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEAS DESGANCHE | P21112500099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 735 | 2021-11-25 | 29400 | keep | 0 | Nov | 2021 | 0.020024 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-11-25 23:08 | 2021-11-26 11:07 | 90 | 011:59 | P | DESGANCHE | 1 X 80 EN SU-7 @ PROVISIONAL AEREO | R21112500156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 719 | 2021-11-25 | 64710 | keep | 0 | Nov | 2021 | 0.044074 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2021-11-26 00:25 | 2021-11-26 09:35 | 50 | 009:10 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21112600003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 550 | 2021-11-26 | 27500 | keep | 0 | Nov | 2021 | 0.01873 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-26 00:41 | 2021-11-26 04:25 | 1588 | 003:44 | S | PROTECCION DEFECTUOSA | DISPARO 0006 Y 0004 SE INSPECCIONO SE ENCONTRO DIFERENCIAL SRL-387 Y TIME LEVEL ALTO DEL 1711-2 LLEVA CARGA 1711-3 | B21112600051 | New_Event | Protection Miscoordination | Include | Include | Other | 224 | 2021-11-26 | 355712 | keep | 0 | Nov | 2021 | 0.24227 | 0.0010816 | Sustained | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2021-11-26 00:41 | 2021-11-26 04:29 | 723 | 003:48 | S | PROTECCION DEFECTUOSA | DISPARO 0006 Y 0004 SE INSPECCIONO SE ENCONTRO DIFERENCIAL SRL-387 Y TIME LEVEL ALTO DEL 1711-2 LLEVA CARGA 1711-5 | B21112600051 | New_Event | Protection Miscoordination | Include | Include | Other | 228 | 2021-11-26 | 164844 | keep | 0 | Nov | 2021 | 0.11227 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2021-11-26 00:41 | 2021-11-26 04:25 | 13 | 003:44 | S | PROTECCION DEFECTUOSA | DISPARO 0006 Y 0004 SE INSPECCIONO SE ENCONTRO DIFERENCIAL SRL-387 Y TIME LEVEL ALTO DEL 1711-2 SU CARGA POR 1711-1 | B21112600051 | New_Event | Protection Miscoordination | Include | Include | Other | 224 | 2021-11-26 | 2912 | keep | 0 | Nov | 2021 | 0.0019833 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2021-11-26 00:41 | 2021-11-26 04:29 | 1976 | 003:48 | S | PROTECCION DEFECTUOSA | DISPARO 0006 Y 0004 SE INSPECCIONO SE ENCONTRO DIFERENCIAL SRL-387 Y TIME LEVEL ALTO DEL 1711-2 SU CARGA POR 1711-2 | B21112600051 | New_Event | Protection Miscoordination | Include | Include | Other | 228 | 2021-11-26 | 450528 | keep | 0 | Nov | 2021 | 0.30685 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
ARECIBO | 2021-11-26 00:46 | 2021-11-26 00:47 | 5042 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DEL INTERRUPTOR LINEA PRIMARIA PARTIDA | A21112600001 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-26 | 5042 | keep | 0 | Nov | 2021 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
ARECIBO | 2021-11-26 00:47 | 2021-11-26 16:43 | 75 | 015:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | A21112600029 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 956 | 2021-11-26 | 71700 | keep | 0 | Nov | 2021 | 0.048835 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2021-11-26 01:05 | 2021-11-26 09:53 | 130 | 008:48 | P | NO SE REPORTO CAUSA | 2 X 40 EN CORTE DE LINEA | C21112600001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 528 | 2021-11-26 | 68640 | keep | 0 | Nov | 2021 | 0.04675 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
CAGUAS | 2021-11-26 01:06 | 2021-11-26 10:34 | 90 | 009:28 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR | C21112600002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 568 | 2021-11-26 | 51120 | keep | 0 | Nov | 2021 | 0.034818 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CAGUAS | 2021-11-26 01:08 | 2021-11-26 11:24 | 80 | 010:16 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21112600003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 616 | 2021-11-26 | 49280 | keep | 0 | Nov | 2021 | 0.033564 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-11-26 01:11 | 2021-11-26 01:12 | 2402 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1720-8 | B21112600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-26 | 2402 | keep | 0 | Nov | 2021 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2021-11-26 01:11 | 2021-11-26 01:12 | 1 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1709-2 | B21112600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-26 | 1 | keep | 0 | Nov | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-11-26 01:16 | 2021-11-26 09:50 | 100 | 008:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | A21112600002 | New_Event | Cutout Failure | Include | Include | Equipment | 514 | 2021-11-26 | 51400 | keep | 0 | Nov | 2021 | 0.035008 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-11-26 01:30 | 2021-11-26 11:19 | 100 | 009:49 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO CAUSA | C21112600004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 589 | 2021-11-26 | 58900 | keep | 0 | Nov | 2021 | 0.040117 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2021-11-26 01:40 | 2021-11-26 09:08 | 35 | 007:28 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA INDICA JOURNEYMAN QUE REQUIERE DESGANCHE | M21112600003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 448 | 2021-11-26 | 15680 | keep | 0 | Nov | 2021 | 0.01068 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-11-26 02:04 | 2021-11-26 11:38 | 100 | 009:34 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA INFORMA JOURNEYMAN QUE REQUIERE DESGANCHE | M21112600004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 574 | 2021-11-26 | 57400 | keep | 0 | Nov | 2021 | 0.039095 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-11-26 02:40 | 2021-11-26 12:48 | 1983 | 010:08 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZO DESGANCHE Y SE CERRARON MACHETES PREVIAMENTE ABIERTOS CARGA POR EL 1801-02 | B21112600069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 608 | 2021-11-26 | 1205664 | keep | 0 | Nov | 2021 | 0.82117 | 0.0013506 | Sustained | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-11-26 02:40 | 2021-11-26 05:57 | 186 | 003:17 | T | DESGANCHE | SE SECCIONALIZO Y SE CERRO POR SCADA | B21112600034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2021-11-26 | 36642 | keep | 0 | Nov | 2021 | 0.024957 | 0.00012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 186
CANOVANAS | 2021-11-26 02:54 | 2021-11-26 14:54 | 2 | 012:00 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE SECUNDARIO | R21112600004 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 720 | 2021-11-26 | 1440 | keep | 0 | Nov | 2021 | 0.00098078 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2021-11-26 03:14 | 2021-11-26 03:17 | 1935 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUARAGUAO L-4100 LLEVA 100 DEL 1708-2 | B21112600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-11-26 | 5805 | keep | 0 | Nov | 2021 | 0.0039538 | 0.0013179 | Momentary | FALSE | FALSE | Not_TMED_Event | 1935
BAYAMON | 2021-11-26 03:14 | 2021-11-26 03:17 | 3 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUARAGUAO L-4100 LLEVA CARGA 1707-3 | B21112600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-11-26 | 9 | keep | 0 | Nov | 2021 | 6.1299e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-11-26 03:14 | 2021-11-26 03:17 | 61 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUARAGUAO L-4100 SU CARGA POR 1707-2 | B21112600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-11-26 | 183 | keep | 0 | Nov | 2021 | 0.00012464 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2021-11-26 03:14 | 2021-11-26 03:17 | 1501 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUARAGUAO L-4100 SU CARGA POR 1707-2 | B21112600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-11-26 | 4503 | keep | 0 | Nov | 2021 | 0.003067 | 0.0010223 | Momentary | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2021-11-26 03:14 | 2021-11-26 03:17 | 546 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUARAGUAO L-4100 SU CARGA POR 1707-2 | B21112600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-11-26 | 1638 | keep | 0 | Nov | 2021 | 0.0011156 | 0.00037188 | Momentary | FALSE | FALSE | Not_TMED_Event | 546
BAYAMON | 2021-11-26 03:14 | 2021-11-26 03:17 | 600 | 000:03 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUARAGUAO L-4100 PARTE DE SU CARGA POR 1707-1 | B21112600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-11-26 | 1800 | keep | 0 | Nov | 2021 | 0.001226 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
BAYAMON | 2021-11-26 03:14 | 2021-11-26 03:17 | 959 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUARAGUAO L-3400 SU CARGA POR BREAKER PORTATIL | B21112600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-11-26 | 2877 | keep | 0 | Nov | 2021 | 0.0019595 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2021-11-26 03:14 | 2021-11-26 03:17 | 1297 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUARAGUAO L-3400 SU VARGA POR 1904-6 | B21112600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-11-26 | 3891 | keep | 0 | Nov | 2021 | 0.0026501 | 0.00088338 | Momentary | FALSE | FALSE | Not_TMED_Event | 1297
BAYAMON | 2021-11-26 03:14 | 2021-11-26 03:17 | 451 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUARAGUAO L-3400 SU CARGA POR 1904-6 | B21112600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-11-26 | 1353 | keep | 0 | Nov | 2021 | 0.00092152 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
BAYAMON | 2021-11-26 03:14 | 2021-11-26 03:17 | 1264 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUARAGUAO L-3400 SU CARGA POR 1904-7 | B21112600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-11-26 | 3792 | keep | 0 | Nov | 2021 | 0.0025827 | 0.0008609 | Momentary | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2021-11-26 03:14 | 2021-11-26 03:17 | 620 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUARAGUAO L-3400 | B21112600000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-11-26 | 1860 | keep | 0 | Nov | 2021 | 0.0012668 | 0.00042228 | Momentary | FALSE | FALSE | Not_TMED_Event | 620
SAN JUAN | 2021-11-26 03:21 | 2021-11-26 03:22 | 770 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21112600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-26 | 770 | keep | 0 | Nov | 2021 | 0.00052444 | 0.00052444 | Momentary | FALSE | FALSE | Not_TMED_Event | 770
SAN JUAN | 2021-11-26 03:29 | 2021-11-26 11:08 | 65 | 007:39 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | S21112600010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 459 | 2021-11-26 | 29835 | keep | 0 | Nov | 2021 | 0.02032 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CANOVANAS | 2021-11-26 03:35 | 2021-11-26 03:36 | 635 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | R21112600000 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-11-26 | 635 | keep | 0 | Nov | 2021 | 0.0004325 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-11-26 03:36 | 2021-11-26 12:41 | 20 | 009:05 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR REEMPLAZO AISLADOR | R21112500143 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 545 | 2021-11-26 | 10900 | keep | 0 | Nov | 2021 | 0.0074239 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-11-26 03:42 | 2021-11-26 17:07 | 50 | 013:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA PRIMARIA | B21112600050 | New_Event | Cutout Failure | Include | Include | Equipment | 805 | 2021-11-26 | 40250 | keep | 0 | Nov | 2021 | 0.027414 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-11-26 04:47 | 2021-11-26 04:51 | 602 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO | S21112600014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-11-26 | 2408 | keep | 0 | Nov | 2021 | 0.0016401 | 0.00041002 | Momentary | FALSE | FALSE | Not_TMED_Event | 602
VEGA BAJA | 2021-11-26 05:15 | 2021-11-26 11:40 | 52 | 006:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 100 EN C/L SE REMPLAZO AISLADOR | B21112600059 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 385 | 2021-11-26 | 20020 | keep | 0 | Nov | 2021 | 0.013636 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
BAYAMON | 2021-11-26 05:57 | 2021-11-26 12:48 | 100 | 006:51 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRARON MACHETES PREVIAMENTE ABIERTOS LLEVA 1711-04 | B21112600069 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 411 | 2021-11-26 | 41100 | keep | 0 | Nov | 2021 | 0.027993 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-11-26 05:59 | 2021-11-26 11:33 | 9 | 005:34 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHO | C21112600010 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 334 | 2021-11-26 | 3006 | keep | 0 | Nov | 2021 | 0.0020474 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-11-26 06:06 | 2021-11-26 08:37 | 27 | 002:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN C/L SE REMPLAZO CAJA | B21112600064 | New_Event | Cutout Failure | Include | Include | Equipment | 151 | 2021-11-26 | 4077 | keep | 0 | Nov | 2021 | 0.0027768 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
AGUADILLA | 2021-11-26 06:17 | 2021-11-26 12:42 | 300 | 006:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA | M21112600007 | New_Event | Wire Down | Include | Include | Equipment | 385 | 2021-11-26 | 115500 | keep | 0 | Nov | 2021 | 0.078667 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
HUMACAO | 2021-11-26 06:38 | 2021-11-26 10:42 | 95 | 004:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C21112600011 | New_Event |  |  | Include | Wildlife | 244 | 2021-11-26 | 23180 | keep | 0 | Nov | 2021 | 0.015788 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
CAGUAS | 2021-11-26 06:42 | 2021-11-26 06:43 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21112600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-26 | 1702 | keep | 0 | Nov | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
BARRANQUITAS | 2021-11-26 06:52 | 2021-11-26 12:59 | 50 | 006:07 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C21112600012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 367 | 2021-11-26 | 18350 | keep | 0 | Nov | 2021 | 0.012498 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-26 06:58 | 2021-11-26 13:19 | 1 | 006:21 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN CORTE DE LINEA Y SE ELIMINO PARARRAYO AVERIADO PRIVADO | S21112600019 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 381 | 2021-11-26 | 381 | keep | 0 | Nov | 2021 | 0.0002595 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-26 07:00 | 2021-11-26 17:10 | 30 | 010:10 | P | DESGANCHE | 1 X 40 EN C/L SE REALIZO DESGANCHE | B21112600081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 610 | 2021-11-26 | 18300 | keep | 0 | Nov | 2021 | 0.012464 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-11-26 07:02 | 2021-11-26 12:04 | 110 | 005:02 | P | PARARRAYOS DEFECTUOSO | 2 X 80 EN CORTE DE LINEA REEMPLAZO PARARRAYO | R21112600005 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 302 | 2021-11-26 | 33220 | keep | 0 | Nov | 2021 | 0.022626 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
HUMACAO | 2021-11-26 07:08 | 2021-11-26 10:19 | 90 | 003:11 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA REEMPLAZO AISLADOR | C21112600015 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 191 | 2021-11-26 | 17190 | keep | 0 | Nov | 2021 | 0.011708 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CAGUAS | 2021-11-26 07:09 | 2021-11-26 12:36 | 100 | 005:27 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHO Y REPARO CONDUCTOR ROTO | C21112600016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 327 | 2021-11-26 | 32700 | keep | 0 | Nov | 2021 | 0.022272 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-26 07:09 | 2021-11-26 10:51 | 80 | 003:42 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21112600008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2021-11-26 | 17760 | keep | 0 | Nov | 2021 | 0.012096 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2021-11-26 07:28 | 2021-11-26 07:29 | 2697 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21112600009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-26 | 2697 | keep | 0 | Nov | 2021 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
ARECIBO | 2021-11-26 07:29 | 2021-11-26 20:00 | 50 | 012:31 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE DETECTO LA CAUSA | A21112600015 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 751 | 2021-11-26 | 37550 | keep | 0 | Nov | 2021 | 0.025575 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-11-26 07:59 | 2021-11-26 09:12 | 15 | 001:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21112600014 | New_Event | Bad Weather | Include | Include | Weather | 73 | 2021-11-26 | 1095 | keep | 0 | Nov | 2021 | 0.0007458 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-11-26 08:12 | 2021-11-26 10:07 | 1 | 001:55 | P | NO SE REPORTO CAUSA | 1 X 15 EN BANCO DE TRANSFORMADORES | C21112600025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2021-11-26 | 115 | keep | 0 | Nov | 2021 | 7.8326e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-26 08:16 | 2021-11-26 13:58 | 100 | 005:42 | P | DESGANCHE | 2 X 50 EN C/L SE REALIZO DESGANCHE | B21112600104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 342 | 2021-11-26 | 34200 | keep | 0 | Nov | 2021 | 0.023293 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-26 08:19 | 2021-11-26 12:20 | 12 | 004:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 8 EN TRANSFORMADOR SE REMPLAZO BAJANTES EN TRANSFORMADOR | A21112600018 | New_Event | Wire Down | Include | Include | Equipment | 241 | 2021-11-26 | 2892 | keep | 0 | Nov | 2021 | 0.0019697 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2021-11-26 08:20 | 2021-11-26 18:47 | 20 | 010:27 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B21112600107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 627 | 2021-11-26 | 12540 | keep | 0 | Nov | 2021 | 0.0085409 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-11-26 08:32 | 2021-11-26 15:26 | 50 | 006:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L REMPLAZO CAJA AVERIADA | C21112600030 | New_Event | Cutout Failure | Include | Include | Equipment | 414 | 2021-11-26 | 20700 | keep | 0 | Nov | 2021 | 0.014099 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2021-11-26 08:32 | 2021-11-26 11:34 | 30 | 003:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21112600020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2021-11-26 | 5460 | keep | 0 | Nov | 2021 | 0.0037188 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-11-26 08:45 | 2021-11-26 11:39 | 80 | 002:54 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C21112600033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2021-11-26 | 13920 | keep | 0 | Nov | 2021 | 0.0094808 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2021-11-26 08:55 | 2021-11-26 11:43 | 125 | 002:48 | P | DESGANCHE | 1 X 100 1 X 80 Y 1 X 65 EN DISTINTOS CORTES DE LINEA POR DESGANCHE | P21112600004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2021-11-26 | 21000 | keep | 0 | Nov | 2021 | 0.014303 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2021-11-26 08:58 | 2021-11-26 12:21 | 70 | 003:23 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C21112600038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 203 | 2021-11-26 | 14210 | keep | 0 | Nov | 2021 | 0.0096784 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2021-11-26 09:19 | 2021-11-26 10:48 | 40 | 001:29 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P21112600014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2021-11-26 | 3560 | keep | 0 | Nov | 2021 | 0.0024247 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-11-26 09:24 | 2021-11-26 21:10 | 15 | 011:46 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B21112600123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 706 | 2021-11-26 | 10590 | keep | 0 | Nov | 2021 | 0.0072128 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-11-26 09:28 | 2021-11-26 13:50 | 50 | 004:22 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21112600015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 262 | 2021-11-26 | 13100 | keep | 0 | Nov | 2021 | 0.0089224 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-11-26 09:33 | 2021-11-26 15:55 | 1 | 006:22 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21112600014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 382 | 2021-11-26 | 382 | keep | 0 | Nov | 2021 | 0.00026018 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-26 09:37 | 2021-11-26 10:32 | 723 | 000:55 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1711-02 LLEVANDO LA CARGA DEL 1711-05 Y SE CERRO PUENTE ABIERTO. | B21112600057 | New_Event | Wire Down | Include | Include | Equipment | 55 | 2021-11-26 | 39765 | keep | 0 | Nov | 2021 | 0.027084 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2021-11-26 09:37 | 2021-11-26 10:32 | 1976 | 000:55 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1711-02 LLEVANDO LA CARGA DEL 1711-05 Y SE CERRO PUENTE ABIERTO. | B21112600057 | New_Event | Wire Down | Include | Include | Equipment | 55 | 2021-11-26 | 108680 | keep | 0 | Nov | 2021 | 0.074021 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2021-11-26 09:45 | 2021-11-27 09:59 | 1 | 024:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN RISER SE REMPLAZO CAJA | S21112600041 | New_Event | Cutout Failure | Include | Include | Equipment | 1454 | 2021-11-26 | 1454 | keep | 0 | Nov | 2021 | 0.00099031 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-11-26 09:51 | 2021-11-26 12:31 | 350 | 002:40 | P | DESGANCHE | 2 X 140 EN CORTE DE LINEA INFORMA JOURNEYMAN QUE REQUIERE DESGANCHE | M21112600025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2021-11-26 | 56000 | keep | 0 | Nov | 2021 | 0.038141 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
GUAYAMA | 2021-11-26 09:52 | 2021-11-26 14:30 | 40 | 004:38 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P21112600017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 278 | 2021-11-26 | 11120 | keep | 0 | Nov | 2021 | 0.0075738 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-11-26 09:54 | 2021-11-26 12:39 | 20 | 002:45 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21112600042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 165 | 2021-11-26 | 3300 | keep | 0 | Nov | 2021 | 0.0022476 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-11-26 10:21 | 2021-11-26 15:24 | 65 | 005:03 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE AVERIADO | S21112600046 | New_Event | Switch Failure | Include | Include | Equipment | 303 | 2021-11-26 | 19695 | keep | 0 | Nov | 2021 | 0.013414 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
HUMACAO | 2021-11-26 10:25 | 2021-11-26 17:18 | 8 | 006:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA Y TOMA | C21112600055 | New_Event | Secondary Wire Down | Include | Include | Equipment | 413 | 2021-11-26 | 3304 | keep | 0 | Nov | 2021 | 0.0022503 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-11-26 10:34 | 2021-11-26 11:20 | 15 | 000:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21112600010 | New_Event | Secondary Wire Down | Include | Include | Equipment | 46 | 2021-11-26 | 690 | keep | 0 | Nov | 2021 | 0.00046996 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-11-26 10:35 | 2021-11-26 11:40 | 15 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M21112600020 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2021-11-26 | 975 | keep | 0 | Nov | 2021 | 0.00066407 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-11-26 10:38 | 2021-11-26 15:42 | 25 | 005:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA QUEMADA | A21112600039 | New_Event | Cutout Failure | Include | Include | Equipment | 304 | 2021-11-26 | 7600 | keep | 0 | Nov | 2021 | 0.0051763 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2021-11-26 10:43 | 2021-11-26 11:19 | 1 | 000:36 | P | DESGANCHE | 1 X 30 EN MONTURA AAA DESGANCHE | P21112600020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 36 | 2021-11-26 | 36 | keep | 0 | Nov | 2021 | 2.4519e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-11-26 10:59 | 2021-11-26 12:34 | 250 | 001:35 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | A21112600040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2021-11-26 | 23750 | keep | 0 | Nov | 2021 | 0.016176 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
AGUADILLA | 2021-11-26 11:00 | 2021-11-26 12:20 | 12 | 001:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | M21112600022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 80 | 2021-11-26 | 960 | keep | 0 | Nov | 2021 | 0.00065385 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2021-11-26 11:02 | 2021-11-26 16:19 | 98 | 005:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21112600022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 317 | 2021-11-26 | 31066 | keep | 0 | Nov | 2021 | 0.021159 | 6.6747e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 98
HUMACAO | 2021-11-26 11:03 | 2021-11-26 11:04 | 1089 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C21112600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-26 | 1089 | keep | 0 | Nov | 2021 | 0.00074171 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2021-11-26 11:03 | 2021-11-26 11:04 | 3896 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C21112600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-26 | 3896 | keep | 0 | Nov | 2021 | 0.0026535 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2021-11-26 11:03 | 2021-11-26 11:04 | 1467 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C21112600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-26 | 1467 | keep | 0 | Nov | 2021 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
BAYAMON | 2021-11-26 11:10 | 2021-11-26 17:43 | 45 | 006:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L AVE | B21112600147 | New_Event |  |  | Include | Wildlife | 393 | 2021-11-26 | 17685 | keep | 0 | Nov | 2021 | 0.012045 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2021-11-26 11:13 | 2021-11-26 14:59 | 100 | 003:46 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21112300150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2021-11-26 | 22600 | keep | 0 | Nov | 2021 | 0.015393 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-11-26 11:22 | 2021-11-26 13:12 | 1089 | 001:50 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C21112600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 110 | 2021-11-26 | 119790 | keep | 0 | Nov | 2021 | 0.081588 | 0.00074171 | Sustained | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2021-11-26 11:22 | 2021-11-26 13:12 | 3896 | 001:50 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C21112600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 110 | 2021-11-26 | 428560 | keep | 0 | Nov | 2021 | 0.29189 | 0.0026535 | Sustained | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2021-11-26 11:22 | 2021-11-26 13:12 | 1467 | 001:50 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C21112600000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 110 | 2021-11-26 | 161370 | keep | 0 | Nov | 2021 | 0.10991 | 0.00099917 | Sustained | FALSE | FALSE | Not_TMED_Event | 1467
VEGA BAJA | 2021-11-26 11:33 | 2021-11-26 13:10 | 1 | 001:37 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21112600155 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 97 | 2021-11-26 | 97 | keep | 0 | Nov | 2021 | 6.6066e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-26 11:38 | 2021-11-26 17:45 | 12 | 006:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21112600054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 367 | 2021-11-26 | 4404 | keep | 0 | Nov | 2021 | 0.0029995 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-11-26 11:40 | 2021-11-26 13:46 | 6 | 002:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR CONECTOR EN SECUNDARIA | C21112600076 | New_Event | Secondary Wire Down | Include | Include | Equipment | 126 | 2021-11-26 | 756 | keep | 0 | Nov | 2021 | 0.00051491 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-11-26 11:40 | 2021-11-27 19:34 | 20 | 031:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA PARTIDA VERIFICADO EN BITACORA | A21112600045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1914 | 2021-11-26 | 38280 | keep | 0 | Nov | 2021 | 0.026072 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-11-26 11:47 | 2021-11-27 21:16 | 12 | 033:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA PARTIDA VERIFICADO EN BITACORA | A21112600048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2009 | 2021-11-26 | 24108 | keep | 0 | Nov | 2021 | 0.01642 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2021-11-26 11:49 | 2021-11-26 18:12 | 25 | 006:23 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L Y 1 X 15 EN XMR | B21112600160 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 383 | 2021-11-26 | 9575 | keep | 0 | Nov | 2021 | 0.0065215 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2021-11-26 12:01 | 2021-11-26 12:06 | 1571 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P211126000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-11-26 | 7855 | keep | 0 | Nov | 2021 | 0.00535 | 0.00107 | Momentary | FALSE | FALSE | Not_TMED_Event | 1571
PONCE | 2021-11-26 12:01 | 2021-11-26 12:06 | 752 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P211126000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-11-26 | 3760 | keep | 0 | Nov | 2021 | 0.0025609 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
PONCE | 2021-11-26 12:09 | 2021-11-26 15:56 | 1571 | 003:47 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 SE PATRULLO LINEA NO SE ENCONTRO CAUSA | P21112600061 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 227 | 2021-11-26 | 356617 | keep | 0 | Nov | 2021 | 0.24289 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-11-26 12:09 | 2021-11-26 15:56 | 752 | 003:47 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 SE PATRULLO LINEA NO SE ENCONTRO CAUSA | P21112600061 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 227 | 2021-11-26 | 170704 | keep | 0 | Nov | 2021 | 0.11627 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-11-26 12:14 | 2021-11-26 13:30 | 10 | 001:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | P21112600001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 76 | 2021-11-26 | 760 | keep | 0 | Nov | 2021 | 0.00051763 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-11-26 12:16 | 2021-11-26 17:11 | 50 | 004:55 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21112600058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 295 | 2021-11-26 | 14750 | keep | 0 | Nov | 2021 | 0.010046 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-26 12:31 | 2021-11-26 15:01 | 50 | 002:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M21112600042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2021-11-26 | 7500 | keep | 0 | Nov | 2021 | 0.0051082 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-11-26 12:35 | 2021-11-27 10:24 | 7 | 021:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BARRA EN PEDESTAL | C21112600100 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1309 | 2021-11-26 | 9163 | keep | 0 | Nov | 2021 | 0.0062409 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-11-26 12:44 | 2021-11-26 12:45 | 225 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 QUE A SU VEZ LLEVA LA CARGA DEL 1303-04 | S21112600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-26 | 225 | keep | 0 | Nov | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-11-26 12:44 | 2021-11-26 12:45 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 QUE A SU VEZ LLEVA LA CARGA DEL 1303-04 | S21112600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-26 | 870 | keep | 0 | Nov | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
MAYAGÃœEZ | 2021-11-26 12:48 | 2021-11-26 15:00 | 27 | 002:12 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21112600045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2021-11-26 | 3564 | keep | 0 | Nov | 2021 | 0.0024274 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2021-11-26 13:08 | 2021-11-26 17:20 | 12 | 004:12 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21112600060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 252 | 2021-11-26 | 3024 | keep | 0 | Nov | 2021 | 0.0020596 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-11-26 13:15 | 2021-11-26 18:14 | 1 | 004:59 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | B21112600174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 299 | 2021-11-26 | 299 | keep | 0 | Nov | 2021 | 0.00020365 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-11-26 13:21 | 2021-11-26 18:10 | 300 | 004:49 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21112600048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 289 | 2021-11-26 | 86700 | keep | 0 | Nov | 2021 | 0.059051 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2021-11-26 13:40 | 2021-11-26 14:31 | 50 | 000:51 | P | DESGANCHE | 1 X 100 EN C/L | C21112600112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 51 | 2021-11-26 | 2550 | keep | 0 | Nov | 2021 | 0.0017368 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-11-26 13:47 | 2021-11-26 15:38 | 80 | 001:51 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21112600177 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 111 | 2021-11-26 | 8880 | keep | 0 | Nov | 2021 | 0.0060481 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2021-11-26 13:59 | 2021-11-26 14:00 | 4132 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21112600065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-26 | 4132 | keep | 0 | Nov | 2021 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
CAGUAS | 2021-11-26 14:05 | 2021-11-26 16:26 | 50 | 002:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN C/L ELIMINO BAJANTE PRIMARIO VACANTE | C21112600119 | New_Event | Wire Down | Include | Include | Equipment | 141 | 2021-11-26 | 7050 | keep | 0 | Nov | 2021 | 0.0048017 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-26 14:09 | 2021-11-26 16:35 | 36 | 002:26 | P | CABLE SOTERRADO AVERIADO | 1 X 65 DE RISER A T-4 AVERIA NUEVA DE T-2 @ T-1 Y VIEJA DE RISER @ T-1 | B21112600180 | New_Event | UG Cable Fault | Include | Include | Equipment | 146 | 2021-11-26 | 5256 | keep | 0 | Nov | 2021 | 0.0035798 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-11-26 14:10 | 2021-11-26 14:12 | 1681 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE LOS ALIMENTADORES 1303-01 Y EL 1346-06 | S21112600071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-26 | 3362 | keep | 0 | Nov | 2021 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-11-26 14:10 | 2021-11-26 14:12 | 1598 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE LOS ALIMENTADORES 1303-01 Y EL 1346-06 | S21112600071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-11-26 | 3196 | keep | 0 | Nov | 2021 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
MAYAGÃœEZ | 2021-11-26 14:19 | 2021-11-26 17:13 | 40 | 002:54 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21112600049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2021-11-26 | 6960 | keep | 0 | Nov | 2021 | 0.0047404 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-11-26 14:26 | 2021-11-26 17:16 | 1 | 002:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA AVERIADA Y PARARRAYOS | M21112600050 | New_Event | Cutout Failure | Include | Include | Equipment | 170 | 2021-11-26 | 170 | keep | 0 | Nov | 2021 | 0.00011579 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-26 14:30 | 2021-11-26 15:05 | 1681 | 000:35 | T | NO SE REPORTO CAUSA | DISPARO DE LOS ALIMENTADORES 1303-01 Y EL 1346-06 | S21112600071 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 35 | 2021-11-26 | 58835 | keep | 0 | Nov | 2021 | 0.040072 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-11-26 14:30 | 2021-11-26 15:05 | 1598 | 000:35 | T | NO SE REPORTO CAUSA | DISPARO DE LOS ALIMENTADORES 1303-01 Y EL 1346-06. SE PATRULLO LINEA Y NO SE REPORTA CAUSA | S21112600071 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 35 | 2021-11-26 | 55930 | keep | 0 | Nov | 2021 | 0.038094 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
HUMACAO | 2021-11-26 14:34 | 2021-11-26 15:42 | 60 | 001:08 | P | DESGANCHE | 2 X 40 EN C/L | C21112600123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2021-11-26 | 4080 | keep | 0 | Nov | 2021 | 0.0027789 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-11-26 14:40 | 2021-11-26 17:50 | 25 | 003:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21112600071 | New_Event | Bad Weather | Include | Include | Weather | 190 | 2021-11-26 | 4750 | keep | 0 | Nov | 2021 | 0.0032352 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2021-11-26 14:47 | 2021-11-26 16:08 | 40 | 001:21 | P | DESGANCHE | 1 X 40 EN C/L | C21112600125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2021-11-26 | 3240 | keep | 0 | Nov | 2021 | 0.0022067 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2021-11-26 15:00 | 2021-11-26 15:33 | 10 | 000:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA AJUSTAR CONEXIONES EN PEDESTAL | P21112600056 | New_Event | Secondary Wire Down | Include | Include | Equipment | 33 | 2021-11-26 | 330 | keep | 0 | Nov | 2021 | 0.00022476 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-11-26 15:44 | 2021-11-27 11:03 | 15 | 019:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CONVERTIDOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21112600074 | New_Event | Bad Weather | Include | Include | Weather | 1159 | 2021-11-26 | 17385 | keep | 0 | Nov | 2021 | 0.011841 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-11-26 15:50 | 2021-11-26 17:00 | 175 | 001:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | R21112600035 | New_Event |  |  | Include | Wildlife | 70 | 2021-11-26 | 12250 | keep | 0 | Nov | 2021 | 0.0083434 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
PONCE | 2021-11-26 16:16 | 2021-11-26 17:45 | 45 | 001:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 1 X 65 EN RISER PAJARO CRUZO FASE | P21112600064 | New_Event |  |  | Include | Wildlife | 89 | 2021-11-26 | 4005 | keep | 0 | Nov | 2021 | 0.0027278 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
HUMACAO | 2021-11-26 16:23 | 2021-11-27 08:53 | 10 | 016:30 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | C21112600132 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 990 | 2021-11-26 | 9900 | keep | 0 | Nov | 2021 | 0.0067428 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-11-26 16:25 | 2021-11-26 18:22 | 325 | 001:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A MACHETE | R21112600042 | New_Event | Wire Down | Include | Include | Equipment | 117 | 2021-11-26 | 38025 | keep | 0 | Nov | 2021 | 0.025899 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
PONCE | 2021-11-26 16:31 | 2021-11-27 10:00 | 57 | 017:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA FUERTE BRISA | P21112600068 | New_Event | Bad Weather | Include | Include | Weather | 1049 | 2021-11-26 | 59793 | keep | 0 | Nov | 2021 | 0.040725 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
BAYAMON | 2021-11-26 16:35 | 2021-11-27 15:27 | 7 | 022:52 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO AVERIADO DE T-2 @ T-1 Y SE ENERGIZO | B21112600196 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1372 | 2021-11-26 | 9604 | keep | 0 | Nov | 2021 | 0.0065412 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-26 16:37 | 2021-11-26 16:38 | 922 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1401-08 QUE A SU VEZ LLE LA CARGA DEL 1346-05 | S21112600097 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-26 | 922 | keep | 0 | Nov | 2021 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-11-26 16:37 | 2021-11-26 16:38 | 135 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1401-08 QUE A SU VEZ LLEVA LA CARGA DEL 1346-05 | S21112600097 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-26 | 135 | keep | 0 | Nov | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2021-11-26 16:38 | 2021-11-26 20:26 | 120 | 003:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE IDENTIFICO PUENTE ABIERTO EN TRONCAL Y SE PROCEDIO A ABRIR MACHETES CON GOI SJ-211126-03 | S21112600103 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 228 | 2021-11-26 | 27360 | keep | 0 | Nov | 2021 | 0.018635 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
PONCE | 2021-11-26 16:40 | 2021-11-26 19:30 | 30 | 002:50 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P21112600069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2021-11-26 | 5100 | keep | 0 | Nov | 2021 | 0.0034736 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2021-11-26 16:42 | 2021-11-26 17:24 | 6 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21112600190 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2021-11-26 | 252 | keep | 0 | Nov | 2021 | 0.00017164 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-11-26 17:01 | 2021-11-27 08:54 | 95 | 015:53 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C21112600135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 953 | 2021-11-26 | 90535 | keep | 0 | Nov | 2021 | 0.061663 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
MAYAGÃœEZ | 2021-11-26 17:05 | 2021-11-26 19:20 | 15 | 002:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M21112600061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 135 | 2021-11-26 | 2025 | keep | 0 | Nov | 2021 | 0.0013792 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2021-11-26 17:28 | 2021-11-27 09:33 | 20 | 016:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21112600078 | New_Event | Bad Weather | Include | Include | Weather | 965 | 2021-11-26 | 19300 | keep | 0 | Nov | 2021 | 0.013145 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-11-26 17:36 | 2021-11-27 08:57 | 8 | 015:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21112600063 | New_Event | Secondary Wire Down | Include | Include | Equipment | 921 | 2021-11-26 | 7368 | keep | 0 | Nov | 2021 | 0.0050183 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-11-26 17:50 | 2021-11-26 17:51 | 1444 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DEL INTERRUPTOR 6014-02 EL CUAL LLEVA LA CARGA DEL 6014-01 NO SE REPORTO CAUSA | M21112600067 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-11-26 | 1444 | keep | 0 | Nov | 2021 | 0.0009835 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2021-11-26 17:50 | 2021-11-26 17:51 | 3630 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6014-01 | M21112600067 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-11-26 | 3630 | keep | 0 | Nov | 2021 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2021-11-26 17:51 | 2021-11-27 11:39 | 50 | 017:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M21112600068 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1068 | 2021-11-26 | 53400 | keep | 0 | Nov | 2021 | 0.03637 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2021-11-26 18:07 | 2021-11-27 09:53 | 75 | 015:46 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C21112600142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 946 | 2021-11-26 | 70950 | keep | 0 | Nov | 2021 | 0.048324 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2021-11-26 18:08 | 2021-11-26 22:26 | 40 | 004:18 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN C/L SE REEMPLAZO PARARRAYO | B21112600200 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 258 | 2021-11-26 | 10320 | keep | 0 | Nov | 2021 | 0.0070289 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-26 18:27 | 2021-11-27 12:18 | 12 | 017:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 25 EN XMR SE REMPLAZO CAJA PRIMARIA | B21112600108 | New_Event | Cutout Failure | Include | Include | Equipment | 1071 | 2021-11-26 | 12852 | keep | 0 | Nov | 2021 | 0.0087534 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-11-26 18:30 | 2021-11-27 09:08 | 6 | 014:38 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21112600071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 878 | 2021-11-26 | 5268 | keep | 0 | Nov | 2021 | 0.003588 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-11-26 18:30 | 2021-11-26 20:23 | 40 | 001:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21112600082 | New_Event | Bad Weather | Include | Include | Weather | 113 | 2021-11-26 | 4520 | keep | 0 | Nov | 2021 | 0.0030786 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-11-26 18:39 | 2021-11-27 16:27 | 2 | 021:48 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA POR UNO DE 37.5 KVA | M21112600070 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1308 | 2021-11-26 | 2616 | keep | 0 | Nov | 2021 | 0.0017817 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2021-11-26 18:40 | 2021-11-27 15:18 | 45 | 020:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C21112600147 | New_Event | Cutout Failure | Include | Include | Equipment | 1238 | 2021-11-26 | 55710 | keep | 0 | Nov | 2021 | 0.037944 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2021-11-26 19:02 | 2021-11-26 21:10 | 21 | 002:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | R21112600051 | New_Event |  |  | Include | Wildlife | 128 | 2021-11-26 | 2688 | keep | 0 | Nov | 2021 | 0.0018308 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BAYAMON | 2021-11-26 19:25 | 2021-11-26 19:26 | 315 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S21112600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-26 | 315 | keep | 0 | Nov | 2021 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
UTUADO | 2021-11-26 19:43 | 2021-11-27 12:30 | 1 | 016:47 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE SECUNDARIO | A21112600087 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1007 | 2021-11-26 | 1007 | keep | 0 | Nov | 2021 | 0.00068586 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-11-26 19:55 | 2021-11-26 21:48 | 50 | 001:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA INFORMA JOURNEYMAN REQUIERE DESGANCHE | A21112600088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2021-11-26 | 5650 | keep | 0 | Nov | 2021 | 0.0038482 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-26 20:02 | 2021-11-27 12:14 | 7 | 016:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR CONECTORES SECUNDARIOS | M21112600077 | New_Event | Secondary Wire Down | Include | Include | Equipment | 972 | 2021-11-26 | 6804 | keep | 0 | Nov | 2021 | 0.0046342 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-11-26 20:04 | 2021-11-26 20:34 | 13 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR CONECTORES EN BAJANTE SECUNDARIO | R21112600029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2021-11-26 | 390 | keep | 0 | Nov | 2021 | 0.00026563 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
FAJARDO | 2021-11-26 20:04 | 2021-11-26 22:43 | 10 | 002:39 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | R21112600054 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 159 | 2021-11-26 | 1590 | keep | 0 | Nov | 2021 | 0.0010829 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-11-26 20:09 | 2021-11-26 23:39 | 3 | 003:30 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR JOURNEYMAN INDICO NO IDENTIFICO CAUSA | M21112600079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 210 | 2021-11-26 | 630 | keep | 0 | Nov | 2021 | 0.00042909 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-11-26 20:26 | 2021-11-26 22:21 | 300 | 001:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES PARA CERRAR PUENTE ABIERTO EN TRONCAL DEL 1346-05 CON GOI SJ-211126-03 | S21112600103 | Additional_clients | Wire Down | Include | Include | Equipment | 115 | 2021-11-26 | 34500 | keep | 0 | Nov | 2021 | 0.023498 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2021-11-26 21:18 | 2021-11-26 21:31 | 2 | 000:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR CONECTORES EN BAJANTE SECUNDARIO | R21112600062 | New_Event | Secondary Wire Down | Include | Include | Equipment | 13 | 2021-11-26 | 26 | keep | 0 | Nov | 2021 | 1.7708e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2021-11-26 21:19 | 2021-11-26 22:53 | 200 | 001:34 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA INDICA JOURNEYMAN QUE REQUIERE DESGANCHE | M21112600099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2021-11-26 | 18800 | keep | 0 | Nov | 2021 | 0.012805 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2021-11-26 22:36 | 2021-11-26 23:25 | 7 | 000:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | A21112600096 | New_Event | Cutout Failure | Include | Include | Equipment | 49 | 2021-11-26 | 343 | keep | 0 | Nov | 2021 | 0.00023362 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2021-11-26 22:42 | 2021-11-27 10:10 | 60 | 011:28 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21112600170 | New_Event | Vegetation Contact | Include | Include | Vegetation | 688 | 2021-11-26 | 41280 | keep | 0 | Nov | 2021 | 0.028116 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2021-11-27 00:46 | 2021-11-27 10:36 | 15 | 009:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21112700001 | New_Event | Bad Weather | Include | Include | Weather | 590 | 2021-11-27 | 8850 | keep | 0 | Nov | 2021 | 0.0060277 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-11-27 01:30 | 2021-11-27 01:31 | 3295 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21112700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-27 | 3295 | keep | 0 | Nov | 2021 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2021-11-27 01:31 | 2021-11-27 09:32 | 50 | 008:01 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B21112700006 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 481 | 2021-11-27 | 24050 | keep | 0 | Nov | 2021 | 0.01638 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-27 01:37 | 2021-11-27 11:39 | 6 | 010:02 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA Y SE REALIZO DESGANCHE | B21112700002 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 602 | 2021-11-27 | 3612 | keep | 0 | Nov | 2021 | 0.0024601 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-11-27 02:07 | 2021-11-27 03:08 | 2450 | 001:01 | T | NO SE REPORTO CAUSA | DISPARO | C21112700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 61 | 2021-11-27 | 149450 | keep | 0 | Nov | 2021 | 0.10179 | 0.0016687 | Sustained | FALSE | FALSE | Not_TMED_Event | 2450
BAYAMON | 2021-11-27 03:21 | 2021-11-27 11:00 | 120 | 007:39 | P | NO SE REPORTO CAUSA | 1 X 65 1 X 50 1 X 40 1 X 25 EN C/L | B21112700004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 459 | 2021-11-27 | 55080 | keep | 0 | Nov | 2021 | 0.037515 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2021-11-27 04:26 | 2021-11-27 04:27 | 1097 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21112700000 | New_Event |  |  | Include | Wildlife | 1 | 2021-11-27 | 1097 | keep | 0 | Nov | 2021 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
MAYAGÃœEZ | 2021-11-27 04:27 | 2021-11-27 17:09 | 60 | 012:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE CRUZO LINEAS | M21112700028 | 1st_after_momentary |  |  | Include | Wildlife | 762 | 2021-11-27 | 45720 | keep | 0 | Nov | 2021 | 0.03114 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2021-11-27 05:07 | 2021-11-27 11:50 | 160 | 006:43 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21112700003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 403 | 2021-11-27 | 64480 | keep | 0 | Nov | 2021 | 0.043917 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
CAGUAS | 2021-11-27 05:53 | 2021-11-27 05:54 | 2417 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21112700006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-27 | 2417 | keep | 0 | Nov | 2021 | 0.0016462 | 0.0016462 | Momentary | FALSE | FALSE | Not_TMED_Event | 2417
CAGUAS | 2021-11-27 05:54 | 2021-11-27 10:21 | 110 | 004:27 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C21112700009 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 267 | 2021-11-27 | 29370 | keep | 0 | Nov | 2021 | 0.020004 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
ARECIBO | 2021-11-27 06:07 | 2021-11-27 09:02 | 125 | 002:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21112700001 | New_Event | Bad Weather | Include | Include | Weather | 175 | 2021-11-27 | 21875 | keep | 0 | Nov | 2021 | 0.014899 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2021-11-27 07:38 | 2021-11-27 09:30 | 52 | 001:52 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S21112700003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2021-11-27 | 5824 | keep | 0 | Nov | 2021 | 0.0039667 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
CAGUAS | 2021-11-27 08:02 | 2021-11-27 16:20 | 112 | 008:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 50 EN CORTE DE LINEA SE ELIMINO SECUNDARIA VACANTE | C21112700014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 498 | 2021-11-27 | 55776 | keep | 0 | Nov | 2021 | 0.037989 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
MAYAGÃœEZ | 2021-11-27 08:24 | 2021-11-27 17:17 | 30 | 008:53 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21112700005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 533 | 2021-11-27 | 15990 | keep | 0 | Nov | 2021 | 0.010891 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-11-27 08:25 | 2021-11-27 14:43 | 6 | 006:18 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 37.5KVA POR UNO DE IGUAL CAPACIDAD | S21112700001 | New_Event | Service Transformer Failure | Include | Include | Equipment | 378 | 2021-11-27 | 2268 | keep | 0 | Nov | 2021 | 0.0015447 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-11-27 08:25 | 2021-11-27 11:46 | 6 | 003:21 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE REPARO SECUNDARIA Y SE DEGANCHO | B21112700005 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 201 | 2021-11-27 | 1206 | keep | 0 | Nov | 2021 | 0.0008214 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-11-27 08:32 | 2021-11-27 14:20 | 79 | 005:48 | P | CABLE SOTERRADO AVERIADO | SE CERRO DE SU-3 @ SU-2 SE LOGRO ENERGIZAR DE TRAMO BUENO REF. BY-211127-02A1 | B21112700013 | New_Event | UG Cable Fault | Include | Include | Equipment | 348 | 2021-11-27 | 27492 | keep | 0 | Nov | 2021 | 0.018725 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
BAYAMON | 2021-11-27 08:43 | 2021-11-27 14:50 | 6 | 006:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO NEUTRAL | B21112700014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 367 | 2021-11-27 | 2202 | keep | 0 | Nov | 2021 | 0.0014998 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-11-27 09:00 | 2021-11-27 10:20 | 6 | 001:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21112600205 | New_Event | Secondary Wire Down | Include | Include | Equipment | 80 | 2021-11-27 | 480 | keep | 0 | Nov | 2021 | 0.00032693 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-11-27 09:25 | 2021-11-27 11:41 | 32 | 002:16 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B21112700017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 136 | 2021-11-27 | 4352 | keep | 0 | Nov | 2021 | 0.0029641 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
PONCE | 2021-11-27 09:33 | 2021-11-27 11:23 | 24 | 001:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA PALOMA CRUZO FASE | P21112700007 | New_Event |  |  | Include | Wildlife | 110 | 2021-11-27 | 2640 | keep | 0 | Nov | 2021 | 0.0017981 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
HUMACAO | 2021-11-27 09:41 | 2021-11-27 09:42 | 5630 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21112700022 | New_Event |  |  | Include | Wildlife | 1 | 2021-11-27 | 5630 | keep | 0 | Nov | 2021 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2021-11-27 09:42 | 2021-11-27 11:02 | 95 | 001:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | C21112700023 | 1st_after_momentary |  |  | Include | Wildlife | 80 | 2021-11-27 | 7600 | keep | 0 | Nov | 2021 | 0.0051763 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
VEGA BAJA | 2021-11-27 09:42 | 2021-11-27 10:31 | 6 | 000:49 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR SE REPARO NEUTRAL Y SE DESGANCHO | B21112600214 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 49 | 2021-11-27 | 294 | keep | 0 | Nov | 2021 | 0.00020024 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-11-27 09:43 | 2021-11-27 13:30 | 10 | 003:47 | P | ESTRUCTURA AVERIADA | SE REALIZO CAMBIO DE POSTE PARTIDO A POSTE EXISTENTE DE CEMENTO | A21112700011 | New_Event | Defective Pole | Include | Include | Equipment | 227 | 2021-11-27 | 2270 | keep | 0 | Nov | 2021 | 0.0015461 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-11-27 09:52 | 2021-11-27 09:53 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21112700011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-27 | 1827 | keep | 0 | Nov | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
ARECIBO | 2021-11-27 09:55 | 2021-11-27 10:14 | 10 | 000:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21112700007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 19 | 2021-11-27 | 190 | keep | 0 | Nov | 2021 | 0.00012941 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-11-27 09:59 | 2021-11-27 11:45 | 120 | 001:46 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21112700004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2021-11-27 | 12720 | keep | 0 | Nov | 2021 | 0.0086635 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
GUAYAMA | 2021-11-27 10:36 | 2021-11-27 12:44 | 4 | 002:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P21112700010 | New_Event | Secondary Wire Down | Include | Include | Equipment | 128 | 2021-11-27 | 512 | keep | 0 | Nov | 2021 | 0.00034872 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2021-11-27 10:57 | 2021-11-27 15:20 | 249 | 004:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE POR RAMA | C21112700030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2021-11-27 | 65487 | keep | 0 | Nov | 2021 | 0.044603 | 0.00016959 | Sustained | FALSE | FALSE | Not_TMED_Event | 249
YAUCO | 2021-11-27 11:00 | 2021-11-27 12:52 | 10 | 001:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P21112700005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 112 | 2021-11-27 | 1120 | keep | 0 | Nov | 2021 | 0.00076283 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-11-27 11:02 | 2021-11-27 11:03 | 863 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21112700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-27 | 863 | keep | 0 | Nov | 2021 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
PONCE | 2021-11-27 11:03 | 2021-11-27 11:36 | 50 | 000:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA PALOMA CRUZO FASE | P21112700011 | New_Event |  |  | Include | Wildlife | 33 | 2021-11-27 | 1650 | keep | 0 | Nov | 2021 | 0.0011238 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-27 11:29 | 2021-11-27 14:52 | 100 | 003:23 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | B21112700024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 203 | 2021-11-27 | 20300 | keep | 0 | Nov | 2021 | 0.013826 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2021-11-27 11:40 | 2021-11-27 14:58 | 100 | 003:18 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | A21112700016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2021-11-27 | 19800 | keep | 0 | Nov | 2021 | 0.013486 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-11-27 11:53 | 2021-11-27 11:54 | 2617 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21112700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-27 | 2617 | keep | 0 | Nov | 2021 | 0.0017824 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
BAYAMON | 2021-11-27 11:57 | 2021-11-27 16:11 | 35 | 004:14 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21112700027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 254 | 2021-11-27 | 8890 | keep | 0 | Nov | 2021 | 0.0060549 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2021-11-27 12:08 | 2021-11-27 15:38 | 120 | 003:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 65 EN C/L SE REMPLAZARON 3 CAJAS PRIMARIAS | B21112700031 | New_Event | Cutout Failure | Include | Include | Equipment | 210 | 2021-11-27 | 25200 | keep | 0 | Nov | 2021 | 0.017164 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
AGUADILLA | 2021-11-27 12:43 | 2021-11-27 15:26 | 200 | 002:43 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21112700019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2021-11-27 | 32600 | keep | 0 | Nov | 2021 | 0.022204 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2021-11-27 13:06 | 2021-11-27 17:04 | 45 | 003:58 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRARON BAMBUAS DE LA LINEA | C21112700034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2021-11-27 | 10710 | keep | 0 | Nov | 2021 | 0.0072945 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2021-11-27 13:18 | 2021-11-27 13:51 | 1 | 000:33 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | R21112600039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 33 | 2021-11-27 | 33 | keep | 0 | Nov | 2021 | 2.2476e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-27 13:20 | 2021-11-27 15:38 | 5 | 002:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21112700037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 138 | 2021-11-27 | 690 | keep | 0 | Nov | 2021 | 0.00046996 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-11-27 13:21 | 2021-11-27 14:40 | 12 | 001:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21112700034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 79 | 2021-11-27 | 948 | keep | 0 | Nov | 2021 | 0.00064568 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2021-11-27 13:26 | 2021-11-27 15:21 | 5 | 001:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 8 EN TRANSFORMADOR CRUCE POR IGUANA | R21112700017 | New_Event |  |  | Include | Wildlife | 115 | 2021-11-27 | 575 | keep | 0 | Nov | 2021 | 0.00039163 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2021-11-27 13:44 | 2021-11-27 15:10 | 95 | 001:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | P21112700025 | New_Event | Wire Down | Include | Include | Equipment | 86 | 2021-11-27 | 8170 | keep | 0 | Nov | 2021 | 0.0055645 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
SAN JUAN | 2021-11-27 14:12 | 2021-11-27 18:41 | 50 | 004:29 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE LINEA | S21112700018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 269 | 2021-11-27 | 13450 | keep | 0 | Nov | 2021 | 0.0091607 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-11-27 14:14 | 2021-11-27 16:01 | 85 | 001:47 | P | PARARRAYOS DEFECTUOSO | 1 X 25 EN CORTE DE LINEA SE REEMPLAZO 2 PARARRAYOS | R21112700018 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 107 | 2021-11-27 | 9095 | keep | 0 | Nov | 2021 | 0.0061946 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
CANOVANAS | 2021-11-27 14:20 | 2021-11-27 15:30 | 45 | 001:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR PALOMA | R21112700019 | New_Event |  |  | Include | Wildlife | 70 | 2021-11-27 | 3150 | keep | 0 | Nov | 2021 | 0.0021455 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
UTUADO | 2021-11-27 15:04 | 2021-11-27 17:00 | 20 | 001:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA EN CORTE DE LINEA | A21112700021 | New_Event | Cutout Failure | Include | Include | Equipment | 116 | 2021-11-27 | 2320 | keep | 0 | Nov | 2021 | 0.0015801 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2021-11-27 15:10 | 2021-11-27 16:10 | 286 | 001:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA CERRAR PUENTE PRIMARIO | P21112700015 | Additional_clients | Wire Down | Include | Include | Equipment | 60 | 2021-11-27 | 17160 | keep | 0 | Nov | 2021 | 0.011688 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-11-27 15:24 | 2021-11-27 16:31 | 6 | 001:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE DE REPTIL | R21112700023 | New_Event |  |  | Include | Wildlife | 67 | 2021-11-27 | 402 | keep | 0 | Nov | 2021 | 0.0002738 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-11-27 15:31 | 2021-11-27 17:11 | 6 | 001:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21112600222 | New_Event | Secondary Wire Down | Include | Include | Equipment | 100 | 2021-11-27 | 600 | keep | 0 | Nov | 2021 | 0.00040866 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2021-11-27 15:53 | 2021-11-27 18:21 | 12 | 002:28 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR BARRA DE NEUTRAL EN PEDESTAL | R21112700024 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 148 | 2021-11-27 | 1776 | keep | 0 | Nov | 2021 | 0.0012096 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-11-27 15:55 | 2021-11-27 17:50 | 35 | 001:55 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE ABREN PUENTES PARA ELIMINAR LINEA FUERA DE USO EN LA CUAL HABIA CAIDO ARBOL | P21112700028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2021-11-27 | 4025 | keep | 0 | Nov | 2021 | 0.0027414 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
YAUCO | 2021-11-27 16:37 | 2021-11-27 16:40 | 1924 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21112700036 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-27 | 5772 | keep | 0 | Nov | 2021 | 0.0039313 | 0.0013104 | Momentary | FALSE | FALSE | Not_TMED_Event | 1924
YAUCO | 2021-11-27 16:37 | 2021-11-27 16:40 | 968 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21112700036 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-27 | 2904 | keep | 0 | Nov | 2021 | 0.0019779 | 0.0006593 | Momentary | FALSE | FALSE | Not_TMED_Event | 968
YAUCO | 2021-11-27 16:37 | 2021-11-27 16:40 | 680 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21112700036 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-27 | 2040 | keep | 0 | Nov | 2021 | 0.0013894 | 0.00046314 | Momentary | FALSE | FALSE | Not_TMED_Event | 680
YAUCO | 2021-11-27 16:37 | 2021-11-27 16:40 | 2246 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21112700036 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-27 | 6738 | keep | 0 | Nov | 2021 | 0.0045892 | 0.0015297 | Momentary | FALSE | FALSE | Not_TMED_Event | 2246
YAUCO | 2021-11-27 16:37 | 2021-11-27 16:40 | 2470 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21112700038 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-27 | 7410 | keep | 0 | Nov | 2021 | 0.0050469 | 0.0016823 | Momentary | FALSE | FALSE | Not_TMED_Event | 2470
YAUCO | 2021-11-27 16:37 | 2021-11-27 16:40 | 1182 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21112700038 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-27 | 3546 | keep | 0 | Nov | 2021 | 0.0024152 | 0.00080505 | Momentary | FALSE | FALSE | Not_TMED_Event | 1182
YAUCO | 2021-11-27 16:37 | 2021-11-27 16:40 | 2340 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21112700038 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-27 | 7020 | keep | 0 | Nov | 2021 | 0.0047813 | 0.0015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 2340
YAUCO | 2021-11-27 16:37 | 2021-11-27 16:40 | 1637 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21112700038 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-27 | 4911 | keep | 0 | Nov | 2021 | 0.0033449 | 0.001115 | Momentary | FALSE | FALSE | Not_TMED_Event | 1637
YAUCO | 2021-11-27 16:37 | 2021-11-27 16:40 | 1475 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21112700040 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-27 | 4425 | keep | 0 | Nov | 2021 | 0.0030138 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
YAUCO | 2021-11-27 16:37 | 2021-11-27 16:40 | 661 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21112700040 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-27 | 1983 | keep | 0 | Nov | 2021 | 0.0013506 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
YAUCO | 2021-11-27 16:37 | 2021-11-27 16:40 | 1569 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21112700037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-27 | 4707 | keep | 0 | Nov | 2021 | 0.0032059 | 0.0010686 | Momentary | FALSE | FALSE | Not_TMED_Event | 1569
YAUCO | 2021-11-27 16:37 | 2021-11-27 16:40 | 2309 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21112700037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-27 | 6927 | keep | 0 | Nov | 2021 | 0.0047179 | 0.0015726 | Momentary | FALSE | FALSE | Not_TMED_Event | 2309
YAUCO | 2021-11-27 16:37 | 2021-11-27 16:40 | 2179 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21112700037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-27 | 6537 | keep | 0 | Nov | 2021 | 0.0044523 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
YAUCO | 2021-11-27 16:37 | 2021-11-27 16:40 | 2440 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21112700037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-27 | 7320 | keep | 0 | Nov | 2021 | 0.0049856 | 0.0016619 | Momentary | FALSE | FALSE | Not_TMED_Event | 2440
YAUCO | 2021-11-27 16:37 | 2021-11-27 18:15 | 1352 | 001:38 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE LLEVO LINEA AL AISLADOR Y SE PUSO ALIMENTADOR EN SERVICIO | P21112700031 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 98 | 2021-11-27 | 132496 | keep | 0 | Nov | 2021 | 0.090242 | 0.00092084 | Sustained | FALSE | FALSE | Not_TMED_Event | 1352
YAUCO | 2021-11-27 16:37 | 2021-11-27 16:40 | 3973 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21112700035 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-27 | 11919 | keep | 0 | Nov | 2021 | 0.008118 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2021-11-27 16:37 | 2021-11-27 16:40 | 2484 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21112700035 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-11-27 | 7452 | keep | 0 | Nov | 2021 | 0.0050755 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
MAYAGÃœEZ | 2021-11-27 16:37 | 2021-11-27 16:42 | 281 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV YAUCO-1 | M21112700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2021-11-27 | 1405 | keep | 0 | Nov | 2021 | 0.00095694 | 0.00019139 | Momentary | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2021-11-27 16:37 | 2021-11-27 16:42 | 1252 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV YAUCO-1 | M21112700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2021-11-27 | 6260 | keep | 0 | Nov | 2021 | 0.0042637 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2021-11-27 16:37 | 2021-11-27 16:42 | 595 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV YAUCO-1 | M21112700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2021-11-27 | 2975 | keep | 0 | Nov | 2021 | 0.0020263 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
MAYAGÃœEZ | 2021-11-27 16:37 | 2021-11-27 16:42 | 51 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV YAUCO-1 | M21112700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2021-11-27 | 255 | keep | 0 | Nov | 2021 | 0.00017368 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2021-11-27 16:37 | 2021-11-27 16:42 | 721 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV YAUCO-1 | M21112700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2021-11-27 | 3605 | keep | 0 | Nov | 2021 | 0.0024553 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
CAGUAS | 2021-11-27 17:11 | 2021-11-27 22:20 | 50 | 005:09 | P | DESGANCHE | 1 X 65 EN C/L | C21112700053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 309 | 2021-11-27 | 15450 | keep | 0 | Nov | 2021 | 0.010523 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-11-27 17:15 | 2021-11-27 18:40 | 10 | 001:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RECONECTO BAJANTE PRIMARIO AL TRANSFORMADOR | P21112700039 | New_Event | Wire Down | Include | Include | Equipment | 85 | 2021-11-27 | 850 | keep | 0 | Nov | 2021 | 0.00057893 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-11-27 17:26 | 2021-11-27 18:39 | 160 | 001:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA CRUCE POR AVE EN EQUIPO DE MEDICION AVERIADO DE PARQUE DE PELOTA | R21112700026 | New_Event |  |  | Include | Wildlife | 73 | 2021-11-27 | 11680 | keep | 0 | Nov | 2021 | 0.0079552 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
UTUADO | 2021-11-27 17:34 | 2021-11-28 10:38 | 10 | 017:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21112700027 | New_Event | Bad Weather | Include | Include | Weather | 1024 | 2021-11-27 | 10240 | keep | 0 | Nov | 2021 | 0.0069744 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-11-27 18:05 | 2021-11-27 18:06 | 776 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C21112700054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-27 | 776 | keep | 0 | Nov | 2021 | 0.00052853 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
HUMACAO | 2021-11-27 18:17 | 2021-11-28 10:34 | 40 | 016:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CRUCE POR AVE | C21112700055 | New_Event |  |  | Include | Wildlife | 977 | 2021-11-27 | 39080 | keep | 0 | Nov | 2021 | 0.026617 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-11-27 18:26 | 2021-11-28 11:43 | 300 | 017:17 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21112700042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1037 | 2021-11-27 | 311100 | keep | 0 | Nov | 2021 | 0.21189 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-11-27 18:27 | 2021-11-28 19:21 | 200 | 024:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | M21112700044 | New_Event | Wire Down | Include | Include | Equipment | 1494 | 2021-11-27 | 298800 | keep | 0 | Nov | 2021 | 0.20351 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-11-27 18:52 | 2021-11-27 21:12 | 35 | 002:20 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21112700047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 140 | 2021-11-27 | 4900 | keep | 0 | Nov | 2021 | 0.0033374 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2021-11-27 19:25 | 2021-11-27 21:36 | 8 | 002:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA PARTIDA | A21112700033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 131 | 2021-11-27 | 1048 | keep | 0 | Nov | 2021 | 0.00071379 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2021-11-27 19:51 | 2021-11-27 19:52 | 1382 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV YAUCO-1 | A21112700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-11-27 | 1382 | keep | 0 | Nov | 2021 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2021-11-27 19:51 | 2021-11-27 19:52 | 654 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV YAUCO-1 | A21112700000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-11-27 | 654 | keep | 0 | Nov | 2021 | 0.00044544 | 0.00044544 | Momentary | FALSE | FALSE | Not_TMED_Event | 654
MAYAGÃœEZ | 2021-11-27 19:54 | 2021-11-28 11:08 | 60 | 015:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | M21112700052 | New_Event | Wire Down | Include | Include | Equipment | 914 | 2021-11-27 | 54840 | keep | 0 | Nov | 2021 | 0.037351 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2021-11-27 20:10 | 2021-11-27 20:11 | 2524 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO INTERRUPTOR CRUCE POR RATA CERRADO POR CONTROL | R21112700029 | New_Event |  |  | Include | Wildlife | 1 | 2021-11-27 | 2524 | keep | 0 | Nov | 2021 | 0.0017191 | 0.0017191 | Momentary | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2021-11-27 20:11 | 2021-11-27 21:25 | 173 | 001:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN RISER AL SU-8 CRUCE POR RATA | R21112700030 | 1st_after_momentary |  |  | Include | Wildlife | 74 | 2021-11-27 | 12802 | keep | 0 | Nov | 2021 | 0.0087194 | 0.00011783 | Sustained | FALSE | FALSE | Not_TMED_Event | 173
AGUADILLA | 2021-11-27 21:01 | 2021-11-27 22:40 | 5 | 001:39 | P | TRANSFORMADOR AVERIADO | SE ABRIO CAJAS DE TRANSFORMADOR PARA AJUSTAR BUSHING SECUNDARIOS | M21112700060 | New_Event | Service Transformer Failure | Include | Include | Equipment | 99 | 2021-11-27 | 495 | keep | 0 | Nov | 2021 | 0.00033714 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-11-27 21:06 | 2021-11-28 14:45 | 10 | 017:39 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA X 25 KVA | M21112700061 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1059 | 2021-11-27 | 10590 | keep | 0 | Nov | 2021 | 0.0072128 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-11-27 21:17 | 2021-11-27 21:18 | 1510 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C21112700063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-27 | 1510 | keep | 0 | Nov | 2021 | 0.0010285 | 0.0010285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1510
CAGUAS | 2021-11-27 21:26 | 2021-11-28 10:29 | 100 | 013:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 80 EN C/L REMPLAZO PIN Y AISLADOR | C21112700065 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 783 | 2021-11-27 | 78300 | keep | 0 | Nov | 2021 | 0.05333 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-11-27 21:42 | 2021-11-27 22:20 | 45 | 000:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE POR AVE | C21112700070 | New_Event |  |  | Include | Wildlife | 38 | 2021-11-27 | 1710 | keep | 0 | Nov | 2021 | 0.0011647 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2021-11-27 22:20 | 2021-11-28 10:13 | 45 | 011:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE POR AVE | C21112700070 | Partial_restoration |  |  | Include | Wildlife | 713 | 2021-11-27 | 32085 | keep | 0 | Nov | 2021 | 0.021853 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-11-27 22:25 | 2021-11-28 11:36 | 50 | 013:11 | P | DESGANCHE | 1 X 65 EN C/L | C21112700053 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 791 | 2021-11-27 | 39550 | keep | 0 | Nov | 2021 | 0.026937 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-11-27 22:55 | 2021-11-28 10:52 | 50 | 011:57 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | C21112700127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 717 | 2021-11-27 | 35850 | keep | 0 | Nov | 2021 | 0.024417 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-27 23:07 | 2021-11-28 09:15 | 15 | 010:08 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S21112700039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 608 | 2021-11-27 | 9120 | keep | 0 | Nov | 2021 | 0.0062116 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-11-27 23:23 | 2021-11-27 23:24 | 553 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1529-15 LLEVANDO 30% DEL 1346-02 | S21112700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-27 | 553 | keep | 0 | Nov | 2021 | 0.00037665 | 0.00037665 | Momentary | FALSE | FALSE | Not_TMED_Event | 553
BAYAMON | 2021-11-27 23:23 | 2021-11-27 23:24 | 1802 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1529-15 LLEVANDO 30% DEL 1346-02 | S21112700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-27 | 1802 | keep | 0 | Nov | 2021 | 0.0012273 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
SAN JUAN | 2021-11-27 23:36 | 2021-11-28 09:35 | 3957 | 009:59 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO LOCAL. SUBESTACION CON PROBLEMAS DE RTU | S21112800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 599 | 2021-11-27 | 2370243 | keep | 0 | Nov | 2021 | 1.6144 | 0.0026951 | Sustained | FALSE | FALSE | Not_TMED_Event | 3957
BAYAMON | 2021-11-27 23:36 | 2021-11-28 11:31 | 45 | 011:55 | P | DESGANCHE | 3 X 100 EN C/L Y 1 X 80 EN C/L SE REALIZO DESGANCHE | S21112700047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 715 | 2021-11-27 | 32175 | keep | 0 | Nov | 2021 | 0.021914 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2021-11-27 23:55 | 2021-11-28 16:17 | 1463 | 016:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA PRIMARIA | S21112700051 | New_Event | Wire Down | Include | Include | Equipment | 982 | 2021-11-27 | 1436666 | keep | 0 | Nov | 2021 | 0.97851 | 0.00099644 | Sustained | FALSE | FALSE | Not_TMED_Event | 1463
ARECIBO | 2021-11-28 00:26 | 2021-11-28 11:11 | 15 | 010:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | VEHICULO IMPACTO POSTE Y SE SALIO EL FUSIBLE DE LA CAJA SE CERRO FUSIBLE EN TRANSFORMADOR | A21112800001 | New_Event |  |  | Include | Wildlife | 645 | 2021-11-28 | 9675 | keep | 0 | Nov | 2021 | 0.0065896 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-11-28 01:05 | 2021-11-28 10:34 | 150 | 009:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21112800002 | New_Event | Bad Weather | Include | Include | Weather | 569 | 2021-11-28 | 85350 | keep | 0 | Nov | 2021 | 0.058131 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2021-11-28 01:36 | 2021-11-28 01:37 | 199 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1529-13 Y SE CERRO POR SCADA | S21112800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-28 | 199 | keep | 0 | Nov | 2021 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
CAGUAS | 2021-11-28 03:02 | 2021-11-28 10:10 | 100 | 007:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L CRUCE POR AVE | C21112800002 | New_Event |  |  | Include | Wildlife | 428 | 2021-11-28 | 42800 | keep | 0 | Nov | 2021 | 0.029151 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-28 03:12 | 2021-11-28 19:00 | 50 | 015:48 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21112800004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 948 | 2021-11-28 | 47400 | keep | 0 | Nov | 2021 | 0.032284 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-11-28 03:17 | 2021-11-28 09:57 | 8 | 006:40 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA RAMA CAYO SOBRE LAS LINEAS | M21112800004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 400 | 2021-11-28 | 3200 | keep | 0 | Nov | 2021 | 0.0021795 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-11-28 03:26 | 2021-11-28 08:23 | 100 | 004:57 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21112800006 | New_Event | Bad Weather | Include | Include | Weather | 297 | 2021-11-28 | 29700 | keep | 0 | Nov | 2021 | 0.020229 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2021-11-28 04:15 | 2021-11-28 14:20 | 66 | 010:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA RATON CRUZO FASE | P21112800028 | New_Event |  |  | Include | Wildlife | 605 | 2021-11-28 | 39930 | keep | 0 | Nov | 2021 | 0.027196 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
CANOVANAS | 2021-11-28 04:51 | 2021-11-28 04:52 | 2580 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11100 | R21112800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-28 | 2580 | keep | 0 | Nov | 2021 | 0.0017572 | 0.0017572 | Momentary | FALSE | FALSE | Not_TMED_Event | 2580
CANOVANAS | 2021-11-28 04:51 | 2021-11-28 04:52 | 500 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11100 | R21112800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-28 | 500 | keep | 0 | Nov | 2021 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
ARECIBO | 2021-11-28 05:28 | 2021-11-28 15:50 | 200 | 010:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ABIERTO SE ABRIO CORTE DE LINEA PARA REPARAR | A21112800017 | New_Event | Wire Down | Include | Include | Equipment | 622 | 2021-11-28 | 124400 | keep | 0 | Nov | 2021 | 0.084728 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2021-11-28 05:58 | 2021-11-28 10:24 | 60 | 004:26 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21112800003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2021-11-28 | 15960 | keep | 0 | Nov | 2021 | 0.01087 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-11-28 06:40 | 2021-11-28 10:35 | 40 | 003:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21112800015 | New_Event | Wire Down | Include | Include | Equipment | 235 | 2021-11-28 | 9400 | keep | 0 | Nov | 2021 | 0.0064023 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-11-28 07:03 | 2021-11-28 12:44 | 100 | 005:41 | P | SOBRECARGA | 1 X 140 EN C/L POR SOBRECARGA | C21112800005 | New_Event | Trip Due To Overload | Include | Include | Other | 341 | 2021-11-28 | 34100 | keep | 0 | Nov | 2021 | 0.023225 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-11-28 07:07 | 2021-11-28 16:23 | 200 | 009:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21112800061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 556 | 2021-11-28 | 111200 | keep | 0 | Nov | 2021 | 0.075738 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-11-28 07:14 | 2021-11-28 07:15 | 271 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21112800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-28 | 271 | keep | 0 | Nov | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
PONCE | 2021-11-28 07:23 | 2021-11-28 10:05 | 10 | 002:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA | P21112800017 | New_Event | Cutout Failure | Include | Include | Equipment | 162 | 2021-11-28 | 1620 | keep | 0 | Nov | 2021 | 0.0011034 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-11-28 07:51 | 2021-11-28 12:57 | 7 | 005:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR REMPLAZO PORTAFUSIBLE | C21112800007 | New_Event | Cutout Failure | Include | Include | Equipment | 306 | 2021-11-28 | 2142 | keep | 0 | Nov | 2021 | 0.0014589 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2021-11-28 08:02 | 2021-11-28 11:40 | 15 | 003:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L CRUCE POR AVE | C21112800009 | New_Event |  |  | Include | Wildlife | 218 | 2021-11-28 | 3270 | keep | 0 | Nov | 2021 | 0.0022272 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2021-11-28 08:09 | 2021-11-28 09:50 | 30 | 001:41 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE REPORTO LA CAUSA | P21112800019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 101 | 2021-11-28 | 3030 | keep | 0 | Nov | 2021 | 0.0020637 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2021-11-28 08:14 | 2021-11-28 14:32 | 10 | 006:18 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50 KVA X 50 KVA | R21112800005 | New_Event | Service Transformer Failure | Include | Include | Equipment | 378 | 2021-11-28 | 3780 | keep | 0 | Nov | 2021 | 0.0025745 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2021-11-28 08:17 | 2021-11-28 09:15 | 15 | 000:58 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO LA CAUSA | P21112800021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 58 | 2021-11-28 | 870 | keep | 0 | Nov | 2021 | 0.00059255 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-11-28 08:18 | 2021-11-28 08:19 | 3744 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE DE ALIMENTADOR DEBIDO A CONTACTO DE AVE CON PARARRAYO CAUSA QUE SE CRUCE CON CRUCETA DE METAL AVERIANDO EL MISMO | P21112800023 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-11-28 | 3744 | keep | 0 | Nov | 2021 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2021-11-28 08:19 | 2021-11-28 11:40 | 85 | 003:21 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN CORTE DE LINEA PARARRAYO AVERIADO POR AVE | P21112800035 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 201 | 2021-11-28 | 17085 | keep | 0 | Nov | 2021 | 0.011637 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
UTUADO | 2021-11-28 08:52 | 2021-11-28 10:26 | 7 | 001:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN TRANSFORMADOR SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A21112800025 | New_Event | Wire Down | Include | Include | Equipment | 94 | 2021-11-28 | 658 | keep | 0 | Nov | 2021 | 0.00044816 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-11-28 08:59 | 2021-11-28 11:19 | 50 | 002:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | A21112800026 | New_Event |  |  | Include | Wildlife | 140 | 2021-11-28 | 7000 | keep | 0 | Nov | 2021 | 0.0047677 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-11-28 09:07 | 2021-11-28 11:17 | 55 | 002:10 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA REEMPLAZO AISLADOR ROTO | R21112800006 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 130 | 2021-11-28 | 7150 | keep | 0 | Nov | 2021 | 0.0048698 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
BAYAMON | 2021-11-28 09:16 | 2021-11-28 11:56 | 16 | 002:40 | P | DESGANCHE | 1 X 15 EN XMR SE REALIZO DESGANCHE | B21112800004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2021-11-28 | 2560 | keep | 0 | Nov | 2021 | 0.0017436 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2021-11-28 09:47 | 2021-11-28 11:11 | 15 | 001:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR PEDESTAL | S21112700025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 84 | 2021-11-28 | 1260 | keep | 0 | Nov | 2021 | 0.00085818 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-11-28 10:22 | 2021-11-28 10:23 | 5630 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21112800014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-28 | 5630 | keep | 0 | Nov | 2021 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
FAJARDO | 2021-11-28 10:27 | 2021-11-28 13:14 | 10 | 002:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR IGUANA | R21112800008 | New_Event |  |  | Include | Wildlife | 167 | 2021-11-28 | 1670 | keep | 0 | Nov | 2021 | 0.0011374 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-11-28 10:35 | 2021-11-28 12:33 | 120 | 001:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 Y 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | R21112800009 | New_Event |  |  | Include | Wildlife | 118 | 2021-11-28 | 14160 | keep | 0 | Nov | 2021 | 0.0096443 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CANOVANAS | 2021-11-28 10:40 | 2021-11-28 13:02 | 15 | 002:22 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR | R21112800010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2021-11-28 | 2130 | keep | 0 | Nov | 2021 | 0.0014507 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-11-28 10:51 | 2021-11-28 12:41 | 20 | 001:50 | P | DESGANCHE | DESGANCHO Y FIJO BAJANTE DE LINEA A CAJA | C21112800018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2021-11-28 | 2200 | keep | 0 | Nov | 2021 | 0.0014984 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-11-28 10:53 | 2021-11-28 14:28 | 8 | 003:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA DE 100 AMP EN TRANSFORMADOR | M21112800015 | New_Event | Cutout Failure | Include | Include | Equipment | 215 | 2021-11-28 | 1720 | keep | 0 | Nov | 2021 | 0.0011715 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-11-28 10:58 | 2021-11-28 14:37 | 50 | 003:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE POR AVE | C21112800020 | New_Event |  |  | Include | Wildlife | 219 | 2021-11-28 | 10950 | keep | 0 | Nov | 2021 | 0.007458 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-11-28 11:05 | 2021-11-28 11:06 | 2228 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE DEL INTERRUPTOR 8007-04 EL CUAL LLEVA LA CARGA DEL 8007-03 MENSAJERO DE LINEA 6900 PEGANDO CON ALIMENTADOR 8007-04 | A21112800044 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-28 | 2228 | keep | 0 | Nov | 2021 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2021-11-28 11:05 | 2021-11-28 11:06 | 438 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE DEL INTERRUPTOR MENSAJERO DE LINEA 6900 PARTIDO PEGANDO CON ALIMENTADOR LLEVA LA CARGA DEL 8007-03 | A21112800044 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-28 | 438 | keep | 0 | Nov | 2021 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
BAYAMON | 2021-11-28 11:07 | 2021-11-28 15:02 | 6 | 003:55 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | B21112800005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 235 | 2021-11-28 | 1410 | keep | 0 | Nov | 2021 | 0.00096034 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2021-11-28 11:15 | 2021-11-28 14:25 | 6 | 003:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B21112800006 | New_Event | Secondary Wire Down | Include | Include | Equipment | 190 | 2021-11-28 | 1140 | keep | 0 | Nov | 2021 | 0.00077645 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-11-28 11:26 | 2021-11-29 16:14 | 5 | 028:48 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN XMR SE DESGANCHO Y SE REPARO SECUNDARIA | S21112800064 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1728 | 2021-11-28 | 8640 | keep | 0 | Nov | 2021 | 0.0058847 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2021-11-28 11:28 | 2021-11-28 15:03 | 8 | 003:35 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR CON DERRAME DE ACEITE DE 25 KVA X 25 KVA | C21112800023 | New_Event | Service Transformer Failure | Include | Include | Equipment | 215 | 2021-11-28 | 1720 | keep | 0 | Nov | 2021 | 0.0011715 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2021-11-28 11:41 | 2021-11-28 13:47 | 46 | 002:06 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21112800037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2021-11-28 | 5796 | keep | 0 | Nov | 2021 | 0.0039476 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
UTUADO | 2021-11-28 11:45 | 2021-11-28 12:30 | 8 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A21112800050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2021-11-28 | 360 | keep | 0 | Nov | 2021 | 0.00024519 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-11-28 11:56 | 2021-11-28 13:01 | 60 | 001:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R21112800016 | New_Event |  |  | Include | Wildlife | 65 | 2021-11-28 | 3900 | keep | 0 | Nov | 2021 | 0.0026563 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2021-11-28 12:28 | 2021-11-28 14:25 | 60 | 001:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA AVE CRUZO FASES | M21112800021 | New_Event |  |  | Include | Wildlife | 117 | 2021-11-28 | 7020 | keep | 0 | Nov | 2021 | 0.0047813 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-11-28 12:41 | 2021-11-28 14:59 | 2228 | 002:18 | T | LINEA DE TRANSMISION 38KV | MENSAJERO DE LINEA 6900 CRUZO EL ALIMENTADOR 8007-04 EL CUAL LLEVA TAMBIEN LA CARGA DEL 8007-03 | A21112800054 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 138 | 2021-11-28 | 307464 | keep | 0 | Nov | 2021 | 0.20941 | 0.0015175 | Sustained | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2021-11-28 12:41 | 2021-11-28 14:59 | 438 | 002:18 | T | LINEA DE TRANSMISION 38KV | MENSAJERO DE LINEA 6900 CRUZO EL ALIMENTADOR 8007-04 EL CUAL LLEVA TAMBIEN LA CARGA DEL 8007-03 | A21112800054 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 138 | 2021-11-28 | 60444 | keep | 0 | Nov | 2021 | 0.041168 | 0.00029832 | Sustained | FALSE | FALSE | Not_TMED_Event | 438
BAYAMON | 2021-11-28 12:52 | 2021-11-28 17:46 | 30 | 004:54 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER Y 3 X 80 EN SU-4 | S21112800038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 294 | 2021-11-28 | 8820 | keep | 0 | Nov | 2021 | 0.0060073 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-11-28 13:27 | 2021-11-28 18:44 | 22 | 005:17 | P | DESGANCHE | ABRIO C/L PARA DESGANCHAR | C21112800028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 317 | 2021-11-28 | 6974 | keep | 0 | Nov | 2021 | 0.00475 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
CANOVANAS | 2021-11-28 13:38 | 2021-11-28 15:28 | 7 | 001:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | R21112800021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 110 | 2021-11-28 | 770 | keep | 0 | Nov | 2021 | 0.00052444 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-11-28 13:52 | 2021-11-28 14:02 | 6 | 000:10 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B21112800010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2021-11-28 | 60 | keep | 0 | Nov | 2021 | 4.0866e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-11-28 13:55 | 2021-11-28 15:55 | 1590 | 002:00 | T | NO SE REPORTO CAUSA | DISPARO NO SE REPORTO CAUSA | C21112800029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2021-11-28 | 190800 | keep | 0 | Nov | 2021 | 0.12995 | 0.0010829 | Sustained | FALSE | FALSE | Not_TMED_Event | 1590
ARECIBO | 2021-11-28 14:21 | 2021-11-28 14:51 | 15 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A21112800067 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2021-11-28 | 450 | keep | 0 | Nov | 2021 | 0.00030649 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-11-28 14:37 | 2021-11-28 17:42 | 2608 | 003:05 | T | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO EL ALIMENTADOR | C21112800063 | New_Event | Switch Failure | Include | Include | Equipment | 185 | 2021-11-28 | 482480 | keep | 0 | Nov | 2021 | 0.32861 | 0.0017763 | Sustained | FALSE | FALSE | Not_TMED_Event | 2608
CAGUAS | 2021-11-28 14:38 | 2021-11-29 09:29 | 11 | 018:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR IGUANA | C21112800041 | New_Event |  |  | Include | Wildlife | 1131 | 2021-11-28 | 12441 | keep | 0 | Nov | 2021 | 0.0084735 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
VEGA BAJA | 2021-11-28 14:43 | 2021-11-28 16:33 | 30 | 001:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE CERRO FUSIBLE ALEGAN CLIENTES ESTABAN REALIZANDO ALGO QUE SE ABRIO | B21112800016 | New_Event |  |  | Include | Wildlife | 110 | 2021-11-28 | 3300 | keep | 0 | Nov | 2021 | 0.0022476 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-11-28 14:45 | 2021-11-29 13:15 | 6 | 022:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA Y SE DESGANCHO | M21112800025 | New_Event | Wire Down | Include | Include | Equipment | 1350 | 2021-11-28 | 8100 | keep | 0 | Nov | 2021 | 0.0055169 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-11-28 14:58 | 2021-11-28 16:57 | 50 | 001:59 | P | DESGANCHE | 1 X 65 EN C/L | C21112800058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2021-11-28 | 5950 | keep | 0 | Nov | 2021 | 0.0040525 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-11-28 15:11 | 2021-11-28 15:12 | 1979 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21112800047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-28 | 1979 | keep | 0 | Nov | 2021 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2021-11-28 15:16 | 2021-11-28 17:56 | 58 | 002:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | P21112800048 | New_Event |  |  | Include | Wildlife | 160 | 2021-11-28 | 9280 | keep | 0 | Nov | 2021 | 0.0063206 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
ARECIBO | 2021-11-28 15:50 | 2021-11-28 17:05 | 400 | 001:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO SE CERRO CORTE DE LINEA | A21112800017 | New_Event | Wire Down | Include | Include | Equipment | 75 | 2021-11-28 | 30000 | keep | 0 | Nov | 2021 | 0.020433 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
ARECIBO | 2021-11-28 15:50 | 2021-11-28 16:51 | 10 | 001:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A21112800072 | New_Event | Secondary Wire Down | Include | Include | Equipment | 61 | 2021-11-28 | 610 | keep | 0 | Nov | 2021 | 0.00041547 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-11-28 15:58 | 2021-11-28 19:08 | 6 | 003:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO NEUTRAL | B21112800019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 190 | 2021-11-28 | 1140 | keep | 0 | Nov | 2021 | 0.00077645 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-11-28 16:11 | 2021-11-28 19:33 | 3 | 003:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M21112800031 | New_Event | Bad Weather | Include | Include | Weather | 202 | 2021-11-28 | 606 | keep | 0 | Nov | 2021 | 0.00041274 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-11-28 16:23 | 2021-11-28 16:31 | 873 | 000:08 | T | FUEGO | SE ABRIO INTERRUPTOR DE EMERGENCIA PARA SECCIONALIZAR POSTE EN FUEGO | M21112800030 | New_Event | Fire | Include | Include | Public | 8 | 2021-11-28 | 6984 | keep | 0 | Nov | 2021 | 0.0047568 | 0.0005946 | Sustained | FALSE | FALSE | Not_TMED_Event | 873
ARECIBO | 2021-11-28 16:29 | 2021-11-28 20:55 | 30 | 004:26 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21112800079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2021-11-28 | 7980 | keep | 0 | Nov | 2021 | 0.0054351 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-11-28 16:38 | 2021-11-28 16:39 | 2147 | 000:01 | T | DESGANCHE | RECIERRE | B21112800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-28 | 2147 | keep | 0 | Nov | 2021 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
MAYAGÃœEZ | 2021-11-28 16:39 | 2021-11-29 12:15 | 500 | 019:36 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETES AVERIADOS | M21112800040 | New_Event | Switch Failure | Include | Include | Equipment | 1176 | 2021-11-28 | 588000 | keep | 0 | Nov | 2021 | 0.40048 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
MAYAGÃœEZ | 2021-11-28 16:43 | 2021-11-28 18:25 | 200 | 001:42 | P | DESGANCHE | 2 X 140 EN CORTE DE LINEA SE RETIRO RAMA | M21112800039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2021-11-28 | 20400 | keep | 0 | Nov | 2021 | 0.013894 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-11-28 16:46 | 2021-11-28 16:47 | 2147 | 000:01 | T | DESGANCHE | RECIERRE | B21112800000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-28 | 2147 | keep | 0 | Nov | 2021 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
FAJARDO | 2021-11-28 17:03 | 2021-11-29 15:54 | 11 | 022:51 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR T-27 DE 50KVA X 50KVA | R21112800023 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1371 | 2021-11-28 | 15081 | keep | 0 | Nov | 2021 | 0.010272 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2021-11-28 17:07 | 2021-11-29 16:54 | 23 | 023:47 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | S21112800049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1427 | 2021-11-28 | 32821 | keep | 0 | Nov | 2021 | 0.022354 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
ARECIBO | 2021-11-28 17:11 | 2021-11-28 21:56 | 80 | 004:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | A21112800087 | New_Event |  |  | Include | Wildlife | 285 | 2021-11-28 | 22800 | keep | 0 | Nov | 2021 | 0.015529 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2021-11-28 17:26 | 2021-11-30 13:30 | 12 | 044:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO EVENTO DEL DIA 28 VERIFICADO EN BITACORA | A21112800085 | New_Event | Wire Down | Include | Include | Equipment | 2644 | 2021-11-28 | 31728 | keep | 0 | Nov | 2021 | 0.02161 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-11-28 17:42 | 2021-11-28 18:50 | 1600 | 001:08 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO MACHETE QUEMADO Y SE TRANSFIRIO PARTE DE LA CARGA AL 3006-02 | C21112800063 | Partial_restoration | Switch Failure | Include | Include | Equipment | 68 | 2021-11-28 | 108800 | keep | 0 | Nov | 2021 | 0.074103 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-11-28 17:55 | 2021-11-28 18:45 | 5 | 000:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | M21112800047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 50 | 2021-11-28 | 250 | keep | 0 | Nov | 2021 | 0.00017027 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-11-28 17:55 | 2021-11-28 20:06 | 150 | 002:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21112800086 | New_Event | Wire Down | Include | Include | Equipment | 131 | 2021-11-28 | 19650 | keep | 0 | Nov | 2021 | 0.013384 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-11-28 18:05 | 2021-11-29 11:10 | 20 | 017:05 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21112800055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1025 | 2021-11-28 | 20500 | keep | 0 | Nov | 2021 | 0.013962 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-11-28 18:15 | 2021-11-28 22:07 | 40 | 003:52 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | S21112800054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 232 | 2021-11-28 | 9280 | keep | 0 | Nov | 2021 | 0.0063206 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-28 18:16 | 2021-11-28 19:01 | 2147 | 000:45 | T | DESGANCHE | SE SECCIONALIZO Y SE CERRO POR SCADA | B21112800027 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 45 | 2021-11-28 | 96615 | keep | 0 | Nov | 2021 | 0.065804 | 0.0014623 | Sustained | FALSE | FALSE | Not_TMED_Event | 2147
UTUADO | 2021-11-28 18:22 | 2021-11-29 12:13 | 2 | 017:51 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | A21112800089 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1071 | 2021-11-28 | 2142 | keep | 0 | Nov | 2021 | 0.0014589 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2021-11-28 18:35 | 2021-11-28 18:36 | 2096 | 000:01 | T | DESGANCHE | RECIERRE | B21112800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-28 | 2096 | keep | 0 | Nov | 2021 | 0.0014276 | 0.0014276 | Momentary | FALSE | FALSE | Not_TMED_Event | 2096
BAYAMON | 2021-11-28 18:36 | 2021-11-28 23:03 | 200 | 004:27 | P | DESGANCHE | 1 X 80 EN C/L Y X X 50 EN OTRO C/L. SE RETIRO ARBOL SOBRE LINEAS Y SE LEVANTO CONDUCTOR | B21112800043 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 267 | 2021-11-28 | 53400 | keep | 0 | Nov | 2021 | 0.03637 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
UTUADO | 2021-11-28 18:40 | 2021-11-28 22:12 | 250 | 003:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 200 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y SE REALIZO DESGANCHE | A21112800042 | New_Event | Wire Down | Include | Include | Equipment | 212 | 2021-11-28 | 53000 | keep | 0 | Nov | 2021 | 0.036098 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
CAGUAS | 2021-11-28 18:59 | 2021-11-29 13:14 | 9 | 018:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BARRA EN PEDESTAL AVERIADA | C21112800119 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1095 | 2021-11-28 | 9855 | keep | 0 | Nov | 2021 | 0.0067122 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-11-28 19:01 | 2021-11-28 20:06 | 1000 | 001:05 | P | DESGANCHE | SE DESGANCHO BAMBUAS Y SE CERRO MACHETES | B21112800027 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 65 | 2021-11-28 | 65000 | keep | 0 | Nov | 2021 | 0.044271 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2021-11-28 19:07 | 2021-11-28 22:14 | 9 | 003:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 25 EN TRANSFORMADOR SE LEVANTO LINEA SECUNDARIA DEL SUELO | P21112800055 | New_Event | Secondary Wire Down | Include | Include | Equipment | 187 | 2021-11-28 | 1683 | keep | 0 | Nov | 2021 | 0.0011463 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2021-11-28 19:29 | 2021-11-28 19:30 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21112800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-28 | 312 | keep | 0 | Nov | 2021 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
ARECIBO | 2021-11-28 20:18 | 2021-11-28 22:42 | 80 | 002:24 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21112800102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2021-11-28 | 11520 | keep | 0 | Nov | 2021 | 0.0078462 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-11-28 20:29 | 2021-11-28 23:00 | 15 | 002:31 | P | NO SE REPORTO CAUSA | 1 X 20 EN C/L | B21112800060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 151 | 2021-11-28 | 2265 | keep | 0 | Nov | 2021 | 0.0015427 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-11-28 20:36 | 2021-11-28 22:53 | 300 | 002:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR FUERTES LLUVIAS | M21112800072 | New_Event | Bad Weather | Include | Include | Weather | 137 | 2021-11-28 | 41100 | keep | 0 | Nov | 2021 | 0.027993 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BARRANQUITAS | 2021-11-28 20:46 | 2021-11-29 10:05 | 11 | 013:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE HACIA XMR | C21112800041 | New_Event | Wire Down | Include | Include | Equipment | 799 | 2021-11-28 | 8789 | keep | 0 | Nov | 2021 | 0.0059861 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
HUMACAO | 2021-11-28 21:10 | 2021-11-29 12:07 | 55 | 014:57 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21112800129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 897 | 2021-11-28 | 49335 | keep | 0 | Nov | 2021 | 0.033602 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
ARECIBO | 2021-11-28 23:44 | 2021-11-29 09:40 | 8 | 009:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21112800110 | New_Event | Bad Weather | Include | Include | Weather | 596 | 2021-11-28 | 4768 | keep | 0 | Nov | 2021 | 0.0032475 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-11-29 00:46 | 2021-11-29 09:08 | 20 | 008:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA FUERTE | B21112900001 | New_Event | Bad Weather | Include | Include | Weather | 502 | 2021-11-29 | 10040 | keep | 0 | Nov | 2021 | 0.0068382 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-11-29 00:58 | 2021-11-29 00:59 | 2126 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C21112900001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-29 | 2126 | keep | 0 | Nov | 2021 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
ARECIBO | 2021-11-29 01:26 | 2021-11-29 10:35 | 40 | 009:09 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA INFORMA JOURNEYMAN REQUIERE DESGANCHE | A21112900001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 549 | 2021-11-29 | 21960 | keep | 0 | Nov | 2021 | 0.014957 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-29 01:51 | 2021-11-29 10:37 | 40 | 008:46 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | S21112900002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 526 | 2021-11-29 | 21040 | keep | 0 | Nov | 2021 | 0.01433 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-11-29 02:32 | 2021-11-29 12:50 | 2 | 010:18 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA INFORMA JOURNEYMAN REQUIERE DESGANCHE | A21112900002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 618 | 2021-11-29 | 1236 | keep | 0 | Nov | 2021 | 0.00084183 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2021-11-29 03:26 | 2021-11-29 09:16 | 2635 | 005:50 | T | BREAKER DEFECTUOSO O NO OPERA | SE TRANSFIRIO CARGA 9902-01 QUE NO QUIERE PERMANECER CERRADO AL 9902-02 POR BARRA DE INSPECCION | C21112900003 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 350 | 2021-11-29 | 922250 | keep | 0 | Nov | 2021 | 0.62814 | 0.0017947 | Sustained | FALSE | FALSE | Not_TMED_Event | 2635
BAYAMON | 2021-11-29 03:44 | 2021-11-29 10:12 | 20 | 006:28 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21112900004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 388 | 2021-11-29 | 7760 | keep | 0 | Nov | 2021 | 0.0052853 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-11-29 04:53 | 2021-11-29 11:09 | 50 | 006:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21112900003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 376 | 2021-11-29 | 18800 | keep | 0 | Nov | 2021 | 0.012805 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-11-29 05:26 | 2021-11-29 06:33 | 1979 | 001:07 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE SUBESTACION LOCKOUT AVES CRUZARON FASES | P21112900031 | New_Event |  |  | Include | Wildlife | 67 | 2021-11-29 | 132593 | keep | 0 | Nov | 2021 | 0.090308 | 0.0013479 | Sustained | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2021-11-29 05:26 | 2021-11-29 06:33 | 3114 | 001:07 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE SUBESTACION LOCKOUT AVES CRUZARON FASES | P21112900031 | New_Event |  |  | Include | Wildlife | 67 | 2021-11-29 | 208638 | keep | 0 | Nov | 2021 | 0.1421 | 0.0021209 | Sustained | FALSE | FALSE | Not_TMED_Event | 3114
PONCE | 2021-11-29 05:26 | 2021-11-29 06:33 | 5069 | 001:07 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE SUBESTACION LOCKOUT AVES CRUZARON FASES | P21112900031 | New_Event |  |  | Include | Wildlife | 67 | 2021-11-29 | 339623 | keep | 0 | Nov | 2021 | 0.23132 | 0.0034525 | Sustained | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2021-11-29 05:26 | 2021-11-29 06:33 | 2696 | 001:07 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE SUBESTACION LOCKOUT AVES CRUZARON FASES | P21112900031 | New_Event |  |  | Include | Wildlife | 67 | 2021-11-29 | 180632 | keep | 0 | Nov | 2021 | 0.12303 | 0.0018362 | Sustained | FALSE | FALSE | Not_TMED_Event | 2696
PONCE | 2021-11-29 05:26 | 2021-11-29 06:33 | 5063 | 001:07 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE SUBESTACION LOCKOUT AVES CRUZARON FASES | P21112900031 | New_Event |  |  | Include | Wildlife | 67 | 2021-11-29 | 339221 | keep | 0 | Nov | 2021 | 0.23104 | 0.0034484 | Sustained | FALSE | FALSE | Not_TMED_Event | 5063
BAYAMON | 2021-11-29 05:49 | 2021-11-29 11:01 | 20 | 005:12 | P | CABLE SOTERRADO AVERIADO | 1 X 30 EN RISER A PM 75 AVERIA SOTERRADA DE PM 76 A PM 77 | B21112900006 | New_Event | UG Cable Fault | Include | Include | Equipment | 312 | 2021-11-29 | 6240 | keep | 0 | Nov | 2021 | 0.00425 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-11-29 06:42 | 2021-11-29 09:43 | 1 | 003:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | M21112900007 | New_Event |  |  | Include | Wildlife | 181 | 2021-11-29 | 181 | keep | 0 | Nov | 2021 | 0.00012328 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-29 07:01 | 2021-11-30 13:06 | 40 | 030:05 | P | TRANSFORMADOR AVERIADO | 1 X 80 EN CORTE DE LINEA 1 X 65 EN RISER 1 X 40 EN SU AVERIA EN TRANSFORMADOR T6 SE DEJO SECCIONALIZADO | S21111300009 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1805 | 2021-11-29 | 72200 | keep | 0 | Nov | 2021 | 0.049175 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2021-11-29 07:15 | 2021-11-29 09:27 | 50 | 002:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA IGUANA CRUZO LINEAS | M21112900008 | New_Event |  |  | Include | Wildlife | 132 | 2021-11-29 | 6600 | keep | 0 | Nov | 2021 | 0.0044952 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2021-11-29 07:20 | 2021-11-29 09:04 | 1 | 001:44 | P | NO SE REPORTO CAUSA | 1 X 15 EN BANCO DE TRANSFORMADOR | R21112900009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2021-11-29 | 104 | keep | 0 | Nov | 2021 | 7.0834e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-29 07:24 | 2021-11-29 10:35 | 1 | 003:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN RISER SE REMPLAZO CAJA PRIMARIA | B21112900010 | New_Event | Cutout Failure | Include | Include | Equipment | 191 | 2021-11-29 | 191 | keep | 0 | Nov | 2021 | 0.00013009 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-11-29 07:37 | 2021-11-29 07:38 | 2126 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA | C21112900025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-29 | 2126 | keep | 0 | Nov | 2021 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
CAGUAS | 2021-11-29 07:39 | 2021-11-29 10:27 | 95 | 002:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA CRUCE POR AVE | C21112900030 | New_Event |  |  | Include | Wildlife | 168 | 2021-11-29 | 15960 | keep | 0 | Nov | 2021 | 0.01087 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
CANOVANAS | 2021-11-29 07:53 | 2021-11-29 11:34 | 60 | 003:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R21112900011 | New_Event |  |  | Include | Wildlife | 221 | 2021-11-29 | 13260 | keep | 0 | Nov | 2021 | 0.0090313 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-11-29 08:00 | 2021-11-29 10:21 | 3 | 002:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21112900014 | New_Event | Bad Weather | Include | Include | Weather | 141 | 2021-11-29 | 423 | keep | 0 | Nov | 2021 | 0.0002881 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-11-29 08:08 | 2021-11-29 12:30 | 50 | 004:22 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S21112900015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 262 | 2021-11-29 | 13100 | keep | 0 | Nov | 2021 | 0.0089224 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2021-11-29 08:16 | 2021-11-29 10:04 | 60 | 001:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO CORTE DE LINEA PARA RETIRAR TENSOR SOBRE CAJA PRIMARIA | C21112900037 | New_Event |  |  | Include | Wildlife | 108 | 2021-11-29 | 6480 | keep | 0 | Nov | 2021 | 0.0044135 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2021-11-29 08:19 | 2021-11-29 10:31 | 80 | 002:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA POR CRUCE DE FASES POR AVE | P21112900070 | New_Event |  |  | Include | Wildlife | 132 | 2021-11-29 | 10560 | keep | 0 | Nov | 2021 | 0.0071924 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-11-29 08:30 | 2021-11-29 17:30 | 13 | 009:00 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 50KVA POR UNO DE IGUAL CAPACIDAD | B21112900017 | New_Event | Service Transformer Failure | Include | Include | Equipment | 540 | 2021-11-29 | 7020 | keep | 0 | Nov | 2021 | 0.0047813 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2021-11-29 08:36 | 2021-11-29 08:37 | 966 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21112900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-29 | 966 | keep | 0 | Nov | 2021 | 0.00065794 | 0.00065794 | Momentary | FALSE | FALSE | Not_TMED_Event | 966
YAUCO | 2021-11-29 08:44 | 2021-11-29 11:35 | 10 | 002:51 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR POR DESGANCHE | P21112900073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2021-11-29 | 1710 | keep | 0 | Nov | 2021 | 0.0011647 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-11-29 08:45 | 2021-11-29 12:18 | 12 | 003:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | R21112900014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 213 | 2021-11-29 | 2556 | keep | 0 | Nov | 2021 | 0.0017409 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-11-29 08:50 | 2021-11-29 08:51 | 2608 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21112900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-29 | 2608 | keep | 0 | Nov | 2021 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
CAGUAS | 2021-11-29 08:51 | 2021-11-29 14:27 | 60 | 005:36 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER @ SU-3 | C21112900012 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 336 | 2021-11-29 | 20160 | keep | 0 | Nov | 2021 | 0.013731 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2021-11-29 08:51 | 2021-11-29 15:54 | 1 | 007:03 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA NO SE REPORTO CAUSA | P21112900074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 423 | 2021-11-29 | 423 | keep | 0 | Nov | 2021 | 0.0002881 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-11-29 08:57 | 2021-11-29 11:43 | 100 | 002:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA NO FUNDIO FUSIBLE | R21112900017 | New_Event | Cutout Failure | Include | Include | Equipment | 166 | 2021-11-29 | 16600 | keep | 0 | Nov | 2021 | 0.011306 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2021-11-29 08:57 | 2021-11-29 11:59 | 20 | 003:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21112900025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2021-11-29 | 3640 | keep | 0 | Nov | 2021 | 0.0024792 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-11-29 09:01 | 2021-11-29 17:33 | 1 | 008:32 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | R21112900018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 512 | 2021-11-29 | 512 | keep | 0 | Nov | 2021 | 0.00034872 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-11-29 09:06 | 2021-11-29 13:16 | 10 | 004:10 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REMPLAZO POSTE SECUNDARIO PARTIDO | B21112900028 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 250 | 2021-11-29 | 2500 | keep | 0 | Nov | 2021 | 0.0017027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-11-29 09:08 | 2021-11-29 11:14 | 12 | 002:06 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA POR PARARRAYO ACTIVADO | P21112900078 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 126 | 2021-11-29 | 1512 | keep | 0 | Nov | 2021 | 0.0010298 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-11-29 09:12 | 2021-11-29 15:17 | 10 | 006:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR AVE CRUZO LINEAS | P21112900080 | New_Event |  |  | Include | Wildlife | 365 | 2021-11-29 | 3650 | keep | 0 | Nov | 2021 | 0.002486 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-11-29 09:14 | 2021-11-29 09:16 | 2280 | 000:02 | T | BREAKER DEFECTUOSO O NO OPERA | SE ABRIO 9902-03 LLEVANDO LA CARGA DEL 9902-02 PARA PODER TRANSFERIR CARGA POR BARRA INSPECCION DEL 9902-01 QUE NO QUIERE PERMANECER CERRADO | C21112900050 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 2 | 2021-11-29 | 4560 | keep | 0 | Nov | 2021 | 0.0031058 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2021-11-29 09:14 | 2021-11-29 09:16 | 1617 | 000:02 | T | BREAKER DEFECTUOSO O NO OPERA | SE ABRIO 9902-03 LLEVANDO LA CARGA DEL 9902-02 PARA PODER TRANSFERIR CARGA POR BARRA INSPECCION DEL 9902-01 QUE NO QUIERE PERMANECER CERRADO | C21112900050 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 2 | 2021-11-29 | 3234 | keep | 0 | Nov | 2021 | 0.0022027 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
BARRANQUITAS | 2021-11-29 09:16 | 2021-11-29 09:45 | 635 | 000:29 | P | DESGANCHE | DESGANCHO BAMBUAS Y CERRO CORTE DE LINEA | C21112900003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 29 | 2021-11-29 | 18415 | keep | 0 | Nov | 2021 | 0.012542 | 0.0004325 | Sustained | FALSE | FALSE | Not_TMED_Event | 635
BAYAMON | 2021-11-29 09:35 | 2021-11-30 16:05 | 1 | 030:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN BANCO DE TRANSFORMADORE Y SE RETIRO GUIDE CRUZANDO CON BANCO DE TRANSFORMADORES | B21112900030 | New_Event |  |  | Include | Wildlife | 1830 | 2021-11-29 | 1830 | keep | 0 | Nov | 2021 | 0.0012464 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-11-29 09:46 | 2021-11-29 13:57 | 20 | 004:11 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA Y 1 X 15 EN XMR | R21112900020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 251 | 2021-11-29 | 5020 | keep | 0 | Nov | 2021 | 0.0034191 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2021-11-29 09:46 | 2021-11-29 12:00 | 10 | 002:14 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA POR UNO DE 50 KVA | M21112900032 | New_Event | Service Transformer Failure | Include | Include | Equipment | 134 | 2021-11-29 | 1340 | keep | 0 | Nov | 2021 | 0.00091267 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-11-29 09:51 | 2021-11-29 10:21 | 3 | 000:30 | T | OTRAS CAUSAS | DISPARO Y SE CERRO POR SCADA | S21112900026 | New_Event | Other Causes | Include | Include | Other | 30 | 2021-11-29 | 90 | keep | 0 | Nov | 2021 | 6.1299e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2021-11-29 10:04 | 2021-11-29 10:05 | 2725 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8500/4800 | C21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 2725 | keep | 0 | Nov | 2021 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2021-11-29 10:04 | 2021-11-29 10:05 | 1834 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8500/4800 | C21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 1834 | keep | 0 | Nov | 2021 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2021-11-29 10:04 | 2021-11-29 10:05 | 1437 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8500/4800 | C21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 1437 | keep | 0 | Nov | 2021 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2021-11-29 10:04 | 2021-11-29 10:05 | 2565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8500/4800 | C21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 2565 | keep | 0 | Nov | 2021 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2021-11-29 10:04 | 2021-11-29 10:05 | 3565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8500/4800 | C21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 3565 | keep | 0 | Nov | 2021 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
PONCE | 2021-11-29 10:04 | 2021-11-29 10:05 | 2751 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA TRANSMISION 4800 | P21112900087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 2751 | keep | 0 | Nov | 2021 | 0.0018737 | 0.0018737 | Momentary | FALSE | FALSE | Not_TMED_Event | 2751
PONCE | 2021-11-29 10:04 | 2021-11-29 10:05 | 576 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA TRANSMISION 4800 | P21112900087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 576 | keep | 0 | Nov | 2021 | 0.00039231 | 0.00039231 | Momentary | FALSE | FALSE | Not_TMED_Event | 576
PONCE | 2021-11-29 10:04 | 2021-11-29 10:05 | 2584 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA TRANSMISION 4800 | P21112900087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 2584 | keep | 0 | Nov | 2021 | 0.00176 | 0.00176 | Momentary | FALSE | FALSE | Not_TMED_Event | 2584
PONCE | 2021-11-29 10:04 | 2021-11-29 10:05 | 1606 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA TRANSMISION 4800 | P21112900087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 1606 | keep | 0 | Nov | 2021 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
PONCE | 2021-11-29 10:04 | 2021-11-29 10:05 | 29 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA TRANSMISION 4800 | P21112900087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 29 | keep | 0 | Nov | 2021 | 1.9752e-05 | 1.9752e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 29
PONCE | 2021-11-29 10:04 | 2021-11-29 10:05 | 4035 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA TRANSMISION 4800 | P21112900087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 4035 | keep | 0 | Nov | 2021 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
PONCE | 2021-11-29 10:04 | 2021-11-29 10:05 | 3718 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA TRANSMISION 4800 | P21112900087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 3718 | keep | 0 | Nov | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
BARRANQUITAS | 2021-11-29 10:05 | 2021-11-29 16:00 | 60 | 005:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO CORTE DE LINEA PARA RETIRAR TENSOR SOBRE CAJA PRIMARIA | C21112900037 | New_Event |  |  | Include | Wildlife | 355 | 2021-11-29 | 21300 | keep | 0 | Nov | 2021 | 0.014507 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-11-29 10:07 | 2021-11-30 11:10 | 12 | 025:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | S21112900029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1503 | 2021-11-29 | 18036 | keep | 0 | Nov | 2021 | 0.012284 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-11-29 10:16 | 2021-11-29 13:10 | 11 | 002:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO BARRA EN PEDESTAL | R21112900022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 174 | 2021-11-29 | 1914 | keep | 0 | Nov | 2021 | 0.0013036 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2021-11-29 10:17 | 2021-11-29 15:00 | 6 | 004:43 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR Y SE REMPLAZO POSTE SECUNDARIO PARTIDO | B21112900039 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 283 | 2021-11-29 | 1698 | keep | 0 | Nov | 2021 | 0.0011565 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-11-29 10:21 | 2021-11-29 11:07 | 1 | 000:46 | P | OTRAS CAUSAS | SE ENCONTRO SUBESTACION PRIVADA DEL POLIDEPORTIVO CON FUSIBLES FUNDIDOS | S21112900026 | New_Event | Other Causes | Include | Include | Other | 46 | 2021-11-29 | 46 | keep | 0 | Nov | 2021 | 3.133e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-29 10:22 | 2021-11-29 12:59 | 30 | 002:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO DE LINEA A CAJA EN CORTE DE LINEA | B21112900040 | New_Event | Wire Down | Include | Include | Equipment | 157 | 2021-11-29 | 4710 | keep | 0 | Nov | 2021 | 0.003208 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-11-29 10:27 | 2021-11-29 17:55 | 4 | 007:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO CONECTOR EN SECUNDARIA | C21112900119 | New_Event | Secondary Wire Down | Include | Include | Equipment | 448 | 2021-11-29 | 1792 | keep | 0 | Nov | 2021 | 0.0012205 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2021-11-29 10:39 | 2021-11-29 16:49 | 12 | 006:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REEMPLAZO CAJA DE TRANSFORMADOR | R21112900025 | New_Event | Cutout Failure | Include | Include | Equipment | 370 | 2021-11-29 | 4440 | keep | 0 | Nov | 2021 | 0.0030241 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-11-29 10:43 | 2021-11-29 15:49 | 10 | 005:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REEMPLAZO BARRA EN PEDESTAL | R21112900024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 306 | 2021-11-29 | 3060 | keep | 0 | Nov | 2021 | 0.0020842 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-29 10:45 | 2021-11-29 11:18 | 7 | 000:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A21112800051 | New_Event | Secondary Wire Down | Include | Include | Equipment | 33 | 2021-11-29 | 231 | keep | 0 | Nov | 2021 | 0.00015733 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-11-29 10:47 | 2021-11-29 13:50 | 1 | 003:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21112900038 | New_Event | Bad Weather | Include | Include | Weather | 183 | 2021-11-29 | 183 | keep | 0 | Nov | 2021 | 0.00012464 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-29 10:54 | 2021-11-29 15:43 | 15 | 004:49 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | S21112900036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 289 | 2021-11-29 | 4335 | keep | 0 | Nov | 2021 | 0.0029525 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-11-29 11:00 | 2021-11-29 16:01 | 6 | 005:01 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE DESGANCHO Y SE REPARO SECUNDARIA | B21112900043 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 301 | 2021-11-29 | 1806 | keep | 0 | Nov | 2021 | 0.0012301 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-11-29 11:01 | 2021-11-30 14:56 | 12 | 027:55 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO DE T-78 @ T-77 Y SE ENERGIZO T-77 | B21112900006 | New_Event | UG Cable Fault | Include | Include | Equipment | 1675 | 2021-11-29 | 20100 | keep | 0 | Nov | 2021 | 0.01369 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-11-29 11:07 | 2021-11-29 11:08 | 3 | 000:01 | T | OTRAS CAUSAS | SE ABRE INTERRUPTOR PARA CERRAR GANGA CONTAMINADA HACIA CLIENTE. 3 X 25 EN RISER SE ORIENTO CLIENTE CONTAMINACION SUBESTACION PRIVADA | S21112900026 | Additional_clients | Other Causes | Include | Include | Other | 1 | 2021-11-29 | 3 | keep | 0 | Nov | 2021 | 2.0433e-06 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-11-29 11:15 | 2021-11-29 11:16 | 1117 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 1117 | keep | 0 | Nov | 2021 | 0.00076078 | 0.00076078 | Momentary | FALSE | FALSE | Not_TMED_Event | 1117
MAYAGÃœEZ | 2021-11-29 11:15 | 2021-11-29 11:16 | 1671 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 1671 | keep | 0 | Nov | 2021 | 0.0011381 | 0.0011381 | Momentary | FALSE | FALSE | Not_TMED_Event | 1671
MAYAGÃœEZ | 2021-11-29 11:15 | 2021-11-29 11:16 | 527 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 527 | keep | 0 | Nov | 2021 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
MAYAGÃœEZ | 2021-11-29 11:15 | 2021-11-29 11:16 | 671 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 671 | keep | 0 | Nov | 2021 | 0.00045702 | 0.00045702 | Momentary | FALSE | FALSE | Not_TMED_Event | 671
ARECIBO | 2021-11-29 11:15 | 2021-11-29 11:45 | 18 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A21112900033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2021-11-29 | 540 | keep | 0 | Nov | 2021 | 0.00036779 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
YAUCO | 2021-11-29 11:16 | 2021-11-29 11:18 | 591 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21112900092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-29 | 1182 | keep | 0 | Nov | 2021 | 0.00080505 | 0.00040253 | Momentary | FALSE | FALSE | Not_TMED_Event | 591
YAUCO | 2021-11-29 11:16 | 2021-11-29 11:18 | 1924 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21112900092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-29 | 3848 | keep | 0 | Nov | 2021 | 0.0026209 | 0.0013104 | Momentary | FALSE | FALSE | Not_TMED_Event | 1924
YAUCO | 2021-11-29 11:16 | 2021-11-29 11:18 | 968 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21112900092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-29 | 1936 | keep | 0 | Nov | 2021 | 0.0013186 | 0.0006593 | Momentary | FALSE | FALSE | Not_TMED_Event | 968
YAUCO | 2021-11-29 11:16 | 2021-11-29 11:18 | 680 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21112900092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-29 | 1360 | keep | 0 | Nov | 2021 | 0.00092629 | 0.00046314 | Momentary | FALSE | FALSE | Not_TMED_Event | 680
YAUCO | 2021-11-29 11:16 | 2021-11-29 11:18 | 2246 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21112900092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-29 | 4492 | keep | 0 | Nov | 2021 | 0.0030595 | 0.0015297 | Momentary | FALSE | FALSE | Not_TMED_Event | 2246
YAUCO | 2021-11-29 11:16 | 2021-11-29 11:18 | 2011 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21112900092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-29 | 4022 | keep | 0 | Nov | 2021 | 0.0027394 | 0.0013697 | Momentary | FALSE | FALSE | Not_TMED_Event | 2011
YAUCO | 2021-11-29 11:16 | 2021-11-29 11:18 | 339 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21112900092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-29 | 678 | keep | 0 | Nov | 2021 | 0.00046178 | 0.00023089 | Momentary | FALSE | FALSE | Not_TMED_Event | 339
YAUCO | 2021-11-29 11:16 | 2021-11-29 11:18 | 2470 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21112900092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-29 | 4940 | keep | 0 | Nov | 2021 | 0.0033646 | 0.0016823 | Momentary | FALSE | FALSE | Not_TMED_Event | 2470
YAUCO | 2021-11-29 11:16 | 2021-11-29 11:18 | 1182 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21112900092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-29 | 2364 | keep | 0 | Nov | 2021 | 0.0016101 | 0.00080505 | Momentary | FALSE | FALSE | Not_TMED_Event | 1182
YAUCO | 2021-11-29 11:16 | 2021-11-29 11:18 | 2340 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21112900092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-29 | 4680 | keep | 0 | Nov | 2021 | 0.0031875 | 0.0015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 2340
YAUCO | 2021-11-29 11:16 | 2021-11-29 11:18 | 1637 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21112900092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-29 | 3274 | keep | 0 | Nov | 2021 | 0.0022299 | 0.001115 | Momentary | FALSE | FALSE | Not_TMED_Event | 1637
YAUCO | 2021-11-29 11:16 | 2021-11-29 11:18 | 1475 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21112900092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-29 | 2950 | keep | 0 | Nov | 2021 | 0.0020092 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
YAUCO | 2021-11-29 11:16 | 2021-11-29 11:18 | 661 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21112900092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-29 | 1322 | keep | 0 | Nov | 2021 | 0.00090041 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
YAUCO | 2021-11-29 11:16 | 2021-11-29 11:18 | 1569 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21112900092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-29 | 3138 | keep | 0 | Nov | 2021 | 0.0021373 | 0.0010686 | Momentary | FALSE | FALSE | Not_TMED_Event | 1569
YAUCO | 2021-11-29 11:16 | 2021-11-29 11:18 | 2309 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21112900092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-29 | 4618 | keep | 0 | Nov | 2021 | 0.0031453 | 0.0015726 | Momentary | FALSE | FALSE | Not_TMED_Event | 2309
YAUCO | 2021-11-29 11:16 | 2021-11-29 11:18 | 2179 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21112900092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-29 | 4358 | keep | 0 | Nov | 2021 | 0.0029682 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
YAUCO | 2021-11-29 11:16 | 2021-11-29 11:18 | 2440 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21112900092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-29 | 4880 | keep | 0 | Nov | 2021 | 0.0033237 | 0.0016619 | Momentary | FALSE | FALSE | Not_TMED_Event | 2440
YAUCO | 2021-11-29 11:16 | 2021-11-29 11:18 | 1352 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21112900092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-29 | 2704 | keep | 0 | Nov | 2021 | 0.0018417 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
YAUCO | 2021-11-29 11:16 | 2021-11-29 11:18 | 3973 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21112900092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-29 | 7946 | keep | 0 | Nov | 2021 | 0.005412 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2021-11-29 11:16 | 2021-11-29 11:18 | 2484 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | P21112900092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-11-29 | 4968 | keep | 0 | Nov | 2021 | 0.0033837 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
BAYAMON | 2021-11-29 11:18 | 2021-11-29 11:19 | 2147 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21112900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-29 | 2147 | keep | 0 | Nov | 2021 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
MAYAGÃœEZ | 2021-11-29 11:42 | 2021-11-29 11:43 | 1253 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1500 | M21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 1253 | keep | 0 | Nov | 2021 | 0.00085341 | 0.00085341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2021-11-29 11:42 | 2021-11-29 11:43 | 1266 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1500 | M21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 1266 | keep | 0 | Nov | 2021 | 0.00086227 | 0.00086227 | Momentary | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2021-11-29 11:42 | 2021-11-29 11:43 | 411 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1500 | M21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 411 | keep | 0 | Nov | 2021 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2021-11-29 11:42 | 2021-11-29 11:43 | 108 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1500 | M21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 108 | keep | 0 | Nov | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
SAN JUAN | 2021-11-29 11:45 | 2021-11-29 12:48 | 2566 | 001:03 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO SE ABRIO SU-14 FTE. PONCE DE LEON 40% EN SERVICIO | S21112900045 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 63 | 2021-11-29 | 161658 | keep | 0 | Nov | 2021 | 0.1101 | 0.0017477 | Sustained | FALSE | FALSE | Not_TMED_Event | 2566
BAYAMON | 2021-11-29 11:45 | 2021-11-29 12:59 | 45 | 001:14 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR 1111-01 QUE LLEVA EL 5% DE LA CARGA DEL 1115-05 | S21112900045 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 74 | 2021-11-29 | 3330 | keep | 0 | Nov | 2021 | 0.002268 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2021-11-29 11:55 | 2021-11-29 14:23 | 1 | 002:28 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 75 KVA POR UNO DE 75 KVA | M21112900056 | New_Event | Service Transformer Failure | Include | Include | Equipment | 148 | 2021-11-29 | 148 | keep | 0 | Nov | 2021 | 0.0001008 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-11-29 12:01 | 2021-11-29 12:02 | 1089 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 JUNCOS @ RIO BLANCO | C21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 1089 | keep | 0 | Nov | 2021 | 0.00074171 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2021-11-29 12:01 | 2021-11-29 12:02 | 3896 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 JUNCOS @ RIO BLANCO | C21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 3896 | keep | 0 | Nov | 2021 | 0.0026535 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2021-11-29 12:01 | 2021-11-29 12:02 | 1467 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 JUNCOS @ RIO BLANCO | C21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 1467 | keep | 0 | Nov | 2021 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
BAYAMON | 2021-11-29 12:06 | 2021-11-29 14:19 | 40 | 002:13 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21112900049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 133 | 2021-11-29 | 5320 | keep | 0 | Nov | 2021 | 0.0036234 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2021-11-29 12:27 | 2021-11-29 16:40 | 4 | 004:13 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR POSTE SECUNDARIO ROTO | C21112900076 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 253 | 2021-11-29 | 1012 | keep | 0 | Nov | 2021 | 0.00068927 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2021-11-29 12:33 | 2021-11-29 16:35 | 15 | 004:02 | P | DESGANCHE | 1 X 40 EN CONVERTIDOR SE RETIRO RAMA | A21112900043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2021-11-29 | 3630 | keep | 0 | Nov | 2021 | 0.0024724 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-11-29 12:35 | 2021-11-29 13:21 | 10 | 000:46 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21112100056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 46 | 2021-11-29 | 460 | keep | 0 | Nov | 2021 | 0.0003133 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-29 12:37 | 2021-11-29 16:26 | 32 | 003:49 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21112900062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 229 | 2021-11-29 | 7328 | keep | 0 | Nov | 2021 | 0.0049911 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
BAYAMON | 2021-11-29 12:43 | 2021-11-29 12:44 | 766 | 000:01 | P | ESTRUCTURA AVERIADA | RECIERRE DE INTERRUPTOR 1909-07 LLEVANDO 50% 1709-03 | S21112900000 | New_Event | Defective Pole | Include | Include | Equipment | 1 | 2021-11-29 | 766 | keep | 0 | Nov | 2021 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2021-11-29 12:43 | 2021-11-29 12:44 | 1139 | 000:01 | T | ESTRUCTURA AVERIADA | RECIERRE DE INTERRUPTOR 1909-07 LLEVANDO 50% 1709-03 | S21112900000 | New_Event | Defective Pole | Include | Include | Equipment | 1 | 2021-11-29 | 1139 | keep | 0 | Nov | 2021 | 0.00077577 | 0.00077577 | Momentary | FALSE | FALSE | Not_TMED_Event | 1139
BAYAMON | 2021-11-29 12:44 | 2021-11-29 18:33 | 26 | 005:49 | P | ESTRUCTURA AVERIADA | SE ABRIO C/L PARA ENDEREZAR POSTE A PUNTO DE CAER | S21112900060 | 1st_after_momentary | Defective Pole | Include | Include | Equipment | 349 | 2021-11-29 | 9074 | keep | 0 | Nov | 2021 | 0.0061803 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
MAYAGÃœEZ | 2021-11-29 12:46 | 2021-11-29 16:00 | 70 | 003:14 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21112900061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2021-11-29 | 13580 | keep | 0 | Nov | 2021 | 0.0092493 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2021-11-29 12:48 | 2021-11-29 12:59 | 2000 | 000:11 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE CERRO SU-14 A SU-12 100% EN SERVICIO | S21112900045 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 11 | 2021-11-29 | 22000 | keep | 0 | Nov | 2021 | 0.014984 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-11-29 12:57 | 2021-11-29 14:40 | 18 | 001:43 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR DE 37.5KVA X 37.5KVA CON DERRAME DE ACEITE | C21112900080 | New_Event | Service Transformer Failure | Include | Include | Equipment | 103 | 2021-11-29 | 1854 | keep | 0 | Nov | 2021 | 0.0012628 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2021-11-29 13:01 | 2021-11-29 13:06 | 2566 | 000:05 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO Y SE ABRIO SU-14 A SU-12 FTE. FIRST BANK 40% EN SERVICIO | S21112900045 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 5 | 2021-11-29 | 12830 | keep | 0 | Nov | 2021 | 0.0087385 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-29 13:01 | 2021-11-29 17:44 | 45 | 004:43 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR 1111-01 QUE LLEVA EL 5% DE LA CARGA DEL 1115-05 SE REALIZARON OPERACIONES DE CAMPO Y SE RESTABLECIO SERVICIO PARCIAL MENOS LA CARGA DEL HOSPITAL PAVIA | S21112900045 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 283 | 2021-11-29 | 12735 | keep | 0 | Nov | 2021 | 0.0086738 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-11-29 13:01 | 2021-11-29 19:32 | 25 | 006:31 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR POSTE PRIMARIO PARTIDO | P21112900101 | New_Event | Defective Pole | Include | Include | Equipment | 391 | 2021-11-29 | 9775 | keep | 0 | Nov | 2021 | 0.0066577 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-11-29 13:06 | 2021-11-29 14:52 | 2000 | 001:46 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE CERRO SU-14 A SU-12 | S21112900045 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 106 | 2021-11-29 | 212000 | keep | 0 | Nov | 2021 | 0.14439 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-29 13:06 | 2021-11-30 19:15 | 12 | 030:09 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO PM T-6 AVERIADO DE 75KVA POR UNO DE 100KVA Y SE ENERGIZO DEL T-5 @ T-6 | S21113000009 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1809 | 2021-11-29 | 21708 | keep | 0 | Nov | 2021 | 0.014785 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-11-29 13:20 | 2021-11-29 16:13 | 8 | 002:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REEMPLAZAR BARRA EN PEDESTAL | C21112900083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 173 | 2021-11-29 | 1384 | keep | 0 | Nov | 2021 | 0.00094264 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-11-29 13:22 | 2021-11-29 22:29 | 8 | 009:07 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO SECUNDARIO | M21112900067 | New_Event | Defective Pole | Include | Include | Equipment | 547 | 2021-11-29 | 4376 | keep | 0 | Nov | 2021 | 0.0029805 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-11-29 13:29 | 2021-11-29 15:51 | 110 | 002:22 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21112900086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2021-11-29 | 15620 | keep | 0 | Nov | 2021 | 0.010639 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
HUMACAO | 2021-11-29 13:33 | 2021-11-29 18:08 | 2 | 004:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | C21112900087 | New_Event | Secondary Wire Down | Include | Include | Equipment | 275 | 2021-11-29 | 550 | keep | 0 | Nov | 2021 | 0.0003746 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2021-11-29 13:36 | 2021-11-29 17:41 | 85 | 004:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA REPARO CONDUCTOR ROTO | C21112900089 | New_Event | Wire Down | Include | Include | Equipment | 245 | 2021-11-29 | 20825 | keep | 0 | Nov | 2021 | 0.014184 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
CAGUAS | 2021-11-29 13:36 | 2021-11-29 15:33 | 110 | 001:57 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C21112900088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2021-11-29 | 12870 | keep | 0 | Nov | 2021 | 0.0087657 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
MAYAGÃœEZ | 2021-11-29 13:46 | 2021-11-29 17:00 | 10 | 003:14 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA POR UNO DE 50 KVA | M21112900073 | New_Event | Service Transformer Failure | Include | Include | Equipment | 194 | 2021-11-29 | 1940 | keep | 0 | Nov | 2021 | 0.0013213 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-11-29 13:48 | 2021-11-29 13:49 | 2457 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21112900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-29 | 2457 | keep | 0 | Nov | 2021 | 0.0016735 | 0.0016735 | Momentary | FALSE | FALSE | Not_TMED_Event | 2457
ARECIBO | 2021-11-29 13:58 | 2021-11-29 13:59 | 2201 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR | A21112900000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-11-29 | 2201 | keep | 0 | Nov | 2021 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
BAYAMON | 2021-11-29 13:59 | 2021-11-30 15:57 | 65 | 025:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | S21112900046 | New_Event | Cutout Failure | Include | Include | Equipment | 1558 | 2021-11-29 | 101270 | keep | 0 | Nov | 2021 | 0.068975 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
ARECIBO | 2021-11-29 13:59 | 2021-11-29 16:38 | 3 | 002:39 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | A21112900058 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 159 | 2021-11-29 | 477 | keep | 0 | Nov | 2021 | 0.00032488 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-11-29 14:07 | 2021-11-29 18:16 | 50 | 004:09 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21112900072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 249 | 2021-11-29 | 12450 | keep | 0 | Nov | 2021 | 0.0084796 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-11-29 14:11 | 2021-11-29 14:12 | 569 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2500 | M21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 569 | keep | 0 | Nov | 2021 | 0.00038754 | 0.00038754 | Momentary | FALSE | FALSE | Not_TMED_Event | 569
AGUADILLA | 2021-11-29 14:11 | 2021-11-29 14:12 | 1245 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2500 | M21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 1245 | keep | 0 | Nov | 2021 | 0.00084796 | 0.00084796 | Momentary | FALSE | FALSE | Not_TMED_Event | 1245
AGUADILLA | 2021-11-29 14:11 | 2021-11-29 14:12 | 1155 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2500 | M21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 1155 | keep | 0 | Nov | 2021 | 0.00078667 | 0.00078667 | Momentary | FALSE | FALSE | Not_TMED_Event | 1155
AGUADILLA | 2021-11-29 14:11 | 2021-11-29 14:12 | 867 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2500 | M21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 867 | keep | 0 | Nov | 2021 | 0.00059051 | 0.00059051 | Momentary | FALSE | FALSE | Not_TMED_Event | 867
AGUADILLA | 2021-11-29 14:11 | 2021-11-29 14:12 | 257 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2500 | M21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 257 | keep | 0 | Nov | 2021 | 0.00017504 | 0.00017504 | Momentary | FALSE | FALSE | Not_TMED_Event | 257
AGUADILLA | 2021-11-29 14:11 | 2021-11-29 14:12 | 1336 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2500 | M21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 1336 | keep | 0 | Nov | 2021 | 0.00090994 | 0.00090994 | Momentary | FALSE | FALSE | Not_TMED_Event | 1336
AGUADILLA | 2021-11-29 14:11 | 2021-11-29 14:12 | 3315 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2500 | M21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 3315 | keep | 0 | Nov | 2021 | 0.0022578 | 0.0022578 | Momentary | FALSE | FALSE | Not_TMED_Event | 3315
AGUADILLA | 2021-11-29 14:11 | 2021-11-29 14:12 | 1718 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2500 | M21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-11-29 | 1718 | keep | 0 | Nov | 2021 | 0.0011701 | 0.0011701 | Momentary | FALSE | FALSE | Not_TMED_Event | 1718
SAN JUAN | 2021-11-29 14:26 | 2021-11-29 17:27 | 25 | 003:01 | P | CABLE SOTERRADO AVERIADO | 1 X 25 EN TRANSFOAMDOR T-5 Y SE REPORTA AVERIA SOTERRADA HACIA T-6 | S21112900072 | New_Event | UG Cable Fault | Include | Include | Equipment | 181 | 2021-11-29 | 4525 | keep | 0 | Nov | 2021 | 0.003082 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2021-11-29 14:28 | 2021-11-29 19:39 | 40 | 005:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21112900054 | New_Event | Bad Weather | Include | Include | Weather | 311 | 2021-11-29 | 12440 | keep | 0 | Nov | 2021 | 0.0084728 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-11-29 14:43 | 2021-11-29 20:23 | 24 | 005:40 | P | DESGANCHE | 1 X 40 EN C/L SE REALIZO DESGANCHE | B21112900063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 340 | 2021-11-29 | 8160 | keep | 0 | Nov | 2021 | 0.0055577 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
SAN JUAN | 2021-11-29 14:52 | 2021-11-29 14:53 | 2566 | 000:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR EN OPERACIONES DE RESTABLECIMIENTO. 60% FUERA | S21112900045 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2021-11-29 | 2566 | keep | 0 | Nov | 2021 | 0.0017477 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-29 14:53 | 2021-11-29 16:26 | 1500 | 001:33 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE CERRO DE VS-7 AL VS-3 | S21112900045 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 93 | 2021-11-29 | 139500 | keep | 0 | Nov | 2021 | 0.095013 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
CAGUAS | 2021-11-29 14:55 | 2021-11-29 18:11 | 6 | 003:16 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA X 37.5KVA | C21112900099 | New_Event | Service Transformer Failure | Include | Include | Equipment | 196 | 2021-11-29 | 1176 | keep | 0 | Nov | 2021 | 0.00080097 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2021-11-29 15:26 | 2021-11-30 12:15 | 8 | 020:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P21112900109 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1249 | 2021-11-29 | 9992 | keep | 0 | Nov | 2021 | 0.0068055 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2021-11-29 15:30 | 2021-11-29 17:43 | 70 | 002:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21112900057 | New_Event | Bad Weather | Include | Include | Weather | 133 | 2021-11-29 | 9310 | keep | 0 | Nov | 2021 | 0.006341 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
YAUCO | 2021-11-29 15:50 | 2021-11-29 17:43 | 10 | 001:53 | P | TRANSFORMADOR AVERIADO | SE ABRIO TRANSFORMADOR PARA REPARAR BUSHING SECUNDARIO NO FUNDIO FUSIBLE | P21112900076 | New_Event | Service Transformer Failure | Include | Include | Equipment | 113 | 2021-11-29 | 1130 | keep | 0 | Nov | 2021 | 0.00076964 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-11-29 15:52 | 2021-11-30 16:46 | 5 | 024:54 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 25 KVA X 25 KVA | C21112900103 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1494 | 2021-11-29 | 7470 | keep | 0 | Nov | 2021 | 0.0050878 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-11-29 15:56 | 2021-11-29 19:00 | 30 | 003:04 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21112900082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2021-11-29 | 5520 | keep | 0 | Nov | 2021 | 0.0037596 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2021-11-29 15:59 | 2021-11-29 20:48 | 1827 | 004:49 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2800 | M21112900173 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 289 | 2021-11-29 | 528003 | keep | 0 | Nov | 2021 | 0.35962 | 0.0012444 | Sustained | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2021-11-29 15:59 | 2021-11-29 20:47 | 1047 | 004:48 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2800 | M21112900247 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 288 | 2021-11-29 | 301536 | keep | 0 | Nov | 2021 | 0.20537 | 0.00071311 | Sustained | FALSE | FALSE | Not_TMED_Event | 1047
AGUADILLA | 2021-11-29 15:59 | 2021-11-29 19:45 | 4882 | 003:46 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2800 | M21112900174 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 226 | 2021-11-29 | 1103332 | keep | 0 | Nov | 2021 | 0.75147 | 0.0033251 | Sustained | FALSE | FALSE | Not_TMED_Event | 4882
BAYAMON | 2021-11-29 16:04 | 2021-11-29 23:36 | 70 | 007:32 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B21112900071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 452 | 2021-11-29 | 31640 | keep | 0 | Nov | 2021 | 0.02155 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2021-11-29 16:07 | 2021-11-29 16:08 | 5042 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21112900067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-29 | 5042 | keep | 0 | Nov | 2021 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
ARECIBO | 2021-11-29 16:10 | 2021-11-29 17:12 | 1 | 001:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | A21112900022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 62 | 2021-11-29 | 62 | keep | 0 | Nov | 2021 | 4.2228e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-11-29 16:26 | 2021-11-29 16:29 | 2566 | 000:03 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR EN OPERACIONES DE RESTABLECIMIENTO. | S21112900045 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 3 | 2021-11-29 | 7698 | keep | 0 | Nov | 2021 | 0.0052431 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-29 16:29 | 2021-11-29 17:14 | 850 | 000:45 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR EN OPERACIONES DE RESTABLECIMIENTO. | S21112900045 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 45 | 2021-11-29 | 38250 | keep | 0 | Nov | 2021 | 0.026052 | 0.00057893 | Sustained | FALSE | FALSE | Not_TMED_Event | 850
YAUCO | 2021-11-29 16:29 | 2021-11-30 12:20 | 100 | 019:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BEJUCO | P21112900111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1191 | 2021-11-29 | 119100 | keep | 0 | Nov | 2021 | 0.081118 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2021-11-29 16:37 | 2021-11-30 12:19 | 30 | 019:42 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | A21112900070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1182 | 2021-11-29 | 35460 | keep | 0 | Nov | 2021 | 0.024152 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-11-29 16:42 | 2021-11-29 18:35 | 15 | 001:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21112900132 | New_Event | Bad Weather | Include | Include | Weather | 113 | 2021-11-29 | 1695 | keep | 0 | Nov | 2021 | 0.0011545 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2021-11-29 16:45 | 2021-11-29 16:46 | 1376 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21112900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-29 | 1376 | keep | 0 | Nov | 2021 | 0.00093719 | 0.00093719 | Momentary | FALSE | FALSE | Not_TMED_Event | 1376
SAN JUAN | 2021-11-29 16:49 | 2021-11-29 22:24 | 34 | 005:35 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | S21112900105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 335 | 2021-11-29 | 11390 | keep | 0 | Nov | 2021 | 0.0077577 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
CAGUAS | 2021-11-29 16:50 | 2021-11-29 18:32 | 90 | 001:42 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | C21112900114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 102 | 2021-11-29 | 9180 | keep | 0 | Nov | 2021 | 0.0062525 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
ARECIBO | 2021-11-29 16:59 | 2021-11-29 18:20 | 1105 | 001:21 | T | DESGANCHE | SE ABRIO MACHETES PARA SECCIONALIZAR POR BAMBUS SOBRE LINEA | A21112900071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2021-11-29 | 89505 | keep | 0 | Nov | 2021 | 0.060961 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
SAN JUAN | 2021-11-29 17:14 | 2021-11-29 17:44 | 2566 | 000:30 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR EN OPERACIONES DE RESTABLECIMIENTO. | S21112900045 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 30 | 2021-11-29 | 76980 | keep | 0 | Nov | 2021 | 0.052431 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-11-29 17:15 | 2021-11-30 10:27 | 8 | 017:12 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR QUEMADO 25 KVA X 25 KVA | C21112900119 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1032 | 2021-11-29 | 8256 | keep | 0 | Nov | 2021 | 0.0056231 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-11-29 17:17 | 2021-11-29 21:20 | 200 | 004:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21112900152 | New_Event | Bad Weather | Include | Include | Weather | 243 | 2021-11-29 | 48600 | keep | 0 | Nov | 2021 | 0.033101 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2021-11-29 17:18 | 2021-11-29 18:23 | 100 | 001:05 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEAS NO SE REPORTO CAUSA | P21112900119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 65 | 2021-11-29 | 6500 | keep | 0 | Nov | 2021 | 0.0044271 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2021-11-29 17:20 | 2021-11-29 18:32 | 120 | 001:12 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21112900029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2021-11-29 | 8640 | keep | 0 | Nov | 2021 | 0.0058847 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
AGUADILLA | 2021-11-29 17:20 | 2021-11-29 17:35 | 25 | 000:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO CAJAS DE TRANSFORMADOR PARA RELOCALIZAR TENSOR CRUZANDO LINEA | M21112900124 | New_Event |  |  | Include | Wildlife | 15 | 2021-11-29 | 375 | keep | 0 | Nov | 2021 | 0.00025541 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2021-11-29 17:31 | 2021-11-29 17:44 | 60 | 000:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | P21112900120 | New_Event |  |  | Include | Wildlife | 13 | 2021-11-29 | 780 | keep | 0 | Nov | 2021 | 0.00053125 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2021-11-29 17:38 | 2021-11-29 18:44 | 25 | 001:06 | P | DESGANCHE | SE ABRIO CORTE DE LINEA POR EMERGENCIA PARA REMOVER ARBOL SOBRE LA LINEA | B21112900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2021-11-29 | 1650 | keep | 0 | Nov | 2021 | 0.0011238 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-11-29 17:44 | 2021-11-29 18:59 | 150 | 001:15 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE DEJO ABIERTO EN VS-3 HACIA SU-23 Y SE CERRO TODAS LAS VIAS. LAS CARGAS RESTANTES PERTENECEN AL 1115-05 | S21112900045 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 75 | 2021-11-29 | 11250 | keep | 0 | Nov | 2021 | 0.0076623 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-29 17:54 | 2021-11-29 19:58 | 50 | 002:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L SE RETIRO GLOBO | B21112900084 | New_Event |  |  | Include | Wildlife | 124 | 2021-11-29 | 6200 | keep | 0 | Nov | 2021 | 0.0042228 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-29 18:02 | 2021-11-29 20:15 | 60 | 002:13 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B21112900086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 133 | 2021-11-29 | 7980 | keep | 0 | Nov | 2021 | 0.0054351 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-11-29 18:20 | 2021-11-29 19:07 | 400 | 000:47 | P | DESGANCHE | SE RETIRO BAMBUS SOBRE LINEAS Y SE CERRO MACHETES | A21112900071 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 47 | 2021-11-29 | 18800 | keep | 0 | Nov | 2021 | 0.012805 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-11-29 18:21 | 2021-11-30 15:54 | 35 | 021:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA TRONCAL EN RISER | S21112900104 | New_Event | Wire Down | Include | Include | Equipment | 1293 | 2021-11-29 | 45255 | keep | 0 | Nov | 2021 | 0.030823 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-11-29 18:26 | 2021-11-29 19:02 | 1268 | 000:36 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | M21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 36 | 2021-11-29 | 45648 | keep | 0 | Nov | 2021 | 0.031091 | 0.00086363 | Sustained | FALSE | FALSE | Not_TMED_Event | 1268
MAYAGÃœEZ | 2021-11-29 18:26 | 2021-11-29 19:02 | 2064 | 000:36 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | M21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 36 | 2021-11-29 | 74304 | keep | 0 | Nov | 2021 | 0.050608 | 0.0014058 | Sustained | FALSE | FALSE | Not_TMED_Event | 2064
MAYAGÃœEZ | 2021-11-29 18:26 | 2021-11-29 19:02 | 3036 | 000:36 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | M21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 36 | 2021-11-29 | 109296 | keep | 0 | Nov | 2021 | 0.074441 | 0.0020678 | Sustained | FALSE | FALSE | Not_TMED_Event | 3036
MAYAGÃœEZ | 2021-11-29 18:26 | 2021-11-29 19:02 | 2952 | 000:36 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | M21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 36 | 2021-11-29 | 106272 | keep | 0 | Nov | 2021 | 0.072381 | 0.0020106 | Sustained | FALSE | FALSE | Not_TMED_Event | 2952
MAYAGÃœEZ | 2021-11-29 18:27 | 2021-11-30 13:10 | 80 | 018:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA | M21112900182 | New_Event | Wire Down | Include | Include | Equipment | 1123 | 2021-11-29 | 89840 | keep | 0 | Nov | 2021 | 0.06119 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2021-11-29 18:33 | 2021-11-29 18:37 | 1222 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-11-29 | 4888 | keep | 0 | Nov | 2021 | 0.0033292 | 0.0008323 | Momentary | FALSE | FALSE | Not_TMED_Event | 1222
ARECIBO | 2021-11-29 18:33 | 2021-11-29 18:37 | 2756 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-11-29 | 11024 | keep | 0 | Nov | 2021 | 0.0075084 | 0.0018771 | Momentary | FALSE | FALSE | Not_TMED_Event | 2756
ARECIBO | 2021-11-29 18:33 | 2021-11-29 18:37 | 2833 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-11-29 | 11332 | keep | 0 | Nov | 2021 | 0.0077182 | 0.0019295 | Momentary | FALSE | FALSE | Not_TMED_Event | 2833
ARECIBO | 2021-11-29 18:33 | 2021-11-29 18:37 | 1218 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-11-29 | 4872 | keep | 0 | Nov | 2021 | 0.0033183 | 0.00082957 | Momentary | FALSE | FALSE | Not_TMED_Event | 1218
ARECIBO | 2021-11-29 18:33 | 2021-11-29 18:37 | 1345 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-11-29 | 5380 | keep | 0 | Nov | 2021 | 0.0036643 | 0.00091607 | Momentary | FALSE | FALSE | Not_TMED_Event | 1345
ARECIBO | 2021-11-29 18:33 | 2021-11-29 18:37 | 1265 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-11-29 | 5060 | keep | 0 | Nov | 2021 | 0.0034463 | 0.00086159 | Momentary | FALSE | FALSE | Not_TMED_Event | 1265
ARECIBO | 2021-11-29 18:33 | 2021-11-29 18:37 | 2071 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-11-29 | 8284 | keep | 0 | Nov | 2021 | 0.0056422 | 0.0014105 | Momentary | FALSE | FALSE | Not_TMED_Event | 2071
ARECIBO | 2021-11-29 18:33 | 2021-11-29 18:37 | 760 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-11-29 | 3040 | keep | 0 | Nov | 2021 | 0.0020705 | 0.00051763 | Momentary | FALSE | FALSE | Not_TMED_Event | 760
ARECIBO | 2021-11-29 18:33 | 2021-11-29 18:37 | 509 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-11-29 | 2036 | keep | 0 | Nov | 2021 | 0.0013867 | 0.00034668 | Momentary | FALSE | FALSE | Not_TMED_Event | 509
ARECIBO | 2021-11-29 18:33 | 2021-11-29 18:37 | 2620 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-11-29 | 10480 | keep | 0 | Nov | 2021 | 0.0071379 | 0.0017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 2620
ARECIBO | 2021-11-29 18:33 | 2021-11-29 18:37 | 1916 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A21112900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-11-29 | 7664 | keep | 0 | Nov | 2021 | 0.0052199 | 0.001305 | Momentary | FALSE | FALSE | Not_TMED_Event | 1916
MAYAGÃœEZ | 2021-11-29 18:50 | 2021-11-29 19:50 | 15 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21112900059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2021-11-29 | 900 | keep | 0 | Nov | 2021 | 0.00061299 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-11-29 18:59 | 2021-11-30 03:00 | 3 | 008:01 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE DIO MANTENIMIENTO EN SU-23 REEMPLAZANDO TERMINACIONES. DA SERVICIO A HOSPITAL PAVIA, CENTRO EUROPA Y CENTRO DE BELLAS ARTES | S21112900045 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 481 | 2021-11-29 | 1443 | keep | 0 | Nov | 2021 | 0.00098282 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-11-29 19:00 | 2021-11-29 20:15 | 10 | 001:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | A21112900062 | New_Event | Secondary Wire Down | Include | Include | Equipment | 75 | 2021-11-29 | 750 | keep | 0 | Nov | 2021 | 0.00051082 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-11-29 19:03 | 2021-11-29 19:04 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21112900242 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-29 | 3041 | keep | 0 | Nov | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
BAYAMON | 2021-11-29 19:04 | 2021-11-29 21:02 | 15 | 001:58 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B21112900095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 118 | 2021-11-29 | 1770 | keep | 0 | Nov | 2021 | 0.0012055 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-11-29 19:08 | 2021-11-29 19:09 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21112900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-29 | 3041 | keep | 0 | Nov | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2021-11-29 19:15 | 2021-11-29 19:16 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21112900247 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-29 | 3041 | keep | 0 | Nov | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2021-11-29 19:17 | 2021-11-29 19:18 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21112900248 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-29 | 3041 | keep | 0 | Nov | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2021-11-29 19:18 | 2021-11-29 19:19 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21112900250 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-29 | 3041 | keep | 0 | Nov | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
CANOVANAS | 2021-11-29 19:19 | 2021-11-29 19:20 | 2039 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECIERRE | R21112900035 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-11-29 | 2039 | keep | 0 | Nov | 2021 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
CANOVANAS | 2021-11-29 19:20 | 2021-11-29 21:01 | 13 | 001:41 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 25 EN RISER SE REEMPLAZO TERMINACION | R21112900037 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 101 | 2021-11-29 | 1313 | keep | 0 | Nov | 2021 | 0.00089428 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2021-11-29 19:24 | 2021-11-30 13:22 | 10 | 017:58 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21112900100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1078 | 2021-11-29 | 10780 | keep | 0 | Nov | 2021 | 0.0073422 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-11-29 19:43 | 2021-11-30 15:30 | 50 | 019:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M21112900261 | New_Event | Bad Weather | Include | Include | Weather | 1187 | 2021-11-29 | 59350 | keep | 0 | Nov | 2021 | 0.040423 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-11-29 19:53 | 2021-11-29 22:42 | 70 | 002:49 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B21112900101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2021-11-29 | 11830 | keep | 0 | Nov | 2021 | 0.0080574 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2021-11-29 19:58 | 2021-11-29 19:59 | 1647 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO AL HACER PRUEBA EN C/L GLOBO | B21112900000 | Additional_clients |  |  | Include | Wildlife | 1 | 2021-11-29 | 1647 | keep | 0 | Nov | 2021 | 0.0011218 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-11-29 19:59 | 2021-11-29 20:07 | 50 | 000:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L SE RETIRO GLOBO | B21112900084 | 1st_after_momentary |  |  | Include | Wildlife | 8 | 2021-11-29 | 400 | keep | 0 | Nov | 2021 | 0.00027244 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2021-11-29 20:04 | 2021-11-29 20:52 | 7 | 000:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA Y CONECTOR ABIERTO | R21112900038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 48 | 2021-11-29 | 336 | keep | 0 | Nov | 2021 | 0.00022885 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2021-11-29 21:01 | 2021-11-29 21:02 | 2039 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECIERRE | R21112900041 | Additional_clients | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-11-29 | 2039 | keep | 0 | Nov | 2021 | 0.0013888 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-11-29 21:02 | 2021-11-29 23:17 | 13 | 002:15 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 25 EN RISER SE REEMPLAZO TERMINACION | R21112900037 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 135 | 2021-11-29 | 1755 | keep | 0 | Nov | 2021 | 0.0011953 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
ARECIBO | 2021-11-29 21:21 | 2021-11-30 11:36 | 80 | 014:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARARON PUENTES PRIMARIOS | A21112900107 | New_Event | Wire Down | Include | Include | Equipment | 855 | 2021-11-29 | 68400 | keep | 0 | Nov | 2021 | 0.046587 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2021-11-29 21:42 | 2021-11-30 09:26 | 136 | 011:44 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21112900158 | New_Event | Vegetation Contact | Include | Include | Vegetation | 704 | 2021-11-29 | 95744 | keep | 0 | Nov | 2021 | 0.065211 | 9.2629e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 136
CAGUAS | 2021-11-29 21:51 | 2021-11-29 21:52 | 2608 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21112900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-29 | 2608 | keep | 0 | Nov | 2021 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
SAN JUAN | 2021-11-29 22:02 | 2021-11-30 10:06 | 80 | 012:04 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21112900131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 724 | 2021-11-29 | 57920 | keep | 0 | Nov | 2021 | 0.039449 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-11-29 22:20 | 2021-11-30 11:58 | 6 | 013:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21112900133 | New_Event | Secondary Wire Down | Include | Include | Equipment | 818 | 2021-11-29 | 4908 | keep | 0 | Nov | 2021 | 0.0033428 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2021-11-29 22:44 | 2021-11-29 22:45 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21112900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-29 | 1192 | keep | 0 | Nov | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
CANOVANAS | 2021-11-29 22:55 | 2021-11-29 22:56 | 2524 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO SE CERRO POR CONTROL | R21112900045 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-11-29 | 2524 | keep | 0 | Nov | 2021 | 0.0017191 | 0.0017191 | Momentary | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2021-11-29 22:56 | 2021-11-30 10:33 | 150 | 011:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 Y 1 X 80 EN C/L REMPLAZO PORTAFUSIBLE QUEMADO | R21112900046 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 697 | 2021-11-29 | 104550 | keep | 0 | Nov | 2021 | 0.071209 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2021-11-29 23:13 | 2021-11-30 11:09 | 8 | 011:56 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR INFORMA JOURNEYMAN NO IDENTIFICO CAUSA | M21112900318 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 716 | 2021-11-29 | 5728 | keep | 0 | Nov | 2021 | 0.0039013 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-11-30 00:50 | 2021-11-30 09:32 | 75 | 008:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CONVERTIDOR MAL TIEMPO DESCARGAS ELECTRICAS | A21113000001 | New_Event | Bad Weather | Include | Include | Weather | 522 | 2021-11-30 | 39150 | keep | 0 | Nov | 2021 | 0.026665 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2021-11-30 01:13 | 2021-11-30 19:25 | 1 | 018:12 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M21113000118 | New_Event | Bad Weather | Include | Include | Weather | 1092 | 2021-11-30 | 1092 | keep | 0 | Nov | 2021 | 0.00074376 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-11-30 01:13 | 2021-11-30 18:00 | 100 | 016:47 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M21113000116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1007 | 2021-11-30 | 100700 | keep | 0 | Nov | 2021 | 0.068586 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-11-30 01:51 | 2021-11-30 01:52 | 2450 | 000:01 | T | PARARRAYOS DEFECTUOSO | DISPARO SE CERRO POR CONTROL | C21113000002 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-11-30 | 2450 | keep | 0 | Nov | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2021-11-30 01:52 | 2021-11-30 14:45 | 1 | 012:53 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN C/L REMPLAZO PARARRAYO | C21113000036 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 773 | 2021-11-30 | 773 | keep | 0 | Nov | 2021 | 0.00052649 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-11-30 03:03 | 2021-11-30 10:03 | 145 | 007:00 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21113000001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 420 | 2021-11-30 | 60900 | keep | 0 | Nov | 2021 | 0.041479 | 9.8759e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 145
HUMACAO | 2021-11-30 04:34 | 2021-11-30 10:04 | 7 | 005:30 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | C21113000004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 330 | 2021-11-30 | 2310 | keep | 0 | Nov | 2021 | 0.0015733 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-11-30 04:51 | 2021-11-30 08:44 | 200 | 003:53 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA INFORMA JOURNEYMAN NO IDENTIFICO CAUSA | M21113000005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 233 | 2021-11-30 | 46600 | keep | 0 | Nov | 2021 | 0.031739 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-11-30 05:58 | 2021-11-30 11:45 | 50 | 005:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE SECCIONALIZO LINEA PRIMARIA PARTIDA | M21113000008 | New_Event | Wire Down | Include | Include | Equipment | 347 | 2021-11-30 | 17350 | keep | 0 | Nov | 2021 | 0.011817 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-11-30 06:08 | 2021-11-30 09:39 | 200 | 003:31 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA INFORMA JOURNEYMAN REQUIERE DESGANCHE | M21113000008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2021-11-30 | 42200 | keep | 0 | Nov | 2021 | 0.028742 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-11-30 06:34 | 2021-11-30 13:15 | 10 | 006:41 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR T 4 CON GOI SJ-211130-01 | S21111300007 | New_Event | Service Transformer Failure | Include | Include | Equipment | 401 | 2021-11-30 | 4010 | keep | 0 | Nov | 2021 | 0.0027312 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-30 06:47 | 2021-11-30 06:48 | 2234 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B21113000003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-30 | 2234 | keep | 0 | Nov | 2021 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2021-11-30 06:52 | 2021-11-30 13:41 | 1 | 006:49 | P | OTRAS CAUSAS | A LAS 1341 DISPARO INTERRUPTOR SE CERRO POR SCADA PERSONAL HIZO PRUEBA EN C/L HACIA ME SALVE Y OPERO SE DEJO FUERA PROA | B21113000004 | New_Event | Other Causes | Include | Include | Other | 409 | 2021-11-30 | 409 | keep | 0 | Nov | 2021 | 0.00027857 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-11-30 07:04 | 2021-11-30 11:04 | 10 | 004:00 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER NO SE ENCONTRO CAUSA | P21113000004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 240 | 2021-11-30 | 2400 | keep | 0 | Nov | 2021 | 0.0016346 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-11-30 07:04 | 2021-11-30 14:48 | 15 | 007:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE CAJA EN TRANSFORMADOR PARA REPARAR SECUNDARIA | P21112900146 | New_Event | Secondary Wire Down | Include | Include | Equipment | 464 | 2021-11-30 | 6960 | keep | 0 | Nov | 2021 | 0.0047404 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-11-30 07:15 | 2021-11-30 09:58 | 40 | 002:43 | P | DESGANCHE | 1 X 40 EN C/L | C21113000005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2021-11-30 | 6520 | keep | 0 | Nov | 2021 | 0.0044407 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-11-30 07:41 | 2021-11-30 07:42 | 4641 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M21113000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-30 | 4641 | keep | 0 | Nov | 2021 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2021-11-30 07:42 | 2021-11-30 14:58 | 80 | 007:16 | P | DESGANCHE | 2 X 50 EN RISER SE RETIRO ENREDADERA | M21113000052 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 436 | 2021-11-30 | 34880 | keep | 0 | Nov | 2021 | 0.023757 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2021-11-30 08:00 | 2021-11-30 08:01 | 551 | 000:01 | T | DESGANCHE | RECIERRE | C21113000010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-11-30 | 551 | keep | 0 | Nov | 2021 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
BARRANQUITAS | 2021-11-30 08:00 | 2021-11-30 11:46 | 25 | 003:46 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | C21113000007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 226 | 2021-11-30 | 5650 | keep | 0 | Nov | 2021 | 0.0038482 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2021-11-30 08:01 | 2021-11-30 11:56 | 40 | 003:55 | P | DESGANCHE | 1 X 100 EN C/L | C21113000031 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 235 | 2021-11-30 | 9400 | keep | 0 | Nov | 2021 | 0.0064023 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-11-30 08:19 | 2021-11-30 15:56 | 6 | 007:37 | P | SECUNDARIA/DESGANCHE | ABRIO XMR PARA DESGANCHAR Y REPARAR SECUNDARIA | C21113000011 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 457 | 2021-11-30 | 2742 | keep | 0 | Nov | 2021 | 0.0018676 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-11-30 08:34 | 2021-11-30 09:40 | 1 | 001:06 | P | SECUNDARIA/DESGANCHE | 1 X 50 EN MONTURA TRIFASICA CRUCE DE LINEAS SECUNDARIAS POR BEJUCO | P21113000010 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 66 | 2021-11-30 | 66 | keep | 0 | Nov | 2021 | 4.4952e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-11-30 08:36 | 2021-11-30 08:37 | 3025 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE CARGA POR EL 2906-02 | C21124000000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-30 | 3025 | keep | 0 | Nov | 2021 | 0.0020603 | 0.0020603 | Momentary | FALSE | FALSE | Not_TMED_Event | 3025
HUMACAO | 2021-11-30 08:39 | 2021-11-30 08:40 | 1593 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE CARGA POR EL 2906-02 | C21124000000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-11-30 | 1593 | keep | 0 | Nov | 2021 | 0.001085 | 0.001085 | Momentary | FALSE | FALSE | Not_TMED_Event | 1593
HUMACAO | 2021-11-30 08:40 | 2021-11-30 15:00 | 5 | 006:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 10 EN XMR LEVANTO NEUTRAL PRIMARIO | C21113000024 | New_Event | Wire Down | Include | Include | Equipment | 380 | 2021-11-30 | 1900 | keep | 0 | Nov | 2021 | 0.0012941 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-11-30 08:52 | 2021-11-30 12:30 | 12 | 003:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21113000015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 218 | 2021-11-30 | 2616 | keep | 0 | Nov | 2021 | 0.0017817 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2021-11-30 09:04 | 2021-11-30 13:16 | 20 | 004:12 | P | DESGANCHE | 1 X 40 EN C/L | R21113000009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 252 | 2021-11-30 | 5040 | keep | 0 | Nov | 2021 | 0.0034327 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2021-11-30 09:16 | 2021-11-30 16:30 | 8 | 007:14 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE RETIRO ENREDADERA | M21113000045 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 434 | 2021-11-30 | 3472 | keep | 0 | Nov | 2021 | 0.0023648 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-11-30 09:17 | 2021-11-30 11:37 | 20 | 002:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA CRUZADA | A21113000011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 140 | 2021-11-30 | 2800 | keep | 0 | Nov | 2021 | 0.0019071 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-11-30 09:26 | 2021-11-30 16:14 | 100 | 006:48 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P21113000022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 408 | 2021-11-30 | 40800 | keep | 0 | Nov | 2021 | 0.027789 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-11-30 09:38 | 2021-11-30 19:08 | 10 | 009:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO CONECTOR BAJANTE DEL XMR | S21113000022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 570 | 2021-11-30 | 5700 | keep | 0 | Nov | 2021 | 0.0038822 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-30 09:57 | 2021-11-30 09:58 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21113000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-30 | 308 | keep | 0 | Nov | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
HUMACAO | 2021-11-30 09:59 | 2021-11-30 12:30 | 1 | 002:31 | P | NO SE REPORTO CAUSA | 2 X 65 EN C/L NO CAUSA | C21113000027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 151 | 2021-11-30 | 151 | keep | 0 | Nov | 2021 | 0.00010285 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-11-30 09:59 | 2021-11-30 12:37 | 10 | 002:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 80 EN CORTE DE LINEA SE REMPLAZARON TRES CAJAS PRIMARIA EN RISER | P21113000026 | New_Event | Cutout Failure | Include | Include | Equipment | 158 | 2021-11-30 | 1580 | keep | 0 | Nov | 2021 | 0.0010761 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-11-30 10:00 | 2021-11-30 14:06 | 20 | 004:06 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S21111300023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 246 | 2021-11-30 | 4920 | keep | 0 | Nov | 2021 | 0.003351 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-11-30 10:00 | 2021-11-30 19:05 | 9 | 009:05 | P | ESTRUCTURA AVERIADA | SE LE RETIRA CARGA A TRANSFORMADOR PARA ABRIR PUENTES, ELIMINAR POSTE PRIMARIO PARTIDO Y RELOCALIZAR LINEA PRIMARIA | P21113000007 | New_Event | Defective Pole | Include | Include | Equipment | 545 | 2021-11-30 | 4905 | keep | 0 | Nov | 2021 | 0.0033408 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
UTUADO | 2021-11-30 10:05 | 2021-11-30 14:30 | 10 | 004:25 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR POSTE SECUNDARIO | A21113000014 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 265 | 2021-11-30 | 2650 | keep | 0 | Nov | 2021 | 0.0018049 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-30 10:16 | 2021-11-30 14:45 | 35 | 004:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y SE RETIRO RAMAS SOBRE LAS LINEAS | A21113000016 | New_Event | Wire Down | Include | Include | Equipment | 269 | 2021-11-30 | 9415 | keep | 0 | Nov | 2021 | 0.0064125 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
UTUADO | 2021-11-30 10:18 | 2021-11-30 12:56 | 25 | 002:38 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21113000017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2021-11-30 | 3950 | keep | 0 | Nov | 2021 | 0.0026903 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2021-11-30 10:29 | 2021-11-30 13:56 | 6 | 003:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 XMR CRUCE POR AVE | C21113000034 | New_Event |  |  | Include | Wildlife | 207 | 2021-11-30 | 1242 | keep | 0 | Nov | 2021 | 0.00084592 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-11-30 10:35 | 2021-11-30 11:47 | 10 | 001:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS Y SE REALIZO DESGANCHE | B21112900111 | New_Event | Secondary Wire Down | Include | Include | Equipment | 72 | 2021-11-30 | 720 | keep | 0 | Nov | 2021 | 0.00049039 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-11-30 10:44 | 2021-11-30 16:21 | 25 | 005:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO BARRAS EN PEDESTAL Y SE CERRO CORTE DE LINEA POR SEGURIDAD PM EN MALAS CONDICIONES | B21113000016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 337 | 2021-11-30 | 8425 | keep | 0 | Nov | 2021 | 0.0057382 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-11-30 10:48 | 2021-11-30 10:49 | 1588 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1711-01 LLEVANDO CARGA 1711-03 | B21113000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-30 | 1588 | keep | 0 | Nov | 2021 | 0.0010816 | 0.0010816 | Momentary | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2021-11-30 10:48 | 2021-11-30 10:49 | 13 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1711-01 LLEVANDO CARGA 1711-03 | B21113000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-30 | 13 | keep | 0 | Nov | 2021 | 8.8542e-06 | 8.8542e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 13
FAJARDO | 2021-11-30 10:49 | 2021-11-30 12:01 | 50 | 001:12 | P | DESGANCHE | 1 X 50 EN C/L | R21113000015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2021-11-30 | 3600 | keep | 0 | Nov | 2021 | 0.0024519 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2021-11-30 10:50 | 2021-11-30 11:45 | 5 | 000:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA PARTIDA | A21113000003 | New_Event | Secondary Wire Down | Include | Include | Equipment | 55 | 2021-11-30 | 275 | keep | 0 | Nov | 2021 | 0.0001873 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-11-30 10:59 | 2021-12-01 12:00 | 12 | 025:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA CERRAR PUENTE LINEA A TRANSFORMADOR TRAS PATIO | S21113000028 | New_Event | Wire Down | Include | Include | Equipment | 1501 | 2021-11-30 | 18012 | keep | 0 | Nov | 2021 | 0.012268 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-11-30 11:03 | 2021-11-30 11:04 | 1180 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21113000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-30 | 1180 | keep | 0 | Nov | 2021 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
SAN JUAN | 2021-11-30 11:10 | 2021-11-30 14:35 | 1 | 003:25 | P | NO SE REPORTO CAUSA | 2 X 25 EN SU-3 | S21113000030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 205 | 2021-11-30 | 205 | keep | 0 | Nov | 2021 | 0.00013962 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-11-30 11:16 | 2021-11-30 11:43 | 1394 | 000:27 | T | DESGANCHE | DISPARO DE INTERRUPTOR A CAUSA DE PERSONAL DESGANCHANDO SE VERIFICO PERSONAL FUERA | R21113000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 27 | 2021-11-30 | 37638 | keep | 0 | Nov | 2021 | 0.025635 | 0.00094945 | Sustained | FALSE | FALSE | Not_TMED_Event | 1394
CAGUAS | 2021-11-30 11:19 | 2021-11-30 16:12 | 40 | 004:53 | P | DESGANCHE | 1 X 40 EN C/L | C21113000039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 293 | 2021-11-30 | 11720 | keep | 0 | Nov | 2021 | 0.0079824 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-11-30 11:25 | 2021-11-30 15:35 | 40 | 004:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CAMION CRUZO FASES | M21113000072 | New_Event |  |  | Include | Wildlife | 250 | 2021-11-30 | 10000 | keep | 0 | Nov | 2021 | 0.006811 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2021-11-30 11:36 | 2021-11-30 15:08 | 60 | 003:32 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M21113000074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2021-11-30 | 12720 | keep | 0 | Nov | 2021 | 0.0086635 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2021-11-30 11:55 | 2021-11-30 12:21 | 40 | 000:26 | P | DESGANCHE | 1 X 40 EN RISER | R21113000028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 26 | 2021-11-30 | 1040 | keep | 0 | Nov | 2021 | 0.00070834 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-11-30 11:59 | 2021-11-30 12:33 | 5 | 000:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR BAJANTE SECUNDARIO Y TOMA | C21113000027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 34 | 2021-11-30 | 170 | keep | 0 | Nov | 2021 | 0.00011579 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-11-30 12:52 | 2021-11-30 20:47 | 56 | 007:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 40 EN C/L SE LEVANTO 2 TRAMOS DE LINEA | B21113000027 | New_Event | Wire Down | Include | Include | Equipment | 475 | 2021-11-30 | 26600 | keep | 0 | Nov | 2021 | 0.018117 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
AGUADILLA | 2021-11-30 12:52 | 2021-11-30 17:50 | 60 | 004:58 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M21113000088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 298 | 2021-11-30 | 17880 | keep | 0 | Nov | 2021 | 0.012178 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-11-30 13:00 | 2021-11-30 19:31 | 50 | 006:31 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B21113000046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 391 | 2021-11-30 | 19550 | keep | 0 | Nov | 2021 | 0.013315 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-11-30 13:03 | 2021-11-30 16:21 | 35 | 003:18 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21113000041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 198 | 2021-11-30 | 6930 | keep | 0 | Nov | 2021 | 0.00472 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2021-11-30 13:10 | 2021-11-30 14:10 | 4 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | M21113000032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2021-11-30 | 240 | keep | 0 | Nov | 2021 | 0.00016346 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-11-30 13:11 | 2021-11-30 20:04 | 36 | 006:53 | T | CABLE SOTERRADO AVERIADO | 1 X 30 Y 1 X 20 EN PROVISIONALES SE QUEDO FUERA T-5 Y T-4 POR AVERIA DE T-8 @ T-5 POSTERIORMENTE SE PREPARO PROVISIONAL AEREO @ T-5 CON EL EVENTO B21113000072 | B21113000028 | New_Event | UG Cable Fault | Include | Include | Equipment | 413 | 2021-11-30 | 14868 | keep | 0 | Nov | 2021 | 0.010127 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CAGUAS | 2021-11-30 13:12 | 2021-11-30 17:44 | 18 | 004:32 | P | CABLE SOTERRADO AVERIADO | TIRO SECUNDARIA NUEVA DEL T - 18 A PEDESTAL | C21113000047 | New_Event | UG Cable Fault | Include | Include | Equipment | 272 | 2021-11-30 | 4896 | keep | 0 | Nov | 2021 | 0.0033346 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2021-11-30 13:31 | 2021-11-30 13:51 | 30 | 000:20 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21113000030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2021-11-30 | 600 | keep | 0 | Nov | 2021 | 0.00040866 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-11-30 13:40 | 2021-11-30 16:21 | 12 | 002:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR TRANSFORMADOR PARA REPARAR SECUNDARIA | S21002900084 | New_Event | Secondary Wire Down | Include | Include | Equipment | 161 | 2021-11-30 | 1932 | keep | 0 | Nov | 2021 | 0.0013159 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-11-30 13:40 | 2021-11-30 13:41 | 1320 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21113000048 | New_Event |  |  | Include | Wildlife | 1 | 2021-11-30 | 1320 | keep | 0 | Nov | 2021 | 0.00089905 | 0.00089905 | Momentary | FALSE | FALSE | Not_TMED_Event | 1320
BAYAMON | 2021-11-30 13:41 | 2021-11-30 13:48 | 966 | 000:07 | T | OTRAS CAUSAS | DISPARO DE INTERRUPTOR SE CERRO POR SCADA PERSONAL HIZO PRUEBA EN C/L HACIA ME SALVE Y OPERO SE DEJO FUERA PROA | B21113000031 | New_Event | Other Causes | Include | Include | Other | 7 | 2021-11-30 | 6762 | keep | 0 | Nov | 2021 | 0.0046056 | 0.00065794 | Sustained | FALSE | FALSE | Not_TMED_Event | 966
FAJARDO | 2021-11-30 14:18 | 2021-11-30 15:34 | 1 | 001:16 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN C/L REEMPLAZO PARARRAYO | R21113000036 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 76 | 2021-11-30 | 76 | keep | 0 | Nov | 2021 | 5.1763e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-11-30 14:29 | 2021-11-30 22:12 | 35 | 007:43 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | S21113000048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 463 | 2021-11-30 | 16205 | keep | 0 | Nov | 2021 | 0.011037 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2021-11-30 14:29 | 2021-11-30 14:31 | 1565 | 000:02 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO | C21113000052 | New_Event |  |  | Include | Wildlife | 2 | 2021-11-30 | 3130 | keep | 0 | Nov | 2021 | 0.0021318 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
CAGUAS | 2021-11-30 14:31 | 2021-11-30 19:21 | 5 | 004:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR REPARO SECUNDARIA AVERIADA POR CAMION | C21113000059 | 1st_after_momentary |  |  | Include | Wildlife | 290 | 2021-11-30 | 1450 | keep | 0 | Nov | 2021 | 0.00098759 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-11-30 15:01 | 2021-12-01 10:33 | 10 | 019:32 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 75 KVA X 75 KVA | M21113000105 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1172 | 2021-11-30 | 11720 | keep | 0 | Nov | 2021 | 0.0079824 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-11-30 15:25 | 2021-11-30 15:50 | 17 | 000:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A21112900108 | New_Event | Secondary Wire Down | Include | Include | Equipment | 25 | 2021-11-30 | 425 | keep | 0 | Nov | 2021 | 0.00028947 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
CAGUAS | 2021-11-30 15:43 | 2021-12-01 14:13 | 20 | 022:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | LINEA ROTA POR EXCAVADORA SE CONSTRUYO AEREO PROVICIONAL | C21113000061 | New_Event |  |  | Include | Wildlife | 1350 | 2021-11-30 | 27000 | keep | 0 | Nov | 2021 | 0.01839 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-11-30 15:47 | 2021-11-30 18:26 | 60 | 002:39 | P | DESGANCHE | 1 X 80 EN C/L SE REALIZO DESGANCHE | B21113000042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2021-11-30 | 9540 | keep | 0 | Nov | 2021 | 0.0064977 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-11-30 15:56 | 2021-11-30 15:57 | 1509 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M21113000113 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-11-30 | 1509 | keep | 0 | Nov | 2021 | 0.0010278 | 0.0010278 | Momentary | FALSE | FALSE | Not_TMED_Event | 1509
MAYAGÃœEZ | 2021-11-30 15:57 | 2021-11-30 18:18 | 40 | 002:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M21113000121 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 141 | 2021-11-30 | 5640 | keep | 0 | Nov | 2021 | 0.0038414 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-11-30 16:00 | 2021-11-30 16:01 | 837 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-07 QUE A SU VEZ LLEVA LA CARGA DEL 1401-06 | SS2111300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-30 | 837 | keep | 0 | Nov | 2021 | 0.00057008 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2021-11-30 16:00 | 2021-11-30 16:01 | 908 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-07 QUE A SU VEZ LLEVA LA CARGA DEL 1401-06 | SS2111300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-30 | 908 | keep | 0 | Nov | 2021 | 0.00061843 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
GUAYAMA | 2021-11-30 16:34 | 2021-11-30 18:33 | 80 | 001:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE CRUZO FASE | P21113000055 | New_Event |  |  | Include | Wildlife | 119 | 2021-11-30 | 9520 | keep | 0 | Nov | 2021 | 0.006484 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2021-11-30 16:34 | 2021-11-30 19:43 | 40 | 003:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE NO FUNDIO | C21113000065 | New_Event | Wire Down | Include | Include | Equipment | 189 | 2021-11-30 | 7560 | keep | 0 | Nov | 2021 | 0.0051491 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2021-11-30 16:37 | 2021-11-30 16:38 | 4132 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21113000056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-30 | 4132 | keep | 0 | Nov | 2021 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
SAN JUAN | 2021-11-30 16:40 | 2021-11-30 18:37 | 40 | 001:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA Y SE RETIRO IGUANA | S21113000060 | New_Event |  |  | Include | Wildlife | 117 | 2021-11-30 | 4680 | keep | 0 | Nov | 2021 | 0.0031875 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-11-30 16:49 | 2021-12-01 14:05 | 30 | 021:16 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S21113000061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1276 | 2021-11-30 | 38280 | keep | 0 | Nov | 2021 | 0.026072 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2021-11-30 17:15 | 2021-11-30 21:08 | 40 | 003:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21113000126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2021-11-30 | 9320 | keep | 0 | Nov | 2021 | 0.0063478 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-11-30 17:18 | 2021-11-30 17:43 | 315 | 000:25 | T | DESGANCHE | SE ABRIO INTERRUPTOR POR ARBOL EN FUEGO EN LA PRIMARIA PARA PODER LOS BOMBEROS APAGARLO Y SE CERRO LUEGO POR SCADA | S21113000066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 25 | 2021-11-30 | 7875 | keep | 0 | Nov | 2021 | 0.0053636 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
CANOVANAS | 2021-11-30 17:19 | 2021-12-01 12:47 | 20 | 019:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR REEMPLAZO BAJANTE SECUNDARIO Y CAJA DE XMR AVERIADA | R21113000042 | New_Event | Cutout Failure | Include | Include | Equipment | 1168 | 2021-11-30 | 23360 | keep | 0 | Nov | 2021 | 0.01591 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2021-11-30 17:44 | 2021-11-30 19:56 | 50 | 002:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO BAJANTE PRIMARIO DE CAJA A XMR | R21113000043 | New_Event | Wire Down | Include | Include | Equipment | 132 | 2021-11-30 | 6600 | keep | 0 | Nov | 2021 | 0.0044952 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-11-30 18:15 | 2021-11-30 20:14 | 6 | 001:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | R21113000044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 119 | 2021-11-30 | 714 | keep | 0 | Nov | 2021 | 0.0004863 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-11-30 18:32 | 2021-11-30 21:55 | 100 | 003:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M21113000147 | New_Event | Bad Weather | Include | Include | Weather | 203 | 2021-11-30 | 20300 | keep | 0 | Nov | 2021 | 0.013826 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-11-30 20:04 | 2021-12-01 16:37 | 20 | 020:33 | P | CABLE SOTERRADO AVERIADO | SE PREPARO PROVISIONAL AEREO @ T-5 | B21113000072 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1233 | 2021-11-30 | 24660 | keep | 0 | Nov | 2021 | 0.016796 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-11-30 22:05 | 2021-11-30 22:06 | 2450 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C21113000095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-30 | 2450 | keep | 0 | Nov | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
ARECIBO | 2021-11-30 23:00 | 2021-12-01 10:57 | 15 | 011:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | A21113000070 | New_Event | Bad Weather | Include | Include | Weather | 717 | 2021-11-30 | 10755 | keep | 0 | Nov | 2021 | 0.0073252 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-11-30 23:25 | 2021-11-30 23:26 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21113000066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-30 | 3046 | keep | 0 | Nov | 2021 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
MAYAGÃœEZ | 2021-11-30 23:28 | 2021-11-30 23:29 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21113000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-30 | 1097 | keep | 0 | Nov | 2021 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
MAYAGÃœEZ | 2021-11-30 23:39 | 2021-12-01 13:15 | 120 | 013:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE SE REMPLAZO CAJA PRIMARIA AVERIADA | M21113000179 | New_Event | Cutout Failure | Include | Include | Equipment | 816 | 2021-11-30 | 97920 | keep | 0 | Nov | 2021 | 0.066693 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
VEGA BAJA | 2021-11-30 23:47 | 2021-11-30 23:48 | 3000 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21113000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-30 | 3000 | keep | 0 | Nov | 2021 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
CAGUAS | 2021-11-30 23:48 | 2021-11-30 23:49 | 1854 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21113000098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-11-30 | 1854 | keep | 0 | Nov | 2021 | 0.0012628 | 0.0012628 | Momentary | FALSE | FALSE | Not_TMED_Event | 1854
MAYAGÃœEZ | 2021-12-01 02:36 | 2021-12-01 16:29 | 30 | 013:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21120100004 | New_Event | Bad Weather | Include | Include | Weather | 833 | 2021-12-01 | 24990 | keep | 0 | Dec | 2021 | 0.017021 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-01 02:55 | 2021-12-01 02:57 | 1935 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUARAGUAO AFECTANDO PORTATIL #7 | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2021-12-01 | 3870 | keep | 0 | Dec | 2021 | 0.0026358 | 0.0013179 | Momentary | FALSE | FALSE | Not_TMED_Event | 1935
BAYAMON | 2021-12-01 02:55 | 2021-12-01 02:57 | 3 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUARAGUAO AFECTANDO PORTATIL #7 | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2021-12-01 | 6 | keep | 0 | Dec | 2021 | 4.0866e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-12-01 02:55 | 2021-12-01 02:57 | 61 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUARAGUAO AFECTANDO PORTATIL #7 | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2021-12-01 | 122 | keep | 0 | Dec | 2021 | 8.3094e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2021-12-01 02:55 | 2021-12-01 02:57 | 1501 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUARAGUAO AFECTANDO PORTATIL #7 | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2021-12-01 | 3002 | keep | 0 | Dec | 2021 | 0.0020446 | 0.0010223 | Momentary | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2021-12-01 02:55 | 2021-12-01 02:57 | 546 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUARAGUAO AFECTANDO PORTATIL #7 | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2021-12-01 | 1092 | keep | 0 | Dec | 2021 | 0.00074376 | 0.00037188 | Momentary | FALSE | FALSE | Not_TMED_Event | 546
HUMACAO | 2021-12-01 03:16 | 2021-12-01 10:00 | 7 | 006:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR CRUCE POR REPTIL | C21120100001 | New_Event |  |  | Include | Wildlife | 404 | 2021-12-01 | 2828 | keep | 0 | Dec | 2021 | 0.0019261 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2021-12-01 04:32 | 2021-12-01 12:02 | 8 | 007:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C21120100002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 450 | 2021-12-01 | 3600 | keep | 0 | Dec | 2021 | 0.0024519 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-12-01 04:45 | 2021-12-01 04:46 | 1533 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1709-03 LLEVANDO LA CARGA DEL 1709-05 Y 50% DEL 1909-07 | S21120100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-01 | 1533 | keep | 0 | Dec | 2021 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
BAYAMON | 2021-12-01 04:45 | 2021-12-01 04:46 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1709-03 LLEVANDO LA CARGA DEL 1709-05 Y 50% DEL 1909-07 | S21120100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-01 | 2364 | keep | 0 | Dec | 2021 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
BAYAMON | 2021-12-01 04:45 | 2021-12-01 04:46 | 569 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1709-03 LLEVANDO LA CARGA DEL 1709-05 Y 50% DEL 1909-07 | S21120100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-01 | 569 | keep | 0 | Dec | 2021 | 0.00038754 | 0.00038754 | Momentary | FALSE | FALSE | Not_TMED_Event | 569
BAYAMON | 2021-12-01 04:46 | 2021-12-01 10:06 | 1 | 005:20 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER Y 2 X 40 EN BOVEDA | S21120100038 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 320 | 2021-12-01 | 320 | keep | 0 | Dec | 2021 | 0.00021795 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-12-01 04:53 | 2021-12-01 04:54 | 1827 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M21120100000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-12-01 | 1827 | keep | 0 | Dec | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2021-12-01 04:54 | 2021-12-01 16:08 | 10 | 011:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21120100081 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 674 | 2021-12-01 | 6740 | keep | 0 | Dec | 2021 | 0.0045906 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-01 05:01 | 2021-12-01 05:02 | 922 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1401-08 LLEVANDO LA CARGA DEL 1346-05 | S21120100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-01 | 922 | keep | 0 | Dec | 2021 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-12-01 05:01 | 2021-12-01 05:02 | 135 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1401-08 LLEVANDO LA CARGA DEL 1346-05 | S21120100008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-01 | 135 | keep | 0 | Dec | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2021-12-01 05:39 | 2021-12-01 12:41 | 50 | 007:02 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S21112010017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 422 | 2021-12-01 | 21100 | keep | 0 | Dec | 2021 | 0.014371 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2021-12-01 05:48 | 2021-12-01 11:24 | 6 | 005:36 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21120100002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 336 | 2021-12-01 | 2016 | keep | 0 | Dec | 2021 | 0.0013731 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-12-01 05:52 | 2021-12-01 11:59 | 100 | 006:07 | P | DESGANCHE | 3 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21120100008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 367 | 2021-12-01 | 36700 | keep | 0 | Dec | 2021 | 0.024996 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-12-01 06:02 | 2021-12-01 11:01 | 6 | 004:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR CRUCE POR AVE | C21120100003 | New_Event |  |  | Include | Wildlife | 299 | 2021-12-01 | 1794 | keep | 0 | Dec | 2021 | 0.0012219 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-12-01 06:22 | 2021-12-01 07:56 | 70 | 001:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA | A21120100004 | New_Event | Wire Down | Include | Include | Equipment | 94 | 2021-12-01 | 6580 | keep | 0 | Dec | 2021 | 0.0044816 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2021-12-01 06:32 | 2021-12-01 13:40 | 75 | 007:08 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZARON MACHETES SOLIDOS QUEMADOS | A21120100005 | New_Event | Switch Failure | Include | Include | Equipment | 428 | 2021-12-01 | 32100 | keep | 0 | Dec | 2021 | 0.021863 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2021-12-01 06:49 | 2021-12-01 11:39 | 25 | 004:50 | P | DESGANCHE | 1 X 40 EN C/L | C21120100004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 290 | 2021-12-01 | 7250 | keep | 0 | Dec | 2021 | 0.0049379 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-12-01 07:00 | 2021-12-01 10:00 | 750 | 003:00 | P | DESGANCHE | DISPARO SECUNDARIO PORTATIL#8 SE RETIRO ARBOL SOBRE LINEA | S21120100003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2021-12-01 | 135000 | keep | 0 | Dec | 2021 | 0.091948 | 0.00051082 | Sustained | FALSE | FALSE | Not_TMED_Event | 750
SAN JUAN | 2021-12-01 07:00 | 2021-12-01 10:00 | 450 | 003:00 | P | DESGANCHE | DISPARO SECUNDARIO PORTATIL#8 SE RETIRO ARBOL SOBRE LINEA SE REALIZO GOI PARA TRABAJOS | S21120100003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2021-12-01 | 81000 | keep | 0 | Dec | 2021 | 0.055169 | 0.00030649 | Sustained | FALSE | FALSE | Not_TMED_Event | 450
SAN JUAN | 2021-12-01 07:00 | 2021-12-01 10:00 | 1290 | 003:00 | S | DESGANCHE | DISPARO SECUNDARIO PORTATIL#8 SE RETIRO ARBOL SOBRE LINEA SE REALIZO GOI PARA TRABAJOS | S21120100003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2021-12-01 | 232200 | keep | 0 | Dec | 2021 | 0.15815 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
UTUADO | 2021-12-01 07:04 | 2021-12-01 15:53 | 10 | 008:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | A21120100006 | New_Event | Cutout Failure | Include | Include | Equipment | 529 | 2021-12-01 | 5290 | keep | 0 | Dec | 2021 | 0.003603 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-01 07:23 | 2021-12-01 15:12 | 15 | 007:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN C/L MAL TIEMPO | C21120100005 | New_Event | Bad Weather | Include | Include | Weather | 469 | 2021-12-01 | 7035 | keep | 0 | Dec | 2021 | 0.0047915 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-12-01 07:34 | 2021-12-01 09:41 | 2 | 002:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA POR AVE CRUZA FASES | P21120100001 | New_Event |  |  | Include | Wildlife | 127 | 2021-12-01 | 254 | keep | 0 | Dec | 2021 | 0.000173 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2021-12-01 07:39 | 2021-12-01 10:59 | 150 | 003:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN C/L DESPEGO BAJANTE DE GRAPA Y LO FIJO | R21120100001 | New_Event | Wire Down | Include | Include | Equipment | 200 | 2021-12-01 | 30000 | keep | 0 | Dec | 2021 | 0.020433 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2021-12-01 07:40 | 2021-12-01 12:45 | 80 | 005:05 | P | NO SE REPORTO CAUSA | 1 SMU 20 DE 80 AMP EN SU 7C NO CAUSA | R21120100002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 305 | 2021-12-01 | 24400 | keep | 0 | Dec | 2021 | 0.016619 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-12-01 07:40 | 2021-12-01 15:50 | 1 | 008:10 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSCLOSURE 1 X 15 EN RISER | B21120100006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 490 | 2021-12-01 | 490 | keep | 0 | Dec | 2021 | 0.00033374 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-12-01 07:43 | 2021-12-01 07:44 | 2791 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21120100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-01 | 2791 | keep | 0 | Dec | 2021 | 0.0019009 | 0.0019009 | Momentary | FALSE | FALSE | Not_TMED_Event | 2791
ARECIBO | 2021-12-01 07:43 | 2021-12-01 07:44 | 1464 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21120100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-01 | 1464 | keep | 0 | Dec | 2021 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
ARECIBO | 2021-12-01 07:43 | 2021-12-01 07:44 | 759 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21120100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-01 | 759 | keep | 0 | Dec | 2021 | 0.00051695 | 0.00051695 | Momentary | FALSE | FALSE | Not_TMED_Event | 759
ARECIBO | 2021-12-01 07:43 | 2021-12-01 07:44 | 1500 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21120100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-01 | 1500 | keep | 0 | Dec | 2021 | 0.0010216 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
ARECIBO | 2021-12-01 07:43 | 2021-12-01 07:44 | 2132 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21120100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-01 | 2132 | keep | 0 | Dec | 2021 | 0.0014521 | 0.0014521 | Momentary | FALSE | FALSE | Not_TMED_Event | 2132
ARECIBO | 2021-12-01 07:43 | 2021-12-01 07:44 | 2366 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21120100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-01 | 2366 | keep | 0 | Dec | 2021 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
ARECIBO | 2021-12-01 07:43 | 2021-12-01 07:44 | 1976 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21120100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-01 | 1976 | keep | 0 | Dec | 2021 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
ARECIBO | 2021-12-01 07:43 | 2021-12-01 07:44 | 3688 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21120100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-01 | 3688 | keep | 0 | Dec | 2021 | 0.0025119 | 0.0025119 | Momentary | FALSE | FALSE | Not_TMED_Event | 3688
BAYAMON | 2021-12-01 07:43 | 2021-12-01 07:44 | 3070 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21120100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-01 | 3070 | keep | 0 | Dec | 2021 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2021-12-01 07:43 | 2021-12-01 07:44 | 2735 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21120100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-01 | 2735 | keep | 0 | Dec | 2021 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2021-12-01 07:43 | 2021-12-01 07:44 | 1070 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21120100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-01 | 1070 | keep | 0 | Dec | 2021 | 0.00072877 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2021-12-01 07:43 | 2021-12-01 07:44 | 1647 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21120100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-01 | 1647 | keep | 0 | Dec | 2021 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2021-12-01 07:43 | 2021-12-01 07:44 | 3295 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21120100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-01 | 3295 | keep | 0 | Dec | 2021 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2021-12-01 07:43 | 2021-12-01 07:44 | 1180 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21120100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-01 | 1180 | keep | 0 | Dec | 2021 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2021-12-01 07:43 | 2021-12-01 07:44 | 320 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21120100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-01 | 320 | keep | 0 | Dec | 2021 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2021-12-01 07:43 | 2021-12-01 07:44 | 2234 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B21120100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-01 | 2234 | keep | 0 | Dec | 2021 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
SAN JUAN | 2021-12-01 07:45 | 2021-12-01 11:31 | 1 | 003:46 | P | DESGANCHE | 1 X 50 Y 1 X 25 EN C/L | R21120100003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2021-12-01 | 226 | keep | 0 | Dec | 2021 | 0.00015393 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-12-01 07:56 | 2021-12-01 08:06 | 437 | 000:10 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR AVERIA DE LINEA PARTIDA | A21120100011 | Additional_clients | Wire Down | Include | Include | Equipment | 10 | 2021-12-01 | 4370 | keep | 0 | Dec | 2021 | 0.0029764 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-12-01 08:06 | 2021-12-01 10:38 | 70 | 002:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA | A21120100004 | Partial_restoration | Wire Down | Include | Include | Equipment | 152 | 2021-12-01 | 10640 | keep | 0 | Dec | 2021 | 0.0072469 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-01 08:22 | 2021-12-01 08:24 | 922 | 000:02 | T | NO SE REPORTO CAUSA | RECERRO 1 VEZ SU CARGA POR 1401-8 SE PROBO QUEDO EN SERVICIO | S21120100045 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-01 | 1844 | keep | 0 | Dec | 2021 | 0.0012559 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-12-01 08:22 | 2021-12-01 08:24 | 135 | 000:02 | T | NO SE REPORTO CAUSA | RECERRO 1 VEZ QUEDO FUERA LLEVA 1346-5 SE PROBO POR CONTROL QUEDO EN SERVICIO | S21120100045 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-01 | 270 | keep | 0 | Dec | 2021 | 0.0001839 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2021-12-01 08:25 | 2021-12-01 09:18 | 726 | 000:53 | T | DESGANCHE | DISPARO SE ABRIO N/O CONTRA 1346-4 CALLE EMILIANO POL SU-4 Y SE PROBO QUEDO EN SERVICIO 1303-3 100% QUEDO FUERA 1346-4 | S21120100064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 53 | 2021-12-01 | 38478 | keep | 0 | Dec | 2021 | 0.026207 | 0.00049448 | Sustained | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-12-01 08:25 | 2021-12-01 10:36 | 3932 | 002:11 | T | DESGANCHE | SE ABRIO CALLE LOS ROBLES URB. HORIZON Y SE CERRO N/O EN SU-4 EMILIANO POL 95% EN SERVICIO SU CARGA POR 1303-3 | S21120100064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2021-12-01 | 515092 | keep | 0 | Dec | 2021 | 0.35083 | 0.0026781 | Sustained | FALSE | FALSE | Not_TMED_Event | 3932
GUAYAMA | 2021-12-01 08:28 | 2021-12-01 08:29 | 215 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21120100002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-01 | 215 | keep | 0 | Dec | 2021 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
SAN JUAN | 2021-12-01 09:03 | 2021-12-01 09:04 | 5062 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21120100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-01 | 5062 | keep | 0 | Dec | 2021 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
BAYAMON | 2021-12-01 09:10 | 2021-12-01 09:52 | 10 | 000:42 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA REALIZAR DESGANCHE SECUNDARIO | S21120100070 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 42 | 2021-12-01 | 420 | keep | 0 | Dec | 2021 | 0.00028606 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-01 09:21 | 2021-12-01 16:52 | 2 | 007:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M21120100025 | New_Event | Wire Down | Include | Include | Equipment | 451 | 2021-12-01 | 902 | keep | 0 | Dec | 2021 | 0.00061435 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2021-12-01 09:24 | 2021-12-01 09:27 | 3957 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S21120100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-12-01 | 11871 | keep | 0 | Dec | 2021 | 0.0080853 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
HUMACAO | 2021-12-01 09:27 | 2021-12-01 14:51 | 10 | 005:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C21120100014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 324 | 2021-12-01 | 3240 | keep | 0 | Dec | 2021 | 0.0022067 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-01 09:27 | 2021-12-01 14:40 | 10 | 005:13 | P | NO SE REPORTO CAUSA | 2 X 10 EN TRANSFORMADOR EL JOURNEYMAN INFORMO QUE NO ENCONTRO CAUSA PARA LOS FUSIBLES FUNDIDOS | M21120100026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 313 | 2021-12-01 | 3130 | keep | 0 | Dec | 2021 | 0.0021318 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-12-01 09:28 | 2021-12-01 16:54 | 6 | 007:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PM PARA INSTALAR PROVISIONAL SECUNDARIO | P21120100006 | New_Event | Secondary Wire Down | Include | Include | Equipment | 446 | 2021-12-01 | 2676 | keep | 0 | Dec | 2021 | 0.0018226 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-12-01 09:31 | 2021-12-01 09:32 | 1742 | 000:01 | P | OTRAS CAUSAS | RECIERRE DEL 3015-07 QUE LLEVA PARTE DEL 3103-05 | C21120100000 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-12-01 | 1742 | keep | 0 | Dec | 2021 | 0.0011865 | 0.0011865 | Momentary | FALSE | FALSE | Not_TMED_Event | 1742
CAGUAS | 2021-12-01 09:32 | 2021-12-01 14:23 | 18 | 004:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR CRUCE POR AVE | C21120100015 | New_Event |  |  | Include | Wildlife | 291 | 2021-12-01 | 5238 | keep | 0 | Dec | 2021 | 0.0035676 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CAGUAS | 2021-12-01 09:32 | 2021-12-01 17:02 | 1 | 007:30 | P | OTRAS CAUSAS | ABRIO RISER PARA REMPLAZAR C/T | C21120100011 | 1st_after_momentary | Other Causes | Include | Include | Other | 450 | 2021-12-01 | 450 | keep | 0 | Dec | 2021 | 0.00030649 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-01 09:35 | 2021-12-01 13:50 | 30 | 004:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21120100028 | New_Event | Bad Weather | Include | Include | Weather | 255 | 2021-12-01 | 7650 | keep | 0 | Dec | 2021 | 0.0052104 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-01 09:39 | 2021-12-01 10:44 | 1185 | 001:05 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA REPARAR LINEA PARTIDA LLEVA CARGA DEL 8002-04 NO HAY EVENTO DE PARCIAL | A21120100021 | New_Event | Wire Down | Include | Include | Equipment | 65 | 2021-12-01 | 77025 | keep | 0 | Dec | 2021 | 0.052461 | 0.0008071 | Sustained | FALSE | FALSE | Not_TMED_Event | 1185
ARECIBO | 2021-12-01 09:39 | 2021-12-01 10:44 | 63 | 001:05 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA REPARAR LINEA PARTIDA SU CARGA POR EL 8002-03 | A21120100021 | New_Event | Wire Down | Include | Include | Equipment | 65 | 2021-12-01 | 4095 | keep | 0 | Dec | 2021 | 0.0027891 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
BAYAMON | 2021-12-01 09:41 | 2021-12-01 11:58 | 1 | 002:17 | P | NO SE REPORTO CAUSA | 1 X 25 EN SU 3 | S21120100081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 137 | 2021-12-01 | 137 | keep | 0 | Dec | 2021 | 9.331e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-01 09:42 | 2021-12-01 14:30 | 80 | 004:48 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA EL JOURNEYMAN NO ENCONTRO CAUSA PARA EL FUSIBLE FUNDIDO | M21120100029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 288 | 2021-12-01 | 23040 | keep | 0 | Dec | 2021 | 0.015692 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-12-01 09:46 | 2021-12-01 09:48 | 922 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SU CARGA POR 1401-08 | S21120100083 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-01 | 1844 | keep | 0 | Dec | 2021 | 0.0012559 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-12-01 09:46 | 2021-12-01 09:48 | 135 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 1346-5 SE PROBO POR CONTROL QUEDO EN SERVICIO | S21120100083 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-01 | 270 | keep | 0 | Dec | 2021 | 0.0001839 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
ARECIBO | 2021-12-01 09:54 | 2021-12-01 12:20 | 1 | 002:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTE SECUNDARIO | A21120100024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 146 | 2021-12-01 | 146 | keep | 0 | Dec | 2021 | 9.944e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-12-01 09:55 | 2021-12-01 10:13 | 3744 | 000:18 | T | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE Y SACO EL INTERRUPTOR DE SERVICIO | P21120100009 | New_Event |  |  | Include | Wildlife | 18 | 2021-12-01 | 67392 | keep | 0 | Dec | 2021 | 0.0459 | 0.00255 | Sustained | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2021-12-01 09:57 | 2021-12-01 12:08 | 658 | 002:11 | T | PARARRAYOS DEFECTUOSO | SE RETIRARON 2 PARARRAYOS DE MONTURA PRIVADA | P21120100012 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 131 | 2021-12-01 | 86198 | keep | 0 | Dec | 2021 | 0.058709 | 0.00044816 | Sustained | FALSE | FALSE | Not_TMED_Event | 658
BAYAMON | 2021-12-01 10:03 | 2021-12-01 12:37 | 10 | 002:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR PEDESTAL Y BARRAS SECUNDARIAS | B21113000071 | New_Event | Secondary Wire Down | Include | Include | Equipment | 154 | 2021-12-01 | 1540 | keep | 0 | Dec | 2021 | 0.0010489 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-12-01 10:03 | 2021-12-01 12:54 | 1 | 002:51 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR POR DESGANCHE | P21120100010 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 171 | 2021-12-01 | 171 | keep | 0 | Dec | 2021 | 0.00011647 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-12-01 10:05 | 2021-12-01 12:53 | 10 | 002:48 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR Y SE REALIZO DESGANCHE | A21120100028 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 168 | 2021-12-01 | 1680 | keep | 0 | Dec | 2021 | 0.0011442 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-12-01 10:10 | 2021-12-01 10:11 | 3718 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE POR AVE EN PIN POLE TOP | P21120100016 | New_Event |  |  | Include | Wildlife | 1 | 2021-12-01 | 3718 | keep | 0 | Dec | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
PONCE | 2021-12-01 10:11 | 2021-12-01 11:56 | 80 | 001:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA POR CRUCE DE FASES POR AVE | P21120100018 | 1st_after_momentary |  |  | Include | Wildlife | 105 | 2021-12-01 | 8400 | keep | 0 | Dec | 2021 | 0.0057212 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-12-01 10:15 | 2021-12-01 15:30 | 150 | 005:15 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21120100014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 315 | 2021-12-01 | 47250 | keep | 0 | Dec | 2021 | 0.032182 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2021-12-01 10:19 | 2021-12-01 13:37 | 100 | 003:18 | P | DESGANCHE | 3 X 50 EN C/L | C21120100019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2021-12-01 | 19800 | keep | 0 | Dec | 2021 | 0.013486 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-12-01 10:21 | 2021-12-01 12:05 | 10 | 001:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21120100015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 104 | 2021-12-01 | 1040 | keep | 0 | Dec | 2021 | 0.00070834 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-12-01 10:21 | 2021-12-01 18:20 | 10 | 007:59 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REALIZAR CAMBIO DE LINEAS A POSTE NUEVO | M21120100035 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 479 | 2021-12-01 | 4790 | keep | 0 | Dec | 2021 | 0.0032624 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-12-01 10:22 | 2021-12-01 11:31 | 8 | 001:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR BARRAS EN 2 PEDESTALES | R21120100009 | New_Event | Secondary Wire Down | Include | Include | Equipment | 69 | 2021-12-01 | 552 | keep | 0 | Dec | 2021 | 0.00037596 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-12-01 10:24 | 2021-12-01 10:25 | 776 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-12-01 | 776 | keep | 0 | Dec | 2021 | 0.00052853 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
VEGA BAJA | 2021-12-01 10:24 | 2021-12-01 10:25 | 2216 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-12-01 | 2216 | keep | 0 | Dec | 2021 | 0.0015093 | 0.0015093 | Momentary | FALSE | FALSE | Not_TMED_Event | 2216
VEGA BAJA | 2021-12-01 10:24 | 2021-12-01 10:25 | 3387 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-12-01 | 3387 | keep | 0 | Dec | 2021 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
VEGA BAJA | 2021-12-01 10:24 | 2021-12-01 10:25 | 4702 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-12-01 | 4702 | keep | 0 | Dec | 2021 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2021-12-01 10:24 | 2021-12-01 10:25 | 377 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-12-01 | 377 | keep | 0 | Dec | 2021 | 0.00025677 | 0.00025677 | Momentary | FALSE | FALSE | Not_TMED_Event | 377
VEGA BAJA | 2021-12-01 10:24 | 2021-12-01 10:25 | 2368 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-12-01 | 2368 | keep | 0 | Dec | 2021 | 0.0016128 | 0.0016128 | Momentary | FALSE | FALSE | Not_TMED_Event | 2368
VEGA BAJA | 2021-12-01 10:24 | 2021-12-01 10:25 | 538 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-12-01 | 538 | keep | 0 | Dec | 2021 | 0.00036643 | 0.00036643 | Momentary | FALSE | FALSE | Not_TMED_Event | 538
VEGA BAJA | 2021-12-01 10:24 | 2021-12-01 10:25 | 1284 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-12-01 | 1284 | keep | 0 | Dec | 2021 | 0.00087453 | 0.00087453 | Momentary | FALSE | FALSE | Not_TMED_Event | 1284
VEGA BAJA | 2021-12-01 10:24 | 2021-12-01 10:25 | 652 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-12-01 | 652 | keep | 0 | Dec | 2021 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2021-12-01 10:24 | 2021-12-01 10:25 | 2704 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-12-01 | 2704 | keep | 0 | Dec | 2021 | 0.0018417 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
VEGA BAJA | 2021-12-01 10:24 | 2021-12-01 10:25 | 1526 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-12-01 | 1526 | keep | 0 | Dec | 2021 | 0.0010394 | 0.0010394 | Momentary | FALSE | FALSE | Not_TMED_Event | 1526
VEGA BAJA | 2021-12-01 10:24 | 2021-12-01 10:25 | 308 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-12-01 | 308 | keep | 0 | Dec | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2021-12-01 10:24 | 2021-12-01 10:25 | 1397 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-12-01 | 1397 | keep | 0 | Dec | 2021 | 0.00095149 | 0.00095149 | Momentary | FALSE | FALSE | Not_TMED_Event | 1397
VEGA BAJA | 2021-12-01 10:24 | 2021-12-01 10:25 | 2926 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-12-01 | 2926 | keep | 0 | Dec | 2021 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
VEGA BAJA | 2021-12-01 10:24 | 2021-12-01 10:25 | 27 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-12-01 | 27 | keep | 0 | Dec | 2021 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
VEGA BAJA | 2021-12-01 10:24 | 2021-12-01 10:25 | 603 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-12-01 | 603 | keep | 0 | Dec | 2021 | 0.0004107 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
VEGA BAJA | 2021-12-01 10:24 | 2021-12-01 10:25 | 6 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-12-01 | 6 | keep | 0 | Dec | 2021 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2021-12-01 10:24 | 2021-12-01 10:25 | 325 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-12-01 | 325 | keep | 0 | Dec | 2021 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
VEGA BAJA | 2021-12-01 10:24 | 2021-12-01 10:25 | 172 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-12-01 | 172 | keep | 0 | Dec | 2021 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
VEGA BAJA | 2021-12-01 10:24 | 2021-12-01 12:49 | 31 | 002:25 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 115 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 145 | 2021-12-01 | 4495 | keep | 0 | Dec | 2021 | 0.0030615 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
BAYAMON | 2021-12-01 10:24 | 2021-12-01 12:49 | 1859 | 002:25 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 115 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 145 | 2021-12-01 | 269555 | keep | 0 | Dec | 2021 | 0.18359 | 0.0012662 | Sustained | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2021-12-01 10:24 | 2021-12-01 12:49 | 7 | 002:25 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 115 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 145 | 2021-12-01 | 1015 | keep | 0 | Dec | 2021 | 0.00069131 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-12-01 10:24 | 2021-12-01 10:25 | 2861 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-12-01 | 2861 | keep | 0 | Dec | 2021 | 0.0019486 | 0.0019486 | Momentary | FALSE | FALSE | Not_TMED_Event | 2861
BAYAMON | 2021-12-01 10:24 | 2021-12-01 10:25 | 2096 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-12-01 | 2096 | keep | 0 | Dec | 2021 | 0.0014276 | 0.0014276 | Momentary | FALSE | FALSE | Not_TMED_Event | 2096
BAYAMON | 2021-12-01 10:24 | 2021-12-01 10:25 | 493 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-12-01 | 493 | keep | 0 | Dec | 2021 | 0.00033578 | 0.00033578 | Momentary | FALSE | FALSE | Not_TMED_Event | 493
VEGA BAJA | 2021-12-01 10:24 | 2021-12-01 10:25 | 425 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-12-01 | 425 | keep | 0 | Dec | 2021 | 0.00028947 | 0.00028947 | Momentary | FALSE | FALSE | Not_TMED_Event | 425
ARECIBO | 2021-12-01 10:25 | 2021-12-01 18:01 | 4 | 007:36 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES | A21120100031 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 456 | 2021-12-01 | 1824 | keep | 0 | Dec | 2021 | 0.0012423 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2021-12-01 10:30 | 2021-12-01 11:47 | 20 | 001:17 | P | DESGANCHE | SE ABRIO CORTE DE LINEA Y SE REALIZO DESGANCHE | A21120100026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2021-12-01 | 1540 | keep | 0 | Dec | 2021 | 0.0010489 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-12-01 10:30 | 2021-12-01 10:32 | 776 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 2 38 KV VEGA BAJA | B21120100000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2021-12-01 | 1552 | keep | 0 | Dec | 2021 | 0.0010571 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
VEGA BAJA | 2021-12-01 10:30 | 2021-12-01 10:32 | 2216 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 2 38 KV VEGA BAJA | B21120100000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2021-12-01 | 4432 | keep | 0 | Dec | 2021 | 0.0030186 | 0.0015093 | Momentary | FALSE | FALSE | Not_TMED_Event | 2216
VEGA BAJA | 2021-12-01 10:30 | 2021-12-01 10:32 | 3387 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DORADO TC | B21120100000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2021-12-01 | 6774 | keep | 0 | Dec | 2021 | 0.0046137 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
VEGA BAJA | 2021-12-01 10:30 | 2021-12-01 10:32 | 4702 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 2 DORADO TC | B21120100000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2021-12-01 | 9404 | keep | 0 | Dec | 2021 | 0.006405 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2021-12-01 10:30 | 2021-12-01 10:32 | 377 | 000:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 2 DORADO TC | B21120100000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2021-12-01 | 754 | keep | 0 | Dec | 2021 | 0.00051355 | 0.00025677 | Momentary | FALSE | FALSE | Not_TMED_Event | 377
VEGA BAJA | 2021-12-01 10:31 | 2021-12-01 12:28 | 2368 | 001:57 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV DORADO TC | B21120100000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 117 | 2021-12-01 | 277056 | keep | 0 | Dec | 2021 | 0.1887 | 0.0016128 | Sustained | FALSE | FALSE | Not_TMED_Event | 2368
VEGA BAJA | 2021-12-01 10:31 | 2021-12-01 12:28 | 538 | 001:57 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV DORADO TC | B21120100000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 117 | 2021-12-01 | 62946 | keep | 0 | Dec | 2021 | 0.042872 | 0.00036643 | Sustained | FALSE | FALSE | Not_TMED_Event | 538
VEGA BAJA | 2021-12-01 10:31 | 2021-12-01 12:28 | 1284 | 001:57 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV DORADO TC | B21120100000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 117 | 2021-12-01 | 150228 | keep | 0 | Dec | 2021 | 0.10232 | 0.00087453 | Sustained | FALSE | FALSE | Not_TMED_Event | 1284
VEGA BAJA | 2021-12-01 10:31 | 2021-12-01 12:50 | 652 | 002:19 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV DORADO TC | B21120100000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 139 | 2021-12-01 | 90628 | keep | 0 | Dec | 2021 | 0.061726 | 0.00044407 | Sustained | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2021-12-01 10:31 | 2021-12-01 12:50 | 2704 | 002:19 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV DORADO TC | B21120100000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 139 | 2021-12-01 | 375856 | keep | 0 | Dec | 2021 | 0.25599 | 0.0018417 | Sustained | FALSE | FALSE | Not_TMED_Event | 2704
VEGA BAJA | 2021-12-01 10:31 | 2021-12-01 12:31 | 1526 | 002:00 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV DORADO TC | B21120100000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 120 | 2021-12-01 | 183120 | keep | 0 | Dec | 2021 | 0.12472 | 0.0010394 | Sustained | FALSE | FALSE | Not_TMED_Event | 1526
VEGA BAJA | 2021-12-01 10:31 | 2021-12-01 12:31 | 308 | 002:00 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV DORADO TC | B21120100000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 120 | 2021-12-01 | 36960 | keep | 0 | Dec | 2021 | 0.025173 | 0.00020978 | Sustained | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2021-12-01 10:31 | 2021-12-01 12:31 | 1397 | 002:00 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV DORADO TC | B21120100000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 120 | 2021-12-01 | 167640 | keep | 0 | Dec | 2021 | 0.11418 | 0.00095149 | Sustained | FALSE | FALSE | Not_TMED_Event | 1397
VEGA BAJA | 2021-12-01 10:31 | 2021-12-01 12:31 | 2926 | 002:00 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV DORADO TC | B21120100000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 120 | 2021-12-01 | 351120 | keep | 0 | Dec | 2021 | 0.23915 | 0.0019929 | Sustained | FALSE | FALSE | Not_TMED_Event | 2926
BAYAMON | 2021-12-01 10:31 | 2021-12-01 12:28 | 1834 | 001:57 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 117 | 2021-12-01 | 214578 | keep | 0 | Dec | 2021 | 0.14615 | 0.0012491 | Sustained | FALSE | FALSE | Not_TMED_Event | 1834
BAYAMON | 2021-12-01 10:31 | 2021-12-01 12:28 | 2324 | 001:57 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 117 | 2021-12-01 | 271908 | keep | 0 | Dec | 2021 | 0.1852 | 0.0015829 | Sustained | FALSE | FALSE | Not_TMED_Event | 2324
VEGA BAJA | 2021-12-01 10:31 | 2021-12-01 12:28 | 1570 | 001:57 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV DORADO TC | B21120100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 117 | 2021-12-01 | 183690 | keep | 0 | Dec | 2021 | 0.12511 | 0.0010693 | Sustained | FALSE | FALSE | Not_TMED_Event | 1570
VEGA BAJA | 2021-12-01 10:31 | 2021-12-01 12:31 | 27 | 002:00 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV DORADO TC | B21120100000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 120 | 2021-12-01 | 3240 | keep | 0 | Dec | 2021 | 0.0022067 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
VEGA BAJA | 2021-12-01 10:31 | 2021-12-01 12:31 | 603 | 002:00 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV DORADO TC | B21120100000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 120 | 2021-12-01 | 72360 | keep | 0 | Dec | 2021 | 0.049284 | 0.0004107 | Sustained | FALSE | FALSE | Not_TMED_Event | 603
VEGA BAJA | 2021-12-01 10:31 | 2021-12-01 12:31 | 6 | 002:00 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV DORADO TC | B21120100000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 120 | 2021-12-01 | 720 | keep | 0 | Dec | 2021 | 0.00049039 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2021-12-01 10:31 | 2021-12-01 12:31 | 325 | 002:00 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV DORADO TC | B21120100000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 120 | 2021-12-01 | 39000 | keep | 0 | Dec | 2021 | 0.026563 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
VEGA BAJA | 2021-12-01 10:31 | 2021-12-01 12:31 | 172 | 002:00 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV DORADO TC | B21120100000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 120 | 2021-12-01 | 20640 | keep | 0 | Dec | 2021 | 0.014058 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
BAYAMON | 2021-12-01 10:31 | 2021-12-01 12:50 | 2861 | 002:19 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV DORADO TC | B21120100000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 139 | 2021-12-01 | 397679 | keep | 0 | Dec | 2021 | 0.27086 | 0.0019486 | Sustained | FALSE | FALSE | Not_TMED_Event | 2861
BAYAMON | 2021-12-01 10:31 | 2021-12-01 12:50 | 2096 | 002:19 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV DORADO TC | B21120100000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 139 | 2021-12-01 | 291344 | keep | 0 | Dec | 2021 | 0.19843 | 0.0014276 | Sustained | FALSE | FALSE | Not_TMED_Event | 2096
BAYAMON | 2021-12-01 10:31 | 2021-12-01 12:50 | 493 | 002:19 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV DORADO TC | B21120100000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 139 | 2021-12-01 | 68527 | keep | 0 | Dec | 2021 | 0.046673 | 0.00033578 | Sustained | FALSE | FALSE | Not_TMED_Event | 493
VEGA BAJA | 2021-12-01 10:31 | 2021-12-01 12:28 | 425 | 001:57 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38 KV DORADO TC | B21120100000 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 117 | 2021-12-01 | 49725 | keep | 0 | Dec | 2021 | 0.033867 | 0.00028947 | Sustained | FALSE | FALSE | Not_TMED_Event | 425
CAGUAS | 2021-12-01 10:33 | 2021-12-01 19:15 | 60 | 008:42 | P | CABLE SOTERRADO AVERIADO | 1 X 100 EN C/L DEJO FUERA RISER QUE ESTA EN CALENTAMINETO SIN CARGA | C21120100021 | New_Event | UG Cable Fault | Include | Include | Equipment | 522 | 2021-12-01 | 31320 | keep | 0 | Dec | 2021 | 0.021332 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-12-01 10:35 | 2021-12-01 13:10 | 1 | 002:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTE SECUNDARIO | A21120100033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 155 | 2021-12-01 | 155 | keep | 0 | Dec | 2021 | 0.00010557 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-12-01 10:36 | 2021-12-01 16:04 | 8 | 005:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C21120100022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 328 | 2021-12-01 | 2624 | keep | 0 | Dec | 2021 | 0.0017872 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-12-01 10:40 | 2021-12-01 13:06 | 80 | 002:26 | P | DESGANCHE | SE HIZO DESGANCHE Y SE CERRO MACHETE 100% EN SERVICIO POR 1303-3 | S21120100064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2021-12-01 | 11680 | keep | 0 | Dec | 2021 | 0.0079552 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2021-12-01 10:43 | 2021-12-01 12:22 | 1746 | 001:39 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE RETIRO AVE DE PIN POLE TOP Y SE CERRO INTERRUPTOR POR SCADA TAMBIEN SE CERTIFICO UN ACCIDENTE POR CONTACTO ELECTRICO DE LA COMPAÃ‘IA PRIVADA SUNSET CONTRACTOR TRABAJOS EN ANTIGUO CORREO CALLE ATOCHA DE PONCE | P21120100021 | New_Event |  |  | Include | Wildlife | 99 | 2021-12-01 | 172854 | keep | 0 | Dec | 2021 | 0.11773 | 0.0011892 | Sustained | FALSE | FALSE | Not_TMED_Event | 1746
BAYAMON | 2021-12-01 10:51 | 2021-12-01 16:43 | 40 | 005:52 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21120100042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 352 | 2021-12-01 | 14080 | keep | 0 | Dec | 2021 | 0.0095898 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-12-01 10:57 | 2021-12-01 14:05 | 1 | 003:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA DE RISER AVERIADA NO FUNDIO | C21120100023 | New_Event | Cutout Failure | Include | Include | Equipment | 188 | 2021-12-01 | 188 | keep | 0 | Dec | 2021 | 0.00012805 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-01 11:19 | 2021-12-01 15:02 | 40 | 003:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M21120100045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 223 | 2021-12-01 | 8920 | keep | 0 | Dec | 2021 | 0.0060754 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-12-01 11:19 | 2021-12-01 11:20 | 1227 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | A21120100037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-01 | 1227 | keep | 0 | Dec | 2021 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2021-12-01 11:19 | 2021-12-01 11:20 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | A21120100038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-01 | 3431 | keep | 0 | Dec | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
CAGUAS | 2021-12-01 11:24 | 2021-12-01 12:01 | 1 | 000:37 | P | NO SE REPORTO CAUSA | 1 RBA DE 10AMP EN SU 6 NO CAUSA | C21120100026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 37 | 2021-12-01 | 37 | keep | 0 | Dec | 2021 | 2.5201e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-01 11:32 | 2021-12-01 18:19 | 25 | 006:47 | P | ESTRUCTURA AVERIADA | SE ABRIO C/L PARA REMPLAZO DE POSTE PARTIDO | S21120100013 | New_Event | Defective Pole | Include | Include | Equipment | 407 | 2021-12-01 | 10175 | keep | 0 | Dec | 2021 | 0.0069301 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-12-01 12:00 | 2021-12-01 12:33 | 50 | 000:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA CERRAR PUENTE LINEA A TRANSFORMADOR TRAS PATIO | S21113000028 | Additional_clients | Wire Down | Include | Include | Equipment | 33 | 2021-12-01 | 1650 | keep | 0 | Dec | 2021 | 0.0011238 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-01 12:04 | 2021-12-01 17:58 | 5 | 005:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO SECUNDARIA | S21120100105 | New_Event | Secondary Wire Down | Include | Include | Equipment | 354 | 2021-12-01 | 1770 | keep | 0 | Dec | 2021 | 0.0012055 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2021-12-01 12:21 | 2021-12-01 12:54 | 20 | 000:33 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 50 KVA 4160 VOLT AVERIADO POR OTRO IGUAL CAPACIDAD Y VOLTAJE. | P21120100036 | New_Event | Service Transformer Failure | Include | Include | Equipment | 33 | 2021-12-01 | 660 | keep | 0 | Dec | 2021 | 0.00044952 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-12-01 12:34 | 2021-12-01 13:59 | 8 | 001:25 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHO | C21120100038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2021-12-01 | 680 | keep | 0 | Dec | 2021 | 0.00046314 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-12-01 12:48 | 2021-12-01 17:26 | 7 | 004:38 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIO XMR PARA REEMPLAZAR POSTE SECUNDARIO | R21120100007 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 278 | 2021-12-01 | 1946 | keep | 0 | Dec | 2021 | 0.0013254 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2021-12-01 12:48 | 2021-12-01 17:38 | 100 | 004:50 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21120100219 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 290 | 2021-12-01 | 29000 | keep | 0 | Dec | 2021 | 0.019752 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-12-01 12:59 | 2021-12-01 13:00 | 67 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | A21120100048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-01 | 67 | keep | 0 | Dec | 2021 | 4.5633e-05 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
FAJARDO | 2021-12-01 13:00 | 2021-12-01 17:10 | 1 | 004:10 | P | DESGANCHE | 2 X 80 EN C/L | R21120100019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 250 | 2021-12-01 | 250 | keep | 0 | Dec | 2021 | 0.00017027 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-12-01 13:07 | 2021-12-01 14:48 | 70 | 001:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | A21120100049 | New_Event | Bad Weather | Include | Include | Weather | 101 | 2021-12-01 | 7070 | keep | 0 | Dec | 2021 | 0.0048153 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2021-12-01 13:08 | 2021-12-01 14:39 | 5 | 001:31 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZAR CONECTORES | A21120100050 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 91 | 2021-12-01 | 455 | keep | 0 | Dec | 2021 | 0.0003099 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-12-01 13:20 | 2021-12-01 16:48 | 50 | 003:28 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M21120100070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2021-12-01 | 10400 | keep | 0 | Dec | 2021 | 0.0070834 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-12-01 13:27 | 2021-12-01 16:53 | 40 | 003:26 | P | DESGANCHE | 1 X 40 EN C/L | C21120100044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2021-12-01 | 8240 | keep | 0 | Dec | 2021 | 0.0056122 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2021-12-01 13:50 | 2021-12-01 19:24 | 50 | 005:34 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHO ENDEREZO POSTE REPARO SECUNDARIA Y CERRO PUENTE | R21120100021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 334 | 2021-12-01 | 16700 | keep | 0 | Dec | 2021 | 0.011374 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-12-01 14:00 | 2021-12-01 16:10 | 60 | 002:10 | P | NO SE REPORTO CAUSA | 2 X 65 EN C/L | S21120100121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2021-12-01 | 7800 | keep | 0 | Dec | 2021 | 0.0053125 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2021-12-01 14:14 | 2021-12-01 16:09 | 1 | 001:55 | P | DESGANCHE | 2 X 50 EN C/L | C21120100048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2021-12-01 | 115 | keep | 0 | Dec | 2021 | 7.8326e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-12-01 14:23 | 2021-12-01 18:44 | 1 | 004:21 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | R21120100026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 261 | 2021-12-01 | 261 | keep | 0 | Dec | 2021 | 0.00017777 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-12-01 14:37 | 2021-12-01 14:38 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE NO SE REPORTO CAUSAS | P21120100048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-01 | 527 | keep | 0 | Dec | 2021 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
SAN JUAN | 2021-12-01 14:52 | 2021-12-01 14:54 | 500 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 20% DE LA CARGA POR 1118-10 | S21120100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-01 | 1000 | keep | 0 | Dec | 2021 | 0.0006811 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2021-12-01 14:52 | 2021-12-01 14:54 | 2782 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S21120100105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-01 | 5564 | keep | 0 | Dec | 2021 | 0.0037896 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
HUMACAO | 2021-12-01 14:53 | 2021-12-01 14:55 | 1089 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21120100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-12-01 | 2178 | keep | 0 | Dec | 2021 | 0.0014834 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2021-12-01 14:53 | 2021-12-01 14:55 | 3896 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21120100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-12-01 | 7792 | keep | 0 | Dec | 2021 | 0.0053071 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2021-12-01 14:53 | 2021-12-01 14:55 | 1467 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21120100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-12-01 | 2934 | keep | 0 | Dec | 2021 | 0.0019983 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
HUMACAO | 2021-12-01 14:55 | 2021-12-01 17:00 | 1089 | 002:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21120100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 125 | 2021-12-01 | 136125 | keep | 0 | Dec | 2021 | 0.092714 | 0.00074171 | Sustained | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2021-12-01 14:55 | 2021-12-01 17:00 | 3896 | 002:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21120100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 125 | 2021-12-01 | 487000 | keep | 0 | Dec | 2021 | 0.33169 | 0.0026535 | Sustained | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2021-12-01 14:55 | 2021-12-01 17:00 | 1467 | 002:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21120100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 125 | 2021-12-01 | 183375 | keep | 0 | Dec | 2021 | 0.1249 | 0.00099917 | Sustained | FALSE | FALSE | Not_TMED_Event | 1467
CAGUAS | 2021-12-01 14:56 | 2021-12-01 17:03 | 3 | 002:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN C/L DESPEGO BAJANTE DE CRUCETA | C21120100060 | New_Event | Wire Down | Include | Include | Equipment | 127 | 2021-12-01 | 381 | keep | 0 | Dec | 2021 | 0.0002595 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
UTUADO | 2021-12-01 15:15 | 2021-12-01 17:06 | 60 | 001:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21120100064 | New_Event | Bad Weather | Include | Include | Weather | 111 | 2021-12-01 | 6660 | keep | 0 | Dec | 2021 | 0.0045361 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2021-12-01 15:20 | 2021-12-01 16:44 | 200 | 001:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA Y OTRO FUSIBLE DE 65 EN DIFERENTES CORTES DE LINEA AVE CRUZO LINEAS | P21120100051 | New_Event |  |  | Include | Wildlife | 84 | 2021-12-01 | 16800 | keep | 0 | Dec | 2021 | 0.011442 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2021-12-01 15:20 | 2021-12-01 16:51 | 50 | 001:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | P21120100057 | New_Event |  |  | Include | Wildlife | 91 | 2021-12-01 | 4550 | keep | 0 | Dec | 2021 | 0.003099 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-12-01 15:24 | 2021-12-01 17:36 | 300 | 002:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21120100066 | New_Event | Bad Weather | Include | Include | Weather | 132 | 2021-12-01 | 39600 | keep | 0 | Dec | 2021 | 0.026971 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
VEGA BAJA | 2021-12-01 15:32 | 2021-12-01 15:52 | 12 | 000:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21120100240 | New_Event | Secondary Wire Down | Include | Include | Equipment | 20 | 2021-12-01 | 240 | keep | 0 | Dec | 2021 | 0.00016346 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-12-01 15:44 | 2021-12-02 11:19 | 8 | 019:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C21120100084 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1175 | 2021-12-01 | 9400 | keep | 0 | Dec | 2021 | 0.0064023 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-12-01 15:50 | 2021-12-01 15:51 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21120100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-01 | 641 | keep | 0 | Dec | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
MAYAGÃœEZ | 2021-12-01 15:50 | 2021-12-01 20:16 | 200 | 004:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO AVERIADO EN CORTE DE LINEA | M21120100095 | New_Event | Wire Down | Include | Include | Equipment | 266 | 2021-12-01 | 53200 | keep | 0 | Dec | 2021 | 0.036234 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-12-01 16:26 | 2021-12-01 16:27 | 1399 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-01 | 1399 | keep | 0 | Dec | 2021 | 0.00095285 | 0.00095285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1399
BAYAMON | 2021-12-01 16:26 | 2021-12-01 16:27 | 302 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-01 | 302 | keep | 0 | Dec | 2021 | 0.00020569 | 0.00020569 | Momentary | FALSE | FALSE | Not_TMED_Event | 302
BAYAMON | 2021-12-01 16:26 | 2021-12-01 16:27 | 1048 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-01 | 1048 | keep | 0 | Dec | 2021 | 0.00071379 | 0.00071379 | Momentary | FALSE | FALSE | Not_TMED_Event | 1048
BAYAMON | 2021-12-01 16:26 | 2021-12-01 16:27 | 573 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-01 | 573 | keep | 0 | Dec | 2021 | 0.00039027 | 0.00039027 | Momentary | FALSE | FALSE | Not_TMED_Event | 573
BAYAMON | 2021-12-01 16:26 | 2021-12-01 16:27 | 1313 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-01 | 1313 | keep | 0 | Dec | 2021 | 0.00089428 | 0.00089428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1313
PONCE | 2021-12-01 16:29 | 2021-12-01 16:30 | 752 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21120100052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-01 | 752 | keep | 0 | Dec | 2021 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
MAYAGÃœEZ | 2021-12-01 16:29 | 2021-12-01 18:05 | 30 | 001:36 | P | DESGANCHE | 3 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEAS | M21120100101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2021-12-01 | 2880 | keep | 0 | Dec | 2021 | 0.0019616 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2021-12-01 16:34 | 2021-12-02 11:42 | 500 | 019:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | M21120100103 | New_Event | Cutout Failure | Include | Include | Equipment | 1148 | 2021-12-01 | 574000 | keep | 0 | Dec | 2021 | 0.39095 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2021-12-01 16:49 | 2021-12-01 16:52 | 922 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR SCADA CARGA POR EL 1401-08 | S21120100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-12-01 | 2766 | keep | 0 | Dec | 2021 | 0.0018839 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-12-01 16:49 | 2021-12-01 16:52 | 135 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR SCADA LLEVA 1346-05 | S21120100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-12-01 | 405 | keep | 0 | Dec | 2021 | 0.00027584 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
BAYAMON | 2021-12-01 16:51 | 2021-12-01 18:11 | 50 | 001:20 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21120100251 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 80 | 2021-12-01 | 4000 | keep | 0 | Dec | 2021 | 0.0027244 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-12-01 16:57 | 2021-12-01 17:01 | 726 | 000:04 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE CERRO POR SCADA LLEVA 1346-04 | S21120100000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 4 | 2021-12-01 | 2904 | keep | 0 | Dec | 2021 | 0.0019779 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-12-01 16:57 | 2021-12-01 17:01 | 3932 | 000:04 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE CERRO POR SCADA CARGA POR EL 1303-03 | S21120100000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 4 | 2021-12-01 | 15728 | keep | 0 | Dec | 2021 | 0.010712 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
SAN JUAN | 2021-12-01 17:05 | 2021-12-01 17:08 | 726 | 000:03 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE CERRO POR SCADA LLEVA EL 1346-04 | S21120100000 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 3 | 2021-12-01 | 2178 | keep | 0 | Dec | 2021 | 0.0014834 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-12-01 17:05 | 2021-12-01 17:08 | 3932 | 000:03 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE CERRO POR SCADA CARGA POR EL 1303-03 | S21120100000 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 3 | 2021-12-01 | 11796 | keep | 0 | Dec | 2021 | 0.0080342 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
SAN JUAN | 2021-12-01 17:08 | 2021-12-01 23:46 | 100 | 006:38 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 2 X 100 EN CORTE DE LINEA 1 X 40 EN PROVISIONAL AEREO SE REPARO TERMINACION | S21120100180 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 398 | 2021-12-01 | 39800 | keep | 0 | Dec | 2021 | 0.027108 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-12-01 17:31 | 2021-12-01 23:03 | 90 | 005:32 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 80 EN SU SE REEMPLAZO TERMINACION QUEMADA | R21120100044 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 332 | 2021-12-01 | 29880 | keep | 0 | Dec | 2021 | 0.020351 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
ARECIBO | 2021-12-01 17:33 | 2021-12-01 20:20 | 80 | 002:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21120100080 | New_Event | Bad Weather | Include | Include | Weather | 167 | 2021-12-01 | 13360 | keep | 0 | Dec | 2021 | 0.0090994 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-12-01 17:34 | 2021-12-01 17:35 | 130 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE ALIMENTADOR 1717-04 LLEVA TRANFERIDO EL 20% DE LA CARGA DEL 1716-02 | B21120100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-01 | 130 | keep | 0 | Dec | 2021 | 8.8542e-05 | 8.8542e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 130
BAYAMON | 2021-12-01 17:34 | 2021-12-01 17:35 | 1362 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 20% DEL ALIMENTADOR 1716-02 | B21120100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-01 | 1362 | keep | 0 | Dec | 2021 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
GUAYAMA | 2021-12-01 18:21 | 2021-12-01 18:22 | 25 | 000:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE EL TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P21120100050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1 | 2021-12-01 | 25 | keep | 0 | Dec | 2021 | 1.7027e-05 | 1.7027e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-12-01 18:22 | 2021-12-01 22:06 | 30 | 003:44 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21120100257 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2021-12-01 | 6720 | keep | 0 | Dec | 2021 | 0.004577 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-12-01 18:26 | 2021-12-01 21:11 | 60 | 002:45 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN C/L ELIMINO PARARRAYO | R21120100048 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 165 | 2021-12-01 | 9900 | keep | 0 | Dec | 2021 | 0.0067428 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2021-12-01 18:46 | 2021-12-02 04:46 | 1 | 010:00 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN C/L REMPLAZO PARARRAYO | C21120100114 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 600 | 2021-12-01 | 600 | keep | 0 | Dec | 2021 | 0.00040866 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-12-01 19:01 | 2021-12-01 19:02 | 1854 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21120100119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-01 | 1854 | keep | 0 | Dec | 2021 | 0.0012628 | 0.0012628 | Momentary | FALSE | FALSE | Not_TMED_Event | 1854
ARECIBO | 2021-12-01 19:04 | 2021-12-01 19:05 | 1923 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | A21120100093 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-12-01 | 1923 | keep | 0 | Dec | 2021 | 0.0013097 | 0.0013097 | Momentary | FALSE | FALSE | Not_TMED_Event | 1923
ARECIBO | 2021-12-01 19:04 | 2021-12-01 19:05 | 308 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | A21120100000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-12-01 | 308 | keep | 0 | Dec | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
ARECIBO | 2021-12-01 19:05 | 2021-12-01 22:34 | 40 | 003:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21120100094 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 209 | 2021-12-01 | 8360 | keep | 0 | Dec | 2021 | 0.005694 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-12-01 19:05 | 2021-12-01 23:12 | 40 | 004:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 Y 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21120100107 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 247 | 2021-12-01 | 9880 | keep | 0 | Dec | 2021 | 0.0067292 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-12-01 19:08 | 2021-12-01 21:38 | 60 | 002:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21120100266 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2021-12-01 | 9000 | keep | 0 | Dec | 2021 | 0.0061299 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-12-01 19:53 | 2021-12-01 20:00 | 381 | 000:07 | P | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37900 30% POR EL 1206-04 | S21120100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-12-01 | 2667 | keep | 0 | Dec | 2021 | 0.0018165 | 0.0002595 | Sustained | FALSE | FALSE | Not_TMED_Event | 381
SAN JUAN | 2021-12-01 19:53 | 2021-12-01 20:00 | 1944 | 000:07 | P | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37900 40% POR EL 1206-04 | S21120100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-12-01 | 13608 | keep | 0 | Dec | 2021 | 0.0092683 | 0.001324 | Sustained | FALSE | FALSE | Not_TMED_Event | 1944
SAN JUAN | 2021-12-01 19:53 | 2021-12-01 20:00 | 10211 | 000:07 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37900 CARGA POR EL 1206-03 | S21120100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-12-01 | 71477 | keep | 0 | Dec | 2021 | 0.048683 | 0.0069547 | Sustained | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-12-01 19:53 | 2021-12-01 20:00 | 641 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37900 | S21120100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-12-01 | 4487 | keep | 0 | Dec | 2021 | 0.0030561 | 0.00043658 | Sustained | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-12-01 19:53 | 2021-12-01 20:00 | 733 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37900 | S21120100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-12-01 | 5131 | keep | 0 | Dec | 2021 | 0.0034947 | 0.00049924 | Sustained | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2021-12-01 19:53 | 2021-12-01 20:00 | 4133 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37900 | S21120100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-12-01 | 28931 | keep | 0 | Dec | 2021 | 0.019705 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-12-01 19:53 | 2021-12-01 20:00 | 1799 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37900 | S21120100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-12-01 | 12593 | keep | 0 | Dec | 2021 | 0.008577 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2021-12-01 19:53 | 2021-12-01 19:58 | 1681 | 000:05 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR BKR 1303-04 | S21120100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-12-01 | 8405 | keep | 0 | Dec | 2021 | 0.0057246 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-12-01 19:53 | 2021-12-01 19:58 | 1598 | 000:05 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL BKR 1303-04 | S21120100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-12-01 | 7990 | keep | 0 | Dec | 2021 | 0.005442 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2021-12-01 19:54 | 2021-12-01 19:57 | 922 | 000:03 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1401-08 | S21120100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-12-01 | 2766 | keep | 0 | Dec | 2021 | 0.0018839 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-12-01 19:54 | 2021-12-01 19:57 | 135 | 000:03 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA 1346-05 | S21120100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-12-01 | 405 | keep | 0 | Dec | 2021 | 0.00027584 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
PONCE | 2021-12-01 20:05 | 2021-12-02 09:40 | 100 | 013:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P21120100069 | New_Event |  |  | Include | Wildlife | 815 | 2021-12-01 | 81500 | keep | 0 | Dec | 2021 | 0.055509 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-12-01 20:08 | 2021-12-02 10:23 | 25 | 014:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA EN CORTE DE LINEA | A21120100098 | New_Event | Cutout Failure | Include | Include | Equipment | 855 | 2021-12-01 | 21375 | keep | 0 | Dec | 2021 | 0.014558 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2021-12-01 20:17 | 2021-12-01 20:18 | 2216 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21120100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-01 | 2216 | keep | 0 | Dec | 2021 | 0.0015093 | 0.0015093 | Momentary | FALSE | FALSE | Not_TMED_Event | 2216
ARECIBO | 2021-12-01 20:32 | 2021-12-02 10:24 | 5 | 013:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA CRUZADA | A21120100100 | New_Event | Secondary Wire Down | Include | Include | Equipment | 832 | 2021-12-01 | 4160 | keep | 0 | Dec | 2021 | 0.0028334 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-12-01 20:42 | 2021-12-01 20:43 | 3431 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | A21120100101 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-12-01 | 3431 | keep | 0 | Dec | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2021-12-01 20:43 | 2021-12-02 10:51 | 70 | 014:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | A21120100105 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 848 | 2021-12-01 | 59360 | keep | 0 | Dec | 2021 | 0.04043 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-12-01 20:54 | 2021-12-01 22:20 | 28 | 001:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21120100120 | New_Event | Bad Weather | Include | Include | Weather | 86 | 2021-12-01 | 2408 | keep | 0 | Dec | 2021 | 0.0016401 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
VEGA BAJA | 2021-12-01 20:58 | 2021-12-02 01:10 | 4702 | 004:12 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR CONTROL | B21120100272 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 252 | 2021-12-01 | 1184904 | keep | 0 | Dec | 2021 | 0.80703 | 0.0032025 | Sustained | FALSE | FALSE | Not_TMED_Event | 4702
MAYAGÃœEZ | 2021-12-01 21:23 | 2021-12-01 21:24 | 2713 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21120100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-01 | 2713 | keep | 0 | Dec | 2021 | 0.0018478 | 0.0018478 | Momentary | FALSE | FALSE | Not_TMED_Event | 2713
CAGUAS | 2021-12-01 21:41 | 2021-12-01 21:42 | 1510 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21120100129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-01 | 1510 | keep | 0 | Dec | 2021 | 0.0010285 | 0.0010285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1510
SAN JUAN | 2021-12-01 21:53 | 2021-12-02 13:07 | 5 | 015:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | S21120100196 | New_Event | Secondary Wire Down | Include | Include | Equipment | 914 | 2021-12-01 | 4570 | keep | 0 | Dec | 2021 | 0.0031126 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-12-01 21:57 | 2021-12-02 12:25 | 22 | 014:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | S21120100197 | New_Event | Secondary Wire Down | Include | Include | Equipment | 868 | 2021-12-01 | 19096 | keep | 0 | Dec | 2021 | 0.013006 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
VEGA BAJA | 2021-12-01 22:19 | 2021-12-02 00:28 | 40 | 002:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21120100328 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2021-12-01 | 5160 | keep | 0 | Dec | 2021 | 0.0035145 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-12-01 22:48 | 2021-12-01 22:49 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21120100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-01 | 1097 | keep | 0 | Dec | 2021 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
PONCE | 2021-12-01 22:53 | 2021-12-01 22:54 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | RECIRRE NO SE REPORTO CAUSA | P21120100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-01 | 3718 | keep | 0 | Dec | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
PONCE | 2021-12-01 23:17 | 2021-12-01 23:20 | 708 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | P21120100072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-12-01 | 2124 | keep | 0 | Dec | 2021 | 0.0014466 | 0.00048222 | Momentary | FALSE | FALSE | Not_TMED_Event | 708
CAGUAS | 2021-12-01 23:32 | 2021-12-02 10:51 | 40 | 011:19 | P | DESGANCHE | 1 X 80 C/L | C21120100135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 679 | 2021-12-01 | 27160 | keep | 0 | Dec | 2021 | 0.018499 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2021-12-02 00:05 | 2021-12-02 00:06 | 2126 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C21120200001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-02 | 2126 | keep | 0 | Dec | 2021 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
ARECIBO | 2021-12-02 00:19 | 2021-12-02 00:20 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21120200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-02 | 308 | keep | 0 | Dec | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
SAN JUAN | 2021-12-02 00:58 | 2021-12-02 02:02 | 10211 | 001:04 | T | DESGANCHE | SE CERRO POR CONTROL SE PATRULLO Y NO SE ENCONTRO CAUSA CARGA POR INTERRUPTOR 1206-03 | S21120200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2021-12-02 | 653504 | keep | 0 | Dec | 2021 | 0.4451 | 0.0069547 | Sustained | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-12-02 00:58 | 2021-12-02 02:02 | 4133 | 001:04 | T | DESGANCHE | SE CERRO POR CONTROL SE PATRULLO Y NO SE ENCONTRO CAUSA LLEVA LA CARGA DEL 1204-05 | S21120200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2021-12-02 | 264512 | keep | 0 | Dec | 2021 | 0.18016 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
VEGA BAJA | 2021-12-02 01:10 | 2021-12-02 16:17 | 10 | 015:07 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACION SOTERRADA TIPO PISTOLA | B21120200094 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 907 | 2021-12-02 | 9070 | keep | 0 | Dec | 2021 | 0.0061775 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-12-02 01:12 | 2021-12-02 01:27 | 708 | 000:15 | T | ESTRUCTURA AVERIADA | SE ABRE ALIMENTADOR POR POSTE PRIMARIO PARTIDO NO HAY EVENTO ANTES | P21120200001 | New_Event | Defective Pole | Include | Include | Equipment | 15 | 2021-12-02 | 10620 | keep | 0 | Dec | 2021 | 0.0072332 | 0.00048222 | Sustained | FALSE | FALSE | Not_TMED_Event | 708
ARECIBO | 2021-12-02 01:35 | 2021-12-02 01:36 | 1227 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | A21120200000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-12-02 | 1227 | keep | 0 | Dec | 2021 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2021-12-02 01:36 | 2021-12-02 10:24 | 50 | 008:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA DE 100 AMP | A21120200003 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 528 | 2021-12-02 | 26400 | keep | 0 | Dec | 2021 | 0.017981 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-02 02:20 | 2021-12-02 05:43 | 120 | 003:23 | P | LINEA DE TRANSMISION 115KV | DISPARO SUBESTACION CREA POR LINEA 37400 1717-04 LLEVA 20% DEL 1716-02 | B21120200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 203 | 2021-12-02 | 24360 | keep | 0 | Dec | 2021 | 0.016591 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2021-12-02 02:20 | 2021-12-02 05:47 | 4533 | 003:27 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37400 | B21120200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 207 | 2021-12-02 | 938331 | keep | 0 | Dec | 2021 | 0.63909 | 0.0030874 | Sustained | FALSE | FALSE | Not_TMED_Event | 4533
BAYAMON | 2021-12-02 02:20 | 2021-12-02 05:43 | 50 | 003:23 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37400 95% DE LA CARGA TRANSFERIDA AL 1713-05 | B21120200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 203 | 2021-12-02 | 10150 | keep | 0 | Dec | 2021 | 0.0069131 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-02 02:20 | 2021-12-02 05:46 | 4431 | 003:26 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37400 | B21120200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 206 | 2021-12-02 | 912786 | keep | 0 | Dec | 2021 | 0.62169 | 0.0030179 | Sustained | FALSE | FALSE | Not_TMED_Event | 4431
BAYAMON | 2021-12-02 02:20 | 2021-12-02 05:43 | 1362 | 003:23 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37400 LLEVA 20% DEL 1716-02 | B21120200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 203 | 2021-12-02 | 276486 | keep | 0 | Dec | 2021 | 0.18831 | 0.00092765 | Sustained | FALSE | FALSE | Not_TMED_Event | 1362
BAYAMON | 2021-12-02 02:20 | 2021-12-02 05:43 | 341 | 003:23 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37400 | B21120200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 203 | 2021-12-02 | 69223 | keep | 0 | Dec | 2021 | 0.047147 | 0.00023225 | Sustained | FALSE | FALSE | Not_TMED_Event | 341
ARECIBO | 2021-12-02 02:27 | 2021-12-02 02:28 | 2791 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21120200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-02 | 2791 | keep | 0 | Dec | 2021 | 0.0019009 | 0.0019009 | Momentary | FALSE | FALSE | Not_TMED_Event | 2791
ARECIBO | 2021-12-02 02:27 | 2021-12-02 02:28 | 1464 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21120200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-02 | 1464 | keep | 0 | Dec | 2021 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
ARECIBO | 2021-12-02 02:27 | 2021-12-02 02:28 | 759 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21120200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-02 | 759 | keep | 0 | Dec | 2021 | 0.00051695 | 0.00051695 | Momentary | FALSE | FALSE | Not_TMED_Event | 759
ARECIBO | 2021-12-02 02:27 | 2021-12-02 02:28 | 1500 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21120200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-02 | 1500 | keep | 0 | Dec | 2021 | 0.0010216 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
ARECIBO | 2021-12-02 02:27 | 2021-12-02 02:28 | 2132 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21120200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-02 | 2132 | keep | 0 | Dec | 2021 | 0.0014521 | 0.0014521 | Momentary | FALSE | FALSE | Not_TMED_Event | 2132
ARECIBO | 2021-12-02 02:27 | 2021-12-02 02:28 | 2366 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21120200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-02 | 2366 | keep | 0 | Dec | 2021 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
ARECIBO | 2021-12-02 02:27 | 2021-12-02 02:28 | 1976 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21120200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-02 | 1976 | keep | 0 | Dec | 2021 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
ARECIBO | 2021-12-02 02:27 | 2021-12-02 02:28 | 3688 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A21120200000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-02 | 3688 | keep | 0 | Dec | 2021 | 0.0025119 | 0.0025119 | Momentary | FALSE | FALSE | Not_TMED_Event | 3688
VEGA BAJA | 2021-12-02 02:33 | 2021-12-02 02:34 | 325 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21120200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-02 | 325 | keep | 0 | Dec | 2021 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2021-12-02 03:52 | 2021-12-02 03:54 | 1681 | 000:02 | T | NO SE REPORTO CAUSA | INTERRUPTOR DISPARO Y SE CERRO POR SCADA, CARGA TRANSFERIDA AL 1303-04 | S21120200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-02 | 3362 | keep | 0 | Dec | 2021 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-12-02 03:52 | 2021-12-02 03:54 | 1598 | 000:02 | T | NO SE REPORTO CAUSA | INTERRUPTOR DISPARO Y SE CERRO POR CONTROL CARGA TRANSFERIDA AL 1303-04 | S21120200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-02 | 3196 | keep | 0 | Dec | 2021 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
CAGUAS | 2021-12-02 04:00 | 2021-12-02 09:34 | 22 | 005:34 | P | DESGANCHE | 1 X 50 EN C/L | C21120200004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 334 | 2021-12-02 | 7348 | keep | 0 | Dec | 2021 | 0.0050047 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
FAJARDO | 2021-12-02 04:01 | 2021-12-02 15:46 | 1 | 011:45 | P | DESGANCHE | DESGANCHO Y REEMPLAZO CAJA NO FUNDIO | R21120200004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 705 | 2021-12-02 | 705 | keep | 0 | Dec | 2021 | 0.00048017 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-12-02 04:46 | 2021-12-02 04:47 | 2450 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO SE CERRO POR CONTROL | C21120200003 | New_Event |  |  | Include | Wildlife | 1 | 2021-12-02 | 2450 | keep | 0 | Dec | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2021-12-02 04:47 | 2021-12-02 13:27 | 40 | 008:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L Y 1 X 15 EN XMR CRUCE POR AVE | C21120200031 | 1st_after_momentary |  |  | Include | Wildlife | 520 | 2021-12-02 | 20800 | keep | 0 | Dec | 2021 | 0.014167 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2021-12-02 04:47 | 2021-12-02 14:27 | 1 | 009:40 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN C/L REMPLAZO PARARRAYO | C21120100114 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 580 | 2021-12-02 | 580 | keep | 0 | Dec | 2021 | 0.00039504 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-12-02 05:13 | 2021-12-02 12:43 | 10 | 007:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 15 EN XMR DESGANCHO Y REMPLAZO 2 CAJAS AVERIADAS | C21120200006 | New_Event | Cutout Failure | Include | Include | Equipment | 450 | 2021-12-02 | 4500 | keep | 0 | Dec | 2021 | 0.0030649 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-02 05:56 | 2021-12-02 15:12 | 40 | 009:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO | M21120200004 | New_Event | Wire Down | Include | Include | Equipment | 556 | 2021-12-02 | 22240 | keep | 0 | Dec | 2021 | 0.015148 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-12-02 06:16 | 2021-12-02 11:02 | 40 | 004:46 | P | DESGANCHE | 1 X 40 EN C/L | C21120200009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 286 | 2021-12-02 | 11440 | keep | 0 | Dec | 2021 | 0.0077917 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-02 06:21 | 2021-12-02 06:23 | 800 | 000:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO SU CARGA POR 1119-4 Y 120 AMP. POR 1119-2 | S21120200000 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2021-12-02 | 1600 | keep | 0 | Dec | 2021 | 0.0010898 | 0.00054488 | Momentary | FALSE | FALSE | Not_TMED_Event | 800
BAYAMON | 2021-12-02 06:21 | 2021-12-02 06:23 | 450 | 000:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO SU CARGA POR 1119-4 | S21120200000 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2021-12-02 | 900 | keep | 0 | Dec | 2021 | 0.00061299 | 0.00030649 | Momentary | FALSE | FALSE | Not_TMED_Event | 450
BAYAMON | 2021-12-02 06:21 | 2021-12-02 06:23 | 2720 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO LLEVA CARGA 95% 1115-5 Y 120 AMP. 1119-2 | S21120200000 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2021-12-02 | 5440 | keep | 0 | Dec | 2021 | 0.0037052 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
BAYAMON | 2021-12-02 06:23 | 2021-12-02 10:45 | 251 | 004:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN CORTE DE LINEA SE REMPLAZO 2 CAJAS QUEMADAS | S21120200034 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 262 | 2021-12-02 | 65762 | keep | 0 | Dec | 2021 | 0.04479 | 0.00017095 | Sustained | FALSE | FALSE | Not_TMED_Event | 251
HUMACAO | 2021-12-02 06:23 | 2021-12-02 11:18 | 50 | 004:55 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L REMPLAZO AISLADOR | C21120200011 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 295 | 2021-12-02 | 14750 | keep | 0 | Dec | 2021 | 0.010046 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-12-02 07:03 | 2021-12-02 17:01 | 80 | 009:58 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21120200010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 598 | 2021-12-02 | 47840 | keep | 0 | Dec | 2021 | 0.032584 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-12-02 07:07 | 2021-12-02 17:46 | 10 | 010:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR SECUNDARIA Y REALIZAR DESGANCHE | B21120000085 | New_Event | Secondary Wire Down | Include | Include | Equipment | 639 | 2021-12-02 | 6390 | keep | 0 | Dec | 2021 | 0.0043522 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-12-02 07:10 | 2021-12-02 11:19 | 30 | 004:09 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B21120200086 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 249 | 2021-12-02 | 7470 | keep | 0 | Dec | 2021 | 0.0050878 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-12-02 07:12 | 2021-12-02 10:31 | 50 | 003:19 | P | PARARRAYOS DEFECTUOSO | 2 X 80 EN C/L REEMPLAZO PARARRAYO | R21120200005 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 199 | 2021-12-02 | 9950 | keep | 0 | Dec | 2021 | 0.0067769 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-12-02 07:13 | 2021-12-02 12:46 | 40 | 005:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LA LINEA | A21120200013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 333 | 2021-12-02 | 13320 | keep | 0 | Dec | 2021 | 0.0090722 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-12-02 07:20 | 2021-12-02 14:52 | 1 | 007:32 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A21120200014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 452 | 2021-12-02 | 452 | keep | 0 | Dec | 2021 | 0.00030786 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-02 07:21 | 2021-12-02 10:54 | 20 | 003:33 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | B21120200090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 213 | 2021-12-02 | 4260 | keep | 0 | Dec | 2021 | 0.0029015 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-12-02 07:29 | 2021-12-02 08:19 | 20 | 000:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA FUERTE | B21120200091 | New_Event | Bad Weather | Include | Include | Weather | 50 | 2021-12-02 | 1000 | keep | 0 | Dec | 2021 | 0.0006811 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-12-02 07:38 | 2021-12-02 13:06 | 1 | 005:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | B21120200092 | New_Event | Cutout Failure | Include | Include | Equipment | 328 | 2021-12-02 | 328 | keep | 0 | Dec | 2021 | 0.0002234 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-02 08:09 | 2021-12-02 14:05 | 30 | 005:56 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21120200042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 356 | 2021-12-02 | 10680 | keep | 0 | Dec | 2021 | 0.0072741 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2021-12-02 08:10 | 2021-12-02 10:28 | 1 | 002:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 15 EN MONTURA TRIFASICA CRUCE DE FASE SECUNDARIA POR AVE | P21120200009 | New_Event |  |  | Include | Wildlife | 138 | 2021-12-02 | 138 | keep | 0 | Dec | 2021 | 9.3991e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-02 08:29 | 2021-12-02 09:30 | 4133 | 001:01 | T | DESGANCHE | RECERRO LLEVA 1204-5 | S21120200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2021-12-02 | 252113 | keep | 0 | Dec | 2021 | 0.17171 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
BAYAMON | 2021-12-02 08:53 | 2021-12-02 12:22 | 10 | 003:29 | P | DESGANCHE | 1 X 50 EN RISER SE REALIZO DESGANCHE | B21120200094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2021-12-02 | 2090 | keep | 0 | Dec | 2021 | 0.0014235 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-12-02 08:56 | 2021-12-02 14:36 | 5 | 005:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA FIJAR BAJANTE SECUNDARIO ZAFADO | P21120200012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 340 | 2021-12-02 | 1700 | keep | 0 | Dec | 2021 | 0.0011579 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-12-02 08:58 | 2021-12-02 15:18 | 15 | 006:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | M21120200021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 380 | 2021-12-02 | 5700 | keep | 0 | Dec | 2021 | 0.0038822 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-12-02 09:10 | 2021-12-02 09:22 | 2888 | 000:12 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR NO SE REPORTO LA CAUSA | A21120200021 | New_Event | Bad Weather | Include | Include | Weather | 12 | 2021-12-02 | 34656 | keep | 0 | Dec | 2021 | 0.023604 | 0.001967 | Sustained | FALSE | FALSE | Not_TMED_Event | 2888
UTUADO | 2021-12-02 09:15 | 2021-12-02 17:38 | 20 | 008:23 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE MASIVO | A21120200022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 503 | 2021-12-02 | 10060 | keep | 0 | Dec | 2021 | 0.0068518 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-12-02 09:19 | 2021-12-02 14:52 | 6 | 005:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR SECUNDARIA | C21120600000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 333 | 2021-12-02 | 1998 | keep | 0 | Dec | 2021 | 0.0013608 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-12-02 09:21 | 2021-12-02 09:23 | 225 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SU CARGA POR 1303-5 | S21120200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-02 | 450 | keep | 0 | Dec | 2021 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-12-02 09:21 | 2021-12-02 09:23 | 870 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO LLEVA CARGA 1303-4 SE PROBO POR CONTROL QUEDO EN SERVICIO | S21120200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-02 | 1740 | keep | 0 | Dec | 2021 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2021-12-02 09:21 | 2021-12-02 09:22 | 2435 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR 1909-08 LLEVANDO CARGA 1907-05 SE REMPLAZO 3 CAJAS PRIMARIAS PARARRAYOS Y BAJANTE PRIMARIO | S21120200053 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-12-02 | 2435 | keep | 0 | Dec | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-12-02 09:21 | 2021-12-02 09:22 | 2956 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR 1909-08 LLEVANDO CARGA 1907-05 SE REMPLAZO 3 CAJAS PRIMARIAS PARARRAYOS Y BAJANTE PRIMARIO | S21120200053 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-12-02 | 2956 | keep | 0 | Dec | 2021 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2021-12-02 09:22 | 2021-12-02 18:19 | 1 | 008:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON 3 CAJAS PRIMARIAS 3 PARARRAYOS Y 3 BAJANTES PRIMARIOS DE LINEA A CAJA | S21120200056 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 537 | 2021-12-02 | 537 | keep | 0 | Dec | 2021 | 0.00036575 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-12-02 09:24 | 2021-12-02 19:12 | 5 | 009:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR NEUTRALES Y GROUND | R21120200007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 588 | 2021-12-02 | 2940 | keep | 0 | Dec | 2021 | 0.0020024 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-12-02 09:26 | 2021-12-02 18:06 | 40 | 008:40 | P | ESTRUCTURA AVERIADA | ABRIO C/L PARA REMPLAZAR POSTE PARTIDO Y ENDEREZAR OTRO | C21120200023 | New_Event | Defective Pole | Include | Include | Equipment | 520 | 2021-12-02 | 20800 | keep | 0 | Dec | 2021 | 0.014167 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-12-02 09:29 | 2021-12-02 09:30 | 10211 | 000:01 | T | DESGANCHE | RECERRO SU CARGA POR 1206-3 | S21120200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-02 | 10211 | keep | 0 | Dec | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-12-02 09:38 | 2021-12-02 13:23 | 40 | 003:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO CAJA NO FUNDIO | R21120200008 | New_Event | Cutout Failure | Include | Include | Equipment | 225 | 2021-12-02 | 9000 | keep | 0 | Dec | 2021 | 0.0061299 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-12-02 09:46 | 2021-12-02 09:48 | 929 | 000:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO CON R/R OFF LLEVA 1421-4 Y 1421-3 | S21120200000 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2021-12-02 | 1858 | keep | 0 | Dec | 2021 | 0.0012655 | 0.00063274 | Momentary | FALSE | FALSE | Not_TMED_Event | 929
SAN JUAN | 2021-12-02 09:46 | 2021-12-02 09:48 | 451 | 000:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO CON R/R OFF SU CARGA POR 1414-4 | S21120200000 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2021-12-02 | 902 | keep | 0 | Dec | 2021 | 0.00061435 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
SAN JUAN | 2021-12-02 09:46 | 2021-12-02 09:48 | 451 | 000:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO CON R/R OFF SU CARGA POR 1414-4 | S21120200000 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2021-12-02 | 902 | keep | 0 | Dec | 2021 | 0.00061435 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
SAN JUAN | 2021-12-02 09:48 | 2021-12-02 13:03 | 5 | 003:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIO | S21120200057 | New_Event | Wire Down | Include | Include | Equipment | 195 | 2021-12-02 | 975 | keep | 0 | Dec | 2021 | 0.00066407 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-12-02 09:50 | 2021-12-02 09:51 | 10211 | 000:01 | T | DESGANCHE | RECERRO SU CARGA POR 1206-3 | S21120200000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-02 | 10211 | keep | 0 | Dec | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-12-02 09:50 | 2021-12-02 09:51 | 4133 | 000:01 | T | DESGANCHE | RECERRO LLEVA 1204-5 | S21120200000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-02 | 4133 | keep | 0 | Dec | 2021 | 0.002815 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2021-12-02 09:50 | 2021-12-02 12:53 | 12 | 003:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR CONECTORES EN LINEAS SECUNDARIAS | P21120200015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 183 | 2021-12-02 | 2196 | keep | 0 | Dec | 2021 | 0.0014957 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-12-02 09:54 | 2021-12-03 12:57 | 6 | 027:03 | P | TRANSFORMADOR AVERIADO | SE REALIZO CAMBIO DE TRANSFORMADOR POR DERRAME DE ACEITE 50KVA X 50KVA | S21120200171 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1623 | 2021-12-02 | 9738 | keep | 0 | Dec | 2021 | 0.0066325 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2021-12-02 10:00 | 2021-12-02 14:50 | 7 | 004:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | A21120200028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 290 | 2021-12-02 | 2030 | keep | 0 | Dec | 2021 | 0.0013826 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2021-12-02 10:09 | 2021-12-02 14:20 | 40 | 004:11 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A21120200031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2021-12-02 | 10040 | keep | 0 | Dec | 2021 | 0.0068382 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-12-02 10:19 | 2021-12-02 11:45 | 10 | 001:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | B21120200084 | New_Event | Secondary Wire Down | Include | Include | Equipment | 86 | 2021-12-02 | 860 | keep | 0 | Dec | 2021 | 0.00058574 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-02 10:27 | 2021-12-02 14:56 | 125 | 004:29 | P | DESCONECTIVO DEFECTUOSO | SE LEVANTO CONDUCTOR Y SE REMPLAZO MACHETE AVERIADO TRABAJOS CON GOI SJ-211202-03 | S21120200068 | New_Event | Switch Failure | Include | Include | Equipment | 269 | 2021-12-02 | 33625 | keep | 0 | Dec | 2021 | 0.022902 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
FAJARDO | 2021-12-02 10:35 | 2021-12-02 12:40 | 4 | 002:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REEMPLAZAR BARRAS DE PEDESTAL | R21120200013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 125 | 2021-12-02 | 500 | keep | 0 | Dec | 2021 | 0.00034055 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-12-02 10:41 | 2021-12-02 16:05 | 10 | 005:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA Y CONEXIONES | B21120100011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 324 | 2021-12-02 | 3240 | keep | 0 | Dec | 2021 | 0.0022067 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-02 10:43 | 2021-12-02 17:40 | 15 | 006:57 | P | ESTRUCTURA AVERIADA | 2 X 15 EN TRANSFORMADOR SE REMPLAZO POSTE Y SE TRANSFIRIO EL TRANSFORMADOR | M21120200036 | New_Event | Defective Pole | Include | Include | Equipment | 417 | 2021-12-02 | 6255 | keep | 0 | Dec | 2021 | 0.0042603 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-12-02 10:50 | 2021-12-02 18:30 | 20 | 007:40 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REEMPLAZAR POSTE PARTIDO | A21120200038 | New_Event | Defective Pole | Include | Include | Equipment | 460 | 2021-12-02 | 9200 | keep | 0 | Dec | 2021 | 0.0062661 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-12-02 11:00 | 2021-12-02 13:32 | 15 | 002:32 | P | TRANSFORMADOR AVERIADO | SE ABRIO TRANSFOMADOR Y SE AJUSTARO LOS BUSHING DEL TRANSFORMADOR | M21120200040 | New_Event | Service Transformer Failure | Include | Include | Equipment | 152 | 2021-12-02 | 2280 | keep | 0 | Dec | 2021 | 0.0015529 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-12-02 11:01 | 2021-12-02 14:50 | 200 | 003:49 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | P21120200034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 229 | 2021-12-02 | 45800 | keep | 0 | Dec | 2021 | 0.031194 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2021-12-02 11:16 | 2021-12-02 11:18 | 215 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B21120200000 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2021-12-02 | 430 | keep | 0 | Dec | 2021 | 0.00029287 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2021-12-02 11:18 | 2021-12-02 23:17 | 30 | 011:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE RETESO LINEA PRIMARIA | B21120200011 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 719 | 2021-12-02 | 21570 | keep | 0 | Dec | 2021 | 0.014691 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2021-12-02 11:23 | 2021-12-02 15:49 | 10 | 004:26 | P | NO SE REPORTO CAUSA | 1 X 50 EN SU 1 | B21120200117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 266 | 2021-12-02 | 2660 | keep | 0 | Dec | 2021 | 0.0018117 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-02 11:31 | 2021-12-02 16:23 | 3654 | 004:52 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADORES ROTOS EN EL TRONCAL DEL ALIMENTADOR Y SE CERRO EL INTERRUPTOR | A21120200049 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 292 | 2021-12-02 | 1066968 | keep | 0 | Dec | 2021 | 0.72671 | 0.0024887 | Sustained | FALSE | FALSE | Not_TMED_Event | 3654
ARECIBO | 2021-12-02 11:31 | 2021-12-02 15:48 | 2888 | 004:17 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR ROTO EN EL TRONCAL DEL ALIMENTADOR Y SE CERRO EL INTERRUPTOR | A21120200048 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 257 | 2021-12-02 | 742216 | keep | 0 | Dec | 2021 | 0.50552 | 0.001967 | Sustained | FALSE | FALSE | Not_TMED_Event | 2888
MAYAGÃœEZ | 2021-12-02 11:51 | 2021-12-02 12:25 | 100 | 000:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | M21120100048 | New_Event | Cutout Failure | Include | Include | Equipment | 34 | 2021-12-02 | 3400 | keep | 0 | Dec | 2021 | 0.0023157 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-12-02 11:56 | 2021-12-02 12:56 | 10 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR LINEA SECUNDARIA Y CONECTORES | B21120200038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2021-12-02 | 600 | keep | 0 | Dec | 2021 | 0.00040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-12-02 12:01 | 2021-12-02 16:50 | 1 | 004:49 | P | OTRAS CAUSAS | 2 X 100 EN CORTE DE LINEA PT AVERIADO | P21120200010 | New_Event | Other Causes | Include | Include | Other | 289 | 2021-12-02 | 289 | keep | 0 | Dec | 2021 | 0.00019684 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-02 12:30 | 2021-12-02 15:11 | 30 | 002:41 | P | DESGANCHE | 1 X 50 EN AEREO PROVISIONAL SE REALIZO DESGANCHE | B21120200128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2021-12-02 | 4830 | keep | 0 | Dec | 2021 | 0.0032897 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2021-12-02 12:30 | 2021-12-02 14:07 | 27 | 001:37 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50 KVA A 4.16 KV POR ESCAPE DE ACEITE SE CAMBIA POR OTRO IGUAL CAPACIDAD Y VOLTAJE | P21120200043 | New_Event | Service Transformer Failure | Include | Include | Equipment | 97 | 2021-12-02 | 2619 | keep | 0 | Dec | 2021 | 0.0017838 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
MAYAGÃœEZ | 2021-12-02 12:38 | 2021-12-02 15:56 | 30 | 003:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | M21120200056 | New_Event | Bad Weather | Include | Include | Weather | 198 | 2021-12-02 | 5940 | keep | 0 | Dec | 2021 | 0.0040457 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-12-02 12:47 | 2021-12-02 16:47 | 20 | 004:00 | P | CABLE SOTERRADO AVERIADO | SECCIONALIZO AVERIA SOTERRADA DEL SU4B9 AL SU 5B6 Y CERRO N/O EN SU 5B6 A SU 5B6A | C21120200046 | New_Event | UG Cable Fault | Include | Include | Equipment | 240 | 2021-12-02 | 4800 | keep | 0 | Dec | 2021 | 0.0032693 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-12-02 12:52 | 2021-12-02 18:58 | 10 | 006:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN TRANSFORMADOR SE RETIRO RATON CRUZANDO BARRAS | B21120200130 | New_Event |  |  | Include | Wildlife | 366 | 2021-12-02 | 3660 | keep | 0 | Dec | 2021 | 0.0024928 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-12-02 13:01 | 2021-12-02 16:49 | 50 | 003:48 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | P21120200047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2021-12-02 | 11400 | keep | 0 | Dec | 2021 | 0.0077645 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2021-12-02 13:21 | 2021-12-02 21:22 | 7 | 008:01 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR QUEMADO DE 37.5 KVA X 37.5 KVA | R21120200019 | New_Event | Service Transformer Failure | Include | Include | Equipment | 481 | 2021-12-02 | 3367 | keep | 0 | Dec | 2021 | 0.0022932 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2021-12-02 13:22 | 2021-12-02 16:12 | 2565 | 002:50 | T | PARARRAYOS DEFECTUOSO | DISPARO REMPLAZO PARARRAYO | C21120200056 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 170 | 2021-12-02 | 436050 | keep | 0 | Dec | 2021 | 0.29699 | 0.001747 | Sustained | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2021-12-02 13:25 | 2021-12-02 13:26 | 2410 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21120200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-02 | 2410 | keep | 0 | Dec | 2021 | 0.0016414 | 0.0016414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2410
SAN JUAN | 2021-12-02 13:28 | 2021-12-02 15:02 | 10211 | 001:34 | T | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO N/O CON 1206-03 | S21120200075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2021-12-02 | 959834 | keep | 0 | Dec | 2021 | 0.65374 | 0.0069547 | Sustained | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-12-02 13:28 | 2021-12-02 14:09 | 4133 | 000:41 | T | DESGANCHE | LLEVANDO LA CARGA DEL 1204-05 SE ABRIO N/O Y SE CERRO POR CONTROL | S21120200075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 41 | 2021-12-02 | 169453 | keep | 0 | Dec | 2021 | 0.11541 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
MAYAGÃœEZ | 2021-12-02 13:33 | 2021-12-02 16:39 | 2 | 003:06 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21120200058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2021-12-02 | 372 | keep | 0 | Dec | 2021 | 0.00025337 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2021-12-02 13:37 | 2021-12-02 14:17 | 4 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR BARRA DE PEDESTAL | C21120200061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2021-12-02 | 160 | keep | 0 | Dec | 2021 | 0.00010898 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2021-12-02 13:42 | 2021-12-02 20:35 | 1 | 006:53 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B21120200134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 413 | 2021-12-02 | 413 | keep | 0 | Dec | 2021 | 0.00028129 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-02 13:46 | 2021-12-02 15:57 | 10 | 002:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21120200108 | New_Event | Secondary Wire Down | Include | Include | Equipment | 131 | 2021-12-02 | 1310 | keep | 0 | Dec | 2021 | 0.00089224 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-12-02 13:46 | 2021-12-02 14:52 | 4 | 001:06 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIO XMR PARA DESGANCHAR PEDESTAL | C21120200063 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 66 | 2021-12-02 | 264 | keep | 0 | Dec | 2021 | 0.00017981 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2021-12-02 13:52 | 2021-12-02 18:51 | 40 | 004:59 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHO Y REMPLAZO PIN | C21120200064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 299 | 2021-12-02 | 11960 | keep | 0 | Dec | 2021 | 0.0081459 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-12-02 14:00 | 2021-12-02 15:10 | 10 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21120100106 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2021-12-02 | 700 | keep | 0 | Dec | 2021 | 0.00047677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-12-02 14:23 | 2021-12-02 14:24 | 2163 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21120200053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-02 | 2163 | keep | 0 | Dec | 2021 | 0.0014732 | 0.0014732 | Momentary | FALSE | FALSE | Not_TMED_Event | 2163
HUMACAO | 2021-12-02 14:33 | 2021-12-02 14:55 | 3896 | 000:22 | T | NO SE REPORTO CAUSA | DISPARO SE VERIFICO PERSONAL FUERA | C21120200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 22 | 2021-12-02 | 85712 | keep | 0 | Dec | 2021 | 0.058378 | 0.0026535 | Sustained | FALSE | FALSE | Not_TMED_Event | 3896
BAYAMON | 2021-12-02 14:37 | 2021-12-02 20:40 | 30 | 006:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN RISER HACIA SU 5 SE REMPLAZO CAJA PRIMARIA | B21120200139 | New_Event | Cutout Failure | Include | Include | Equipment | 363 | 2021-12-02 | 10890 | keep | 0 | Dec | 2021 | 0.0074171 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2021-12-02 14:43 | 2021-12-02 18:49 | 1336 | 004:06 | T | DESGANCHE | SE RETIRO ARBOL CRUZANDO LINEAS PRIMARIAS | M21120200063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2021-12-02 | 328656 | keep | 0 | Dec | 2021 | 0.22385 | 0.00090994 | Sustained | FALSE | FALSE | Not_TMED_Event | 1336
SAN JUAN | 2021-12-02 14:56 | 2021-12-02 15:35 | 929 | 000:39 | T | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO MACHETES AVERIADOS LLEVA LA CARGA DEL 1421-04 Y 1421-03 | S21120200000 | New_Event | Switch Failure | Include | Include | Equipment | 39 | 2021-12-02 | 36231 | keep | 0 | Dec | 2021 | 0.024677 | 0.00063274 | Sustained | FALSE | FALSE | Not_TMED_Event | 929
SAN JUAN | 2021-12-02 14:56 | 2021-12-02 15:35 | 533 | 000:39 | T | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO MACHETE AVERIADO CARGA TRANSFERIDA AL 1414-04 | S21120200000 | New_Event | Switch Failure | Include | Include | Equipment | 39 | 2021-12-02 | 20787 | keep | 0 | Dec | 2021 | 0.014158 | 0.00036302 | Sustained | FALSE | FALSE | Not_TMED_Event | 533
SAN JUAN | 2021-12-02 14:56 | 2021-12-02 15:35 | 451 | 000:39 | T | DESCONECTIVO DEFECTUOSO | CARGA TRANSFERIDA AL 1414-04 SE SECCIONALIZO MACHETE AVERIADO | S21120200000 | Additional_clients | Switch Failure | Include | Include | Equipment | 39 | 2021-12-02 | 17589 | keep | 0 | Dec | 2021 | 0.01198 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-02 15:07 | 2021-12-02 17:35 | 10 | 002:28 | P | DESGANCHE | 2 X 50 EN RISER SE REALIZO DESGANCHE | B21120200144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2021-12-02 | 1480 | keep | 0 | Dec | 2021 | 0.001008 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-12-02 15:14 | 2021-12-02 18:18 | 3041 | 003:04 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADORES ROTOS EN EL TRONCAL DEL ALIMENTADOR Y SE CERRO EL INTERRUPTOR | M21120200072 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 184 | 2021-12-02 | 559544 | keep | 0 | Dec | 2021 | 0.3811 | 0.0020712 | Sustained | FALSE | FALSE | Not_TMED_Event | 3041
SAN JUAN | 2021-12-02 15:35 | 2021-12-02 17:37 | 125 | 002:02 | P | DESCONECTIVO DEFECTUOSO | SE LEVANTO CONDUCTOR Y SE REMPLAZO MACHETE AVERIADO TRABAJOS CON GOI SJ-211202-03 | S21120200068 | Partial_restoration | Switch Failure | Include | Include | Equipment | 122 | 2021-12-02 | 15250 | keep | 0 | Dec | 2021 | 0.010387 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-12-02 15:48 | 2021-12-02 20:15 | 100 | 004:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21120200004 | New_Event | Bad Weather | Include | Include | Weather | 267 | 2021-12-02 | 26700 | keep | 0 | Dec | 2021 | 0.018185 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2021-12-02 16:03 | 2021-12-02 17:22 | 1 | 001:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO DE DOS CAJAS PRIMARIAS EN TRANSFORMADOR | P21120200057 | New_Event | Cutout Failure | Include | Include | Equipment | 79 | 2021-12-02 | 79 | keep | 0 | Dec | 2021 | 5.3807e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-02 16:07 | 2021-12-02 18:02 | 60 | 001:55 | P | NO SE REPORTO CAUSA | 2 X 65 EN RISER | S21120200158 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2021-12-02 | 6900 | keep | 0 | Dec | 2021 | 0.0046996 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2021-12-02 16:11 | 2021-12-03 10:17 | 10 | 018:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C21120200112 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1086 | 2021-12-02 | 10860 | keep | 0 | Dec | 2021 | 0.0073967 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-12-02 16:34 | 2021-12-02 18:30 | 30 | 001:56 | P | DESGANCHE | 1 X 50 EN C/L | R21120200029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2021-12-02 | 3480 | keep | 0 | Dec | 2021 | 0.0023702 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-12-02 16:56 | 2021-12-02 20:28 | 5 | 003:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | M21120200088 | New_Event | Bad Weather | Include | Include | Weather | 212 | 2021-12-02 | 1060 | keep | 0 | Dec | 2021 | 0.00072196 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-12-02 17:00 | 2021-12-02 17:55 | 11 | 000:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BARRAS SECUNDARIAS | M21120200086 | New_Event | Secondary Wire Down | Include | Include | Equipment | 55 | 2021-12-02 | 605 | keep | 0 | Dec | 2021 | 0.00041206 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2021-12-02 17:04 | 2021-12-02 18:48 | 20 | 001:44 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21120200156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2021-12-02 | 2080 | keep | 0 | Dec | 2021 | 0.0014167 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-12-02 17:36 | 2021-12-02 17:37 | 1709 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21120200126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-02 | 1709 | keep | 0 | Dec | 2021 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
SAN JUAN | 2021-12-02 17:40 | 2021-12-02 17:57 | 1 | 000:17 | P | NO SE REPORTO CAUSA | 1 SMU 20 DE 25 AMP NO CAUSA | R21120200038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 17 | 2021-12-02 | 17 | keep | 0 | Dec | 2021 | 1.1579e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-12-02 17:58 | 2021-12-02 19:50 | 5 | 001:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN XMR TOMA QUEMADA | C21120200128 | New_Event | Secondary Wire Down | Include | Include | Equipment | 112 | 2021-12-02 | 560 | keep | 0 | Dec | 2021 | 0.00038141 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-12-02 18:13 | 2021-12-02 18:16 | 3718 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S21120200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-12-02 | 11154 | keep | 0 | Dec | 2021 | 0.0075969 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
CAGUAS | 2021-12-02 18:15 | 2021-12-02 20:56 | 21 | 002:41 | P | OTRAS CAUSAS | 1 X 20 EN C/L ABRIO C/L PARA HACER PUNTO DE CONEXION E INSTALAR C/L | C21120200130 | New_Event | Other Causes | Include | Include | Other | 161 | 2021-12-02 | 3381 | keep | 0 | Dec | 2021 | 0.0023028 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
VEGA BAJA | 2021-12-02 18:29 | 2021-12-03 11:07 | 20 | 016:38 | P | DESGANCHE | 1 X 40 Y 1 X 30 EN CORTES DE LINEA SE REALIZO DESGANCHE | B21120200173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 998 | 2021-12-02 | 19960 | keep | 0 | Dec | 2021 | 0.013595 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-12-02 18:31 | 2021-12-03 13:02 | 30 | 018:31 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21120200100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1111 | 2021-12-02 | 33330 | keep | 0 | Dec | 2021 | 0.022701 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2021-12-02 18:40 | 2021-12-02 20:08 | 20 | 001:28 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21120200175 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 88 | 2021-12-02 | 1760 | keep | 0 | Dec | 2021 | 0.0011987 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-12-02 18:41 | 2021-12-02 22:59 | 50 | 004:18 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | B21120200176 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 258 | 2021-12-02 | 12900 | keep | 0 | Dec | 2021 | 0.0087861 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-12-02 19:08 | 2021-12-03 10:48 | 50 | 015:40 | P | DESGANCHE | 1 X 65 EN C/L | C21120200137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 940 | 2021-12-02 | 47000 | keep | 0 | Dec | 2021 | 0.032011 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-12-02 19:15 | 2021-12-02 20:17 | 25 | 001:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR NEUTRAL SECUNDARIO | M21120200037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 62 | 2021-12-02 | 1550 | keep | 0 | Dec | 2021 | 0.0010557 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2021-12-02 19:43 | 2021-12-03 15:28 | 20 | 019:45 | P | CABLE SOTERRADO AVERIADO | CONSTRUYO AEREO PROVICIONAL DEL T56 AL T53 | C21120200143 | New_Event | UG Cable Fault | Include | Include | Equipment | 1185 | 2021-12-02 | 23700 | keep | 0 | Dec | 2021 | 0.016142 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-12-02 19:50 | 2021-12-02 22:04 | 1339 | 002:14 | T | ANIMAL U OBJETO EXTRAÃ‘O | AUTO IMPACTO POSTE Y SACO LINEAS DEL AISLADOR Y CAEN SOBRE CRUCETA | P21120200061 | New_Event |  |  | Include | Wildlife | 134 | 2021-12-02 | 179426 | keep | 0 | Dec | 2021 | 0.12221 | 0.00091199 | Sustained | FALSE | FALSE | Not_TMED_Event | 1339
BAYAMON | 2021-12-02 19:52 | 2021-12-02 21:42 | 12 | 001:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN TRANSFORMADOR SE RETIRO IGUANA CRUZANDO XMR | S21120200183 | New_Event |  |  | Include | Wildlife | 110 | 2021-12-02 | 1320 | keep | 0 | Dec | 2021 | 0.00089905 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-12-02 19:59 | 2021-12-03 10:37 | 50 | 014:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L MAL TIEMPO | C21120200145 | New_Event | Bad Weather | Include | Include | Weather | 878 | 2021-12-02 | 43900 | keep | 0 | Dec | 2021 | 0.0299 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-12-02 20:42 | 2021-12-02 20:43 | 4154 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | R21120200047 | New_Event |  |  | Include | Wildlife | 1 | 2021-12-02 | 4154 | keep | 0 | Dec | 2021 | 0.0028293 | 0.0028293 | Momentary | FALSE | FALSE | Not_TMED_Event | 4154
CANOVANAS | 2021-12-02 20:43 | 2021-12-02 22:29 | 4154 | 001:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ENCONTRARON MACHETES DEL RISER DE SALIDA DEL 2301-02 ABIERTOS POR APARENTE PERSONAL AJENO A LUMA NO SE ENCONTRO CAUSA DE OPERACION. | R21120200059 | 1st_after_momentary |  |  | Include | Wildlife | 106 | 2021-12-02 | 440324 | keep | 0 | Dec | 2021 | 0.2999 | 0.0028293 | Sustained | FALSE | FALSE | Not_TMED_Event | 4154
BARRANQUITAS | 2021-12-02 21:32 | 2021-12-03 11:24 | 40 | 013:52 | P | DESGANCHE | 1 X 40 EN C/L | C21120200149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 832 | 2021-12-02 | 33280 | keep | 0 | Dec | 2021 | 0.022667 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-12-02 21:38 | 2021-12-03 12:00 | 30 | 014:22 | P | DESGANCHE | 1 X 50 EN C/L | C21120200150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 862 | 2021-12-02 | 25860 | keep | 0 | Dec | 2021 | 0.017613 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-12-02 21:42 | 2021-12-03 12:53 | 15 | 015:11 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S21120200179 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 911 | 2021-12-02 | 13665 | keep | 0 | Dec | 2021 | 0.0093072 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2021-12-02 21:44 | 2021-12-02 22:36 | 1 | 000:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO BAJANTE SECUNDARIO EN XMR | R21120200083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 52 | 2021-12-02 | 52 | keep | 0 | Dec | 2021 | 3.5417e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2021-12-02 22:10 | 2021-12-03 18:23 | 50 | 020:13 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L REMPLAZO AISLADOR | C21120200152 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1213 | 2021-12-02 | 60650 | keep | 0 | Dec | 2021 | 0.041308 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-12-03 00:51 | 2021-12-03 00:52 | 2106 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21120300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-03 | 2106 | keep | 0 | Dec | 2021 | 0.0014344 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
MAYAGÃœEZ | 2021-12-03 01:24 | 2021-12-03 01:25 | 2999 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | M21120300000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-12-03 | 2999 | keep | 0 | Dec | 2021 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
MAYAGÃœEZ | 2021-12-03 01:25 | 2021-12-03 10:58 | 1 | 009:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA QUEMADA | M21120300016 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 573 | 2021-12-03 | 573 | keep | 0 | Dec | 2021 | 0.00039027 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-03 01:26 | 2021-12-03 01:27 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21120300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-03 | 312 | keep | 0 | Dec | 2021 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
MAYAGÃœEZ | 2021-12-03 01:46 | 2021-12-03 14:51 | 50 | 013:05 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACIONES AVERIADAS EN SU-2 | M21120300005 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 785 | 2021-12-03 | 39250 | keep | 0 | Dec | 2021 | 0.026733 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-12-03 01:53 | 2021-12-03 09:45 | 20 | 007:52 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR | B21120300023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 472 | 2021-12-03 | 9440 | keep | 0 | Dec | 2021 | 0.0064295 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-12-03 02:52 | 2021-12-03 04:49 | 844 | 001:57 | T | DESGANCHE | SE ABRIO MACHETE CARR 8838 FRENTE A CENTENIAL CEREZAL Y SE CERRO INTERRUPTOR 25% EN SERVICIO DESGANCHE | S21120300001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2021-12-03 | 98748 | keep | 0 | Dec | 2021 | 0.067257 | 0.00057484 | Sustained | FALSE | FALSE | Not_TMED_Event | 844
HUMACAO | 2021-12-03 03:01 | 2021-12-03 13:07 | 3902 | 010:06 | T | AISLADOR ROTO, PARTIDO O SAFADO | REMPLAZO AISLADORES EN DIFERENTES PUNTOS REPARO SECUNDARIA CRUZADA Y CERRO PUENTE | C21120300001 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 606 | 2021-12-03 | 2364612 | keep | 0 | Dec | 2021 | 1.6105 | 0.0026576 | Sustained | FALSE | FALSE | Not_TMED_Event | 3902
VEGA BAJA | 2021-12-03 04:41 | 2021-12-03 04:42 | 2468 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21120300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-03 | 2468 | keep | 0 | Dec | 2021 | 0.0016809 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
VEGA BAJA | 2021-12-03 04:42 | 2021-12-03 12:47 | 1 | 008:05 | P | NO SE REPORTO CAUSA | 3 X 100 EN CORTE DE LINEA | B21120300014 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 485 | 2021-12-03 | 485 | keep | 0 | Dec | 2021 | 0.00033033 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-03 04:49 | 2021-12-03 05:34 | 633 | 000:45 | P | DESGANCHE | SE ABRIO MACHETE CALLE GEORGINA CEREZAL Y SE CERRO MACHETE CARR 8838 FRENTE A CENTENIAL CEREZAL 50% EN SERVICIO DESGANCHE | S21120300001 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 45 | 2021-12-03 | 28485 | keep | 0 | Dec | 2021 | 0.019401 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-03 05:34 | 2021-12-03 07:07 | 422 | 001:33 | P | DESGANCHE | SE HIZO DESGANCHE Y SE CERRO MACHETE 100% EN SERVICIO | S21120300001 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 93 | 2021-12-03 | 39246 | keep | 0 | Dec | 2021 | 0.02673 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-03 06:15 | 2021-12-03 09:32 | 20 | 003:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21120300004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2021-12-03 | 3940 | keep | 0 | Dec | 2021 | 0.0026835 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-12-03 06:24 | 2021-12-03 12:51 | 30 | 006:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA AVERIADA NO FUNDIO | C21120300008 | New_Event | Cutout Failure | Include | Include | Equipment | 387 | 2021-12-03 | 11610 | keep | 0 | Dec | 2021 | 0.0079075 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2021-12-03 06:46 | 2021-12-03 09:46 | 50 | 003:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO VIENTOS FUERTES | A21120300004 | New_Event | Bad Weather | Include | Include | Weather | 180 | 2021-12-03 | 9000 | keep | 0 | Dec | 2021 | 0.0061299 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-12-03 06:51 | 2021-12-03 10:54 | 20 | 004:03 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21120300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2021-12-03 | 4860 | keep | 0 | Dec | 2021 | 0.0033101 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2021-12-03 07:05 | 2021-12-03 16:25 | 2 | 009:20 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | M21120300012 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 560 | 2021-12-03 | 1120 | keep | 0 | Dec | 2021 | 0.00076283 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2021-12-03 07:18 | 2021-12-03 09:56 | 60 | 002:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L Y 1 X 15 EN XMR CRUCE X AVE Y REEMPLAZO CAJA | R21120300004 | New_Event |  |  | Include | Wildlife | 158 | 2021-12-03 | 9480 | keep | 0 | Dec | 2021 | 0.0064568 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2021-12-03 07:27 | 2021-12-03 12:12 | 50 | 004:45 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21120300004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 285 | 2021-12-03 | 14250 | keep | 0 | Dec | 2021 | 0.0097056 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-12-03 07:28 | 2021-12-03 12:49 | 55 | 005:21 | P | DESGANCHE | 1 X 65 EN C/L | R21120300005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 321 | 2021-12-03 | 17655 | keep | 0 | Dec | 2021 | 0.012025 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
PONCE | 2021-12-03 07:45 | 2021-12-03 07:46 | 3718 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P21120300005 | New_Event |  |  | Include | Wildlife | 1 | 2021-12-03 | 3718 | keep | 0 | Dec | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
PONCE | 2021-12-03 07:46 | 2021-12-03 10:06 | 50 | 002:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA POR CONTACTO DE AVE | P21120300010 | 1st_after_momentary |  |  | Include | Wildlife | 140 | 2021-12-03 | 7000 | keep | 0 | Dec | 2021 | 0.0047677 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-12-03 07:46 | 2021-12-03 11:32 | 30 | 003:46 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE CERRO N/O DE T6 A T5 POR TERMINACION AVERIADA EN T5 | B21120300009 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 226 | 2021-12-03 | 6780 | keep | 0 | Dec | 2021 | 0.0046178 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-03 07:54 | 2021-12-03 07:55 | 3431 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | A21120300007 | New_Event |  |  | Include | Wildlife | 1 | 2021-12-03 | 3431 | keep | 0 | Dec | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
AGUADILLA | 2021-12-03 07:55 | 2021-12-03 13:28 | 15 | 005:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | M21120300020 | New_Event | Wire Down | Include | Include | Equipment | 333 | 2021-12-03 | 4995 | keep | 0 | Dec | 2021 | 0.0034021 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-12-03 07:55 | 2021-12-03 12:25 | 30 | 004:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | A21120300013 | 1st_after_momentary |  |  | Include | Wildlife | 270 | 2021-12-03 | 8100 | keep | 0 | Dec | 2021 | 0.0055169 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2021-12-03 07:58 | 2021-12-03 12:50 | 15 | 004:52 | P | ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR Y SE REMPLAZO POSTE | A21120300008 | New_Event | Defective Pole | Include | Include | Equipment | 292 | 2021-12-03 | 4380 | keep | 0 | Dec | 2021 | 0.0029832 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-12-03 08:21 | 2021-12-03 16:13 | 5 | 007:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A21120300011 | New_Event |  |  | Include | Wildlife | 472 | 2021-12-03 | 2360 | keep | 0 | Dec | 2021 | 0.0016074 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-12-03 08:26 | 2021-12-03 12:04 | 30 | 003:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA Y SE REALIZO DESGANCHE | B21120300010 | New_Event | Cutout Failure | Include | Include | Equipment | 218 | 2021-12-03 | 6540 | keep | 0 | Dec | 2021 | 0.0044544 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-12-03 08:39 | 2021-12-03 08:40 | 3420 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21124000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-03 | 3420 | keep | 0 | Dec | 2021 | 0.0023293 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
CANOVANAS | 2021-12-03 08:45 | 2021-12-03 09:09 | 2 | 000:24 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | R21120300012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 24 | 2021-12-03 | 48 | keep | 0 | Dec | 2021 | 3.2693e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2021-12-03 08:51 | 2021-12-03 10:08 | 85 | 001:17 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L Y 2 X 25 EN RISER NO CAUSA | R21120300013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 77 | 2021-12-03 | 6545 | keep | 0 | Dec | 2021 | 0.0044578 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
SAN JUAN | 2021-12-03 09:02 | 2021-12-03 14:06 | 4 | 005:04 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIO XMR PARA REMPLAZAR PEDESTAL | R21120300014 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 304 | 2021-12-03 | 1216 | keep | 0 | Dec | 2021 | 0.00082821 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2021-12-03 09:03 | 2021-12-03 11:32 | 10 | 002:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 XMR REMPLAZO PORTA FUSIBLE | C21120300014 | New_Event | Cutout Failure | Include | Include | Equipment | 149 | 2021-12-03 | 1490 | keep | 0 | Dec | 2021 | 0.0010148 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-03 09:11 | 2021-12-03 13:23 | 7 | 004:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA QUEMADA | M21120300038 | New_Event | Cutout Failure | Include | Include | Equipment | 252 | 2021-12-03 | 1764 | keep | 0 | Dec | 2021 | 0.0012015 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-12-03 09:17 | 2021-12-03 10:12 | 50 | 000:55 | P | AISLADOR ROTO, PARTIDO O SAFADO | REEMPLAZO DE AISLADOR | S21120300039 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 55 | 2021-12-03 | 2750 | keep | 0 | Dec | 2021 | 0.001873 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-12-03 09:21 | 2021-12-03 13:40 | 2 | 004:19 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR REQUIERE DESGANCHE | A21120300017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2021-12-03 | 518 | keep | 0 | Dec | 2021 | 0.00035281 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2021-12-03 09:25 | 2021-12-03 11:32 | 1 | 002:07 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A21120300018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 127 | 2021-12-03 | 127 | keep | 0 | Dec | 2021 | 8.6499e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-03 09:27 | 2021-12-03 15:57 | 12 | 006:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 37.5 KVA POR UNO DE IGUAL CAPACIDAD | S21120300000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 390 | 2021-12-03 | 4680 | keep | 0 | Dec | 2021 | 0.0031875 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-12-03 09:42 | 2021-12-03 12:00 | 10 | 002:18 | P | DESGANCHE | SE ABRIO TRANSFORMADOR PARA REALIZAR DESGANCHE Y LEVANTAR SECUNDARIA | S21120300023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2021-12-03 | 1380 | keep | 0 | Dec | 2021 | 0.00093991 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-12-03 09:44 | 2021-12-03 12:47 | 50 | 003:03 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21120300014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2021-12-03 | 9150 | keep | 0 | Dec | 2021 | 0.006232 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2021-12-03 09:46 | 2021-12-03 10:51 | 20 | 001:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A MACHETE | R21120300018 | New_Event | Wire Down | Include | Include | Equipment | 65 | 2021-12-03 | 1300 | keep | 0 | Dec | 2021 | 0.00088542 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-12-03 10:07 | 2021-12-03 11:12 | 1648 | 001:05 | T | ANIMAL U OBJETO EXTRAÃ‘O | SECCIONALIZO TENSOR PARTIDO POR CAMION CRUZANDO LINEA 3100 CON LA DISTRIBUCION | R21120300021 | New_Event |  |  | Include | Wildlife | 65 | 2021-12-03 | 107120 | keep | 0 | Dec | 2021 | 0.072959 | 0.0011224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1648
GUAYAMA | 2021-12-03 10:13 | 2021-12-03 12:42 | 100 | 002:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE LEVANTO ALAMBRE PRIMARIO Y NEUTRAL | P21120300017 | New_Event | Wire Down | Include | Include | Equipment | 149 | 2021-12-03 | 14900 | keep | 0 | Dec | 2021 | 0.010148 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-12-03 10:22 | 2021-12-03 21:11 | 26 | 010:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE RELOCALIZO SECUNDARIA | S21120300032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 649 | 2021-12-03 | 16874 | keep | 0 | Dec | 2021 | 0.011493 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
CAGUAS | 2021-12-03 10:34 | 2021-12-03 18:53 | 10 | 008:19 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO 15 KVA X 25 KVA | C21120300029 | New_Event | Service Transformer Failure | Include | Include | Equipment | 499 | 2021-12-03 | 4990 | keep | 0 | Dec | 2021 | 0.0033987 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-03 10:46 | 2021-12-03 12:35 | 1 | 001:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO C/L PARA RETEZAR LINEAS | C21120300034 | New_Event | Wire Down | Include | Include | Equipment | 109 | 2021-12-03 | 109 | keep | 0 | Dec | 2021 | 7.4239e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-03 10:52 | 2021-12-03 14:00 | 50 | 003:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA SE RETIRO AVE | B21120300023 | New_Event |  |  | Include | Wildlife | 188 | 2021-12-03 | 9400 | keep | 0 | Dec | 2021 | 0.0064023 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-12-03 10:57 | 2021-12-03 14:57 | 30 | 004:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | M21120300050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 240 | 2021-12-03 | 7200 | keep | 0 | Dec | 2021 | 0.0049039 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-03 11:05 | 2021-12-03 11:44 | 10 | 000:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | B21120300020 | New_Event | Secondary Wire Down | Include | Include | Equipment | 39 | 2021-12-03 | 390 | keep | 0 | Dec | 2021 | 0.00026563 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-12-03 11:10 | 2021-12-03 14:45 | 30 | 003:35 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21120300027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 215 | 2021-12-03 | 6450 | keep | 0 | Dec | 2021 | 0.0043931 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2021-12-03 11:12 | 2021-12-03 13:50 | 300 | 002:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE RETIRO TENSOR CRUZANDO LAS LINEAS IMPACTADO POR CAMION Y CERRO PUUENTE | R21120300022 | Partial_restoration |  |  | Include | Wildlife | 158 | 2021-12-03 | 47400 | keep | 0 | Dec | 2021 | 0.032284 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-03 11:17 | 2021-12-03 13:16 | 1 | 001:59 | T | NO SE REPORTO CAUSA | DISPARO SE ABRIO SU-3 A NAUTICO Y SE PASO 95% AL 1014-18 MH-11 CALLE MATIAS LEDESMA ESQ. FERNANDEZ JUNCOS | S21120300049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 119 | 2021-12-03 | 119 | keep | 0 | Dec | 2021 | 8.105e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-12-03 11:24 | 2021-12-03 13:20 | 4 | 001:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | A21120300030 | New_Event | Bad Weather | Include | Include | Weather | 116 | 2021-12-03 | 464 | keep | 0 | Dec | 2021 | 0.00031603 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-12-03 11:38 | 2021-12-03 15:00 | 10 | 003:22 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 50 KVA X 50 KVA | M21120300054 | New_Event | Service Transformer Failure | Include | Include | Equipment | 202 | 2021-12-03 | 2020 | keep | 0 | Dec | 2021 | 0.0013758 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-03 11:48 | 2021-12-03 16:21 | 44 | 004:33 | P | DESGANCHE | 1 X 65 EN C/L | C21120300039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 273 | 2021-12-03 | 12012 | keep | 0 | Dec | 2021 | 0.0081813 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
ARECIBO | 2021-12-03 11:59 | 2021-12-04 13:00 | 9 | 025:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO DE TRANSFORMADOR | A21120300032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1501 | 2021-12-03 | 13509 | keep | 0 | Dec | 2021 | 0.0092009 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2021-12-03 12:22 | 2021-12-03 12:51 | 7 | 000:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C21120300044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 29 | 2021-12-03 | 203 | keep | 0 | Dec | 2021 | 0.00013826 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-12-03 12:42 | 2021-12-03 14:25 | 30 | 001:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA SE RETIRO AVE | B21120300032 | New_Event |  |  | Include | Wildlife | 103 | 2021-12-03 | 3090 | keep | 0 | Dec | 2021 | 0.0021046 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2021-12-03 12:56 | 2021-12-03 16:25 | 6 | 003:29 | P | SECUNDARIA/DESGANCHE | ABRIO XMR PARA REPARAR DESGANCHAR Y REPARAR SECUNDARIA | R21120300034 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 209 | 2021-12-03 | 1254 | keep | 0 | Dec | 2021 | 0.00085409 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2021-12-03 13:11 | 2021-12-03 17:49 | 5 | 004:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | P21120300024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 278 | 2021-12-03 | 1390 | keep | 0 | Dec | 2021 | 0.00094672 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-12-03 13:16 | 2021-12-03 13:42 | 1 | 000:26 | P | NO SE REPORTO CAUSA | SE ABRIO EN SU-1 FTE. SIZLER Y SE CERRO 1120-10 100% EN SERVICIO | S21120300049 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 26 | 2021-12-03 | 26 | keep | 0 | Dec | 2021 | 1.7708e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-12-03 13:59 | 2021-12-03 16:25 | 1 | 002:26 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C21120300055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2021-12-03 | 146 | keep | 0 | Dec | 2021 | 9.944e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-03 14:15 | 2021-12-03 14:17 | 1297 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S21120300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-03 | 2594 | keep | 0 | Dec | 2021 | 0.0017668 | 0.00088338 | Momentary | FALSE | FALSE | Not_TMED_Event | 1297
BAYAMON | 2021-12-03 14:15 | 2021-12-03 14:17 | 451 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S21120300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-03 | 902 | keep | 0 | Dec | 2021 | 0.00061435 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
SAN JUAN | 2021-12-03 14:24 | 2021-12-03 16:12 | 50 | 001:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN C/L SE RETIRO GLOBO | S21120300069 | New_Event |  |  | Include | Wildlife | 108 | 2021-12-03 | 5400 | keep | 0 | Dec | 2021 | 0.0036779 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2021-12-03 14:40 | 2021-12-03 15:27 | 100 | 000:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 Y 1 X 50 EN C/L CRUCE POR AVE | R21120300040 | New_Event |  |  | Include | Wildlife | 47 | 2021-12-03 | 4700 | keep | 0 | Dec | 2021 | 0.0032011 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2021-12-03 14:50 | 2021-12-03 18:06 | 4 | 003:16 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZAR POSTE SECUNDARIO DE 35' MADERA AVERIADO POR POSTE 35' METAL | A21120300036 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 196 | 2021-12-03 | 784 | keep | 0 | Dec | 2021 | 0.00053398 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-12-03 14:58 | 2021-12-03 16:16 | 25 | 001:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LLEVAR CONDUCTOR AISLADOR | S21120300033 | New_Event | Wire Down | Include | Include | Equipment | 78 | 2021-12-03 | 1950 | keep | 0 | Dec | 2021 | 0.0013281 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-12-03 14:59 | 2021-12-03 18:48 | 25 | 003:49 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | S21120300081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2021-12-03 | 5725 | keep | 0 | Dec | 2021 | 0.0038993 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-12-03 15:08 | 2021-12-03 22:57 | 30 | 007:49 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21120300077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 469 | 2021-12-03 | 14070 | keep | 0 | Dec | 2021 | 0.009583 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2021-12-03 15:20 | 2021-12-03 16:33 | 21 | 001:13 | P | AISLADOR ROTO, PARTIDO O SAFADO | ABRIO C/L PARA REMPLAZAR AISLADOR ROTO Y PARARRAYO | R21120300035 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 73 | 2021-12-03 | 1533 | keep | 0 | Dec | 2021 | 0.0010441 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
VEGA BAJA | 2021-12-03 15:20 | 2021-12-03 16:36 | 8 | 001:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR PEDESTAL SECUNDARIO | B21120300042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 76 | 2021-12-03 | 608 | keep | 0 | Dec | 2021 | 0.00041411 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2021-12-03 15:27 | 2021-12-03 15:28 | 2722 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | R21120300098 | Additional_clients |  |  | Include | Wildlife | 1 | 2021-12-03 | 2722 | keep | 0 | Dec | 2021 | 0.0018539 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2021-12-03 15:28 | 2021-12-03 17:00 | 100 | 001:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 Y 1 X 50 EN C/L CRUCE POR AVE | R21120300040 | 1st_after_momentary |  |  | Include | Wildlife | 92 | 2021-12-03 | 9200 | keep | 0 | Dec | 2021 | 0.0062661 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2021-12-03 15:37 | 2021-12-03 16:56 | 50 | 001:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE POR AVE | R21120300063 | New_Event |  |  | Include | Wildlife | 79 | 2021-12-03 | 3950 | keep | 0 | Dec | 2021 | 0.0026903 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-12-03 15:50 | 2021-12-03 18:11 | 3766 | 002:21 | S | DESCONECTIVO DEFECTUOSO | REMPLAZO MACHETE QUEMADO | R21120300078 | New_Event | Switch Failure | Include | Include | Equipment | 141 | 2021-12-03 | 531006 | keep | 0 | Dec | 2021 | 0.36167 | 0.002565 | Sustained | FALSE | FALSE | Not_TMED_Event | 3766
CANOVANAS | 2021-12-03 15:50 | 2021-12-03 18:11 | 1608 | 002:21 | S | DESCONECTIVO DEFECTUOSO | REMPLAZO MACHETE QUEMADO | R21120300078 | New_Event | Switch Failure | Include | Include | Equipment | 141 | 2021-12-03 | 226728 | keep | 0 | Dec | 2021 | 0.15442 | 0.0010952 | Sustained | FALSE | FALSE | Not_TMED_Event | 1608
CANOVANAS | 2021-12-03 16:00 | 2021-12-04 21:18 | 41 | 029:18 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 3 X 140 EN RISER REMPLAZO TERMINACIONES Y REMPLAZO AISLADORES | R21120300073 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1758 | 2021-12-03 | 72078 | keep | 0 | Dec | 2021 | 0.049092 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
ARECIBO | 2021-12-03 16:02 | 2021-12-03 18:40 | 1 | 002:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN RISER LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21120300041 | New_Event | Bad Weather | Include | Include | Weather | 158 | 2021-12-03 | 158 | keep | 0 | Dec | 2021 | 0.00010761 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-12-03 16:17 | 2021-12-03 17:08 | 15 | 000:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21120300036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 51 | 2021-12-03 | 765 | keep | 0 | Dec | 2021 | 0.00052104 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-12-03 16:25 | 2021-12-03 17:05 | 26 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | S21120300078 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2021-12-03 | 1040 | keep | 0 | Dec | 2021 | 0.00070834 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
HUMACAO | 2021-12-03 16:47 | 2021-12-03 18:06 | 40 | 001:19 | P | DESGANCHE | 1 X 65 EN C/L | C21120300060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2021-12-03 | 3160 | keep | 0 | Dec | 2021 | 0.0021523 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-12-03 17:07 | 2021-12-04 10:15 | 15 | 017:08 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | S21120300097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1028 | 2021-12-03 | 15420 | keep | 0 | Dec | 2021 | 0.010502 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2021-12-03 17:08 | 2021-12-03 17:09 | 10 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO EN CAJA DE CORTE DE LINEA | P21120300025 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-12-03 | 10 | keep | 0 | Dec | 2021 | 6.811e-06 | 6.811e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-03 17:09 | 2021-12-03 20:23 | 2608 | 003:14 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO EL ALIMENTADOR | C21120300101 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 194 | 2021-12-03 | 505952 | keep | 0 | Dec | 2021 | 0.3446 | 0.0017763 | Sustained | FALSE | FALSE | Not_TMED_Event | 2608
VEGA BAJA | 2021-12-03 17:21 | 2021-12-03 19:26 | 12 | 002:05 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 75 KVA POR 75KVA | B21120300044 | New_Event | Service Transformer Failure | Include | Include | Equipment | 125 | 2021-12-03 | 1500 | keep | 0 | Dec | 2021 | 0.0010216 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-12-03 17:28 | 2021-12-05 15:55 | 100 | 046:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABRIERTO SE ABRIO CORTE DE LINEA PARA REPARAR | M21120300086 | New_Event | Wire Down | Include | Include | Equipment | 2787 | 2021-12-03 | 278700 | keep | 0 | Dec | 2021 | 0.18982 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2021-12-03 17:32 | 2021-12-03 19:14 | 6 | 001:42 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | C21120300077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 102 | 2021-12-03 | 612 | keep | 0 | Dec | 2021 | 0.00041683 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-12-03 17:51 | 2021-12-03 19:52 | 100 | 002:01 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | P21120300040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2021-12-03 | 12100 | keep | 0 | Dec | 2021 | 0.0082413 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-12-03 17:53 | 2021-12-04 11:41 | 20 | 017:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21120300087 | New_Event | Bad Weather | Include | Include | Weather | 1068 | 2021-12-03 | 21360 | keep | 0 | Dec | 2021 | 0.014548 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2021-12-03 17:54 | 2021-12-03 19:45 | 30 | 001:51 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | P21120300041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2021-12-03 | 3330 | keep | 0 | Dec | 2021 | 0.002268 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-03 17:59 | 2021-12-03 20:10 | 15 | 002:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21120300091 | New_Event | Secondary Wire Down | Include | Include | Equipment | 131 | 2021-12-03 | 1965 | keep | 0 | Dec | 2021 | 0.0013384 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-12-03 18:10 | 2021-12-03 21:02 | 1514 | 002:52 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA | B21120300057 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 172 | 2021-12-03 | 260408 | keep | 0 | Dec | 2021 | 0.17736 | 0.0010312 | Sustained | FALSE | FALSE | Not_TMED_Event | 1514
GUAYAMA | 2021-12-03 18:11 | 2021-12-03 20:30 | 75 | 002:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | P21120300043 | New_Event | Bad Weather | Include | Include | Weather | 139 | 2021-12-03 | 10425 | keep | 0 | Dec | 2021 | 0.0071004 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2021-12-03 18:24 | 2021-12-03 18:25 | 637 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR CAUSA LLEVA LA CARGA DEL 6703-03 | M21120300092 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-12-03 | 637 | keep | 0 | Dec | 2021 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
MAYAGÃœEZ | 2021-12-03 18:24 | 2021-12-03 18:25 | 1491 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | CARGA POR 6703-02 | M21120300092 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-12-03 | 1491 | keep | 0 | Dec | 2021 | 0.0010155 | 0.0010155 | Momentary | FALSE | FALSE | Not_TMED_Event | 1491
MAYAGÃœEZ | 2021-12-03 18:25 | 2021-12-03 23:25 | 80 | 005:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21120300093 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 300 | 2021-12-03 | 24000 | keep | 0 | Dec | 2021 | 0.016346 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2021-12-03 18:29 | 2021-12-03 21:57 | 100 | 003:28 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | P21120300051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2021-12-03 | 20800 | keep | 0 | Dec | 2021 | 0.014167 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-12-03 18:59 | 2021-12-03 23:20 | 6 | 004:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA Y SE REPARO BAJANTE DE CORTE DE LINEA | M21120300084 | New_Event | Cutout Failure | Include | Include | Equipment | 261 | 2021-12-03 | 1566 | keep | 0 | Dec | 2021 | 0.0010666 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-12-03 19:03 | 2021-12-03 19:45 | 10 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21120300052 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2021-12-03 | 420 | keep | 0 | Dec | 2021 | 0.00028606 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-12-03 19:09 | 2021-12-03 19:10 | 7621 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21120300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-03 | 7621 | keep | 0 | Dec | 2021 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
MAYAGÃœEZ | 2021-12-03 19:25 | 2021-12-04 10:06 | 50 | 014:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21120300099 | New_Event | Bad Weather | Include | Include | Weather | 881 | 2021-12-03 | 44050 | keep | 0 | Dec | 2021 | 0.030002 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-12-03 19:25 | 2021-12-03 19:55 | 30 | 000:30 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA EL FOREMAN INFORMO QUE NO ENCONTRO CAUSA PARA EL FUSIBLE FUNDIDO | A21120300050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 30 | 2021-12-03 | 900 | keep | 0 | Dec | 2021 | 0.00061299 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-12-03 19:36 | 2021-12-03 21:46 | 870 | 002:10 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SECCIONALIZO CONDUCTOR EN EL SUELO | C21120300091 | New_Event | Wire Down | Include | Include | Equipment | 130 | 2021-12-03 | 113100 | keep | 0 | Dec | 2021 | 0.077032 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
YAUCO | 2021-12-03 19:55 | 2021-12-04 08:54 | 80 | 012:59 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA POR DESGANCHE | P21120300057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 779 | 2021-12-03 | 62320 | keep | 0 | Dec | 2021 | 0.042446 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2021-12-03 20:07 | 2021-12-04 09:19 | 20 | 013:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE X AVE | C21120300122 | New_Event |  |  | Include | Wildlife | 792 | 2021-12-03 | 15840 | keep | 0 | Dec | 2021 | 0.010789 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-12-03 20:19 | 2021-12-03 22:29 | 63 | 002:10 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S21120300101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2021-12-03 | 8190 | keep | 0 | Dec | 2021 | 0.0055782 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
CAGUAS | 2021-12-03 20:23 | 2021-12-03 21:06 | 500 | 000:43 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO EL ALIMENTADOR | C21120300101 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 43 | 2021-12-03 | 21500 | keep | 0 | Dec | 2021 | 0.014644 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-03 21:02 | 2021-12-03 21:31 | 1136 | 000:29 | P | AISLADOR ROTO, PARTIDO O SAFADO | HACIENDO OPERACIONES DISPARO | B21120300057 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 29 | 2021-12-03 | 32944 | keep | 0 | Dec | 2021 | 0.022438 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-12-03 21:06 | 2021-12-03 21:10 | 2608 | 000:04 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO PERSONAL REALIZANDO OPERACIONES SECCIONALIZO CONDUCTOR SAFADO DE AISLADOR ABRIENDO MACHETES CARR 156 FTE JARDIN BOTANICO | C21120300091 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 4 | 2021-12-03 | 10432 | keep | 0 | Dec | 2021 | 0.0071052 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-12-03 21:10 | 2021-12-03 23:03 | 1608 | 001:53 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REPARO CONDUCTOR SAFADO DE AISLADOR Y CERRO MACHTES EN CARR 156 FTE JARDIN BOTANICO | C21120300101 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 113 | 2021-12-03 | 181704 | keep | 0 | Dec | 2021 | 0.12376 | 0.0010952 | Sustained | FALSE | FALSE | Not_TMED_Event | 1608
BAYAMON | 2021-12-03 21:31 | 2021-12-03 21:34 | 1514 | 000:03 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO NUEVAMENTE Y SE CERRO POR SCADA | B21120300057 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 3 | 2021-12-03 | 4542 | keep | 0 | Dec | 2021 | 0.0030935 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-03 21:34 | 2021-12-03 23:10 | 1136 | 001:36 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y SE NORMALIZO LA CARGA | B21120300057 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 96 | 2021-12-03 | 109056 | keep | 0 | Dec | 2021 | 0.074278 | 0.00077372 | Sustained | FALSE | FALSE | Not_TMED_Event | 1136
CAGUAS | 2021-12-03 21:46 | 2021-12-03 23:26 | 400 | 001:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR ROTO Y CERRO MACHETES | C21120300091 | Partial_restoration | Wire Down | Include | Include | Equipment | 100 | 2021-12-03 | 40000 | keep | 0 | Dec | 2021 | 0.027244 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-12-03 22:01 | 2021-12-04 09:12 | 45 | 011:11 | P | DESGANCHE | 1 X 65 EN C/L | C21120300138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 671 | 2021-12-03 | 30195 | keep | 0 | Dec | 2021 | 0.020566 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2021-12-03 22:11 | 2021-12-03 22:53 | 50 | 000:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L CRUCE X AVE | C21120300141 | New_Event |  |  | Include | Wildlife | 42 | 2021-12-03 | 2100 | keep | 0 | Dec | 2021 | 0.0014303 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-12-03 22:14 | 2021-12-04 10:32 | 10 | 012:18 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21120300111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 738 | 2021-12-03 | 7380 | keep | 0 | Dec | 2021 | 0.0050265 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-03 22:21 | 2021-12-04 10:14 | 40 | 011:53 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA Y SE RETIRO RAMA SOBRE LA LINEA | S21120300106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 713 | 2021-12-03 | 28520 | keep | 0 | Dec | 2021 | 0.019425 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-03 22:27 | 2021-12-04 14:02 | 25 | 015:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21120300107 | New_Event | Secondary Wire Down | Include | Include | Equipment | 935 | 2021-12-03 | 23375 | keep | 0 | Dec | 2021 | 0.015921 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-12-03 22:51 | 2021-12-03 23:00 | 1588 | 000:09 | S | NO SE REPORTO CAUSA | DISPARO DE LA ALTA DE SUBESTACION 1711-00 | B21120300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2021-12-03 | 14292 | keep | 0 | Dec | 2021 | 0.0097342 | 0.0010816 | Sustained | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2021-12-03 22:51 | 2021-12-03 23:00 | 723 | 000:09 | S | NO SE REPORTO CAUSA | DISPARO DE LA ALTA DE SUBESTACION 1711-00 | B21120300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2021-12-03 | 6507 | keep | 0 | Dec | 2021 | 0.0044319 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2021-12-03 22:51 | 2021-12-03 23:00 | 13 | 000:09 | S | NO SE REPORTO CAUSA | DISPARO DE LA ALTA DE SUBESTACION 1711-00 | B21120300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2021-12-03 | 117 | keep | 0 | Dec | 2021 | 7.9688e-05 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2021-12-03 22:51 | 2021-12-03 23:00 | 1976 | 000:09 | S | NO SE REPORTO CAUSA | DISPARO DE LA ALTA DE SUBESTACION 1711-00 | B21120300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2021-12-03 | 17784 | keep | 0 | Dec | 2021 | 0.012113 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
CAGUAS | 2021-12-03 22:53 | 2021-12-03 22:56 | 476 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 3054/19420 | C21120300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-03 | 1428 | keep | 0 | Dec | 2021 | 0.0009726 | 0.0003242 | Momentary | FALSE | FALSE | Not_TMED_Event | 476
CAGUAS | 2021-12-03 22:53 | 2021-12-03 22:56 | 1655 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 3054/19420 | C21120300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-03 | 4965 | keep | 0 | Dec | 2021 | 0.0033816 | 0.0011272 | Momentary | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2021-12-03 22:53 | 2021-12-03 22:56 | 361 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 3054/19420 | C21120300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-03 | 1083 | keep | 0 | Dec | 2021 | 0.00073763 | 0.00024588 | Momentary | FALSE | FALSE | Not_TMED_Event | 361
CAGUAS | 2021-12-03 22:53 | 2021-12-03 22:56 | 2842 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 3054/19420 | C21120300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-03 | 8526 | keep | 0 | Dec | 2021 | 0.005807 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
CAGUAS | 2021-12-03 22:53 | 2021-12-03 22:56 | 1702 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 CAGUAX @ JUNCOS 3054/19420 | C21120300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-03 | 5106 | keep | 0 | Dec | 2021 | 0.0034777 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2021-12-03 22:53 | 2021-12-03 22:56 | 918 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 CAGUAX @ JUNCOS 3054/19420 | C21120300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-03 | 2754 | keep | 0 | Dec | 2021 | 0.0018757 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2021-12-03 22:56 | 2021-12-04 09:45 | 50 | 010:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L CRUCE X AVE | C21120300141 | Partial_restoration |  |  | Include | Wildlife | 649 | 2021-12-03 | 32450 | keep | 0 | Dec | 2021 | 0.022102 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2021-12-03 23:04 | 2021-12-04 04:00 | 1173 | 004:56 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR. SALIDA SOTERRADA DEL ALIMENTADOR AVERIADA. SE TRANSFIERE LA CARGA AL 4006-04 | P21120300062 | New_Event | UG Cable Fault | Include | Include | Equipment | 296 | 2021-12-03 | 347208 | keep | 0 | Dec | 2021 | 0.23648 | 0.00079892 | Sustained | FALSE | FALSE | Not_TMED_Event | 1173
BAYAMON | 2021-12-03 23:15 | 2021-12-04 11:08 | 60 | 011:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO C/L TOTAL (NO FUNDIO FUSIBLE) Y SE LEVANTARON DOS CONDUCTORES DEL SUELO | B21120300088 | New_Event | Wire Down | Include | Include | Equipment | 713 | 2021-12-03 | 42780 | keep | 0 | Dec | 2021 | 0.029137 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2021-12-03 23:18 | 2021-12-04 10:43 | 60 | 011:25 | P | DESGANCHE | 1 X 65 EN C/L | R21120300102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 685 | 2021-12-03 | 41100 | keep | 0 | Dec | 2021 | 0.027993 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2021-12-03 23:32 | 2021-12-03 23:33 | 50 | 000:01 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE REPORTO CAUSA | P21120300031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-03 | 50 | keep | 0 | Dec | 2021 | 3.4055e-05 | 3.4055e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-12-04 00:04 | 2021-12-04 13:49 | 10 | 013:45 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO 50 KVA X 50 KVA | C21120400001 | New_Event | Service Transformer Failure | Include | Include | Equipment | 825 | 2021-12-04 | 8250 | keep | 0 | Dec | 2021 | 0.005619 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-12-04 00:27 | 2021-12-04 00:28 | 652 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 9201-03(SPARE) LLEVA EL 9201-01 | B21120400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-04 | 652 | keep | 0 | Dec | 2021 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2021-12-04 01:54 | 2021-12-04 09:44 | 70 | 007:50 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L Y 1 X 40 EN OTRO C/L | B21120400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 470 | 2021-12-04 | 32900 | keep | 0 | Dec | 2021 | 0.022408 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2021-12-04 02:14 | 2021-12-04 09:55 | 20 | 007:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | CERRO CAJA ABIERTA POR IMPACTO DE AUTO AL POSTE | C21120400002 | New_Event |  |  | Include | Wildlife | 461 | 2021-12-04 | 9220 | keep | 0 | Dec | 2021 | 0.0062797 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-12-04 02:35 | 2021-12-04 02:36 | 3000 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21120400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-04 | 3000 | keep | 0 | Dec | 2021 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
CANOVANAS | 2021-12-04 04:36 | 2021-12-04 04:37 | 3012 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21120400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-04 | 3012 | keep | 0 | Dec | 2021 | 0.0020515 | 0.0020515 | Momentary | FALSE | FALSE | Not_TMED_Event | 3012
MAYAGÃœEZ | 2021-12-04 04:51 | 2021-12-04 04:52 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21120400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-04 | 312 | keep | 0 | Dec | 2021 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
ARECIBO | 2021-12-04 05:23 | 2021-12-04 08:55 | 100 | 003:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO POSTE PARTIDO POR IMPACTO DE VEHICULO | A21120400005 | New_Event |  |  | Include | Wildlife | 212 | 2021-12-04 | 21200 | keep | 0 | Dec | 2021 | 0.014439 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-12-04 05:27 | 2021-12-04 05:28 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21120400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-04 | 4133 | keep | 0 | Dec | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
FAJARDO | 2021-12-04 06:19 | 2021-12-04 08:45 | 1 | 002:26 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | R21120400019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2021-12-04 | 146 | keep | 0 | Dec | 2021 | 9.944e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-04 06:51 | 2021-12-04 17:39 | 200 | 010:48 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO | M21110400013 | New_Event | Defective Pole | Include | Include | Equipment | 648 | 2021-12-04 | 129600 | keep | 0 | Dec | 2021 | 0.08827 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2021-12-04 07:20 | 2021-12-04 14:10 | 40 | 006:50 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21120400012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 410 | 2021-12-04 | 16400 | keep | 0 | Dec | 2021 | 0.01117 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-04 07:22 | 2021-12-04 09:54 | 80 | 002:32 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN C/L. SE REEMPLAZARON RIGIDO Y PIN POLE TOP | B21120400009 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 152 | 2021-12-04 | 12160 | keep | 0 | Dec | 2021 | 0.0082821 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2021-12-04 07:37 | 2021-12-04 13:01 | 30 | 005:24 | P | SECUNDARIA/ESTRUCTURA AVERIADA | 1 X 50 EN C/L REMPLAZO POSTE SECUNDARIO PARTIDO | C21120400006 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 324 | 2021-12-04 | 9720 | keep | 0 | Dec | 2021 | 0.0066202 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2021-12-04 07:53 | 2021-12-04 11:05 | 150 | 003:12 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21120400016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2021-12-04 | 28800 | keep | 0 | Dec | 2021 | 0.019616 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2021-12-04 08:00 | 2021-12-04 10:27 | 10 | 002:27 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B21120400014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 147 | 2021-12-04 | 1470 | keep | 0 | Dec | 2021 | 0.0010012 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-04 08:27 | 2021-12-04 11:38 | 35 | 003:11 | P | DESGANCHE | 1 X 65 EN C/L. SE REALIZO DESGANCHE | B21120400019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2021-12-04 | 6685 | keep | 0 | Dec | 2021 | 0.0045531 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 10:46 | 445 | 002:13 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 CARGA A TRAVES DE 1437-05 UN 60% | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 133 | 2021-12-04 | 59185 | keep | 0 | Dec | 2021 | 0.040311 | 0.00030309 | Sustained | FALSE | FALSE | Not_TMED_Event | 445
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 08:38 | 100 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-04 | 500 | keep | 0 | Dec | 2021 | 0.00034055 | 6.811e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 08:38 | 644 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-04 | 3220 | keep | 0 | Dec | 2021 | 0.0021931 | 0.00043863 | Momentary | FALSE | FALSE | Not_TMED_Event | 644
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 08:38 | 525 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-04 | 2625 | keep | 0 | Dec | 2021 | 0.0017879 | 0.00035758 | Momentary | FALSE | FALSE | Not_TMED_Event | 525
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 08:38 | 45 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-04 | 225 | keep | 0 | Dec | 2021 | 0.00015325 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 08:38 | 418 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-04 | 2090 | keep | 0 | Dec | 2021 | 0.0014235 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 10:41 | 1384 | 002:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 128 | 2021-12-04 | 177152 | keep | 0 | Dec | 2021 | 0.12066 | 0.00094264 | Sustained | FALSE | FALSE | Not_TMED_Event | 1384
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 10:41 | 869 | 002:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 128 | 2021-12-04 | 111232 | keep | 0 | Dec | 2021 | 0.07576 | 0.00059187 | Sustained | FALSE | FALSE | Not_TMED_Event | 869
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 08:38 | 1058 | 000:05 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200. CARGA PARCIAL UN 20% A TRAVES DE UNIDAD PORTATIL EN SUBESTACION VENEZUELA | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-04 | 5290 | keep | 0 | Dec | 2021 | 0.003603 | 0.0007206 | Momentary | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 11:05 | 255 | 002:32 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 152 | 2021-12-04 | 38760 | keep | 0 | Dec | 2021 | 0.026399 | 0.00017368 | Sustained | FALSE | FALSE | Not_TMED_Event | 255
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 11:05 | 928 | 002:32 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 152 | 2021-12-04 | 141056 | keep | 0 | Dec | 2021 | 0.096073 | 0.00063206 | Sustained | FALSE | FALSE | Not_TMED_Event | 928
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 11:05 | 200 | 002:32 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 152 | 2021-12-04 | 30400 | keep | 0 | Dec | 2021 | 0.020705 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 11:05 | 185 | 002:32 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 152 | 2021-12-04 | 28120 | keep | 0 | Dec | 2021 | 0.019152 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 11:05 | 73 | 002:32 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 152 | 2021-12-04 | 11096 | keep | 0 | Dec | 2021 | 0.0075574 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 08:38 | 750 | 000:05 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200. CARGA PARCIAL UN 20% A TRAVES DE UNIDAD PORTATIL EN SUBESTACION VENEZUELA | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-04 | 3750 | keep | 0 | Dec | 2021 | 0.0025541 | 0.00051082 | Momentary | FALSE | FALSE | Not_TMED_Event | 750
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 08:38 | 1290 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-04 | 6450 | keep | 0 | Dec | 2021 | 0.0043931 | 0.00087861 | Momentary | FALSE | FALSE | Not_TMED_Event | 1290
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 11:05 | 372 | 002:32 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 CARGA A TRAVES DEL 1423-04 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 152 | 2021-12-04 | 56544 | keep | 0 | Dec | 2021 | 0.038512 | 0.00025337 | Sustained | FALSE | FALSE | Not_TMED_Event | 372
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 11:05 | 732 | 002:32 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 CARGA A TRAVES DEL 1423-04 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 152 | 2021-12-04 | 111264 | keep | 0 | Dec | 2021 | 0.075781 | 0.00049856 | Sustained | FALSE | FALSE | Not_TMED_Event | 732
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 11:05 | 721 | 002:32 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 152 | 2021-12-04 | 109592 | keep | 0 | Dec | 2021 | 0.074643 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 11:05 | 325 | 002:32 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 152 | 2021-12-04 | 49400 | keep | 0 | Dec | 2021 | 0.033646 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 11:05 | 600 | 002:32 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 152 | 2021-12-04 | 91200 | keep | 0 | Dec | 2021 | 0.062116 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 11:05 | 267 | 002:32 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 152 | 2021-12-04 | 40584 | keep | 0 | Dec | 2021 | 0.027642 | 0.00018185 | Sustained | FALSE | FALSE | Not_TMED_Event | 267
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 11:05 | 621 | 002:32 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 152 | 2021-12-04 | 94392 | keep | 0 | Dec | 2021 | 0.06429 | 0.00042296 | Sustained | FALSE | FALSE | Not_TMED_Event | 621
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 10:46 | 601 | 002:13 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 133 | 2021-12-04 | 79933 | keep | 0 | Dec | 2021 | 0.054442 | 0.00040934 | Sustained | FALSE | FALSE | Not_TMED_Event | 601
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 10:46 | 640 | 002:13 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 133 | 2021-12-04 | 85120 | keep | 0 | Dec | 2021 | 0.057975 | 0.0004359 | Sustained | FALSE | FALSE | Not_TMED_Event | 640
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 10:46 | 1699 | 002:13 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 133 | 2021-12-04 | 225967 | keep | 0 | Dec | 2021 | 0.15391 | 0.0011572 | Sustained | FALSE | FALSE | Not_TMED_Event | 1699
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 10:46 | 892 | 002:13 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 133 | 2021-12-04 | 118636 | keep | 0 | Dec | 2021 | 0.080802 | 0.00060754 | Sustained | FALSE | FALSE | Not_TMED_Event | 892
SAN JUAN | 2021-12-04 08:33 | 2021-12-04 10:46 | 1066 | 002:13 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 133 | 2021-12-04 | 141778 | keep | 0 | Dec | 2021 | 0.096564 | 0.00072605 | Sustained | FALSE | FALSE | Not_TMED_Event | 1066
MAYAGÃœEZ | 2021-12-04 08:36 | 2021-12-04 16:03 | 10 | 007:27 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M21120400017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 447 | 2021-12-04 | 4470 | keep | 0 | Dec | 2021 | 0.0030445 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-04 08:41 | 2021-12-04 15:31 | 40 | 006:50 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER Y 1 SMU 20 DE 25AMP NO CAUSA | R21120400021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 410 | 2021-12-04 | 16400 | keep | 0 | Dec | 2021 | 0.01117 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-12-04 08:55 | 2021-12-04 18:58 | 50 | 010:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REMPLAZO TRANSFORMADOR DE 50 KVA POR 50 KVA Y POSTE SE INSTALO CORTE DE LINEA EN FID-33969484 | A21120400008 | Partial_restoration |  |  | Include | Wildlife | 603 | 2021-12-04 | 30150 | keep | 0 | Dec | 2021 | 0.020535 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-12-04 08:56 | 2021-12-04 09:45 | 7 | 000:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR REMPLAZO PORTAFUSIBLE PARTIDO | R21120400025 | New_Event | Cutout Failure | Include | Include | Equipment | 49 | 2021-12-04 | 343 | keep | 0 | Dec | 2021 | 0.00023362 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2021-12-04 09:11 | 2021-12-04 11:07 | 50 | 001:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21120400012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2021-12-04 | 5800 | keep | 0 | Dec | 2021 | 0.0039504 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-12-04 09:26 | 2021-12-04 12:27 | 40 | 003:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CRUCE POR AVE | C21120400009 | New_Event |  |  | Include | Wildlife | 181 | 2021-12-04 | 7240 | keep | 0 | Dec | 2021 | 0.0049311 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-04 09:31 | 2021-12-04 10:54 | 45 | 001:23 | P | DESGANCHE | SE ABRIO C/L TOTAL Y SE DESGANCHO ARBOL SOBRE LINEAS (NO FUNDIO FUSIBLE) | S21120300095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2021-12-04 | 3735 | keep | 0 | Dec | 2021 | 0.0025439 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
VEGA BAJA | 2021-12-04 09:37 | 2021-12-04 15:23 | 1 | 005:46 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21120400032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 346 | 2021-12-04 | 346 | keep | 0 | Dec | 2021 | 0.00023566 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-12-04 09:40 | 2021-12-04 11:42 | 7 | 002:02 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR CON DERRAME DE ACEITE | R21120400030 | New_Event | Service Transformer Failure | Include | Include | Equipment | 122 | 2021-12-04 | 854 | keep | 0 | Dec | 2021 | 0.00058166 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-12-04 09:45 | 2021-12-04 11:06 | 80 | 001:21 | P | NO SE REPORTO CAUSA | 1 X 140 EN C/L | B21120400034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2021-12-04 | 6480 | keep | 0 | Dec | 2021 | 0.0044135 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2021-12-04 09:45 | 2021-12-04 15:13 | 20 | 005:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN C/L LEVANTO CONDUCTOR | C21120400012 | New_Event | Wire Down | Include | Include | Equipment | 328 | 2021-12-04 | 6560 | keep | 0 | Dec | 2021 | 0.004468 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-12-04 09:46 | 2021-12-04 09:47 | 179 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21120400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-04 | 179 | keep | 0 | Dec | 2021 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
ARECIBO | 2021-12-04 09:46 | 2021-12-04 14:27 | 8 | 004:41 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 25KVA POR 37.5 KVA Y EL POSTE DE MADERA POR METAL 40' | A21120400025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 281 | 2021-12-04 | 2248 | keep | 0 | Dec | 2021 | 0.0015311 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2021-12-04 09:49 | 2021-12-04 09:50 | 1834 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21120400015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-04 | 1834 | keep | 0 | Dec | 2021 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BAYAMON | 2021-12-04 10:11 | 2021-12-04 14:15 | 15 | 004:04 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | B21120400037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 244 | 2021-12-04 | 3660 | keep | 0 | Dec | 2021 | 0.0024928 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-12-04 10:15 | 2021-12-04 10:16 | 5069 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21120400014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-04 | 5069 | keep | 0 | Dec | 2021 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
GUAYAMA | 2021-12-04 10:20 | 2021-12-04 11:32 | 9 | 001:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P21120400004 | New_Event | Secondary Wire Down | Include | Include | Equipment | 72 | 2021-12-04 | 648 | keep | 0 | Dec | 2021 | 0.00044135 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2021-12-04 10:21 | 2021-12-04 16:11 | 70 | 005:50 | P | SOBRECARGA | 1 X 80 EN CORTE DE LINEA EL UL2 TRAINED INFORMO QUE EL FUSIBLE FUNDIO POR SOBRECARGA | M21120400027 | New_Event | Trip Due To Overload | Include | Include | Other | 350 | 2021-12-04 | 24500 | keep | 0 | Dec | 2021 | 0.016687 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-12-04 10:25 | 2021-12-04 18:59 | 50 | 008:34 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21120400029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 514 | 2021-12-04 | 25700 | keep | 0 | Dec | 2021 | 0.017504 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2021-12-04 10:29 | 2021-12-04 10:32 | 1924 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P211204000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-04 | 5772 | keep | 0 | Dec | 2021 | 0.0039313 | 0.0013104 | Momentary | FALSE | FALSE | Not_TMED_Event | 1924
YAUCO | 2021-12-04 10:29 | 2021-12-04 10:32 | 968 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P211204000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-04 | 2904 | keep | 0 | Dec | 2021 | 0.0019779 | 0.0006593 | Momentary | FALSE | FALSE | Not_TMED_Event | 968
YAUCO | 2021-12-04 10:29 | 2021-12-04 10:32 | 680 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P211204000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-04 | 2040 | keep | 0 | Dec | 2021 | 0.0013894 | 0.00046314 | Momentary | FALSE | FALSE | Not_TMED_Event | 680
YAUCO | 2021-12-04 10:29 | 2021-12-04 10:32 | 2246 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P211204000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-04 | 6738 | keep | 0 | Dec | 2021 | 0.0045892 | 0.0015297 | Momentary | FALSE | FALSE | Not_TMED_Event | 2246
YAUCO | 2021-12-04 10:29 | 2021-12-04 11:10 | 2340 | 000:41 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE RETIRO ARBOL DE LA LINEA EN TRONCAL DEL ALIMENTADOR | P21120400015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 41 | 2021-12-04 | 95940 | keep | 0 | Dec | 2021 | 0.065344 | 0.0015938 | Sustained | FALSE | FALSE | Not_TMED_Event | 2340
YAUCO | 2021-12-04 10:29 | 2021-12-04 10:32 | 1475 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P211204000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-04 | 4425 | keep | 0 | Dec | 2021 | 0.0030138 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
YAUCO | 2021-12-04 10:29 | 2021-12-04 10:32 | 661 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P211204000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-04 | 1983 | keep | 0 | Dec | 2021 | 0.0013506 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
YAUCO | 2021-12-04 10:29 | 2021-12-04 10:32 | 1569 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P211204000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-04 | 4707 | keep | 0 | Dec | 2021 | 0.0032059 | 0.0010686 | Momentary | FALSE | FALSE | Not_TMED_Event | 1569
YAUCO | 2021-12-04 10:29 | 2021-12-04 10:32 | 2309 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P211204000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-04 | 6927 | keep | 0 | Dec | 2021 | 0.0047179 | 0.0015726 | Momentary | FALSE | FALSE | Not_TMED_Event | 2309
YAUCO | 2021-12-04 10:29 | 2021-12-04 10:32 | 2179 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P211204000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-04 | 6537 | keep | 0 | Dec | 2021 | 0.0044523 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
YAUCO | 2021-12-04 10:29 | 2021-12-04 10:32 | 2440 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P211204000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-04 | 7320 | keep | 0 | Dec | 2021 | 0.0049856 | 0.0016619 | Momentary | FALSE | FALSE | Not_TMED_Event | 2440
YAUCO | 2021-12-04 10:29 | 2021-12-04 10:32 | 1352 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P211204000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-04 | 4056 | keep | 0 | Dec | 2021 | 0.0027625 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
YAUCO | 2021-12-04 10:29 | 2021-12-04 10:32 | 3973 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P211204000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-04 | 11919 | keep | 0 | Dec | 2021 | 0.008118 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2021-12-04 10:29 | 2021-12-04 10:32 | 2484 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P211204000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-04 | 7452 | keep | 0 | Dec | 2021 | 0.0050755 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
SAN JUAN | 2021-12-04 11:04 | 2021-12-04 11:05 | 2179 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | R21120400040 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2021-12-04 | 2179 | keep | 0 | Dec | 2021 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
MAYAGÃœEZ | 2021-12-04 11:05 | 2021-12-04 14:22 | 25 | 003:17 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21120400033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2021-12-04 | 4925 | keep | 0 | Dec | 2021 | 0.0033544 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-12-04 11:11 | 2021-12-04 13:38 | 65 | 002:27 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21120400162 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 147 | 2021-12-04 | 9555 | keep | 0 | Dec | 2021 | 0.0065079 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2021-12-04 11:22 | 2021-12-04 15:21 | 25 | 003:59 | P | TRANSFORMADOR AVERIADO | 1 X 40 EN CORTE DE LINEA SE DEJO ABIERTO TRANSFORMADOR AVERIADO | M21120400038 | New_Event | Service Transformer Failure | Include | Include | Equipment | 239 | 2021-12-04 | 5975 | keep | 0 | Dec | 2021 | 0.0040695 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-12-04 11:23 | 2021-12-04 12:36 | 100 | 001:13 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S21120400163 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2021-12-04 | 7300 | keep | 0 | Dec | 2021 | 0.004972 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-12-04 11:29 | 2021-12-04 14:28 | 35 | 002:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN C/L LEVANTO CONDUCTOR | C21120400022 | New_Event | Wire Down | Include | Include | Equipment | 179 | 2021-12-04 | 6265 | keep | 0 | Dec | 2021 | 0.0042671 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2021-12-04 11:30 | 2021-12-04 12:44 | 15 | 001:14 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S21120400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 74 | 2021-12-04 | 1110 | keep | 0 | Dec | 2021 | 0.00075602 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-12-04 13:13 | 2021-12-04 13:14 | 776 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21120400028 | New_Event |  |  | Include | Wildlife | 1 | 2021-12-04 | 776 | keep | 0 | Dec | 2021 | 0.00052853 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
HUMACAO | 2021-12-04 13:14 | 2021-12-04 16:30 | 55 | 003:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE POR AVE | C21120400029 | 1st_after_momentary |  |  | Include | Wildlife | 196 | 2021-12-04 | 10780 | keep | 0 | Dec | 2021 | 0.0073422 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
BARRANQUITAS | 2021-12-04 13:19 | 2021-12-04 16:18 | 45 | 002:59 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO CAUSA | C21120400030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 179 | 2021-12-04 | 8055 | keep | 0 | Dec | 2021 | 0.0054862 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2021-12-04 13:22 | 2021-12-04 16:09 | 50 | 002:47 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21120400031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2021-12-04 | 8350 | keep | 0 | Dec | 2021 | 0.0056871 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2021-12-04 13:29 | 2021-12-04 15:51 | 12 | 002:22 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR DERRAME DE ACEITE 75 KVA X 75 KVA | R21120400041 | New_Event | Service Transformer Failure | Include | Include | Equipment | 142 | 2021-12-04 | 1704 | keep | 0 | Dec | 2021 | 0.0011606 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-12-04 13:30 | 2021-12-04 13:33 | 1089 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-04 | 3267 | keep | 0 | Dec | 2021 | 0.0022251 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2021-12-04 13:30 | 2021-12-04 13:33 | 3896 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-04 | 11688 | keep | 0 | Dec | 2021 | 0.0079606 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2021-12-04 13:30 | 2021-12-04 13:33 | 1467 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-04 | 4401 | keep | 0 | Dec | 2021 | 0.0029975 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
ARECIBO | 2021-12-04 13:34 | 2021-12-04 13:35 | 100 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21120400007 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-12-04 | 100 | keep | 0 | Dec | 2021 | 6.811e-05 | 6.811e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-12-04 13:42 | 2021-12-04 14:15 | 40 | 000:33 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21120400048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 33 | 2021-12-04 | 1320 | keep | 0 | Dec | 2021 | 0.00089905 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-12-04 13:44 | 2021-12-04 16:50 | 40 | 003:06 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21120400049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 186 | 2021-12-04 | 7440 | keep | 0 | Dec | 2021 | 0.0050674 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-12-04 14:05 | 2021-12-04 15:12 | 200 | 001:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21120400046 | New_Event | Bad Weather | Include | Include | Weather | 67 | 2021-12-04 | 13400 | keep | 0 | Dec | 2021 | 0.0091267 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-12-04 14:07 | 2021-12-04 14:09 | 1681 | 000:02 | T | PROTECCION DEFECTUOSA | SE CERRO POR SCADA CARGA POR BKR 1303-04 | S21120400000 | New_Event | Protection Miscoordination | Include | Include | Other | 2 | 2021-12-04 | 3362 | keep | 0 | Dec | 2021 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-12-04 14:07 | 2021-12-04 14:09 | 1598 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1303-04 SE CERRO POR SCADA LLEVA CARGA 1346-06 | S21120400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-04 | 3196 | keep | 0 | Dec | 2021 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
ARECIBO | 2021-12-04 14:08 | 2021-12-04 17:19 | 80 | 003:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | A21120400033 | New_Event | Wire Down | Include | Include | Equipment | 191 | 2021-12-04 | 15280 | keep | 0 | Dec | 2021 | 0.010407 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-12-04 14:15 | 2021-12-04 14:16 | 4176 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21120400000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-04 | 4176 | keep | 0 | Dec | 2021 | 0.0028443 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-04 14:16 | 2021-12-04 14:30 | 40 | 000:14 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21120400048 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 14 | 2021-12-04 | 560 | keep | 0 | Dec | 2021 | 0.00038141 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-12-04 14:18 | 2021-12-04 14:26 | 451 | 000:08 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S21120400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2021-12-04 | 3608 | keep | 0 | Dec | 2021 | 0.0024574 | 0.00030717 | Sustained | FALSE | FALSE | Not_TMED_Event | 451
AGUADILLA | 2021-12-04 14:19 | 2021-12-04 18:44 | 500 | 004:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA QUEMADA | M21120400050 | New_Event | Cutout Failure | Include | Include | Equipment | 265 | 2021-12-04 | 132500 | keep | 0 | Dec | 2021 | 0.090245 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CAGUAS | 2021-12-04 14:20 | 2021-12-04 15:43 | 21 | 001:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN C/L MAL TIEMPO | C21120400034 | New_Event | Bad Weather | Include | Include | Weather | 83 | 2021-12-04 | 1743 | keep | 0 | Dec | 2021 | 0.0011871 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
SAN JUAN | 2021-12-04 14:21 | 2021-12-04 15:14 | 418 | 000:53 | T | LINEA DE TRANSMISION 38KV | SE ABRIO BKR PARA RETIRAR LINEA 1000 SOBRE ALIMENTADOR | S21120400171 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 53 | 2021-12-04 | 22154 | keep | 0 | Dec | 2021 | 0.015089 | 0.0002847 | Sustained | FALSE | FALSE | Not_TMED_Event | 418
SAN JUAN | 2021-12-04 14:27 | 2021-12-04 15:00 | 20 | 000:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21120300105 | New_Event | Secondary Wire Down | Include | Include | Equipment | 33 | 2021-12-04 | 660 | keep | 0 | Dec | 2021 | 0.00044952 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-12-04 14:41 | 2021-12-04 14:42 | 1105 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR | A21120400034 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-12-04 | 1105 | keep | 0 | Dec | 2021 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
UTUADO | 2021-12-04 14:42 | 2021-12-04 19:24 | 12 | 004:42 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21120400037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 282 | 2021-12-04 | 3384 | keep | 0 | Dec | 2021 | 0.0023048 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-12-04 14:42 | 2021-12-04 18:25 | 100 | 003:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21120400036 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 223 | 2021-12-04 | 22300 | keep | 0 | Dec | 2021 | 0.015188 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-12-04 14:48 | 2021-12-04 17:33 | 5 | 002:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REMPLAZO BAJANTE SECUNDARIO Y PARARRAYO | C21120400038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 165 | 2021-12-04 | 825 | keep | 0 | Dec | 2021 | 0.0005619 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2021-12-04 14:53 | 2021-12-04 14:54 | 2926 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21120400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-04 | 2926 | keep | 0 | Dec | 2021 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
YAUCO | 2021-12-04 15:14 | 2021-12-04 16:29 | 25 | 001:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO A CAJA EN CORTE DE LINEA | P21120400029 | New_Event | Wire Down | Include | Include | Equipment | 75 | 2021-12-04 | 1875 | keep | 0 | Dec | 2021 | 0.0012771 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-12-04 15:16 | 2021-12-04 21:15 | 40 | 005:59 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M21120400063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 359 | 2021-12-04 | 14360 | keep | 0 | Dec | 2021 | 0.0097805 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-12-04 15:29 | 2021-12-04 15:30 | 1268 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1200 | M21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-04 | 1268 | keep | 0 | Dec | 2021 | 0.00086363 | 0.00086363 | Momentary | FALSE | FALSE | Not_TMED_Event | 1268
MAYAGÃœEZ | 2021-12-04 15:29 | 2021-12-04 15:30 | 2064 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1200 | M21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-04 | 2064 | keep | 0 | Dec | 2021 | 0.0014058 | 0.0014058 | Momentary | FALSE | FALSE | Not_TMED_Event | 2064
MAYAGÃœEZ | 2021-12-04 15:29 | 2021-12-04 15:30 | 3036 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1200 | M21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-04 | 3036 | keep | 0 | Dec | 2021 | 0.0020678 | 0.0020678 | Momentary | FALSE | FALSE | Not_TMED_Event | 3036
MAYAGÃœEZ | 2021-12-04 15:29 | 2021-12-04 15:30 | 2952 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1200 | M21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-04 | 2952 | keep | 0 | Dec | 2021 | 0.0020106 | 0.0020106 | Momentary | FALSE | FALSE | Not_TMED_Event | 2952
MAYAGÃœEZ | 2021-12-04 15:37 | 2021-12-04 18:06 | 1268 | 002:29 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LA LINEA 1200 Y SE ENERGIZO LA SUBESTACION | M21120400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 149 | 2021-12-04 | 188932 | keep | 0 | Dec | 2021 | 0.12868 | 0.00086363 | Sustained | FALSE | FALSE | Not_TMED_Event | 1268
MAYAGÃœEZ | 2021-12-04 15:37 | 2021-12-04 18:06 | 2064 | 002:29 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LA LINEA 1200 Y SE ENERGIZO LA SUBESTACION | M21120400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 149 | 2021-12-04 | 307536 | keep | 0 | Dec | 2021 | 0.20946 | 0.0014058 | Sustained | FALSE | FALSE | Not_TMED_Event | 2064
MAYAGÃœEZ | 2021-12-04 15:37 | 2021-12-04 18:06 | 3036 | 002:29 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LA LINEA 1200 Y SE ENERGIZO LA SUBESTACION | M21120400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 149 | 2021-12-04 | 452364 | keep | 0 | Dec | 2021 | 0.3081 | 0.0020678 | Sustained | FALSE | FALSE | Not_TMED_Event | 3036
MAYAGÃœEZ | 2021-12-04 15:37 | 2021-12-04 18:06 | 2952 | 002:29 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LA LINEA 1200 Y SE ENERGIZO LA SUBESTACION | M21120400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 149 | 2021-12-04 | 439848 | keep | 0 | Dec | 2021 | 0.29958 | 0.0020106 | Sustained | FALSE | FALSE | Not_TMED_Event | 2952
MAYAGÃœEZ | 2021-12-04 16:19 | 2021-12-04 17:30 | 1 | 001:11 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA Y 1 X 30 EN LA MEDICION SE RETIRO PARARRAYOS CRUZADO | M21120400093 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 71 | 2021-12-04 | 71 | keep | 0 | Dec | 2021 | 4.8358e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2021-12-04 16:22 | 2021-12-04 17:29 | 75 | 001:07 | P | NO SE REPORTO CAUSA | 1 X 15 EN MONTURA Y 1 X 100 EN CORTE DE LINEA NO SE REPORTO LA CAUSA | P21120400031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 67 | 2021-12-04 | 5025 | keep | 0 | Dec | 2021 | 0.0034225 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2021-12-04 16:33 | 2021-12-04 20:45 | 2179 | 004:12 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETES EN 2 PUNTOS DIFERENTES | R21120400049 | New_Event | Switch Failure | Include | Include | Equipment | 252 | 2021-12-04 | 549108 | keep | 0 | Dec | 2021 | 0.37399 | 0.0014841 | Sustained | FALSE | FALSE | Not_TMED_Event | 2179
MAYAGÃœEZ | 2021-12-04 16:35 | 2021-12-04 18:08 | 5 | 001:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BARRA SECUNDARIA AVERIADA EN PEDESTAL | M21120400042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 93 | 2021-12-04 | 465 | keep | 0 | Dec | 2021 | 0.00031671 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2021-12-04 16:36 | 2021-12-05 14:25 | 10 | 021:49 | P | NO SE REPORTO CAUSA | 1 X 5 EN TRANSFORMADOR JOURNEYMAN INFORMA NO ENCONTRO CAUSA | M21120400112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1309 | 2021-12-04 | 13090 | keep | 0 | Dec | 2021 | 0.0089155 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-12-04 16:40 | 2021-12-05 10:53 | 7 | 018:13 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | C21120400044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1093 | 2021-12-04 | 7651 | keep | 0 | Dec | 2021 | 0.0052111 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-12-04 16:42 | 2021-12-04 19:51 | 100 | 003:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINERA 1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 189 | 2021-12-04 | 18900 | keep | 0 | Dec | 2021 | 0.012873 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-12-04 16:42 | 2021-12-04 19:51 | 644 | 003:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINERA 1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 189 | 2021-12-04 | 121716 | keep | 0 | Dec | 2021 | 0.0829 | 0.00043863 | Sustained | FALSE | FALSE | Not_TMED_Event | 644
SAN JUAN | 2021-12-04 16:42 | 2021-12-04 19:51 | 525 | 003:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINERA 1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 189 | 2021-12-04 | 99225 | keep | 0 | Dec | 2021 | 0.067582 | 0.00035758 | Sustained | FALSE | FALSE | Not_TMED_Event | 525
SAN JUAN | 2021-12-04 16:42 | 2021-12-04 19:51 | 45 | 003:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINERA 1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 189 | 2021-12-04 | 8505 | keep | 0 | Dec | 2021 | 0.0057927 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2021-12-04 16:42 | 2021-12-04 19:51 | 418 | 003:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINERA 1000 | S21120400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 189 | 2021-12-04 | 79002 | keep | 0 | Dec | 2021 | 0.053808 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-12-04 16:46 | 2021-12-04 21:18 | 200 | 004:32 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN CORTE DE LINEA SE REMPLAZO DOS AISLADORES ROTOS | M21120400123 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 272 | 2021-12-04 | 54400 | keep | 0 | Dec | 2021 | 0.037052 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-12-04 16:48 | 2021-12-05 12:00 | 100 | 019:12 | P | ESTRUCTURA AVERIADA | 3 X 65 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO | M21120400125 | New_Event | Defective Pole | Include | Include | Equipment | 1152 | 2021-12-04 | 115200 | keep | 0 | Dec | 2021 | 0.078462 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-12-04 17:09 | 2021-12-04 22:32 | 200 | 005:23 | P | DESGANCHE | 3 X 100 EN C/L SE REALIZO DESGANCHE | B21120400064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 323 | 2021-12-04 | 64600 | keep | 0 | Dec | 2021 | 0.043999 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-12-04 17:10 | 2021-12-04 18:28 | 15 | 001:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21120400054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 78 | 2021-12-04 | 1170 | keep | 0 | Dec | 2021 | 0.00079688 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-12-04 17:21 | 2021-12-04 17:22 | 3420 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21120400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-04 | 3420 | keep | 0 | Dec | 2021 | 0.0023293 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
CANOVANAS | 2021-12-04 17:26 | 2021-12-05 12:13 | 20 | 018:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIAS | R21120400068 | New_Event | Bad Weather | Include | Include | Weather | 1127 | 2021-12-04 | 22540 | keep | 0 | Dec | 2021 | 0.015352 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-12-04 17:35 | 2021-12-04 21:46 | 100 | 004:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE DE LINEA A CAJA | R21120400070 | New_Event | Wire Down | Include | Include | Equipment | 251 | 2021-12-04 | 25100 | keep | 0 | Dec | 2021 | 0.017095 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-12-04 17:39 | 2021-12-04 18:43 | 20 | 001:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21120400058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 64 | 2021-12-04 | 1280 | keep | 0 | Dec | 2021 | 0.0008718 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-12-04 17:39 | 2021-12-04 23:53 | 2999 | 006:14 | T | DESGANCHE | DISPARO DEL INTERRUPTOR SE RETIRO BAMBUS CRUZANDO LAS TRES FASES DEL ALIMENTADOR | M21120400144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 374 | 2021-12-04 | 1121626 | keep | 0 | Dec | 2021 | 0.76393 | 0.0020426 | Sustained | FALSE | FALSE | Not_TMED_Event | 2999
ARECIBO | 2021-12-04 17:40 | 2021-12-04 21:12 | 50 | 003:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DE AISLADOR | A21120400043 | New_Event | Wire Down | Include | Include | Equipment | 212 | 2021-12-04 | 10600 | keep | 0 | Dec | 2021 | 0.0072196 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-12-04 17:44 | 2021-12-04 17:45 | 4381 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21120400149 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-04 | 4381 | keep | 0 | Dec | 2021 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
HUMACAO | 2021-12-04 17:55 | 2021-12-05 10:54 | 50 | 016:59 | P | DESGANCHE | 1 X 50 EN C/L | C21120400048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1019 | 2021-12-04 | 50950 | keep | 0 | Dec | 2021 | 0.034702 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-12-04 17:55 | 2021-12-05 17:55 | 80 | 024:00 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PARARRAYO DEFECTUOSO | M21120400159 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1440 | 2021-12-04 | 115200 | keep | 0 | Dec | 2021 | 0.078462 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2021-12-04 18:06 | 2021-12-04 21:47 | 50 | 003:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21120400045 | New_Event | Bad Weather | Include | Include | Weather | 221 | 2021-12-04 | 11050 | keep | 0 | Dec | 2021 | 0.0075261 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-04 18:08 | 2021-12-04 21:01 | 40 | 002:53 | P | NO SE REPORTO CAUSA | 1 X 25 EN PROVISIONAL AEREO | B21120400066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 173 | 2021-12-04 | 6920 | keep | 0 | Dec | 2021 | 0.0047132 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-12-04 18:26 | 2021-12-05 15:38 | 60 | 021:12 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA INFORMA JOURNAYMAN REQUIRERE DESGANCHE | M21120400179 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1272 | 2021-12-04 | 76320 | keep | 0 | Dec | 2021 | 0.051981 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2021-12-04 18:37 | 2021-12-05 10:47 | 8 | 016:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C21120400053 | New_Event | Secondary Wire Down | Include | Include | Equipment | 970 | 2021-12-04 | 7760 | keep | 0 | Dec | 2021 | 0.0052853 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-12-04 18:38 | 2021-12-05 09:07 | 25 | 014:29 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S21120400195 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 869 | 2021-12-04 | 21725 | keep | 0 | Dec | 2021 | 0.014797 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-12-04 18:49 | 2021-12-04 23:09 | 32 | 004:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO PRIMARIA Y SE CERRO C/L | S21120400198 | New_Event | Wire Down | Include | Include | Equipment | 260 | 2021-12-04 | 8320 | keep | 0 | Dec | 2021 | 0.0056667 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
SAN JUAN | 2021-12-04 18:52 | 2021-12-04 18:54 | 1384 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-12-04 | 2768 | keep | 0 | Dec | 2021 | 0.0018853 | 0.00094264 | Momentary | FALSE | FALSE | Not_TMED_Event | 1384
SAN JUAN | 2021-12-04 18:52 | 2021-12-04 18:54 | 869 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 | S21120400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-12-04 | 1738 | keep | 0 | Dec | 2021 | 0.0011837 | 0.00059187 | Momentary | FALSE | FALSE | Not_TMED_Event | 869
FAJARDO | 2021-12-04 18:58 | 2021-12-04 19:56 | 7 | 000:58 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | R21120400083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 58 | 2021-12-04 | 406 | keep | 0 | Dec | 2021 | 0.00027652 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-12-04 19:00 | 2021-12-04 19:01 | 4089 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21120400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-04 | 4089 | keep | 0 | Dec | 2021 | 0.002785 | 0.002785 | Momentary | FALSE | FALSE | Not_TMED_Event | 4089
UTUADO | 2021-12-04 19:13 | 2021-12-05 12:08 | 200 | 016:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 Y 1 X 100 EN CORTE DE LINEA SE REMPLAZO UNA CAJA PRIMARIA AVERIADA DE 100AMP | A21120400052 | New_Event | Cutout Failure | Include | Include | Equipment | 1015 | 2021-12-04 | 203000 | keep | 0 | Dec | 2021 | 0.13826 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2021-12-04 19:27 | 2021-12-05 18:07 | 10 | 022:40 | P | NO SE REPORTO CAUSA | 1 X 30 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | P21120400037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1360 | 2021-12-04 | 13600 | keep | 0 | Dec | 2021 | 0.0092629 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-04 19:35 | 2021-12-05 09:30 | 10 | 013:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21120400056 | New_Event | Bad Weather | Include | Include | Weather | 835 | 2021-12-04 | 8350 | keep | 0 | Dec | 2021 | 0.0056871 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-04 19:48 | 2021-12-05 07:49 | 1 | 012:01 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S21120400206 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 721 | 2021-12-04 | 721 | keep | 0 | Dec | 2021 | 0.00049107 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-12-04 19:54 | 2021-12-04 22:25 | 60 | 002:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | R21120400099 | New_Event |  |  | Include | Wildlife | 151 | 2021-12-04 | 9060 | keep | 0 | Dec | 2021 | 0.0061707 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-12-04 20:05 | 2021-12-05 08:22 | 50 | 012:17 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21120500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 737 | 2021-12-04 | 36850 | keep | 0 | Dec | 2021 | 0.025098 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-04 20:11 | 2021-12-04 21:44 | 60 | 001:33 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | B21120400074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2021-12-04 | 5580 | keep | 0 | Dec | 2021 | 0.0038005 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2021-12-04 20:24 | 2021-12-04 20:26 | 2126 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA | C21120400056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-04 | 4252 | keep | 0 | Dec | 2021 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
MAYAGÃœEZ | 2021-12-04 20:31 | 2021-12-05 16:05 | 200 | 019:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | M21120400219 | New_Event |  |  | Include | Wildlife | 1174 | 2021-12-04 | 234800 | keep | 0 | Dec | 2021 | 0.15992 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-12-04 20:45 | 2021-12-04 22:36 | 500 | 001:51 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZARON MACHETES Y CAJAS PRIMARIAS QUEMADAS | R21120400049 | Partial_restoration | Switch Failure | Include | Include | Equipment | 111 | 2021-12-04 | 55500 | keep | 0 | Dec | 2021 | 0.037801 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-12-04 21:09 | 2021-12-04 21:10 | 4702 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21120400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-04 | 4702 | keep | 0 | Dec | 2021 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
ARECIBO | 2021-12-04 21:21 | 2021-12-05 11:30 | 10 | 014:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 10 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO | A21120400066 | New_Event | Wire Down | Include | Include | Equipment | 849 | 2021-12-04 | 8490 | keep | 0 | Dec | 2021 | 0.0057825 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-04 21:25 | 2021-12-05 09:39 | 40 | 012:14 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21120400077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 734 | 2021-12-04 | 29360 | keep | 0 | Dec | 2021 | 0.019997 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-12-04 21:31 | 2021-12-05 16:05 | 60 | 018:34 | P | DESGANCHE | 3 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21120400227 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1114 | 2021-12-04 | 66840 | keep | 0 | Dec | 2021 | 0.045524 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-12-04 21:51 | 2021-12-05 12:33 | 60 | 014:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO CONDUCTOR | B21120400084 | New_Event | Wire Down | Include | Include | Equipment | 882 | 2021-12-04 | 52920 | keep | 0 | Dec | 2021 | 0.036044 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-12-04 21:59 | 2021-12-05 11:21 | 60 | 013:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21120400068 | New_Event | Bad Weather | Include | Include | Weather | 802 | 2021-12-04 | 48120 | keep | 0 | Dec | 2021 | 0.032774 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2021-12-04 22:09 | 2021-12-04 22:10 | 2708 | 000:01 | T | DESGANCHE | RECIERRE | R21120400137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-04 | 2708 | keep | 0 | Dec | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2021-12-04 22:10 | 2021-12-04 22:51 | 130 | 000:41 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA RETIRO BAMBUAS SOBRE LINEAS | R21120400143 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 41 | 2021-12-04 | 5330 | keep | 0 | Dec | 2021 | 0.0036302 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
CAGUAS | 2021-12-04 23:09 | 2021-12-05 14:40 | 40 | 015:31 | P | DESGANCHE | 1 X 40 EN C/L | C21120400062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 931 | 2021-12-04 | 37240 | keep | 0 | Dec | 2021 | 0.025364 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-12-04 23:11 | 2021-12-05 11:22 | 35 | 012:11 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S21120400210 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 731 | 2021-12-04 | 25585 | keep | 0 | Dec | 2021 | 0.017426 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2021-12-04 23:16 | 2021-12-04 23:17 | 2926 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21120400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-04 | 2926 | keep | 0 | Dec | 2021 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
CANOVANAS | 2021-12-04 23:32 | 2021-12-05 11:21 | 70 | 011:49 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21120400161 | New_Event | Vegetation Contact | Include | Include | Vegetation | 709 | 2021-12-04 | 49630 | keep | 0 | Dec | 2021 | 0.033803 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-12-04 23:53 | 2021-12-05 02:28 | 200 | 002:35 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO | M21110400013 | New_Event | Defective Pole | Include | Include | Equipment | 155 | 2021-12-04 | 31000 | keep | 0 | Dec | 2021 | 0.021114 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2021-12-05 00:14 | 2021-12-05 00:15 | 436 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO EL RESTO DE LA CARGA ESTA X 3015-07 | C21120500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-05 | 436 | keep | 0 | Dec | 2021 | 0.00029696 | 0.00029696 | Momentary | FALSE | FALSE | Not_TMED_Event | 436
SAN JUAN | 2021-12-05 00:56 | 2021-12-05 14:33 | 2 | 013:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN SECUNDARIA | R21120500001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 817 | 2021-12-05 | 1634 | keep | 0 | Dec | 2021 | 0.0011129 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2021-12-05 01:39 | 2021-12-05 09:25 | 25 | 007:46 | P | DESGANCHE | 1 X 50 EN C/L | C21120500001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 466 | 2021-12-05 | 11650 | keep | 0 | Dec | 2021 | 0.0079348 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-12-05 01:49 | 2021-12-05 09:24 | 21 | 007:35 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S21120500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 455 | 2021-12-05 | 9555 | keep | 0 | Dec | 2021 | 0.0065079 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
VEGA BAJA | 2021-12-05 01:49 | 2021-12-05 01:50 | 27 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21120500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-05 | 27 | keep | 0 | Dec | 2021 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
HUMACAO | 2021-12-05 02:19 | 2021-12-05 10:50 | 7 | 008:31 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHO | C21120500002 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 511 | 2021-12-05 | 3577 | keep | 0 | Dec | 2021 | 0.0024363 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-12-05 02:34 | 2021-12-05 09:25 | 50 | 006:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO EN LINEA PRIMARIA | A21120500003 | New_Event | Wire Down | Include | Include | Equipment | 411 | 2021-12-05 | 20550 | keep | 0 | Dec | 2021 | 0.013997 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-12-05 02:46 | 2021-12-05 10:27 | 60 | 007:41 | P | SOBRECARGA | 1 X 65 EN RISER REPORTARON QUE EL FUSIBLE FUNDIO POR SOBRECARGA | A21120500004 | New_Event | Trip Due To Overload | Include | Include | Other | 461 | 2021-12-05 | 27660 | keep | 0 | Dec | 2021 | 0.018839 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2021-12-05 03:16 | 2021-12-05 10:27 | 80 | 007:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIAS | R21120500003 | New_Event | Bad Weather | Include | Include | Weather | 431 | 2021-12-05 | 34480 | keep | 0 | Dec | 2021 | 0.023484 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2021-12-05 04:02 | 2021-12-05 11:43 | 574 | 007:41 | T | NO SE REPORTO CAUSA | CARGA POR 7301-04 | M21120500010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 461 | 2021-12-05 | 264614 | keep | 0 | Dec | 2021 | 0.18023 | 0.00039095 | Sustained | FALSE | FALSE | Not_TMED_Event | 574
AGUADILLA | 2021-12-05 04:02 | 2021-12-05 11:43 | 1428 | 007:41 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVA LA CARGA DEL 7301-01 SE CERRO MANUAL POR PERSONAL DE SUBESTACIONES | M21120500010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 461 | 2021-12-05 | 658308 | keep | 0 | Dec | 2021 | 0.44837 | 0.0009726 | Sustained | FALSE | FALSE | Not_TMED_Event | 1428
BAYAMON | 2021-12-05 06:21 | 2021-12-05 06:22 | 3511 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21120500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-05 | 3511 | keep | 0 | Dec | 2021 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
SAN JUAN | 2021-12-05 06:23 | 2021-12-05 14:16 | 70 | 007:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZARON CAJA PRIMARIA | R21120500006 | New_Event | Cutout Failure | Include | Include | Equipment | 473 | 2021-12-05 | 33110 | keep | 0 | Dec | 2021 | 0.022551 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2021-12-05 06:26 | 2021-12-05 06:27 | 27 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21120500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-05 | 27 | keep | 0 | Dec | 2021 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
HUMACAO | 2021-12-05 06:45 | 2021-12-05 06:46 | 551 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21120500004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-05 | 551 | keep | 0 | Dec | 2021 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
CAGUAS | 2021-12-05 06:45 | 2021-12-05 10:49 | 65 | 004:04 | P | DESGANCHE | 1 X 65 EN C/L | C21120500003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 244 | 2021-12-05 | 15860 | keep | 0 | Dec | 2021 | 0.010802 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2021-12-05 06:54 | 2021-12-05 10:04 | 30 | 003:10 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | B21120500006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 190 | 2021-12-05 | 5700 | keep | 0 | Dec | 2021 | 0.0038822 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-05 07:24 | 2021-12-05 12:34 | 30 | 005:10 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21120500009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 310 | 2021-12-05 | 9300 | keep | 0 | Dec | 2021 | 0.0063342 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-05 07:30 | 2021-12-05 14:32 | 7 | 007:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21120500012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 422 | 2021-12-05 | 2954 | keep | 0 | Dec | 2021 | 0.002012 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-12-05 07:36 | 2021-12-05 07:37 | 1615 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S21120500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-05 | 1615 | keep | 0 | Dec | 2021 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
SAN JUAN | 2021-12-05 07:39 | 2021-12-05 07:40 | 1447 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA A CARGA 1419-09 Y 1419-12 | S21120500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-05 | 1447 | keep | 0 | Dec | 2021 | 0.00098555 | 0.00098555 | Momentary | FALSE | FALSE | Not_TMED_Event | 1447
SAN JUAN | 2021-12-05 07:39 | 2021-12-05 07:40 | 266 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1112-04 | S21120500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-05 | 266 | keep | 0 | Dec | 2021 | 0.00018117 | 0.00018117 | Momentary | FALSE | FALSE | Not_TMED_Event | 266
SAN JUAN | 2021-12-05 07:39 | 2021-12-05 07:40 | 73 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1112-04 | S21120520000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-05 | 73 | keep | 0 | Dec | 2021 | 4.972e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
BAYAMON | 2021-12-05 07:40 | 2021-12-05 09:46 | 80 | 002:06 | P | DESGANCHE | 1 X 65 Y 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21120500014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2021-12-05 | 10080 | keep | 0 | Dec | 2021 | 0.0068654 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-12-05 07:49 | 2021-12-05 08:25 | 1681 | 000:36 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR BKR 1303-04 | S21120500000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 36 | 2021-12-05 | 60516 | keep | 0 | Dec | 2021 | 0.041217 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-05 07:49 | 2021-12-05 08:25 | 1598 | 000:36 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR BKR 1303-04 | S21120500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 36 | 2021-12-05 | 57528 | keep | 0 | Dec | 2021 | 0.039182 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2021-12-05 07:50 | 2021-12-05 11:44 | 200 | 003:54 | P | DESCONECTIVO DEFECTUOSO | CONECTOR DE MACHETE QUEMADO | R21120500014 | New_Event | Switch Failure | Include | Include | Equipment | 234 | 2021-12-05 | 46800 | keep | 0 | Dec | 2021 | 0.031875 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2021-12-05 07:57 | 2021-12-05 07:58 | 1712 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P211205000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-05 | 1712 | keep | 0 | Dec | 2021 | 0.001166 | 0.001166 | Momentary | FALSE | FALSE | Not_TMED_Event | 1712
PONCE | 2021-12-05 07:57 | 2021-12-05 07:58 | 7 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P211205000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-05 | 7 | keep | 0 | Dec | 2021 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2021-12-05 08:38 | 2021-12-05 08:39 | 1712 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P211205000XX | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-05 | 1712 | keep | 0 | Dec | 2021 | 0.001166 | 0.001166 | Momentary | FALSE | FALSE | Not_TMED_Event | 1712
PONCE | 2021-12-05 08:38 | 2021-12-05 08:39 | 7 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P211205000XX | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-05 | 7 | keep | 0 | Dec | 2021 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2021-12-05 08:39 | 2021-12-06 11:59 | 4 | 027:20 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE DESCONTAMINO PEDESTAL SOTERRADO | R21120500019 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 1640 | 2021-12-05 | 6560 | keep | 0 | Dec | 2021 | 0.004468 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-12-05 08:50 | 2021-12-05 12:40 | 75 | 003:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA | S21120500032 | New_Event | Cutout Failure | Include | Include | Equipment | 230 | 2021-12-05 | 17250 | keep | 0 | Dec | 2021 | 0.011749 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2021-12-05 08:58 | 2021-12-05 12:05 | 75 | 003:07 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21120500020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 187 | 2021-12-05 | 14025 | keep | 0 | Dec | 2021 | 0.0095524 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2021-12-05 09:04 | 2021-12-05 11:39 | 1 | 002:35 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S21120500034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 155 | 2021-12-05 | 155 | keep | 0 | Dec | 2021 | 0.00010557 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-12-05 09:16 | 2021-12-05 12:00 | 30 | 002:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA | A21120500018 | New_Event | Wire Down | Include | Include | Equipment | 164 | 2021-12-05 | 4920 | keep | 0 | Dec | 2021 | 0.003351 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2021-12-05 09:19 | 2021-12-05 11:29 | 1 | 002:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR AUTO IMPACTO POSTE | R21120500031 | New_Event |  |  | Include | Wildlife | 130 | 2021-12-05 | 130 | keep | 0 | Dec | 2021 | 8.8542e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-12-05 09:23 | 2021-12-05 12:26 | 70 | 003:03 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21120500033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2021-12-05 | 12810 | keep | 0 | Dec | 2021 | 0.0087248 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2021-12-05 09:30 | 2021-12-05 10:13 | 15 | 000:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | M21120400183 | New_Event | Secondary Wire Down | Include | Include | Equipment | 43 | 2021-12-05 | 645 | keep | 0 | Dec | 2021 | 0.00043931 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-12-05 09:45 | 2021-12-05 09:57 | 10 | 000:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIAS | R21120500037 | New_Event | Bad Weather | Include | Include | Weather | 12 | 2021-12-05 | 120 | keep | 0 | Dec | 2021 | 8.1731e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-12-05 09:46 | 2021-12-05 09:47 | 1250 | 000:01 | T | DESGANCHE | RECIERRE | C21120500018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-05 | 1250 | keep | 0 | Dec | 2021 | 0.00085137 | 0.00085137 | Momentary | FALSE | FALSE | Not_TMED_Event | 1250
SAN JUAN | 2021-12-05 09:47 | 2021-12-05 20:40 | 100 | 010:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 Y 1 X 25 EN SU SE REEMPLAZO BASE QUEMADA SMU 20 | R21120500039 | New_Event | Cutout Failure | Include | Include | Equipment | 653 | 2021-12-05 | 65300 | keep | 0 | Dec | 2021 | 0.044476 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-12-05 09:47 | 2021-12-05 12:27 | 40 | 002:40 | P | DESGANCHE | 1 X 80 EN C/L | C21120500019 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 160 | 2021-12-05 | 6400 | keep | 0 | Dec | 2021 | 0.004359 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-12-05 09:52 | 2021-12-05 12:02 | 9 | 002:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21120500002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 130 | 2021-12-05 | 1170 | keep | 0 | Dec | 2021 | 0.00079688 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2021-12-05 10:17 | 2021-12-05 14:46 | 3 | 004:29 | P | SECUNDARIA/DESGANCHE | 1 X 5 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | M21120500027 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 269 | 2021-12-05 | 807 | keep | 0 | Dec | 2021 | 0.00054964 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-12-05 10:27 | 2021-12-05 18:12 | 59 | 007:45 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 50 EN RISER SE REEMPLAZO TERMINACION QUEMADA | R21120500047 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 465 | 2021-12-05 | 27435 | keep | 0 | Dec | 2021 | 0.018686 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
SAN JUAN | 2021-12-05 10:30 | 2021-12-05 10:31 | 15 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2112050000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-05 | 15 | keep | 0 | Dec | 2021 | 1.0216e-05 | 1.0216e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-12-05 10:32 | 2021-12-05 10:33 | 2203 | 000:01 | T | DESGANCHE | RECIERRE | C21120500020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-05 | 2203 | keep | 0 | Dec | 2021 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
CAGUAS | 2021-12-05 10:33 | 2021-12-05 15:22 | 200 | 004:49 | P | DESGANCHE | 1 X 100 Y 3 X 80 EN DIFERENTES C/L | C21120500021 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 289 | 2021-12-05 | 57800 | keep | 0 | Dec | 2021 | 0.039367 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2021-12-05 10:42 | 2021-12-05 14:11 | 4 | 003:29 | P | OTRAS CAUSAS | 1 X 30 EN CORTE DE LINEA PROBLEMA DEL CLIENTE | R21120500049 | New_Event | Other Causes | Include | Include | Other | 209 | 2021-12-05 | 836 | keep | 0 | Dec | 2021 | 0.0005694 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2021-12-05 10:59 | 2021-12-06 12:35 | 20 | 025:36 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 EN CORTE DE LINEA REEMPLAZO AISLADOR | C21120500053 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1536 | 2021-12-05 | 30720 | keep | 0 | Dec | 2021 | 0.020923 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-12-05 11:01 | 2021-12-05 14:28 | 4 | 003:27 | P | DESGANCHE | 1 X 100 EN PROVISIONAL AEREO SE REALIZO DESGANCHE | B21120500029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2021-12-05 | 828 | keep | 0 | Dec | 2021 | 0.00056395 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2021-12-05 11:08 | 2021-12-05 11:46 | 6 | 000:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C21120500023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 38 | 2021-12-05 | 228 | keep | 0 | Dec | 2021 | 0.00015529 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-12-05 11:09 | 2021-12-05 12:28 | 1 | 001:19 | P | SECUNDARIA/DESGANCHE | 2 X 20 EN XMR DESGANCHO | C21120500024 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 79 | 2021-12-05 | 79 | keep | 0 | Dec | 2021 | 5.3807e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-05 11:25 | 2021-12-05 14:31 | 50 | 003:06 | P | NO SE REPORTO CAUSA | 2 X 40 EN CORTE DE LINEA | S21120500038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 186 | 2021-12-05 | 9300 | keep | 0 | Dec | 2021 | 0.0063342 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-12-05 11:42 | 2021-12-06 09:23 | 50 | 021:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA QUEMADA | C21120500082 | New_Event | Cutout Failure | Include | Include | Equipment | 1301 | 2021-12-05 | 65050 | keep | 0 | Dec | 2021 | 0.044305 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-12-05 11:44 | 2021-12-05 11:45 | 200 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO SE VERIFICO PERSONAL FUERA | R21120500068 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-12-05 | 200 | keep | 0 | Dec | 2021 | 0.00013622 | 0.00013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-12-05 11:45 | 2021-12-05 13:10 | 200 | 001:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISCOS PARTIDOS Y CONECTORES DE MACHETES QUEMADOS | R21120500014 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 85 | 2021-12-05 | 17000 | keep | 0 | Dec | 2021 | 0.011579 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2021-12-05 12:00 | 2021-12-05 12:41 | 13 | 000:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | M21120400051 | New_Event | Secondary Wire Down | Include | Include | Equipment | 41 | 2021-12-05 | 533 | keep | 0 | Dec | 2021 | 0.00036302 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CAGUAS | 2021-12-05 12:24 | 2021-12-05 12:26 | 1403 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA | C21120500031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-05 | 2806 | keep | 0 | Dec | 2021 | 0.0019112 | 0.00095558 | Momentary | FALSE | FALSE | Not_TMED_Event | 1403
AGUADILLA | 2021-12-05 12:31 | 2021-12-05 15:36 | 30 | 003:05 | P | DESGANCHE | 1 X 100 Y 2 X 50 EN CORTES DE LINEA DISTINTOS SE RETIRO RAMAS SOBRE LAS LINEAS | M21120500041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2021-12-05 | 5550 | keep | 0 | Dec | 2021 | 0.0037801 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-12-05 12:33 | 2021-12-05 19:24 | 45 | 006:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L REMPLAZO CAJA QUEMADA | C21120500032 | New_Event | Cutout Failure | Include | Include | Equipment | 411 | 2021-12-05 | 18495 | keep | 0 | Dec | 2021 | 0.012597 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2021-12-05 12:43 | 2021-12-05 17:19 | 2 | 004:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN SECUNDARIA | R21120500077 | New_Event | Secondary Wire Down | Include | Include | Equipment | 276 | 2021-12-05 | 552 | keep | 0 | Dec | 2021 | 0.00037596 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2021-12-05 12:50 | 2021-12-05 13:42 | 2 | 000:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | M21120300045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 52 | 2021-12-05 | 104 | keep | 0 | Dec | 2021 | 7.0834e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2021-12-05 12:54 | 2021-12-05 14:08 | 30 | 001:14 | P | CABLE SOTERRADO AVERIADO | 1 X 25 EN RISER SE SECCIONALIZO TRAMO SOTERRADO | B21120500033 | New_Event | UG Cable Fault | Include | Include | Equipment | 74 | 2021-12-05 | 2220 | keep | 0 | Dec | 2021 | 0.001512 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-12-05 13:10 | 2021-12-05 13:12 | 200 | 000:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO SE VERIFICO PERSONAL FUERA | R21120500080 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2021-12-05 | 400 | keep | 0 | Dec | 2021 | 0.00027244 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-05 13:12 | 2021-12-05 13:50 | 200 | 000:38 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZARON DISCOS Y CONECTORES DE MACHETES QUEMADOS | R21120500014 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 38 | 2021-12-05 | 7600 | keep | 0 | Dec | 2021 | 0.0051763 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-12-05 13:18 | 2021-12-05 17:10 | 65 | 003:52 | P | NO SE REPORTO CAUSA | 2 X 65 EN C/L | S21120500047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 232 | 2021-12-05 | 15080 | keep | 0 | Dec | 2021 | 0.010271 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2021-12-05 13:20 | 2021-12-05 13:21 | 5961 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 95% DE LA CARGA DEL 1717-02 | B21120500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-05 | 5961 | keep | 0 | Dec | 2021 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2021-12-05 13:20 | 2021-12-05 13:21 | 850 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DEL ALIMENTADOR 1713-05 Y LLEVA 95% DE LA CARGA DEL 1717-02 | B21120500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-05 | 850 | keep | 0 | Dec | 2021 | 0.00057893 | 0.00057893 | Momentary | FALSE | FALSE | Not_TMED_Event | 850
PONCE | 2021-12-05 13:22 | 2021-12-05 13:23 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21120500013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-05 | 969 | keep | 0 | Dec | 2021 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
MAYAGÃœEZ | 2021-12-05 13:38 | 2021-12-06 11:40 | 40 | 022:02 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL SOBRE LINEA | M21120500045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1322 | 2021-12-05 | 52880 | keep | 0 | Dec | 2021 | 0.036016 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-12-05 13:46 | 2021-12-05 14:34 | 10 | 000:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21120500029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 48 | 2021-12-05 | 480 | keep | 0 | Dec | 2021 | 0.00032693 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-05 14:07 | 2021-12-05 16:28 | 1 | 002:21 | P | NO SE REPORTO CAUSA | 1 X 100 EN TRANSCLOSURE DE CLIENTE EL FOREMAN INFORMO QUE NO DETECTO CAUSA DEL FUSIBLE FUNDIDO | A21120500031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 141 | 2021-12-05 | 141 | keep | 0 | Dec | 2021 | 9.6034e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-05 14:20 | 2021-12-05 15:37 | 1 | 001:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21120500049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 77 | 2021-12-05 | 77 | keep | 0 | Dec | 2021 | 5.2444e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2021-12-05 14:25 | 2021-12-05 16:00 | 202 | 001:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA SECCIONALIZAR LINEA PRIMARIA EN EL PISO | P21120500016 | New_Event | Wire Down | Include | Include | Equipment | 95 | 2021-12-05 | 19190 | keep | 0 | Dec | 2021 | 0.01307 | 0.00013758 | Sustained | FALSE | FALSE | Not_TMED_Event | 202
CAGUAS | 2021-12-05 14:30 | 2021-12-05 15:50 | 55 | 001:20 | P | DESGANCHE | 1 X 100 EN C/L | C21120500035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2021-12-05 | 4400 | keep | 0 | Dec | 2021 | 0.0029968 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
SAN JUAN | 2021-12-05 14:44 | 2021-12-05 22:03 | 20 | 007:19 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | R21120500090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 439 | 2021-12-05 | 8780 | keep | 0 | Dec | 2021 | 0.00598 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-12-05 14:57 | 2021-12-05 17:47 | 25 | 002:50 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE LLEVO CONDUCTOR A CAJA | S21120500051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2021-12-05 | 4250 | keep | 0 | Dec | 2021 | 0.0028947 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2021-12-05 14:59 | 2021-12-05 15:00 | 1637 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21120500015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-05 | 1637 | keep | 0 | Dec | 2021 | 0.001115 | 0.001115 | Momentary | FALSE | FALSE | Not_TMED_Event | 1637
MAYAGÃœEZ | 2021-12-05 15:00 | 2021-12-05 18:46 | 30 | 003:46 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA INFORMA JOURNEYMAN REQUIERE DESGANCHE | M21120500050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2021-12-05 | 6780 | keep | 0 | Dec | 2021 | 0.0046178 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-12-05 15:02 | 2021-12-05 15:03 | 1142 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21120500052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-05 | 1142 | keep | 0 | Dec | 2021 | 0.00077781 | 0.00077781 | Momentary | FALSE | FALSE | Not_TMED_Event | 1142
MAYAGÃœEZ | 2021-12-05 15:14 | 2021-12-08 16:45 | 12 | 073:31 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA X TRANSFORMADOR DE 25 KVA EVENTO QUE DIERON FUE DEL DIA 5 | M21120500054 | New_Event | Service Transformer Failure | Include | Include | Equipment | 4411 | 2021-12-05 | 52932 | keep | 0 | Dec | 2021 | 0.036052 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-12-05 15:20 | 2021-12-06 10:40 | 20 | 019:20 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | R21120500128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1160 | 2021-12-05 | 23200 | keep | 0 | Dec | 2021 | 0.015801 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-12-05 15:25 | 2021-12-05 16:10 | 15 | 000:45 | P | TRANSFORMADOR AVERIADO | SE ABRIO MONTURA DE TRANSFORMADORES PARA RETIRAR TRANSFORMADOR CON ESCAPE DE ACEITE | A21120500034 | New_Event | Service Transformer Failure | Include | Include | Equipment | 45 | 2021-12-05 | 675 | keep | 0 | Dec | 2021 | 0.00045974 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-12-05 15:36 | 2021-12-05 19:27 | 150 | 003:51 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHO Y LEVANTO CONDUCTOR | C21120500048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 231 | 2021-12-05 | 34650 | keep | 0 | Dec | 2021 | 0.0236 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2021-12-05 15:38 | 2021-12-05 15:39 | 1812 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21120500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-05 | 1812 | keep | 0 | Dec | 2021 | 0.0012341 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
MAYAGÃœEZ | 2021-12-05 15:55 | 2021-12-05 16:20 | 200 | 000:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO SE CERRO CORTE DE LINEA | M21120300086 | Additional_clients | Wire Down | Include | Include | Equipment | 25 | 2021-12-05 | 5000 | keep | 0 | Dec | 2021 | 0.0034055 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2021-12-05 16:00 | 2021-12-06 14:47 | 5 | 022:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA Y SE CERRARON PUENTES | P21120500017 | Partial_restoration | Wire Down | Include | Include | Equipment | 1367 | 2021-12-05 | 6835 | keep | 0 | Dec | 2021 | 0.0046553 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-12-05 16:00 | 2021-12-05 16:01 | 2067 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21120500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-05 | 2067 | keep | 0 | Dec | 2021 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
ARECIBO | 2021-12-05 16:10 | 2021-12-05 18:49 | 50 | 002:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A21120500035 | New_Event | Cutout Failure | Include | Include | Equipment | 159 | 2021-12-05 | 7950 | keep | 0 | Dec | 2021 | 0.0054147 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-12-05 16:27 | 2021-12-05 16:28 | 4664 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21120500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-05 | 4664 | keep | 0 | Dec | 2021 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
VEGA BAJA | 2021-12-05 16:39 | 2021-12-05 17:10 | 1 | 000:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | B21120500000 | New_Event | Wire Down | Include | Include | Equipment | 31 | 2021-12-05 | 31 | keep | 0 | Dec | 2021 | 2.1114e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-05 16:56 | 2021-12-05 21:39 | 100 | 004:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | B21120500044 | New_Event | Wire Down | Include | Include | Equipment | 283 | 2021-12-05 | 28300 | keep | 0 | Dec | 2021 | 0.019275 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-12-05 17:05 | 2021-12-05 17:07 | 2900 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C21120500054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-05 | 5800 | keep | 0 | Dec | 2021 | 0.0039504 | 0.0019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 2900
SAN JUAN | 2021-12-05 17:08 | 2021-12-05 17:10 | 5290 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S21120500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-05 | 10580 | keep | 0 | Dec | 2021 | 0.007206 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2021-12-05 17:08 | 2021-12-05 17:10 | 207 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1336-08 | S21120500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-05 | 414 | keep | 0 | Dec | 2021 | 0.00028197 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
AGUADILLA | 2021-12-05 17:15 | 2021-12-05 18:20 | 5 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M21120500049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2021-12-05 | 325 | keep | 0 | Dec | 2021 | 0.00022136 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-12-05 17:45 | 2021-12-05 17:47 | 290 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S21120500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-05 | 580 | keep | 0 | Dec | 2021 | 0.00039504 | 0.00019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 290
AGUADILLA | 2021-12-05 18:05 | 2021-12-06 10:10 | 60 | 016:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 50 EN CORTE DE LINEA SE REPARO SECUNDARIA QUE CRUZO FASES | M21120500100 | New_Event | Secondary Wire Down | Include | Include | Equipment | 965 | 2021-12-05 | 57900 | keep | 0 | Dec | 2021 | 0.039435 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2021-12-05 18:15 | 2021-12-05 18:41 | 20 | 000:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | M21120500062 | New_Event | Secondary Wire Down | Include | Include | Equipment | 26 | 2021-12-05 | 520 | keep | 0 | Dec | 2021 | 0.00035417 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-12-05 19:26 | 2021-12-05 20:23 | 50 | 000:57 | P | DESGANCHE | 1 X 50 EN C/L | C21120500074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2021-12-05 | 2850 | keep | 0 | Dec | 2021 | 0.0019411 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-12-05 19:30 | 2021-12-05 22:20 | 30 | 002:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE INFORMA REQUIERE DESGANCHE | M21120500089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2021-12-05 | 5100 | keep | 0 | Dec | 2021 | 0.0034736 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-05 19:52 | 2021-12-06 11:00 | 12 | 015:08 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO 4160/7200 120/240 37.5KVA X 37.5KVA | A21120500055 | New_Event | Service Transformer Failure | Include | Include | Equipment | 908 | 2021-12-05 | 10896 | keep | 0 | Dec | 2021 | 0.0074212 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-12-05 20:18 | 2021-12-05 20:19 | 1227 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR POR LINEA ZAFADA DE AISLADOR | A21120500058 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-12-05 | 1227 | keep | 0 | Dec | 2021 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2021-12-05 20:19 | 2021-12-05 21:37 | 15 | 001:18 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A21120500059 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 78 | 2021-12-05 | 1170 | keep | 0 | Dec | 2021 | 0.00079688 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-12-05 21:10 | 2021-12-06 09:53 | 90 | 012:43 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21120500085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 763 | 2021-12-05 | 68670 | keep | 0 | Dec | 2021 | 0.046771 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2021-12-05 21:28 | 2021-12-06 13:18 | 100 | 015:50 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21120500062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 950 | 2021-12-05 | 95000 | keep | 0 | Dec | 2021 | 0.064704 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-12-05 21:31 | 2021-12-06 11:52 | 60 | 014:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L. SE REEMPALZO CAJA AVERIADA | B21120500091 | New_Event | Cutout Failure | Include | Include | Equipment | 861 | 2021-12-05 | 51660 | keep | 0 | Dec | 2021 | 0.035185 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2021-12-05 21:51 | 2021-12-06 00:16 | 3973 | 002:25 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO RISER PARA SECCIONALISAR AVERIA YA QUE HUBO UN TIROTEO Y AVERIO RISER | P21120500039 | New_Event |  |  | Include | Wildlife | 145 | 2021-12-05 | 576085 | keep | 0 | Dec | 2021 | 0.39237 | 0.002706 | Sustained | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2021-12-05 21:51 | 2021-12-06 00:16 | 2484 | 002:25 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO RISER PARA SECCIONALIZAR AVERIA Y SE CERRO BREAKER LLEVANDO LA CARGA DEL 5602-02 | P21120500034 | New_Event |  |  | Include | Wildlife | 145 | 2021-12-05 | 360180 | keep | 0 | Dec | 2021 | 0.24532 | 0.0016918 | Sustained | FALSE | FALSE | Not_TMED_Event | 2484
FAJARDO | 2021-12-05 22:01 | 2021-12-06 10:07 | 23 | 012:06 | P | DESGANCHE | 1 X 25 EN CORE DE LINEA | R21120500125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 726 | 2021-12-05 | 16698 | keep | 0 | Dec | 2021 | 0.011373 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
CAGUAS | 2021-12-05 22:02 | 2021-12-06 11:45 | 36 | 013:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA REPARO LINEA CRUZADA CON POSTE | C21120500087 | New_Event | Wire Down | Include | Include | Equipment | 823 | 2021-12-05 | 29628 | keep | 0 | Dec | 2021 | 0.020179 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
BAYAMON | 2021-12-05 22:08 | 2021-12-06 14:46 | 15 | 016:38 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | B21120500093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 998 | 2021-12-05 | 14970 | keep | 0 | Dec | 2021 | 0.010196 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-12-05 22:12 | 2021-12-06 17:43 | 1 | 019:31 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE Y LINEA ROTA Y SE CERRO CORTE DE LINEA | C21120500086 | New_Event | Defective Pole | Include | Include | Equipment | 1171 | 2021-12-05 | 1171 | keep | 0 | Dec | 2021 | 0.00079756 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-05 22:47 | 2021-12-06 17:07 | 12 | 018:20 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE REPARO PUENTE | S21120500064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1100 | 2021-12-05 | 13200 | keep | 0 | Dec | 2021 | 0.0089905 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2021-12-06 00:16 | 2021-12-06 20:05 | 356 | 019:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | RISER IMPACTADO POR PROYECTIL | P21120600001 | Partial_restoration |  |  | Include | Wildlife | 1189 | 2021-12-06 | 423284 | keep | 0 | Dec | 2021 | 0.2883 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-06 01:06 | 2021-12-06 10:48 | 100 | 009:42 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTES DE LINEA SE PATRULLO | R21120600001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 582 | 2021-12-06 | 58200 | keep | 0 | Dec | 2021 | 0.03964 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-12-06 01:08 | 2021-12-06 09:45 | 80 | 008:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M21120600001 | New_Event | Bad Weather | Include | Include | Weather | 517 | 2021-12-06 | 41360 | keep | 0 | Dec | 2021 | 0.02817 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2021-12-06 01:20 | 2021-12-06 01:21 | 2379 | 000:01 | T | DESGANCHE | RECIERRE | P21120600003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-06 | 2379 | keep | 0 | Dec | 2021 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
PONCE | 2021-12-06 01:21 | 2021-12-06 09:45 | 50 | 008:24 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | P21120600004 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 504 | 2021-12-06 | 25200 | keep | 0 | Dec | 2021 | 0.017164 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-12-06 01:51 | 2021-12-06 11:46 | 1 | 009:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21120600002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 595 | 2021-12-06 | 595 | keep | 0 | Dec | 2021 | 0.00040525 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-12-06 01:55 | 2021-12-06 10:13 | 60 | 008:18 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21120600007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 498 | 2021-12-06 | 29880 | keep | 0 | Dec | 2021 | 0.020351 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-12-06 02:30 | 2021-12-06 02:31 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21110600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-06 | 308 | keep | 0 | Dec | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
MAYAGÃœEZ | 2021-12-06 02:50 | 2021-12-06 02:51 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21120600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-06 | 1097 | keep | 0 | Dec | 2021 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
ARECIBO | 2021-12-06 03:04 | 2021-12-06 09:46 | 20 | 006:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO TREE WIRE PARTIDO | A21120600002 | New_Event | Wire Down | Include | Include | Equipment | 402 | 2021-12-06 | 8040 | keep | 0 | Dec | 2021 | 0.005476 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-12-06 03:25 | 2021-12-06 03:26 | 27 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21120600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-06 | 27 | keep | 0 | Dec | 2021 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2021-12-06 04:12 | 2021-12-06 11:54 | 12 | 007:42 | P | NO SE REPORTO CAUSA | 1 X 10 EN SU-10 | B21120600006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 462 | 2021-12-06 | 5544 | keep | 0 | Dec | 2021 | 0.003776 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2021-12-06 04:27 | 2021-12-06 09:24 | 250 | 004:57 | P | NO SE REPORTO CAUSA | 1 X 80, 2 X 65 Y 1 X 100 EN DISTINTOS CORTES DE LINEAS | B21120600010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 297 | 2021-12-06 | 74250 | keep | 0 | Dec | 2021 | 0.050571 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
YAUCO | 2021-12-06 05:26 | 2021-12-06 10:42 | 100 | 005:16 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN CORTE DE LINEA Y OTRO DE 3 AMP EN TRANSFORMADOR PARARAYO DESECTUOSO EN TRANSFORMADOR | P21120600005 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 316 | 2021-12-06 | 31600 | keep | 0 | Dec | 2021 | 0.021523 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-12-06 05:41 | 2021-12-06 05:42 | 2697 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | A21120600000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-12-06 | 2697 | keep | 0 | Dec | 2021 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
ARECIBO | 2021-12-06 05:42 | 2021-12-06 09:35 | 25 | 003:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA Y 1 X 40 EN RISER POR FUERTES LLUVIAS | A21120600003 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 233 | 2021-12-06 | 5825 | keep | 0 | Dec | 2021 | 0.0039674 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2021-12-06 05:43 | 2021-12-06 09:13 | 100 | 003:30 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21120600005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2021-12-06 | 21000 | keep | 0 | Dec | 2021 | 0.014303 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-12-06 06:25 | 2021-12-06 06:26 | 1 | 000:01 | T | ERROR HUMANO | TOC ABRIO INTERRUPTOR POR ERROR EN PREPARATIVOS PARA RELEVO DE CARGA MANUAL | S21120600000 | New_Event | Human Error | Include | Include | Other | 1 | 2021-12-06 | 1 | keep | 0 | Dec | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-06 06:25 | 2021-12-06 06:26 | 47 | 000:01 | T | ERROR HUMANO | TOC ABRIO INTERRUPTOR POR ERROR EN PREPARATIVOS PARA RELEVO DE CARGA MANUAL | S21120600000 | New_Event | Human Error | Include | Include | Other | 1 | 2021-12-06 | 47 | keep | 0 | Dec | 2021 | 3.2011e-05 | 3.2011e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 47
BAYAMON | 2021-12-06 06:25 | 2021-12-06 06:26 | 245 | 000:01 | T | ERROR HUMANO | TOC ABRIO INTERRUPTOR POR ERROR EN PREPARATIVOS PARA RELEVO DE CARGA MANUAL | S21120600000 | New_Event | Human Error | Include | Include | Other | 1 | 2021-12-06 | 245 | keep | 0 | Dec | 2021 | 0.00016687 | 0.00016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 245
BAYAMON | 2021-12-06 06:25 | 2021-12-06 06:26 | 35 | 000:01 | T | ERROR HUMANO | TOC ABRIO INTERRUPTOR POR ERROR EN PREPARATIVOS PARA RELEVO DE CARGA MANUAL | S21120600000 | New_Event | Human Error | Include | Include | Other | 1 | 2021-12-06 | 35 | keep | 0 | Dec | 2021 | 2.3838e-05 | 2.3838e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2021-12-06 06:25 | 2021-12-06 06:26 | 126 | 000:01 | T | ERROR HUMANO | TOC ABRIO INTERRUPTOR POR ERROR EN PREPARATIVOS PARA RELEVO DE CARGA MANUAL CARGA POR EL 1107-05 | S21120600000 | New_Event | Human Error | Include | Include | Other | 1 | 2021-12-06 | 126 | keep | 0 | Dec | 2021 | 8.5818e-05 | 8.5818e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 126
BAYAMON | 2021-12-06 06:25 | 2021-12-06 06:26 | 350 | 000:01 | T | ERROR HUMANO | TOC ABRIO INTERRUPTOR POR ERROR EN PREPARATIVOS PARA RELEVO DE CARGA MANUAL CARGA POR EL 1100-02 | S21120600000 | New_Event | Human Error | Include | Include | Other | 1 | 2021-12-06 | 350 | keep | 0 | Dec | 2021 | 0.00023838 | 0.00023838 | Momentary | FALSE | FALSE | Not_TMED_Event | 350
BAYAMON | 2021-12-06 06:25 | 2021-12-06 06:26 | 215 | 000:01 | T | ERROR HUMANO | TOC ABRIO INTERRUPTOR POR ERROR EN PREPARATIVOS PARA RELEVO DE CARGA MANUAL LLEVA 1100-01 | S21120600000 | New_Event | Human Error | Include | Include | Other | 1 | 2021-12-06 | 215 | keep | 0 | Dec | 2021 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
BAYAMON | 2021-12-06 06:25 | 2021-12-06 06:26 | 262 | 000:01 | T | ERROR HUMANO | TOC ABRIO INTERRUPTOR POR ERROR EN PREPARATIVOS PARA RELEVO DE CARGA MANUAL | S21120600000 | New_Event | Human Error | Include | Include | Other | 1 | 2021-12-06 | 262 | keep | 0 | Dec | 2021 | 0.00017845 | 0.00017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 262
BAYAMON | 2021-12-06 06:25 | 2021-12-06 06:26 | 90 | 000:01 | T | ERROR HUMANO | TOC ABRIO INTERRUPTOR POR ERROR EN PREPARATIVOS PARA RELEVO DE CARGA MANUAL | S21120600000 | New_Event | Human Error | Include | Include | Other | 1 | 2021-12-06 | 90 | keep | 0 | Dec | 2021 | 6.1299e-05 | 6.1299e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2021-12-06 06:25 | 2021-12-06 06:26 | 453 | 000:01 | T | ERROR HUMANO | TOC ABRIO INTERRUPTOR POR ERROR EN PREPARATIVOS PARA RELEVO DE CARGA MANUAL CARGA POR EL 1107-05 | S21120600000 | New_Event | Human Error | Include | Include | Other | 1 | 2021-12-06 | 453 | keep | 0 | Dec | 2021 | 0.00030854 | 0.00030854 | Momentary | FALSE | FALSE | Not_TMED_Event | 453
BAYAMON | 2021-12-06 06:25 | 2021-12-06 06:26 | 733 | 000:01 | T | ERROR HUMANO | TOC ABRIO INTERRUPTOR POR ERROR EN PREPARATIVOS PARA RELEVO DE CARGA MANUAL | S21120600000 | New_Event | Human Error | Include | Include | Other | 1 | 2021-12-06 | 733 | keep | 0 | Dec | 2021 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
BAYAMON | 2021-12-06 06:25 | 2021-12-06 06:26 | 626 | 000:01 | T | ERROR HUMANO | TOC ABRIO INTERRUPTOR POR ERROR EN PREPARATIVOS PARA RELEVO DE CARGA MANUAL LLEVA 1002-02 Y 1101-01 | S21120600000 | New_Event | Human Error | Include | Include | Other | 1 | 2021-12-06 | 626 | keep | 0 | Dec | 2021 | 0.00042637 | 0.00042637 | Momentary | FALSE | FALSE | Not_TMED_Event | 626
BAYAMON | 2021-12-06 06:25 | 2021-12-06 06:26 | 1105 | 000:01 | T | ERROR HUMANO | TOC ABRIO INTERRUPTOR POR ERROR EN PREPARATIVOS PARA RELEVO DE CARGA MANUAL | S21120600000 | New_Event | Human Error | Include | Include | Other | 1 | 2021-12-06 | 1105 | keep | 0 | Dec | 2021 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
SAN JUAN | 2021-12-06 06:25 | 2021-12-06 06:26 | 641 | 000:01 | T | ERROR HUMANO | TOC ABRIO INTERRUPTOR POR ERROR EN PREPARATIVOS PARA RELEVO DE CARGA MANUAL LLEVA 1206-02 | S21120600000 | New_Event | Human Error | Include | Include | Other | 1 | 2021-12-06 | 641 | keep | 0 | Dec | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-12-06 06:25 | 2021-12-06 06:26 | 733 | 000:01 | T | ERROR HUMANO | TOC ABRIO INTERRUPTOR POR ERROR EN PREPARATIVOS PARA RELEVO DE CARGA MANUAL CARGA POR 1206-01 | S21120600000 | New_Event | Human Error | Include | Include | Other | 1 | 2021-12-06 | 733 | keep | 0 | Dec | 2021 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
MAYAGÃœEZ | 2021-12-06 06:32 | 2021-12-06 11:13 | 150 | 004:41 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21120600014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 281 | 2021-12-06 | 42150 | keep | 0 | Dec | 2021 | 0.028708 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
GUAYAMA | 2021-12-06 06:33 | 2021-12-06 06:34 | 4132 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21120600011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-06 | 4132 | keep | 0 | Dec | 2021 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
MAYAGÃœEZ | 2021-12-06 06:44 | 2021-12-06 17:56 | 50 | 011:12 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21120600015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 672 | 2021-12-06 | 33600 | keep | 0 | Dec | 2021 | 0.022885 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-12-06 06:56 | 2021-12-06 11:39 | 10 | 004:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR REEMPLAZO CAJA XMR | C21120600011 | New_Event | Cutout Failure | Include | Include | Equipment | 283 | 2021-12-06 | 2830 | keep | 0 | Dec | 2021 | 0.0019275 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-06 06:56 | 2021-12-06 09:50 | 4 | 002:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | M21120600016 | New_Event | Bad Weather | Include | Include | Weather | 174 | 2021-12-06 | 696 | keep | 0 | Dec | 2021 | 0.00047404 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-12-06 07:06 | 2021-12-06 11:17 | 50 | 004:11 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21120600016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 251 | 2021-12-06 | 12550 | keep | 0 | Dec | 2021 | 0.0085477 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-12-06 07:10 | 2021-12-06 09:15 | 1 | 002:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M21120600017 | New_Event | Bad Weather | Include | Include | Weather | 125 | 2021-12-06 | 125 | keep | 0 | Dec | 2021 | 8.5137e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-06 07:15 | 2021-12-06 13:00 | 309 | 005:45 | T | DESGANCHE | SE RETIRO ARBOL SOBRE LINEA Y SE CERRO INTERRUPTOR MANUAL ELECTRICO | M21120600021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 345 | 2021-12-06 | 106605 | keep | 0 | Dec | 2021 | 0.072608 | 0.00021046 | Sustained | FALSE | FALSE | Not_TMED_Event | 309
BAYAMON | 2021-12-06 07:16 | 2021-12-06 16:32 | 10 | 009:16 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21120600018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 556 | 2021-12-06 | 5560 | keep | 0 | Dec | 2021 | 0.0037869 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-06 07:29 | 2021-12-06 07:30 | 5961 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1713-05 LLEVANDO 95% DEL 1717-02 | B21120600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-06 | 5961 | keep | 0 | Dec | 2021 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2021-12-06 07:29 | 2021-12-06 07:30 | 865 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1713-05 LLEVANDO 95% DEL 1717-02 | B21120600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-06 | 865 | keep | 0 | Dec | 2021 | 0.00058915 | 0.00058915 | Momentary | FALSE | FALSE | Not_TMED_Event | 865
BARRANQUITAS | 2021-12-06 07:35 | 2021-12-06 10:18 | 80 | 002:43 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA MAL TIEMPO | C21120600019 | New_Event | Bad Weather | Include | Include | Weather | 163 | 2021-12-06 | 13040 | keep | 0 | Dec | 2021 | 0.0088815 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2021-12-06 07:37 | 2021-12-06 19:09 | 70 | 011:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARARON LINEAS PRIMARIAS PARTIDAS | A21120600004 | New_Event | Wire Down | Include | Include | Equipment | 692 | 2021-12-06 | 48440 | keep | 0 | Dec | 2021 | 0.032992 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2021-12-06 07:40 | 2021-12-06 12:13 | 103 | 004:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA LLUVIAS | R21120600013 | New_Event | Bad Weather | Include | Include | Weather | 273 | 2021-12-06 | 28119 | keep | 0 | Dec | 2021 | 0.019152 | 7.0153e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 103
BAYAMON | 2021-12-06 07:41 | 2021-12-06 10:01 | 40 | 002:20 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21120600019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 140 | 2021-12-06 | 5600 | keep | 0 | Dec | 2021 | 0.0038141 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-12-06 07:54 | 2021-12-06 11:10 | 60 | 003:16 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M21120600023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2021-12-06 | 11760 | keep | 0 | Dec | 2021 | 0.0080097 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2021-12-06 07:56 | 2021-12-06 11:08 | 70 | 003:12 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C21120600020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 192 | 2021-12-06 | 13440 | keep | 0 | Dec | 2021 | 0.0091539 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-12-06 08:05 | 2021-12-06 13:35 | 2 | 005:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M21120600026 | New_Event | Bad Weather | Include | Include | Weather | 330 | 2021-12-06 | 660 | keep | 0 | Dec | 2021 | 0.00044952 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
FAJARDO | 2021-12-06 08:07 | 2021-12-06 10:41 | 60 | 002:34 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | R21120600017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2021-12-06 | 9240 | keep | 0 | Dec | 2021 | 0.0062933 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2021-12-06 08:18 | 2021-12-06 14:24 | 40 | 006:06 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21120600022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 366 | 2021-12-06 | 14640 | keep | 0 | Dec | 2021 | 0.0099712 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-12-06 08:27 | 2021-12-06 12:29 | 30 | 004:02 | P | DESGANCHE | 1 X 30 EN C/L SE REALIZO DESGANCHE | B21120600025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2021-12-06 | 7260 | keep | 0 | Dec | 2021 | 0.0049448 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-06 08:31 | 2021-12-06 08:32 | 959 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-06 | 959 | keep | 0 | Dec | 2021 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2021-12-06 08:31 | 2021-12-06 08:32 | 1382 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-06 | 1382 | keep | 0 | Dec | 2021 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2021-12-06 08:31 | 2021-12-06 08:32 | 663 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9100 | B21120600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-06 | 663 | keep | 0 | Dec | 2021 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2021-12-06 08:31 | 2021-12-06 08:32 | 1715 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-06 | 1715 | keep | 0 | Dec | 2021 | 0.0011681 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2021-12-06 08:31 | 2021-12-06 08:32 | 1498 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-06 | 1498 | keep | 0 | Dec | 2021 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2021-12-06 08:31 | 2021-12-06 08:32 | 1221 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-06 | 1221 | keep | 0 | Dec | 2021 | 0.00083162 | 0.00083162 | Momentary | FALSE | FALSE | Not_TMED_Event | 1221
BAYAMON | 2021-12-06 08:31 | 2021-12-06 08:32 | 1100 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-06 | 1100 | keep | 0 | Dec | 2021 | 0.0007492 | 0.0007492 | Momentary | FALSE | FALSE | Not_TMED_Event | 1100
BAYAMON | 2021-12-06 08:31 | 2021-12-06 08:32 | 1514 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-06 | 1514 | keep | 0 | Dec | 2021 | 0.0010312 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2021-12-06 08:31 | 2021-12-06 08:32 | 1105 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-06 | 1105 | keep | 0 | Dec | 2021 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2021-12-06 08:31 | 2021-12-06 08:32 | 4176 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-06 | 4176 | keep | 0 | Dec | 2021 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2021-12-06 08:31 | 2021-12-06 08:32 | 252 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-06 | 252 | keep | 0 | Dec | 2021 | 0.00017164 | 0.00017164 | Momentary | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2021-12-06 08:31 | 2021-12-06 08:32 | 2147 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-06 | 2147 | keep | 0 | Dec | 2021 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2021-12-06 08:31 | 2021-12-06 08:32 | 2858 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-06 | 2858 | keep | 0 | Dec | 2021 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
CAGUAS | 2021-12-06 08:41 | 2021-12-06 12:53 | 1 | 004:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO TOMA | C21120600027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 252 | 2021-12-06 | 252 | keep | 0 | Dec | 2021 | 0.00017164 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-12-06 08:53 | 2021-12-06 10:20 | 10 | 001:27 | P | SECUNDARIA/DESGANCHE | 1 X 15 TRANSFORMADOR | C21120600034 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 87 | 2021-12-06 | 870 | keep | 0 | Dec | 2021 | 0.00059255 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-06 08:58 | 2021-12-06 11:20 | 4 | 002:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA DE 100 AMP EN TRANSFORMADOR | M21120600035 | New_Event | Cutout Failure | Include | Include | Equipment | 142 | 2021-12-06 | 568 | keep | 0 | Dec | 2021 | 0.00038686 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-12-06 08:58 | 2021-12-06 20:01 | 10 | 011:03 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR INFORMA JOURNEYMAN REQUIERE DESGANCHE | M21120600036 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 663 | 2021-12-06 | 6630 | keep | 0 | Dec | 2021 | 0.0045157 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2021-12-06 09:00 | 2021-12-06 13:54 | 10 | 004:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | P21120600022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 294 | 2021-12-06 | 2940 | keep | 0 | Dec | 2021 | 0.0020024 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-06 09:07 | 2021-12-06 14:08 | 30 | 005:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21120600038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 301 | 2021-12-06 | 9030 | keep | 0 | Dec | 2021 | 0.0061503 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2021-12-06 09:15 | 2021-12-06 13:10 | 10 | 003:55 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | R21120600021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 235 | 2021-12-06 | 2350 | keep | 0 | Dec | 2021 | 0.0016006 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-12-06 09:22 | 2021-12-07 13:42 | 12 | 028:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CONVERTIDOR SE REPARO NEUTRAL PARTIDO | A21120600011 | New_Event | Wire Down | Include | Include | Equipment | 1700 | 2021-12-06 | 20400 | keep | 0 | Dec | 2021 | 0.013894 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-12-06 09:32 | 2021-12-06 10:31 | 6 | 000:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIO | C21120600207 | New_Event | Secondary Wire Down | Include | Include | Equipment | 59 | 2021-12-06 | 354 | keep | 0 | Dec | 2021 | 0.00024111 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-12-06 09:33 | 2021-12-06 11:12 | 50 | 001:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA DE 100 AMP MARCA CHINT | A21120600012 | New_Event | Cutout Failure | Include | Include | Equipment | 99 | 2021-12-06 | 4950 | keep | 0 | Dec | 2021 | 0.0033714 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-12-06 09:45 | 2021-12-06 11:46 | 40 | 002:01 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 75 X 75KVA | R21120600024 | New_Event | Service Transformer Failure | Include | Include | Equipment | 121 | 2021-12-06 | 4840 | keep | 0 | Dec | 2021 | 0.0032965 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-06 09:48 | 2021-12-06 12:49 | 35 | 003:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO C/L Y SE CERRO PUENTE DE LINEA CAJA | B21120600044 | New_Event | Wire Down | Include | Include | Equipment | 181 | 2021-12-06 | 6335 | keep | 0 | Dec | 2021 | 0.0043147 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2021-12-06 09:50 | 2021-12-06 14:30 | 12 | 004:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA REPARAR SECUNDARIA | S21120600023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 280 | 2021-12-06 | 3360 | keep | 0 | Dec | 2021 | 0.0022885 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-12-06 09:56 | 2021-12-06 11:44 | 33 | 001:48 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R21120600026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2021-12-06 | 3564 | keep | 0 | Dec | 2021 | 0.0024274 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
CAGUAS | 2021-12-06 10:18 | 2021-12-06 10:19 | 2457 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21120600011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-06 | 2457 | keep | 0 | Dec | 2021 | 0.0016735 | 0.0016735 | Momentary | FALSE | FALSE | Not_TMED_Event | 2457
ARECIBO | 2021-12-06 10:18 | 2021-12-06 12:35 | 10 | 002:17 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | A21120600015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2021-12-06 | 1370 | keep | 0 | Dec | 2021 | 0.0009331 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-06 10:22 | 2021-12-06 11:08 | 5 | 000:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA ABIERTA | C21120600042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 46 | 2021-12-06 | 230 | keep | 0 | Dec | 2021 | 0.00015665 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2021-12-06 10:35 | 2021-12-06 16:53 | 90 | 006:18 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA REEMPLAZO DISCO ROTO | C21120600046 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 378 | 2021-12-06 | 34020 | keep | 0 | Dec | 2021 | 0.023171 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2021-12-06 10:36 | 2021-12-06 14:55 | 6 | 004:19 | P | CABLE SOTERRADO AVERIADO | 1 X 25 EN RISER SE INSTALO LINEA PROVISIONAL AEREA | M21120600024 | New_Event | UG Cable Fault | Include | Include | Equipment | 259 | 2021-12-06 | 1554 | keep | 0 | Dec | 2021 | 0.0010584 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-12-06 10:42 | 2021-12-06 14:54 | 30 | 004:12 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA INFORMA JOURNEYMAN REQUIERE DESGANCHE MASIVO | M21120600055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 252 | 2021-12-06 | 7560 | keep | 0 | Dec | 2021 | 0.0051491 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2021-12-06 10:49 | 2021-12-06 17:29 | 2 | 006:40 | P | ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR POR POSTE PARTIDO SE MOVIO A POSTE NUEVO EXISTENTE | A21120600020 | New_Event | Defective Pole | Include | Include | Equipment | 400 | 2021-12-06 | 800 | keep | 0 | Dec | 2021 | 0.00054488 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2021-12-06 11:17 | 2021-12-06 16:49 | 20 | 005:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO CAJA RPIMARIA Y DESGANCHE | B21120600052 | New_Event | Cutout Failure | Include | Include | Equipment | 332 | 2021-12-06 | 6640 | keep | 0 | Dec | 2021 | 0.0045225 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-12-06 11:17 | 2021-12-06 14:24 | 5 | 003:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA ABIERTA | C21120600042 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 187 | 2021-12-06 | 935 | keep | 0 | Dec | 2021 | 0.00063682 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-12-06 11:20 | 2021-12-06 13:20 | 3 | 002:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | M21120600054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 120 | 2021-12-06 | 360 | keep | 0 | Dec | 2021 | 0.00024519 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-12-06 11:33 | 2021-12-06 13:03 | 10 | 001:30 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA DESGANCHAR Y REPARAR SECUNDARIA | B21120600050 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 90 | 2021-12-06 | 900 | keep | 0 | Dec | 2021 | 0.00061299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-06 11:34 | 2021-12-06 13:30 | 8 | 001:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES SECUNDARIAS Y SE REPARO TREE WIRE PARTIDO | A21120600029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 116 | 2021-12-06 | 928 | keep | 0 | Dec | 2021 | 0.00063206 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-12-06 11:47 | 2021-12-06 12:36 | 5 | 000:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO PEDESTAL AVERIADO | C21120600083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 49 | 2021-12-06 | 245 | keep | 0 | Dec | 2021 | 0.00016687 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-12-06 11:54 | 2021-12-06 17:33 | 10 | 005:39 | P | HERRAJE ROTO O PODRIDO | SE REMPLAZO CRUCETA PRIMARIA PARTIDA | A21120600031 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 339 | 2021-12-06 | 3390 | keep | 0 | Dec | 2021 | 0.0023089 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-06 11:55 | 2021-12-06 15:19 | 60 | 003:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA | A21120600032 | New_Event | Cutout Failure | Include | Include | Equipment | 204 | 2021-12-06 | 12240 | keep | 0 | Dec | 2021 | 0.0083366 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2021-12-06 12:01 | 2021-12-06 15:21 | 10 | 003:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE ELIMINO CABLE CRUZANDO SECUNDARIA | B21120600076 | New_Event | Secondary Wire Down | Include | Include | Equipment | 200 | 2021-12-06 | 2000 | keep | 0 | Dec | 2021 | 0.0013622 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-06 12:55 | 2021-12-06 14:30 | 40 | 001:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN RISER POR FUERTES LLUVIAS | A21120600038 | New_Event | Bad Weather | Include | Include | Weather | 95 | 2021-12-06 | 3800 | keep | 0 | Dec | 2021 | 0.0025882 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2021-12-06 12:59 | 2021-12-06 13:26 | 49 | 000:27 | P | DESGANCHE | 1 X 50 CORTE DE LINEA | R21120600075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 27 | 2021-12-06 | 1323 | keep | 0 | Dec | 2021 | 0.00090109 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
PONCE | 2021-12-06 13:05 | 2021-12-06 15:31 | 120 | 002:26 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P21120600043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2021-12-06 | 17520 | keep | 0 | Dec | 2021 | 0.011933 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CAGUAS | 2021-12-06 13:42 | 2021-12-06 16:11 | 60 | 002:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21120600092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2021-12-06 | 8940 | keep | 0 | Dec | 2021 | 0.006089 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2021-12-06 13:44 | 2021-12-06 15:41 | 9 | 001:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA ABIERTA | R21120600079 | New_Event | Secondary Wire Down | Include | Include | Equipment | 117 | 2021-12-06 | 1053 | keep | 0 | Dec | 2021 | 0.00071719 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2021-12-06 13:45 | 2021-12-06 16:15 | 6 | 002:30 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA RELOCALIZAR LINEA SECUNDARIA POR POSTE PARTIDO | M21120600081 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 150 | 2021-12-06 | 900 | keep | 0 | Dec | 2021 | 0.00061299 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-12-06 13:52 | 2021-12-06 13:54 | 844 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21120600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-06 | 1688 | keep | 0 | Dec | 2021 | 0.0011497 | 0.00057484 | Momentary | FALSE | FALSE | Not_TMED_Event | 844
SAN JUAN | 2021-12-06 13:54 | 2021-12-06 16:42 | 12 | 002:48 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21120600118 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 168 | 2021-12-06 | 2016 | keep | 0 | Dec | 2021 | 0.0013731 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-12-06 13:54 | 2021-12-06 18:17 | 90 | 004:23 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA INFORMA JOURNEYMAN REQUIERE DESGANCHE | M21120600092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2021-12-06 | 23670 | keep | 0 | Dec | 2021 | 0.016122 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
GUAYAMA | 2021-12-06 14:02 | 2021-12-06 17:35 | 500 | 003:33 | P | DESGANCHE | 2 X 140 Y 1 X 65 EN DIFERENTES CORTES DE LINEA POR DESGANCHE | P21120600046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2021-12-06 | 106500 | keep | 0 | Dec | 2021 | 0.072537 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
PONCE | 2021-12-06 14:08 | 2021-12-06 17:14 | 100 | 003:06 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | P21120600048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2021-12-06 | 18600 | keep | 0 | Dec | 2021 | 0.012668 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-12-06 14:37 | 2021-12-06 16:00 | 30 | 001:23 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBU SOBRE LAS LINEAS | M21120600047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2021-12-06 | 2490 | keep | 0 | Dec | 2021 | 0.0016959 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2021-12-06 14:40 | 2021-12-06 20:07 | 20 | 005:27 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | C21120600101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 327 | 2021-12-06 | 6540 | keep | 0 | Dec | 2021 | 0.0044544 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-12-06 14:41 | 2021-12-06 17:50 | 50 | 003:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | S21120600112 | New_Event | Cutout Failure | Include | Include | Equipment | 189 | 2021-12-06 | 9450 | keep | 0 | Dec | 2021 | 0.0064364 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-12-06 14:45 | 2021-12-06 14:46 | 2791 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21120600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-06 | 2791 | keep | 0 | Dec | 2021 | 0.0019009 | 0.0019009 | Momentary | FALSE | FALSE | Not_TMED_Event | 2791
ARECIBO | 2021-12-06 14:45 | 2021-12-06 14:46 | 1464 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21120600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-06 | 1464 | keep | 0 | Dec | 2021 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
ARECIBO | 2021-12-06 14:45 | 2021-12-06 14:46 | 759 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21120600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-06 | 759 | keep | 0 | Dec | 2021 | 0.00051695 | 0.00051695 | Momentary | FALSE | FALSE | Not_TMED_Event | 759
ARECIBO | 2021-12-06 14:45 | 2021-12-06 14:46 | 1500 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21120600000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-06 | 1500 | keep | 0 | Dec | 2021 | 0.0010216 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
BAYAMON | 2021-12-06 14:45 | 2021-12-06 18:33 | 30 | 003:48 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE NO HABIA FUNDIDO | B21120500028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2021-12-06 | 6840 | keep | 0 | Dec | 2021 | 0.0046587 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-06 14:47 | 2021-12-06 15:37 | 20 | 000:50 | P | SECUNDARIA/DESGANCHE | SE REPARO SECUNDARIA DESGANCHE | B21120600109 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 50 | 2021-12-06 | 1000 | keep | 0 | Dec | 2021 | 0.0006811 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-12-06 14:48 | 2021-12-06 14:50 | 225 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SU CARGA POR 1303-5 SE PROBO POR CONTROL QUEDO EN SERVICIO | S21120600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-06 | 450 | keep | 0 | Dec | 2021 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-12-06 14:48 | 2021-12-06 14:50 | 870 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO LLEVA 1303-4 SE PROBO POR CONTROL QUEDO EN SERVICIO | S21120600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-06 | 1740 | keep | 0 | Dec | 2021 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
HUMACAO | 2021-12-06 14:53 | 2021-12-06 19:19 | 10 | 004:26 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR | C21120600102 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 266 | 2021-12-06 | 2660 | keep | 0 | Dec | 2021 | 0.0018117 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-06 14:55 | 2021-12-06 17:16 | 7 | 002:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA SE REPARO SECUNDARIA | S21120600117 | New_Event | Secondary Wire Down | Include | Include | Equipment | 141 | 2021-12-06 | 987 | keep | 0 | Dec | 2021 | 0.00067224 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2021-12-06 14:59 | 2021-12-06 17:34 | 10 | 002:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR REPARO BAJANTE SECUNDARIO EN XMR | C21120600103 | New_Event | Secondary Wire Down | Include | Include | Equipment | 155 | 2021-12-06 | 1550 | keep | 0 | Dec | 2021 | 0.0010557 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-12-06 15:01 | 2021-12-06 15:02 | 3315 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21120600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-06 | 3315 | keep | 0 | Dec | 2021 | 0.0022578 | 0.0022578 | Momentary | FALSE | FALSE | Not_TMED_Event | 3315
CAGUAS | 2021-12-06 15:06 | 2021-12-06 18:39 | 33 | 003:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21120600106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2021-12-06 | 7029 | keep | 0 | Dec | 2021 | 0.0047874 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
PONCE | 2021-12-06 15:13 | 2021-12-06 15:37 | 50 | 000:24 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P21120600051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 24 | 2021-12-06 | 1200 | keep | 0 | Dec | 2021 | 0.00081731 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2021-12-06 15:25 | 2021-12-06 17:15 | 70 | 001:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21120600110 | New_Event | Bad Weather | Include | Include | Weather | 110 | 2021-12-06 | 7700 | keep | 0 | Dec | 2021 | 0.0052444 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
FAJARDO | 2021-12-06 15:53 | 2021-12-06 16:38 | 1 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN XMR | R21120600133 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2021-12-06 | 45 | keep | 0 | Dec | 2021 | 3.0649e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-12-06 16:08 | 2021-12-06 17:32 | 10 | 001:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO TRANSFORMADOR PARA REMPLAZAR CAJA PRIMARIA REMPLAZAR PARARRAYOS Y REPARAR SECUNDARIA | B21120600123 | New_Event | Cutout Failure | Include | Include | Equipment | 84 | 2021-12-06 | 840 | keep | 0 | Dec | 2021 | 0.00057212 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-12-06 16:37 | 2021-12-06 18:11 | 50 | 001:34 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P21120600051 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 94 | 2021-12-06 | 4700 | keep | 0 | Dec | 2021 | 0.0032011 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-12-06 16:59 | 2021-12-06 17:50 | 30 | 000:51 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21120600047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 51 | 2021-12-06 | 1530 | keep | 0 | Dec | 2021 | 0.0010421 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-06 17:10 | 2021-12-06 17:11 | 2107 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21120600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-06 | 2107 | keep | 0 | Dec | 2021 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
CANOVANAS | 2021-12-06 18:06 | 2021-12-06 19:29 | 90 | 001:23 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | R21120600181 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 83 | 2021-12-06 | 7470 | keep | 0 | Dec | 2021 | 0.0050878 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2021-12-06 18:16 | 2021-12-08 17:52 | 5 | 047:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 25 EN CORTE DE LINEA SE REPARO LINEA SECUNDARIA VERIFICADO EN BITACORA | M21120600192 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2856 | 2021-12-06 | 14280 | keep | 0 | Dec | 2021 | 0.009726 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-12-06 18:17 | 2021-12-06 18:18 | 24 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21120600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-06 | 24 | keep | 0 | Dec | 2021 | 1.6346e-05 | 1.6346e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 24
ARECIBO | 2021-12-06 18:18 | 2021-12-06 19:59 | 10 | 001:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR FUERTES LLUVIAS | A21120600098 | New_Event | Bad Weather | Include | Include | Weather | 101 | 2021-12-06 | 1010 | keep | 0 | Dec | 2021 | 0.00068791 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-06 18:21 | 2021-12-06 20:28 | 20 | 002:07 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | B21120600179 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 127 | 2021-12-06 | 2540 | keep | 0 | Dec | 2021 | 0.00173 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-12-06 18:54 | 2021-12-06 22:08 | 30 | 003:14 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21120600198 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 194 | 2021-12-06 | 5820 | keep | 0 | Dec | 2021 | 0.003964 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-06 19:35 | 2021-12-07 11:45 | 25 | 016:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21120600117 | New_Event | Bad Weather | Include | Include | Weather | 970 | 2021-12-06 | 24250 | keep | 0 | Dec | 2021 | 0.016517 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-12-06 20:09 | 2021-12-06 21:40 | 20 | 001:31 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA PODER REALIZAR DESGANCHE DE ARBOL SOBRE LA LINEA | S21120600257 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2021-12-06 | 1820 | keep | 0 | Dec | 2021 | 0.0012396 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2021-12-06 20:14 | 2021-12-06 20:25 | 5 | 000:11 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R21120600280 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 11 | 2021-12-06 | 55 | keep | 0 | Dec | 2021 | 3.746e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-12-06 20:15 | 2021-12-07 09:52 | 10 | 013:37 | P | NO SE REPORTO CAUSA | 1 X 10 XMR NO CAUSA | C21120600210 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 817 | 2021-12-06 | 8170 | keep | 0 | Dec | 2021 | 0.0055645 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-06 20:26 | 2021-12-06 21:20 | 60 | 000:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA | S21120600260 | New_Event | Cutout Failure | Include | Include | Equipment | 54 | 2021-12-06 | 3240 | keep | 0 | Dec | 2021 | 0.0022067 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-12-06 20:42 | 2021-12-06 20:43 | 478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1705-01 LLEVANDO PARTE DE LA CARGA 1705-03 | B21120600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-06 | 478 | keep | 0 | Dec | 2021 | 0.00032556 | 0.00032556 | Momentary | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2021-12-06 20:42 | 2021-12-06 20:43 | 850 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1705-01 LLEVANDO PARTE DE LA CARGA 1705-03 | B21120600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-06 | 850 | keep | 0 | Dec | 2021 | 0.00057893 | 0.00057893 | Momentary | FALSE | FALSE | Not_TMED_Event | 850
MAYAGÃœEZ | 2021-12-06 20:50 | 2021-12-06 20:51 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21120600223 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-06 | 990 | keep | 0 | Dec | 2021 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
CANOVANAS | 2021-12-06 21:00 | 2021-12-06 21:24 | 90 | 000:24 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | R21120600124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 24 | 2021-12-06 | 2160 | keep | 0 | Dec | 2021 | 0.0014712 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2021-12-06 21:05 | 2021-12-06 21:06 | 4188 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21120600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-06 | 4188 | keep | 0 | Dec | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
SAN JUAN | 2021-12-06 21:09 | 2021-12-07 11:40 | 50 | 014:31 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21120600065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 871 | 2021-12-06 | 43550 | keep | 0 | Dec | 2021 | 0.029662 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-12-06 21:35 | 2021-12-07 12:12 | 10 | 014:37 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO Y LEVANTO SECUNDARIA | C21120600218 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 877 | 2021-12-06 | 8770 | keep | 0 | Dec | 2021 | 0.0059732 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-06 21:38 | 2021-12-06 21:39 | 290 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO | S21120600267 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-06 | 290 | keep | 0 | Dec | 2021 | 0.00019752 | 0.00019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 290
AGUADILLA | 2021-12-06 22:08 | 2021-12-07 10:09 | 100 | 012:01 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21120600226 | New_Event | Vegetation Contact | Include | Include | Vegetation | 721 | 2021-12-06 | 72100 | keep | 0 | Dec | 2021 | 0.049107 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-12-06 22:43 | 2021-12-07 09:30 | 80 | 010:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L CRUCE X AVE | C21120600219 | New_Event |  |  | Include | Wildlife | 647 | 2021-12-06 | 51760 | keep | 0 | Dec | 2021 | 0.035254 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2021-12-06 23:26 | 2021-12-07 10:11 | 40 | 010:45 | P | DESGANCHE | 1 X 65 EN C/L | C21120600222 | New_Event | Vegetation Contact | Include | Include | Vegetation | 645 | 2021-12-06 | 25800 | keep | 0 | Dec | 2021 | 0.017572 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-12-07 00:21 | 2021-12-07 00:22 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21120700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-07 | 308 | keep | 0 | Dec | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
PONCE | 2021-12-07 01:27 | 2021-12-07 11:33 | 100 | 010:06 | P | PROTECCION DEFECTUOSA | 2 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSAS | P21120700003 | New_Event | Protection Miscoordination | Include | Include | Other | 606 | 2021-12-07 | 60600 | keep | 0 | Dec | 2021 | 0.041274 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-12-07 01:49 | 2021-12-07 09:16 | 100 | 007:27 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA | B21120700002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 447 | 2021-12-07 | 44700 | keep | 0 | Dec | 2021 | 0.030445 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-12-07 02:19 | 2021-12-07 11:22 | 20 | 009:03 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21120700003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 543 | 2021-12-07 | 10860 | keep | 0 | Dec | 2021 | 0.0073967 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-12-07 02:34 | 2021-12-07 11:36 | 50 | 009:02 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA Y DESGANCHE | B21120700005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 542 | 2021-12-07 | 27100 | keep | 0 | Dec | 2021 | 0.018458 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-12-07 03:53 | 2021-12-07 03:54 | 2126 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21120700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-07 | 2126 | keep | 0 | Dec | 2021 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
ARECIBO | 2021-12-07 04:15 | 2021-12-07 09:17 | 15 | 005:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21120700001 | New_Event | Bad Weather | Include | Include | Weather | 302 | 2021-12-07 | 4530 | keep | 0 | Dec | 2021 | 0.0030854 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-12-07 04:52 | 2021-12-07 14:52 | 25 | 010:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR CAUSA RATA | B21120700036 | New_Event |  |  | Include | Wildlife | 600 | 2021-12-07 | 15000 | keep | 0 | Dec | 2021 | 0.010216 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2021-12-07 05:05 | 2021-12-07 10:52 | 2608 | 005:47 | S | PARARRAYOS DEFECTUOSO | SE REMPLAZO PARARRAYO Y CAJA DE LA MEDICION REMOTA | C21120700042 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 347 | 2021-12-07 | 904976 | keep | 0 | Dec | 2021 | 0.61638 | 0.0017763 | Sustained | FALSE | FALSE | Not_TMED_Event | 2608
CAGUAS | 2021-12-07 05:05 | 2021-12-07 10:52 | 845 | 005:47 | S | PARARRAYOS DEFECTUOSO | SE REMPLAZO PARARRAYO Y CAJA DE LA MEDICION REMOTA | C21120700042 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 347 | 2021-12-07 | 293215 | keep | 0 | Dec | 2021 | 0.19971 | 0.00057553 | Sustained | FALSE | FALSE | Not_TMED_Event | 845
HUMACAO | 2021-12-07 05:23 | 2021-12-07 05:24 | 2126 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21120700008 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-07 | 2126 | keep | 0 | Dec | 2021 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
PONCE | 2021-12-07 05:33 | 2021-12-07 10:26 | 100 | 004:53 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE REPORTO CAUSA | P21120700007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 293 | 2021-12-07 | 29300 | keep | 0 | Dec | 2021 | 0.019956 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2021-12-07 05:43 | 2021-12-07 10:16 | 1 | 004:33 | P | NO SE REPORTO CAUSA | 1 X 15 EN MONTURA NO SE REPORTO CAUSA | P21120700009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 273 | 2021-12-07 | 273 | keep | 0 | Dec | 2021 | 0.00018594 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-07 05:57 | 2021-12-07 09:36 | 40 | 003:39 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21120700010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 219 | 2021-12-07 | 8760 | keep | 0 | Dec | 2021 | 0.0059664 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-12-07 06:05 | 2021-12-07 13:34 | 50 | 007:29 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21120700002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 449 | 2021-12-07 | 22450 | keep | 0 | Dec | 2021 | 0.015291 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-12-07 06:30 | 2021-12-07 10:56 | 10 | 004:26 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | C21120700014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 266 | 2021-12-07 | 2660 | keep | 0 | Dec | 2021 | 0.0018117 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-07 06:37 | 2021-12-07 15:13 | 5 | 008:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO PEDESTAL SECUNDARIO | R21120600011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 516 | 2021-12-07 | 2580 | keep | 0 | Dec | 2021 | 0.0017572 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-12-07 06:37 | 2021-12-07 06:38 | 5961 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1713-05 LLEVANDO 95% DEL 1717-02 | B21120700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-07 | 5961 | keep | 0 | Dec | 2021 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2021-12-07 06:37 | 2021-12-07 06:38 | 865 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE ALIMENTADOR 1713-05 LLEVA TRANSFERIDA EL 95% DE LA CARGA DEL ALIMENTADOR 1717-02 | B21120700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-07 | 865 | keep | 0 | Dec | 2021 | 0.00058915 | 0.00058915 | Momentary | FALSE | FALSE | Not_TMED_Event | 865
BAYAMON | 2021-12-07 06:38 | 2021-12-07 06:39 | 5961 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1713-05 LLEVANDO 95% DEL 1717-02 | B21120700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-07 | 5961 | keep | 0 | Dec | 2021 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2021-12-07 06:38 | 2021-12-07 06:39 | 865 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE ALIMENTADOR 1713-05 LLEVA TRANSFERIDA EL 95% DE LA CARGA DEL ALIMENTADOR 1717-02 | B21120700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-07 | 865 | keep | 0 | Dec | 2021 | 0.00058915 | 0.00058915 | Momentary | FALSE | FALSE | Not_TMED_Event | 865
PONCE | 2021-12-07 06:39 | 2021-12-07 09:15 | 150 | 002:36 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21120700011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2021-12-07 | 23400 | keep | 0 | Dec | 2021 | 0.015938 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2021-12-07 06:52 | 2021-12-07 09:59 | 50 | 003:07 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | P21120700012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2021-12-07 | 9350 | keep | 0 | Dec | 2021 | 0.0063682 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-12-07 07:16 | 2021-12-07 12:07 | 120 | 004:51 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA SE PATRULLO | R21120700002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 291 | 2021-12-07 | 34920 | keep | 0 | Dec | 2021 | 0.023784 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2021-12-07 07:24 | 2021-12-07 16:39 | 10 | 009:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | M21120700008 | New_Event |  |  | Include | Wildlife | 555 | 2021-12-07 | 5550 | keep | 0 | Dec | 2021 | 0.0037801 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-07 07:36 | 2021-12-07 11:46 | 1 | 004:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA CAJA EN CORTE DE LINEA | S21120700005 | New_Event | Wire Down | Include | Include | Equipment | 250 | 2021-12-07 | 250 | keep | 0 | Dec | 2021 | 0.00017027 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-12-07 07:41 | 2021-12-08 11:27 | 1 | 027:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR FUERTES LLUVIAS | A21120700007 | New_Event | Bad Weather | Include | Include | Weather | 1666 | 2021-12-07 | 1666 | keep | 0 | Dec | 2021 | 0.0011347 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-12-07 07:41 | 2021-12-07 14:17 | 10 | 006:36 | P | NO SE REPORTO CAUSA | 1 X 15 Y SE DESGANCHO | B21120700030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 396 | 2021-12-07 | 3960 | keep | 0 | Dec | 2021 | 0.0026971 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-12-07 07:42 | 2021-12-07 10:06 | 100 | 002:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN C/L REPARO BAJANTE PRIMARIO DE LINEA A CAJA | R21120700003 | New_Event | Wire Down | Include | Include | Equipment | 144 | 2021-12-07 | 14400 | keep | 0 | Dec | 2021 | 0.0098078 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2021-12-07 07:51 | 2021-12-07 10:20 | 20 | 002:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN C/L CRUCE X AVE Y REEMPLAZO AISLADOR | R21120700004 | New_Event |  |  | Include | Wildlife | 149 | 2021-12-07 | 2980 | keep | 0 | Dec | 2021 | 0.0020297 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-12-07 07:57 | 2021-12-07 14:41 | 5 | 006:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN XMR REPARO BAJANTE SECUNDARIO | C21120700025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 404 | 2021-12-07 | 2020 | keep | 0 | Dec | 2021 | 0.0013758 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-12-07 08:01 | 2021-12-07 17:24 | 70 | 009:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | M21120700013 | New_Event | Cutout Failure | Include | Include | Equipment | 563 | 2021-12-07 | 39410 | keep | 0 | Dec | 2021 | 0.026842 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2021-12-07 08:02 | 2021-12-07 16:12 | 8 | 008:10 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | C21120700027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 490 | 2021-12-07 | 3920 | keep | 0 | Dec | 2021 | 0.0026699 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2021-12-07 08:12 | 2021-12-07 15:30 | 15 | 007:18 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO Y SE CERRARON PUENTES SIN CARGA CON VOLTAJE | P21120700021 | New_Event | Defective Pole | Include | Include | Equipment | 438 | 2021-12-07 | 6570 | keep | 0 | Dec | 2021 | 0.0044748 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-12-07 08:21 | 2021-12-07 10:59 | 100 | 002:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | P21120700022 | New_Event | Bad Weather | Include | Include | Weather | 158 | 2021-12-07 | 15800 | keep | 0 | Dec | 2021 | 0.010761 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2021-12-07 08:22 | 2021-12-07 09:50 | 10 | 001:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | R21120700006 | New_Event | Secondary Wire Down | Include | Include | Equipment | 88 | 2021-12-07 | 880 | keep | 0 | Dec | 2021 | 0.00059936 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-12-07 08:41 | 2021-12-07 16:29 | 50 | 007:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21120700010 | New_Event | Bad Weather | Include | Include | Weather | 468 | 2021-12-07 | 23400 | keep | 0 | Dec | 2021 | 0.015938 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-12-07 08:48 | 2021-12-07 10:34 | 1565 | 001:46 | T | DESGANCHE | SECCIONALIZO EL ALIMENTADOR | C21120700033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2021-12-07 | 165890 | keep | 0 | Dec | 2021 | 0.11299 | 0.0010659 | Sustained | FALSE | FALSE | Not_TMED_Event | 1565
SAN JUAN | 2021-12-07 08:56 | 2021-12-07 11:07 | 20 | 002:11 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21120700009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2021-12-07 | 2620 | keep | 0 | Dec | 2021 | 0.0017845 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-12-07 09:00 | 2021-12-07 13:14 | 65 | 004:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN SU-1 Y SE REEMPLAZO CAJA AVERIADA EN RISER | S21120700010 | New_Event | Cutout Failure | Include | Include | Equipment | 254 | 2021-12-07 | 16510 | keep | 0 | Dec | 2021 | 0.011245 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2021-12-07 09:11 | 2021-12-07 15:32 | 12 | 006:21 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | S21120700012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 381 | 2021-12-07 | 4572 | keep | 0 | Dec | 2021 | 0.003114 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-12-07 09:12 | 2021-12-07 09:54 | 7 | 000:42 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHO | C21120700038 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 42 | 2021-12-07 | 294 | keep | 0 | Dec | 2021 | 0.00020024 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2021-12-07 09:15 | 2021-12-07 11:04 | 253 | 001:49 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO BREAKER DE EMERGENCIA PARA REMPLAZAR MACHETE QUEMADO EN TRONCAL NO HAY PARCIAL | P21120700033 | New_Event | Switch Failure | Include | Include | Equipment | 109 | 2021-12-07 | 27577 | keep | 0 | Dec | 2021 | 0.018783 | 0.00017232 | Sustained | FALSE | FALSE | Not_TMED_Event | 253
VEGA BAJA | 2021-12-07 09:19 | 2021-12-07 14:54 | 20 | 005:35 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA Y DESGANCHE | B21120700026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 335 | 2021-12-07 | 6700 | keep | 0 | Dec | 2021 | 0.0045633 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-12-07 09:27 | 2021-12-07 10:50 | 10 | 001:23 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | A21120700016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2021-12-07 | 830 | keep | 0 | Dec | 2021 | 0.00056531 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-07 09:28 | 2021-12-07 20:45 | 40 | 011:17 | P | ESTRUCTURA AVERIADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO | A21120700018 | New_Event | Defective Pole | Include | Include | Equipment | 677 | 2021-12-07 | 27080 | keep | 0 | Dec | 2021 | 0.018444 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2021-12-07 09:39 | 2021-12-07 09:41 | 934 | 000:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR NO RECERRO CERRADO POR SCADA | A21120700022 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2021-12-07 | 1868 | keep | 0 | Dec | 2021 | 0.0012723 | 0.00063614 | Momentary | FALSE | FALSE | Not_TMED_Event | 934
ARECIBO | 2021-12-07 09:40 | 2021-12-07 11:00 | 4 | 001:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21120700020 | New_Event | Secondary Wire Down | Include | Include | Equipment | 80 | 2021-12-07 | 320 | keep | 0 | Dec | 2021 | 0.00021795 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2021-12-07 09:41 | 2021-12-07 16:50 | 150 | 007:09 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO CORTE DE LINEA PARA REPARAR AISLADOR PARTIDO | A21120700033 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 429 | 2021-12-07 | 64350 | keep | 0 | Dec | 2021 | 0.043828 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2021-12-07 10:05 | 2021-12-07 13:40 | 30 | 003:35 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21120700030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 215 | 2021-12-07 | 6450 | keep | 0 | Dec | 2021 | 0.0043931 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-12-07 10:13 | 2021-12-07 11:52 | 25 | 001:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE X AVE | C21120700051 | New_Event |  |  | Include | Wildlife | 99 | 2021-12-07 | 2475 | keep | 0 | Dec | 2021 | 0.0016857 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-12-07 10:18 | 2021-12-07 10:19 | 112 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA PARTE DEL 1801-01 | B21120700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-07 | 112 | keep | 0 | Dec | 2021 | 7.6283e-05 | 7.6283e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 112
CAGUAS | 2021-12-07 10:34 | 2021-12-07 11:12 | 1000 | 000:38 | P | DESGANCHE | SE RETIRO RAMAS CRUZANDO LAS LINEAS | C21120700033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 38 | 2021-12-07 | 38000 | keep | 0 | Dec | 2021 | 0.025882 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
CANOVANAS | 2021-12-07 10:37 | 2021-12-07 12:10 | 16 | 001:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE QUEMADO | R21120700017 | New_Event | Cutout Failure | Include | Include | Equipment | 93 | 2021-12-07 | 1488 | keep | 0 | Dec | 2021 | 0.0010135 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
UTUADO | 2021-12-07 10:40 | 2021-12-07 13:20 | 100 | 002:40 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR POSTE PARTIDO 35' MADERA X 45' METAL | A21120700027 | New_Event | Defective Pole | Include | Include | Equipment | 160 | 2021-12-07 | 16000 | keep | 0 | Dec | 2021 | 0.010898 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2021-12-07 10:41 | 2021-12-07 14:37 | 10 | 003:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA CRUCE CON AVE | R21120700019 | New_Event |  |  | Include | Wildlife | 236 | 2021-12-07 | 2360 | keep | 0 | Dec | 2021 | 0.0016074 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-07 10:44 | 2021-12-07 17:11 | 6 | 006:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | M21120700035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 387 | 2021-12-07 | 2322 | keep | 0 | Dec | 2021 | 0.0015815 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2021-12-07 11:00 | 2021-12-07 11:52 | 25 | 000:52 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21120700025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 52 | 2021-12-07 | 1300 | keep | 0 | Dec | 2021 | 0.00088542 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-12-07 11:02 | 2021-12-07 13:24 | 69 | 002:22 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA 2 X 40 EN RISER SE PATRULLO NO SE ENCONTRO CAUSA | R21120700021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 142 | 2021-12-07 | 9798 | keep | 0 | Dec | 2021 | 0.0066734 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
PONCE | 2021-12-07 11:04 | 2021-12-07 14:00 | 150 | 002:56 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21120700011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2021-12-07 | 26400 | keep | 0 | Dec | 2021 | 0.017981 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2021-12-07 11:15 | 2021-12-07 14:31 | 4 | 003:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REEMPLAZO PORTAFUSIBLE PARTIDO | C21120700062 | New_Event | Cutout Failure | Include | Include | Equipment | 196 | 2021-12-07 | 784 | keep | 0 | Dec | 2021 | 0.00053398 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2021-12-07 11:28 | 2021-12-07 16:48 | 10 | 005:20 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR QUEMADO DE 50 KVA X 50 KVA Y CAJAS QUEMADAS | C21120700063 | New_Event | Service Transformer Failure | Include | Include | Equipment | 320 | 2021-12-07 | 3200 | keep | 0 | Dec | 2021 | 0.0021795 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2021-12-07 11:30 | 2021-12-07 12:07 | 15 | 000:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | P21120700051 | New_Event | Secondary Wire Down | Include | Include | Equipment | 37 | 2021-12-07 | 555 | keep | 0 | Dec | 2021 | 0.00037801 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-12-07 11:46 | 2021-12-07 11:54 | 290 | 000:08 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA TRABAJAR PUENTE ABIERTO DE LINEA A CAJA EN AZOTEA | S21120700024 | New_Event | Wire Down | Include | Include | Equipment | 8 | 2021-12-07 | 2320 | keep | 0 | Dec | 2021 | 0.0015801 | 0.00019752 | Sustained | FALSE | FALSE | Not_TMED_Event | 290
VEGA BAJA | 2021-12-07 11:52 | 2021-12-07 11:53 | 603 | 000:01 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR | B21120700000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2021-12-07 | 603 | keep | 0 | Dec | 2021 | 0.0004107 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
VEGA BAJA | 2021-12-07 11:53 | 2021-12-07 15:58 | 1 | 004:05 | P | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR AL HACER PRUEBA DE VS EN CALLE PASEO DEL CRISTO HACIA SU DE ESCUELA EN CASCO URBANO DE DORADO | B21120700000 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 245 | 2021-12-07 | 245 | keep | 0 | Dec | 2021 | 0.00016687 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-07 11:54 | 2021-12-07 12:14 | 1 | 000:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA CAJA EN CORTE DE LINEA | S21120700005 | Partial_restoration | Wire Down | Include | Include | Equipment | 20 | 2021-12-07 | 20 | keep | 0 | Dec | 2021 | 1.3622e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-12-07 12:05 | 2021-12-07 14:26 | 20 | 002:21 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21120700034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 141 | 2021-12-07 | 2820 | keep | 0 | Dec | 2021 | 0.0019207 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2021-12-07 12:08 | 2021-12-08 13:25 | 100 | 025:17 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO CORTE DE LINEA PARA REMPLAZAR AISLADOR | M21120700043 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1517 | 2021-12-07 | 151700 | keep | 0 | Dec | 2021 | 0.10332 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-12-07 12:11 | 2021-12-07 12:12 | 199 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21120700045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-07 | 199 | keep | 0 | Dec | 2021 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
HUMACAO | 2021-12-07 12:12 | 2021-12-07 14:58 | 1 | 002:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 140 EN RISER SE REEMPLAZO CAJA PRIMARIA QUEMADA | C21120700069 | New_Event | Cutout Failure | Include | Include | Equipment | 166 | 2021-12-07 | 166 | keep | 0 | Dec | 2021 | 0.00011306 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2021-12-07 12:12 | 2021-12-07 20:14 | 40 | 008:02 | P | DESGANCHE | 1 X 40 EN C/L | C21120700071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 482 | 2021-12-07 | 19280 | keep | 0 | Dec | 2021 | 0.013132 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-07 12:14 | 2021-12-07 12:24 | 290 | 000:10 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE DE LINEA TRONCAL EN AZOTEA | S21120700028 | Additional_clients | Wire Down | Include | Include | Equipment | 10 | 2021-12-07 | 2900 | keep | 0 | Dec | 2021 | 0.0019752 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-12-07 12:15 | 2021-12-07 14:48 | 100 | 002:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21120700046 | New_Event | Bad Weather | Include | Include | Weather | 153 | 2021-12-07 | 15300 | keep | 0 | Dec | 2021 | 0.010421 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-12-07 12:20 | 2021-12-07 14:26 | 50 | 002:06 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21120700037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2021-12-07 | 6300 | keep | 0 | Dec | 2021 | 0.0042909 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2021-12-07 12:26 | 2021-12-07 12:27 | 10 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR | P21120700016 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-12-07 | 10 | keep | 0 | Dec | 2021 | 6.811e-06 | 6.811e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-12-07 12:33 | 2021-12-07 13:59 | 10 | 001:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR REEMPLAZO CAJA AVERIADA | R21120700026 | New_Event | Cutout Failure | Include | Include | Equipment | 86 | 2021-12-07 | 860 | keep | 0 | Dec | 2021 | 0.00058574 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-07 12:36 | 2021-12-07 15:18 | 35 | 002:42 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 20 EN CORTES DE LINEAS Y 1 X 15 EN RISER | B21120700040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 162 | 2021-12-07 | 5670 | keep | 0 | Dec | 2021 | 0.0038618 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2021-12-07 12:48 | 2021-12-07 12:49 | 225 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 QUE LLEVA A SU VEZ EL 1303-04 | S21120700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-07 | 225 | keep | 0 | Dec | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-12-07 12:48 | 2021-12-07 12:49 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 QUE LLEVA A SU VEZ EL 1303-04 | S21120700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-07 | 870 | keep | 0 | Dec | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2021-12-07 13:00 | 2021-12-07 14:03 | 10 | 001:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | S21120700008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 63 | 2021-12-07 | 630 | keep | 0 | Dec | 2021 | 0.00042909 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-07 13:27 | 2021-12-07 23:30 | 12 | 010:03 | P | SECUNDARIA/ESTRUCTURA AVERIADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO POSTE SECUNDARIO PARTIDO | M21120700005 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 603 | 2021-12-07 | 7236 | keep | 0 | Dec | 2021 | 0.0049284 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2021-12-07 13:41 | 2021-12-07 15:40 | 20 | 001:59 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21120700048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 119 | 2021-12-07 | 2380 | keep | 0 | Dec | 2021 | 0.001621 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-12-07 13:42 | 2021-12-07 18:52 | 100 | 005:10 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21120700037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 310 | 2021-12-07 | 31000 | keep | 0 | Dec | 2021 | 0.021114 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-12-07 14:02 | 2021-12-07 17:04 | 60 | 003:02 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA INFORMA JOURNEYMAN NO ENCONTRO CAUSA | M21120700060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 182 | 2021-12-07 | 10920 | keep | 0 | Dec | 2021 | 0.0074376 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-12-07 14:18 | 2021-12-07 19:09 | 60 | 004:51 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA INFORMA JOURNEYMAN REQUIERE DESGANCHE | M21120700066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 291 | 2021-12-07 | 17460 | keep | 0 | Dec | 2021 | 0.011892 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-12-07 14:18 | 2021-12-07 15:44 | 9 | 001:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | A21120700069 | New_Event | Bad Weather | Include | Include | Weather | 86 | 2021-12-07 | 774 | keep | 0 | Dec | 2021 | 0.00052717 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2021-12-07 14:31 | 2021-12-07 16:26 | 3 | 001:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | R21120700036 | New_Event | Cutout Failure | Include | Include | Equipment | 115 | 2021-12-07 | 345 | keep | 0 | Dec | 2021 | 0.00023498 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2021-12-07 14:33 | 2021-12-07 16:29 | 6 | 001:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REGULARLO Y REPARAR SECUNDARIA SUBIO TAP 4 AL 5 QUEDO 125/250V | C21120700107 | New_Event | Secondary Wire Down | Include | Include | Equipment | 116 | 2021-12-07 | 696 | keep | 0 | Dec | 2021 | 0.00047404 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-12-07 14:34 | 2021-12-07 15:05 | 12 | 000:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | B21120700036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 31 | 2021-12-07 | 372 | keep | 0 | Dec | 2021 | 0.00025337 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-12-07 14:37 | 2021-12-07 16:08 | 7 | 001:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR LINEA SECUNDARIA | C21120700000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 91 | 2021-12-07 | 637 | keep | 0 | Dec | 2021 | 0.00043386 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2021-12-07 14:41 | 2021-12-07 14:56 | 1 | 000:15 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | R21120700038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2021-12-07 | 15 | keep | 0 | Dec | 2021 | 1.0216e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-12-07 14:46 | 2021-12-07 16:51 | 50 | 002:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE X AVE | C21120700113 | New_Event |  |  | Include | Wildlife | 125 | 2021-12-07 | 6250 | keep | 0 | Dec | 2021 | 0.0042568 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-12-07 14:46 | 2021-12-07 20:24 | 100 | 005:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L CRUCE X AVE | C21120700152 | New_Event |  |  | Include | Wildlife | 338 | 2021-12-07 | 33800 | keep | 0 | Dec | 2021 | 0.023021 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-12-07 14:47 | 2021-12-07 16:15 | 4 | 001:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C21120700114 | New_Event | Secondary Wire Down | Include | Include | Equipment | 88 | 2021-12-07 | 352 | keep | 0 | Dec | 2021 | 0.00023975 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2021-12-07 14:50 | 2021-12-07 16:43 | 11 | 001:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | M21120700064 | New_Event | Secondary Wire Down | Include | Include | Equipment | 113 | 2021-12-07 | 1243 | keep | 0 | Dec | 2021 | 0.0008466 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2021-12-07 14:56 | 2021-12-07 18:34 | 30 | 003:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 Y 1 X 50 EN CORTES DE LINEA SE LEVANTO ALAMBRE PRIMARIO PARTIDO | B21120700068 | New_Event | Wire Down | Include | Include | Equipment | 218 | 2021-12-07 | 6540 | keep | 0 | Dec | 2021 | 0.0044544 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-12-07 15:05 | 2021-12-07 18:26 | 12 | 003:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | S21120700070 | New_Event | Secondary Wire Down | Include | Include | Equipment | 201 | 2021-12-07 | 2412 | keep | 0 | Dec | 2021 | 0.0016428 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-12-07 15:12 | 2021-12-07 18:55 | 150 | 003:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO | B21120700069 | New_Event | Wire Down | Include | Include | Equipment | 223 | 2021-12-07 | 33450 | keep | 0 | Dec | 2021 | 0.022783 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2021-12-07 15:17 | 2021-12-07 15:57 | 6 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO CONECTORES | R21120700039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2021-12-07 | 240 | keep | 0 | Dec | 2021 | 0.00016346 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-12-07 15:24 | 2021-12-07 21:40 | 2 | 006:16 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN TRANSFORMADOR SE RETIRO ENREDADERA | M21120700083 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 376 | 2021-12-07 | 752 | keep | 0 | Dec | 2021 | 0.00051218 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2021-12-07 15:40 | 2021-12-07 17:38 | 100 | 001:58 | P | DESGANCHE | 2 X 50 EN C/L | C21120700125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2021-12-07 | 11800 | keep | 0 | Dec | 2021 | 0.0080369 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-12-07 15:43 | 2021-12-07 18:11 | 200 | 002:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | M21120700088 | New_Event |  |  | Include | Wildlife | 148 | 2021-12-07 | 29600 | keep | 0 | Dec | 2021 | 0.02016 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
GUAYAMA | 2021-12-07 15:46 | 2021-12-07 19:41 | 50 | 003:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21120700086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 235 | 2021-12-07 | 11750 | keep | 0 | Dec | 2021 | 0.0080029 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-12-07 15:46 | 2021-12-07 17:48 | 20 | 002:02 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21120700072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2021-12-07 | 2440 | keep | 0 | Dec | 2021 | 0.0016619 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-12-07 15:58 | 2021-12-07 15:59 | 603 | 000:01 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR AL HACER PRUEBA DE VS EN CALLE PASEO DEL CRISTO HACIA SU DE ESCUELA EN CASCO URBANO DE DORADO | B21120600000 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1 | 2021-12-07 | 603 | keep | 0 | Dec | 2021 | 0.0004107 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-12-07 16:00 | 2021-12-07 16:41 | 3 | 000:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | M21120700016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 41 | 2021-12-07 | 123 | keep | 0 | Dec | 2021 | 8.3775e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2021-12-07 16:07 | 2021-12-07 18:02 | 7 | 001:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR LINEA SECUNDARIA | P21120700087 | New_Event | Secondary Wire Down | Include | Include | Equipment | 115 | 2021-12-07 | 805 | keep | 0 | Dec | 2021 | 0.00054828 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-12-07 16:21 | 2021-12-07 16:50 | 10 | 000:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA EN PEDESTAL | B21120700031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 29 | 2021-12-07 | 290 | keep | 0 | Dec | 2021 | 0.00019752 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-07 16:41 | 2021-12-08 09:30 | 12 | 016:49 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO | M21120700101 | New_Event | Bad Weather | Include | Include | Weather | 1009 | 2021-12-07 | 12108 | keep | 0 | Dec | 2021 | 0.0082467 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2021-12-07 16:50 | 2021-12-08 12:22 | 1 | 019:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR POR FUERTES LLUVIAS | A21120700083 | New_Event | Bad Weather | Include | Include | Weather | 1172 | 2021-12-07 | 1172 | keep | 0 | Dec | 2021 | 0.00079824 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-07 16:51 | 2021-12-07 19:02 | 20 | 002:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA IGUANA CRUZO FASE | S21120700082 | New_Event |  |  | Include | Wildlife | 131 | 2021-12-07 | 2620 | keep | 0 | Dec | 2021 | 0.0017845 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-12-07 16:54 | 2021-12-07 16:56 | 1565 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO | C21120700131 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2021-12-07 | 3130 | keep | 0 | Dec | 2021 | 0.0021318 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
CAGUAS | 2021-12-07 16:56 | 2021-12-07 19:51 | 250 | 002:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE | C21120700000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 175 | 2021-12-07 | 43750 | keep | 0 | Dec | 2021 | 0.029798 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
ARECIBO | 2021-12-07 17:12 | 2021-12-08 00:24 | 4 | 007:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO LINEAS SECUNDARIAS CRUZADAS | A21120700099 | New_Event | Secondary Wire Down | Include | Include | Equipment | 432 | 2021-12-07 | 1728 | keep | 0 | Dec | 2021 | 0.0011769 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2021-12-07 17:20 | 2021-12-07 18:16 | 10 | 000:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR CONECTORES Y BAJANTE SECUNDARIO | B21120700078 | New_Event | Secondary Wire Down | Include | Include | Equipment | 56 | 2021-12-07 | 560 | keep | 0 | Dec | 2021 | 0.00038141 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-12-07 17:21 | 2021-12-07 19:31 | 100 | 002:10 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21120700044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2021-12-07 | 13000 | keep | 0 | Dec | 2021 | 0.0088542 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-12-07 17:30 | 2021-12-07 19:58 | 8 | 002:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR BAJANTE | S21120700087 | New_Event | Secondary Wire Down | Include | Include | Equipment | 148 | 2021-12-07 | 1184 | keep | 0 | Dec | 2021 | 0.00080642 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-12-07 17:32 | 2021-12-07 19:07 | 45 | 001:35 | P | DESGANCHE | 1 X 65 EN C/L | C21120700138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2021-12-07 | 4275 | keep | 0 | Dec | 2021 | 0.0029117 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2021-12-07 17:48 | 2021-12-08 09:51 | 50 | 016:03 | P | DESGANCHE | 1 X 50 EN C/L | C21120700143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 963 | 2021-12-07 | 48150 | keep | 0 | Dec | 2021 | 0.032795 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-12-07 17:50 | 2021-12-07 19:53 | 20 | 002:03 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA X 37.5 KVA | A21120700088 | New_Event | Service Transformer Failure | Include | Include | Equipment | 123 | 2021-12-07 | 2460 | keep | 0 | Dec | 2021 | 0.0016755 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2021-12-07 18:00 | 2021-12-07 18:35 | 2 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21120700054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2021-12-07 | 70 | keep | 0 | Dec | 2021 | 4.7677e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2021-12-07 18:06 | 2021-12-07 18:29 | 990 | 000:23 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR PERSONAL TRABAJANDO CON RECIERRE EN OFF SE VERIFICO PERSONAL FUERA DE LAS LINEAS SE CERRO INTERRUPTOR | M21120700117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 23 | 2021-12-07 | 22770 | keep | 0 | Dec | 2021 | 0.015509 | 0.00067428 | Sustained | FALSE | FALSE | Not_TMED_Event | 990
BAYAMON | 2021-12-07 18:33 | 2021-12-07 19:28 | 10 | 000:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21120700080 | New_Event | Secondary Wire Down | Include | Include | Equipment | 55 | 2021-12-07 | 550 | keep | 0 | Dec | 2021 | 0.0003746 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-12-07 18:46 | 2021-12-08 11:57 | 5 | 017:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR NEUTRAL SECUNDARIO | C21120700154 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1031 | 2021-12-07 | 5155 | keep | 0 | Dec | 2021 | 0.003511 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2021-12-07 19:22 | 2021-12-08 16:39 | 30 | 021:17 | P | DESGANCHE | 1 X 30 EN C/L | C21120700155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1277 | 2021-12-07 | 38310 | keep | 0 | Dec | 2021 | 0.026093 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-07 19:46 | 2021-12-08 11:25 | 12 | 015:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR FUERTES LLUVIAS | A21120700093 | New_Event | Bad Weather | Include | Include | Weather | 939 | 2021-12-07 | 11268 | keep | 0 | Dec | 2021 | 0.0076746 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-12-07 19:51 | 2021-12-07 20:43 | 1565 | 000:52 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE | C21120700156 | Additional_clients | Wire Down | Include | Include | Equipment | 52 | 2021-12-07 | 81380 | keep | 0 | Dec | 2021 | 0.055428 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-07 19:58 | 2021-12-07 21:08 | 12 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | S21120700075 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2021-12-07 | 840 | keep | 0 | Dec | 2021 | 0.00057212 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-12-07 20:11 | 2021-12-07 20:12 | 181 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21120700164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-07 | 181 | keep | 0 | Dec | 2021 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
HUMACAO | 2021-12-07 20:12 | 2021-12-07 20:13 | 181 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21120700167 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-07 | 181 | keep | 0 | Dec | 2021 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
SAN JUAN | 2021-12-07 20:17 | 2021-12-07 20:18 | 225 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1303-5 | S21120700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-07 | 225 | keep | 0 | Dec | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-12-07 20:17 | 2021-12-07 20:18 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA CARGA 1303-4 | S21120700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-07 | 870 | keep | 0 | Dec | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
VEGA BAJA | 2021-12-07 21:37 | 2021-12-07 23:23 | 3 | 001:46 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B21120700087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2021-12-07 | 318 | keep | 0 | Dec | 2021 | 0.00021659 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2021-12-07 23:04 | 2021-12-08 15:32 | 100 | 016:28 | P | DESGANCHE | 2 X 65 EN C/L | C21120700178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 988 | 2021-12-07 | 98800 | keep | 0 | Dec | 2021 | 0.067292 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2021-12-07 23:24 | 2021-12-08 09:57 | 100 | 010:33 | P | DESGANCHE | 1 X 80 EN SU-9 Y 1 X 40 EN SU-5 MATERIAL VEGETATIVO CRUZO FASE | P21120700103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 633 | 2021-12-07 | 63300 | keep | 0 | Dec | 2021 | 0.043113 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-12-07 23:25 | 2021-12-08 11:51 | 2 | 012:26 | P | DESGANCHE | 1 X 65 EN C/L | C21120700180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 746 | 2021-12-07 | 1492 | keep | 0 | Dec | 2021 | 0.0010162 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
UTUADO | 2021-12-07 23:35 | 2021-12-08 01:00 | 4 | 001:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21120700097 | New_Event | Secondary Wire Down | Include | Include | Equipment | 85 | 2021-12-07 | 340 | keep | 0 | Dec | 2021 | 0.00023157 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
FAJARDO | 2021-12-08 02:30 | 2021-12-08 10:32 | 30 | 008:02 | P | NO SE REPORTO CAUSA | 1 X 30 EN AEREO PROVISIONAL NO CAUSA | R21120800001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 482 | 2021-12-08 | 14460 | keep | 0 | Dec | 2021 | 0.0098486 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-12-08 02:48 | 2021-12-08 12:00 | 12 | 009:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21120700098 | New_Event | Secondary Wire Down | Include | Include | Equipment | 552 | 2021-12-08 | 6624 | keep | 0 | Dec | 2021 | 0.0045116 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-12-08 04:35 | 2021-12-08 09:10 | 10 | 004:35 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | R21120800003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 275 | 2021-12-08 | 2750 | keep | 0 | Dec | 2021 | 0.001873 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-08 05:27 | 2021-12-08 10:01 | 40 | 004:34 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A21120800003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 274 | 2021-12-08 | 10960 | keep | 0 | Dec | 2021 | 0.0074648 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2021-12-08 05:43 | 2021-12-08 14:55 | 10 | 009:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA ROTA | M21120800002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 552 | 2021-12-08 | 5520 | keep | 0 | Dec | 2021 | 0.0037596 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-08 05:59 | 2021-12-08 10:46 | 131 | 004:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN C/L A PETICION DE GREG TURNER SE ABRIO EL BKR PARA REEMPLAZAR CAJA A ESPUELAS EN AREA DE DIFICIL ACCESO | C21120800007 | New_Event | Cutout Failure | Include | Include | Equipment | 287 | 2021-12-08 | 37597 | keep | 0 | Dec | 2021 | 0.025607 | 8.9224e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 131
GUAYAMA | 2021-12-08 06:00 | 2021-12-08 09:18 | 1 | 003:18 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE REPORTA CAUSA | P21120800002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 198 | 2021-12-08 | 198 | keep | 0 | Dec | 2021 | 0.00013486 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2021-12-08 06:24 | 2021-12-08 17:28 | 100 | 011:04 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN C/L | C21120800009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 664 | 2021-12-08 | 66400 | keep | 0 | Dec | 2021 | 0.045225 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2021-12-08 06:31 | 2021-12-08 11:57 | 40 | 005:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE DE LINEA PRIMARIA POR AVE | P21120800003 | New_Event |  |  | Include | Wildlife | 326 | 2021-12-08 | 13040 | keep | 0 | Dec | 2021 | 0.0088815 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-08 06:50 | 2021-12-08 06:51 | 1399 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-08 | 1399 | keep | 0 | Dec | 2021 | 0.00095285 | 0.00095285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1399
BAYAMON | 2021-12-08 06:50 | 2021-12-08 06:51 | 302 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-08 | 302 | keep | 0 | Dec | 2021 | 0.00020569 | 0.00020569 | Momentary | FALSE | FALSE | Not_TMED_Event | 302
BAYAMON | 2021-12-08 06:50 | 2021-12-08 06:51 | 1048 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-08 | 1048 | keep | 0 | Dec | 2021 | 0.00071379 | 0.00071379 | Momentary | FALSE | FALSE | Not_TMED_Event | 1048
BAYAMON | 2021-12-08 06:50 | 2021-12-08 06:51 | 573 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-08 | 573 | keep | 0 | Dec | 2021 | 0.00039027 | 0.00039027 | Momentary | FALSE | FALSE | Not_TMED_Event | 573
BAYAMON | 2021-12-08 06:50 | 2021-12-08 06:51 | 1313 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-08 | 1313 | keep | 0 | Dec | 2021 | 0.00089428 | 0.00089428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1313
BAYAMON | 2021-12-08 06:50 | 2021-12-08 08:54 | 1715 | 002:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 124 | 2021-12-08 | 212660 | keep | 0 | Dec | 2021 | 0.14484 | 0.0011681 | Sustained | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2021-12-08 06:50 | 2021-12-08 08:54 | 1498 | 002:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 124 | 2021-12-08 | 185752 | keep | 0 | Dec | 2021 | 0.12651 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2021-12-08 06:50 | 2021-12-08 08:54 | 1221 | 002:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 124 | 2021-12-08 | 151404 | keep | 0 | Dec | 2021 | 0.10312 | 0.00083162 | Sustained | FALSE | FALSE | Not_TMED_Event | 1221
BAYAMON | 2021-12-08 06:50 | 2021-12-08 08:54 | 1100 | 002:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 124 | 2021-12-08 | 136400 | keep | 0 | Dec | 2021 | 0.092901 | 0.0007492 | Sustained | FALSE | FALSE | Not_TMED_Event | 1100
BAYAMON | 2021-12-08 06:55 | 2021-12-08 06:56 | 1399 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120800000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-08 | 1399 | keep | 0 | Dec | 2021 | 0.00095285 | 0.00095285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1399
BAYAMON | 2021-12-08 06:55 | 2021-12-08 06:56 | 302 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120800000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-08 | 302 | keep | 0 | Dec | 2021 | 0.00020569 | 0.00020569 | Momentary | FALSE | FALSE | Not_TMED_Event | 302
BAYAMON | 2021-12-08 06:55 | 2021-12-08 06:56 | 1048 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120800000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-08 | 1048 | keep | 0 | Dec | 2021 | 0.00071379 | 0.00071379 | Momentary | FALSE | FALSE | Not_TMED_Event | 1048
BAYAMON | 2021-12-08 06:55 | 2021-12-08 06:56 | 573 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120800000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-08 | 573 | keep | 0 | Dec | 2021 | 0.00039027 | 0.00039027 | Momentary | FALSE | FALSE | Not_TMED_Event | 573
BAYAMON | 2021-12-08 06:55 | 2021-12-08 06:56 | 1313 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21120800000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-08 | 1313 | keep | 0 | Dec | 2021 | 0.00089428 | 0.00089428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1313
CAGUAS | 2021-12-08 07:00 | 2021-12-08 12:40 | 40 | 005:40 | P | NO SE REPORTO CAUSA | 2 X 100 EN RISER NO CAUSA | C21120800011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 340 | 2021-12-08 | 13600 | keep | 0 | Dec | 2021 | 0.0092629 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-12-08 07:04 | 2021-12-08 10:14 | 1 | 003:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L Y 1 X 50 EN RISER CRUCE X AVE | C21120800012 | New_Event |  |  | Include | Wildlife | 190 | 2021-12-08 | 190 | keep | 0 | Dec | 2021 | 0.00012941 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-12-08 07:19 | 2021-12-08 09:52 | 10 | 002:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | R21120800006 | New_Event | Secondary Wire Down | Include | Include | Equipment | 153 | 2021-12-08 | 1530 | keep | 0 | Dec | 2021 | 0.0010421 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-12-08 07:25 | 2021-12-08 07:26 | 424 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR Y SE CERRO POR SCADA | R21120800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-08 | 424 | keep | 0 | Dec | 2021 | 0.00028878 | 0.00028878 | Momentary | FALSE | FALSE | Not_TMED_Event | 424
ARECIBO | 2021-12-08 07:37 | 2021-12-08 07:38 | 2107 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | A21120800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-08 | 2107 | keep | 0 | Dec | 2021 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
ARECIBO | 2021-12-08 07:38 | 2021-12-08 11:10 | 5 | 003:32 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | A21120800007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2021-12-08 | 1060 | keep | 0 | Dec | 2021 | 0.00072196 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-12-08 07:38 | 2021-12-08 09:41 | 30 | 002:03 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE NECESITA DESGANCHE | A21120800009 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 123 | 2021-12-08 | 3690 | keep | 0 | Dec | 2021 | 0.0025132 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-12-08 07:45 | 2021-12-08 18:31 | 40 | 010:46 | P | DESGANCHE | 1 X 40 EN C/L | C21120800016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 646 | 2021-12-08 | 25840 | keep | 0 | Dec | 2021 | 0.0176 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-12-08 07:46 | 2021-12-08 15:00 | 150 | 007:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR FUERTES VIENTOS | M21120800005 | New_Event | Bad Weather | Include | Include | Weather | 434 | 2021-12-08 | 65100 | keep | 0 | Dec | 2021 | 0.044339 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2021-12-08 07:50 | 2021-12-08 18:15 | 3 | 010:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO 37.5 KVA A 8.32/4.8 KV POR LA MISMA CAPACIDAD | P21120800007 | New_Event | Service Transformer Failure | Include | Include | Equipment | 625 | 2021-12-08 | 1875 | keep | 0 | Dec | 2021 | 0.0012771 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-12-08 07:55 | 2021-12-08 11:07 | 6 | 003:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA Y VIENTO | M21120800006 | New_Event | Bad Weather | Include | Include | Weather | 192 | 2021-12-08 | 1152 | keep | 0 | Dec | 2021 | 0.00078462 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-12-08 07:56 | 2021-12-08 22:18 | 2 | 014:22 | P | CABLE SOTERRADO AVERIADO | 1 X 100 EN RISER AVERIA DEL SU-2B AL SU-2C SE DEJO GOI SJ-211208-50 ABIERTO PARA REPARAR AVERIA | R21120800009 | New_Event | UG Cable Fault | Include | Include | Equipment | 862 | 2021-12-08 | 1724 | keep | 0 | Dec | 2021 | 0.0011742 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2021-12-08 08:22 | 2021-12-08 17:57 | 20 | 009:35 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21120800040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 575 | 2021-12-08 | 11500 | keep | 0 | Dec | 2021 | 0.0078326 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-12-08 08:34 | 2021-12-08 10:49 | 10 | 002:15 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA REALIZAR DESGANCHE SECUNDARIO Y SE RETEZO LINEA | B21120800043 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 135 | 2021-12-08 | 1350 | keep | 0 | Dec | 2021 | 0.00091948 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-12-08 08:39 | 2021-12-08 17:00 | 25 | 008:21 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 75 KVA QUEMADO POR 75 KVA | M21120800010 | New_Event | Service Transformer Failure | Include | Include | Equipment | 501 | 2021-12-08 | 12525 | keep | 0 | Dec | 2021 | 0.0085307 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2021-12-08 08:58 | 2021-12-08 08:59 | 2697 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | A21120800000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-12-08 | 2697 | keep | 0 | Dec | 2021 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
ARECIBO | 2021-12-08 08:59 | 2021-12-08 12:07 | 80 | 003:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA POR FUERTES LLUVIAS | A21120800015 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 188 | 2021-12-08 | 15040 | keep | 0 | Dec | 2021 | 0.010244 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-12-08 09:06 | 2021-12-08 09:07 | 5062 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | R21120800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-08 | 5062 | keep | 0 | Dec | 2021 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
CANOVANAS | 2021-12-08 09:07 | 2021-12-08 11:01 | 10 | 001:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | R21120800010 | New_Event | Secondary Wire Down | Include | Include | Equipment | 114 | 2021-12-08 | 1140 | keep | 0 | Dec | 2021 | 0.00077645 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-08 09:08 | 2021-12-08 14:22 | 12 | 005:14 | P | SOBRECARGA | SE ABRIO XMR PARA INSTALAR XMR NUEVO DE 37.5 KVA Y SE DIVIDIO LA CARGA | C21120800036 | New_Event | Trip Due To Overload | Include | Include | Other | 314 | 2021-12-08 | 3768 | keep | 0 | Dec | 2021 | 0.0025664 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-12-08 09:10 | 2021-12-08 11:34 | 14 | 002:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REMPLAZAR 150 PIES DE LINEA SECUNDARIA | P21120800012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 144 | 2021-12-08 | 2016 | keep | 0 | Dec | 2021 | 0.0013731 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2021-12-08 09:18 | 2021-12-08 13:27 | 2 | 004:09 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21120800012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 249 | 2021-12-08 | 498 | keep | 0 | Dec | 2021 | 0.00033919 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2021-12-08 09:23 | 2021-12-08 11:28 | 1 | 002:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONECTORES EN ALAMBRE PRIMARIO | S21120800014 | New_Event | Wire Down | Include | Include | Equipment | 125 | 2021-12-08 | 125 | keep | 0 | Dec | 2021 | 8.5137e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-12-08 09:26 | 2021-12-08 11:04 | 30 | 001:38 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | A21120800016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 98 | 2021-12-08 | 2940 | keep | 0 | Dec | 2021 | 0.0020024 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-12-08 09:44 | 2021-12-08 09:45 | 3420 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21120800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-08 | 3420 | keep | 0 | Dec | 2021 | 0.0023293 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
ARECIBO | 2021-12-08 09:44 | 2021-12-08 17:36 | 7 | 007:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTES SECUNDARIOS | A21120800018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 472 | 2021-12-08 | 3304 | keep | 0 | Dec | 2021 | 0.0022503 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-12-08 09:51 | 2021-12-08 09:52 | 290 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21120800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-12-08 | 290 | keep | 0 | Dec | 2021 | 0.00019752 | 0.00019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 290
BAYAMON | 2021-12-08 09:52 | 2021-12-08 12:43 | 1 | 002:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO DE LINEA TRONCAL EN RISER | S21120800024 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 171 | 2021-12-08 | 171 | keep | 0 | Dec | 2021 | 0.00011647 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-12-08 10:05 | 2021-12-08 10:06 | 4035 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21120800016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-08 | 4035 | keep | 0 | Dec | 2021 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
MAYAGÃœEZ | 2021-12-08 10:10 | 2021-12-08 14:30 | 50 | 004:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR FUERTES VIENTOS | M21120800017 | New_Event | Bad Weather | Include | Include | Weather | 260 | 2021-12-08 | 13000 | keep | 0 | Dec | 2021 | 0.0088542 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-12-08 10:13 | 2021-12-08 15:00 | 9 | 004:47 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR AVERIADO DE 37.5 KVA X 37.5 KVA | C21120800046 | New_Event | Service Transformer Failure | Include | Include | Equipment | 287 | 2021-12-08 | 2583 | keep | 0 | Dec | 2021 | 0.0017593 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2021-12-08 10:15 | 2021-12-08 10:16 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | CARGA TRANSFERIDA AL 1206-03 | S21120800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-08 | 10211 | keep | 0 | Dec | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-12-08 10:15 | 2021-12-08 10:16 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA LA CARGA DEL 1204-05 | S21120800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-08 | 4133 | keep | 0 | Dec | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
AGUADILLA | 2021-12-08 10:17 | 2021-12-09 11:41 | 200 | 025:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA AVERIADA | M21120800095 | New_Event | Cutout Failure | Include | Include | Equipment | 1524 | 2021-12-08 | 304800 | keep | 0 | Dec | 2021 | 0.2076 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2021-12-08 10:19 | 2021-12-08 13:26 | 100 | 003:07 | P | DESGANCHE | 2 X 65 EN C/L | C21120800047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2021-12-08 | 18700 | keep | 0 | Dec | 2021 | 0.012736 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-12-08 10:25 | 2021-12-08 10:27 | 723 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1711-02 LLEVANDO CARGA 1711-05 | B21120800055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-08 | 1446 | keep | 0 | Dec | 2021 | 0.00098486 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2021-12-08 10:25 | 2021-12-08 10:27 | 1976 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1711-02 LLEVANDO CARGA 1711-05 | B21120800055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-08 | 3952 | keep | 0 | Dec | 2021 | 0.0026917 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
HUMACAO | 2021-12-08 10:28 | 2021-12-08 10:44 | 22 | 000:16 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIO XMR PARA REMPLAZAR POSTE SECUNDARIO | C21120800055 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 16 | 2021-12-08 | 352 | keep | 0 | Dec | 2021 | 0.00023975 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
ARECIBO | 2021-12-08 10:38 | 2021-12-08 11:52 | 7 | 001:14 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA RELOCALIZAR LINEA SECUNDARIA POR POSTE PARTIDO | A21120800021 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 74 | 2021-12-08 | 518 | keep | 0 | Dec | 2021 | 0.00035281 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2021-12-08 10:44 | 2021-12-08 10:45 | 989 | 000:01 | T | ERROR HUMANO | ABRI BKR EQUIVOCADAMENTE | C21120800051 | New_Event | Human Error | Include | Include | Other | 1 | 2021-12-08 | 989 | keep | 0 | Dec | 2021 | 0.0006736 | 0.0006736 | Momentary | FALSE | FALSE | Not_TMED_Event | 989
HUMACAO | 2021-12-08 10:45 | 2021-12-08 12:07 | 22 | 001:22 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIO XMR PARA REMPLAZAR POSTE SECUNDARIO | C21120800055 | Partial_restoration | Secondary Defective Pole | Include | Include | Equipment | 82 | 2021-12-08 | 1804 | keep | 0 | Dec | 2021 | 0.0012287 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-12-08 10:46 | 2021-12-08 12:37 | 3131 | 001:51 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN C/L A PETICION DE GREG TURNER SE ABRIO EL BKR PARA REMPLAZAR CAJA A ESPUELAS EN AREA DE DIFICIL ACCESO | C21120800053 | New_Event | Cutout Failure | Include | Include | Equipment | 111 | 2021-12-08 | 347541 | keep | 0 | Dec | 2021 | 0.23671 | 0.0021325 | Sustained | FALSE | FALSE | Not_TMED_Event | 3131
MAYAGÃœEZ | 2021-12-08 10:57 | 2021-12-08 16:16 | 30 | 005:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | M21120800027 | New_Event | Wire Down | Include | Include | Equipment | 319 | 2021-12-08 | 9570 | keep | 0 | Dec | 2021 | 0.0065181 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-08 11:00 | 2021-12-08 12:12 | 10 | 001:12 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | S21120800022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2021-12-08 | 720 | keep | 0 | Dec | 2021 | 0.00049039 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-08 11:04 | 2021-12-08 13:25 | 10 | 002:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BARRAS SECUNDARIAS EN PEDESTAL Y SECUNDARIA | B21120800059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 141 | 2021-12-08 | 1410 | keep | 0 | Dec | 2021 | 0.00096034 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-08 11:09 | 2021-12-08 15:15 | 60 | 004:06 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PODRIDO | R21120800013 | New_Event | Defective Pole | Include | Include | Equipment | 246 | 2021-12-08 | 14760 | keep | 0 | Dec | 2021 | 0.010053 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-12-08 11:15 | 2021-12-08 12:45 | 25 | 001:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 15 KVA POR 25 KVA | M21120800033 | New_Event | Service Transformer Failure | Include | Include | Equipment | 90 | 2021-12-08 | 2250 | keep | 0 | Dec | 2021 | 0.0015325 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2021-12-08 11:17 | 2021-12-08 17:16 | 734 | 005:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE NO FUNDIO | C21120800058 | New_Event | Wire Down | Include | Include | Equipment | 359 | 2021-12-08 | 263506 | keep | 0 | Dec | 2021 | 0.17947 | 0.00049992 | Sustained | FALSE | FALSE | Not_TMED_Event | 734
MAYAGÃœEZ | 2021-12-08 11:20 | 2021-12-08 18:20 | 60 | 007:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 20 EN CORTE DE LINEA SE REPARO LINEA SECUNDARIA PARTIDA POR VEHICULO | M21120800039 | New_Event |  |  | Include | Wildlife | 420 | 2021-12-08 | 25200 | keep | 0 | Dec | 2021 | 0.017164 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2021-12-08 11:22 | 2021-12-08 11:54 | 10 | 000:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTES SECUNDARIOS | B21120600031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 32 | 2021-12-08 | 320 | keep | 0 | Dec | 2021 | 0.00021795 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-08 11:28 | 2021-12-08 11:45 | 10 | 000:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21120800002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 17 | 2021-12-08 | 170 | keep | 0 | Dec | 2021 | 0.00011579 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-12-08 11:30 | 2021-12-08 20:44 | 40 | 009:14 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21120800066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 554 | 2021-12-08 | 22160 | keep | 0 | Dec | 2021 | 0.015093 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-08 11:33 | 2021-12-08 12:10 | 10 | 000:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR FASE SECUNDARIA EN PEDESTAL | B21120800061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 37 | 2021-12-08 | 370 | keep | 0 | Dec | 2021 | 0.00025201 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-08 11:34 | 2021-12-08 11:35 | 1 | 000:01 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER NO CAUSA | C21120800020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-08 | 1 | keep | 0 | Dec | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2021-12-08 11:42 | 2021-12-08 15:09 | 50 | 003:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L REEMPLAZO CAJA QUEMADA | C21120800062 | New_Event | Cutout Failure | Include | Include | Equipment | 207 | 2021-12-08 | 10350 | keep | 0 | Dec | 2021 | 0.0070493 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2021-12-08 11:53 | 2021-12-08 15:00 | 12 | 003:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA Y VIENTO | A21120800029 | New_Event | Bad Weather | Include | Include | Weather | 187 | 2021-12-08 | 2244 | keep | 0 | Dec | 2021 | 0.0015284 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-12-08 12:26 | 2021-12-08 19:02 | 5 | 006:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C21120800068 | New_Event | Secondary Wire Down | Include | Include | Equipment | 396 | 2021-12-08 | 1980 | keep | 0 | Dec | 2021 | 0.0013486 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2021-12-08 12:36 | 2021-12-08 21:00 | 10 | 008:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN TRANSFORMADOR SE REMPLAZO BAJANTE PRIMARIO PARTIDO Y CAJA PRIMARIA QUEMADA | M21120800047 | New_Event | Wire Down | Include | Include | Equipment | 504 | 2021-12-08 | 5040 | keep | 0 | Dec | 2021 | 0.0034327 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-08 12:43 | 2021-12-08 13:08 | 290 | 000:25 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE DE LINEA TRONCAL | S21120800031 | New_Event | Wire Down | Include | Include | Equipment | 25 | 2021-12-08 | 7250 | keep | 0 | Dec | 2021 | 0.0049379 | 0.00019752 | Sustained | FALSE | FALSE | Not_TMED_Event | 290
MAYAGÃœEZ | 2021-12-08 12:46 | 2021-12-08 16:55 | 8 | 004:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO A TRANSFORMADOR | M21120800048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 249 | 2021-12-08 | 1992 | keep | 0 | Dec | 2021 | 0.0013567 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-12-08 12:56 | 2021-12-08 17:44 | 42 | 004:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21120800049 | New_Event | Bad Weather | Include | Include | Weather | 288 | 2021-12-08 | 12096 | keep | 0 | Dec | 2021 | 0.0082385 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
BAYAMON | 2021-12-08 13:07 | 2021-12-08 14:50 | 10 | 001:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA LEVANTAR NEUTRAL PRIMARIO PARTIDO | B21120800077 | New_Event | Secondary Wire Down | Include | Include | Equipment | 103 | 2021-12-08 | 1030 | keep | 0 | Dec | 2021 | 0.00070153 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-08 13:21 | 2021-12-08 17:41 | 10 | 004:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO Y 3 TOMAS | B21120800080 | New_Event | Secondary Wire Down | Include | Include | Equipment | 260 | 2021-12-08 | 2600 | keep | 0 | Dec | 2021 | 0.0017708 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-08 13:21 | 2021-12-08 17:05 | 6 | 003:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C21120800071 | New_Event | Secondary Wire Down | Include | Include | Equipment | 224 | 2021-12-08 | 1344 | keep | 0 | Dec | 2021 | 0.00091539 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-12-08 13:36 | 2021-12-08 13:37 | 199 | 000:01 | T | BREAKER DEFECTUOSO O NO OPERA | INTERRUPTOR QUEMADO SU CARGA SE PASO AL 8013-04 | A21120800033 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 1 | 2021-12-08 | 199 | keep | 0 | Dec | 2021 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2021-12-08 13:37 | 2021-12-08 13:38 | 2694 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 6900 | A21120800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-08 | 2694 | keep | 0 | Dec | 2021 | 0.0018349 | 0.0018349 | Momentary | FALSE | FALSE | Not_TMED_Event | 2694
ARECIBO | 2021-12-08 13:37 | 2021-12-08 13:38 | 2228 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 6900 | A21120800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-08 | 2228 | keep | 0 | Dec | 2021 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2021-12-08 13:37 | 2021-12-08 13:38 | 438 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 6900 | A21120800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-08 | 438 | keep | 0 | Dec | 2021 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
ARECIBO | 2021-12-08 13:37 | 2021-12-08 18:34 | 2201 | 004:57 | S | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA DE SUBESTACION POR PUENTES ABIERTOS EN LINEA 6900 | A21120800071 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 297 | 2021-12-08 | 653697 | keep | 0 | Dec | 2021 | 0.44523 | 0.0014991 | Sustained | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2021-12-08 13:37 | 2021-12-08 18:34 | 1986 | 004:57 | S | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA DE SUBESTACION POR PUENTES ABIERTOS EN LINEA 6900 | A21120800071 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 297 | 2021-12-08 | 589842 | keep | 0 | Dec | 2021 | 0.40174 | 0.0013527 | Sustained | FALSE | FALSE | Not_TMED_Event | 1986
ARECIBO | 2021-12-08 13:37 | 2021-12-08 18:34 | 199 | 004:57 | S | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA DE SUBESTACION POR PUENTES ABIERTOS EN LINEA 6900 | A21120800071 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 297 | 2021-12-08 | 59103 | keep | 0 | Dec | 2021 | 0.040255 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2021-12-08 13:37 | 2021-12-08 18:34 | 24 | 004:57 | S | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA DE SUBESTACION POR PUENTES ABIERTOS EN LINEA 6900 | A21120800071 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 297 | 2021-12-08 | 7128 | keep | 0 | Dec | 2021 | 0.0048548 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
ARECIBO | 2021-12-08 13:41 | 2021-12-08 15:12 | 5 | 001:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTES SECUNDARIOS | A21120800034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 91 | 2021-12-08 | 455 | keep | 0 | Dec | 2021 | 0.0003099 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-12-08 13:42 | 2021-12-08 16:29 | 40 | 002:47 | P | DESGANCHE | 1 X 40 EN C/L | C21120800074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2021-12-08 | 6680 | keep | 0 | Dec | 2021 | 0.0045497 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-12-08 14:00 | 2021-12-08 16:00 | 1 | 002:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR LLUVIA Y VIENTO | M21120800054 | New_Event | Bad Weather | Include | Include | Weather | 120 | 2021-12-08 | 120 | keep | 0 | Dec | 2021 | 8.1731e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-08 14:03 | 2021-12-08 20:08 | 50 | 006:05 | P | ESTRUCTURA AVERIADA | POSTE EN EL PISO SE SECCIONALIZO SE ABRIO PUENTE 1 X 65 EN CORTE DE LINEA | S21120800038 | New_Event | Defective Pole | Include | Include | Equipment | 365 | 2021-12-08 | 18250 | keep | 0 | Dec | 2021 | 0.01243 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-12-08 14:11 | 2021-12-08 16:05 | 1284 | 001:54 | T | DESGANCHE | SE CERRO INTERRUPTOR ABRIENDO MACHETES SALIDA DE SOTERRADO EN CARRETERA 695 PARA REALIZAR DESGANCHE | B21120800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2021-12-08 | 146376 | keep | 0 | Dec | 2021 | 0.099696 | 0.00087453 | Sustained | FALSE | FALSE | Not_TMED_Event | 1284
SAN JUAN | 2021-12-08 14:18 | 2021-12-08 14:20 | 1681 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO CON R/R OFF SU CARGA POR 1303-4 | S21120800040 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2021-12-08 | 3362 | keep | 0 | Dec | 2021 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-12-08 14:18 | 2021-12-08 14:20 | 1598 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO CON R/R OFF SU CARGA POR 1303-4 | S21120800040 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2021-12-08 | 3196 | keep | 0 | Dec | 2021 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2021-12-08 14:20 | 2021-12-08 17:40 | 156 | 003:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE MACHETE PARA LEVANTAR LINEA PRIMARIA | S21120800041 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 200 | 2021-12-08 | 31200 | keep | 0 | Dec | 2021 | 0.02125 | 0.00010625 | Sustained | FALSE | FALSE | Not_TMED_Event | 156
AGUADILLA | 2021-12-08 14:20 | 2021-12-08 17:18 | 150 | 002:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | M21120800059 | New_Event | Wire Down | Include | Include | Equipment | 178 | 2021-12-08 | 26700 | keep | 0 | Dec | 2021 | 0.018185 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
UTUADO | 2021-12-08 14:34 | 2021-12-08 15:45 | 5 | 001:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR TENSOR EN POSTE | A21120800059 | New_Event |  |  | Include | Wildlife | 71 | 2021-12-08 | 355 | keep | 0 | Dec | 2021 | 0.00024179 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-12-08 14:55 | 2021-12-08 19:17 | 500 | 004:22 | P | DESGANCHE | 3 X 80 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | A21120800065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 262 | 2021-12-08 | 131000 | keep | 0 | Dec | 2021 | 0.089224 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2021-12-08 15:27 | 2021-12-08 16:50 | 12 | 001:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE T-36 PARA REMPLAZAR BARRA PEDESTAL | S21120800049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 83 | 2021-12-08 | 996 | keep | 0 | Dec | 2021 | 0.00067837 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-12-08 15:29 | 2021-12-08 19:06 | 1 | 003:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO BAJANTE DE LINEA A CAJA | C21120800087 | New_Event | Wire Down | Include | Include | Equipment | 217 | 2021-12-08 | 217 | keep | 0 | Dec | 2021 | 0.0001478 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-12-08 15:29 | 2021-12-08 16:29 | 10 | 001:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE X AVE | C21120800080 | New_Event |  |  | Include | Wildlife | 60 | 2021-12-08 | 600 | keep | 0 | Dec | 2021 | 0.00040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-08 15:42 | 2021-12-08 20:07 | 85 | 004:25 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21120800050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 265 | 2021-12-08 | 22525 | keep | 0 | Dec | 2021 | 0.015342 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
UTUADO | 2021-12-08 15:51 | 2021-12-08 19:55 | 15 | 004:04 | P | PARARRAYOS DEFECTUOSO | 1 X 15 EN TRANSFORMADOR POR PARARRAYO CRUZADO | A21120800081 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 244 | 2021-12-08 | 3660 | keep | 0 | Dec | 2021 | 0.0024928 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-12-08 16:05 | 2021-12-08 16:42 | 284 | 000:37 | P | DESGANCHE | SE CERRO INTERRUPTOR ABRIENDO MACHETES SALIDA DE SOTERRADO EN CARRETERA 695 PARA REALIZAR DESGANCHE | B21120800000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 37 | 2021-12-08 | 10508 | keep | 0 | Dec | 2021 | 0.007157 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-12-08 16:20 | 2021-12-08 17:15 | 5 | 000:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C21120800000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 55 | 2021-12-08 | 275 | keep | 0 | Dec | 2021 | 0.0001873 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-12-08 16:26 | 2021-12-08 18:36 | 1 | 002:10 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE REPORTO CAUSA | P21120800036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2021-12-08 | 130 | keep | 0 | Dec | 2021 | 8.8542e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-12-08 16:42 | 2021-12-08 16:45 | 1284 | 000:03 | T | DESGANCHE | SE ABRIO INTERRUPTOR PARA CERRAR MACHETES EN SALIDA DE SOTERRADO CARRETERA 695 SE REALIZO DESGANCHE EN CARRETERA 695 | B21120800000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-12-08 | 3852 | keep | 0 | Dec | 2021 | 0.0026236 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-12-08 16:55 | 2021-12-08 17:34 | 13 | 000:39 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERAS EN LINEA SECUNDARIA | M21120800076 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 39 | 2021-12-08 | 507 | keep | 0 | Dec | 2021 | 0.00034532 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2021-12-08 17:08 | 2021-12-08 19:08 | 12 | 002:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE T-7 PARA REMPLAZO BARRA PEDESTAL | S21120800060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 120 | 2021-12-08 | 1440 | keep | 0 | Dec | 2021 | 0.00098078 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-12-08 17:55 | 2021-12-08 17:56 | 766 | 000:01 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1709-03 50% DE SU CARGA POR 1909-07 Y LLEVANDO CARGA 1709-05 | S21120800000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2021-12-08 | 766 | keep | 0 | Dec | 2021 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2021-12-08 17:55 | 2021-12-08 17:56 | 2364 | 000:01 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1709-03 50% DE SU CARGA POR 1909-07 Y LLEVANDO CARGA 1709-05 | S21120800000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2021-12-08 | 2364 | keep | 0 | Dec | 2021 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
BAYAMON | 2021-12-08 17:56 | 2021-12-08 22:22 | 20 | 004:26 | P | CABLE SOTERRADO AVERIADO | AVERIA SOTERRADA DE RISER @ T-2 SE CERRO N/O DE RISER @ T-1 | S21120800065 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 266 | 2021-12-08 | 5320 | keep | 0 | Dec | 2021 | 0.0036234 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-12-08 18:05 | 2021-12-08 22:32 | 3 | 004:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA Y VIENTO | A21120800102 | New_Event | Bad Weather | Include | Include | Weather | 267 | 2021-12-08 | 801 | keep | 0 | Dec | 2021 | 0.00054556 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-12-08 18:18 | 2021-12-08 19:21 | 10 | 001:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZARON CONECTORES Y SE REPARO NEUTRAL | B21120800081 | New_Event | Secondary Wire Down | Include | Include | Equipment | 63 | 2021-12-08 | 630 | keep | 0 | Dec | 2021 | 0.00042909 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-08 18:20 | 2021-12-08 21:50 | 10 | 003:30 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACIONES SOTERRADAS EN T348 | B21120800099 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 210 | 2021-12-08 | 2100 | keep | 0 | Dec | 2021 | 0.0014303 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-12-08 18:27 | 2021-12-09 10:11 | 72 | 015:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA FUERTE BRISA | P21120800041 | New_Event | Bad Weather | Include | Include | Weather | 944 | 2021-12-08 | 67968 | keep | 0 | Dec | 2021 | 0.046293 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
ARECIBO | 2021-12-08 18:34 | 2021-12-08 18:47 | 199 | 000:13 | T | BREAKER DEFECTUOSO O NO OPERA | INTERRUPTOR QUEMADO SU CARGA SE PASO AL 8013-04 | A21120800033 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 13 | 2021-12-08 | 2587 | keep | 0 | Dec | 2021 | 0.001762 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
BAYAMON | 2021-12-08 18:37 | 2021-12-09 10:32 | 1 | 015:55 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21120800160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 955 | 2021-12-08 | 955 | keep | 0 | Dec | 2021 | 0.00065045 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-12-08 18:40 | 2021-12-08 19:39 | 1923 | 000:59 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO INTERRUPTOR PARA RETIRAR PELIGRO DE LINEA PARTIDA POR CONTACTO ELECTRICO NO HAY PARCIAL DEL EVENTO | A21120800109 | New_Event |  |  | Include | Wildlife | 59 | 2021-12-08 | 113457 | keep | 0 | Dec | 2021 | 0.077275 | 0.0013097 | Sustained | FALSE | FALSE | Not_TMED_Event | 1923
MAYAGÃœEZ | 2021-12-08 18:50 | 2021-12-09 22:13 | 6 | 027:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 10 EN TRANSFORMADOR SE REPARO BAJANTE PRIMARIO DE CAJA A TRANSFORMADOR | M21120800082 | New_Event | Wire Down | Include | Include | Equipment | 1643 | 2021-12-08 | 9858 | keep | 0 | Dec | 2021 | 0.0067142 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2021-12-08 18:53 | 2021-12-08 22:31 | 15 | 003:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA Y VIENTO | M21120800083 | New_Event | Bad Weather | Include | Include | Weather | 218 | 2021-12-08 | 3270 | keep | 0 | Dec | 2021 | 0.0022272 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-12-08 19:15 | 2021-12-09 15:42 | 15 | 020:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO EN VIVO | M21120800086 | New_Event | Wire Down | Include | Include | Equipment | 1227 | 2021-12-08 | 18405 | keep | 0 | Dec | 2021 | 0.012536 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-12-08 19:39 | 2021-12-08 23:48 | 200 | 004:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA POR CONTACTO DE PERSONA | A21120800107 | Partial_restoration |  |  | Include | Wildlife | 249 | 2021-12-08 | 49800 | keep | 0 | Dec | 2021 | 0.033919 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-08 20:00 | 2021-12-08 22:47 | 60 | 002:47 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21120800067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 167 | 2021-12-08 | 10020 | keep | 0 | Dec | 2021 | 0.0068246 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-12-08 20:08 | 2021-12-09 16:00 | 12 | 019:52 | P | ESTRUCTURA AVERIADA | SE ABRE CORTE DE LINEA PARA LEVANTAR LINEA Y SE INSTALO POSTE Y SE CERRO PUENTE PRIMARIO | S21120800038 | Partial_restoration | Defective Pole | Include | Include | Equipment | 1192 | 2021-12-08 | 14304 | keep | 0 | Dec | 2021 | 0.0097424 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-12-08 20:56 | 2021-12-09 14:08 | 8 | 017:12 | P | NO SE REPORTO CAUSA | 1 X 8 EN XMR NO CAUSA | C21120900101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1032 | 2021-12-08 | 8256 | keep | 0 | Dec | 2021 | 0.0056231 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-12-08 21:41 | 2021-12-09 15:16 | 40 | 017:35 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO DISCOS ROTOS | A21120800124 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1055 | 2021-12-08 | 42200 | keep | 0 | Dec | 2021 | 0.028742 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-12-08 22:11 | 2021-12-08 22:12 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21120800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-08 | 308 | keep | 0 | Dec | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
SAN JUAN | 2021-12-08 22:18 | 2021-12-09 19:30 | 300 | 021:12 | P | CABLE SOTERRADO AVERIADO | SE REPARO AVERIA DEL SU2C AL SU2B | R21120800009 | New_Event | UG Cable Fault | Include | Include | Equipment | 1272 | 2021-12-08 | 381600 | keep | 0 | Dec | 2021 | 0.25991 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2021-12-08 22:18 | 2021-12-08 22:20 | 1001 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C21120800103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-08 | 2002 | keep | 0 | Dec | 2021 | 0.0013636 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
HUMACAO | 2021-12-08 23:26 | 2021-12-09 12:08 | 5 | 012:42 | P | SECUNDARIA/DESGANCHE | 2 X 10 EN XMR DESGANCHO | C21120800104 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 762 | 2021-12-08 | 3810 | keep | 0 | Dec | 2021 | 0.002595 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-12-09 00:38 | 2021-12-09 12:35 | 55 | 011:57 | P | DESGANCHE | 1 X 65 EN C/L | C21120900001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 717 | 2021-12-09 | 39435 | keep | 0 | Dec | 2021 | 0.026859 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CANOVANAS | 2021-12-09 01:41 | 2021-12-09 05:30 | 424 | 003:49 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO INTERRUPTOR 3 VECES QUEDO FUERA SE REEMPLAZO AISLADOR ROTO Y SE REPARO PUENTE PRIMARIO CERRADO POR CONTROL | R21120900001 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 229 | 2021-12-09 | 97096 | keep | 0 | Dec | 2021 | 0.066132 | 0.00028878 | Sustained | FALSE | FALSE | Not_TMED_Event | 424
MAYAGÃœEZ | 2021-12-09 02:58 | 2021-12-09 02:59 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21120900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-09 | 1097 | keep | 0 | Dec | 2021 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
MAYAGÃœEZ | 2021-12-09 04:24 | 2021-12-09 04:25 | 1287 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21120900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-09 | 1287 | keep | 0 | Dec | 2021 | 0.00087657 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
SAN JUAN | 2021-12-09 04:35 | 2021-12-09 04:38 | 68 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO Y SE CERRO POR CONTROL LLEVA LA CARGA DEL 1102-04 & 05 LLEVA LA CARGA DEL 1105-04 & 05 | S21120900000 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2021-12-09 | 204 | keep | 0 | Dec | 2021 | 0.00013894 | 4.6314e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 68
SAN JUAN | 2021-12-09 04:35 | 2021-12-09 04:38 | 536 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | CARGA TRANSFERIDA AL 1102-01 ESTE INTERRUPTOR DISPARO Y SE CERRO POR CONTROL | S21120900000 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2021-12-09 | 1608 | keep | 0 | Dec | 2021 | 0.0010952 | 0.00036507 | Momentary | FALSE | FALSE | Not_TMED_Event | 536
BAYAMON | 2021-12-09 04:35 | 2021-12-09 04:38 | 348 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | CARGA TRANSFERIDA AL 1102-01 ESTE INTERRUPTOR DISPARO Y SE CERRO POR CONTROL | S21120900000 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2021-12-09 | 1044 | keep | 0 | Dec | 2021 | 0.00071106 | 0.00023702 | Momentary | FALSE | FALSE | Not_TMED_Event | 348
BAYAMON | 2021-12-09 04:35 | 2021-12-09 04:38 | 559 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | CARGA TRANSFERIDA AL 1102-01 ESTE INTERRUPTOR DISPARO Y SE CERRO POR CONTROL | S21120900000 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2021-12-09 | 1677 | keep | 0 | Dec | 2021 | 0.0011422 | 0.00038073 | Momentary | FALSE | FALSE | Not_TMED_Event | 559
BAYAMON | 2021-12-09 04:35 | 2021-12-09 04:38 | 370 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | CARGA TRANSFERIDA AL 1102-01 ESTE INTERRUPTOR DISPARO Y SE CERRO POR CONTROL | S21120900000 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2021-12-09 | 1110 | keep | 0 | Dec | 2021 | 0.00075602 | 0.00025201 | Momentary | FALSE | FALSE | Not_TMED_Event | 370
BAYAMON | 2021-12-09 04:35 | 2021-12-09 04:37 | 4398 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S21120900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-09 | 8796 | keep | 0 | Dec | 2021 | 0.0059909 | 0.0029955 | Momentary | FALSE | FALSE | Not_TMED_Event | 4398
BAYAMON | 2021-12-09 04:38 | 2021-12-09 10:00 | 150 | 005:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE MACHETE PARA SECCIONALIZAR LINEA PRIMARIA EN EL PISO SU CARGA POR 1102-01 | S21120900016 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 322 | 2021-12-09 | 48300 | keep | 0 | Dec | 2021 | 0.032897 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2021-12-09 05:15 | 2021-12-09 05:17 | 1066 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S21120900014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-09 | 2132 | keep | 0 | Dec | 2021 | 0.0014521 | 0.00072605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1066
CAGUAS | 2021-12-09 07:33 | 2021-12-09 13:34 | 14 | 006:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C21120900019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 361 | 2021-12-09 | 5054 | keep | 0 | Dec | 2021 | 0.0034423 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2021-12-09 07:34 | 2021-12-09 07:38 | 4028 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B21120900004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-12-09 | 16112 | keep | 0 | Dec | 2021 | 0.010974 | 0.0027435 | Momentary | FALSE | FALSE | Not_TMED_Event | 4028
CAGUAS | 2021-12-09 07:42 | 2021-12-09 11:41 | 100 | 003:59 | P | DESGANCHE | 1 X 50 Y 1 X 40 Y 1 X 30 EN C/L'S | C21120900006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2021-12-09 | 23900 | keep | 0 | Dec | 2021 | 0.016278 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2021-12-09 07:43 | 2021-12-09 10:08 | 18 | 002:25 | P | DESGANCHE | 1 X 20 EN C/L | R21120900005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 145 | 2021-12-09 | 2610 | keep | 0 | Dec | 2021 | 0.0017777 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
ARECIBO | 2021-12-09 07:51 | 2021-12-09 07:53 | 1222 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 NO REPORTARON AVERIA | A21120900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-12-09 | 2444 | keep | 0 | Dec | 2021 | 0.0016646 | 0.0008323 | Momentary | FALSE | FALSE | Not_TMED_Event | 1222
ARECIBO | 2021-12-09 07:51 | 2021-12-09 07:53 | 2756 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 NO REPORTARON AVERIA | A21120900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-12-09 | 5512 | keep | 0 | Dec | 2021 | 0.0037542 | 0.0018771 | Momentary | FALSE | FALSE | Not_TMED_Event | 2756
ARECIBO | 2021-12-09 07:51 | 2021-12-09 07:53 | 2833 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 NO REPORTARON AVERIA | A21120900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-12-09 | 5666 | keep | 0 | Dec | 2021 | 0.0038591 | 0.0019295 | Momentary | FALSE | FALSE | Not_TMED_Event | 2833
ARECIBO | 2021-12-09 07:51 | 2021-12-09 07:53 | 1218 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A21120900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-12-09 | 2436 | keep | 0 | Dec | 2021 | 0.0016591 | 0.00082957 | Momentary | FALSE | FALSE | Not_TMED_Event | 1218
ARECIBO | 2021-12-09 07:51 | 2021-12-09 07:53 | 1345 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A21120900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-12-09 | 2690 | keep | 0 | Dec | 2021 | 0.0018321 | 0.00091607 | Momentary | FALSE | FALSE | Not_TMED_Event | 1345
ARECIBO | 2021-12-09 07:51 | 2021-12-09 07:53 | 1265 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A21120900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-12-09 | 2530 | keep | 0 | Dec | 2021 | 0.0017232 | 0.00086159 | Momentary | FALSE | FALSE | Not_TMED_Event | 1265
ARECIBO | 2021-12-09 07:51 | 2021-12-09 07:53 | 2071 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A21120900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-12-09 | 4142 | keep | 0 | Dec | 2021 | 0.0028211 | 0.0014105 | Momentary | FALSE | FALSE | Not_TMED_Event | 2071
ARECIBO | 2021-12-09 07:51 | 2021-12-09 07:53 | 760 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A21120900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-12-09 | 1520 | keep | 0 | Dec | 2021 | 0.0010353 | 0.00051763 | Momentary | FALSE | FALSE | Not_TMED_Event | 760
ARECIBO | 2021-12-09 07:51 | 2021-12-09 07:53 | 509 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A21120900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-12-09 | 1018 | keep | 0 | Dec | 2021 | 0.00069336 | 0.00034668 | Momentary | FALSE | FALSE | Not_TMED_Event | 509
ARECIBO | 2021-12-09 07:51 | 2021-12-09 07:53 | 2620 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A21120900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-12-09 | 5240 | keep | 0 | Dec | 2021 | 0.0035689 | 0.0017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 2620
ARECIBO | 2021-12-09 07:51 | 2021-12-09 07:53 | 1916 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 | A21120900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-12-09 | 3832 | keep | 0 | Dec | 2021 | 0.00261 | 0.001305 | Momentary | FALSE | FALSE | Not_TMED_Event | 1916
ARECIBO | 2021-12-09 07:53 | 2021-12-09 10:55 | 1222 | 003:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 SE REMPLAZO FUSIBLE 38 KV | A21120900022 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 182 | 2021-12-09 | 222404 | keep | 0 | Dec | 2021 | 0.15148 | 0.0008323 | Sustained | FALSE | FALSE | Not_TMED_Event | 1222
ARECIBO | 2021-12-09 07:53 | 2021-12-09 10:55 | 2756 | 003:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 SE REMPLAZO FUSIBLE FUNDIDO 38 KV | A21120900022 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 182 | 2021-12-09 | 501592 | keep | 0 | Dec | 2021 | 0.34163 | 0.0018771 | Sustained | FALSE | FALSE | Not_TMED_Event | 2756
ARECIBO | 2021-12-09 07:53 | 2021-12-09 10:55 | 2833 | 003:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2100 SE REMPLAZO FUSIBLE FUNDIDO 38 KV | A21120900022 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 182 | 2021-12-09 | 515606 | keep | 0 | Dec | 2021 | 0.35118 | 0.0019295 | Sustained | FALSE | FALSE | Not_TMED_Event | 2833
SAN JUAN | 2021-12-09 07:55 | 2021-12-09 10:22 | 50 | 002:27 | P | CABLE SOTERRADO AVERIADO | 1 SMU 20 DE 100 AMP EN EL SU 5B AVERIA DEL SU 3G AL SU 2A | R21120900006 | New_Event | UG Cable Fault | Include | Include | Equipment | 147 | 2021-12-09 | 7350 | keep | 0 | Dec | 2021 | 0.0050061 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-12-09 08:02 | 2021-12-09 09:27 | 9 | 001:25 | P | PARARRAYOS DEFECTUOSO | 1 X 25 EN CORTE DE LINEA SE REMPLAZO PARARRAYO | A21120900004 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 85 | 2021-12-09 | 765 | keep | 0 | Dec | 2021 | 0.00052104 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2021-12-09 08:14 | 2021-12-09 12:38 | 20 | 004:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE FIJO LINEA ZAFADA | A21120900008 | New_Event | Wire Down | Include | Include | Equipment | 264 | 2021-12-09 | 5280 | keep | 0 | Dec | 2021 | 0.0035962 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-12-09 08:21 | 2021-12-09 11:48 | 200 | 003:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21120900024 | New_Event | Bad Weather | Include | Include | Weather | 207 | 2021-12-09 | 41400 | keep | 0 | Dec | 2021 | 0.028197 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
GUAYAMA | 2021-12-09 08:23 | 2021-12-09 10:06 | 4 | 001:43 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P21120900003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 103 | 2021-12-09 | 412 | keep | 0 | Dec | 2021 | 0.00028061 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-12-09 08:23 | 2021-12-09 08:25 | 2234 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B21120900008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-09 | 4468 | keep | 0 | Dec | 2021 | 0.0030431 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2021-12-09 08:32 | 2021-12-09 11:27 | 1 | 002:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B21120900009 | New_Event | Cutout Failure | Include | Include | Equipment | 175 | 2021-12-09 | 175 | keep | 0 | Dec | 2021 | 0.00011919 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-09 08:42 | 2021-12-09 08:52 | 169 | 000:10 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1116-5 | S21120900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2021-12-09 | 1690 | keep | 0 | Dec | 2021 | 0.0011511 | 0.00011511 | Sustained | FALSE | FALSE | Not_TMED_Event | 169
BAYAMON | 2021-12-09 08:42 | 2021-12-09 08:43 | 5 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1116-4 Y 1117-8 | S21120900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-09 | 5 | keep | 0 | Dec | 2021 | 3.4055e-06 | 3.4055e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-12-09 08:42 | 2021-12-09 08:52 | 466 | 000:10 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE P[ROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1116-5 | S21120900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2021-12-09 | 4660 | keep | 0 | Dec | 2021 | 0.0031739 | 0.00031739 | Sustained | FALSE | FALSE | Not_TMED_Event | 466
FAJARDO | 2021-12-09 09:09 | 2021-12-09 10:50 | 50 | 001:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L REEMPLAZO CAJA QUEMADA | R21120800035 | New_Event | Cutout Failure | Include | Include | Equipment | 101 | 2021-12-09 | 5050 | keep | 0 | Dec | 2021 | 0.0034395 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-12-09 09:25 | 2021-12-09 12:11 | 80 | 002:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE X AVE | R21120900015 | New_Event |  |  | Include | Wildlife | 166 | 2021-12-09 | 13280 | keep | 0 | Dec | 2021 | 0.0090449 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2021-12-09 09:30 | 2021-12-09 17:30 | 275 | 008:00 | P | DESGANCHE | SE REPARO NEUTRAL PARTIDO Y SE REALIZO DESGANCHE PRIMARIO | A21120900040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 480 | 2021-12-09 | 132000 | keep | 0 | Dec | 2021 | 0.089905 | 0.0001873 | Sustained | FALSE | FALSE | Not_TMED_Event | 275
ARECIBO | 2021-12-09 09:30 | 2021-12-09 12:06 | 100 | 002:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | A21120900026 | New_Event | Bad Weather | Include | Include | Weather | 156 | 2021-12-09 | 15600 | keep | 0 | Dec | 2021 | 0.010625 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-12-09 09:38 | 2021-12-09 12:49 | 14 | 003:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR CONECTORES SECUNDARIO | A21120900029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 191 | 2021-12-09 | 2674 | keep | 0 | Dec | 2021 | 0.0018212 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2021-12-09 09:57 | 2021-12-09 09:58 | 411 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21120900034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-09 | 411 | keep | 0 | Dec | 2021 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
BAYAMON | 2021-12-09 10:00 | 2021-12-09 14:28 | 300 | 004:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA Y SE CERRO MACHETE SU CARGA POR 1102-01 | S21120900016 | New_Event | Wire Down | Include | Include | Equipment | 268 | 2021-12-09 | 80400 | keep | 0 | Dec | 2021 | 0.05476 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2021-12-09 10:10 | 2021-12-09 10:29 | 10 | 000:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONDUCTOR SECUNDARIO | B21120900006 | New_Event | Secondary Wire Down | Include | Include | Equipment | 19 | 2021-12-09 | 190 | keep | 0 | Dec | 2021 | 0.00012941 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-09 10:12 | 2021-12-09 12:44 | 10 | 002:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR Y RETEZAR LINEA SECUNDARIA | B21120900018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 152 | 2021-12-09 | 1520 | keep | 0 | Dec | 2021 | 0.0010353 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-09 10:13 | 2021-12-09 10:28 | 1200 | 000:15 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR POSTE PRIMARIO PARTIDO | A21120900035 | New_Event | Defective Pole | Include | Include | Equipment | 15 | 2021-12-09 | 18000 | keep | 0 | Dec | 2021 | 0.01226 | 0.00081731 | Sustained | FALSE | FALSE | Not_TMED_Event | 1200
FAJARDO | 2021-12-09 10:17 | 2021-12-09 10:18 | 1394 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21120900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-09 | 1394 | keep | 0 | Dec | 2021 | 0.00094945 | 0.00094945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1394
ARECIBO | 2021-12-09 10:28 | 2021-12-09 21:00 | 10 | 010:32 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR POSTE PARTIDO | A21120800035 | Partial_restoration | Defective Pole | Include | Include | Equipment | 632 | 2021-12-09 | 6320 | keep | 0 | Dec | 2021 | 0.0043045 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-09 10:33 | 2021-12-09 12:53 | 7 | 002:20 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR QUEMADO DE 25 KVA X 25 KVA | R21120900025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 140 | 2021-12-09 | 980 | keep | 0 | Dec | 2021 | 0.00066747 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-12-09 10:43 | 2021-12-09 10:47 | 1085 | 000:04 | T | NO SE REPORTO CAUSA | RECERRO UNA VEZ QUEDO FUERA SE PROBO POR CONTROL QUEDO EN SERVICIO | S21120900042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-12-09 | 4340 | keep | 0 | Dec | 2021 | 0.002956 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
CAGUAS | 2021-12-09 10:46 | 2021-12-09 14:54 | 4 | 004:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN XMR REEMPLAZO SECUNDARIA | C21120900019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 248 | 2021-12-09 | 992 | keep | 0 | Dec | 2021 | 0.00067565 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2021-12-09 10:53 | 2021-12-09 14:05 | 16 | 003:12 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR REQUIERE DESGANCHE | M21120900037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2021-12-09 | 3072 | keep | 0 | Dec | 2021 | 0.0020923 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
GUAYAMA | 2021-12-09 11:17 | 2021-12-09 13:04 | 45 | 001:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO FASES | P21120900012 | New_Event |  |  | Include | Wildlife | 107 | 2021-12-09 | 4815 | keep | 0 | Dec | 2021 | 0.0032795 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2021-12-09 11:42 | 2021-12-09 11:43 | 1510 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE PERSONAL DE CLARO TRABAJANDO | C21120900022 | New_Event |  |  | Include | Wildlife | 1 | 2021-12-09 | 1510 | keep | 0 | Dec | 2021 | 0.0010285 | 0.0010285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1510
CAGUAS | 2021-12-09 11:43 | 2021-12-09 15:17 | 200 | 003:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 Y 2 X 80 EN C/L PERSONAL DE CLARO INSTALANDO POSTE GOLPEO LAS LINEAS | C21120900027 | 1st_after_momentary |  |  | Include | Wildlife | 214 | 2021-12-09 | 42800 | keep | 0 | Dec | 2021 | 0.029151 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
UTUADO | 2021-12-09 11:46 | 2021-12-09 13:36 | 50 | 001:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | A21120900057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2021-12-09 | 5500 | keep | 0 | Dec | 2021 | 0.003746 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2021-12-09 11:47 | 2021-12-09 16:04 | 7 | 004:17 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR AVERIADO DE 37.5 KVA X 37.5 KVA | C21120900025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 257 | 2021-12-09 | 1799 | keep | 0 | Dec | 2021 | 0.0012253 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2021-12-09 11:51 | 2021-12-09 15:13 | 10 | 003:22 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR AVERIADO DE 50 KVA X 50 KVA | C21120900012 | New_Event | Service Transformer Failure | Include | Include | Equipment | 202 | 2021-12-09 | 2020 | keep | 0 | Dec | 2021 | 0.0013758 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-09 11:52 | 2021-12-09 13:54 | 50 | 002:02 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | C21120900026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2021-12-09 | 6100 | keep | 0 | Dec | 2021 | 0.0041547 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-12-09 12:00 | 2021-12-09 18:06 | 1 | 006:06 | P | DESGANCHE | 1 X 30 EN RISER SE REALIZO DESGANCHE | B21120900031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 366 | 2021-12-09 | 366 | keep | 0 | Dec | 2021 | 0.00024928 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-09 12:10 | 2021-12-09 12:24 | 10 | 000:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | S21120900032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 14 | 2021-12-09 | 140 | keep | 0 | Dec | 2021 | 9.5353e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-09 12:17 | 2021-12-09 14:15 | 30 | 001:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN C/L LEVANTO CONDUCTOR | C21120900031 | New_Event | Wire Down | Include | Include | Equipment | 118 | 2021-12-09 | 3540 | keep | 0 | Dec | 2021 | 0.0024111 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-09 12:23 | 2021-12-09 16:23 | 25 | 004:00 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21120900032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2021-12-09 | 6000 | keep | 0 | Dec | 2021 | 0.0040866 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2021-12-09 12:48 | 2021-12-09 15:47 | 30 | 002:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | B21120900037 | New_Event | Cutout Failure | Include | Include | Equipment | 179 | 2021-12-09 | 5370 | keep | 0 | Dec | 2021 | 0.0036575 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-12-09 12:50 | 2021-12-09 14:56 | 8 | 002:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C21120900033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 126 | 2021-12-09 | 1008 | keep | 0 | Dec | 2021 | 0.00068654 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-12-09 12:55 | 2021-12-09 15:35 | 12 | 002:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA CERRAR PUENTE SECUNDARIO SOBRE EL TRANSFORMADOR | S21120900060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 160 | 2021-12-09 | 1920 | keep | 0 | Dec | 2021 | 0.0013077 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-12-09 13:01 | 2021-12-09 14:21 | 40 | 001:20 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21120900040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 80 | 2021-12-09 | 3200 | keep | 0 | Dec | 2021 | 0.0021795 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-12-09 13:12 | 2021-12-09 17:19 | 20 | 004:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA LEVANTAR PRIMARIA | S21120900062 | New_Event | Wire Down | Include | Include | Equipment | 247 | 2021-12-09 | 4940 | keep | 0 | Dec | 2021 | 0.0033646 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-12-09 13:12 | 2021-12-09 16:17 | 10 | 003:05 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B21120900042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 185 | 2021-12-09 | 1850 | keep | 0 | Dec | 2021 | 0.00126 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-09 13:20 | 2021-12-09 13:22 | 1746 | 000:02 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR SE CERRO POR SCADA PERSONAL PRIVADO CRUZO LINEAS CON BRAZO MECANICO DE GRUA | B21120900044 | New_Event |  |  | Include | Wildlife | 2 | 2021-12-09 | 3492 | keep | 0 | Dec | 2021 | 0.0023784 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
BAYAMON | 2021-12-09 13:22 | 2021-12-09 13:52 | 25 | 000:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR TRAMO DE LINEA DONDE PERSONAL PRIVADO CRUZO LINEAS CON BRAZO MECANICO DE GRUA | B21120900000 | 1st_after_momentary |  |  | Include | Wildlife | 30 | 2021-12-09 | 750 | keep | 0 | Dec | 2021 | 0.00051082 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2021-12-09 13:30 | 2021-12-09 13:51 | 551 | 000:21 | T | NO SE REPORTO CAUSA | DISPARO SE VERIFICO PERSONAL FUERA | C21120900036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 21 | 2021-12-09 | 11571 | keep | 0 | Dec | 2021 | 0.007881 | 0.00037528 | Sustained | FALSE | FALSE | Not_TMED_Event | 551
CAGUAS | 2021-12-09 13:35 | 2021-12-09 13:45 | 1001 | 000:10 | T | NO SE REPORTO CAUSA | DISPARO | C21120900037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2021-12-09 | 10010 | keep | 0 | Dec | 2021 | 0.0068178 | 0.00068178 | Sustained | FALSE | FALSE | Not_TMED_Event | 1001
BAYAMON | 2021-12-09 13:35 | 2021-12-09 16:55 | 30 | 003:20 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21120900046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 200 | 2021-12-09 | 6000 | keep | 0 | Dec | 2021 | 0.0040866 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-09 13:40 | 2021-12-09 15:11 | 12 | 001:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21120900045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 91 | 2021-12-09 | 1092 | keep | 0 | Dec | 2021 | 0.00074376 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2021-12-09 13:40 | 2021-12-09 15:33 | 43 | 001:53 | P | DESGANCHE | 1 X 20 Y 1 X 10 EN CORTE DE LINEA | R21120900037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2021-12-09 | 4859 | keep | 0 | Dec | 2021 | 0.0033094 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
HUMACAO | 2021-12-09 13:51 | 2021-12-09 16:35 | 30 | 002:44 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L NO CAUSA | C21120900042 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 164 | 2021-12-09 | 4920 | keep | 0 | Dec | 2021 | 0.003351 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-09 13:52 | 2021-12-09 15:03 | 1746 | 001:11 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR TRAMO DE LINEA DONDE PERSONAL PRIVADO CRUZO LINEAS CON BRAZO MECANICO DE GRUA | B21120900000 | Additional_clients |  |  | Include | Wildlife | 71 | 2021-12-09 | 123966 | keep | 0 | Dec | 2021 | 0.084433 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2021-12-09 13:53 | 2021-12-09 14:13 | 1 | 000:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE DE FASE POR AVE | P21120900023 | New_Event |  |  | Include | Wildlife | 20 | 2021-12-09 | 20 | keep | 0 | Dec | 2021 | 1.3622e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-09 13:55 | 2021-12-09 19:20 | 35 | 005:25 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE DE ARBOL | M21120900056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 325 | 2021-12-09 | 11375 | keep | 0 | Dec | 2021 | 0.0077475 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
GUAYAMA | 2021-12-09 13:58 | 2021-12-09 13:59 | 464 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | P21120900040 | New_Event |  |  | Include | Wildlife | 1 | 2021-12-09 | 464 | keep | 0 | Dec | 2021 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
ARECIBO | 2021-12-09 13:58 | 2021-12-09 15:10 | 15 | 001:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A21120900075 | New_Event | Bad Weather | Include | Include | Weather | 72 | 2021-12-09 | 1080 | keep | 0 | Dec | 2021 | 0.00073558 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2021-12-09 13:59 | 2021-12-09 16:00 | 30 | 002:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P21120900024 | 1st_after_momentary |  |  | Include | Wildlife | 121 | 2021-12-09 | 3630 | keep | 0 | Dec | 2021 | 0.0024724 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2021-12-09 14:07 | 2021-12-09 16:47 | 1 | 002:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | M21120900058 | New_Event | Wire Down | Include | Include | Equipment | 160 | 2021-12-09 | 160 | keep | 0 | Dec | 2021 | 0.00010898 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-12-09 14:18 | 2021-12-09 17:54 | 130 | 003:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | R21120900039 | New_Event | Cutout Failure | Include | Include | Equipment | 216 | 2021-12-09 | 28080 | keep | 0 | Dec | 2021 | 0.019125 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
UTUADO | 2021-12-09 14:30 | 2021-12-09 15:54 | 30 | 001:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21120900070 | New_Event | Bad Weather | Include | Include | Weather | 84 | 2021-12-09 | 2520 | keep | 0 | Dec | 2021 | 0.0017164 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2021-12-09 14:36 | 2021-12-09 18:00 | 8 | 003:24 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA PARTIDA POR RAMA | P21120900028 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 204 | 2021-12-09 | 1632 | keep | 0 | Dec | 2021 | 0.0011115 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2021-12-09 14:38 | 2021-12-09 16:30 | 1 | 001:52 | P | NO SE REPORTO CAUSA | 1 X 15 EN MONTURA DE TRANSFORMADORES NO SE ENCONTRO CAUSA | P21120900029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2021-12-09 | 112 | keep | 0 | Dec | 2021 | 7.6283e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-09 14:40 | 2021-12-09 14:41 | 302 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21120900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-09 | 302 | keep | 0 | Dec | 2021 | 0.00020569 | 0.00020569 | Momentary | FALSE | FALSE | Not_TMED_Event | 302
CAGUAS | 2021-12-09 14:43 | 2021-12-09 16:21 | 1 | 001:38 | P | DESGANCHE | 1 X 40 EN C/L | C21120900050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 98 | 2021-12-09 | 98 | keep | 0 | Dec | 2021 | 6.6747e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-09 14:48 | 2021-12-09 15:03 | 1117 | 000:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M21120900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-12-09 | 16755 | keep | 0 | Dec | 2021 | 0.011412 | 0.00076078 | Sustained | FALSE | FALSE | Not_TMED_Event | 1117
MAYAGÃœEZ | 2021-12-09 14:48 | 2021-12-09 15:03 | 1671 | 000:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M21120900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-12-09 | 25065 | keep | 0 | Dec | 2021 | 0.017072 | 0.0011381 | Sustained | FALSE | FALSE | Not_TMED_Event | 1671
MAYAGÃœEZ | 2021-12-09 14:48 | 2021-12-09 15:03 | 527 | 000:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M21120900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-12-09 | 7905 | keep | 0 | Dec | 2021 | 0.0053841 | 0.00035894 | Sustained | FALSE | FALSE | Not_TMED_Event | 527
MAYAGÃœEZ | 2021-12-09 14:48 | 2021-12-09 15:03 | 671 | 000:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M21120900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-12-09 | 10065 | keep | 0 | Dec | 2021 | 0.0068552 | 0.00045702 | Sustained | FALSE | FALSE | Not_TMED_Event | 671
HUMACAO | 2021-12-09 14:50 | 2021-12-09 15:48 | 65 | 000:58 | P | DESGANCHE | 2 X 40 EN C/L | C21120900051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2021-12-09 | 3770 | keep | 0 | Dec | 2021 | 0.0025677 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2021-12-09 15:01 | 2021-12-09 15:55 | 8 | 000:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21120900070 | New_Event | Secondary Wire Down | Include | Include | Equipment | 54 | 2021-12-09 | 432 | keep | 0 | Dec | 2021 | 0.00029423 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-12-09 15:03 | 2021-12-09 18:42 | 25 | 003:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE RETIRO GRUA CRUZANDO LAS LINEAS Y SE CERRO SU-1 | B21120900000 | Partial_restoration |  |  | Include | Wildlife | 219 | 2021-12-09 | 5475 | keep | 0 | Dec | 2021 | 0.003729 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-12-09 15:14 | 2021-12-09 17:17 | 80 | 002:03 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE DE ARBOL | M21120900081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2021-12-09 | 9840 | keep | 0 | Dec | 2021 | 0.006702 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2021-12-09 15:31 | 2021-12-09 16:47 | 1 | 001:16 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | C21120900057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 76 | 2021-12-09 | 76 | keep | 0 | Dec | 2021 | 5.1763e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-12-09 15:33 | 2021-12-09 22:00 | 70 | 006:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO CORTE DE LINEA PARA REMPLAZAR POSTE PRIMARIO DE MADERA 40 PIES IMPACTADO POR VEHICULO Y PARTIDO EN EL FID31399386 POR POSTE DE METAL 40 PIES | M21120900085 | New_Event |  |  | Include | Wildlife | 387 | 2021-12-09 | 27090 | keep | 0 | Dec | 2021 | 0.018451 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-12-09 15:45 | 2021-12-10 11:45 | 50 | 020:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA DE 100 AMP | M21120900086 | New_Event | Cutout Failure | Include | Include | Equipment | 1200 | 2021-12-09 | 60000 | keep | 0 | Dec | 2021 | 0.040866 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-12-09 15:45 | 2021-12-10 09:12 | 100 | 017:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | M21120900086 | New_Event | Cutout Failure | Include | Include | Equipment | 1047 | 2021-12-09 | 104700 | keep | 0 | Dec | 2021 | 0.071311 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-12-09 15:47 | 2021-12-09 16:55 | 5 | 001:08 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHE | C21120900062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2021-12-09 | 340 | keep | 0 | Dec | 2021 | 0.00023157 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2021-12-09 15:50 | 2021-12-09 17:28 | 75 | 001:38 | P | DESGANCHE | 2 X 40 EN C/L | C21120900063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 98 | 2021-12-09 | 7350 | keep | 0 | Dec | 2021 | 0.0050061 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
UTUADO | 2021-12-09 15:51 | 2021-12-09 16:30 | 60 | 000:39 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA ENDEREZAR POSTE VIRADO | A21120800082 | New_Event | Defective Pole | Include | Include | Equipment | 39 | 2021-12-09 | 2340 | keep | 0 | Dec | 2021 | 0.0015938 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-12-09 16:00 | 2021-12-09 19:07 | 50 | 003:07 | P | ESTRUCTURA AVERIADA | SE ABRE CORTE DE LINEA PARA LEVANTAR LINEA Y SE INSTALO POSTE Y SE CERRO PUENTE PRIMARIO | S21120800038 | Additional_clients | Defective Pole | Include | Include | Equipment | 187 | 2021-12-09 | 9350 | keep | 0 | Dec | 2021 | 0.0063682 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-09 16:18 | 2021-12-09 18:41 | 60 | 002:23 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | S21120900076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2021-12-09 | 8580 | keep | 0 | Dec | 2021 | 0.0058438 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2021-12-09 16:32 | 2021-12-09 18:22 | 80 | 001:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE X AVE | C21120900069 | New_Event |  |  | Include | Wildlife | 110 | 2021-12-09 | 8800 | keep | 0 | Dec | 2021 | 0.0059936 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-12-09 16:34 | 2021-12-09 16:35 | 271 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21120900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-09 | 271 | keep | 0 | Dec | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
BAYAMON | 2021-12-09 16:47 | 2021-12-09 18:24 | 12 | 001:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21120900062 | New_Event | Secondary Wire Down | Include | Include | Equipment | 97 | 2021-12-09 | 1164 | keep | 0 | Dec | 2021 | 0.0007928 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-12-09 18:14 | 2021-12-09 18:15 | 4188 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21120900044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-09 | 4188 | keep | 0 | Dec | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CAGUAS | 2021-12-09 18:43 | 2021-12-10 10:32 | 30 | 015:49 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L NO CAUSA | C21120900082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 949 | 2021-12-09 | 28470 | keep | 0 | Dec | 2021 | 0.019391 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-09 18:53 | 2021-12-09 23:00 | 60 | 004:07 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21120900086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 247 | 2021-12-09 | 14820 | keep | 0 | Dec | 2021 | 0.010094 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2021-12-09 22:00 | 2021-12-09 22:35 | 26 | 000:35 | P | DESGANCHE | ARBOL CAE SOBRE TRANSFORMADOR AVERIANDO PUENTES PRIMARIOS EN EL TRANSFORMADOR Y LINEA SECUNDARIA | P21120900041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 35 | 2021-12-09 | 910 | keep | 0 | Dec | 2021 | 0.0006198 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
SAN JUAN | 2021-12-09 22:11 | 2021-12-10 00:10 | 10211 | 001:59 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR CONTROL CARGA POR EL 1206-03 | S21120900090 | New_Event |  |  | Include | Wildlife | 119 | 2021-12-09 | 1215109 | keep | 0 | Dec | 2021 | 0.82761 | 0.0069547 | Sustained | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-12-09 22:11 | 2021-12-10 00:10 | 4133 | 001:59 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR CONTROL LLEVA LA CARGA DEL 1204-05 | S21120900090 | New_Event |  |  | Include | Wildlife | 119 | 2021-12-09 | 491827 | keep | 0 | Dec | 2021 | 0.33498 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
MAYAGÃœEZ | 2021-12-09 23:33 | 2021-12-09 23:34 | 1287 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21120900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-09 | 1287 | keep | 0 | Dec | 2021 | 0.00087657 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
BAYAMON | 2021-12-10 01:00 | 2021-12-10 11:31 | 27 | 010:31 | P | CABLE SOTERRADO AVERIADO | 1 X 40 RISER. SE DEJO FUERA DEL T-9 @ T-7 POR AVERIA SOTERRADA | B21121000001 | New_Event | UG Cable Fault | Include | Include | Equipment | 631 | 2021-12-10 | 17037 | keep | 0 | Dec | 2021 | 0.011604 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
SAN JUAN | 2021-12-10 02:03 | 2021-12-10 03:15 | 10211 | 001:12 | T | ANIMAL U OBJETO EXTRAÃ‘O | CARGA TRANSFERIDA AL 1206-03 SE RETIRO CULEBRA SOBRE CRUCETA | S21120900090 | New_Event |  |  | Include | Wildlife | 72 | 2021-12-10 | 735192 | keep | 0 | Dec | 2021 | 0.50074 | 0.0069547 | Sustained | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-12-10 02:03 | 2021-12-10 02:04 | 4133 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR CONTROL LLEVA LA CARGA DEL 1204-05 | S21120900090 | New_Event |  |  | Include | Wildlife | 1 | 2021-12-10 | 4133 | keep | 0 | Dec | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
MAYAGÃœEZ | 2021-12-10 02:03 | 2021-12-10 09:32 | 200 | 007:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO EN LINEA PRIMARIA | M21121000002 | New_Event | Wire Down | Include | Include | Equipment | 449 | 2021-12-10 | 89800 | keep | 0 | Dec | 2021 | 0.061162 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-12-10 02:04 | 2021-12-10 03:15 | 3000 | 001:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE RETIRO CULEBRA SOBRE CRUCETA Y PARARAYO LLEVA LA CARGA DEL 1204-05 | S21120900090 | 1st_after_momentary |  |  | Include | Wildlife | 71 | 2021-12-10 | 213000 | keep | 0 | Dec | 2021 | 0.14507 | 0.0020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 3000
MAYAGÃœEZ | 2021-12-10 02:43 | 2021-12-10 02:44 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21121000003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-10 | 1097 | keep | 0 | Dec | 2021 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
BAYAMON | 2021-12-10 02:46 | 2021-12-11 18:13 | 20 | 039:27 | P | CABLE SOTERRADO AVERIADO | SE REPARO AVERIA SOTERRADA DE SU-2 @ T-3 | B21121000003 | New_Event | UG Cable Fault | Include | Include | Equipment | 2367 | 2021-12-10 | 47340 | keep | 0 | Dec | 2021 | 0.032243 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-12-10 04:45 | 2021-12-10 09:06 | 52 | 004:21 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S21121000021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 261 | 2021-12-10 | 13572 | keep | 0 | Dec | 2021 | 0.0092438 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
BAYAMON | 2021-12-10 05:08 | 2021-12-10 15:44 | 30 | 010:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA 1 X 15 EN TRANSFORMADOR Y SE REMPLAZO CAJA | B21121000004 | New_Event | Cutout Failure | Include | Include | Equipment | 636 | 2021-12-10 | 19080 | keep | 0 | Dec | 2021 | 0.012995 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-10 05:43 | 2021-12-10 05:44 | 3431 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | A21121000001 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-12-10 | 3431 | keep | 0 | Dec | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2021-12-10 05:44 | 2021-12-10 09:30 | 80 | 003:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21121000003 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 226 | 2021-12-10 | 18080 | keep | 0 | Dec | 2021 | 0.012314 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-12-10 06:06 | 2021-12-10 12:31 | 30 | 006:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA Y SE REALIZO DESGANCHE | S21121000024 | New_Event | Cutout Failure | Include | Include | Equipment | 385 | 2021-12-10 | 11550 | keep | 0 | Dec | 2021 | 0.0078667 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2021-12-10 06:21 | 2021-12-10 16:40 | 40 | 010:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CRUCE X AVE | C21121000002 | New_Event |  |  | Include | Wildlife | 619 | 2021-12-10 | 24760 | keep | 0 | Dec | 2021 | 0.016864 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-12-10 07:14 | 2021-12-10 09:03 | 20 | 001:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN C/L MAL TIEMPO | C21121000003 | New_Event | Bad Weather | Include | Include | Weather | 109 | 2021-12-10 | 2180 | keep | 0 | Dec | 2021 | 0.0014848 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-12-10 07:34 | 2021-12-10 11:27 | 100 | 003:53 | P | NO SE REPORTO CAUSA | 2 X 50 EN C/L NO CAUSA | R21121000006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 233 | 2021-12-10 | 23300 | keep | 0 | Dec | 2021 | 0.01587 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-12-10 07:46 | 2021-12-10 08:05 | 1588 | 000:19 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR DE ALTA CONDUCTOR EN EL SUELO EN ALIMENTADOR 1711-02 | B21121000000 | New_Event | Wire Down | Include | Include | Equipment | 19 | 2021-12-10 | 30172 | keep | 0 | Dec | 2021 | 0.02055 | 0.0010816 | Sustained | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2021-12-10 07:46 | 2021-12-10 13:25 | 723 | 005:39 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR FRENTE A BTC | B21121000000 | New_Event | Wire Down | Include | Include | Equipment | 339 | 2021-12-10 | 245097 | keep | 0 | Dec | 2021 | 0.16693 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2021-12-10 07:46 | 2021-12-10 08:05 | 13 | 000:19 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR DE ALTA CONDUCTOR EN EL SUELO EN ALIMENTADOR 1711-02 | B21121000000 | New_Event | Wire Down | Include | Include | Equipment | 19 | 2021-12-10 | 247 | keep | 0 | Dec | 2021 | 0.00016823 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2021-12-10 07:46 | 2021-12-10 13:25 | 1976 | 005:39 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR FRENTE A BTC | B21121000000 | New_Event | Wire Down | Include | Include | Equipment | 339 | 2021-12-10 | 669864 | keep | 0 | Dec | 2021 | 0.45624 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
FAJARDO | 2021-12-10 07:49 | 2021-12-10 10:41 | 1 | 002:52 | P | SECUNDARIA/DESGANCHE | 2 X 10 EN XMR DESGANCHO | R21121000009 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 172 | 2021-12-10 | 172 | keep | 0 | Dec | 2021 | 0.00011715 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-10 07:52 | 2021-12-10 20:15 | 10 | 012:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21121000011 | New_Event | Bad Weather | Include | Include | Weather | 743 | 2021-12-10 | 7430 | keep | 0 | Dec | 2021 | 0.0050605 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-10 07:58 | 2021-12-10 07:59 | 3597 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21121000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-10 | 3597 | keep | 0 | Dec | 2021 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2021-12-10 07:59 | 2021-12-10 15:58 | 75 | 007:59 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21121000025 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 479 | 2021-12-10 | 35925 | keep | 0 | Dec | 2021 | 0.024468 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2021-12-10 08:05 | 2021-12-10 08:06 | 1597 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21121000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-10 | 1597 | keep | 0 | Dec | 2021 | 0.0010877 | 0.0010877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1597
ARECIBO | 2021-12-10 08:07 | 2021-12-10 10:23 | 20 | 002:16 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR | A21121000005 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 136 | 2021-12-10 | 2720 | keep | 0 | Dec | 2021 | 0.0018526 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-12-10 08:09 | 2021-12-10 08:10 | 1342 | 000:01 | T | DESGANCHE | RECIERRE | C21121000018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-10 | 1342 | keep | 0 | Dec | 2021 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
SAN JUAN | 2021-12-10 08:10 | 2021-12-11 09:25 | 20 | 025:15 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | S21121000031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1515 | 2021-12-10 | 30300 | keep | 0 | Dec | 2021 | 0.020637 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-12-10 08:10 | 2021-12-10 10:33 | 80 | 002:23 | P | DESGANCHE | 1 X 65 EN C/L | C21121000005 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 143 | 2021-12-10 | 11440 | keep | 0 | Dec | 2021 | 0.0077917 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2021-12-10 08:19 | 2021-12-10 09:58 | 10 | 001:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN C/L MAL TIEMPO | R21121000011 | New_Event | Bad Weather | Include | Include | Weather | 99 | 2021-12-10 | 990 | keep | 0 | Dec | 2021 | 0.00067428 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-10 08:20 | 2021-12-10 13:24 | 1 | 005:04 | P | NO SE REPORTO CAUSA | 2 X 40 1 X 80 EN CORTE DE LINEA | S21121000058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 304 | 2021-12-10 | 304 | keep | 0 | Dec | 2021 | 0.00020705 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-10 08:23 | 2021-12-10 09:34 | 10 | 001:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | M21121000031 | New_Event | Bad Weather | Include | Include | Weather | 71 | 2021-12-10 | 710 | keep | 0 | Dec | 2021 | 0.00048358 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-10 08:35 | 2021-12-10 08:36 | 4304 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | M21121000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-10 | 4304 | keep | 0 | Dec | 2021 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
CAGUAS | 2021-12-10 08:58 | 2021-12-10 12:49 | 5 | 003:51 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIO XMR PARA REMPLAZAR 2 POSTES SECUNDARIOS Y LINEA SECUNDARIA | C21121000007 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 231 | 2021-12-10 | 1155 | keep | 0 | Dec | 2021 | 0.00078667 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2021-12-10 09:00 | 2021-12-10 11:52 | 26 | 002:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA DE 100 AMP EN TRANSFORMADOR | P21121000004 | New_Event | Cutout Failure | Include | Include | Equipment | 172 | 2021-12-10 | 4472 | keep | 0 | Dec | 2021 | 0.0030459 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
VEGA BAJA | 2021-12-10 09:00 | 2021-12-10 11:52 | 3332 | 002:52 | T | DESGANCHE | SE ENCONTRO INTERRUPTOR ABIERTO TIENE MACHETE EN RISER DE SALIDA QUEMADO SE TRANSFIRIO POR B/I AL 9002-02 | B21121000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2021-12-10 | 573104 | keep | 0 | Dec | 2021 | 0.39034 | 0.0022694 | Sustained | FALSE | FALSE | Not_TMED_Event | 3332
BAYAMON | 2021-12-10 09:10 | 2021-12-10 10:01 | 16 | 000:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO SECUNDARIA | B21121000033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 51 | 2021-12-10 | 816 | keep | 0 | Dec | 2021 | 0.00055577 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
YAUCO | 2021-12-10 09:28 | 2021-12-10 17:30 | 12 | 008:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE CAJA DE TRANSFORMADOR PARA REPARAR CONECTOR SECUNDARIO | P21121000007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 482 | 2021-12-10 | 5784 | keep | 0 | Dec | 2021 | 0.0039395 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-12-10 09:31 | 2021-12-10 11:21 | 6 | 001:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | R21121000018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 110 | 2021-12-10 | 660 | keep | 0 | Dec | 2021 | 0.00044952 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2021-12-10 09:32 | 2021-12-10 12:24 | 5 | 002:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN XMR | R21121000017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 172 | 2021-12-10 | 860 | keep | 0 | Dec | 2021 | 0.00058574 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-12-10 09:32 | 2021-12-10 09:34 | 1 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2600 | A21121000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-12-10 | 2 | keep | 0 | Dec | 2021 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-12-10 09:32 | 2021-12-10 09:34 | 2266 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2600 | A21121000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-12-10 | 4532 | keep | 0 | Dec | 2021 | 0.0030867 | 0.0015434 | Momentary | FALSE | FALSE | Not_TMED_Event | 2266
ARECIBO | 2021-12-10 09:32 | 2021-12-10 09:34 | 1399 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2600 | A21121000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-12-10 | 2798 | keep | 0 | Dec | 2021 | 0.0019057 | 0.00095285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1399
MAYAGÃœEZ | 2021-12-10 09:34 | 2021-12-10 11:09 | 200 | 001:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO EN LINEA PRIMARIA | M21121000002 | Partial_restoration | Wire Down | Include | Include | Equipment | 95 | 2021-12-10 | 19000 | keep | 0 | Dec | 2021 | 0.012941 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-12-10 09:34 | 2021-12-10 11:27 | 27 | 001:53 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR ROTO | B21121000000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 113 | 2021-12-10 | 3051 | keep | 0 | Dec | 2021 | 0.002078 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
CAGUAS | 2021-12-10 09:42 | 2021-12-10 14:07 | 4 | 004:25 | P | ESTRUCTURA AVERIADA | ABRIO XMR PARA REEMPLAZAR POSTE PARTIDO | C21121000012 | New_Event | Defective Pole | Include | Include | Equipment | 265 | 2021-12-10 | 1060 | keep | 0 | Dec | 2021 | 0.00072196 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-12-10 09:43 | 2021-12-10 17:22 | 30 | 007:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | S21120900033 | New_Event | Cutout Failure | Include | Include | Equipment | 459 | 2021-12-10 | 13770 | keep | 0 | Dec | 2021 | 0.0093787 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-12-10 09:54 | 2021-12-10 12:25 | 45 | 002:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE X AVE | C21121000013 | New_Event |  |  | Include | Wildlife | 151 | 2021-12-10 | 6795 | keep | 0 | Dec | 2021 | 0.004628 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
YAUCO | 2021-12-10 09:54 | 2021-12-10 13:28 | 2 | 003:34 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21121000008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 214 | 2021-12-10 | 428 | keep | 0 | Dec | 2021 | 0.00029151 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2021-12-10 09:56 | 2021-12-10 12:20 | 60 | 002:24 | P | PARARRAYOS DEFECTUOSO | 1 X 30 Y 1 X 40 EN C/L REEMPLAZO PARARRAYO | C21121000015 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 144 | 2021-12-10 | 8640 | keep | 0 | Dec | 2021 | 0.0058847 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-12-10 10:02 | 2021-12-10 11:13 | 18 | 001:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR CONECTORES SECUNDARIOS | A21121000015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 71 | 2021-12-10 | 1278 | keep | 0 | Dec | 2021 | 0.00087044 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
PONCE | 2021-12-10 10:16 | 2021-12-10 16:45 | 7 | 006:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA DE TRANSFORMADOR PARA REPARAR SECUNDARIA | P21121000017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 389 | 2021-12-10 | 2723 | keep | 0 | Dec | 2021 | 0.0018546 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-12-10 10:25 | 2021-12-10 10:27 | 500 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1118-10 LLEVANDO 20% 1111-01 SE CERRO POR SCADA | S21121000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-10 | 1000 | keep | 0 | Dec | 2021 | 0.0006811 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2021-12-10 10:25 | 2021-12-10 10:27 | 2782 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1118-10 LLEVANDO 20% 1111-01 SE CERRO POR SCADA | S21121000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-10 | 5564 | keep | 0 | Dec | 2021 | 0.0037896 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
GUAYAMA | 2021-12-10 10:27 | 2021-12-10 11:37 | 13 | 001:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 EN CORTE DE LINEA LINEA SECUNDARIA CRUZADA CON LINEA PRIMARIA | P21121000012 | New_Event | Wire Down | Include | Include | Equipment | 70 | 2021-12-10 | 910 | keep | 0 | Dec | 2021 | 0.0006198 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
ARECIBO | 2021-12-10 10:28 | 2021-12-10 13:49 | 30 | 003:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | A21121000016 | New_Event | Cutout Failure | Include | Include | Equipment | 201 | 2021-12-10 | 6030 | keep | 0 | Dec | 2021 | 0.004107 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2021-12-10 10:39 | 2021-12-10 16:21 | 35 | 005:42 | P | DESGANCHE | SE ABRIO CORTE DE LINEA Y SE REALIZO DESGANCHE | A21121000017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 342 | 2021-12-10 | 11970 | keep | 0 | Dec | 2021 | 0.0081527 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
HUMACAO | 2021-12-10 10:48 | 2021-12-10 11:45 | 21 | 000:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA Y TOMAS | C21121000020 | New_Event | Secondary Wire Down | Include | Include | Equipment | 57 | 2021-12-10 | 1197 | keep | 0 | Dec | 2021 | 0.00081527 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BAYAMON | 2021-12-10 10:49 | 2021-12-10 12:59 | 1 | 002:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B21121000049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 130 | 2021-12-10 | 130 | keep | 0 | Dec | 2021 | 8.8542e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-10 11:04 | 2021-12-10 12:41 | 10 | 001:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR Y LEVANTAR SECUNDARIA | S21121000025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 97 | 2021-12-10 | 970 | keep | 0 | Dec | 2021 | 0.00066066 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-10 11:09 | 2021-12-10 11:39 | 1 | 000:30 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A21121000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 30 | 2021-12-10 | 30 | keep | 0 | Dec | 2021 | 2.0433e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-12-10 11:09 | 2021-12-10 11:39 | 2266 | 000:30 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A21121000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 30 | 2021-12-10 | 67980 | keep | 0 | Dec | 2021 | 0.046301 | 0.0015434 | Sustained | FALSE | FALSE | Not_TMED_Event | 2266
ARECIBO | 2021-12-10 11:09 | 2021-12-10 11:39 | 1399 | 000:30 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A21121000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 30 | 2021-12-10 | 41970 | keep | 0 | Dec | 2021 | 0.028586 | 0.00095285 | Sustained | FALSE | FALSE | Not_TMED_Event | 1399
BAYAMON | 2021-12-10 11:14 | 2021-12-11 10:00 | 1 | 022:46 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L | B21121000054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1366 | 2021-12-10 | 1366 | keep | 0 | Dec | 2021 | 0.00093038 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-12-10 11:15 | 2021-12-10 12:43 | 5 | 001:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | R21121000022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 88 | 2021-12-10 | 440 | keep | 0 | Dec | 2021 | 0.00029968 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-12-10 11:15 | 2021-12-10 13:10 | 1 | 001:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M21121000059 | New_Event | Bad Weather | Include | Include | Weather | 115 | 2021-12-10 | 115 | keep | 0 | Dec | 2021 | 7.8326e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-10 11:16 | 2021-12-10 17:52 | 1 | 006:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REMPLAZO BAJANTE PRIMARIO LINEA A CAJA | S21121000041 | New_Event | Wire Down | Include | Include | Equipment | 396 | 2021-12-10 | 396 | keep | 0 | Dec | 2021 | 0.00026971 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-12-10 11:25 | 2021-12-10 12:57 | 14 | 001:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REMPLAZO DE CONEXIONES SECUNDARIAS | P21121000018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 92 | 2021-12-10 | 1288 | keep | 0 | Dec | 2021 | 0.00087725 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2021-12-10 11:31 | 2021-12-11 19:37 | 14 | 032:06 | P | CABLE SOTERRADO AVERIADO | SE INSTALO AEREO PROVISIONAL DESDE T-9 @ T-7 MEDIANTE GOI BY-211210-01 | B21121100001 | New_Event | UG Cable Fault | Include | Include | Equipment | 1926 | 2021-12-10 | 26964 | keep | 0 | Dec | 2021 | 0.018365 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
HUMACAO | 2021-12-10 11:31 | 2021-12-10 15:20 | 1 | 003:49 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO CAUSA | C21121000025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 229 | 2021-12-10 | 229 | keep | 0 | Dec | 2021 | 0.00015597 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-10 11:36 | 2021-12-10 16:22 | 10 | 004:46 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE REALIZO DESGANCHE SECUNDARIO | M21121000066 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 286 | 2021-12-10 | 2860 | keep | 0 | Dec | 2021 | 0.0019479 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-10 11:39 | 2021-12-10 16:00 | 200 | 004:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO EN LINEA PRIMARIA | M21121000002 | New_Event | Wire Down | Include | Include | Equipment | 261 | 2021-12-10 | 52200 | keep | 0 | Dec | 2021 | 0.035553 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2021-12-10 11:42 | 2021-12-10 14:00 | 40 | 002:18 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | R21121000025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 138 | 2021-12-10 | 5520 | keep | 0 | Dec | 2021 | 0.0037596 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-12-10 11:49 | 2021-12-10 11:51 | 553 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-15 LLEVANDO 30% 1346-02 SE CERRO POR SCADA | S21121000044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-10 | 1106 | keep | 0 | Dec | 2021 | 0.00075329 | 0.00037665 | Momentary | FALSE | FALSE | Not_TMED_Event | 553
BAYAMON | 2021-12-10 11:49 | 2021-12-10 11:51 | 1802 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-15 LLEVANDO 30% 1346-02 SE CERRO POR SCADA | S21121000044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-10 | 3604 | keep | 0 | Dec | 2021 | 0.0024547 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
MAYAGÃœEZ | 2021-12-10 11:51 | 2021-12-10 14:46 | 372 | 002:55 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE RETIRO RAMA SOBRE TRONCAL DEL ALIMENTADOR | M21121000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2021-12-10 | 65100 | keep | 0 | Dec | 2021 | 0.044339 | 0.00025337 | Sustained | FALSE | FALSE | Not_TMED_Event | 372
ARECIBO | 2021-12-10 11:56 | 2021-12-10 14:40 | 5 | 002:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21121000027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 164 | 2021-12-10 | 820 | keep | 0 | Dec | 2021 | 0.0005585 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-12-10 12:07 | 2021-12-10 12:08 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21121000055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-10 | 2203 | keep | 0 | Dec | 2021 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2021-12-10 12:08 | 2021-12-10 15:02 | 1 | 002:54 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | S21121000051 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 174 | 2021-12-10 | 174 | keep | 0 | Dec | 2021 | 0.00011851 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-12-10 12:10 | 2021-12-10 17:56 | 100 | 005:46 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHO Y REEMPLAZO CAJA AVERIADA | C21121000028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 346 | 2021-12-10 | 34600 | keep | 0 | Dec | 2021 | 0.023566 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-12-10 12:14 | 2021-12-10 15:16 | 30 | 003:02 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21121000048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2021-12-10 | 5460 | keep | 0 | Dec | 2021 | 0.0037188 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-12-10 12:14 | 2021-12-10 17:14 | 165 | 005:00 | P | LINEA DE TRANSMISION 38KV | 3 X 50 EN C/L LEVANTO FASE DE LA LINEA 37800 CRUZANDO LA DISTRIBUCION | C21121000029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 300 | 2021-12-10 | 49500 | keep | 0 | Dec | 2021 | 0.033714 | 0.00011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 165
CANOVANAS | 2021-12-10 12:22 | 2021-12-10 15:11 | 60 | 002:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA REEMPLAZO PORTAFUSIBLE | R21121000027 | New_Event | Cutout Failure | Include | Include | Equipment | 169 | 2021-12-10 | 10140 | keep | 0 | Dec | 2021 | 0.0069063 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2021-12-10 12:23 | 2021-12-10 13:57 | 543 | 001:34 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE REPARO LINEA PRIMARIA PARTIDA | M21121000065 | New_Event | Wire Down | Include | Include | Equipment | 94 | 2021-12-10 | 51042 | keep | 0 | Dec | 2021 | 0.034764 | 0.00036983 | Sustained | FALSE | FALSE | Not_TMED_Event | 543
ARECIBO | 2021-12-10 12:27 | 2021-12-10 19:02 | 10 | 006:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | A21121000030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 395 | 2021-12-10 | 3950 | keep | 0 | Dec | 2021 | 0.0026903 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-10 12:30 | 2021-12-10 13:09 | 20 | 000:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M21121000084 | New_Event | Bad Weather | Include | Include | Weather | 39 | 2021-12-10 | 780 | keep | 0 | Dec | 2021 | 0.00053125 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-12-10 12:33 | 2021-12-10 14:47 | 50 | 002:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR LLUVIA | A21121000032 | New_Event | Bad Weather | Include | Include | Weather | 134 | 2021-12-10 | 6700 | keep | 0 | Dec | 2021 | 0.0045633 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-12-10 12:37 | 2021-12-10 15:41 | 30 | 003:04 | P | DESGANCHE | 1 X 30 EN C/L | C21121000031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2021-12-10 | 5520 | keep | 0 | Dec | 2021 | 0.0037596 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-12-10 12:37 | 2021-12-10 15:23 | 91 | 002:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO CAJA AVERIADA NO FUNDIO | C21121000032 | New_Event | Cutout Failure | Include | Include | Equipment | 166 | 2021-12-10 | 15106 | keep | 0 | Dec | 2021 | 0.010289 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
MAYAGÃœEZ | 2021-12-10 12:48 | 2021-12-10 21:48 | 15 | 009:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21121000088 | New_Event | Bad Weather | Include | Include | Weather | 540 | 2021-12-10 | 8100 | keep | 0 | Dec | 2021 | 0.0055169 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-12-10 12:50 | 2021-12-10 15:27 | 80 | 002:37 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | R21121000030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 157 | 2021-12-10 | 12560 | keep | 0 | Dec | 2021 | 0.0085546 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2021-12-10 13:07 | 2021-12-10 15:30 | 75 | 002:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO Y SE REMPLAZO CAJA PRIMARIA QUEMADA | M21121000055 | New_Event | Wire Down | Include | Include | Equipment | 143 | 2021-12-10 | 10725 | keep | 0 | Dec | 2021 | 0.0073047 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2021-12-10 13:21 | 2021-12-10 13:22 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21121000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-10 | 3041 | keep | 0 | Dec | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
BAYAMON | 2021-12-10 13:24 | 2021-12-10 13:25 | 1533 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21121000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-10 | 1533 | keep | 0 | Dec | 2021 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
MAYAGÃœEZ | 2021-12-10 13:24 | 2021-12-10 20:48 | 40 | 007:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21121000096 | New_Event | Bad Weather | Include | Include | Weather | 444 | 2021-12-10 | 17760 | keep | 0 | Dec | 2021 | 0.012096 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-10 13:24 | 2021-12-10 13:31 | 3070 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21121000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-12-10 | 21490 | keep | 0 | Dec | 2021 | 0.014637 | 0.002091 | Sustained | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2021-12-10 13:24 | 2021-12-10 13:31 | 2735 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21121000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-12-10 | 19145 | keep | 0 | Dec | 2021 | 0.01304 | 0.0018628 | Sustained | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2021-12-10 13:24 | 2021-12-10 13:31 | 1070 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21121000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-12-10 | 7490 | keep | 0 | Dec | 2021 | 0.0051014 | 0.00072877 | Sustained | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2021-12-10 13:24 | 2021-12-10 13:31 | 1647 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21121000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-12-10 | 11529 | keep | 0 | Dec | 2021 | 0.0078523 | 0.0011218 | Sustained | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2021-12-10 13:24 | 2021-12-10 13:31 | 3295 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21121000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-12-10 | 23065 | keep | 0 | Dec | 2021 | 0.015709 | 0.0022442 | Sustained | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2021-12-10 13:24 | 2021-12-10 13:31 | 1180 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21121000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-12-10 | 8260 | keep | 0 | Dec | 2021 | 0.0056258 | 0.00080369 | Sustained | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2021-12-10 13:24 | 2021-12-10 13:31 | 320 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21121000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-12-10 | 2240 | keep | 0 | Dec | 2021 | 0.0015257 | 0.00021795 | Sustained | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2021-12-10 13:24 | 2021-12-10 13:31 | 2234 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | B21121000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-12-10 | 15638 | keep | 0 | Dec | 2021 | 0.010651 | 0.0015216 | Sustained | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2021-12-10 13:25 | 2021-12-10 17:15 | 1 | 003:50 | P | NO SE REPORTO CAUSA | 2 X 40 1 X 80 EN CORTE DE LINEA | S21121000058 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 230 | 2021-12-10 | 230 | keep | 0 | Dec | 2021 | 0.00015665 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-12-10 13:25 | 2021-12-10 13:26 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21121000000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-10 | 3041 | keep | 0 | Dec | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
CANOVANAS | 2021-12-10 13:27 | 2021-12-10 16:47 | 80 | 003:20 | P | DESGANCHE | 1 X 50 Y 1 X 65 EN CORTES DE LINEAS | R21121000031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2021-12-10 | 16000 | keep | 0 | Dec | 2021 | 0.010898 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2021-12-10 13:28 | 2021-12-10 18:52 | 20 | 005:24 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHO Y REEMPLAZO DISCO | C21121000036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 324 | 2021-12-10 | 6480 | keep | 0 | Dec | 2021 | 0.0044135 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-12-10 13:32 | 2021-12-10 15:33 | 40 | 002:01 | P | DESGANCHE | 1 X 50 EN C/L | C21121000037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2021-12-10 | 4840 | keep | 0 | Dec | 2021 | 0.0032965 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-12-10 13:32 | 2021-12-10 17:11 | 4664 | 003:39 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE RETIRO BAMBUAS SOBRE TRONCAL DEL ALIMENTADOR | M21121000103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2021-12-10 | 1021416 | keep | 0 | Dec | 2021 | 0.69568 | 0.0031766 | Sustained | FALSE | FALSE | Not_TMED_Event | 4664
SAN JUAN | 2021-12-10 13:35 | 2021-12-10 14:24 | 1 | 000:49 | P | OTRAS CAUSAS | SE LE REALIZO BYPASS A EQUIPOS DE MEDICION SE REPUSO FUSIBLES | S21121000055 | New_Event | Other Causes | Include | Include | Other | 49 | 2021-12-10 | 49 | keep | 0 | Dec | 2021 | 3.3374e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-10 13:38 | 2021-12-10 14:45 | 30 | 001:07 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21121000069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 67 | 2021-12-10 | 2010 | keep | 0 | Dec | 2021 | 0.001369 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2021-12-10 13:50 | 2021-12-10 13:51 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | M21111200109 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-10 | 3041 | keep | 0 | Dec | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
HUMACAO | 2021-12-10 13:53 | 2021-12-10 14:37 | 6 | 000:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR NEUTRAL SECUNDARIO | C21121000041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 44 | 2021-12-10 | 264 | keep | 0 | Dec | 2021 | 0.00017981 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-12-10 13:55 | 2021-12-10 13:56 | 2073 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13500 | M21121000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-10 | 2073 | keep | 0 | Dec | 2021 | 0.0014119 | 0.0014119 | Momentary | FALSE | FALSE | Not_TMED_Event | 2073
MAYAGÃœEZ | 2021-12-10 13:55 | 2021-12-10 13:56 | 637 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13500 | M21121000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-10 | 637 | keep | 0 | Dec | 2021 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
MAYAGÃœEZ | 2021-12-10 13:55 | 2021-12-10 13:56 | 1491 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13500 | M21121000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-10 | 1491 | keep | 0 | Dec | 2021 | 0.0010155 | 0.0010155 | Momentary | FALSE | FALSE | Not_TMED_Event | 1491
AGUADILLA | 2021-12-10 13:58 | 2021-12-10 16:23 | 100 | 002:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21121000112 | New_Event | Bad Weather | Include | Include | Weather | 145 | 2021-12-10 | 14500 | keep | 0 | Dec | 2021 | 0.0098759 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2021-12-10 14:04 | 2021-12-11 14:17 | 40 | 024:13 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | A21121000038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1453 | 2021-12-10 | 58120 | keep | 0 | Dec | 2021 | 0.039585 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-10 14:19 | 2021-12-10 17:52 | 75 | 003:33 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21121000075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 213 | 2021-12-10 | 15975 | keep | 0 | Dec | 2021 | 0.01088 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2021-12-10 14:20 | 2021-12-11 14:03 | 15 | 023:43 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S21121000059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1423 | 2021-12-10 | 21345 | keep | 0 | Dec | 2021 | 0.014538 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-12-10 14:28 | 2021-12-10 18:56 | 40 | 004:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21121000129 | New_Event | Bad Weather | Include | Include | Weather | 268 | 2021-12-10 | 10720 | keep | 0 | Dec | 2021 | 0.0073013 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2021-12-10 14:29 | 2021-12-10 17:44 | 400 | 003:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA POR VEHICULO IMPACTAR POSTE | P21121000025 | New_Event |  |  | Include | Wildlife | 195 | 2021-12-10 | 78000 | keep | 0 | Dec | 2021 | 0.053125 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
HUMACAO | 2021-12-10 14:30 | 2021-12-10 14:33 | 551 | 000:03 | T | DESGANCHE | DISPARO SE VERIFICO PERSONAL FUERA | C21121000046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-12-10 | 1653 | keep | 0 | Dec | 2021 | 0.0011259 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
HUMACAO | 2021-12-10 14:33 | 2021-12-10 18:04 | 10 | 003:31 | P | DESGANCHE | 1 X 100 EN C/L | C21121000048 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 211 | 2021-12-10 | 2110 | keep | 0 | Dec | 2021 | 0.0014371 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-12-10 14:34 | 2021-12-10 16:53 | 9 | 002:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REEMPLAZO SECUNDARIA | A21121000042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 139 | 2021-12-10 | 1251 | keep | 0 | Dec | 2021 | 0.00085205 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
HUMACAO | 2021-12-10 14:35 | 2021-12-10 17:40 | 85 | 003:05 | P | DESGANCHE | 2 X 50 EN C/L | C21121000047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2021-12-10 | 15725 | keep | 0 | Dec | 2021 | 0.01071 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
BAYAMON | 2021-12-10 14:36 | 2021-12-10 14:53 | 15 | 000:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA | S21121000053 | New_Event | Secondary Wire Down | Include | Include | Equipment | 17 | 2021-12-10 | 255 | keep | 0 | Dec | 2021 | 0.00017368 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-12-10 14:45 | 2021-12-10 16:50 | 50 | 002:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA QUEMADA | A21121000043 | New_Event | Cutout Failure | Include | Include | Equipment | 125 | 2021-12-10 | 6250 | keep | 0 | Dec | 2021 | 0.0042568 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-10 14:45 | 2021-12-10 14:46 | 3511 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21121000000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-10 | 3511 | keep | 0 | Dec | 2021 | 0.0023913 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-10 14:46 | 2021-12-10 16:35 | 30 | 001:49 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21121000069 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 109 | 2021-12-10 | 3270 | keep | 0 | Dec | 2021 | 0.0022272 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-12-10 14:48 | 2021-12-10 16:38 | 50 | 001:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN C/L MAL TIEMPO | C21121000049 | New_Event | Bad Weather | Include | Include | Weather | 110 | 2021-12-10 | 5500 | keep | 0 | Dec | 2021 | 0.003746 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-12-10 14:59 | 2021-12-10 17:04 | 65 | 002:05 | P | DESGANCHE | 1 X 100 EN C/L | C21121000053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2021-12-10 | 8125 | keep | 0 | Dec | 2021 | 0.0055339 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
YAUCO | 2021-12-10 15:01 | 2021-12-10 16:48 | 60 | 001:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR POR CONTACTO DE AVE | P21121000029 | New_Event |  |  | Include | Wildlife | 107 | 2021-12-10 | 6420 | keep | 0 | Dec | 2021 | 0.0043726 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-12-10 15:06 | 2021-12-10 18:36 | 20 | 003:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21121000139 | New_Event | Bad Weather | Include | Include | Weather | 210 | 2021-12-10 | 4200 | keep | 0 | Dec | 2021 | 0.0028606 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-12-10 15:07 | 2021-12-10 16:30 | 5 | 001:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR REEMPLAZO PORTAFUSIBLE | R21121000038 | New_Event | Cutout Failure | Include | Include | Equipment | 83 | 2021-12-10 | 415 | keep | 0 | Dec | 2021 | 0.00028265 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2021-12-10 15:07 | 2021-12-10 15:57 | 1945 | 000:50 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR PUENTE ABIERTO Y CAYO SOBRE FASE PRIMARIA | P21121000030 | New_Event | Wire Down | Include | Include | Equipment | 50 | 2021-12-10 | 97250 | keep | 0 | Dec | 2021 | 0.066237 | 0.0013247 | Sustained | FALSE | FALSE | Not_TMED_Event | 1945
BAYAMON | 2021-12-10 15:10 | 2021-12-10 18:13 | 40 | 003:03 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21121000086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 183 | 2021-12-10 | 7320 | keep | 0 | Dec | 2021 | 0.0049856 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-10 15:10 | 2021-12-10 18:13 | 30 | 003:03 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21121000086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2021-12-10 | 5490 | keep | 0 | Dec | 2021 | 0.0037392 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2021-12-10 15:30 | 2021-12-10 15:49 | 10 | 000:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA ABIERTA | M21121000145 | New_Event | Secondary Wire Down | Include | Include | Equipment | 19 | 2021-12-10 | 190 | keep | 0 | Dec | 2021 | 0.00012941 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-12-10 15:30 | 2021-12-11 02:20 | 39 | 010:50 | T | DESGANCHE | SE PATRULLO SE CONFIRMO INTERRUPTOR ABIERTO Y SE CERRO EL INTERRUPTOR EN LA SUBESTACION YA QUE EL RTU ESTA FUERA DE SERVICIO ALIMENTADOR REQUIERE DESGANCHE | M21121000146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 650 | 2021-12-10 | 25350 | keep | 0 | Dec | 2021 | 0.017266 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
HUMACAO | 2021-12-10 15:35 | 2021-12-10 17:12 | 40 | 001:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE X AVE | C21121000057 | New_Event |  |  | Include | Wildlife | 97 | 2021-12-10 | 3880 | keep | 0 | Dec | 2021 | 0.0026427 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-12-10 15:54 | 2021-12-10 22:26 | 20 | 006:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA FUERTE VIENTO | M21121000159 | New_Event | Bad Weather | Include | Include | Weather | 392 | 2021-12-10 | 7840 | keep | 0 | Dec | 2021 | 0.0053398 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2021-12-10 15:54 | 2021-12-10 15:55 | 1036 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR POR DESCARGAS ELECTRICAS | M21121000000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-12-10 | 1036 | keep | 0 | Dec | 2021 | 0.00070561 | 0.00070561 | Momentary | FALSE | FALSE | Not_TMED_Event | 1036
GUAYAMA | 2021-12-10 15:57 | 2021-12-10 17:27 | 972 | 001:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO Y SE CERRO MACHETE | P21121000032 | Partial_restoration | Wire Down | Include | Include | Equipment | 90 | 2021-12-10 | 87480 | keep | 0 | Dec | 2021 | 0.059582 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-12-10 15:58 | 2021-12-10 18:37 | 65 | 002:39 | P | DESGANCHE | 2 X 40 EN C/L | C21121000060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2021-12-10 | 10335 | keep | 0 | Dec | 2021 | 0.0070391 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2021-12-10 16:00 | 2021-12-10 18:21 | 30 | 002:21 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21121000067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2021-12-10 | 4230 | keep | 0 | Dec | 2021 | 0.002881 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2021-12-10 16:00 | 2021-12-10 18:29 | 50 | 002:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE CAMBIO PORTA FUSIBLE QUEMADO | P21121000039 | New_Event | Cutout Failure | Include | Include | Equipment | 149 | 2021-12-10 | 7450 | keep | 0 | Dec | 2021 | 0.0050742 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-12-10 16:21 | 2021-12-10 20:51 | 10 | 004:30 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21121000069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 270 | 2021-12-10 | 2700 | keep | 0 | Dec | 2021 | 0.001839 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-12-10 16:57 | 2021-12-10 18:17 | 15 | 001:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21121000094 | New_Event | Secondary Wire Down | Include | Include | Equipment | 80 | 2021-12-10 | 1200 | keep | 0 | Dec | 2021 | 0.00081731 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-12-10 16:59 | 2021-12-10 17:21 | 3230 | 000:22 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE SECCIONALIZO LINEA PRIMARIA ROTA Y SE CERRO EL INTERRUPTOR | M21121000175 | New_Event | Wire Down | Include | Include | Equipment | 22 | 2021-12-10 | 71060 | keep | 0 | Dec | 2021 | 0.048399 | 0.0021999 | Sustained | FALSE | FALSE | Not_TMED_Event | 3230
AGUADILLA | 2021-12-10 17:01 | 2021-12-10 21:00 | 180 | 003:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21121000177 | New_Event | Bad Weather | Include | Include | Weather | 239 | 2021-12-10 | 43020 | keep | 0 | Dec | 2021 | 0.029301 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
ARECIBO | 2021-12-10 17:11 | 2021-12-10 22:15 | 60 | 005:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 40 Y 1 X 100 EN CORTES DE LINEA SE REMPLAZO DOS CAJAS AVERIADA MARCA CHINT DE 100AMP EN EL FID16435141 | A21121000052 | New_Event | Cutout Failure | Include | Include | Equipment | 304 | 2021-12-10 | 18240 | keep | 0 | Dec | 2021 | 0.012423 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-12-10 17:12 | 2021-12-10 20:59 | 200 | 003:47 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | B21121000095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 227 | 2021-12-10 | 45400 | keep | 0 | Dec | 2021 | 0.030922 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2021-12-10 17:14 | 2021-12-10 18:32 | 50 | 001:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA POR CAJA PRIMARIA QUEMADA | P21121000048 | New_Event | Cutout Failure | Include | Include | Equipment | 78 | 2021-12-10 | 3900 | keep | 0 | Dec | 2021 | 0.0026563 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-12-10 17:21 | 2021-12-10 19:31 | 300 | 002:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA Y SE CERRO CORTE DE LINEA | M21121000175 | Partial_restoration | Wire Down | Include | Include | Equipment | 130 | 2021-12-10 | 39000 | keep | 0 | Dec | 2021 | 0.026563 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-12-10 17:45 | 2021-12-10 19:10 | 100 | 001:25 | P | DESGANCHE | 2 X 65 EN C/L | C21121000067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2021-12-10 | 8500 | keep | 0 | Dec | 2021 | 0.0057893 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2021-12-10 17:52 | 2021-12-10 22:04 | 50 | 004:12 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B21121000096 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 252 | 2021-12-10 | 12600 | keep | 0 | Dec | 2021 | 0.0085818 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-12-10 17:57 | 2021-12-10 19:04 | 80 | 001:07 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR RAMA SOBRE LINEA PRIMARIA | M21121000182 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2021-12-10 | 5360 | keep | 0 | Dec | 2021 | 0.0036507 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2021-12-10 18:06 | 2021-12-10 20:12 | 80 | 002:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | A21121000054 | New_Event | Cutout Failure | Include | Include | Equipment | 126 | 2021-12-10 | 10080 | keep | 0 | Dec | 2021 | 0.0068654 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-12-10 19:01 | 2021-12-10 20:34 | 12 | 001:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA SECCIONALIZAR TOMA AVERIADA | S21121000073 | New_Event | Secondary Wire Down | Include | Include | Equipment | 93 | 2021-12-10 | 1116 | keep | 0 | Dec | 2021 | 0.0007601 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-12-10 19:02 | 2021-12-11 09:54 | 6 | 014:52 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M21121000193 | New_Event | Vegetation Contact | Include | Include | Vegetation | 892 | 2021-12-10 | 5352 | keep | 0 | Dec | 2021 | 0.0036452 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-12-10 19:40 | 2021-12-10 19:41 | 551 | 000:01 | T | DESGANCHE | RECIERRE | C21121000081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-10 | 551 | keep | 0 | Dec | 2021 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
HUMACAO | 2021-12-10 19:41 | 2021-12-11 15:02 | 30 | 019:21 | P | DESGANCHE | 1 X 100 EN C/L | C21121000082 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1161 | 2021-12-10 | 34830 | keep | 0 | Dec | 2021 | 0.023723 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-12-10 20:01 | 2021-12-10 20:07 | 3025 | 000:06 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO BKR PARA CERRAR EL N/O CONTRA EL 2604-03 POR CONECTOR QUEMADO EN EL RISER DE SALIDA DEL 2604-03 | C21121000071 | New_Event | Switch Failure | Include | Include | Equipment | 6 | 2021-12-10 | 18150 | keep | 0 | Dec | 2021 | 0.012362 | 0.0020603 | Sustained | FALSE | FALSE | Not_TMED_Event | 3025
HUMACAO | 2021-12-10 20:01 | 2021-12-10 20:07 | 1593 | 000:06 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO BKR PARA CERRAR EL N/O CONTRA EL 2604-02 POR CONECTOR QUEMADO EN EL RISER DE SALIDA DEL 2604-03 | C21121000071 | New_Event | Switch Failure | Include | Include | Equipment | 6 | 2021-12-10 | 9558 | keep | 0 | Dec | 2021 | 0.0065099 | 0.001085 | Sustained | FALSE | FALSE | Not_TMED_Event | 1593
ARECIBO | 2021-12-10 20:07 | 2021-12-11 08:49 | 100 | 012:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ABIERTO SE ABRIO CORTE DE LINEA PARA REPARAR | A21121000060 | New_Event | Wire Down | Include | Include | Equipment | 762 | 2021-12-10 | 76200 | keep | 0 | Dec | 2021 | 0.051899 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-12-10 21:14 | 2021-12-10 21:15 | 723 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA LA CARGA DEL 1711-05 | B21121000101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-10 | 723 | keep | 0 | Dec | 2021 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2021-12-10 21:14 | 2021-12-10 21:15 | 1976 | 000:01 | T | NO SE REPORTO CAUSA | CARGA TRANSFERIDA AL 1711-02 INTERRUPTOR DISPARO Y SE CERRO POR CONTROL | B21121000101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-10 | 1976 | keep | 0 | Dec | 2021 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2021-12-10 21:14 | 2021-12-10 21:19 | 1812 | 000:05 | T | NO SE REPORTO CAUSA | INTERRUPTOR DISPARO Y SE CERRO POR CONTROL | B21121000102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-12-10 | 9060 | keep | 0 | Dec | 2021 | 0.0061707 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
VEGA BAJA | 2021-12-10 21:16 | 2021-12-11 08:54 | 80 | 011:38 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B21121100003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 698 | 2021-12-10 | 55840 | keep | 0 | Dec | 2021 | 0.038032 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2021-12-10 21:33 | 2021-12-11 14:03 | 5 | 016:30 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | C21121000086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 990 | 2021-12-10 | 4950 | keep | 0 | Dec | 2021 | 0.0033714 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-12-10 21:43 | 2021-12-10 23:14 | 60 | 001:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA | B21121000107 | New_Event | Cutout Failure | Include | Include | Equipment | 91 | 2021-12-10 | 5460 | keep | 0 | Dec | 2021 | 0.0037188 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-12-10 21:46 | 2021-12-11 12:11 | 36 | 014:25 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S21121000076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 865 | 2021-12-10 | 31140 | keep | 0 | Dec | 2021 | 0.021209 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-12-10 22:03 | 2021-12-11 21:13 | 24 | 023:10 | P | CABLE SOTERRADO AVERIADO | 1 X 65 EN CORTE DE LINEA Y SE REPORTA AVERIA SOTERRADA NUEVA DEL T-58 AL T-57 | S21121000080 | New_Event | UG Cable Fault | Include | Include | Equipment | 1390 | 2021-12-10 | 33360 | keep | 0 | Dec | 2021 | 0.022721 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
HUMACAO | 2021-12-10 22:07 | 2021-12-11 14:15 | 65 | 016:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L CRUCE X AVE | C21121000087 | New_Event |  |  | Include | Wildlife | 968 | 2021-12-10 | 62920 | keep | 0 | Dec | 2021 | 0.042855 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2021-12-10 22:10 | 2021-12-11 09:54 | 1 | 011:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN C/L TERMINACION QUEMADA | C21121000088 | New_Event | Wire Down | Include | Include | Equipment | 704 | 2021-12-10 | 704 | keep | 0 | Dec | 2021 | 0.00047949 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-10 22:14 | 2021-12-10 22:15 | 3295 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21121000110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-10 | 3295 | keep | 0 | Dec | 2021 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
SAN JUAN | 2021-12-10 22:35 | 2021-12-11 09:27 | 65 | 010:52 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L NO CAUSA | R21121000046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 652 | 2021-12-10 | 42380 | keep | 0 | Dec | 2021 | 0.028865 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2021-12-10 23:06 | 2021-12-10 23:07 | 2900 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C21121000089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-10 | 2900 | keep | 0 | Dec | 2021 | 0.0019752 | 0.0019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 2900
BARRANQUITAS | 2021-12-10 23:08 | 2021-12-10 23:09 | 3296 | 000:01 | T | DESGANCHE | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C21121000090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-10 | 3296 | keep | 0 | Dec | 2021 | 0.0022449 | 0.0022449 | Momentary | FALSE | FALSE | Not_TMED_Event | 3296
BARRANQUITAS | 2021-12-10 23:09 | 2021-12-10 23:39 | 175 | 000:30 | P | DESGANCHE | 2 X 100 EN C/L | C21121000091 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 30 | 2021-12-10 | 5250 | keep | 0 | Dec | 2021 | 0.0035758 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
BARRANQUITAS | 2021-12-10 23:39 | 2021-12-10 23:40 | 3296 | 000:01 | T | DESGANCHE | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C21121000092 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-10 | 3296 | keep | 0 | Dec | 2021 | 0.0022449 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-12-10 23:40 | 2021-12-11 13:45 | 175 | 014:05 | P | DESGANCHE | 2 X 100 EN C/L | C21121000091 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 845 | 2021-12-10 | 147875 | keep | 0 | Dec | 2021 | 0.10072 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
HUMACAO | 2021-12-11 00:21 | 2021-12-11 09:33 | 85 | 009:12 | P | DESGANCHE | 2 X 40 EN C/L | C21121100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 552 | 2021-12-11 | 46920 | keep | 0 | Dec | 2021 | 0.031957 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
BAYAMON | 2021-12-11 01:00 | 2021-12-11 17:27 | 60 | 016:27 | P | DESGANCHE | 1 X 80 EN C/L, SE REALIZO DESGANCHE Y SE CERRO PUENTE DE LINEA A CAJA DE CORTE DE LINEA | S21121100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 987 | 2021-12-11 | 59220 | keep | 0 | Dec | 2021 | 0.040334 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-12-11 01:50 | 2021-12-11 14:52 | 40 | 013:02 | P | DESGANCHE | 1 X 65 EN C/L Y SE REALIZO DESGANCHE | B21121100004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 782 | 2021-12-11 | 31280 | keep | 0 | Dec | 2021 | 0.021305 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2021-12-11 02:20 | 2021-12-11 11:04 | 2 | 008:44 | P | DESGANCHE | SE CERRO MACHETES SE HABIA RETIRADO BAMBUS SOBRE LAS LINEAS | M21121000168 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 524 | 2021-12-11 | 1048 | keep | 0 | Dec | 2021 | 0.00071379 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-12-11 02:25 | 2021-12-11 08:54 | 150 | 006:29 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE EVENTO DIFERENTE MISMA CARRETERA | M21121100006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 389 | 2021-12-11 | 58350 | keep | 0 | Dec | 2021 | 0.039742 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-12-11 02:25 | 2021-12-11 10:56 | 200 | 008:31 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE EVENTOS DIFERENTE MISMA CARRETERA | M21121100041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 511 | 2021-12-11 | 102200 | keep | 0 | Dec | 2021 | 0.069608 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2021-12-11 02:49 | 2021-12-11 05:55 | 7 | 003:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REEMPLAZAR SECUNDARIA | R21121100001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 186 | 2021-12-11 | 1302 | keep | 0 | Dec | 2021 | 0.00088679 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-12-11 03:15 | 2021-12-11 03:16 | 1287 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21121100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 1287 | keep | 0 | Dec | 2021 | 0.00087657 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
MAYAGÃœEZ | 2021-12-11 03:20 | 2021-12-11 03:21 | 1287 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21121100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 1287 | keep | 0 | Dec | 2021 | 0.00087657 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
MAYAGÃœEZ | 2021-12-11 04:26 | 2021-12-11 04:27 | 1287 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21121100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 1287 | keep | 0 | Dec | 2021 | 0.00087657 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
MAYAGÃœEZ | 2021-12-11 04:41 | 2021-12-11 04:42 | 1287 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21121100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 1287 | keep | 0 | Dec | 2021 | 0.00087657 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
MAYAGÃœEZ | 2021-12-11 05:06 | 2021-12-11 05:07 | 1287 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21121100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 1287 | keep | 0 | Dec | 2021 | 0.00087657 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
MAYAGÃœEZ | 2021-12-11 05:10 | 2021-12-11 05:11 | 1287 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21121100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 1287 | keep | 0 | Dec | 2021 | 0.00087657 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
MAYAGÃœEZ | 2021-12-11 05:16 | 2021-12-11 05:17 | 1287 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21121100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 1287 | keep | 0 | Dec | 2021 | 0.00087657 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
MAYAGÃœEZ | 2021-12-11 05:25 | 2021-12-11 05:26 | 1287 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21121100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 1287 | keep | 0 | Dec | 2021 | 0.00087657 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
MAYAGÃœEZ | 2021-12-11 05:27 | 2021-12-11 05:28 | 1287 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21121100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 1287 | keep | 0 | Dec | 2021 | 0.00087657 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
MAYAGÃœEZ | 2021-12-11 05:38 | 2021-12-11 05:39 | 1287 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21121100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 1287 | keep | 0 | Dec | 2021 | 0.00087657 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
MAYAGÃœEZ | 2021-12-11 05:42 | 2021-12-11 10:55 | 1287 | 005:13 | T | NO SE REPORTO CAUSA | SE PATRULLO EL ALIMENTADOR Y NO SE ENCONTRÃ“ CAUSA | M21121100016 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 313 | 2021-12-11 | 402831 | keep | 0 | Dec | 2021 | 0.27437 | 0.00087657 | Sustained | FALSE | FALSE | Not_TMED_Event | 1287
VEGA BAJA | 2021-12-11 06:15 | 2021-12-11 06:16 | 2926 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21121100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 2926 | keep | 0 | Dec | 2021 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
SAN JUAN | 2021-12-11 06:24 | 2021-12-11 08:19 | 2000 | 001:55 | P | NO SE REPORTO CAUSA | DISPARO DEL 1619-02, SE ENCONTRO EL BKR ABIERTO EN LA SUBESTACION | R21121100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2021-12-11 | 230000 | keep | 0 | Dec | 2021 | 0.15665 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
CAGUAS | 2021-12-11 06:25 | 2021-12-11 10:15 | 10 | 003:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE POR REPTIL | C21121100006 | New_Event |  |  | Include | Wildlife | 230 | 2021-12-11 | 2300 | keep | 0 | Dec | 2021 | 0.0015665 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-11 06:49 | 2021-12-11 12:30 | 150 | 005:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR | S21121100008 | New_Event | Wire Down | Include | Include | Equipment | 341 | 2021-12-11 | 51150 | keep | 0 | Dec | 2021 | 0.034838 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2021-12-11 06:50 | 2021-12-11 11:31 | 20 | 004:41 | P | DESGANCHE | 1 X 25 EN CL | C21121100008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 281 | 2021-12-11 | 5620 | keep | 0 | Dec | 2021 | 0.0038278 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2021-12-11 07:03 | 2021-12-11 10:20 | 12 | 003:17 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA FUERTE BRISA | P21121100006 | New_Event | Bad Weather | Include | Include | Weather | 197 | 2021-12-11 | 2364 | keep | 0 | Dec | 2021 | 0.0016101 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-12-11 07:16 | 2021-12-11 10:51 | 40 | 003:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE POR AVE | C21121100009 | New_Event |  |  | Include | Wildlife | 215 | 2021-12-11 | 8600 | keep | 0 | Dec | 2021 | 0.0058574 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2021-12-11 07:19 | 2021-12-11 16:05 | 4 | 008:46 | P | ESTRUCTURA AVERIADA | SE RETIRO CARGA A XMR PARA ABRIR PUENTE Y REEMPLAZAR POSTE ROTO | R21121100020 | New_Event | Defective Pole | Include | Include | Equipment | 526 | 2021-12-11 | 2104 | keep | 0 | Dec | 2021 | 0.001433 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-12-11 07:59 | 2021-12-11 10:55 | 30 | 002:56 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21121100010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 176 | 2021-12-11 | 5280 | keep | 0 | Dec | 2021 | 0.0035962 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-11 08:00 | 2021-12-11 08:01 | 1983 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1801-02 Y SE CERRO POR SCADA LLEVA 1711-04 | B21121100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 1983 | keep | 0 | Dec | 2021 | 0.0013506 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-12-11 08:00 | 2021-12-11 08:01 | 300 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1801-02 Y SE CERRO POR SCADA LLEVA PARTE DEL 1717-01 | B21121100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 300 | keep | 0 | Dec | 2021 | 0.00020433 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2021-12-11 08:00 | 2021-12-11 08:01 | 186 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1801-02 Y SE CERRO POR SCADA LLEVA 1711-04 Y PARTE DEL 1717-01 | B21121100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 186 | keep | 0 | Dec | 2021 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2021-12-11 08:02 | 2021-12-11 08:03 | 199 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S21121100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 199 | keep | 0 | Dec | 2021 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2021-12-11 08:49 | 2021-12-11 08:50 | 1222 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21121100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-11 | 1222 | keep | 0 | Dec | 2021 | 0.0008323 | 0.0008323 | Momentary | FALSE | FALSE | Not_TMED_Event | 1222
ARECIBO | 2021-12-11 08:49 | 2021-12-11 08:50 | 2756 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21121100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-11 | 2756 | keep | 0 | Dec | 2021 | 0.0018771 | 0.0018771 | Momentary | FALSE | FALSE | Not_TMED_Event | 2756
ARECIBO | 2021-12-11 08:49 | 2021-12-11 08:50 | 2833 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21121100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-11 | 2833 | keep | 0 | Dec | 2021 | 0.0019295 | 0.0019295 | Momentary | FALSE | FALSE | Not_TMED_Event | 2833
ARECIBO | 2021-12-11 08:49 | 2021-12-11 08:50 | 1218 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21121100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-11 | 1218 | keep | 0 | Dec | 2021 | 0.00082957 | 0.00082957 | Momentary | FALSE | FALSE | Not_TMED_Event | 1218
ARECIBO | 2021-12-11 08:49 | 2021-12-11 08:50 | 1345 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21121100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-11 | 1345 | keep | 0 | Dec | 2021 | 0.00091607 | 0.00091607 | Momentary | FALSE | FALSE | Not_TMED_Event | 1345
ARECIBO | 2021-12-11 08:49 | 2021-12-11 08:50 | 1265 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21121100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-11 | 1265 | keep | 0 | Dec | 2021 | 0.00086159 | 0.00086159 | Momentary | FALSE | FALSE | Not_TMED_Event | 1265
ARECIBO | 2021-12-11 08:49 | 2021-12-11 08:50 | 2071 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21121100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-11 | 2071 | keep | 0 | Dec | 2021 | 0.0014105 | 0.0014105 | Momentary | FALSE | FALSE | Not_TMED_Event | 2071
ARECIBO | 2021-12-11 08:49 | 2021-12-11 08:50 | 760 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21121100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-11 | 760 | keep | 0 | Dec | 2021 | 0.00051763 | 0.00051763 | Momentary | FALSE | FALSE | Not_TMED_Event | 760
ARECIBO | 2021-12-11 08:49 | 2021-12-11 08:50 | 509 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21121100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-11 | 509 | keep | 0 | Dec | 2021 | 0.00034668 | 0.00034668 | Momentary | FALSE | FALSE | Not_TMED_Event | 509
ARECIBO | 2021-12-11 08:49 | 2021-12-11 08:50 | 2620 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21121100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-11 | 2620 | keep | 0 | Dec | 2021 | 0.0017845 | 0.0017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 2620
ARECIBO | 2021-12-11 08:49 | 2021-12-11 08:50 | 1916 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21121100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-11 | 1916 | keep | 0 | Dec | 2021 | 0.001305 | 0.001305 | Momentary | FALSE | FALSE | Not_TMED_Event | 1916
ARECIBO | 2021-12-11 08:50 | 2021-12-11 09:40 | 100 | 000:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ABIERTO SE ABRIO CORTE DE LINEA PARA REPARAR | A21121000060 | Partial_restoration | Wire Down | Include | Include | Equipment | 50 | 2021-12-11 | 5000 | keep | 0 | Dec | 2021 | 0.0034055 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-12-11 09:10 | 2021-12-11 09:11 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21121100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 1702 | keep | 0 | Dec | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
VEGA BAJA | 2021-12-11 09:11 | 2021-12-11 16:47 | 10 | 007:36 | P | PARARRAYOS DEFECTUOSO | 1 X 15 EN XMR Y SE REEMPLAZO PARARRAYO | B21121100019 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 456 | 2021-12-11 | 4560 | keep | 0 | Dec | 2021 | 0.0031058 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-12-11 09:19 | 2021-12-11 11:42 | 60 | 002:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L CRUCE X AVE | C21121100019 | New_Event |  |  | Include | Wildlife | 143 | 2021-12-11 | 8580 | keep | 0 | Dec | 2021 | 0.0058438 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-12-11 09:21 | 2021-12-11 11:42 | 6 | 002:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIO | B21121100020 | New_Event | Secondary Wire Down | Include | Include | Equipment | 141 | 2021-12-11 | 846 | keep | 0 | Dec | 2021 | 0.00057621 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-12-11 09:29 | 2021-12-11 12:10 | 15 | 002:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21121100025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 161 | 2021-12-11 | 2415 | keep | 0 | Dec | 2021 | 0.0016448 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-12-11 09:40 | 2021-12-11 12:04 | 150 | 002:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO SE CERRO CORTE DE LINEA | A21121000060 | Additional_clients | Wire Down | Include | Include | Equipment | 144 | 2021-12-11 | 21600 | keep | 0 | Dec | 2021 | 0.014712 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-12-11 09:50 | 2021-12-11 11:33 | 8 | 001:43 | P | NO SE REPORTO CAUSA | 1 X 15 EN PROVISIONAL | B21121100025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 103 | 2021-12-11 | 824 | keep | 0 | Dec | 2021 | 0.00056122 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-12-11 09:54 | 2021-12-11 18:09 | 200 | 008:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN C/L REPARO TERMINACION QUEMADA | C21121000088 | Additional_clients | Wire Down | Include | Include | Equipment | 495 | 2021-12-11 | 99000 | keep | 0 | Dec | 2021 | 0.067428 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-12-11 10:16 | 2021-12-11 10:17 | 863 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21121100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 863 | keep | 0 | Dec | 2021 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2021-12-11 10:17 | 2021-12-11 16:02 | 40 | 005:45 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M21121100054 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 345 | 2021-12-11 | 13800 | keep | 0 | Dec | 2021 | 0.0093991 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2021-12-11 10:20 | 2021-12-11 13:00 | 13 | 002:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 25 KVA POR 50 KVA MEJORA DE VOLTAJE | A21121100015 | New_Event | Service Transformer Failure | Include | Include | Equipment | 160 | 2021-12-11 | 2080 | keep | 0 | Dec | 2021 | 0.0014167 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BARRANQUITAS | 2021-12-11 10:25 | 2021-12-11 16:05 | 40 | 005:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE NO FUNDIO | C21121100025 | New_Event | Wire Down | Include | Include | Equipment | 340 | 2021-12-11 | 13600 | keep | 0 | Dec | 2021 | 0.0092629 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2021-12-11 10:41 | 2021-12-11 16:03 | 55 | 005:22 | P | DESGANCHE | 1 X 80 EN C/L | C21121100026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 322 | 2021-12-11 | 17710 | keep | 0 | Dec | 2021 | 0.012062 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CAGUAS | 2021-12-11 10:42 | 2021-12-11 16:13 | 46 | 005:31 | P | LINEA DE TRANSMISION 38KV | ABRIO C/L PARA LEVANTAR FASE DE LA LINEA 37800 | C21121100027 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 331 | 2021-12-11 | 15226 | keep | 0 | Dec | 2021 | 0.01037 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
YAUCO | 2021-12-11 10:43 | 2021-12-11 13:00 | 2 | 002:17 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA POR DESGANCHE | P21121100021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2021-12-11 | 274 | keep | 0 | Dec | 2021 | 0.00018662 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2021-12-11 10:53 | 2021-12-11 13:08 | 30 | 002:15 | P | DESGANCHE | 1 X 30 EN C/L | C21121100030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2021-12-11 | 4050 | keep | 0 | Dec | 2021 | 0.0027584 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-12-11 11:02 | 2021-12-11 12:01 | 4 | 000:59 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIO XMR PARA REEMPLAZAR PEDESTAL | R21121100028 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 59 | 2021-12-11 | 236 | keep | 0 | Dec | 2021 | 0.00016074 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-12-11 11:03 | 2021-12-11 20:46 | 100 | 009:43 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21121100045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 583 | 2021-12-11 | 58300 | keep | 0 | Dec | 2021 | 0.039708 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-12-11 11:14 | 2021-12-11 13:23 | 40 | 002:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA POR BOMBA DE HELIO CRUZO FASE A TIERRA | M21121100051 | New_Event |  |  | Include | Wildlife | 129 | 2021-12-11 | 5160 | keep | 0 | Dec | 2021 | 0.0035145 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2021-12-11 11:17 | 2021-12-11 16:41 | 100 | 005:24 | P | DESGANCHE | 2 X 40 EN C/L | C21121100031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 324 | 2021-12-11 | 32400 | keep | 0 | Dec | 2021 | 0.022067 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2021-12-11 11:19 | 2021-12-11 15:54 | 10 | 004:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | M21121100052 | New_Event | Secondary Wire Down | Include | Include | Equipment | 275 | 2021-12-11 | 2750 | keep | 0 | Dec | 2021 | 0.001873 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-11 11:27 | 2021-12-12 11:20 | 100 | 023:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21121100056 | New_Event | Bad Weather | Include | Include | Weather | 1433 | 2021-12-11 | 143300 | keep | 0 | Dec | 2021 | 0.097601 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-12-11 11:42 | 2021-12-11 11:43 | 3420 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21121100000 | New_Event |  |  | Include | Wildlife | 1 | 2021-12-11 | 3420 | keep | 0 | Dec | 2021 | 0.0023293 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
HUMACAO | 2021-12-11 11:43 | 2021-12-11 14:59 | 60 | 003:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L CRUCE X AVE | C21121100019 | 1st_after_momentary |  |  | Include | Wildlife | 196 | 2021-12-11 | 11760 | keep | 0 | Dec | 2021 | 0.0080097 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-12-11 11:47 | 2021-12-11 13:48 | 1834 | 002:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y SE LLEVO LINEA SOBRE CRUCETA A SU SITIO | B21121100036 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 121 | 2021-12-11 | 221914 | keep | 0 | Dec | 2021 | 0.15114 | 0.0012491 | Sustained | FALSE | FALSE | Not_TMED_Event | 1834
MAYAGÃœEZ | 2021-12-11 12:00 | 2021-12-11 23:03 | 40 | 011:03 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M21121100058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 663 | 2021-12-11 | 26520 | keep | 0 | Dec | 2021 | 0.018063 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-11 12:12 | 2021-12-11 16:17 | 50 | 004:05 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21121100040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 245 | 2021-12-11 | 12250 | keep | 0 | Dec | 2021 | 0.0083434 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-12-11 12:16 | 2021-12-11 18:37 | 2999 | 006:21 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA SAN GERMAN TC | M21121100062 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 381 | 2021-12-11 | 1142619 | keep | 0 | Dec | 2021 | 0.77823 | 0.0020426 | Sustained | FALSE | FALSE | Not_TMED_Event | 2999
MAYAGÃœEZ | 2021-12-11 12:16 | 2021-12-11 18:37 | 1597 | 006:21 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA SAN GERMAN TC | M21121100062 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 381 | 2021-12-11 | 608457 | keep | 0 | Dec | 2021 | 0.41442 | 0.0010877 | Sustained | FALSE | FALSE | Not_TMED_Event | 1597
BAYAMON | 2021-12-11 12:19 | 2021-12-11 14:52 | 40 | 002:33 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21121100041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 153 | 2021-12-11 | 6120 | keep | 0 | Dec | 2021 | 0.0041683 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2021-12-11 12:20 | 2021-12-11 18:50 | 13 | 006:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REEMPLAZAR SECUNDARIA | P21121100083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 390 | 2021-12-11 | 5070 | keep | 0 | Dec | 2021 | 0.0034532 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2021-12-11 12:22 | 2021-12-11 16:00 | 105 | 003:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50, 1 X 80 Y 1 X 100 EN DISTINTOS CORTE DE LINEA. ADEMAS SE REEMPLAZO CAJA QUEMADA | S21121100037 | New_Event | Cutout Failure | Include | Include | Equipment | 218 | 2021-12-11 | 22890 | keep | 0 | Dec | 2021 | 0.01559 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
AGUADILLA | 2021-12-11 12:22 | 2021-12-12 11:05 | 80 | 022:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M21121100064 | New_Event | Wire Down | Include | Include | Equipment | 1363 | 2021-12-11 | 109040 | keep | 0 | Dec | 2021 | 0.074267 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-12-11 12:32 | 2021-12-11 13:32 | 3230 | 001:00 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO LINEA PRIMARIA PARTIDA SE CERRO INTERRUPTOR | M21121100070 | New_Event | Wire Down | Include | Include | Equipment | 60 | 2021-12-11 | 193800 | keep | 0 | Dec | 2021 | 0.132 | 0.0021999 | Sustained | FALSE | FALSE | Not_TMED_Event | 3230
AGUADILLA | 2021-12-11 12:37 | 2021-12-11 22:46 | 80 | 010:09 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 30 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M21121100073 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 609 | 2021-12-11 | 48720 | keep | 0 | Dec | 2021 | 0.033183 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-12-11 12:45 | 2021-12-12 10:59 | 1 | 022:14 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | B21121100044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1334 | 2021-12-11 | 1334 | keep | 0 | Dec | 2021 | 0.00090858 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-12-11 12:51 | 2021-12-11 12:52 | 1105 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | A21121100037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 1105 | keep | 0 | Dec | 2021 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
SAN JUAN | 2021-12-11 12:56 | 2021-12-11 17:23 | 20 | 004:27 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | R21121100029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 267 | 2021-12-11 | 5340 | keep | 0 | Dec | 2021 | 0.003637 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-12-11 12:57 | 2021-12-12 13:41 | 15 | 024:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21121100084 | New_Event | Bad Weather | Include | Include | Weather | 1484 | 2021-12-11 | 22260 | keep | 0 | Dec | 2021 | 0.015161 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-12-11 12:58 | 2021-12-11 13:01 | 436 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO, PARTE DE LA CARGA POR EL 3015-07 | C21121100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-12-11 | 1308 | keep | 0 | Dec | 2021 | 0.00089087 | 0.00029696 | Momentary | FALSE | FALSE | Not_TMED_Event | 436
UTUADO | 2021-12-11 13:00 | 2021-12-11 15:53 | 80 | 002:53 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21121100039 | New_Event | Bad Weather | Include | Include | Weather | 173 | 2021-12-11 | 13840 | keep | 0 | Dec | 2021 | 0.0094264 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-12-11 13:12 | 2021-12-11 15:02 | 12 | 001:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR MAL TIEMPO | M21121100092 | New_Event | Bad Weather | Include | Include | Weather | 110 | 2021-12-11 | 1320 | keep | 0 | Dec | 2021 | 0.00089905 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-12-11 13:20 | 2021-12-11 13:22 | 514 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1520-05 | S21121100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-11 | 1028 | keep | 0 | Dec | 2021 | 0.00070017 | 0.00035008 | Momentary | FALSE | FALSE | Not_TMED_Event | 514
BAYAMON | 2021-12-11 13:20 | 2021-12-11 21:49 | 50 | 008:29 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21121100049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 509 | 2021-12-11 | 25450 | keep | 0 | Dec | 2021 | 0.017334 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-11 13:20 | 2021-12-11 13:22 | 752 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR 1520-05 | S21121100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-11 | 1504 | keep | 0 | Dec | 2021 | 0.0010244 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
BAYAMON | 2021-12-11 13:20 | 2021-12-11 13:22 | 68 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA CARGA DE 1520-01 Y 1520-04 | S21121100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-11 | 136 | keep | 0 | Dec | 2021 | 9.2629e-05 | 4.6314e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 68
HUMACAO | 2021-12-11 13:20 | 2021-12-11 13:21 | 2450 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 12600 | C21121100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-11 | 2450 | keep | 0 | Dec | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2021-12-11 13:20 | 2021-12-11 13:21 | 640 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 12600 | C21121100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-11 | 640 | keep | 0 | Dec | 2021 | 0.0004359 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
CAGUAS | 2021-12-11 13:20 | 2021-12-11 13:23 | 436 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO PARTE DE LA CARGA POR 3015-07 | C21121100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-12-11 | 1308 | keep | 0 | Dec | 2021 | 0.00089087 | 0.00029696 | Momentary | FALSE | FALSE | Not_TMED_Event | 436
ARECIBO | 2021-12-11 13:25 | 2021-12-11 16:51 | 5 | 003:26 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA PRIMARIA | A21121100047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2021-12-11 | 1030 | keep | 0 | Dec | 2021 | 0.00070153 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-12-11 13:32 | 2021-12-11 13:33 | 4390 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 9300 | C21121100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-11 | 4390 | keep | 0 | Dec | 2021 | 0.00299 | 0.00299 | Momentary | FALSE | FALSE | Not_TMED_Event | 4390
CAGUAS | 2021-12-11 13:32 | 2021-12-11 13:33 | 2092 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 9300 | C21121100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-11 | 2092 | keep | 0 | Dec | 2021 | 0.0014249 | 0.0014249 | Momentary | FALSE | FALSE | Not_TMED_Event | 2092
CAGUAS | 2021-12-11 13:32 | 2021-12-11 13:33 | 540 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 9300 | C21121100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-11 | 540 | keep | 0 | Dec | 2021 | 0.00036779 | 0.00036779 | Momentary | FALSE | FALSE | Not_TMED_Event | 540
CAGUAS | 2021-12-11 13:32 | 2021-12-11 13:33 | 131 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 9300 | C21121100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-11 | 131 | keep | 0 | Dec | 2021 | 8.9224e-05 | 8.9224e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 131
CAGUAS | 2021-12-11 13:32 | 2021-12-11 13:33 | 2281 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 9300 | C21121100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-11 | 2281 | keep | 0 | Dec | 2021 | 0.0015536 | 0.0015536 | Momentary | FALSE | FALSE | Not_TMED_Event | 2281
CAGUAS | 2021-12-11 13:32 | 2021-12-11 13:33 | 1569 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 9300 | C21121100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-11 | 1569 | keep | 0 | Dec | 2021 | 0.0010686 | 0.0010686 | Momentary | FALSE | FALSE | Not_TMED_Event | 1569
CAGUAS | 2021-12-11 13:32 | 2021-12-11 13:33 | 2417 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 9300 | C21121100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-11 | 2417 | keep | 0 | Dec | 2021 | 0.0016462 | 0.0016462 | Momentary | FALSE | FALSE | Not_TMED_Event | 2417
MAYAGÃœEZ | 2021-12-11 13:32 | 2021-12-11 18:00 | 137 | 004:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA Y SE CERRO MACHETES | M21121100099 | Partial_restoration | Wire Down | Include | Include | Equipment | 268 | 2021-12-11 | 36716 | keep | 0 | Dec | 2021 | 0.025007 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-11 13:38 | 2021-12-11 13:39 | 3 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO 1707-02 Y SE CERRO POR SCADA LLEVA 1707-03, 1707-04 Y 1707-05 | B21121100055 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-12-11 | 3 | keep | 0 | Dec | 2021 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-12-11 13:38 | 2021-12-11 13:39 | 61 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO 1707-02 Y SE CERRO POR SCADA LLEVA 1707-03, 1707-04 Y 1707-05 | B21121100055 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-12-11 | 61 | keep | 0 | Dec | 2021 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2021-12-11 13:38 | 2021-12-11 13:39 | 1501 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO 1707-02 Y SE CERRO POR SCADA LLEVA 1707-03, 1707-04 Y 1707-05 | B21121100055 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-12-11 | 1501 | keep | 0 | Dec | 2021 | 0.0010223 | 0.0010223 | Momentary | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2021-12-11 13:38 | 2021-12-11 13:39 | 546 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO 1707-02 Y SE CERRO POR SCADA LLEVA 1707-03, 1707-04 Y 1707-05 | B21121100055 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-12-11 | 546 | keep | 0 | Dec | 2021 | 0.00037188 | 0.00037188 | Momentary | FALSE | FALSE | Not_TMED_Event | 546
BAYAMON | 2021-12-11 13:44 | 2021-12-11 13:45 | 3 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO 1707-02 Y SE CERRO POR SCADA LLEVA 1707-03, 1707-04 Y 1707-05 | B21121100055 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-12-11 | 3 | keep | 0 | Dec | 2021 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-12-11 13:44 | 2021-12-11 13:45 | 61 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO 1707-02 Y SE CERRO POR SCADA LLEVA 1707-03, 1707-04 Y 1707-05 | B21121100055 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-12-11 | 61 | keep | 0 | Dec | 2021 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2021-12-11 13:44 | 2021-12-11 13:45 | 1501 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO 1707-02 Y SE CERRO POR SCADA LLEVA 1707-03, 1707-04 Y 1707-05 | B21121100055 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-12-11 | 1501 | keep | 0 | Dec | 2021 | 0.0010223 | 0.0010223 | Momentary | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2021-12-11 13:44 | 2021-12-11 13:45 | 546 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO 1707-02 Y SE CERRO POR SCADA LLEVA 1707-03, 1707-04 Y 1707-05 | B21121100055 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-12-11 | 546 | keep | 0 | Dec | 2021 | 0.00037188 | 0.00037188 | Momentary | FALSE | FALSE | Not_TMED_Event | 546
BAYAMON | 2021-12-11 13:48 | 2021-12-11 15:01 | 3 | 001:13 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO DEL 1707-03 Y SE CERRO BKR PROVISONAL #6 QUE LLEVA LAS CARGAS DEL 1707-02, 1707-03, 1707-04 Y 1707-05 | B21121100058 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 73 | 2021-12-11 | 219 | keep | 0 | Dec | 2021 | 0.00014916 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-12-11 13:48 | 2021-12-11 15:01 | 61 | 001:13 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO DEL 1707-03 Y SE CERRO BKR PROVISONAL #6 QUE LLEVA LAS CARGAS DEL 1707-02, 1707-03, 1707-04 Y 1707-05 | B21121100058 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 73 | 2021-12-11 | 4453 | keep | 0 | Dec | 2021 | 0.0030329 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2021-12-11 13:48 | 2021-12-11 15:01 | 1501 | 001:13 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO DEL 1707-03 Y SE CERRO BKR PROVISONAL #6 QUE LLEVA LAS CARGAS DEL 1707-02, 1707-03, 1707-04 Y 1707-05 | B21121100058 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 73 | 2021-12-11 | 109573 | keep | 0 | Dec | 2021 | 0.07463 | 0.0010223 | Sustained | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2021-12-11 13:48 | 2021-12-11 15:01 | 546 | 001:13 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO DEL 1707-03 Y SE CERRO BKR PROVISONAL #6 QUE LLEVA LAS CARGAS DEL 1707-02, 1707-03, 1707-04 Y 1707-05 | B21121100058 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 73 | 2021-12-11 | 39858 | keep | 0 | Dec | 2021 | 0.027147 | 0.00037188 | Sustained | FALSE | FALSE | Not_TMED_Event | 546
ARECIBO | 2021-12-11 13:49 | 2021-12-11 16:15 | 100 | 002:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21121100052 | New_Event | Bad Weather | Include | Include | Weather | 146 | 2021-12-11 | 14600 | keep | 0 | Dec | 2021 | 0.009944 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2021-12-11 14:24 | 2021-12-11 17:30 | 100 | 003:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR FUERTES VIENTOS | M21121100108 | New_Event | Bad Weather | Include | Include | Weather | 186 | 2021-12-11 | 18600 | keep | 0 | Dec | 2021 | 0.012668 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-12-11 14:34 | 2021-12-11 14:35 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21121100046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 2203 | keep | 0 | Dec | 2021 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
ARECIBO | 2021-12-11 14:34 | 2021-12-11 18:31 | 20 | 003:57 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | A21121100060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 237 | 2021-12-11 | 4740 | keep | 0 | Dec | 2021 | 0.0032284 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-12-11 14:34 | 2021-12-11 19:20 | 1222 | 004:46 | S | ESTRUCTURA AVERIADA | FUSIBLE FUNDIDO EN LA ALTA DEL TRANSFORMADOR SOPORTE BARRA AVERIADO | A21121100000 | New_Event | Defective Pole | Include | Include | Equipment | 286 | 2021-12-11 | 349492 | keep | 0 | Dec | 2021 | 0.23804 | 0.0008323 | Sustained | FALSE | FALSE | Not_TMED_Event | 1222
ARECIBO | 2021-12-11 14:34 | 2021-12-11 19:20 | 2756 | 004:46 | S | ESTRUCTURA AVERIADA | FUSIBLE FUNDIDO EN LA ALTA DEL TRANSFORMADOR SOPORTE DE BARRAS AVERIADO | A21121100000 | New_Event | Defective Pole | Include | Include | Equipment | 286 | 2021-12-11 | 788216 | keep | 0 | Dec | 2021 | 0.53685 | 0.0018771 | Sustained | FALSE | FALSE | Not_TMED_Event | 2756
ARECIBO | 2021-12-11 14:34 | 2021-12-11 19:20 | 2833 | 004:46 | S | ESTRUCTURA AVERIADA | FUSIBLE FUNDIDO EN LA ALTA DEL TRANSFORMADOR SOPORTE DE BARRA AVERIADO | A21121100000 | New_Event | Defective Pole | Include | Include | Equipment | 286 | 2021-12-11 | 810238 | keep | 0 | Dec | 2021 | 0.55185 | 0.0019295 | Sustained | FALSE | FALSE | Not_TMED_Event | 2833
SAN JUAN | 2021-12-11 14:35 | 2021-12-11 14:36 | 60 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR POR CAJA QUEMADA EN ORDEN DE TRABAJO EVENTO S21121100037 AL CERRAR INTERRUPTOR SE QUEMO LA CAJA | S21121100046 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-12-11 | 60 | keep | 0 | Dec | 2021 | 4.0866e-05 | 4.0866e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-12-11 14:35 | 2021-12-11 14:36 | 55 | 000:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR POR CAJA QUEMADA EN OORDEN DE TRABAJO EVENTO S21121100037 CARGA TRANSFERIDA AL 1420-02 | S21121100046 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-12-11 | 55 | keep | 0 | Dec | 2021 | 3.746e-05 | 3.746e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 55
MAYAGÃœEZ | 2021-12-11 14:40 | 2021-12-11 17:52 | 60 | 003:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | M21121000133 | New_Event | Wire Down | Include | Include | Equipment | 192 | 2021-12-11 | 11520 | keep | 0 | Dec | 2021 | 0.0078462 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-12-11 15:01 | 2021-12-11 16:27 | 22 | 001:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DIO SERVICIO A MAS CLIENTES CERRANDO N/O DEL 1707-03 Y 1707-05 FID 19410882 Y ABRIENDO MACHETES EN FID 19410736 MEDIANTE GOI BY-211211-03 PARA REALIZAR DESGANCHE Y LEVANTAR TRAMO EN EL SUELO. SE QUEDARON 9 CLIENTES SIN SERVICIO | B21121100058 | Partial_restoration | Wire Down | Include | Include | Equipment | 86 | 2021-12-11 | 1892 | keep | 0 | Dec | 2021 | 0.0012886 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-12-11 15:10 | 2021-12-11 16:08 | 80 | 000:58 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21121100031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2021-12-11 | 4640 | keep | 0 | Dec | 2021 | 0.0031603 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-12-11 15:23 | 2021-12-11 15:24 | 1681 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CARGA POR EL 1303-04 | S21121100050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 1681 | keep | 0 | Dec | 2021 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-12-11 15:23 | 2021-12-11 15:24 | 1598 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CARGA POR EL 1303-04 | S21121100050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 1598 | keep | 0 | Dec | 2021 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
MAYAGÃœEZ | 2021-12-11 15:26 | 2021-12-12 13:25 | 10 | 021:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M21121100116 | New_Event | Bad Weather | Include | Include | Weather | 1319 | 2021-12-11 | 13190 | keep | 0 | Dec | 2021 | 0.0089836 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-11 15:26 | 2021-12-11 16:00 | 80 | 000:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | M21121100115 | New_Event | Bad Weather | Include | Include | Weather | 34 | 2021-12-11 | 2720 | keep | 0 | Dec | 2021 | 0.0018526 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-12-11 15:39 | 2021-12-11 16:45 | 10 | 001:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA CERRAR BAJANTE SECUNDARIO ABIERTO Y SE REALIZO DESGANCHE CRITICO | S21121100034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 66 | 2021-12-11 | 660 | keep | 0 | Dec | 2021 | 0.00044952 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-11 15:50 | 2021-12-11 18:00 | 2076 | 002:10 | P | DESGANCHE | SE DESGANCHO BAMBUAS CON VARETA DEL 1718-03. 40% DE SU CARGA POR EL 1718-03 | B21121100082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2021-12-11 | 269880 | keep | 0 | Dec | 2021 | 0.18381 | 0.001414 | Sustained | FALSE | FALSE | Not_TMED_Event | 2076
BAYAMON | 2021-12-11 15:50 | 2021-12-11 18:00 | 2605 | 002:10 | T | DESGANCHE | SE DESGANCHO BAMBUAS CON VARETA. LLEVA 40% DEL 1710-05 | B21121100082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2021-12-11 | 338650 | keep | 0 | Dec | 2021 | 0.23065 | 0.0017743 | Sustained | FALSE | FALSE | Not_TMED_Event | 2605
AGUADILLA | 2021-12-11 15:54 | 2021-12-11 15:55 | 4882 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21121100122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 4882 | keep | 0 | Dec | 2021 | 0.0033251 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
PONCE | 2021-12-11 15:56 | 2021-12-11 19:45 | 80 | 003:49 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P21121100049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2021-12-11 | 18320 | keep | 0 | Dec | 2021 | 0.012478 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2021-12-11 16:00 | 2021-12-11 18:00 | 167 | 002:00 | S | DESCONECTIVO DEFECTUOSO | DISPARO DE SUBESTACION POR AUXILIAR DE LINEA DEL 5021-02 QUEMADO | P21121100015 | New_Event | Switch Failure | Include | Include | Equipment | 120 | 2021-12-11 | 20040 | keep | 0 | Dec | 2021 | 0.013649 | 0.00011374 | Sustained | FALSE | FALSE | Not_TMED_Event | 167
PONCE | 2021-12-11 16:00 | 2021-12-11 18:00 | 202 | 002:00 | S | DESCONECTIVO DEFECTUOSO | DISPARO DE SUBESTACION POR AUXILIAR DE LINEA DEL 5021-02 QUEMADO | P21121100015 | New_Event | Switch Failure | Include | Include | Equipment | 120 | 2021-12-11 | 24240 | keep | 0 | Dec | 2021 | 0.01651 | 0.00013758 | Sustained | FALSE | FALSE | Not_TMED_Event | 202
BAYAMON | 2021-12-11 16:05 | 2021-12-11 18:35 | 50 | 002:30 | P | DESGANCHE | 1 X 65 EN C/L. SE REALIZO DESGANCHE | B21121100046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2021-12-11 | 7500 | keep | 0 | Dec | 2021 | 0.0051082 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-11 16:06 | 2021-12-11 16:58 | 30 | 000:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L. PALOMA | B21121100091 | New_Event |  |  | Include | Wildlife | 52 | 2021-12-11 | 1560 | keep | 0 | Dec | 2021 | 0.0010625 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-11 16:06 | 2021-12-11 16:14 | 2694 | 000:08 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR PARA RETIRAR OVERHEAD PARTIDO LINEA 13600 | A21111100073 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-12-11 | 21552 | keep | 0 | Dec | 2021 | 0.014679 | 0.0018349 | Sustained | FALSE | FALSE | Not_TMED_Event | 2694
ARECIBO | 2021-12-11 16:06 | 2021-12-11 16:14 | 316 | 000:08 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR PARA RETIRAR OVERHEAD PARTIDO LINEA 13600 | A21121100072 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-12-11 | 2528 | keep | 0 | Dec | 2021 | 0.0017218 | 0.00021523 | Sustained | FALSE | FALSE | Not_TMED_Event | 316
SAN JUAN | 2021-12-11 16:20 | 2021-12-11 20:20 | 40 | 004:00 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21121100058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 240 | 2021-12-11 | 9600 | keep | 0 | Dec | 2021 | 0.0065385 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-12-11 16:25 | 2021-12-12 15:46 | 60 | 023:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21121100049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1401 | 2021-12-11 | 84060 | keep | 0 | Dec | 2021 | 0.057253 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-12-11 16:27 | 2021-12-14 21:01 | 6 | 076:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRARON MACHETES PARA ENERGIZAR LOS 9 CLIENTES MEDIANTE GOI BY-211211-03 PERO HAY PUENTE ABIERTO QUE SE TRABAJARA MAÃ‘ANA AFECTANDOSE 3 CLIENTES TODAVIA. SE REALIZO DESGANCHE, SE LEVANTO CONDUCTOR Y SE REEMPLAZO POSTE | B21121100058 | Partial_restoration | Wire Down | Include | Include | Equipment | 4594 | 2021-12-11 | 27564 | keep | 0 | Dec | 2021 | 0.018774 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-12-11 16:27 | 2021-12-12 09:08 | 50 | 016:41 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU#3 NO SE ENCONTRO CAUSA | P21121100051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1001 | 2021-12-11 | 50050 | keep | 0 | Dec | 2021 | 0.034089 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-12-11 16:43 | 2021-12-11 19:30 | 12 | 002:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR PEDESTAL SECUNDARIO | S21121100059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 167 | 2021-12-11 | 2004 | keep | 0 | Dec | 2021 | 0.0013649 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2021-12-11 16:55 | 2021-12-11 16:56 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21121100138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 1192 | keep | 0 | Dec | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2021-12-11 17:10 | 2021-12-11 19:26 | 2366 | 002:16 | T | DESGANCHE | SE RETIRO ARBOL SOBRE LINEA Y SE CERRO INTERRUPTOR | M21121100139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2021-12-11 | 321776 | keep | 0 | Dec | 2021 | 0.21916 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
MAYAGÃœEZ | 2021-12-11 17:16 | 2021-12-12 11:58 | 15 | 018:42 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA POR 50 KVA | M21121100141 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1122 | 2021-12-11 | 16830 | keep | 0 | Dec | 2021 | 0.011463 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-12-11 18:00 | 2021-12-11 23:39 | 115 | 005:39 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA POR DESGANCHE | P21121100053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 339 | 2021-12-11 | 38985 | keep | 0 | Dec | 2021 | 0.026553 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
UTUADO | 2021-12-11 18:05 | 2021-12-11 19:17 | 25 | 001:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21121100087 | New_Event | Bad Weather | Include | Include | Weather | 72 | 2021-12-11 | 1800 | keep | 0 | Dec | 2021 | 0.001226 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-12-11 18:08 | 2021-12-12 21:29 | 20 | 027:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | M21121100148 | New_Event | Bad Weather | Include | Include | Weather | 1641 | 2021-12-11 | 32820 | keep | 0 | Dec | 2021 | 0.022354 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-12-11 18:12 | 2021-12-12 10:00 | 40 | 015:48 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21121100151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 948 | 2021-12-11 | 37920 | keep | 0 | Dec | 2021 | 0.025827 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-12-11 18:19 | 2021-12-11 19:25 | 10 | 001:06 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21121100068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 66 | 2021-12-11 | 660 | keep | 0 | Dec | 2021 | 0.00044952 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-12-11 18:43 | 2021-12-12 14:13 | 10 | 019:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA AVERIADA | C21121100058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1170 | 2021-12-11 | 11700 | keep | 0 | Dec | 2021 | 0.0079688 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-12-11 18:44 | 2021-12-11 20:12 | 5 | 001:28 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | R21121100040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 88 | 2021-12-11 | 440 | keep | 0 | Dec | 2021 | 0.00029968 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2021-12-11 18:46 | 2021-12-12 10:12 | 100 | 015:26 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21121100059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 926 | 2021-12-11 | 92600 | keep | 0 | Dec | 2021 | 0.063069 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2021-12-11 19:03 | 2021-12-11 20:15 | 652 | 001:12 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B21121100114 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2021-12-11 | 46944 | keep | 0 | Dec | 2021 | 0.031973 | 0.00044407 | Sustained | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2021-12-11 19:03 | 2021-12-11 20:15 | 2704 | 001:12 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B21121100114 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2021-12-11 | 194688 | keep | 0 | Dec | 2021 | 0.1326 | 0.0018417 | Sustained | FALSE | FALSE | Not_TMED_Event | 2704
MAYAGÃœEZ | 2021-12-11 19:16 | 2021-12-12 16:58 | 20 | 021:42 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR UNO IGUAL | M21121100162 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1302 | 2021-12-11 | 26040 | keep | 0 | Dec | 2021 | 0.017736 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-12-11 19:20 | 2021-12-11 22:09 | 20 | 002:49 | P | CABLE SOTERRADO AVERIADO | 1 X 30 EN AEREO PROVISIONAL AVERIA NUEVA DEL T-29 AL T-28 SE CREO EVENTO R21121100047 PARA CONSTRUIR AEREO PROVISIONAL | R21121100041 | New_Event | UG Cable Fault | Include | Include | Equipment | 169 | 2021-12-11 | 3380 | keep | 0 | Dec | 2021 | 0.0023021 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-12-11 19:24 | 2021-12-11 19:25 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21121100164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 108 | keep | 0 | Dec | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
CAGUAS | 2021-12-11 19:30 | 2021-12-12 10:18 | 100 | 014:48 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21121100061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 888 | 2021-12-11 | 88800 | keep | 0 | Dec | 2021 | 0.060481 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-12-11 19:48 | 2021-12-12 11:40 | 10 | 015:52 | P | DESGANCHE | 1 X 8 EN TRANSFORMADOR | C21121100062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 952 | 2021-12-11 | 9520 | keep | 0 | Dec | 2021 | 0.006484 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-12-11 20:28 | 2021-12-12 19:40 | 652 | 023:12 | S | LINEA DE TRANSMISION 38KV | SE REPARO AVERIA DE PUENTE ABIERTO Y SE TIRO BY-PASS EN EL MOD 7807 | B21121100116 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1392 | 2021-12-11 | 907584 | keep | 0 | Dec | 2021 | 0.61815 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-12-11 20:28 | 2021-12-12 19:40 | 2704 | 023:12 | S | LINEA DE TRANSMISION 38KV | SE REPARO AVERIA DE PUENTE ABIERTO Y SE TIRO BY-PASS EN EL MOD 7807 | B21121100116 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1392 | 2021-12-11 | 3763968 | keep | 0 | Dec | 2021 | 2.5636 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-12-11 20:32 | 2021-12-12 08:02 | 4 | 011:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A21121100092 | New_Event | Bad Weather | Include | Include | Weather | 690 | 2021-12-11 | 2760 | keep | 0 | Dec | 2021 | 0.0018798 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-12-11 20:35 | 2021-12-12 10:30 | 40 | 013:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21121100174 | New_Event | Bad Weather | Include | Include | Weather | 835 | 2021-12-11 | 33400 | keep | 0 | Dec | 2021 | 0.022749 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-12-11 20:40 | 2021-12-11 22:35 | 38 | 001:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR PALOMA | R21121100043 | New_Event |  |  | Include | Wildlife | 115 | 2021-12-11 | 4370 | keep | 0 | Dec | 2021 | 0.0029764 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
MAYAGÃœEZ | 2021-12-11 20:40 | 2021-12-11 20:41 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUTPTOR NO SE REPORTO CAUSA | M21121100175 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 108 | keep | 0 | Dec | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
CAGUAS | 2021-12-11 20:45 | 2021-12-12 12:07 | 200 | 015:22 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C21121100063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 922 | 2021-12-11 | 184400 | keep | 0 | Dec | 2021 | 0.12559 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2021-12-11 20:50 | 2021-12-12 11:42 | 73 | 014:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIAS | C21121100065 | New_Event | Bad Weather | Include | Include | Weather | 892 | 2021-12-11 | 65116 | keep | 0 | Dec | 2021 | 0.04435 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
SAN JUAN | 2021-12-11 21:13 | 2021-12-12 15:57 | 50 | 018:44 | P | CABLE SOTERRADO AVERIADO | SE REALIZO PROVISIONAL AEREO HACIA T-54 Y SE RESTABLECIO SERVICIO | S21121100080 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1124 | 2021-12-11 | 56200 | keep | 0 | Dec | 2021 | 0.038278 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-12-11 21:19 | 2021-12-11 22:33 | 12 | 001:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21121100051 | New_Event | Secondary Wire Down | Include | Include | Equipment | 74 | 2021-12-11 | 888 | keep | 0 | Dec | 2021 | 0.00060481 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-12-11 22:09 | 2021-12-12 22:21 | 20 | 024:12 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL | R21121100047 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1452 | 2021-12-11 | 29040 | keep | 0 | Dec | 2021 | 0.019779 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2021-12-11 22:16 | 2021-12-11 23:00 | 91 | 000:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA DEFECTUOSA | R21121100046 | New_Event | Cutout Failure | Include | Include | Equipment | 44 | 2021-12-11 | 4004 | keep | 0 | Dec | 2021 | 0.0027271 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
CANOVANAS | 2021-12-11 22:25 | 2021-12-13 16:08 | 10 | 041:43 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | R21121100048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2503 | 2021-12-11 | 25030 | keep | 0 | Dec | 2021 | 0.017048 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-12-11 23:30 | 2021-12-12 11:11 | 197 | 011:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE CAMBIO CAJA PRIMARIA EN CORTE DE LINEA | P21121100069 | New_Event | Cutout Failure | Include | Include | Equipment | 701 | 2021-12-11 | 138097 | keep | 0 | Dec | 2021 | 0.094057 | 0.00013418 | Sustained | FALSE | FALSE | Not_TMED_Event | 197
AGUADILLA | 2021-12-11 23:37 | 2021-12-11 23:38 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21121100185 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-11 | 1192 | keep | 0 | Dec | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
ARECIBO | 2021-12-12 00:07 | 2021-12-12 12:47 | 50 | 012:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | A21121200001 | New_Event | Wire Down | Include | Include | Equipment | 760 | 2021-12-12 | 38000 | keep | 0 | Dec | 2021 | 0.025882 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-12-12 00:13 | 2021-12-12 08:57 | 70 | 008:44 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21121200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 524 | 2021-12-12 | 36680 | keep | 0 | Dec | 2021 | 0.024983 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
GUAYAMA | 2021-12-12 00:30 | 2021-12-12 00:31 | 4132 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21121300001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-12 | 4132 | keep | 0 | Dec | 2021 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
MAYAGÃœEZ | 2021-12-12 00:45 | 2021-12-12 08:40 | 50 | 007:55 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS | M21121200001 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 475 | 2021-12-12 | 23750 | keep | 0 | Dec | 2021 | 0.016176 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-12-12 04:48 | 2021-12-12 04:49 | 31 | 000:01 | T | DESGANCHE | RECERRO | B21121200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-12 | 31 | keep | 0 | Dec | 2021 | 2.1114e-05 | 2.1114e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 31
ARECIBO | 2021-12-12 05:01 | 2021-12-12 09:32 | 2201 | 004:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6900 | A21121200010 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 271 | 2021-12-12 | 596471 | keep | 0 | Dec | 2021 | 0.40625 | 0.0014991 | Sustained | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2021-12-12 05:01 | 2021-12-12 09:32 | 1986 | 004:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6900 | A21121200010 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 271 | 2021-12-12 | 538206 | keep | 0 | Dec | 2021 | 0.36657 | 0.0013527 | Sustained | FALSE | FALSE | Not_TMED_Event | 1986
ARECIBO | 2021-12-12 05:01 | 2021-12-12 09:32 | 199 | 004:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6900 | A21121200010 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 271 | 2021-12-12 | 53929 | keep | 0 | Dec | 2021 | 0.036731 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2021-12-12 05:01 | 2021-12-12 09:32 | 24 | 004:31 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6900 | A21121200010 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 271 | 2021-12-12 | 6504 | keep | 0 | Dec | 2021 | 0.0044298 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
SAN JUAN | 2021-12-12 05:21 | 2021-12-12 05:22 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21121200002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-12 | 641 | keep | 0 | Dec | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-12-12 05:21 | 2021-12-12 05:22 | 733 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S21121200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-12 | 733 | keep | 0 | Dec | 2021 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
ARECIBO | 2021-12-12 06:33 | 2021-12-12 17:57 | 30 | 011:24 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21121200016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 684 | 2021-12-12 | 20520 | keep | 0 | Dec | 2021 | 0.013976 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-12-12 06:56 | 2021-12-12 09:08 | 200 | 002:12 | P | DESGANCHE | 1 X 40 Y 1 X 80 EN CORTES DE LINEA | C21121200006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2021-12-12 | 26400 | keep | 0 | Dec | 2021 | 0.017981 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2021-12-12 07:07 | 2021-12-12 11:39 | 130 | 004:32 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 50 EN CORTE DE LINEA SE REEMPLAZO AISLADOR ROTO | C21121200008 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 272 | 2021-12-12 | 35360 | keep | 0 | Dec | 2021 | 0.024084 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
BAYAMON | 2021-12-12 07:08 | 2021-12-12 15:15 | 40 | 008:07 | P | DESGANCHE | 1 X 80 EN C/L. SE REALIZO DESGANCHE | S21121200003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 487 | 2021-12-12 | 19480 | keep | 0 | Dec | 2021 | 0.013268 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2021-12-12 07:13 | 2021-12-12 10:25 | 79 | 003:12 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBUA DE LINEA | P21121200002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2021-12-12 | 15168 | keep | 0 | Dec | 2021 | 0.010331 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
MAYAGÃœEZ | 2021-12-12 07:21 | 2021-12-12 07:22 | 2483 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21121200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-12 | 2483 | keep | 0 | Dec | 2021 | 0.0016912 | 0.0016912 | Momentary | FALSE | FALSE | Not_TMED_Event | 2483
UTUADO | 2021-12-12 07:24 | 2021-12-12 11:23 | 20 | 003:59 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA INFORMA JOURNEYMAN REQUIERE DESGANCHE | A21121200020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2021-12-12 | 4780 | keep | 0 | Dec | 2021 | 0.0032556 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-12-12 07:26 | 2021-12-12 15:34 | 35 | 008:08 | P | DESGANCHE | 1 X 50 EN C/L | R21121200004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 488 | 2021-12-12 | 17080 | keep | 0 | Dec | 2021 | 0.011633 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2021-12-12 07:29 | 2021-12-12 07:30 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21121200004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-12 | 2113 | keep | 0 | Dec | 2021 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
SAN JUAN | 2021-12-12 07:35 | 2021-12-12 12:15 | 46 | 004:40 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 40 EN RISER SE REEMPLAZARON TERMINACIONES QUEMADAS | R21121200005 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 280 | 2021-12-12 | 12880 | keep | 0 | Dec | 2021 | 0.0087725 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
MAYAGÃœEZ | 2021-12-12 07:35 | 2021-12-12 11:15 | 150 | 003:40 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21121200003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2021-12-12 | 33000 | keep | 0 | Dec | 2021 | 0.022476 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2021-12-12 07:36 | 2021-12-12 10:15 | 30 | 002:39 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 30 EN PROVISIONAL SE REPARO TERMINACION | B21121200003 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 159 | 2021-12-12 | 4770 | keep | 0 | Dec | 2021 | 0.0032488 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-12 07:44 | 2021-12-12 12:35 | 30 | 004:51 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B21121200005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 291 | 2021-12-12 | 8730 | keep | 0 | Dec | 2021 | 0.005946 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-12-12 07:55 | 2021-12-12 17:57 | 90 | 010:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO | M21121200004 | New_Event | Wire Down | Include | Include | Equipment | 602 | 2021-12-12 | 54180 | keep | 0 | Dec | 2021 | 0.036902 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
ARECIBO | 2021-12-12 08:02 | 2021-12-12 08:03 | 1222 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21121200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-12 | 1222 | keep | 0 | Dec | 2021 | 0.0008323 | 0.0008323 | Momentary | FALSE | FALSE | Not_TMED_Event | 1222
ARECIBO | 2021-12-12 08:02 | 2021-12-12 08:03 | 2756 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21121200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-12 | 2756 | keep | 0 | Dec | 2021 | 0.0018771 | 0.0018771 | Momentary | FALSE | FALSE | Not_TMED_Event | 2756
ARECIBO | 2021-12-12 08:02 | 2021-12-12 08:03 | 2833 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21121200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-12 | 2833 | keep | 0 | Dec | 2021 | 0.0019295 | 0.0019295 | Momentary | FALSE | FALSE | Not_TMED_Event | 2833
ARECIBO | 2021-12-12 08:02 | 2021-12-12 08:03 | 1218 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21121200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-12 | 1218 | keep | 0 | Dec | 2021 | 0.00082957 | 0.00082957 | Momentary | FALSE | FALSE | Not_TMED_Event | 1218
ARECIBO | 2021-12-12 08:02 | 2021-12-12 08:03 | 1345 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21121200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-12 | 1345 | keep | 0 | Dec | 2021 | 0.00091607 | 0.00091607 | Momentary | FALSE | FALSE | Not_TMED_Event | 1345
ARECIBO | 2021-12-12 08:02 | 2021-12-12 08:03 | 1265 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21121200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-12 | 1265 | keep | 0 | Dec | 2021 | 0.00086159 | 0.00086159 | Momentary | FALSE | FALSE | Not_TMED_Event | 1265
ARECIBO | 2021-12-12 08:02 | 2021-12-12 08:03 | 2071 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21121200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-12 | 2071 | keep | 0 | Dec | 2021 | 0.0014105 | 0.0014105 | Momentary | FALSE | FALSE | Not_TMED_Event | 2071
ARECIBO | 2021-12-12 08:02 | 2021-12-12 08:03 | 760 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21121200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-12 | 760 | keep | 0 | Dec | 2021 | 0.00051763 | 0.00051763 | Momentary | FALSE | FALSE | Not_TMED_Event | 760
ARECIBO | 2021-12-12 08:02 | 2021-12-12 08:03 | 509 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21121200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-12 | 509 | keep | 0 | Dec | 2021 | 0.00034668 | 0.00034668 | Momentary | FALSE | FALSE | Not_TMED_Event | 509
ARECIBO | 2021-12-12 08:02 | 2021-12-12 08:03 | 2620 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21121200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-12 | 2620 | keep | 0 | Dec | 2021 | 0.0017845 | 0.0017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 2620
ARECIBO | 2021-12-12 08:02 | 2021-12-12 08:03 | 1916 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A21121200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-12 | 1916 | keep | 0 | Dec | 2021 | 0.001305 | 0.001305 | Momentary | FALSE | FALSE | Not_TMED_Event | 1916
ARECIBO | 2021-12-12 08:03 | 2021-12-12 08:49 | 4 | 000:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A21121100092 | Partial_restoration | Bad Weather | Include | Include | Weather | 46 | 2021-12-12 | 184 | keep | 0 | Dec | 2021 | 0.00012532 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-12-12 08:06 | 2021-12-13 12:20 | 4 | 028:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | C21121200010 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1694 | 2021-12-12 | 6776 | keep | 0 | Dec | 2021 | 0.0046151 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-12-12 08:11 | 2021-12-12 17:27 | 6 | 009:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTA FUSIBLE AVERIADO | A21121200024 | New_Event | Cutout Failure | Include | Include | Equipment | 556 | 2021-12-12 | 3336 | keep | 0 | Dec | 2021 | 0.0022721 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-12-12 08:15 | 2021-12-12 15:02 | 7 | 006:47 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C21121200012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 407 | 2021-12-12 | 2849 | keep | 0 | Dec | 2021 | 0.0019404 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-12-12 08:32 | 2021-12-12 08:34 | 1447 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA 1419-09 | S21121200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-12 | 2894 | keep | 0 | Dec | 2021 | 0.0019711 | 0.00098555 | Momentary | FALSE | FALSE | Not_TMED_Event | 1447
SAN JUAN | 2021-12-12 08:32 | 2021-12-12 08:34 | 266 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1112-04 | S21121200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-12 | 532 | keep | 0 | Dec | 2021 | 0.00036234 | 0.00018117 | Momentary | FALSE | FALSE | Not_TMED_Event | 266
SAN JUAN | 2021-12-12 08:32 | 2021-12-12 08:34 | 73 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1112-04 | S21121200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-12 | 146 | keep | 0 | Dec | 2021 | 9.944e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
MAYAGÃœEZ | 2021-12-12 08:55 | 2021-12-12 10:47 | 8 | 001:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | M21121100134 | New_Event | Secondary Wire Down | Include | Include | Equipment | 112 | 2021-12-12 | 896 | keep | 0 | Dec | 2021 | 0.00061026 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-12-12 09:05 | 2021-12-12 15:22 | 6 | 006:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN XMR | C21121200021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 377 | 2021-12-12 | 2262 | keep | 0 | Dec | 2021 | 0.0015406 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-12-12 09:10 | 2021-12-12 16:50 | 11 | 007:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BARRA EN PEDESTAL | C21121200033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 460 | 2021-12-12 | 5060 | keep | 0 | Dec | 2021 | 0.0034463 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2021-12-12 09:10 | 2021-12-12 16:50 | 4 | 007:40 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C21121200022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 460 | 2021-12-12 | 1840 | keep | 0 | Dec | 2021 | 0.0012532 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2021-12-12 09:10 | 2021-12-12 09:11 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21121200009 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-12 | 3114 | keep | 0 | Dec | 2021 | 0.0021209 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-12-12 09:17 | 2021-12-12 21:22 | 30 | 012:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21121200028 | New_Event | Bad Weather | Include | Include | Weather | 725 | 2021-12-12 | 21750 | keep | 0 | Dec | 2021 | 0.014814 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-12-12 09:18 | 2021-12-12 11:18 | 30 | 002:00 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S21121200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2021-12-12 | 3600 | keep | 0 | Dec | 2021 | 0.0024519 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-12-12 09:28 | 2021-12-12 12:13 | 6 | 002:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR REMPLAZO CAJA QUEMADA | C21121200023 | New_Event | Cutout Failure | Include | Include | Equipment | 165 | 2021-12-12 | 990 | keep | 0 | Dec | 2021 | 0.00067428 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2021-12-12 09:44 | 2021-12-12 17:25 | 40 | 007:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | P21121200011 | New_Event | Bad Weather | Include | Include | Weather | 461 | 2021-12-12 | 18440 | keep | 0 | Dec | 2021 | 0.012559 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2021-12-12 10:19 | 2021-12-12 19:40 | 150 | 009:21 | P | CABLE SOTERRADO AVERIADO | 2 X 80 EN PROVICIONAL AEREO NUEVO CABLE SOTERRADO AVERIADO SE COSNTRUYO PROVICIONAL AEREO | P21121200012 | New_Event | UG Cable Fault | Include | Include | Equipment | 561 | 2021-12-12 | 84150 | keep | 0 | Dec | 2021 | 0.057314 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2021-12-12 10:34 | 2021-12-12 20:28 | 4 | 009:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN XMR REEMPLAZO PORTAFUSIBLE QUEMADO | R21121200014 | New_Event | Cutout Failure | Include | Include | Equipment | 594 | 2021-12-12 | 2376 | keep | 0 | Dec | 2021 | 0.0016183 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-12-12 10:36 | 2021-12-12 11:08 | 6 | 000:32 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO XMR Y SE REPARO EN PEDESTAL | B21121200020 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 32 | 2021-12-12 | 192 | keep | 0 | Dec | 2021 | 0.00013077 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-12-12 10:46 | 2021-12-12 12:40 | 35 | 001:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA PALOMA CRUZO FASE | P21121200016 | New_Event |  |  | Include | Wildlife | 114 | 2021-12-12 | 3990 | keep | 0 | Dec | 2021 | 0.0027176 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2021-12-12 10:51 | 2021-12-12 10:53 | 1681 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1303-04 | S21121200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-12 | 3362 | keep | 0 | Dec | 2021 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-12-12 10:51 | 2021-12-12 10:53 | 1598 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1303-04 | S21121200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-12 | 3196 | keep | 0 | Dec | 2021 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
MAYAGÃœEZ | 2021-12-12 10:53 | 2021-12-12 13:34 | 30 | 002:41 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M21121200018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2021-12-12 | 4830 | keep | 0 | Dec | 2021 | 0.0032897 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-12 11:07 | 2021-12-12 14:30 | 10 | 003:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE CERRO BAJANTE SECUNDARIO | B21121200023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 203 | 2021-12-12 | 2030 | keep | 0 | Dec | 2021 | 0.0013826 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-12 11:18 | 2021-12-12 16:15 | 60 | 004:57 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER @ LINEA AEREA NO CAUSA | C21121200030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 297 | 2021-12-12 | 17820 | keep | 0 | Dec | 2021 | 0.012137 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-12-12 11:32 | 2021-12-12 15:27 | 4 | 003:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A21121200038 | New_Event | Wire Down | Include | Include | Equipment | 235 | 2021-12-12 | 940 | keep | 0 | Dec | 2021 | 0.00064023 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2021-12-12 11:33 | 2021-12-12 23:38 | 100 | 012:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN C/L MAL TIEMPO | R21121200019 | New_Event | Bad Weather | Include | Include | Weather | 725 | 2021-12-12 | 72500 | keep | 0 | Dec | 2021 | 0.049379 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-12-12 11:57 | 2021-12-12 14:23 | 300 | 002:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M21121200021 | New_Event | Bad Weather | Include | Include | Weather | 146 | 2021-12-12 | 43800 | keep | 0 | Dec | 2021 | 0.029832 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2021-12-12 11:58 | 2021-12-12 14:56 | 50 | 002:58 | P | DESGANCHE | 1 X 50 EN C/L | R21121200021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2021-12-12 | 8900 | keep | 0 | Dec | 2021 | 0.0060617 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-12-12 12:00 | 2021-12-14 23:38 | 100 | 059:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO EVENTO DEL DIA 12 DIC DE 2021 | A21121400140 | New_Event | Wire Down | Include | Include | Equipment | 3578 | 2021-12-12 | 357800 | keep | 0 | Dec | 2021 | 0.2437 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2021-12-12 12:08 | 2021-12-12 17:12 | 25 | 005:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO LINEA SECUNDARIA | M21121200026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 304 | 2021-12-12 | 7600 | keep | 0 | Dec | 2021 | 0.0051763 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-12-12 12:10 | 2021-12-12 17:48 | 180 | 005:38 | P | DESGANCHE | 3 X 100, 3 X 80 EN DISTINTOS CORTE DE LINEA Y SE REALIZO DESGANCHE | S21121200051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 338 | 2021-12-12 | 60840 | keep | 0 | Dec | 2021 | 0.041438 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
ARECIBO | 2021-12-12 12:14 | 2021-12-12 13:18 | 4 | 001:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | A21121200042 | New_Event | Cutout Failure | Include | Include | Equipment | 64 | 2021-12-12 | 256 | keep | 0 | Dec | 2021 | 0.00017436 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-12-12 12:16 | 2021-12-12 13:40 | 1681 | 001:24 | T | NO SE REPORTO CAUSA | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA CARGA POR BKR 1303-04 | S21121200021 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 84 | 2021-12-12 | 141204 | keep | 0 | Dec | 2021 | 0.096173 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-12-12 12:16 | 2021-12-12 13:40 | 1598 | 001:24 | T | NO SE REPORTO CAUSA | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA CARGA POR BKR 1303-04 | S21121200021 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 84 | 2021-12-12 | 134232 | keep | 0 | Dec | 2021 | 0.091425 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
ARECIBO | 2021-12-12 12:19 | 2021-12-12 15:54 | 5 | 003:35 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A21121200044 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 215 | 2021-12-12 | 1075 | keep | 0 | Dec | 2021 | 0.00073218 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2021-12-12 12:20 | 2021-12-12 13:06 | 10 | 000:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | M21121100052 | New_Event | Secondary Wire Down | Include | Include | Equipment | 46 | 2021-12-12 | 460 | keep | 0 | Dec | 2021 | 0.0003133 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-12 12:21 | 2021-12-12 12:23 | 2422 | 000:02 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE CERRO POR SCADA | S21121200000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 2 | 2021-12-12 | 4844 | keep | 0 | Dec | 2021 | 0.0032992 | 0.0016496 | Momentary | FALSE | FALSE | Not_TMED_Event | 2422
SAN JUAN | 2021-12-12 12:23 | 2021-12-12 14:05 | 40 | 001:42 | P | NO SE REPORTO CAUSA | 1 80 EN CORTE DE LINEA | S21121200049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 102 | 2021-12-12 | 4080 | keep | 0 | Dec | 2021 | 0.0027789 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-12-12 12:23 | 2021-12-12 17:10 | 25 | 004:47 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 50 EN RISER Y SE REMPLAZO TERMINACION | S21121200006 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 287 | 2021-12-12 | 7175 | keep | 0 | Dec | 2021 | 0.0048869 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-12-12 12:31 | 2021-12-12 14:08 | 15 | 001:37 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | M21121200034 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 97 | 2021-12-12 | 1455 | keep | 0 | Dec | 2021 | 0.00099099 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-12-12 12:34 | 2021-12-12 16:58 | 65 | 004:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN C/L. SE CERRO PUENTE DE LINEA A CAJA | S21121200039 | New_Event | Wire Down | Include | Include | Equipment | 264 | 2021-12-12 | 17160 | keep | 0 | Dec | 2021 | 0.011688 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
ARECIBO | 2021-12-12 12:42 | 2021-12-12 18:59 | 1 | 006:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN RISER MAL TIEMPO VIENTOS FUERTES | A21121200045 | New_Event | Bad Weather | Include | Include | Weather | 377 | 2021-12-12 | 377 | keep | 0 | Dec | 2021 | 0.00025677 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-12 12:47 | 2021-12-12 14:47 | 100 | 002:00 | P | DESGANCHE | 2 X 100 EN C/L. SE DESGANCHO BAMBUAS | B21121200032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2021-12-12 | 12000 | keep | 0 | Dec | 2021 | 0.0081731 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-12-12 12:57 | 2021-12-12 13:44 | 2 | 000:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | C21121200034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 47 | 2021-12-12 | 94 | keep | 0 | Dec | 2021 | 6.4023e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2021-12-12 12:58 | 2021-12-12 13:37 | 60 | 000:39 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21121200024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 39 | 2021-12-12 | 2340 | keep | 0 | Dec | 2021 | 0.0015938 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2021-12-12 13:01 | 2021-12-12 18:28 | 12 | 005:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BAJANTE SECUNDARIO | M21121200035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 327 | 2021-12-12 | 3924 | keep | 0 | Dec | 2021 | 0.0026726 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-12-12 13:17 | 2021-12-12 16:27 | 10 | 003:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA INFORMA JOURNEYMAN REQUIERE DESGANCHE | A21121200048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2021-12-12 | 1900 | keep | 0 | Dec | 2021 | 0.0012941 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-12-12 13:17 | 2021-12-12 13:18 | 2635 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | C21121200000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-12-12 | 2635 | keep | 0 | Dec | 2021 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2021-12-12 13:18 | 2021-12-12 15:23 | 110 | 002:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | C21121200005 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 125 | 2021-12-12 | 13750 | keep | 0 | Dec | 2021 | 0.0093651 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
VEGA BAJA | 2021-12-12 13:24 | 2021-12-12 13:25 | 2368 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | B21121200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-12 | 2368 | keep | 0 | Dec | 2021 | 0.0016128 | 0.0016128 | Momentary | FALSE | FALSE | Not_TMED_Event | 2368
VEGA BAJA | 2021-12-12 13:24 | 2021-12-12 13:25 | 538 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | B21121200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-12 | 538 | keep | 0 | Dec | 2021 | 0.00036643 | 0.00036643 | Momentary | FALSE | FALSE | Not_TMED_Event | 538
VEGA BAJA | 2021-12-12 13:24 | 2021-12-12 13:25 | 1284 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | B21121200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-12 | 1284 | keep | 0 | Dec | 2021 | 0.00087453 | 0.00087453 | Momentary | FALSE | FALSE | Not_TMED_Event | 1284
SAN JUAN | 2021-12-12 13:26 | 2021-12-12 22:20 | 180 | 008:54 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 2 X 80 Y 2 X 100 EN CORTE DE LINEA TERMINACION AVERIADA | S21121200064 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 534 | 2021-12-12 | 96120 | keep | 0 | Dec | 2021 | 0.065467 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
MAYAGÃœEZ | 2021-12-12 13:33 | 2021-12-13 16:45 | 70 | 027:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 1 X 65 Y 1 X 140 EN DIFERENTES CORTES DE LINEA SE REPARO ALAMBRE PARTIDO Y SE REALIZO DESGANCHE | M21121200036 | New_Event | Wire Down | Include | Include | Equipment | 1632 | 2021-12-12 | 114240 | keep | 0 | Dec | 2021 | 0.077808 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2021-12-12 13:56 | 2021-12-12 16:47 | 15 | 002:51 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA INFORMA JOURNEYMAN NO IDENTIFICO CAUSA | A21121200050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 171 | 2021-12-12 | 2565 | keep | 0 | Dec | 2021 | 0.001747 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-12-12 13:56 | 2021-12-12 16:14 | 35 | 002:18 | P | DESGANCHE | 1 X 65 EN C/L. SE RETIRO RAMA | B21121200042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2021-12-12 | 4830 | keep | 0 | Dec | 2021 | 0.0032897 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2021-12-12 13:59 | 2021-12-12 18:40 | 50 | 004:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21121200051 | New_Event | Bad Weather | Include | Include | Weather | 281 | 2021-12-12 | 14050 | keep | 0 | Dec | 2021 | 0.0095694 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-12-12 14:03 | 2021-12-12 14:04 | 5042 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21121200052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-12 | 5042 | keep | 0 | Dec | 2021 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
ARECIBO | 2021-12-12 14:05 | 2021-12-12 14:06 | 5042 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21121200052 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-12 | 5042 | keep | 0 | Dec | 2021 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
BAYAMON | 2021-12-12 14:13 | 2021-12-13 17:26 | 25 | 027:13 | P | DESGANCHE | 1 X 20 EN C/L SE REALIZO DESGANCHE DE RAMA | S21121200071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1633 | 2021-12-12 | 40825 | keep | 0 | Dec | 2021 | 0.027806 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2021-12-12 14:20 | 2021-12-12 15:26 | 8 | 001:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P21121200021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 66 | 2021-12-12 | 528 | keep | 0 | Dec | 2021 | 0.00035962 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2021-12-12 14:28 | 2021-12-13 10:20 | 4 | 019:52 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A21121200056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1192 | 2021-12-12 | 4768 | keep | 0 | Dec | 2021 | 0.0032475 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2021-12-12 14:29 | 2021-12-12 15:45 | 100 | 001:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | P21121200023 | New_Event | Bad Weather | Include | Include | Weather | 76 | 2021-12-12 | 7600 | keep | 0 | Dec | 2021 | 0.0051763 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2021-12-12 14:44 | 2021-12-12 14:45 | 2216 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21121200049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-12 | 2216 | keep | 0 | Dec | 2021 | 0.0015093 | 0.0015093 | Momentary | FALSE | FALSE | Not_TMED_Event | 2216
CANOVANAS | 2021-12-12 14:51 | 2021-12-12 21:10 | 45 | 006:19 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L NO CAUSA | R21121200027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 379 | 2021-12-12 | 17055 | keep | 0 | Dec | 2021 | 0.011616 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2021-12-12 14:55 | 2021-12-12 19:30 | 60 | 004:35 | P | DESGANCHE | 1 X 50 Y 1 X 30 EN DISTINTOS CORTES DE LINEA. SE REALIZO DESGANCHE | B21121200048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2021-12-12 | 16500 | keep | 0 | Dec | 2021 | 0.011238 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-12-12 15:05 | 2021-12-12 17:26 | 200 | 002:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | M21121200042 | New_Event | Bad Weather | Include | Include | Weather | 141 | 2021-12-12 | 28200 | keep | 0 | Dec | 2021 | 0.019207 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-12-12 15:06 | 2021-12-12 22:21 | 10 | 007:15 | P | CABLE SOTERRADO AVERIADO | 1 X 10 EN XMR CONSTRUYO AEREO PROVICIONAL DEL T-18 AL T-28 | R21121200029 | New_Event | UG Cable Fault | Include | Include | Equipment | 435 | 2021-12-12 | 4350 | keep | 0 | Dec | 2021 | 0.0029628 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-12 15:29 | 2021-12-12 18:44 | 2 | 003:15 | P | OTRAS CAUSAS | 1 X 15 EN XMR. BY-PASS A CT QUEMADO | B21121200052 | New_Event | Other Causes | Include | Include | Other | 195 | 2021-12-12 | 390 | keep | 0 | Dec | 2021 | 0.00026563 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2021-12-12 15:30 | 2021-12-12 16:36 | 14 | 001:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | P21121200033 | New_Event | Bad Weather | Include | Include | Weather | 66 | 2021-12-12 | 924 | keep | 0 | Dec | 2021 | 0.00062933 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CAGUAS | 2021-12-12 15:33 | 2021-12-12 18:27 | 95 | 002:54 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21121200046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2021-12-12 | 16530 | keep | 0 | Dec | 2021 | 0.011259 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
SAN JUAN | 2021-12-12 15:39 | 2021-12-12 15:40 | 3957 | 000:01 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR | S21121200000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2021-12-12 | 3957 | keep | 0 | Dec | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
BAYAMON | 2021-12-12 15:40 | 2021-12-12 18:28 | 55 | 002:48 | P | CABLE SOTERRADO AVERIADO | SE CERRO N\O DEL T-18 AL T-17 Y SE SECCIONALIZO AVERIA NUEVA DE RISER HACIA T-16. QUEDA T-16 FUERA | S21121200011 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 168 | 2021-12-12 | 9240 | keep | 0 | Dec | 2021 | 0.0062933 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
ARECIBO | 2021-12-12 15:50 | 2021-12-13 10:55 | 1 | 019:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA SE CORRIGIO LINEAS PRIMARIA CRUZADA CON TENSOR | A21121200060 | New_Event |  |  | Include | Wildlife | 1145 | 2021-12-12 | 1145 | keep | 0 | Dec | 2021 | 0.00077985 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-12 15:51 | 2021-12-12 15:52 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21121200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-12 | 641 | keep | 0 | Dec | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-12-12 15:51 | 2021-12-12 15:52 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21121200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-12 | 733 | keep | 0 | Dec | 2021 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
CANOVANAS | 2021-12-12 15:53 | 2021-12-12 19:38 | 4 | 003:45 | P | DESGANCHE | 1 X 8 EN XMR DESGANCHE | R21121200031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2021-12-12 | 900 | keep | 0 | Dec | 2021 | 0.00061299 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-12-12 15:55 | 2021-12-12 16:43 | 1 | 000:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | A21121200059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 48 | 2021-12-12 | 48 | keep | 0 | Dec | 2021 | 3.2693e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-12-12 16:00 | 2021-12-12 21:10 | 10 | 005:10 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN XMR Y SE REALIZO DESGANCHE | B21121200055 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 310 | 2021-12-12 | 3100 | keep | 0 | Dec | 2021 | 0.0021114 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-12 16:08 | 2021-12-13 10:03 | 60 | 017:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO CAJA PRIMARIA | B21121200059 | New_Event | Cutout Failure | Include | Include | Equipment | 1075 | 2021-12-12 | 64500 | keep | 0 | Dec | 2021 | 0.043931 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2021-12-12 16:10 | 2021-12-12 17:56 | 50 | 001:46 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO LA CAUSA | P21121200032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2021-12-12 | 5300 | keep | 0 | Dec | 2021 | 0.0036098 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-12 16:11 | 2021-12-13 10:35 | 15 | 018:24 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | S21121200081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1104 | 2021-12-12 | 16560 | keep | 0 | Dec | 2021 | 0.011279 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2021-12-12 16:24 | 2021-12-12 17:11 | 50 | 000:47 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA POR DESGANCHE | P21121200034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 47 | 2021-12-12 | 2350 | keep | 0 | Dec | 2021 | 0.0016006 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-12 16:38 | 2021-12-12 18:23 | 50 | 001:45 | P | DESGANCHE | 1 X 65 EN C/L. SE REALIZO DESGANCHE | S21121200098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2021-12-12 | 5250 | keep | 0 | Dec | 2021 | 0.0035758 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-12-12 16:50 | 2021-12-12 23:11 | 40 | 006:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO ZAFADO EN CORTE DE LINEA | A21121200062 | New_Event | Wire Down | Include | Include | Equipment | 381 | 2021-12-12 | 15240 | keep | 0 | Dec | 2021 | 0.01038 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-12-12 16:58 | 2021-12-12 21:27 | 2999 | 004:29 | S | TRANSFORMADOR AVERIADO | SE ABRIO 0010 PARA REEMPLAZAR PT DE LA BARRA DE SAN GERMAN TC | M21121200075 | Additional_clients | Service Transformer Failure | Include | Include | Equipment | 269 | 2021-12-12 | 806731 | keep | 0 | Dec | 2021 | 0.54946 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-12-12 16:58 | 2021-12-12 21:27 | 1597 | 004:29 | S | TRANSFORMADOR AVERIADO | SE ABRIO 0010 PARA REEMPLAZAR PT DE LA BARRA DE SAN GERMAN TC | M21121200075 | New_Event | Service Transformer Failure | Include | Include | Equipment | 269 | 2021-12-12 | 429593 | keep | 0 | Dec | 2021 | 0.29259 | 0.0010877 | Sustained | FALSE | FALSE | Not_TMED_Event | 1597
HUMACAO | 2021-12-12 16:59 | 2021-12-12 19:16 | 20 | 002:17 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | C21121200048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2021-12-12 | 2740 | keep | 0 | Dec | 2021 | 0.0018662 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-12-12 17:00 | 2021-12-12 17:01 | 1984 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-12 QUE A SU VEZ LLEVA LA CARGA DEL 1911-07 | S21121200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-12 | 1984 | keep | 0 | Dec | 2021 | 0.0013513 | 0.0013513 | Momentary | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2021-12-12 17:00 | 2021-12-12 17:01 | 577 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-12 QUE A SU VEZ LLEVA LA CARGA DEL 1911-07 | S21121200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-12 | 577 | keep | 0 | Dec | 2021 | 0.00039299 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
PONCE | 2021-12-12 17:10 | 2021-12-12 17:30 | 12 | 000:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | P21121200029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 20 | 2021-12-12 | 240 | keep | 0 | Dec | 2021 | 0.00016346 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-12-12 17:12 | 2021-12-14 10:31 | 40 | 041:19 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | S21121200298 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2479 | 2021-12-12 | 99160 | keep | 0 | Dec | 2021 | 0.067537 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-12-12 17:12 | 2021-12-13 11:48 | 80 | 018:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21121200067 | New_Event | Bad Weather | Include | Include | Weather | 1116 | 2021-12-12 | 89280 | keep | 0 | Dec | 2021 | 0.060808 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2021-12-12 17:14 | 2021-12-12 19:23 | 40 | 002:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21121200064 | New_Event | Bad Weather | Include | Include | Weather | 129 | 2021-12-12 | 5160 | keep | 0 | Dec | 2021 | 0.0035145 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2021-12-12 17:37 | 2021-12-12 17:38 | 2286 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21121200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-12 | 2286 | keep | 0 | Dec | 2021 | 0.001557 | 0.001557 | Momentary | FALSE | FALSE | Not_TMED_Event | 2286
PONCE | 2021-12-12 17:50 | 2021-12-12 19:15 | 1 | 001:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN RISER | P21121200035 | New_Event | Wire Down | Include | Include | Equipment | 85 | 2021-12-12 | 85 | keep | 0 | Dec | 2021 | 5.7893e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-12 17:58 | 2021-12-12 20:08 | 12 | 002:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21121200075 | New_Event | Secondary Wire Down | Include | Include | Equipment | 130 | 2021-12-12 | 1560 | keep | 0 | Dec | 2021 | 0.0010625 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-12-12 17:58 | 2021-12-13 10:01 | 100 | 016:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 Y 1 X 30 EN CORTE DE LINEA LLUVIA FUERTE | C21121200049 | New_Event | Bad Weather | Include | Include | Weather | 963 | 2021-12-12 | 96300 | keep | 0 | Dec | 2021 | 0.065589 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2021-12-12 18:12 | 2021-12-13 10:48 | 3 | 016:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO PEDESTAL SECUNDARIO | R21121300006 | New_Event | Secondary Wire Down | Include | Include | Equipment | 996 | 2021-12-12 | 2988 | keep | 0 | Dec | 2021 | 0.0020351 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-12-12 18:27 | 2021-12-12 22:38 | 50 | 004:11 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE ENCONTRO ARBOL EN EL SUELO QUE CRUZO LAS LINEAS AL CAER | B21121200068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2021-12-12 | 12550 | keep | 0 | Dec | 2021 | 0.0085477 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-12-12 18:27 | 2021-12-13 12:37 | 40 | 018:10 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P21121200037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1090 | 2021-12-12 | 43600 | keep | 0 | Dec | 2021 | 0.029696 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-12 18:28 | 2021-12-13 12:28 | 10 | 018:00 | P | CABLE SOTERRADO AVERIADO | SE REPARO AVERIA SOTERRADA DE RISER @ T-16 | S21121200011 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1080 | 2021-12-12 | 10800 | keep | 0 | Dec | 2021 | 0.0073558 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-12-12 18:59 | 2021-12-13 12:23 | 4 | 017:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA AVERIADA | C21121200054 | New_Event | Cutout Failure | Include | Include | Equipment | 1044 | 2021-12-12 | 4176 | keep | 0 | Dec | 2021 | 0.0028443 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-12-12 19:00 | 2021-12-13 01:11 | 50 | 006:11 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21121200095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 371 | 2021-12-12 | 18550 | keep | 0 | Dec | 2021 | 0.012634 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-12 19:10 | 2021-12-12 19:11 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO EL 1909-08 LLEVANDO LA CARGA DEL 1907-05 | B21121200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-12 | 2435 | keep | 0 | Dec | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-12-12 19:10 | 2021-12-12 19:11 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO EL 1909-08 LLEVANDO LA CARGA DEL 1907-05 | B21121200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-12 | 2956 | keep | 0 | Dec | 2021 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2021-12-12 19:11 | 2021-12-13 01:31 | 80 | 006:20 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S21121200108 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 380 | 2021-12-12 | 30400 | keep | 0 | Dec | 2021 | 0.020705 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2021-12-12 19:36 | 2021-12-13 14:22 | 60 | 018:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A21121200070 | New_Event | Cutout Failure | Include | Include | Equipment | 1126 | 2021-12-12 | 67560 | keep | 0 | Dec | 2021 | 0.046015 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-12-12 19:42 | 2021-12-12 21:45 | 15 | 002:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BARRAS DE PEDESTAL | S21121200091 | New_Event | Secondary Wire Down | Include | Include | Equipment | 123 | 2021-12-12 | 1845 | keep | 0 | Dec | 2021 | 0.0012566 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-12-12 19:54 | 2021-12-12 21:11 | 80 | 001:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA POR BOMBA DE HELIO | M21121200098 | New_Event |  |  | Include | Wildlife | 77 | 2021-12-12 | 6160 | keep | 0 | Dec | 2021 | 0.0041955 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2021-12-12 19:57 | 2021-12-12 22:39 | 50 | 002:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN C/L MAL TIEMO | R21121200038 | New_Event | Bad Weather | Include | Include | Weather | 162 | 2021-12-12 | 8100 | keep | 0 | Dec | 2021 | 0.0055169 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-12-12 20:23 | 2021-12-13 17:30 | 40 | 021:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO PUENTE ABIERTO | M21121200105 | New_Event | Wire Down | Include | Include | Equipment | 1267 | 2021-12-12 | 50680 | keep | 0 | Dec | 2021 | 0.034518 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-12-12 20:32 | 2021-12-13 12:57 | 39 | 016:25 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | R21121200040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 985 | 2021-12-12 | 38415 | keep | 0 | Dec | 2021 | 0.026164 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
SAN JUAN | 2021-12-12 20:42 | 2021-12-13 01:47 | 75 | 005:05 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21121200106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 305 | 2021-12-12 | 22875 | keep | 0 | Dec | 2021 | 0.01558 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2021-12-12 20:43 | 2021-12-13 00:46 | 4607 | 004:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO LINEA PRIMARIA ROTA Y SE CERRO EL INTERRUPTOR | A21121200072 | New_Event | Wire Down | Include | Include | Equipment | 243 | 2021-12-12 | 1119501 | keep | 0 | Dec | 2021 | 0.76249 | 0.0031378 | Sustained | FALSE | FALSE | Not_TMED_Event | 4607
MAYAGÃœEZ | 2021-12-12 20:50 | 2021-12-13 09:23 | 130 | 012:33 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21121200113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 753 | 2021-12-12 | 97890 | keep | 0 | Dec | 2021 | 0.066672 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
UTUADO | 2021-12-12 20:50 | 2021-12-13 10:12 | 60 | 013:22 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A21121200076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 802 | 2021-12-12 | 48120 | keep | 0 | Dec | 2021 | 0.032774 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-12-12 21:00 | 2021-12-12 21:01 | 3431 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21121200087 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-12-12 | 3431 | keep | 0 | Dec | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2021-12-12 21:01 | 2021-12-12 22:48 | 200 | 001:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA Y VIENTO | A21121200089 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 107 | 2021-12-12 | 21400 | keep | 0 | Dec | 2021 | 0.014575 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-12-12 21:32 | 2021-12-12 21:33 | 485 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1404-09 QUE A SU VEZ LLEVA LA CARGA DEL 1420-05 | S21121200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-12 | 485 | keep | 0 | Dec | 2021 | 0.00033033 | 0.00033033 | Momentary | FALSE | FALSE | Not_TMED_Event | 485
SAN JUAN | 2021-12-12 21:32 | 2021-12-12 21:33 | 4 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1404-09 QUE A SU VEZ LLEVA LA CARGA DEL 1420-05 | S21121200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-12 | 4 | keep | 0 | Dec | 2021 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-12-12 21:37 | 2021-12-13 11:13 | 45 | 013:36 | P | NO SE REPORTO CAUSA | 1 X 40 Y 1 X 30 EN C/L | B21121200082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 816 | 2021-12-12 | 36720 | keep | 0 | Dec | 2021 | 0.02501 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2021-12-12 21:54 | 2021-12-13 09:05 | 50 | 011:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIAS | C21121200061 | New_Event | Bad Weather | Include | Include | Weather | 671 | 2021-12-12 | 33550 | keep | 0 | Dec | 2021 | 0.022851 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-12-12 22:20 | 2021-12-12 22:24 | 2422 | 000:04 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | INTERRUPTOR DISPARO, SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL | S21121200000 | Additional_clients | UG - Broken Splice / Terminal | Include | Include | Equipment | 4 | 2021-12-12 | 9688 | keep | 0 | Dec | 2021 | 0.0065985 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-12 22:24 | 2021-12-13 11:35 | 180 | 013:11 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 2 X 80 Y 2 X 100 EN CORTE DE LINEA TERMINACION AVERIADA | S21121200064 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 791 | 2021-12-12 | 142380 | keep | 0 | Dec | 2021 | 0.096974 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
CANOVANAS | 2021-12-12 22:27 | 2021-12-13 00:44 | 80 | 002:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN C/L RETEZO LINEAS | R21121200042 | New_Event | Wire Down | Include | Include | Equipment | 137 | 2021-12-12 | 10960 | keep | 0 | Dec | 2021 | 0.0074648 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2021-12-12 22:53 | 2021-12-13 10:34 | 60 | 011:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIAS | R21121200045 | New_Event | Bad Weather | Include | Include | Weather | 701 | 2021-12-12 | 42060 | keep | 0 | Dec | 2021 | 0.028647 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2021-12-12 23:07 | 2021-12-13 17:10 | 10 | 018:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B21121200086 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1083 | 2021-12-12 | 10830 | keep | 0 | Dec | 2021 | 0.0073763 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-12 23:14 | 2021-12-12 23:15 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21121200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-12 | 3941 | keep | 0 | Dec | 2021 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
FAJARDO | 2021-12-12 23:47 | 2021-12-13 10:05 | 4 | 010:18 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | R21121200047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 618 | 2021-12-12 | 2472 | keep | 0 | Dec | 2021 | 0.0016837 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
GUAYAMA | 2021-12-13 00:31 | 2021-12-13 09:40 | 150 | 009:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO | P21121300016 | New_Event | Wire Down | Include | Include | Equipment | 549 | 2021-12-13 | 82350 | keep | 0 | Dec | 2021 | 0.056088 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2021-12-13 00:46 | 2021-12-13 04:39 | 2300 | 003:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE CERRO LOS MACHETES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR LA AVERIA | A21121200072 | Partial_restoration | Wire Down | Include | Include | Equipment | 233 | 2021-12-13 | 535900 | keep | 0 | Dec | 2021 | 0.365 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-12-13 00:57 | 2021-12-13 00:58 | 2092 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C21121300001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-13 | 2092 | keep | 0 | Dec | 2021 | 0.0014249 | 0.0014249 | Momentary | FALSE | FALSE | Not_TMED_Event | 2092
BAYAMON | 2021-12-13 01:31 | 2021-12-13 01:33 | 2435 | 000:02 | T | NO SE REPORTO CAUSA | CARGA TRANSFERIDA AL 1909-08 DISPARO Y SE CERRO POR CONTROL | S21121300003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-13 | 4870 | keep | 0 | Dec | 2021 | 0.0033169 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-12-13 01:31 | 2021-12-13 01:33 | 2956 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA LA CARGA DEL 1907-05 | S21121300003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-13 | 5912 | keep | 0 | Dec | 2021 | 0.0040266 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2021-12-13 01:33 | 2021-12-13 09:45 | 80 | 008:12 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S21121200108 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 492 | 2021-12-13 | 39360 | keep | 0 | Dec | 2021 | 0.026808 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2021-12-13 01:49 | 2021-12-13 01:50 | 2216 | 000:01 | T | NO SE REPORTO CAUSA | INTERRUPTOR DISPARO Y SE CERRO POR CONTROL | B21121300003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-13 | 2216 | keep | 0 | Dec | 2021 | 0.0015093 | 0.0015093 | Momentary | FALSE | FALSE | Not_TMED_Event | 2216
VEGA BAJA | 2021-12-13 01:51 | 2021-12-13 09:03 | 31 | 007:12 | T | PROTECCION DEFECTUOSA | PROBLEMAS CON BUCHHOLZ | B21121300000 | New_Event | Protection Miscoordination | Include | Include | Other | 432 | 2021-12-13 | 13392 | keep | 0 | Dec | 2021 | 0.0091212 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
BAYAMON | 2021-12-13 01:51 | 2021-12-13 09:03 | 1859 | 007:12 | S | PROTECCION DEFECTUOSA | SUB. LOCK OUT PROBLEMAS CON BUCHHOLZ SE CORRIGIO Y SE ENERGIZO XMR | B21121300000 | New_Event | Protection Miscoordination | Include | Include | Other | 432 | 2021-12-13 | 803088 | keep | 0 | Dec | 2021 | 0.54698 | 0.0012662 | Sustained | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2021-12-13 01:51 | 2021-12-13 09:03 | 7 | 007:12 | S | PROTECCION DEFECTUOSA | SUB. LOCK OUT PROBLEMAS CON BUCHHOLZ SE CORRIGIO Y SE ENERGIZO XMR | B21121300000 | New_Event | Protection Miscoordination | Include | Include | Other | 432 | 2021-12-13 | 3024 | keep | 0 | Dec | 2021 | 0.0020596 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-12-13 02:21 | 2021-12-13 02:22 | 4622 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21121300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-13 | 4622 | keep | 0 | Dec | 2021 | 0.003148 | 0.003148 | Momentary | FALSE | FALSE | Not_TMED_Event | 4622
SAN JUAN | 2021-12-13 05:12 | 2021-12-13 11:22 | 225 | 006:10 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA CARGA POR EL 1303-05 | S21121300000 | New_Event | Wire Down | Include | Include | Equipment | 370 | 2021-12-13 | 83250 | keep | 0 | Dec | 2021 | 0.056701 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-12-13 05:12 | 2021-12-13 11:22 | 870 | 006:10 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA LLEVA 1303-04 | S21121300000 | New_Event | Wire Down | Include | Include | Equipment | 370 | 2021-12-13 | 321900 | keep | 0 | Dec | 2021 | 0.21924 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
MAYAGÃœEZ | 2021-12-13 05:30 | 2021-12-13 13:57 | 15 | 008:27 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR POSTE PARTIDO | M21121300002 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 507 | 2021-12-13 | 7605 | keep | 0 | Dec | 2021 | 0.0051797 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-12-13 06:16 | 2021-12-13 08:08 | 60 | 001:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REMPLAZO CAJA PRIMARIA | B21121300071 | New_Event | Cutout Failure | Include | Include | Equipment | 112 | 2021-12-13 | 6720 | keep | 0 | Dec | 2021 | 0.004577 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-12-13 06:17 | 2021-12-13 12:12 | 200 | 005:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21121300012 | New_Event | Bad Weather | Include | Include | Weather | 355 | 2021-12-13 | 71000 | keep | 0 | Dec | 2021 | 0.048358 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-12-13 06:32 | 2021-12-13 06:33 | 1647 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21121300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-13 | 1647 | keep | 0 | Dec | 2021 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
AGUADILLA | 2021-12-13 06:36 | 2021-12-13 06:37 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21121300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-13 | 1192 | keep | 0 | Dec | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
GUAYAMA | 2021-12-13 06:44 | 2021-12-13 08:20 | 125 | 001:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA PAJARO CRUZO FASE | P21121300019 | New_Event |  |  | Include | Wildlife | 96 | 2021-12-13 | 12000 | keep | 0 | Dec | 2021 | 0.0081731 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2021-12-13 07:34 | 2021-12-13 16:55 | 35 | 009:21 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 65 EN RISER Y SE REEMPLAZO TERMINACION | S21121300044 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 561 | 2021-12-13 | 19635 | keep | 0 | Dec | 2021 | 0.013373 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2021-12-13 07:42 | 2021-12-13 13:29 | 293 | 005:47 | S | LINEA DE TRANSMISION 38KV | SE ELIMINO NEUTRAL CRUZADO DE LINEA 4300 | S21121300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 347 | 2021-12-13 | 101671 | keep | 0 | Dec | 2021 | 0.069248 | 0.00019956 | Sustained | FALSE | FALSE | Not_TMED_Event | 293
BAYAMON | 2021-12-13 07:42 | 2021-12-13 13:29 | 315 | 005:47 | S | LINEA DE TRANSMISION 38KV | SE ELIMINO NEUTRAL CRUZADO DE LINEA 4300 | S21121300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 347 | 2021-12-13 | 109305 | keep | 0 | Dec | 2021 | 0.074447 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
BAYAMON | 2021-12-13 07:42 | 2021-12-13 13:29 | 216 | 005:47 | S | LINEA DE TRANSMISION 38KV | SE ELIMINO NEUTRAL CRUZADO DE LINEA 4300 | S21121300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 347 | 2021-12-13 | 74952 | keep | 0 | Dec | 2021 | 0.051049 | 0.00014712 | Sustained | FALSE | FALSE | Not_TMED_Event | 216
BAYAMON | 2021-12-13 07:42 | 2021-12-13 13:29 | 1310 | 005:47 | S | LINEA DE TRANSMISION 38KV | SE ELIMINO NEUTRAL CRUZADO DE LINEA 4300 | S21121300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 347 | 2021-12-13 | 454570 | keep | 0 | Dec | 2021 | 0.30961 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
ARECIBO | 2021-12-13 07:45 | 2021-12-13 18:50 | 50 | 011:05 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 25 EN CONVERTIDOR MAL TIEMPO VIENTOS FUERTES | A21121300016 | New_Event | Bad Weather | Include | Include | Weather | 665 | 2021-12-13 | 33250 | keep | 0 | Dec | 2021 | 0.022646 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-12-13 07:50 | 2021-12-13 09:27 | 3 | 001:37 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | C21121300007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2021-12-13 | 291 | keep | 0 | Dec | 2021 | 0.0001982 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-12-13 07:58 | 2021-12-14 10:31 | 20 | 026:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA EN RISER | B21121300054 | New_Event | Cutout Failure | Include | Include | Equipment | 1593 | 2021-12-13 | 31860 | keep | 0 | Dec | 2021 | 0.0217 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-12-13 08:00 | 2021-12-13 11:45 | 1 | 003:45 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA INFORMA JOURNEYMAN NO IDENTIFICO CAUSA | M21121300010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 225 | 2021-12-13 | 225 | keep | 0 | Dec | 2021 | 0.00015325 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-12-13 08:04 | 2021-12-13 08:05 | 2926 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21121300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-13 | 2926 | keep | 0 | Dec | 2021 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
BAYAMON | 2021-12-13 08:08 | 2021-12-13 08:09 | 3871 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | B21121300000 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2021-12-13 | 3871 | keep | 0 | Dec | 2021 | 0.0026365 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-13 08:09 | 2021-12-13 10:29 | 60 | 002:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REMPLAZO CAJA PRIMARIA | B21121300071 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 140 | 2021-12-13 | 8400 | keep | 0 | Dec | 2021 | 0.0057212 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2021-12-13 08:15 | 2021-12-13 21:58 | 50 | 013:43 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21121300058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 823 | 2021-12-13 | 41150 | keep | 0 | Dec | 2021 | 0.028027 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-13 08:21 | 2021-12-13 08:22 | 3438 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | B21121300000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-12-13 | 3438 | keep | 0 | Dec | 2021 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
BAYAMON | 2021-12-13 08:22 | 2021-12-13 19:56 | 30 | 011:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN C/L, DESGANCHE Y SE REEMPLAZO CAJA QUEMADA | B21121300066 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 694 | 2021-12-13 | 20820 | keep | 0 | Dec | 2021 | 0.01418 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-12-13 08:23 | 2021-12-13 10:04 | 2 | 001:41 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 Y 1 X10 EN CORTES DE LINEA Y TRANSFORMADOR LLUVIAS | C21121300008 | New_Event | Bad Weather | Include | Include | Weather | 101 | 2021-12-13 | 202 | keep | 0 | Dec | 2021 | 0.00013758 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2021-12-13 08:25 | 2021-12-13 13:05 | 2 | 004:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO CONECTORES QUEMADOS | C21121300010 | New_Event | Secondary Wire Down | Include | Include | Equipment | 280 | 2021-12-13 | 560 | keep | 0 | Dec | 2021 | 0.00038141 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2021-12-13 08:36 | 2021-12-13 08:45 | 2216 | 000:09 | T | NO SE REPORTO CAUSA | DISPARO DE BREAKER SE CERRO POR SCADA | B21121300071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2021-12-13 | 19944 | keep | 0 | Dec | 2021 | 0.013584 | 0.0015093 | Sustained | FALSE | FALSE | Not_TMED_Event | 2216
PONCE | 2021-12-13 08:46 | 2021-12-13 08:47 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21121300028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-13 | 2113 | keep | 0 | Dec | 2021 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
YAUCO | 2021-12-13 08:48 | 2021-12-13 08:49 | 661 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21121300030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-13 | 661 | keep | 0 | Dec | 2021 | 0.0004502 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
HUMACAO | 2021-12-13 08:51 | 2021-12-13 11:09 | 100 | 002:18 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21121300015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2021-12-13 | 13800 | keep | 0 | Dec | 2021 | 0.0093991 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2021-12-13 08:56 | 2021-12-13 08:57 | 661 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21121300032 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-13 | 661 | keep | 0 | Dec | 2021 | 0.0004502 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
BAYAMON | 2021-12-13 08:56 | 2021-12-13 13:21 | 10 | 004:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO XMR Y SE CERRO PUENTE DE LINEA A CAJA DE XMR | B21121300109 | New_Event | Wire Down | Include | Include | Equipment | 265 | 2021-12-13 | 2650 | keep | 0 | Dec | 2021 | 0.0018049 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-13 08:59 | 2021-12-13 16:03 | 20 | 007:04 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21121300074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 424 | 2021-12-13 | 8480 | keep | 0 | Dec | 2021 | 0.0057757 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-12-13 09:03 | 2021-12-13 11:00 | 31 | 001:57 | T | DESGANCHE | SE REALIZO DESGANCHE MEDIANTE GOI BY-211213-01 Y SE CERRARON MACHETES | B21121300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2021-12-13 | 3627 | keep | 0 | Dec | 2021 | 0.0024703 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
CAGUAS | 2021-12-13 09:06 | 2021-12-13 10:42 | 1 | 001:36 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR SE INSPECCIONO | C21121300017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2021-12-13 | 96 | keep | 0 | Dec | 2021 | 6.5385e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-13 09:09 | 2021-12-13 14:31 | 100 | 005:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M21121300026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 322 | 2021-12-13 | 32200 | keep | 0 | Dec | 2021 | 0.021931 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-12-13 09:10 | 2021-12-13 09:11 | 781 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 60% POR EL 1206-04 | S21121300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-13 | 781 | keep | 0 | Dec | 2021 | 0.00053194 | 0.00053194 | Momentary | FALSE | FALSE | Not_TMED_Event | 781
SAN JUAN | 2021-12-13 09:10 | 2021-12-13 09:11 | 2200 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INETRRUPTOR 40% POR EL 1206-04 | S21121300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-13 | 2200 | keep | 0 | Dec | 2021 | 0.0014984 | 0.0014984 | Momentary | FALSE | FALSE | Not_TMED_Event | 2200
SAN JUAN | 2021-12-13 09:10 | 2021-12-13 09:11 | 1799 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 40% 1204-04 Y 605 1204-03 | S21121300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-13 | 1799 | keep | 0 | Dec | 2021 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
MAYAGÃœEZ | 2021-12-13 09:10 | 2021-12-13 09:11 | 2999 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21121300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-13 | 2999 | keep | 0 | Dec | 2021 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
SAN JUAN | 2021-12-13 09:12 | 2021-12-13 09:13 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-03 LLEVANDO CARGA DE 1204-05 | S21121300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-13 | 10211 | keep | 0 | Dec | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-12-13 09:12 | 2021-12-13 09:13 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-03 LLEVA 1204-05 | S21121300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-13 | 4133 | keep | 0 | Dec | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
MAYAGÃœEZ | 2021-12-13 09:12 | 2021-12-13 11:30 | 30 | 002:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M21121300027 | New_Event | Cutout Failure | Include | Include | Equipment | 138 | 2021-12-13 | 4140 | keep | 0 | Dec | 2021 | 0.0028197 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-12-13 09:13 | 2021-12-13 09:17 | 512 | 000:04 | P | NO SE REPORTO CAUSA | SE CERRO POR SCADA 20% CARGA POR EL 1118-10 | S21121300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-12-13 | 2048 | keep | 0 | Dec | 2021 | 0.0013949 | 0.00034872 | Momentary | FALSE | FALSE | Not_TMED_Event | 512
SAN JUAN | 2021-12-13 09:13 | 2021-12-13 09:17 | 2782 | 000:04 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA 20% 1111-01 | S21121300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-12-13 | 11128 | keep | 0 | Dec | 2021 | 0.0075792 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
AGUADILLA | 2021-12-13 09:13 | 2021-12-13 16:20 | 70 | 007:07 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M21121300029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 427 | 2021-12-13 | 29890 | keep | 0 | Dec | 2021 | 0.020358 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2021-12-13 09:15 | 2021-12-13 14:55 | 11 | 005:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN XMR CRUCE POR CULEBRA | C21121300019 | New_Event |  |  | Include | Wildlife | 340 | 2021-12-13 | 3740 | keep | 0 | Dec | 2021 | 0.0025473 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
ARECIBO | 2021-12-13 09:15 | 2021-12-13 10:06 | 10 | 000:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21121300014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 51 | 2021-12-13 | 510 | keep | 0 | Dec | 2021 | 0.00034736 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-13 09:21 | 2021-12-13 09:22 | 1227 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21121300067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-13 | 1227 | keep | 0 | Dec | 2021 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
VEGA BAJA | 2021-12-13 09:21 | 2021-12-13 09:22 | 1859 | 000:01 | T | OTRAS CAUSAS | RECIERRE DEL 9207-08 QUE LLEVA 9207-09 | B21121300000 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-12-13 | 1859 | keep | 0 | Dec | 2021 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2021-12-13 09:21 | 2021-12-13 09:22 | 7 | 000:01 | T | OTRAS CAUSAS | RECIERRE DEL 9207-08 QUE LLEVA 9207-09 | B21121300000 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-12-13 | 7 | keep | 0 | Dec | 2021 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2021-12-13 09:22 | 2021-12-13 12:53 | 200 | 003:31 | P | OTRAS CAUSAS | 2 X 100 EN CORTE DE LINEA SE DEJO ESCUELA FUERA(PROA) | B21121300259 | 1st_after_momentary | Other Causes | Include | Include | Other | 211 | 2021-12-13 | 42200 | keep | 0 | Dec | 2021 | 0.028742 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-12-13 09:26 | 2021-12-13 17:55 | 60 | 008:29 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | M21121300040 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 509 | 2021-12-13 | 30540 | keep | 0 | Dec | 2021 | 0.020801 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-12-13 09:26 | 2021-12-13 12:15 | 1 | 002:49 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | M21121300039 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 169 | 2021-12-13 | 169 | keep | 0 | Dec | 2021 | 0.00011511 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2021-12-13 09:30 | 2021-12-13 11:33 | 20 | 002:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RETEZO LINEA ARRIADA | C21121300021 | New_Event | Wire Down | Include | Include | Equipment | 123 | 2021-12-13 | 2460 | keep | 0 | Dec | 2021 | 0.0016755 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-12-13 09:31 | 2021-12-13 11:12 | 6 | 001:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO EN PEDESTAL | B21121300008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 101 | 2021-12-13 | 606 | keep | 0 | Dec | 2021 | 0.00041274 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-12-13 09:40 | 2021-12-13 16:36 | 55 | 006:56 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE SECUNDARIO | S21121300108 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 416 | 2021-12-13 | 22880 | keep | 0 | Dec | 2021 | 0.015583 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
VEGA BAJA | 2021-12-13 09:42 | 2021-12-13 12:22 | 6 | 002:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B21121300079 | New_Event | Secondary Wire Down | Include | Include | Equipment | 160 | 2021-12-13 | 960 | keep | 0 | Dec | 2021 | 0.00065385 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-12-13 09:50 | 2021-12-13 11:00 | 10 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZO DE CONEXIONES EN LINEA SECUNDARIA | P21121200036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2021-12-13 | 700 | keep | 0 | Dec | 2021 | 0.00047677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-13 09:52 | 2021-12-13 14:35 | 50 | 004:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M21121300046 | New_Event | Bad Weather | Include | Include | Weather | 283 | 2021-12-13 | 14150 | keep | 0 | Dec | 2021 | 0.0096375 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-13 10:00 | 2021-12-14 11:48 | 30 | 025:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO BAJANTE DE LINEA A CAJA DE C/L | B21121300275 | New_Event | Wire Down | Include | Include | Equipment | 1548 | 2021-12-13 | 46440 | keep | 0 | Dec | 2021 | 0.03163 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2021-12-13 10:04 | 2021-12-15 16:25 | 12 | 054:21 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO AVERIADO ENTRE T-1 Y T-2 Y SE NORMALIZO (VER BITACORA 14-DIC-2021) | B21121300029 | New_Event | UG Cable Fault | Include | Include | Equipment | 3261 | 2021-12-13 | 39132 | keep | 0 | Dec | 2021 | 0.026653 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-12-13 10:08 | 2021-12-13 10:09 | 2999 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21121300047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-13 | 2999 | keep | 0 | Dec | 2021 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
UTUADO | 2021-12-13 10:10 | 2021-12-14 11:00 | 6 | 024:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA. EN OMS SIN SERVICIO DESDE EL DIA 13 | A21121300182 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1490 | 2021-12-13 | 8940 | keep | 0 | Dec | 2021 | 0.006089 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-12-13 10:22 | 2021-12-13 14:15 | 80 | 003:53 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P21121300049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2021-12-13 | 18640 | keep | 0 | Dec | 2021 | 0.012696 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2021-12-13 10:25 | 2021-12-13 10:48 | 25 | 000:23 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L Y 1 X 15 EN XMR | B21121300228 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 23 | 2021-12-13 | 575 | keep | 0 | Dec | 2021 | 0.00039163 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-12-13 10:29 | 2021-12-13 10:30 | 3871 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | B21121300000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-12-13 | 3871 | keep | 0 | Dec | 2021 | 0.0026365 | 0.0026365 | Momentary | FALSE | FALSE | Not_TMED_Event | 3871
BAYAMON | 2021-12-13 10:30 | 2021-12-13 12:54 | 60 | 002:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REMPLAZO CAJA PRIMARIA | B21121300071 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 144 | 2021-12-13 | 8640 | keep | 0 | Dec | 2021 | 0.0058847 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-12-13 10:30 | 2021-12-13 16:01 | 70 | 005:31 | P | NO SE REPORTO CAUSA | 2 X 80 EN C/L | B21121300216 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 331 | 2021-12-13 | 23170 | keep | 0 | Dec | 2021 | 0.015781 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2021-12-13 10:30 | 2021-12-13 11:26 | 1 | 000:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO LINEA HACIA CASA | C21121300027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 56 | 2021-12-13 | 56 | keep | 0 | Dec | 2021 | 3.8141e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-12-13 10:42 | 2021-12-14 15:50 | 6 | 029:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | A21121300199 | New_Event | Wire Down | Include | Include | Equipment | 1748 | 2021-12-13 | 10488 | keep | 0 | Dec | 2021 | 0.0071433 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-12-13 10:50 | 2021-12-13 11:25 | 20 | 000:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIAS | C21121300031 | New_Event | Bad Weather | Include | Include | Weather | 35 | 2021-12-13 | 700 | keep | 0 | Dec | 2021 | 0.00047677 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-12-13 11:00 | 2021-12-13 18:41 | 15 | 007:41 | P | DESGANCHE | SE REALIZO DESGANCHE MEDIANTE GOI BY-211213-01 Y SE CERRARON MACHETES | B21121300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 461 | 2021-12-13 | 6915 | keep | 0 | Dec | 2021 | 0.0047098 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-12-13 11:02 | 2021-12-13 18:08 | 9 | 007:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO NEUTRAL SECUNDARIO ROTO | C21121300033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 426 | 2021-12-13 | 3834 | keep | 0 | Dec | 2021 | 0.0026113 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2021-12-13 11:05 | 2021-12-13 15:00 | 100 | 003:55 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M21121300064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 235 | 2021-12-13 | 23500 | keep | 0 | Dec | 2021 | 0.016006 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-12-13 11:11 | 2021-12-13 16:35 | 30 | 005:24 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO AISLADOR PARTIDO | A21121300117 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 324 | 2021-12-13 | 9720 | keep | 0 | Dec | 2021 | 0.0066202 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-13 11:14 | 2021-12-13 15:17 | 40 | 004:03 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA INFORMA JOURNEYMAN QUE REQUIERE DESGANCHE | A21121300119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2021-12-13 | 9720 | keep | 0 | Dec | 2021 | 0.0066202 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2021-12-13 11:18 | 2021-12-13 13:23 | 19 | 002:05 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR CON DERRAME DE ACEITE DE 37.5 X 37.5KVA | R21121300016 | New_Event | Service Transformer Failure | Include | Include | Equipment | 125 | 2021-12-13 | 2375 | keep | 0 | Dec | 2021 | 0.0016176 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2021-12-13 11:22 | 2021-12-13 11:52 | 100 | 000:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO Y SE CERRARON MACHETES PREVIAMENTE ABIERTO Y SE CONTINUARA PATRULLANDO | S21121300000 | New_Event | Wire Down | Include | Include | Equipment | 30 | 2021-12-13 | 3000 | keep | 0 | Dec | 2021 | 0.0020433 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-12-13 11:22 | 2021-12-13 11:52 | 500 | 000:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO Y SE CERRARON MACHETES PREVIAMENTE ABIERTO Y SE CONTINUARA PATRULLANDO | S21121300000 | New_Event | Wire Down | Include | Include | Equipment | 30 | 2021-12-13 | 15000 | keep | 0 | Dec | 2021 | 0.010216 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
MAYAGÃœEZ | 2021-12-13 11:25 | 2021-12-13 16:50 | 15 | 005:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | M21121300069 | New_Event | Secondary Wire Down | Include | Include | Equipment | 325 | 2021-12-13 | 4875 | keep | 0 | Dec | 2021 | 0.0033203 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-12-13 11:26 | 2021-12-13 13:07 | 3 | 001:41 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | A21121300024 | New_Event | Bad Weather | Include | Include | Weather | 101 | 2021-12-13 | 303 | keep | 0 | Dec | 2021 | 0.00020637 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-12-13 11:28 | 2021-12-14 15:50 | 6 | 028:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS VERIFICADA EN OMS | M21121300067 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1702 | 2021-12-13 | 10212 | keep | 0 | Dec | 2021 | 0.0069553 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-12-13 11:29 | 2021-12-13 13:09 | 1447 | 001:40 | T | ERROR HUMANO | PERSONAL DE CONSERVACION DISPARO LA SUBESTACION POR ERROR CARGA POR EL 1420-01 SE VERIFICO EN SCADA Y SE INFORMA QUE ESTA POR 1420-01 FRENTE A HATO REY GIS | S21121300000 | New_Event | Human Error | Include | Include | Other | 100 | 2021-12-13 | 144700 | keep | 0 | Dec | 2021 | 0.098555 | 0.00098555 | Sustained | FALSE | FALSE | Not_TMED_Event | 1447
SAN JUAN | 2021-12-13 11:29 | 2021-12-13 13:09 | 146 | 001:40 | P | ERROR HUMANO | PERSONAL DE CONSERVACION DISPARO LA SUBESTACION POR ERROR 30% POR EL 1420-04 | S21121300000 | New_Event | Human Error | Include | Include | Other | 100 | 2021-12-13 | 14600 | keep | 0 | Dec | 2021 | 0.009944 | 9.944e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 146
SAN JUAN | 2021-12-13 11:29 | 2021-12-13 13:09 | 1191 | 001:40 | S | ERROR HUMANO | PERSONAL DE CONSERVACION DISPARO LA SUBESTACION POR ERROR LLEVA CARGA DE 1112-04 SE VERIFICO EN SCADA Y SE INFORMA QUE 1420-01 LLEVA 1112-04 FRENTE A HATO REY GIS | S21121300000 | New_Event | Human Error | Include | Include | Other | 100 | 2021-12-13 | 119100 | keep | 0 | Dec | 2021 | 0.081118 | 0.00081118 | Sustained | FALSE | FALSE | Not_TMED_Event | 1191
SAN JUAN | 2021-12-13 11:29 | 2021-12-13 13:09 | 60 | 001:40 | S | ERROR HUMANO | PERSONAL DE CONSERVACION DISPARO LA SUBESTACION POR ERROR LLEVA 10% DEL 1420-03 | S21121300000 | New_Event | Human Error | Include | Include | Other | 100 | 2021-12-13 | 6000 | keep | 0 | Dec | 2021 | 0.0040866 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-12-13 11:29 | 2021-12-13 13:09 | 55 | 001:40 | P | ERROR HUMANO | PERSONAL DE CONSERVACION DISPARO LA SUBESTACION POR ERROR 10% POR EL 1420-02 | S21121300000 | New_Event | Human Error | Include | Include | Other | 100 | 2021-12-13 | 5500 | keep | 0 | Dec | 2021 | 0.003746 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
SAN JUAN | 2021-12-13 11:29 | 2021-12-13 13:09 | 449 | 001:40 | S | ERROR HUMANO | PERSONAL DE CONSERVACION DISPARO LA SUBESTACION POR ERROR LLEVA EL 30% DEL 1404-09 | S21121300000 | New_Event | Human Error | Include | Include | Other | 100 | 2021-12-13 | 44900 | keep | 0 | Dec | 2021 | 0.030581 | 0.00030581 | Sustained | FALSE | FALSE | Not_TMED_Event | 449
YAUCO | 2021-12-13 11:33 | 2021-12-13 15:18 | 1 | 003:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN RISER AVE CRUZO FASE | P21121300054 | New_Event |  |  | Include | Wildlife | 225 | 2021-12-13 | 225 | keep | 0 | Dec | 2021 | 0.00015325 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-12-13 11:33 | 2021-12-13 23:15 | 30 | 011:42 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | B21121300253 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 702 | 2021-12-13 | 21060 | keep | 0 | Dec | 2021 | 0.014344 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-13 11:35 | 2021-12-13 17:39 | 50 | 006:04 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | S21121300175 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 364 | 2021-12-13 | 18200 | keep | 0 | Dec | 2021 | 0.012396 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-12-13 11:37 | 2021-12-13 14:04 | 40 | 002:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA SE RETIRO CULEBRA | R21121300023 | New_Event |  |  | Include | Wildlife | 147 | 2021-12-13 | 5880 | keep | 0 | Dec | 2021 | 0.0040048 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-13 11:38 | 2021-12-13 16:35 | 15 | 004:57 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | S21121300177 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 297 | 2021-12-13 | 4455 | keep | 0 | Dec | 2021 | 0.0030343 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2021-12-13 11:48 | 2021-12-13 13:20 | 70 | 001:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIAS | C21121300037 | New_Event | Bad Weather | Include | Include | Weather | 92 | 2021-12-13 | 6440 | keep | 0 | Dec | 2021 | 0.0043863 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2021-12-13 11:52 | 2021-12-13 17:30 | 370 | 005:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO EN CARR 176 Y SE CERRO MACHETES | S21121300000 | Partial_restoration | Wire Down | Include | Include | Equipment | 338 | 2021-12-13 | 125060 | keep | 0 | Dec | 2021 | 0.085178 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-12-13 11:57 | 2021-12-13 15:55 | 15 | 003:58 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21121300039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2021-12-13 | 3570 | keep | 0 | Dec | 2021 | 0.0024315 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-12-13 12:00 | 2021-12-14 13:13 | 12 | 025:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE ZAFADO EN TRANSFORMADOR | A21121300132 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1513 | 2021-12-13 | 18156 | keep | 0 | Dec | 2021 | 0.012366 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2021-12-13 12:06 | 2021-12-13 19:30 | 25 | 007:24 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B21121300261 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 444 | 2021-12-13 | 11100 | keep | 0 | Dec | 2021 | 0.0075602 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2021-12-13 12:10 | 2021-12-13 16:26 | 30 | 004:16 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE MASIVO | A21121300020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 256 | 2021-12-13 | 7680 | keep | 0 | Dec | 2021 | 0.0052308 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-12-13 12:13 | 2021-12-13 15:24 | 11 | 003:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO BAJANTE SECUNDARIO EN XMR | C21121300041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 191 | 2021-12-13 | 2101 | keep | 0 | Dec | 2021 | 0.001431 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2021-12-13 12:18 | 2021-12-13 16:15 | 40 | 003:57 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | M21121300077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 237 | 2021-12-13 | 9480 | keep | 0 | Dec | 2021 | 0.0064568 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-12-13 12:20 | 2021-12-13 12:24 | 1681 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-04 LLEVANDO CARGA 1346-06 Y 1303-01 SE CERRO POR SCADA CARGA DE 1303-04 POR 1303-05 | S21121300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-12-13 | 6724 | keep | 0 | Dec | 2021 | 0.0045797 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-12-13 12:20 | 2021-12-13 12:24 | 1598 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-04 LLEVANDO CARGA 1303-01 Y 1346-06 SE CERRO POR SCADA | S21121300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-12-13 | 6392 | keep | 0 | Dec | 2021 | 0.0043536 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
HUMACAO | 2021-12-13 12:27 | 2021-12-13 16:26 | 4 | 003:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR TOMAS EN PEDESTAL | C21121300044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 239 | 2021-12-13 | 956 | keep | 0 | Dec | 2021 | 0.00065113 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-12-13 12:27 | 2021-12-13 16:48 | 2735 | 004:21 | T | NO SE REPORTO CAUSA | SE PATRULLO 9501-02 PERO NO SE ENCONTRO CONDICION APARENTE. BANDERAS FASE A Y FASE C. AL OPERAR FUNDIO FUSIBLE EN LA ALTA DEL TRANSFORMADOR. GOI BY-211213-03 | B21121300422 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 261 | 2021-12-13 | 713835 | keep | 0 | Dec | 2021 | 0.48619 | 0.0018628 | Sustained | FALSE | FALSE | Not_TMED_Event | 2735
HUMACAO | 2021-12-13 12:28 | 2021-12-13 15:13 | 110 | 002:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA REPARO CONDUCTOR ROTO | C21121300098 | New_Event | Wire Down | Include | Include | Equipment | 165 | 2021-12-13 | 18150 | keep | 0 | Dec | 2021 | 0.012362 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
CAGUAS | 2021-12-13 12:28 | 2021-12-13 14:59 | 55 | 002:31 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21121300046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2021-12-13 | 8305 | keep | 0 | Dec | 2021 | 0.0056565 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
HUMACAO | 2021-12-13 12:41 | 2021-12-13 15:11 | 55 | 002:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 140 EN CORTE DE LINEA MAQUINA DE CONSTRUCCION CRUZO LINEAS | C21121300066 | New_Event |  |  | Include | Wildlife | 150 | 2021-12-13 | 8250 | keep | 0 | Dec | 2021 | 0.005619 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
PONCE | 2021-12-13 12:49 | 2021-12-13 14:05 | 40 | 001:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P21121200037 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 76 | 2021-12-13 | 3040 | keep | 0 | Dec | 2021 | 0.0020705 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-13 12:50 | 2021-12-13 13:54 | 35 | 001:04 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B21121300269 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 64 | 2021-12-13 | 2240 | keep | 0 | Dec | 2021 | 0.0015257 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-12-13 12:50 | 2021-12-13 17:20 | 1 | 004:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | M21121300081 | New_Event | Secondary Wire Down | Include | Include | Equipment | 270 | 2021-12-13 | 270 | keep | 0 | Dec | 2021 | 0.0001839 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2021-12-13 12:52 | 2021-12-13 20:11 | 50 | 007:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR PUENTE ABIERTO | C21121300080 | New_Event | Wire Down | Include | Include | Equipment | 439 | 2021-12-13 | 21950 | keep | 0 | Dec | 2021 | 0.01495 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-12-13 12:56 | 2021-12-13 17:25 | 5 | 004:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | M21121300091 | New_Event | Bad Weather | Include | Include | Weather | 269 | 2021-12-13 | 1345 | keep | 0 | Dec | 2021 | 0.00091607 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-12-13 13:02 | 2021-12-13 22:57 | 100 | 009:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21121300093 | New_Event | Bad Weather | Include | Include | Weather | 595 | 2021-12-13 | 59500 | keep | 0 | Dec | 2021 | 0.040525 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-12-13 13:10 | 2021-12-13 13:11 | 2457 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C21121300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-13 | 2457 | keep | 0 | Dec | 2021 | 0.0016735 | 0.0016735 | Momentary | FALSE | FALSE | Not_TMED_Event | 2457
MAYAGÃœEZ | 2021-12-13 13:10 | 2021-12-13 14:25 | 15 | 001:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | M21121300096 | New_Event | Bad Weather | Include | Include | Weather | 75 | 2021-12-13 | 1125 | keep | 0 | Dec | 2021 | 0.00076623 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-12-13 13:19 | 2021-12-13 14:39 | 10 | 001:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO Y REALIZAR DESGANCHE | R21121300002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 80 | 2021-12-13 | 800 | keep | 0 | Dec | 2021 | 0.00054488 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-13 13:21 | 2021-12-13 13:35 | 959 | 000:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21121300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2021-12-13 | 13426 | keep | 0 | Dec | 2021 | 0.0091444 | 0.00065317 | Sustained | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2021-12-13 13:21 | 2021-12-13 13:35 | 1382 | 000:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21121300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2021-12-13 | 19348 | keep | 0 | Dec | 2021 | 0.013178 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2021-12-13 13:21 | 2021-12-13 13:35 | 663 | 000:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21121300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2021-12-13 | 9282 | keep | 0 | Dec | 2021 | 0.0063219 | 0.00045157 | Sustained | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2021-12-13 13:21 | 2021-12-13 13:35 | 1514 | 000:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21121300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2021-12-13 | 21196 | keep | 0 | Dec | 2021 | 0.014436 | 0.0010312 | Sustained | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2021-12-13 13:21 | 2021-12-13 13:35 | 1105 | 000:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21121300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2021-12-13 | 15470 | keep | 0 | Dec | 2021 | 0.010537 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2021-12-13 13:21 | 2021-12-13 13:35 | 4176 | 000:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21121300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2021-12-13 | 58464 | keep | 0 | Dec | 2021 | 0.03982 | 0.0028443 | Sustained | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2021-12-13 13:21 | 2021-12-13 13:35 | 252 | 000:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21121300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2021-12-13 | 3528 | keep | 0 | Dec | 2021 | 0.0024029 | 0.00017164 | Sustained | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2021-12-13 13:21 | 2021-12-13 13:35 | 2147 | 000:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21121300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2021-12-13 | 30058 | keep | 0 | Dec | 2021 | 0.020472 | 0.0014623 | Sustained | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2021-12-13 13:21 | 2021-12-13 13:35 | 2858 | 000:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21121300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2021-12-13 | 40012 | keep | 0 | Dec | 2021 | 0.027252 | 0.0019466 | Sustained | FALSE | FALSE | Not_TMED_Event | 2858
BAYAMON | 2021-12-13 13:35 | 2021-12-13 18:56 | 10 | 005:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO XMR Y SE CERRO PUENTE DE LINEA A CAJA DE XMR | B21121300109 | New_Event | Wire Down | Include | Include | Equipment | 321 | 2021-12-13 | 3210 | keep | 0 | Dec | 2021 | 0.0021863 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-12-13 13:37 | 2021-12-13 14:52 | 80 | 001:15 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21121300093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2021-12-13 | 6000 | keep | 0 | Dec | 2021 | 0.0040866 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-12-13 13:42 | 2021-12-13 17:17 | 80 | 003:35 | P | DESGANCHE | 1 X 100 EN C/L. HAY QUE REALIZAR DESGANCHE DE BAMBUAS | B21121300319 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2021-12-13 | 17200 | keep | 0 | Dec | 2021 | 0.011715 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2021-12-13 13:48 | 2021-12-13 15:33 | 30 | 001:45 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | R21121300044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2021-12-13 | 3150 | keep | 0 | Dec | 2021 | 0.0021455 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-13 14:01 | 2021-12-13 22:44 | 60 | 008:43 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21121300328 | New_Event | Vegetation Contact | Include | Include | Vegetation | 523 | 2021-12-13 | 31380 | keep | 0 | Dec | 2021 | 0.021373 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2021-12-13 14:03 | 2021-12-13 17:01 | 110 | 002:58 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21121300099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2021-12-13 | 19580 | keep | 0 | Dec | 2021 | 0.013336 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
ARECIBO | 2021-12-13 14:14 | 2021-12-13 20:54 | 12 | 006:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A21121300141 | New_Event | Bad Weather | Include | Include | Weather | 400 | 2021-12-13 | 4800 | keep | 0 | Dec | 2021 | 0.0032693 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-12-13 14:15 | 2021-12-14 12:24 | 80 | 022:09 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B21121300330 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1329 | 2021-12-13 | 106320 | keep | 0 | Dec | 2021 | 0.072414 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2021-12-13 14:21 | 2021-12-13 18:50 | 100 | 004:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA AREADA | M21121300113 | New_Event | Wire Down | Include | Include | Equipment | 269 | 2021-12-13 | 26900 | keep | 0 | Dec | 2021 | 0.018321 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2021-12-13 14:24 | 2021-12-13 14:25 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21121300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-13 | 3041 | keep | 0 | Dec | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
ARECIBO | 2021-12-13 14:29 | 2021-12-13 14:30 | 3157 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2200 | A21121300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-13 | 3157 | keep | 0 | Dec | 2021 | 0.0021502 | 0.0021502 | Momentary | FALSE | FALSE | Not_TMED_Event | 3157
ARECIBO | 2021-12-13 14:29 | 2021-12-13 14:30 | 35 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2200 | A21121300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-13 | 35 | keep | 0 | Dec | 2021 | 2.3838e-05 | 2.3838e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2021-12-13 14:29 | 2021-12-13 14:30 | 2916 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2200 | A21121300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-13 | 2916 | keep | 0 | Dec | 2021 | 0.0019861 | 0.0019861 | Momentary | FALSE | FALSE | Not_TMED_Event | 2916
BAYAMON | 2021-12-13 14:31 | 2021-12-13 14:54 | 723 | 000:23 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1711-02 QUE LLEVA LA CARGA DEL 1711-05 A PETICION DEL FOREMAN YORLEIBIS POR SEGURIDAD PARA RETIRAR NEUTRAL ENCIMA DE CAJA DE C/L QUE NO DA SERVICIO A CLIENTES. | B21121300340 | New_Event | Wire Down | Include | Include | Equipment | 23 | 2021-12-13 | 16629 | keep | 0 | Dec | 2021 | 0.011326 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2021-12-13 14:31 | 2021-12-13 14:54 | 1976 | 000:23 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1711-02 QUE LLEVA LA CARGA DEL 1711-05 A PETICION DEL FOREMAN YORLEIBIS POR SEGURIDAD PARA RETIRAR NEUTRAL ENCIMA DE CAJA DE C/L QUE NO DA SERVICIO A CLIENTES. | B21121300340 | New_Event | Wire Down | Include | Include | Equipment | 23 | 2021-12-13 | 45448 | keep | 0 | Dec | 2021 | 0.030954 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
MAYAGÃœEZ | 2021-12-13 14:34 | 2021-12-13 20:47 | 60 | 006:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | M21121300118 | New_Event | Wire Down | Include | Include | Equipment | 373 | 2021-12-13 | 22380 | keep | 0 | Dec | 2021 | 0.015243 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2021-12-13 14:51 | 2021-12-13 16:01 | 100 | 001:10 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | C21121300102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 70 | 2021-12-13 | 7000 | keep | 0 | Dec | 2021 | 0.0047677 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-12-13 14:52 | 2021-12-13 16:28 | 70 | 001:36 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21121300103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2021-12-13 | 6720 | keep | 0 | Dec | 2021 | 0.004577 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2021-12-13 14:57 | 2021-12-13 15:25 | 9 | 000:28 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REEMPLAZAR POSTE SECUNDARIO ROTO | C21121300101 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 28 | 2021-12-13 | 252 | keep | 0 | Dec | 2021 | 0.00017164 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2021-12-13 15:00 | 2021-12-13 19:38 | 100 | 004:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA Y DESCARGAS ELECTRICAS | M21121300126 | New_Event | Bad Weather | Include | Include | Weather | 278 | 2021-12-13 | 27800 | keep | 0 | Dec | 2021 | 0.018934 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-12-13 15:06 | 2021-12-13 15:28 | 10 | 000:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO Y LINEA SECUNDARIA | R21121300015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 22 | 2021-12-13 | 220 | keep | 0 | Dec | 2021 | 0.00014984 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-13 15:11 | 2021-12-13 21:34 | 40 | 006:23 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21211300269 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 383 | 2021-12-13 | 15320 | keep | 0 | Dec | 2021 | 0.010434 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-12-13 15:12 | 2021-12-14 11:39 | 63 | 020:27 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA | C21121300106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1227 | 2021-12-13 | 77301 | keep | 0 | Dec | 2021 | 0.052649 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
VEGA BAJA | 2021-12-13 15:16 | 2021-12-13 17:44 | 35 | 002:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE IDENTIFICO PUENTE ABIERTO EN RAMAL | B21121300375 | New_Event | Wire Down | Include | Include | Equipment | 148 | 2021-12-13 | 5180 | keep | 0 | Dec | 2021 | 0.0035281 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2021-12-13 15:18 | 2021-12-13 17:45 | 10 | 002:27 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21121300270 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 147 | 2021-12-13 | 1470 | keep | 0 | Dec | 2021 | 0.0010012 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-13 15:24 | 2021-12-13 17:48 | 10 | 002:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21121300157 | New_Event | Bad Weather | Include | Include | Weather | 144 | 2021-12-13 | 1440 | keep | 0 | Dec | 2021 | 0.00098078 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-13 15:37 | 2021-12-14 11:24 | 100 | 019:47 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21121300110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1187 | 2021-12-13 | 118700 | keep | 0 | Dec | 2021 | 0.080846 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-12-13 15:44 | 2021-12-13 18:02 | 1 | 002:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | M21121300146 | New_Event | Bad Weather | Include | Include | Weather | 138 | 2021-12-13 | 138 | keep | 0 | Dec | 2021 | 9.3991e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-13 16:07 | 2021-12-13 19:24 | 25 | 003:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21121300281 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2021-12-13 | 4925 | keep | 0 | Dec | 2021 | 0.0033544 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-12-13 16:08 | 2021-12-13 19:51 | 30 | 003:43 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B21121300397 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 223 | 2021-12-13 | 6690 | keep | 0 | Dec | 2021 | 0.0045565 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-12-13 16:09 | 2021-12-13 16:10 | 2999 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | M21121300000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-12-13 | 2999 | keep | 0 | Dec | 2021 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
MAYAGÃœEZ | 2021-12-13 16:10 | 2021-12-13 16:12 | 100 | 000:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ALAMBRE PARTIDO | M21121300000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 2 | 2021-12-13 | 200 | keep | 0 | Dec | 2021 | 0.00013622 | 6.811e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-12-13 16:12 | 2021-12-14 11:40 | 1 | 019:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 40 EN CORTE DE LINEA REEMPLAZARON CAJAS PRIMARIAS | C21121300123 | New_Event | Cutout Failure | Include | Include | Equipment | 1168 | 2021-12-13 | 1168 | keep | 0 | Dec | 2021 | 0.00079552 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-12-13 16:12 | 2021-12-13 16:13 | 1342 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | C21121300118 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-12-13 | 1342 | keep | 0 | Dec | 2021 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
MAYAGÃœEZ | 2021-12-13 16:13 | 2021-12-13 18:19 | 2999 | 002:06 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES PARA SECCIONALIZAR ALAMBRE PARTIDO | M21121300157 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 126 | 2021-12-13 | 377874 | keep | 0 | Dec | 2021 | 0.25737 | 0.0020426 | Sustained | FALSE | FALSE | Not_TMED_Event | 2999
MAYAGÃœEZ | 2021-12-13 16:14 | 2021-12-13 17:30 | 60 | 001:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M21121300158 | New_Event | Bad Weather | Include | Include | Weather | 76 | 2021-12-13 | 4560 | keep | 0 | Dec | 2021 | 0.0031058 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2021-12-13 16:26 | 2021-12-13 16:30 | 1093 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | P21121300081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-12-13 | 4372 | keep | 0 | Dec | 2021 | 0.0029777 | 0.00074444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1093
BAYAMON | 2021-12-13 16:42 | 2021-12-13 16:43 | 3798 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21121300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-13 | 3798 | keep | 0 | Dec | 2021 | 0.0025868 | 0.0025868 | Momentary | FALSE | FALSE | Not_TMED_Event | 3798
YAUCO | 2021-12-13 16:42 | 2021-12-13 18:18 | 3973 | 001:36 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 5602-03 CON CARGA DEL 5602-02 SE NORMALIZO CARGA DE INTERRUPTOR 5602-02 Y SE ABRIO AMARRE CON 5602-03 NO SE REPORTO LA CAUSA | P21121300084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2021-12-13 | 381408 | keep | 0 | Dec | 2021 | 0.25978 | 0.002706 | Sustained | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2021-12-13 16:42 | 2021-12-13 18:02 | 2484 | 001:20 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO SE REPORTO LA CAUSA | P21121300084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 80 | 2021-12-13 | 198720 | keep | 0 | Dec | 2021 | 0.13535 | 0.0016918 | Sustained | FALSE | FALSE | Not_TMED_Event | 2484
BAYAMON | 2021-12-13 16:48 | 2021-12-13 21:25 | 3070 | 004:37 | S | NO SE REPORTO CAUSA | SE PATRULLO 9501-02 PERO NO SE ENCONTRO CONDICION APARENTE. BANDERAS FASE A Y FASE C. AL OPERAR FUNDIO FUSIBLE EN LA ALTA DEL TRANSFORMADOR Y SE RETIRO LA CARGA PARA REEMPLAZARLO. GOI BY-211213-03 | B21121300422 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 277 | 2021-12-13 | 850390 | keep | 0 | Dec | 2021 | 0.5792 | 0.002091 | Sustained | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2021-12-13 16:48 | 2021-12-13 21:16 | 2735 | 004:28 | S | NO SE REPORTO CAUSA | SE PATRULLO 9501-02 PERO NO SE ENCONTRO CONDICION APARENTE. BANDERAS FASE A Y FASE C. AL OPERAR FUNDIO FUSIBLE EN LA ALTA DEL TRANSFORMADOR Y SE RETIRO LA CARGA PARA REEMPLAZARLO. GOI BY-211213-03 | B21121300422 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 268 | 2021-12-13 | 732980 | keep | 0 | Dec | 2021 | 0.49923 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-13 16:48 | 2021-12-13 21:17 | 1070 | 004:29 | S | NO SE REPORTO CAUSA | SE PATRULLO 9501-02 PERO NO SE ENCONTRO CONDICION APARENTE. BANDERAS FASE A Y FASE C. AL OPERAR FUNDIO FUSIBLE EN LA ALTA DEL TRANSFORMADOR Y SE RETIRO LA CARGA PARA REEMPLAZARLO. GOI BY-211213-03 | B21121300422 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 269 | 2021-12-13 | 287830 | keep | 0 | Dec | 2021 | 0.19604 | 0.00072877 | Sustained | FALSE | FALSE | Not_TMED_Event | 1070
CAGUAS | 2021-12-13 16:52 | 2021-12-14 10:53 | 160 | 018:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA CRUCE CON AVE | C21121300126 | New_Event |  |  | Include | Wildlife | 1081 | 2021-12-13 | 172960 | keep | 0 | Dec | 2021 | 0.1178 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
MAYAGÃœEZ | 2021-12-13 16:55 | 2021-12-13 19:14 | 12 | 002:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | M21121300188 | New_Event | Bad Weather | Include | Include | Weather | 139 | 2021-12-13 | 1668 | keep | 0 | Dec | 2021 | 0.0011361 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-12-13 16:56 | 2021-12-14 10:31 | 30 | 017:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21121300173 | New_Event | Bad Weather | Include | Include | Weather | 1055 | 2021-12-13 | 31650 | keep | 0 | Dec | 2021 | 0.021557 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-13 16:57 | 2021-12-13 18:07 | 10 | 001:10 | P | PARARRAYOS DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO PARARRAYO ARQUEANDO | B21121300415 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 70 | 2021-12-13 | 700 | keep | 0 | Dec | 2021 | 0.00047677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-13 17:01 | 2021-12-13 20:50 | 150 | 003:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 50 EN CORTE DE LINEA SE REPARARON LINEAS PRIMARIAS PARTIDAS | A21121300175 | New_Event | Wire Down | Include | Include | Equipment | 229 | 2021-12-13 | 34350 | keep | 0 | Dec | 2021 | 0.023396 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
UTUADO | 2021-12-13 17:06 | 2021-12-13 17:15 | 20 | 000:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21121300177 | New_Event | Bad Weather | Include | Include | Weather | 9 | 2021-12-13 | 180 | keep | 0 | Dec | 2021 | 0.0001226 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-12-13 17:08 | 2021-12-14 10:28 | 100 | 017:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE CON AVE | C21112130133 | New_Event |  |  | Include | Wildlife | 1040 | 2021-12-13 | 104000 | keep | 0 | Dec | 2021 | 0.070834 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-12-13 17:09 | 2021-12-13 19:46 | 60 | 002:37 | P | DESGANCHE | 2 X 80 EN C/L. SE REALIZO DESGANCHE DE BAMBUAS | S21121300295 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2021-12-13 | 9420 | keep | 0 | Dec | 2021 | 0.0064159 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2021-12-13 17:12 | 2021-12-13 21:10 | 40 | 003:58 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M21121300197 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2021-12-13 | 9520 | keep | 0 | Dec | 2021 | 0.006484 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-12-13 17:15 | 2021-12-13 20:45 | 200 | 003:30 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M21121300200 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2021-12-13 | 42000 | keep | 0 | Dec | 2021 | 0.028606 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-12-13 17:19 | 2021-12-13 20:41 | 30 | 003:22 | P | TRANSFORMADOR AVERIADO | 1 X 65 EN CORTE DE LINEA SE SECCIONALIZO TRANSFORMADOR CON BARRAS SECUNDARIAS ROTAS Y FUERTE DERRAME DE ACEITE | R21121300057 | New_Event | Service Transformer Failure | Include | Include | Equipment | 202 | 2021-12-13 | 6060 | keep | 0 | Dec | 2021 | 0.0041274 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-12-13 17:26 | 2021-12-14 13:47 | 80 | 020:21 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21121300301 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1221 | 2021-12-13 | 97680 | keep | 0 | Dec | 2021 | 0.066529 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2021-12-13 17:38 | 2021-12-13 21:05 | 15 | 003:27 | P | NO SE REPORTO CAUSA | 2 X 65 EN RISER @ SU-7 | B21121300438 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 207 | 2021-12-13 | 3105 | keep | 0 | Dec | 2021 | 0.0021148 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-12-13 17:44 | 2021-12-13 18:56 | 100 | 001:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO C/L Y SE CERRO PUENTE ABIERTO | B21121300375 | Additional_clients | Wire Down | Include | Include | Equipment | 72 | 2021-12-13 | 7200 | keep | 0 | Dec | 2021 | 0.0049039 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-12-13 17:49 | 2021-12-13 20:35 | 10 | 002:46 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B21121300440 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 166 | 2021-12-13 | 1660 | keep | 0 | Dec | 2021 | 0.0011306 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-13 18:00 | 2021-12-13 18:30 | 15 | 000:30 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PARARRAYO CRUZADO | M21121300224 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 30 | 2021-12-13 | 450 | keep | 0 | Dec | 2021 | 0.00030649 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-12-13 18:10 | 2021-12-14 11:34 | 35 | 017:24 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B21121300445 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1044 | 2021-12-13 | 36540 | keep | 0 | Dec | 2021 | 0.024887 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2021-12-13 18:15 | 2021-12-14 12:13 | 10 | 017:58 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 50 X 50 KVA | B21121300037 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1078 | 2021-12-13 | 10780 | keep | 0 | Dec | 2021 | 0.0073422 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-13 18:18 | 2021-12-14 12:47 | 50 | 018:29 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 37.5 KVA X 37.5 KVA Y 1 X 25 EN CORTE DE LINEA | A21121300184 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1109 | 2021-12-13 | 55450 | keep | 0 | Dec | 2021 | 0.037767 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-12-13 18:19 | 2021-12-13 20:17 | 100 | 001:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO Y SE CERRO MACHETES | M21121300230 | Partial_restoration | Wire Down | Include | Include | Equipment | 118 | 2021-12-13 | 11800 | keep | 0 | Dec | 2021 | 0.0080369 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-13 18:26 | 2021-12-14 13:47 | 10 | 019:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTE SECUNDARIO | S21121300314 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1161 | 2021-12-13 | 11610 | keep | 0 | Dec | 2021 | 0.0079075 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-13 18:32 | 2021-12-14 12:36 | 1 | 018:04 | P | DESGANCHE | 3 X 15 EN BANCO DE TRANSFORMADORES | C21121300144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1084 | 2021-12-13 | 1084 | keep | 0 | Dec | 2021 | 0.00073831 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-13 18:40 | 2021-12-14 12:56 | 25 | 018:16 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B21121300450 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1096 | 2021-12-13 | 27400 | keep | 0 | Dec | 2021 | 0.018662 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2021-12-13 18:46 | 2021-12-13 20:13 | 10 | 001:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO T-11A @ T-15 PARA LLEVAR A SU LUGAR PM IMPACTADO POR VEHICULO | C21121300107 | New_Event |  |  | Include | Wildlife | 87 | 2021-12-13 | 870 | keep | 0 | Dec | 2021 | 0.00059255 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-12-13 18:53 | 2021-12-14 09:30 | 1 | 014:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | M21121300229 | New_Event | Cutout Failure | Include | Include | Equipment | 877 | 2021-12-13 | 877 | keep | 0 | Dec | 2021 | 0.00059732 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-12-13 18:59 | 2021-12-13 19:13 | 35 | 000:14 | P | DESGANCHE | 1 X 40 EN C/L. SE REALIZO DESGANCHE | B21121300459 | New_Event | Vegetation Contact | Include | Include | Vegetation | 14 | 2021-12-13 | 490 | keep | 0 | Dec | 2021 | 0.00033374 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-12-13 19:03 | 2021-12-14 09:47 | 8 | 014:44 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | M21121300231 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 884 | 2021-12-13 | 7072 | keep | 0 | Dec | 2021 | 0.0048167 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2021-12-13 19:19 | 2021-12-14 10:10 | 4 | 014:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRE PM - 103 PARA REPARAR LINEA SECUNDARIA SOTERRADA PARTIDA POR MAQUINARIA PESADA | P21121300106 | New_Event |  |  | Include | Wildlife | 891 | 2021-12-13 | 3564 | keep | 0 | Dec | 2021 | 0.0024274 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2021-12-13 19:31 | 2021-12-14 16:27 | 17 | 020:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE HACIA CAJA DE XMR | C21121300151 | New_Event | Wire Down | Include | Include | Equipment | 1256 | 2021-12-13 | 21352 | keep | 0 | Dec | 2021 | 0.014543 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
ARECIBO | 2021-12-13 19:38 | 2021-12-14 16:40 | 10 | 021:02 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA X 37.5 KVA | A21121300189 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1262 | 2021-12-13 | 12620 | keep | 0 | Dec | 2021 | 0.0085954 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-13 19:41 | 2021-12-14 14:10 | 10 | 018:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | A21121300190 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1109 | 2021-12-13 | 11090 | keep | 0 | Dec | 2021 | 0.0075533 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-13 19:53 | 2021-12-14 11:09 | 17 | 015:16 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21121300325 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 916 | 2021-12-13 | 15572 | keep | 0 | Dec | 2021 | 0.010606 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
CAGUAS | 2021-12-13 20:05 | 2021-12-14 11:30 | 99 | 015:25 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21121300152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 925 | 2021-12-13 | 91575 | keep | 0 | Dec | 2021 | 0.062371 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
ARECIBO | 2021-12-13 20:07 | 2021-12-13 21:55 | 5042 | 001:48 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO ALIMENTADOR SE CERRO INTERRUPTOR | A21121300191 | New_Event | Wire Down | Include | Include | Equipment | 108 | 2021-12-13 | 544536 | keep | 0 | Dec | 2021 | 0.37088 | 0.0034341 | Sustained | FALSE | FALSE | Not_TMED_Event | 5042
SAN JUAN | 2021-12-13 20:13 | 2021-12-13 21:56 | 80 | 001:43 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21121300330 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 103 | 2021-12-13 | 8240 | keep | 0 | Dec | 2021 | 0.0056122 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2021-12-13 20:15 | 2021-12-14 00:50 | 20 | 004:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA FIJAR BAJANTE SECUNDARIO | P21121300107 | New_Event | Secondary Wire Down | Include | Include | Equipment | 275 | 2021-12-13 | 5500 | keep | 0 | Dec | 2021 | 0.003746 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2021-12-13 20:15 | 2021-12-14 11:17 | 4 | 015:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21121300237 | New_Event | Bad Weather | Include | Include | Weather | 902 | 2021-12-13 | 3608 | keep | 0 | Dec | 2021 | 0.0024574 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-12-13 20:19 | 2021-12-14 14:45 | 30 | 018:26 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21121300193 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1106 | 2021-12-13 | 33180 | keep | 0 | Dec | 2021 | 0.022599 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-12-13 20:30 | 2021-12-13 21:38 | 4 | 001:08 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | S21121300334 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 68 | 2021-12-13 | 272 | keep | 0 | Dec | 2021 | 0.00018526 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2021-12-13 20:40 | 2021-12-14 09:42 | 40 | 013:02 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE REPORTO CAUSA | P21121300109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 782 | 2021-12-13 | 31280 | keep | 0 | Dec | 2021 | 0.021305 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-12-13 20:46 | 2021-12-14 11:06 | 39 | 014:20 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 75 X 100 KVA QUEMADO | R21121300061 | New_Event | Service Transformer Failure | Include | Include | Equipment | 860 | 2021-12-13 | 33540 | keep | 0 | Dec | 2021 | 0.022844 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
ARECIBO | 2021-12-13 21:00 | 2021-12-13 21:01 | 1 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2600 | A21121300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-13 | 1 | keep | 0 | Dec | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-12-13 21:00 | 2021-12-13 21:01 | 2266 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2600 | A21121300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-13 | 2266 | keep | 0 | Dec | 2021 | 0.0015434 | 0.0015434 | Momentary | FALSE | FALSE | Not_TMED_Event | 2266
ARECIBO | 2021-12-13 21:00 | 2021-12-13 21:01 | 1399 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2600 | A21121300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-13 | 1399 | keep | 0 | Dec | 2021 | 0.00095285 | 0.00095285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1399
SAN JUAN | 2021-12-13 21:03 | 2021-12-13 21:59 | 10 | 000:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | R21121300056 | New_Event | Secondary Wire Down | Include | Include | Equipment | 56 | 2021-12-13 | 560 | keep | 0 | Dec | 2021 | 0.00038141 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-12-13 21:03 | 2021-12-13 23:14 | 30 | 002:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA, PARARRAYO Y AISLADOR | R21121300062 | New_Event | Cutout Failure | Include | Include | Equipment | 131 | 2021-12-13 | 3930 | keep | 0 | Dec | 2021 | 0.0026767 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-12-13 21:08 | 2021-12-13 23:08 | 50 | 002:00 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU-3 | S21121300336 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2021-12-13 | 6000 | keep | 0 | Dec | 2021 | 0.0040866 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-13 21:29 | 2021-12-14 10:11 | 100 | 012:42 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21121300338 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 762 | 2021-12-13 | 76200 | keep | 0 | Dec | 2021 | 0.051899 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-12-13 21:39 | 2021-12-13 21:40 | 2126 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C21121300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-13 | 2126 | keep | 0 | Dec | 2021 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
ARECIBO | 2021-12-13 21:55 | 2021-12-14 14:32 | 4500 | 016:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO PUENTES Y SE CERRO MACHETES PARA MINIMIZAR CLIENTES SIN SERVICIO | A21121300200 | Partial_restoration | Wire Down | Include | Include | Equipment | 997 | 2021-12-13 | 4486500 | keep | 0 | Dec | 2021 | 3.0557 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-12-13 22:09 | 2021-12-14 10:42 | 30 | 012:33 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21121300468 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 753 | 2021-12-13 | 22590 | keep | 0 | Dec | 2021 | 0.015386 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2021-12-13 22:11 | 2021-12-14 08:59 | 100 | 010:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO EN RISER | R21121300067 | New_Event | Wire Down | Include | Include | Equipment | 648 | 2021-12-13 | 64800 | keep | 0 | Dec | 2021 | 0.044135 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2021-12-13 22:31 | 2021-12-15 18:06 | 40 | 043:35 | P | ESTRUCTURA AVERIADA | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE REEMPLAZO POSTE PRIMARIO PARTIDO | C21121300159 | New_Event | Defective Pole | Include | Include | Equipment | 2615 | 2021-12-13 | 104600 | keep | 0 | Dec | 2021 | 0.071243 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-12-13 22:39 | 2021-12-14 09:26 | 100 | 010:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21121300202 | New_Event | Bad Weather | Include | Include | Weather | 647 | 2021-12-13 | 64700 | keep | 0 | Dec | 2021 | 0.044067 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-12-13 23:09 | 2021-12-13 23:11 | 2900 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C21121300160 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-13 | 5800 | keep | 0 | Dec | 2021 | 0.0039504 | 0.0019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 2900
BAYAMON | 2021-12-13 23:26 | 2021-12-14 04:20 | 1984 | 004:54 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA | S21121300343 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 294 | 2021-12-13 | 583296 | keep | 0 | Dec | 2021 | 0.39728 | 0.0013513 | Sustained | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2021-12-13 23:26 | 2021-12-14 04:20 | 577 | 004:54 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO ALIMENTADOR 1529-12 Y SE CERRO POR SCADA LLEVA 1911-07 | S21121300343 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 294 | 2021-12-13 | 169638 | keep | 0 | Dec | 2021 | 0.11554 | 0.00039299 | Sustained | FALSE | FALSE | Not_TMED_Event | 577
BARRANQUITAS | 2021-12-14 00:33 | 2021-12-14 00:34 | 1131 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C21121400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 1131 | keep | 0 | Dec | 2021 | 0.00077032 | 0.00077032 | Momentary | FALSE | FALSE | Not_TMED_Event | 1131
UTUADO | 2021-12-14 00:58 | 2021-12-14 10:40 | 70 | 009:42 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21121400001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 582 | 2021-12-14 | 40740 | keep | 0 | Dec | 2021 | 0.027748 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2021-12-14 02:45 | 2021-12-14 09:25 | 5 | 006:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIAS | C21121400001 | New_Event | Bad Weather | Include | Include | Weather | 400 | 2021-12-14 | 2000 | keep | 0 | Dec | 2021 | 0.0013622 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-12-14 03:08 | 2021-12-14 09:48 | 150 | 006:40 | P | NO SE REPORTO CAUSA | 1 X 40 Y 1 X 100 EN CORTE DE LINEA | S21121400010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 400 | 2021-12-14 | 60000 | keep | 0 | Dec | 2021 | 0.040866 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-12-14 03:13 | 2021-12-14 03:14 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21121400005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 108 | keep | 0 | Dec | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
ARECIBO | 2021-12-14 03:37 | 2021-12-14 03:38 | 67 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21121400005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 67 | keep | 0 | Dec | 2021 | 4.5633e-05 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
ARECIBO | 2021-12-14 03:54 | 2021-12-14 08:25 | 50 | 004:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21121400007 | New_Event | Bad Weather | Include | Include | Weather | 271 | 2021-12-14 | 13550 | keep | 0 | Dec | 2021 | 0.0092288 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2021-12-14 03:56 | 2021-12-14 03:57 | 1830 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R21121400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 1830 | keep | 0 | Dec | 2021 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
BAYAMON | 2021-12-14 04:20 | 2021-12-14 06:17 | 800 | 001:57 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | HACIENDO OPERACIONES DISPARO 1529-12 | S21121300343 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 117 | 2021-12-14 | 93600 | keep | 0 | Dec | 2021 | 0.063751 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-14 04:20 | 2021-12-14 06:17 | 250 | 001:57 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE AMARRO TRAMO RESTANTE DEL 1911-07 CONTRA 1529-13 | S21121300343 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 117 | 2021-12-14 | 29250 | keep | 0 | Dec | 2021 | 0.019922 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-12-14 04:26 | 2021-12-14 11:03 | 25 | 006:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21121400006 | New_Event | Bad Weather | Include | Include | Weather | 397 | 2021-12-14 | 9925 | keep | 0 | Dec | 2021 | 0.0067599 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2021-12-14 05:33 | 2021-12-14 11:03 | 19 | 005:30 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA NO CAUSA | R21121400003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 330 | 2021-12-14 | 6270 | keep | 0 | Dec | 2021 | 0.0042705 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
GUAYAMA | 2021-12-14 06:11 | 2021-12-14 10:39 | 258 | 004:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADOR AVERIADO | P21121400009 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 268 | 2021-12-14 | 69144 | keep | 0 | Dec | 2021 | 0.047094 | 0.00017572 | Sustained | FALSE | FALSE | Not_TMED_Event | 258
MAYAGÃœEZ | 2021-12-14 06:13 | 2021-12-14 21:12 | 100 | 014:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21121400008 | New_Event | Bad Weather | Include | Include | Weather | 899 | 2021-12-14 | 89900 | keep | 0 | Dec | 2021 | 0.06123 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-12-14 06:17 | 2021-12-14 06:41 | 1984 | 000:24 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO ALIMENTADOR 1529-12 Y SE CERRO POR SCADA LLEVA 1911-07 | S21121300343 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 24 | 2021-12-14 | 47616 | keep | 0 | Dec | 2021 | 0.032431 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-14 06:17 | 2021-12-14 06:41 | 577 | 000:24 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO ALIMENTADOR 1529-12 Y SE CERRO POR SCADA LLEVA 1911-07 | S21121300343 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 24 | 2021-12-14 | 13848 | keep | 0 | Dec | 2021 | 0.0094318 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2021-12-14 06:19 | 2021-12-14 08:41 | 200 | 002:22 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO CAUSA | R21121400005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 142 | 2021-12-14 | 28400 | keep | 0 | Dec | 2021 | 0.019343 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2021-12-14 06:25 | 2021-12-14 10:07 | 100 | 003:42 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 Y 1 X 20 EN CORTE DE LINEA Y TRANSFORMADOR REMPLAZO AISLADOR | R21121400006 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 222 | 2021-12-14 | 22200 | keep | 0 | Dec | 2021 | 0.01512 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2021-12-14 06:32 | 2021-12-14 11:03 | 100 | 004:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA FUERTES VIENTOS | P21121400010 | New_Event | Bad Weather | Include | Include | Weather | 271 | 2021-12-14 | 27100 | keep | 0 | Dec | 2021 | 0.018458 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-12-14 06:35 | 2021-12-14 06:41 | 199 | 000:06 | T | ERROR HUMANO | HACIENDO OPERACIONES PARA DAR SERVICIO DISPARO | S21121400000 | New_Event | Human Error | Include | Include | Other | 6 | 2021-12-14 | 1194 | keep | 0 | Dec | 2021 | 0.00081323 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
BAYAMON | 2021-12-14 06:41 | 2021-12-14 17:46 | 800 | 011:05 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REMPLAZO VACUUM SWITCH Y SE NORMALIZO LA CARGA | S21121300343 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 665 | 2021-12-14 | 532000 | keep | 0 | Dec | 2021 | 0.36234 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-14 06:41 | 2021-12-14 09:51 | 250 | 003:10 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE AMARRO TRAMO RESTANTE DEL 1911-07 CONTRA 1529-13 | S21121300343 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 190 | 2021-12-14 | 47500 | keep | 0 | Dec | 2021 | 0.032352 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-12-14 07:20 | 2021-12-14 07:21 | 2635 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C21121400008 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-12-14 | 2635 | keep | 0 | Dec | 2021 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2021-12-14 07:21 | 2021-12-14 11:43 | 90 | 004:22 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO CAUSA | C21121400007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 262 | 2021-12-14 | 23580 | keep | 0 | Dec | 2021 | 0.01606 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BARRANQUITAS | 2021-12-14 07:21 | 2021-12-14 13:52 | 160 | 006:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE RETEZO LINEA ARRIADA | C21121400010 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 391 | 2021-12-14 | 62560 | keep | 0 | Dec | 2021 | 0.042609 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
ARECIBO | 2021-12-14 07:31 | 2021-12-15 11:40 | 60 | 028:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21121400016 | New_Event | Bad Weather | Include | Include | Weather | 1689 | 2021-12-14 | 101340 | keep | 0 | Dec | 2021 | 0.069022 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-12-14 07:52 | 2021-12-14 09:01 | 30 | 001:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L, 1 X 20 EN C/L Y SE REEMPLAZO CAJA AVERIADA | B21121400012 | New_Event | Cutout Failure | Include | Include | Equipment | 69 | 2021-12-14 | 2070 | keep | 0 | Dec | 2021 | 0.0014099 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-14 07:54 | 2021-12-14 11:42 | 1 | 003:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21121400020 | New_Event | Bad Weather | Include | Include | Weather | 228 | 2021-12-14 | 228 | keep | 0 | Dec | 2021 | 0.00015529 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-14 08:07 | 2021-12-14 16:24 | 50 | 008:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21121400017 | New_Event | Bad Weather | Include | Include | Weather | 497 | 2021-12-14 | 24850 | keep | 0 | Dec | 2021 | 0.016925 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-12-14 08:13 | 2021-12-14 12:00 | 60 | 003:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE ABRIO PUENTES PARA SECCIONALIZAR LINEA PRIMARIA ROTA | M21121400018 | New_Event | Wire Down | Include | Include | Equipment | 227 | 2021-12-14 | 13620 | keep | 0 | Dec | 2021 | 0.0092765 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-12-14 08:14 | 2021-12-14 15:19 | 100 | 007:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21121400019 | New_Event | Bad Weather | Include | Include | Weather | 425 | 2021-12-14 | 42500 | keep | 0 | Dec | 2021 | 0.028947 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-12-14 08:17 | 2021-12-14 14:20 | 45 | 006:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | C21121400017 | New_Event |  |  | Include | Wildlife | 363 | 2021-12-14 | 16335 | keep | 0 | Dec | 2021 | 0.011126 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
UTUADO | 2021-12-14 08:30 | 2021-12-14 15:58 | 12 | 007:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21121400026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 448 | 2021-12-14 | 5376 | keep | 0 | Dec | 2021 | 0.0036616 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-12-14 08:47 | 2021-12-14 15:31 | 20 | 006:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA PARTIDA | M21121400027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 404 | 2021-12-14 | 8080 | keep | 0 | Dec | 2021 | 0.0055033 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-12-14 08:49 | 2021-12-14 17:37 | 180 | 008:48 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | C21121400019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 528 | 2021-12-14 | 95040 | keep | 0 | Dec | 2021 | 0.064731 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
UTUADO | 2021-12-14 08:50 | 2021-12-14 18:30 | 20 | 009:40 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A21121400030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 580 | 2021-12-14 | 11600 | keep | 0 | Dec | 2021 | 0.0079007 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2021-12-14 08:53 | 2021-12-14 14:23 | 10 | 005:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21121400020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 330 | 2021-12-14 | 3300 | keep | 0 | Dec | 2021 | 0.0022476 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-14 09:01 | 2021-12-14 15:53 | 1 | 006:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE X REPTIL | R21121400014 | New_Event |  |  | Include | Wildlife | 412 | 2021-12-14 | 412 | keep | 0 | Dec | 2021 | 0.00028061 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-14 09:01 | 2021-12-14 09:02 | 120 | 000:01 | P | DESGANCHE | RECIERRE 1717-04 Y LLEVA 20% DEL 1716-02 SE REALIZO DESGANCHE | B21121400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-14 | 120 | keep | 0 | Dec | 2021 | 8.1731e-05 | 8.1731e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2021-12-14 09:01 | 2021-12-14 09:02 | 1362 | 000:01 | T | DESGANCHE | RECIERRE 1717-04 Y LLEVA 20% DEL 1716-02 SE REALIZO DESGANCHE | B21121400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-14 | 1362 | keep | 0 | Dec | 2021 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
BAYAMON | 2021-12-14 09:02 | 2021-12-14 11:18 | 30 | 002:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L, 1 X 20 EN C/L Y SE REEMPLAZO CAJA AVERIADA | B21121400012 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 136 | 2021-12-14 | 4080 | keep | 0 | Dec | 2021 | 0.0027789 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-14 09:02 | 2021-12-14 15:09 | 30 | 006:07 | P | DESGANCHE | 1 X 100 EN C/L. SE REALIZO DESGANCHE | B21121400025 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 367 | 2021-12-14 | 11010 | keep | 0 | Dec | 2021 | 0.0074989 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2021-12-14 09:02 | 2021-12-14 16:50 | 10 | 007:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M21121400030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 468 | 2021-12-14 | 4680 | keep | 0 | Dec | 2021 | 0.0031875 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-12-14 09:11 | 2021-12-14 17:07 | 10 | 007:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO XMR | C21121400031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 476 | 2021-12-14 | 4760 | keep | 0 | Dec | 2021 | 0.003242 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2021-12-14 09:19 | 2021-12-14 10:14 | 20 | 000:55 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21121400021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2021-12-14 | 1100 | keep | 0 | Dec | 2021 | 0.0007492 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2021-12-14 09:34 | 2021-12-14 14:08 | 10 | 004:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | ABRIO CAJA PARA DESPEGAR TENSOR DE BAJANTE | R21121400016 | New_Event |  |  | Include | Wildlife | 274 | 2021-12-14 | 2740 | keep | 0 | Dec | 2021 | 0.0018662 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-14 09:40 | 2021-12-14 14:19 | 4 | 004:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L MAL TIEMPO | R21121400018 | New_Event | Bad Weather | Include | Include | Weather | 279 | 2021-12-14 | 1116 | keep | 0 | Dec | 2021 | 0.0007601 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2021-12-14 09:50 | 2021-12-14 17:58 | 9 | 008:08 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | C21121400041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 488 | 2021-12-14 | 4392 | keep | 0 | Dec | 2021 | 0.0029914 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2021-12-14 09:51 | 2021-12-14 16:20 | 1 | 006:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR CAJAS PRIMARIAS Y REPARAR LINEA SECUNDARIA | M21121400041 | New_Event | Cutout Failure | Include | Include | Equipment | 389 | 2021-12-14 | 389 | keep | 0 | Dec | 2021 | 0.00026495 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-14 09:57 | 2021-12-14 14:37 | 100 | 004:40 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA Y SE REALIZO DESGACHE DE BAMBUAS | S21121400055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2021-12-14 | 28000 | keep | 0 | Dec | 2021 | 0.019071 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-12-14 10:01 | 2021-12-14 18:00 | 45 | 007:59 | P | NO SE REPORTO CAUSA | 1 X 80 Y 1 X 65 EN DISTINTOS C/L | B21121400028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 479 | 2021-12-14 | 21555 | keep | 0 | Dec | 2021 | 0.014681 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
PONCE | 2021-12-14 10:10 | 2021-12-14 10:54 | 15 | 000:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REPARO LINEA SECUNDARIA SOTERRADA PARTIDA POR MAQUINARIA PESADA Y SE COLOCO PM-103 EN SERVICIO | P21121300106 | Additional_clients |  |  | Include | Wildlife | 44 | 2021-12-14 | 660 | keep | 0 | Dec | 2021 | 0.00044952 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-12-14 10:28 | 2021-12-14 19:00 | 30 | 008:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M21121400048 | New_Event | Wire Down | Include | Include | Equipment | 512 | 2021-12-14 | 15360 | keep | 0 | Dec | 2021 | 0.010462 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-12-14 10:32 | 2021-12-14 13:16 | 50 | 002:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | S21121400064 | New_Event | Bad Weather | Include | Include | Weather | 164 | 2021-12-14 | 8200 | keep | 0 | Dec | 2021 | 0.005585 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-12-14 10:40 | 2021-12-14 15:57 | 9 | 005:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y REEMPLAZO BARRA EN PEDESTAL | C21121400066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 317 | 2021-12-14 | 2853 | keep | 0 | Dec | 2021 | 0.0019432 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
UTUADO | 2021-12-14 10:53 | 2021-12-14 16:23 | 200 | 005:30 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE RETIRO RAMA | A21121400057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 330 | 2021-12-14 | 66000 | keep | 0 | Dec | 2021 | 0.044952 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2021-12-14 10:59 | 2021-12-14 12:38 | 10 | 001:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21121400058 | New_Event | Bad Weather | Include | Include | Weather | 99 | 2021-12-14 | 990 | keep | 0 | Dec | 2021 | 0.00067428 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2021-12-14 11:03 | 2021-12-14 11:13 | 591 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | P21121400065 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2021-12-14 | 5910 | keep | 0 | Dec | 2021 | 0.0040253 | 0.00040253 | Sustained | FALSE | FALSE | Not_TMED_Event | 591
YAUCO | 2021-12-14 11:03 | 2021-12-14 14:57 | 1924 | 003:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21121400098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 234 | 2021-12-14 | 450216 | keep | 0 | Dec | 2021 | 0.30664 | 0.0013104 | Sustained | FALSE | FALSE | Not_TMED_Event | 1924
YAUCO | 2021-12-14 11:03 | 2021-12-14 14:57 | 968 | 003:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21121400098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 234 | 2021-12-14 | 226512 | keep | 0 | Dec | 2021 | 0.15428 | 0.0006593 | Sustained | FALSE | FALSE | Not_TMED_Event | 968
YAUCO | 2021-12-14 11:03 | 2021-12-14 14:57 | 680 | 003:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21121400098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 234 | 2021-12-14 | 159120 | keep | 0 | Dec | 2021 | 0.10838 | 0.00046314 | Sustained | FALSE | FALSE | Not_TMED_Event | 680
YAUCO | 2021-12-14 11:03 | 2021-12-14 14:57 | 2246 | 003:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21121400098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 234 | 2021-12-14 | 525564 | keep | 0 | Dec | 2021 | 0.35796 | 0.0015297 | Sustained | FALSE | FALSE | Not_TMED_Event | 2246
YAUCO | 2021-12-14 11:03 | 2021-12-14 16:34 | 2011 | 005:31 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21121400098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 331 | 2021-12-14 | 665641 | keep | 0 | Dec | 2021 | 0.45337 | 0.0013697 | Sustained | FALSE | FALSE | Not_TMED_Event | 2011
YAUCO | 2021-12-14 11:03 | 2021-12-14 16:34 | 339 | 005:31 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21121400098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 331 | 2021-12-14 | 112209 | keep | 0 | Dec | 2021 | 0.076425 | 0.00023089 | Sustained | FALSE | FALSE | Not_TMED_Event | 339
YAUCO | 2021-12-14 11:03 | 2021-12-14 18:10 | 2470 | 007:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21121400098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 427 | 2021-12-14 | 1054690 | keep | 0 | Dec | 2021 | 0.71834 | 0.0016823 | Sustained | FALSE | FALSE | Not_TMED_Event | 2470
YAUCO | 2021-12-14 11:03 | 2021-12-14 18:13 | 1182 | 007:10 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21121400098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 430 | 2021-12-14 | 508260 | keep | 0 | Dec | 2021 | 0.34617 | 0.00080505 | Sustained | FALSE | FALSE | Not_TMED_Event | 1182
YAUCO | 2021-12-14 11:03 | 2021-12-14 18:38 | 2340 | 007:35 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21121400098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 455 | 2021-12-14 | 1064700 | keep | 0 | Dec | 2021 | 0.72516 | 0.0015938 | Sustained | FALSE | FALSE | Not_TMED_Event | 2340
YAUCO | 2021-12-14 11:03 | 2021-12-14 18:38 | 1637 | 007:35 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21121400098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 455 | 2021-12-14 | 744835 | keep | 0 | Dec | 2021 | 0.5073 | 0.001115 | Sustained | FALSE | FALSE | Not_TMED_Event | 1637
YAUCO | 2021-12-14 11:03 | 2021-12-14 14:57 | 1475 | 003:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21121400098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 234 | 2021-12-14 | 345150 | keep | 0 | Dec | 2021 | 0.23508 | 0.0010046 | Sustained | FALSE | FALSE | Not_TMED_Event | 1475
YAUCO | 2021-12-14 11:03 | 2021-12-14 14:57 | 661 | 003:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21121400098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 234 | 2021-12-14 | 154674 | keep | 0 | Dec | 2021 | 0.10535 | 0.0004502 | Sustained | FALSE | FALSE | Not_TMED_Event | 661
YAUCO | 2021-12-14 11:03 | 2021-12-14 14:57 | 1569 | 003:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21121400098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 234 | 2021-12-14 | 367146 | keep | 0 | Dec | 2021 | 0.25006 | 0.0010686 | Sustained | FALSE | FALSE | Not_TMED_Event | 1569
YAUCO | 2021-12-14 11:03 | 2021-12-14 14:57 | 2179 | 003:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21121400098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 234 | 2021-12-14 | 509886 | keep | 0 | Dec | 2021 | 0.34728 | 0.0014841 | Sustained | FALSE | FALSE | Not_TMED_Event | 2179
YAUCO | 2021-12-14 11:03 | 2021-12-14 14:57 | 2440 | 003:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21121400098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 234 | 2021-12-14 | 570960 | keep | 0 | Dec | 2021 | 0.38888 | 0.0016619 | Sustained | FALSE | FALSE | Not_TMED_Event | 2440
YAUCO | 2021-12-14 11:03 | 2021-12-14 18:38 | 1352 | 007:35 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21121400098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 455 | 2021-12-14 | 615160 | keep | 0 | Dec | 2021 | 0.41898 | 0.00092084 | Sustained | FALSE | FALSE | Not_TMED_Event | 1352
YAUCO | 2021-12-14 11:03 | 2021-12-14 18:38 | 3973 | 007:35 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21121400098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 455 | 2021-12-14 | 1807715 | keep | 0 | Dec | 2021 | 1.2312 | 0.002706 | Sustained | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2021-12-14 11:03 | 2021-12-14 18:38 | 2484 | 007:35 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P21121400098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 455 | 2021-12-14 | 1130220 | keep | 0 | Dec | 2021 | 0.76979 | 0.0016918 | Sustained | FALSE | FALSE | Not_TMED_Event | 2484
MAYAGÃœEZ | 2021-12-14 11:03 | 2021-12-14 11:12 | 281 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA YAUCO 38 KV | M21121400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2021-12-14 | 2529 | keep | 0 | Dec | 2021 | 0.0017225 | 0.00019139 | Sustained | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2021-12-14 11:03 | 2021-12-14 11:12 | 1252 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA YAUCO 38 KV | M21121400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2021-12-14 | 11268 | keep | 0 | Dec | 2021 | 0.0076746 | 0.00085273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2021-12-14 11:03 | 2021-12-14 11:12 | 595 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA YAUCO 38 KV | M21121400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2021-12-14 | 5355 | keep | 0 | Dec | 2021 | 0.0036473 | 0.00040525 | Sustained | FALSE | FALSE | Not_TMED_Event | 595
MAYAGÃœEZ | 2021-12-14 11:03 | 2021-12-14 11:12 | 51 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA YAUCO 38 KV | M21121400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2021-12-14 | 459 | keep | 0 | Dec | 2021 | 0.00031262 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2021-12-14 11:03 | 2021-12-14 11:12 | 721 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA YAUCO 38 KV | M21121400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2021-12-14 | 6489 | keep | 0 | Dec | 2021 | 0.0044196 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2021-12-14 11:03 | 2021-12-14 11:12 | 1382 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV YAUCO | A21121400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2021-12-14 | 12438 | keep | 0 | Dec | 2021 | 0.0084715 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2021-12-14 11:03 | 2021-12-14 11:12 | 654 | 000:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV YAUCO | A21121400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 9 | 2021-12-14 | 5886 | keep | 0 | Dec | 2021 | 0.0040089 | 0.00044544 | Sustained | FALSE | FALSE | Not_TMED_Event | 654
CAGUAS | 2021-12-14 11:08 | 2021-12-14 13:48 | 20 | 002:40 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5 X 37.5KVA | C21121400072 | New_Event | Service Transformer Failure | Include | Include | Equipment | 160 | 2021-12-14 | 3200 | keep | 0 | Dec | 2021 | 0.0021795 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-12-14 11:12 | 2021-12-14 13:10 | 25 | 001:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21121400006 | New_Event | Bad Weather | Include | Include | Weather | 118 | 2021-12-14 | 2950 | keep | 0 | Dec | 2021 | 0.0020092 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-12-14 11:12 | 2021-12-14 17:51 | 20 | 006:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21121400028 | New_Event | Bad Weather | Include | Include | Weather | 399 | 2021-12-14 | 7980 | keep | 0 | Dec | 2021 | 0.0054351 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2021-12-14 11:13 | 2021-12-14 12:22 | 100 | 001:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA FUERTES VIENTOS | P21121400010 | New_Event | Bad Weather | Include | Include | Weather | 69 | 2021-12-14 | 6900 | keep | 0 | Dec | 2021 | 0.0046996 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-12-14 11:23 | 2021-12-14 19:28 | 200 | 008:05 | P | DESGANCHE | A PETICION DE FOREMAN SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE CRITICO Y REPARAR SECUNDARIA | S21121400038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 485 | 2021-12-14 | 97000 | keep | 0 | Dec | 2021 | 0.066066 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2021-12-14 11:23 | 2021-12-14 12:05 | 40 | 000:42 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21121400040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 42 | 2021-12-14 | 1680 | keep | 0 | Dec | 2021 | 0.0011442 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-12-14 11:36 | 2021-12-14 22:10 | 1 | 010:34 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA RETIRAR ENREDADERA | A21121400066 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 634 | 2021-12-14 | 634 | keep | 0 | Dec | 2021 | 0.00043181 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-12-14 11:41 | 2021-12-14 14:26 | 140 | 002:45 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | C21121400074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2021-12-14 | 23100 | keep | 0 | Dec | 2021 | 0.015733 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
BAYAMON | 2021-12-14 11:49 | 2021-12-14 11:50 | 6136 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1709-01 LLEVANDO CARGA 1720-07 | S21121400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 6136 | keep | 0 | Dec | 2021 | 0.0041792 | 0.0041792 | Momentary | FALSE | FALSE | Not_TMED_Event | 6136
ARECIBO | 2021-12-14 11:49 | 2021-12-14 13:45 | 1 | 001:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN RISER LLUVIA Y FUERTES VIENTOS | A21121400068 | New_Event | Bad Weather | Include | Include | Weather | 116 | 2021-12-14 | 116 | keep | 0 | Dec | 2021 | 7.9007e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-14 11:50 | 2021-12-14 12:12 | 12 | 000:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN C/L. SE CERRO PUENTE DE CAJA A LINEA | B21121400044 | Partial_restoration | Wire Down | Include | Include | Equipment | 22 | 2021-12-14 | 264 | keep | 0 | Dec | 2021 | 0.00017981 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-12-14 11:51 | 2021-12-14 16:18 | 6 | 004:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21121400069 | New_Event | Bad Weather | Include | Include | Weather | 267 | 2021-12-14 | 1602 | keep | 0 | Dec | 2021 | 0.0010911 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-12-14 11:54 | 2021-12-14 12:09 | 1889 | 000:15 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO EL INTERRUPTOR PARA RETIRAR TENSOR CRUZANDO LAS LINEAS | M21121400000 | New_Event |  |  | Include | Wildlife | 15 | 2021-12-14 | 28335 | keep | 0 | Dec | 2021 | 0.019299 | 0.0012866 | Sustained | FALSE | FALSE | Not_TMED_Event | 1889
ARECIBO | 2021-12-14 11:57 | 2021-12-14 12:58 | 1 | 001:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A21121400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 61 | 2021-12-14 | 61 | keep | 0 | Dec | 2021 | 4.1547e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-12-14 11:57 | 2021-12-14 12:58 | 2266 | 001:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A21121400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 61 | 2021-12-14 | 138226 | keep | 0 | Dec | 2021 | 0.094145 | 0.0015434 | Sustained | FALSE | FALSE | Not_TMED_Event | 2266
ARECIBO | 2021-12-14 11:57 | 2021-12-14 12:58 | 1399 | 001:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A21121400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 61 | 2021-12-14 | 85339 | keep | 0 | Dec | 2021 | 0.058124 | 0.00095285 | Sustained | FALSE | FALSE | Not_TMED_Event | 1399
SAN JUAN | 2021-12-14 11:58 | 2021-12-14 18:16 | 1 | 006:18 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21121400073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 378 | 2021-12-14 | 378 | keep | 0 | Dec | 2021 | 0.00025745 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-12-14 11:59 | 2021-12-14 12:00 | 67 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21121400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 67 | keep | 0 | Dec | 2021 | 4.5633e-05 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
MAYAGÃœEZ | 2021-12-14 12:03 | 2021-12-14 12:09 | 2067 | 000:06 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO EL INTERRUPTOR 6012-05 PARA RETIRAR TENSOR CRUZANDO LAS LINEAS EL CUAL LLEVA LA CARGA DEL 6012-03 | M21121400069 | New_Event |  |  | Include | Wildlife | 6 | 2021-12-14 | 12402 | keep | 0 | Dec | 2021 | 0.0084469 | 0.0014078 | Sustained | FALSE | FALSE | Not_TMED_Event | 2067
MAYAGÃœEZ | 2021-12-14 12:03 | 2021-12-14 12:09 | 1352 | 000:06 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO EL INTERRUPTOR PARA RETIRAR TENSOR CRUZANDO LAS LINEAS LLEVA LA CARGA DEL 6012-03 | M21121400069 | New_Event | Wire Down | Include | Include | Equipment | 6 | 2021-12-14 | 8112 | keep | 0 | Dec | 2021 | 0.005525 | 0.00092084 | Sustained | FALSE | FALSE | Not_TMED_Event | 1352
ARECIBO | 2021-12-14 12:05 | 2021-12-14 14:40 | 20 | 002:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A21121400072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2021-12-14 | 3100 | keep | 0 | Dec | 2021 | 0.0021114 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-12-14 12:15 | 2021-12-14 12:16 | 550 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1206-04 QUE A SU VEZ LLEVA LA CARGA PARCIAL DE LOS ALIMENTADORES 1204-04 UN 40% Y 1204-03 UN 60% | S21121400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 550 | keep | 0 | Dec | 2021 | 0.0003746 | 0.0003746 | Momentary | FALSE | FALSE | Not_TMED_Event | 550
SAN JUAN | 2021-12-14 12:15 | 2021-12-14 12:16 | 2600 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1206-04 QUE A SU VEZ LLEVA LA CARGA PARCIAL DE LOS ALIMENTADORES 1204-04 UN 40% Y 1204-03 UN 60% | S21121400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 2600 | keep | 0 | Dec | 2021 | 0.0017708 | 0.0017708 | Momentary | FALSE | FALSE | Not_TMED_Event | 2600
SAN JUAN | 2021-12-14 12:15 | 2021-12-14 12:16 | 1799 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 60% 1204-3 LLEVA 40% 1204-4 Y 60 AMP. DEL 1303-2 | S21121400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 1799 | keep | 0 | Dec | 2021 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2021-12-14 12:15 | 2021-12-14 12:16 | 1600 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 60 AMP POR 1206-04 | S21121400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 1600 | keep | 0 | Dec | 2021 | 0.0010898 | 0.0010898 | Momentary | FALSE | FALSE | Not_TMED_Event | 1600
MAYAGÃœEZ | 2021-12-14 12:20 | 2021-12-14 18:57 | 60 | 006:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21121400084 | New_Event | Bad Weather | Include | Include | Weather | 397 | 2021-12-14 | 23820 | keep | 0 | Dec | 2021 | 0.016224 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2021-12-14 12:24 | 2021-12-14 20:43 | 60 | 008:19 | P | ESTRUCTURA AVERIADA | 1 X 65 EN CORTE DE LINEA REEMPLAZO POSTE ROTO Y XMR DE 50KVA X 50KVA | C21121400080 | New_Event | Defective Pole | Include | Include | Equipment | 499 | 2021-12-14 | 29940 | keep | 0 | Dec | 2021 | 0.020392 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2021-12-14 12:24 | 2021-12-14 13:31 | 50 | 001:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P21121400092 | New_Event |  |  | Include | Wildlife | 67 | 2021-12-14 | 3350 | keep | 0 | Dec | 2021 | 0.0022817 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-12-14 12:29 | 2021-12-14 12:30 | 1047 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR MAL TIEMPO | M21121400033 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-12-14 | 1047 | keep | 0 | Dec | 2021 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
GUAYAMA | 2021-12-14 12:30 | 2021-12-14 14:24 | 100 | 001:54 | P | ESTRUCTURA AVERIADA | SE ABRE CORTE DE LINEA DE EMERGENCIA PARA REEMPLAZAR POSTE PRIMARIO PARTIDO | P21121400096 | New_Event | Defective Pole | Include | Include | Equipment | 114 | 2021-12-14 | 11400 | keep | 0 | Dec | 2021 | 0.0077645 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2021-12-14 12:30 | 2021-12-14 13:40 | 5 | 001:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21121400105 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 70 | 2021-12-14 | 350 | keep | 0 | Dec | 2021 | 0.00023838 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2021-12-14 12:40 | 2021-12-14 14:21 | 25 | 001:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L MAL TIEMPO | R21121400027 | New_Event | Bad Weather | Include | Include | Weather | 101 | 2021-12-14 | 2525 | keep | 0 | Dec | 2021 | 0.0017198 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2021-12-14 12:40 | 2021-12-14 14:45 | 10 | 002:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21121400081 | New_Event | Bad Weather | Include | Include | Weather | 125 | 2021-12-14 | 1250 | keep | 0 | Dec | 2021 | 0.00085137 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-14 13:00 | 2021-12-14 15:35 | 15 | 002:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | A21121400090 | New_Event | Secondary Wire Down | Include | Include | Equipment | 155 | 2021-12-14 | 2325 | keep | 0 | Dec | 2021 | 0.0015835 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-12-14 13:04 | 2021-12-14 14:39 | 10 | 001:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B21121300464 | New_Event | Secondary Wire Down | Include | Include | Equipment | 95 | 2021-12-14 | 950 | keep | 0 | Dec | 2021 | 0.00064704 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-14 13:04 | 2021-12-14 16:31 | 2735 | 003:27 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO Y SE SECCIONALIZO CONDUCTOR EN EL SUELO MEDIANTE GOI BY-211214-02 | B21121400056 | New_Event | Wire Down | Include | Include | Equipment | 207 | 2021-12-14 | 566145 | keep | 0 | Dec | 2021 | 0.3856 | 0.0018628 | Sustained | FALSE | FALSE | Not_TMED_Event | 2735
MAYAGÃœEZ | 2021-12-14 13:06 | 2021-12-14 14:52 | 40 | 001:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21121400101 | New_Event | Bad Weather | Include | Include | Weather | 106 | 2021-12-14 | 4240 | keep | 0 | Dec | 2021 | 0.0028878 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-12-14 13:07 | 2021-12-14 14:30 | 1 | 001:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21121400102 | New_Event | Bad Weather | Include | Include | Weather | 83 | 2021-12-14 | 83 | keep | 0 | Dec | 2021 | 5.6531e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-14 13:08 | 2021-12-14 16:51 | 35 | 003:43 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21121400057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 223 | 2021-12-14 | 7805 | keep | 0 | Dec | 2021 | 0.0053159 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2021-12-14 13:10 | 2021-12-14 17:53 | 80 | 004:43 | P | DESGANCHE | 3 X 65 EN C/L . ES NECESARIO REALIZAR DESGANCHE | B21121400058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2021-12-14 | 22640 | keep | 0 | Dec | 2021 | 0.01542 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2021-12-14 13:12 | 2021-12-14 16:04 | 79 | 002:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | P21121400122 | New_Event | Wire Down | Include | Include | Equipment | 172 | 2021-12-14 | 13588 | keep | 0 | Dec | 2021 | 0.0092547 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
BARRANQUITAS | 2021-12-14 13:17 | 2021-12-14 17:39 | 60 | 004:22 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO CAUSA | C21121400088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 262 | 2021-12-14 | 15720 | keep | 0 | Dec | 2021 | 0.010707 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2021-12-14 13:30 | 2021-12-14 18:48 | 33 | 005:18 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRE TRANSFORMADOR PARA REEMPLAZAR POSTE SECUNDARIO Y SECUNDARIA AVERIADA | P21121400001 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 318 | 2021-12-14 | 10494 | keep | 0 | Dec | 2021 | 0.0071474 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
UTUADO | 2021-12-14 13:35 | 2021-12-14 14:28 | 5 | 000:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE | A21121400086 | New_Event | Secondary Wire Down | Include | Include | Equipment | 53 | 2021-12-14 | 265 | keep | 0 | Dec | 2021 | 0.00018049 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2021-12-14 13:43 | 2021-12-15 10:38 | 25 | 020:55 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | P21121400136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1255 | 2021-12-14 | 31375 | keep | 0 | Dec | 2021 | 0.021369 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2021-12-14 13:49 | 2021-12-14 14:50 | 150 | 001:01 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21121400096 | New_Event | Bad Weather | Include | Include | Weather | 61 | 2021-12-14 | 9150 | keep | 0 | Dec | 2021 | 0.006232 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2021-12-14 13:50 | 2021-12-15 10:27 | 20 | 020:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21121400139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1237 | 2021-12-14 | 24740 | keep | 0 | Dec | 2021 | 0.01685 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2021-12-14 13:51 | 2021-12-14 16:28 | 40 | 002:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21121400109 | New_Event | Bad Weather | Include | Include | Weather | 157 | 2021-12-14 | 6280 | keep | 0 | Dec | 2021 | 0.0042773 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-12-14 13:51 | 2021-12-14 17:00 | 25 | 003:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CULEBRA CRUZO FASES | A21121400097 | New_Event |  |  | Include | Wildlife | 189 | 2021-12-14 | 4725 | keep | 0 | Dec | 2021 | 0.0032182 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-12-14 14:07 | 2021-12-14 21:08 | 100 | 007:01 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21121400112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 421 | 2021-12-14 | 42100 | keep | 0 | Dec | 2021 | 0.028674 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-12-14 14:11 | 2021-12-14 14:12 | 2126 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21121400095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 2126 | keep | 0 | Dec | 2021 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
AGUADILLA | 2021-12-14 14:12 | 2021-12-14 14:34 | 3041 | 000:22 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO SE INFORMO CAUSA | M21121400114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 22 | 2021-12-14 | 66902 | keep | 0 | Dec | 2021 | 0.045567 | 0.0020712 | Sustained | FALSE | FALSE | Not_TMED_Event | 3041
ARECIBO | 2021-12-14 14:32 | 2021-12-14 19:23 | 1500 | 004:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO | A21121300200 | Partial_restoration | Wire Down | Include | Include | Equipment | 291 | 2021-12-14 | 436500 | keep | 0 | Dec | 2021 | 0.2973 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-12-14 14:44 | 2021-12-14 18:55 | 50 | 004:11 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A21121400109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2021-12-14 | 12550 | keep | 0 | Dec | 2021 | 0.0085477 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-14 14:45 | 2021-12-14 15:37 | 10 | 000:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B21121400036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 52 | 2021-12-14 | 520 | keep | 0 | Dec | 2021 | 0.00035417 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-14 14:46 | 2021-12-15 10:20 | 283 | 019:34 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21121400101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1174 | 2021-12-14 | 332242 | keep | 0 | Dec | 2021 | 0.22629 | 0.00019275 | Sustained | FALSE | FALSE | Not_TMED_Event | 283
UTUADO | 2021-12-14 14:49 | 2021-12-14 18:42 | 25 | 003:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21121400110 | New_Event | Bad Weather | Include | Include | Weather | 233 | 2021-12-14 | 5825 | keep | 0 | Dec | 2021 | 0.0039674 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-12-14 14:51 | 2021-12-14 15:19 | 356 | 000:28 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1342-04 QUE A SU VEZ LLEVA LA CARGA DEL 1342-01. SE ABRIO MACHETE DE AMARRE EN BARRA DE INSPECCION Y SE NORMALIZO BKR ENTRANDO LA CARGA DEL 1342-01 SE LEVANTO LINEA PRIMARIA | S21121400097 | New_Event | Wire Down | Include | Include | Equipment | 28 | 2021-12-14 | 9968 | keep | 0 | Dec | 2021 | 0.0067892 | 0.00024247 | Sustained | FALSE | FALSE | Not_TMED_Event | 356
SAN JUAN | 2021-12-14 14:51 | 2021-12-14 16:04 | 390 | 001:13 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1342-04 SE ROMPIO AMARRE CONTRA 1342-1. SE ABRIO MACHETE LINEA TRONCAL PARA SECCIONALIZAR AVERIA CONDUCTOR EN EL SUELO. ENTRA UN 60% EN SERVICIO | S21121400097 | New_Event | Wire Down | Include | Include | Equipment | 73 | 2021-12-14 | 28470 | keep | 0 | Dec | 2021 | 0.019391 | 0.00026563 | Sustained | FALSE | FALSE | Not_TMED_Event | 390
BAYAMON | 2021-12-14 15:11 | 2021-12-14 18:28 | 150 | 003:17 | P | ESTRUCTURA AVERIADA | SE ABRIO PUENTE PARA SECCIONALIZAR POSTE PARTIDO Y SE REEMPLAZO 1 X 50 EN CORTE DE LINEA. SE QUEDARON SIN SERVICIO 2 CLIENTES | B21121400082 | New_Event | Defective Pole | Include | Include | Equipment | 197 | 2021-12-14 | 29550 | keep | 0 | Dec | 2021 | 0.020126 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
UTUADO | 2021-12-14 15:22 | 2021-12-14 17:50 | 7 | 002:28 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO ENREDADERA | A21121400114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2021-12-14 | 1036 | keep | 0 | Dec | 2021 | 0.00070561 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-12-14 15:33 | 2021-12-14 16:57 | 150 | 001:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21121400132 | New_Event | Bad Weather | Include | Include | Weather | 84 | 2021-12-14 | 12600 | keep | 0 | Dec | 2021 | 0.0085818 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-12-14 15:38 | 2021-12-14 22:10 | 60 | 006:32 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21121400135 | New_Event | Bad Weather | Include | Include | Weather | 392 | 2021-12-14 | 23520 | keep | 0 | Dec | 2021 | 0.016019 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-12-14 15:41 | 2021-12-14 15:42 | 1834 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21121400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 1834 | keep | 0 | Dec | 2021 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
UTUADO | 2021-12-14 15:45 | 2021-12-14 20:08 | 15 | 004:23 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A21121400118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2021-12-14 | 3945 | keep | 0 | Dec | 2021 | 0.0026869 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-12-14 15:46 | 2021-12-14 15:47 | 552 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1206-04 QUE A SU VEZ LLEVA LA CARGA PARCIAL DE LOS ALIMENTADORES 1204-04 UN 40% Y 1204-03 UN 60% | S21121400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 552 | keep | 0 | Dec | 2021 | 0.00037596 | 0.00037596 | Momentary | FALSE | FALSE | Not_TMED_Event | 552
SAN JUAN | 2021-12-14 15:46 | 2021-12-14 15:47 | 2966 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1206-04 QUE A SU VEZ LLEVA LA CARGA PARCIAL DE LOS ALIMENTADORES 1204-04 UN 40% Y 1204-03 UN 60% | S21121400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 2966 | keep | 0 | Dec | 2021 | 0.0020201 | 0.0020201 | Momentary | FALSE | FALSE | Not_TMED_Event | 2966
SAN JUAN | 2021-12-14 15:48 | 2021-12-14 15:49 | 552 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1206-04 QUE A SU VEZ LLEVA LA CARGA PARCIAL DE LOS ALIMENTADORES 1204-04 UN 40% Y 1204-03 UN 60% | S21121400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 552 | keep | 0 | Dec | 2021 | 0.00037596 | 0.00037596 | Momentary | FALSE | FALSE | Not_TMED_Event | 552
SAN JUAN | 2021-12-14 15:48 | 2021-12-14 15:49 | 2966 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1206-04 QUE A SU VEZ LLEVA LA CARGA PARCIAL DE LOS ALIMENTADORES 1204-04 UN 40% Y 1204-03 UN 60% | S21121400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 2966 | keep | 0 | Dec | 2021 | 0.0020201 | 0.0020201 | Momentary | FALSE | FALSE | Not_TMED_Event | 2966
SAN JUAN | 2021-12-14 15:48 | 2021-12-14 15:49 | 1799 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1206-04 QUE A SU VEZ LLEVA LA CARGA PARCIAL DE LOS ALIMENTADORES 1204-04 UN 40% Y 1204-03 UN 60% | S21121400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 1799 | keep | 0 | Dec | 2021 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2021-12-14 15:51 | 2021-12-14 15:52 | 552 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1206-04 QUE A SU VEZ LLEVA LA CARGA PARCIAL DE LOS ALIMENTADORES 1204-04 UN 40% Y 1204-03 UN 60% | S21121400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 552 | keep | 0 | Dec | 2021 | 0.00037596 | 0.00037596 | Momentary | FALSE | FALSE | Not_TMED_Event | 552
SAN JUAN | 2021-12-14 15:51 | 2021-12-14 15:52 | 2966 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1206-04 QUE A SU VEZ LLEVA LA CARGA PARCIAL DE LOS ALIMENTADORES 1204-04 UN 40% Y 1204-03 UN 60% | S21121400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 2966 | keep | 0 | Dec | 2021 | 0.0020201 | 0.0020201 | Momentary | FALSE | FALSE | Not_TMED_Event | 2966
SAN JUAN | 2021-12-14 15:51 | 2021-12-14 15:52 | 1799 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1206-04 QUE A SU VEZ LLEVA LA CARGA PARCIAL DE LOS ALIMENTADORES 1204-04 UN 40% Y 1204-03 UN 60% | S21121400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 1799 | keep | 0 | Dec | 2021 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
MAYAGÃœEZ | 2021-12-14 15:51 | 2021-12-14 22:10 | 150 | 006:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | M21121400140 | New_Event | Wire Down | Include | Include | Equipment | 379 | 2021-12-14 | 56850 | keep | 0 | Dec | 2021 | 0.03872 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2021-12-14 15:53 | 2021-12-14 18:19 | 50 | 002:26 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21121400106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2021-12-14 | 7300 | keep | 0 | Dec | 2021 | 0.004972 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-12-14 15:56 | 2021-12-14 17:56 | 50 | 002:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REEMPLAZO CAJA QUEMADA | B21121400088 | New_Event | Cutout Failure | Include | Include | Equipment | 120 | 2021-12-14 | 6000 | keep | 0 | Dec | 2021 | 0.0040866 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-14 16:01 | 2021-12-14 19:07 | 15 | 003:06 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSCLOUSURE | S21121400110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 186 | 2021-12-14 | 2790 | keep | 0 | Dec | 2021 | 0.0019003 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-12-14 16:04 | 2021-12-14 16:15 | 156 | 000:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1342-04 SE ROMPIO AMARRE CONTRA 1342-1. SE CERRO AMARRE CONTRA 1201-01. ENTRA UN 95% EN SERVICIO LINEA PRIMARIA EN EL SUELO | S21121400097 | Partial_restoration | Wire Down | Include | Include | Equipment | 11 | 2021-12-14 | 1716 | keep | 0 | Dec | 2021 | 0.0011688 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2021-12-14 16:10 | 2021-12-14 17:19 | 8 | 001:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | P21121400137 | New_Event | Secondary Wire Down | Include | Include | Equipment | 69 | 2021-12-14 | 552 | keep | 0 | Dec | 2021 | 0.00037596 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-12-14 16:13 | 2021-12-14 17:15 | 60 | 001:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21121400125 | New_Event | Bad Weather | Include | Include | Weather | 62 | 2021-12-14 | 3720 | keep | 0 | Dec | 2021 | 0.0025337 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-12-14 16:15 | 2021-12-14 18:33 | 25 | 002:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1342-04 SE ROMPIO AMARRE CONTRA 1342-1. SE LEVANTO LINEA PRIMARIA. ENTRA UN 100% EN SERVICIO | S21121400097 | Partial_restoration | Wire Down | Include | Include | Equipment | 138 | 2021-12-14 | 3450 | keep | 0 | Dec | 2021 | 0.0023498 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-12-14 16:23 | 2021-12-14 17:42 | 60 | 001:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21121400117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2021-12-14 | 4740 | keep | 0 | Dec | 2021 | 0.0032284 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-12-14 16:23 | 2021-12-15 17:00 | 8 | 024:37 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA LINEAS CRUZADAS POR RAMA | A21121400128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1477 | 2021-12-14 | 11816 | keep | 0 | Dec | 2021 | 0.0080478 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2021-12-14 16:24 | 2021-12-14 16:51 | 40 | 000:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CRUCE X AVE | R21121400048 | New_Event |  |  | Include | Wildlife | 27 | 2021-12-14 | 1080 | keep | 0 | Dec | 2021 | 0.00073558 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-12-14 16:24 | 2021-12-14 17:47 | 1 | 001:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21121400129 | New_Event | Bad Weather | Include | Include | Weather | 83 | 2021-12-14 | 83 | keep | 0 | Dec | 2021 | 5.6531e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-14 16:25 | 2021-12-14 17:52 | 60 | 001:27 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21121400150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2021-12-14 | 5220 | keep | 0 | Dec | 2021 | 0.0035553 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-12-14 16:31 | 2021-12-14 19:47 | 700 | 003:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y SE CERRARON MACHETES MEDIANTE GOI BY-211214-02 | B21121400056 | Partial_restoration | Wire Down | Include | Include | Equipment | 196 | 2021-12-14 | 137200 | keep | 0 | Dec | 2021 | 0.093446 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-14 16:38 | 2021-12-14 21:58 | 30 | 005:20 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21121400119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 320 | 2021-12-14 | 9600 | keep | 0 | Dec | 2021 | 0.0065385 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2021-12-14 16:40 | 2021-12-14 18:28 | 66 | 001:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | P21121400189 | New_Event |  |  | Include | Wildlife | 108 | 2021-12-14 | 7128 | keep | 0 | Dec | 2021 | 0.0048548 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
VEGA BAJA | 2021-12-14 16:42 | 2021-12-14 19:18 | 10 | 002:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B21121400096 | New_Event | Secondary Wire Down | Include | Include | Equipment | 156 | 2021-12-14 | 1560 | keep | 0 | Dec | 2021 | 0.0010625 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-14 16:49 | 2021-12-14 16:50 | 135 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 ADEMAS LLEVA LA CARGA DEL 1346-05 | S21121400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 135 | keep | 0 | Dec | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2021-12-14 16:49 | 2021-12-14 16:50 | 135 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 ADEMAS LLEVA LA CARGA DEL 1346-05 | S21121400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 135 | keep | 0 | Dec | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
BAYAMON | 2021-12-14 16:52 | 2021-12-14 17:54 | 50 | 001:02 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21121400120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2021-12-14 | 3100 | keep | 0 | Dec | 2021 | 0.0021114 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-12-14 16:55 | 2021-12-15 17:10 | 10 | 024:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | A21121400130 | New_Event | Wire Down | Include | Include | Equipment | 1455 | 2021-12-14 | 14550 | keep | 0 | Dec | 2021 | 0.0099099 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-14 17:01 | 2021-12-15 12:29 | 127 | 019:28 | P | DESGANCHE | 1 X 65 EN C/L. SE REALIZO DESGANCHE | S21121500023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1168 | 2021-12-14 | 148336 | keep | 0 | Dec | 2021 | 0.10103 | 8.6499e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 127
BAYAMON | 2021-12-14 17:01 | 2021-12-14 20:18 | 40 | 003:17 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S21121400123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 197 | 2021-12-14 | 7880 | keep | 0 | Dec | 2021 | 0.005367 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-12-14 17:04 | 2021-12-14 20:55 | 10 | 003:51 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21121400133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 231 | 2021-12-14 | 2310 | keep | 0 | Dec | 2021 | 0.0015733 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-14 17:06 | 2021-12-14 22:49 | 20 | 005:43 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | S21121400124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 343 | 2021-12-14 | 6860 | keep | 0 | Dec | 2021 | 0.0046723 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-12-14 17:15 | 2021-12-14 17:48 | 1 | 000:33 | P | SECUNDARIA/DESGANCHE | SE ABRE MONTURA PARA REALIZAR DEGANCHE SECUNDARIO | P21121400202 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 33 | 2021-12-14 | 33 | keep | 0 | Dec | 2021 | 2.2476e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-12-14 17:39 | 2021-12-14 17:40 | 1047 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21121400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 1047 | keep | 0 | Dec | 2021 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
FAJARDO | 2021-12-14 17:43 | 2021-12-14 17:44 | 1571 | 000:01 | T | DESGANCHE | RECIERRE | R21121400053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-14 | 1571 | keep | 0 | Dec | 2021 | 0.00107 | 0.00107 | Momentary | FALSE | FALSE | Not_TMED_Event | 1571
FAJARDO | 2021-12-14 17:44 | 2021-12-14 20:40 | 40 | 002:56 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHO Y REPARO BAJANTE DE LINEA A CAJA | R21121400054 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 176 | 2021-12-14 | 7040 | keep | 0 | Dec | 2021 | 0.0047949 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-14 18:08 | 2021-12-14 18:47 | 10 | 000:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B21121400056 | New_Event | Secondary Wire Down | Include | Include | Equipment | 39 | 2021-12-14 | 390 | keep | 0 | Dec | 2021 | 0.00026563 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-14 18:09 | 2021-12-14 18:10 | 514 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1520-05 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1520-01 Y 1520-04 | S21121400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-14 | 514 | keep | 0 | Dec | 2021 | 0.00035008 | 0.00035008 | Momentary | FALSE | FALSE | Not_TMED_Event | 514
BAYAMON | 2021-12-14 18:09 | 2021-12-14 18:10 | 752 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1520-05 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1520-01 Y 1520-04 | S21121400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-14 | 752 | keep | 0 | Dec | 2021 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
BAYAMON | 2021-12-14 18:10 | 2021-12-14 18:58 | 100 | 000:48 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21121400128 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 48 | 2021-12-14 | 4800 | keep | 0 | Dec | 2021 | 0.0032693 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2021-12-14 18:17 | 2021-12-14 18:38 | 3 | 000:21 | P | NO SE REPORTO CAUSA | 1 X 20 EN SU | B21121400107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 21 | 2021-12-14 | 63 | keep | 0 | Dec | 2021 | 4.2909e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-12-14 18:28 | 2021-12-16 10:48 | 2 | 040:20 | P | ESTRUCTURA AVERIADA | SE ABRIO PUENTE PARA SECCIONALIZAR POSTE PARTIDO Y SE REEMPLAZO 1 X 50 EN CORTE DE LINEA. SE QUEDARON SIN SERVICIO 2 CLIENTES | B21121400082 | Partial_restoration | Defective Pole | Include | Include | Equipment | 2420 | 2021-12-14 | 4840 | keep | 0 | Dec | 2021 | 0.0032965 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2021-12-14 18:38 | 2021-12-14 20:47 | 2484 | 002:09 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR ROTO EN TRONCAL DEL ALIMENTADOR Y SE CERRO INTERRUPTOR | P21121400222 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 129 | 2021-12-14 | 320436 | keep | 0 | Dec | 2021 | 0.21825 | 0.0016918 | Sustained | FALSE | FALSE | Not_TMED_Event | 2484
BAYAMON | 2021-12-14 19:04 | 2021-12-14 19:05 | 68 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1520-05 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1520-01 Y 1520-04 | S21121400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-14 | 68 | keep | 0 | Dec | 2021 | 4.6314e-05 | 4.6314e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 68
BAYAMON | 2021-12-14 19:05 | 2021-12-14 19:06 | 2435 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECERRO 1909-08 LLEVANDO EL 1907-05 PARARRAYO DEFECTUOSO | B21121400000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-12-14 | 2435 | keep | 0 | Dec | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-12-14 19:05 | 2021-12-14 19:06 | 2956 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECERRO 1909-08 LLEVANDO EL 1907-05 SE ELIMINO PARARRAYO | S21121400000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-12-14 | 2956 | keep | 0 | Dec | 2021 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2021-12-14 19:06 | 2021-12-14 22:07 | 80 | 003:01 | P | PARARRAYOS DEFECTUOSO | 1 X 140 EN C/L PARARRAYO DEFECTUOSO | S21121400130 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 181 | 2021-12-14 | 14480 | keep | 0 | Dec | 2021 | 0.0098623 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2021-12-14 19:23 | 2021-12-14 19:25 | 5042 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA ABRIR MACHETES AUTORIZADO POR ORLANDO VELEZ EN SUSTITUCION DE ANGEL SOTO | A21121400000 | Additional_clients | Wire Down | Include | Include | Equipment | 2 | 2021-12-14 | 10084 | keep | 0 | Dec | 2021 | 0.0068682 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-12-14 19:25 | 2021-12-14 20:19 | 4500 | 000:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTES Y MACHETES | A21121300200 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 54 | 2021-12-14 | 243000 | keep | 0 | Dec | 2021 | 0.16551 | 0.0030649 | Sustained | FALSE | FALSE | Not_TMED_Event | 4500
SAN JUAN | 2021-12-14 19:38 | 2021-12-14 19:39 | 1268 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | S21121400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 1268 | keep | 0 | Dec | 2021 | 0.00086363 | 0.00086363 | Momentary | FALSE | FALSE | Not_TMED_Event | 1268
BAYAMON | 2021-12-14 20:39 | 2021-12-14 22:26 | 1 | 001:47 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21121400111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 107 | 2021-12-14 | 107 | keep | 0 | Dec | 2021 | 7.2877e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-14 21:01 | 2021-12-15 11:08 | 3 | 014:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO MEDIANTE GOI BY-211211-03 Y SE DIO SERVICIO TOTAL. | B21121100058 | Partial_restoration | Wire Down | Include | Include | Equipment | 847 | 2021-12-14 | 2541 | keep | 0 | Dec | 2021 | 0.0017307 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-14 22:07 | 2021-12-14 22:08 | 2435 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECERRO 1909-08 LLEVANDO EL 1907-05 SE ELIMINO PARARRAYO | S21121400000 | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-12-14 | 2435 | keep | 0 | Dec | 2021 | 0.0016585 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-14 22:07 | 2021-12-14 22:08 | 2956 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECERRO 1909-08 LLEVANDO EL 1907-05 SE ELIMINO PARARRAYO | S21121400000 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-12-14 | 2956 | keep | 0 | Dec | 2021 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2021-12-14 22:08 | 2021-12-15 01:23 | 40 | 003:15 | P | PARARRAYOS DEFECTUOSO | 1 X 100 Y 1 X 80 EN CORTES DE LINEA SE ELIMINO PARARRAYO | S21121400138 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 195 | 2021-12-14 | 7800 | keep | 0 | Dec | 2021 | 0.0053125 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-12-14 22:25 | 2021-12-14 22:26 | 215 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B21121400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 215 | keep | 0 | Dec | 2021 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
MAYAGÃœEZ | 2021-12-14 22:30 | 2021-12-14 23:09 | 160 | 000:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M21121400193 | New_Event | Bad Weather | Include | Include | Weather | 39 | 2021-12-14 | 6240 | keep | 0 | Dec | 2021 | 0.00425 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
CAGUAS | 2021-12-14 22:40 | 2021-12-14 22:41 | 1261 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21121400132 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-14 | 1261 | keep | 0 | Dec | 2021 | 0.00085886 | 0.00085886 | Momentary | FALSE | FALSE | Not_TMED_Event | 1261
HUMACAO | 2021-12-14 22:53 | 2021-12-15 08:12 | 19 | 009:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21121400130 | New_Event | Bad Weather | Include | Include | Weather | 559 | 2021-12-14 | 10621 | keep | 0 | Dec | 2021 | 0.0072339 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
ARECIBO | 2021-12-15 00:33 | 2021-12-15 10:00 | 50 | 009:27 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE INFORMA SECTOR NECESITA DESGANCHE | A21121500001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 567 | 2021-12-15 | 28350 | keep | 0 | Dec | 2021 | 0.019309 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-12-15 01:04 | 2021-12-15 10:30 | 5 | 009:26 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M21121500001 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 566 | 2021-12-15 | 2830 | keep | 0 | Dec | 2021 | 0.0019275 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-12-15 01:28 | 2021-12-15 14:20 | 10 | 012:52 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 10 KVA X 37.5 KVA | C21121500001 | New_Event | Service Transformer Failure | Include | Include | Equipment | 772 | 2021-12-15 | 7720 | keep | 0 | Dec | 2021 | 0.0052581 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-15 01:39 | 2021-12-15 02:40 | 352 | 001:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21121500002 | New_Event | Bad Weather | Include | Include | Weather | 61 | 2021-12-15 | 21472 | keep | 0 | Dec | 2021 | 0.014624 | 0.00023975 | Sustained | FALSE | FALSE | Not_TMED_Event | 352
MAYAGÃœEZ | 2021-12-15 02:16 | 2021-12-15 12:24 | 60 | 010:08 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN CORTES DE LINEA DISTINTOS SE RETIRO RAMAS SOBRE LAS LINEAS | M21121500002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 608 | 2021-12-15 | 36480 | keep | 0 | Dec | 2021 | 0.024846 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2021-12-15 02:40 | 2021-12-15 02:41 | 1590 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | C21121500003 | Additional_clients | Bad Weather | Include | Include | Weather | 1 | 2021-12-15 | 1590 | keep | 0 | Dec | 2021 | 0.0010829 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-12-15 02:41 | 2021-12-15 09:31 | 352 | 006:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21121500002 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 410 | 2021-12-15 | 144320 | keep | 0 | Dec | 2021 | 0.098296 | 0.00023975 | Sustained | FALSE | FALSE | Not_TMED_Event | 352
SAN JUAN | 2021-12-15 02:50 | 2021-12-15 10:24 | 130 | 007:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50, 1 X 65 Y 1 X 80 EN CORTES DE LINEA CRUCE CON RATA | R21121500001 | New_Event |  |  | Include | Wildlife | 454 | 2021-12-15 | 59020 | keep | 0 | Dec | 2021 | 0.040198 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
MAYAGÃœEZ | 2021-12-15 03:31 | 2021-12-15 11:00 | 60 | 007:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21121500004 | New_Event | Bad Weather | Include | Include | Weather | 449 | 2021-12-15 | 26940 | keep | 0 | Dec | 2021 | 0.018349 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2021-12-15 05:11 | 2021-12-15 18:47 | 81 | 013:36 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21121500004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 816 | 2021-12-15 | 66096 | keep | 0 | Dec | 2021 | 0.045018 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
ARECIBO | 2021-12-15 05:36 | 2021-12-15 05:37 | 1976 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21121500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-15 | 1976 | keep | 0 | Dec | 2021 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
CAGUAS | 2021-12-15 05:41 | 2021-12-15 18:04 | 10 | 012:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21121500005 | New_Event | Bad Weather | Include | Include | Weather | 743 | 2021-12-15 | 7430 | keep | 0 | Dec | 2021 | 0.0050605 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-15 06:02 | 2021-12-15 09:49 | 65 | 003:47 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21121500003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2021-12-15 | 14755 | keep | 0 | Dec | 2021 | 0.01005 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
ARECIBO | 2021-12-15 06:04 | 2021-12-15 09:42 | 1628 | 003:38 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DEL INTERRUPTOR SE ABRIO MACHETES PARA SECCIONALIZAR LA AVERIA | A21121500003 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 218 | 2021-12-15 | 354904 | keep | 0 | Dec | 2021 | 0.24172 | 0.0011088 | Sustained | FALSE | FALSE | Not_TMED_Event | 1628
UTUADO | 2021-12-15 06:14 | 2021-12-15 10:06 | 50 | 003:52 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21121500004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2021-12-15 | 11600 | keep | 0 | Dec | 2021 | 0.0079007 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-12-15 06:17 | 2021-12-15 10:04 | 100 | 003:47 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21121500005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2021-12-15 | 22700 | keep | 0 | Dec | 2021 | 0.015461 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2021-12-15 06:31 | 2021-12-15 06:32 | 2926 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 9202-04 | B21121500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-15 | 2926 | keep | 0 | Dec | 2021 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
UTUADO | 2021-12-15 06:34 | 2021-12-15 09:40 | 20 | 003:06 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21121500006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2021-12-15 | 3720 | keep | 0 | Dec | 2021 | 0.0025337 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-12-15 07:06 | 2021-12-15 11:56 | 100 | 004:50 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21121500005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 290 | 2021-12-15 | 29000 | keep | 0 | Dec | 2021 | 0.019752 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2021-12-15 07:09 | 2021-12-15 13:00 | 125 | 005:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21121500009 | New_Event | Wire Down | Include | Include | Equipment | 351 | 2021-12-15 | 43875 | keep | 0 | Dec | 2021 | 0.029883 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2021-12-15 07:17 | 2021-12-15 08:40 | 10 | 001:23 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B21121500012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 83 | 2021-12-15 | 830 | keep | 0 | Dec | 2021 | 0.00056531 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-15 07:28 | 2021-12-15 07:29 | 3431 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21121500020 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-12-15 | 3431 | keep | 0 | Dec | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2021-12-15 07:29 | 2021-12-15 09:13 | 150 | 001:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21121500013 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 104 | 2021-12-15 | 15600 | keep | 0 | Dec | 2021 | 0.010625 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-12-15 07:43 | 2021-12-15 18:15 | 400 | 010:32 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE RETIRO RAMA VERIFICADO HORARIO | M21121500012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 632 | 2021-12-15 | 252800 | keep | 0 | Dec | 2021 | 0.17218 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
MAYAGÃœEZ | 2021-12-15 07:43 | 2021-12-15 13:38 | 125 | 005:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES VERIFICAEDO HORARIO | M21121500012 | New_Event | Bad Weather | Include | Include | Weather | 355 | 2021-12-15 | 44375 | keep | 0 | Dec | 2021 | 0.030224 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
MAYAGÃœEZ | 2021-12-15 07:50 | 2021-12-15 13:53 | 100 | 006:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE CRUZO LINEAS | M21121500013 | New_Event |  |  | Include | Wildlife | 363 | 2021-12-15 | 36300 | keep | 0 | Dec | 2021 | 0.024724 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2021-12-15 07:57 | 2021-12-15 12:28 | 120 | 004:31 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21121500015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 271 | 2021-12-15 | 32520 | keep | 0 | Dec | 2021 | 0.022149 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2021-12-15 08:03 | 2021-12-15 13:32 | 40 | 005:29 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE Y SE REPARO SECUNDARIA | B21121500019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 329 | 2021-12-15 | 13160 | keep | 0 | Dec | 2021 | 0.0089632 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-12-15 08:16 | 2021-12-16 18:40 | 20 | 034:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | M21121500021 | New_Event | Wire Down | Include | Include | Equipment | 2064 | 2021-12-15 | 41280 | keep | 0 | Dec | 2021 | 0.028116 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2021-12-15 08:26 | 2021-12-15 09:40 | 15 | 001:14 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE INFORMO QUE EL SECTOR NECESITA DESGANCHE | A21121500021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2021-12-15 | 1110 | keep | 0 | Dec | 2021 | 0.00075602 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-12-15 08:27 | 2021-12-15 12:04 | 1 | 003:37 | P | OTRAS CAUSAS | 1 X 40 EN CORTE DE LINEA EQUIPO DE MEDICION DEL CLIENTE | R21121500014 | New_Event | Other Causes | Include | Include | Other | 217 | 2021-12-15 | 217 | keep | 0 | Dec | 2021 | 0.0001478 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2021-12-15 08:31 | 2021-12-15 12:31 | 5 | 004:00 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PRIMARIO Y TRANSFORMADOR DE 25 KVA X 25 KVA | C21121500019 | New_Event | Defective Pole | Include | Include | Equipment | 240 | 2021-12-15 | 1200 | keep | 0 | Dec | 2021 | 0.00081731 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-12-15 08:35 | 2021-12-15 11:18 | 1 | 002:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN RISER SE REMPLAZO CAJA PRIMARIA AVERIADA | P21121500009 | New_Event | Cutout Failure | Include | Include | Equipment | 163 | 2021-12-15 | 163 | keep | 0 | Dec | 2021 | 0.00011102 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-15 08:38 | 2021-12-15 08:40 | 10211 | 000:02 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1206-3 | S21121500016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-15 | 20422 | keep | 0 | Dec | 2021 | 0.013909 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-12-15 08:38 | 2021-12-15 08:40 | 4133 | 000:02 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1204-5 | S21121500016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-15 | 8266 | keep | 0 | Dec | 2021 | 0.0056299 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
YAUCO | 2021-12-15 08:39 | 2021-12-15 13:15 | 30 | 004:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA CERRAR PUENTE PRIMARIO | P21121500011 | New_Event | Wire Down | Include | Include | Equipment | 276 | 2021-12-15 | 8280 | keep | 0 | Dec | 2021 | 0.0056395 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2021-12-15 08:40 | 2021-12-15 08:41 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21121500025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-15 | 3041 | keep | 0 | Dec | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2021-12-15 08:44 | 2021-12-15 11:10 | 25 | 002:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE AVERIADO | M21121500026 | New_Event | Cutout Failure | Include | Include | Equipment | 146 | 2021-12-15 | 3650 | keep | 0 | Dec | 2021 | 0.002486 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2021-12-15 08:49 | 2021-12-15 09:05 | 10 | 000:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21121500008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 16 | 2021-12-15 | 160 | keep | 0 | Dec | 2021 | 0.00010898 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-15 08:51 | 2021-12-15 10:15 | 70 | 001:24 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L Y 1 X 25 EN OTRO C/L | S21121500017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2021-12-15 | 5880 | keep | 0 | Dec | 2021 | 0.0040048 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BARRANQUITAS | 2021-12-15 08:55 | 2021-12-15 08:56 | 2725 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 8500 DE SANTA ISABEL A CAYEY | C21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-15 | 2725 | keep | 0 | Dec | 2021 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2021-12-15 08:55 | 2021-12-15 08:56 | 1834 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 8500 DE SANTA ISABEL A CAYEY | C21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-15 | 1834 | keep | 0 | Dec | 2021 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2021-12-15 08:55 | 2021-12-15 08:56 | 1437 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 8500 DE SANTA ISABEL A CAYEY | C21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-15 | 1437 | keep | 0 | Dec | 2021 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2021-12-15 08:55 | 2021-12-15 08:56 | 2565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 8500 DE SANTA ISABEL A CAYEY | C21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-15 | 2565 | keep | 0 | Dec | 2021 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2021-12-15 08:55 | 2021-12-15 08:56 | 3565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 8500 DE SANTA ISABEL A CAYEY | C21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-15 | 3565 | keep | 0 | Dec | 2021 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
PONCE | 2021-12-15 08:55 | 2021-12-15 08:56 | 2751 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P21121500016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-15 | 2751 | keep | 0 | Dec | 2021 | 0.0018737 | 0.0018737 | Momentary | FALSE | FALSE | Not_TMED_Event | 2751
PONCE | 2021-12-15 08:55 | 2021-12-15 08:56 | 576 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P21121500016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-15 | 576 | keep | 0 | Dec | 2021 | 0.00039231 | 0.00039231 | Momentary | FALSE | FALSE | Not_TMED_Event | 576
PONCE | 2021-12-15 08:55 | 2021-12-15 08:56 | 2584 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P21121500016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-15 | 2584 | keep | 0 | Dec | 2021 | 0.00176 | 0.00176 | Momentary | FALSE | FALSE | Not_TMED_Event | 2584
PONCE | 2021-12-15 08:55 | 2021-12-15 08:56 | 1606 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P21121500016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-15 | 1606 | keep | 0 | Dec | 2021 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
PONCE | 2021-12-15 08:55 | 2021-12-15 08:56 | 29 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P21121500016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-15 | 29 | keep | 0 | Dec | 2021 | 1.9752e-05 | 1.9752e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 29
PONCE | 2021-12-15 08:55 | 2021-12-15 08:56 | 4035 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P21121500016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-15 | 4035 | keep | 0 | Dec | 2021 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
PONCE | 2021-12-15 08:55 | 2021-12-15 08:56 | 3718 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P21121500016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-15 | 3718 | keep | 0 | Dec | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
HUMACAO | 2021-12-15 09:05 | 2021-12-15 09:51 | 39 | 000:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BAJANTE SECUNDARIO | C21121400129 | New_Event | Secondary Wire Down | Include | Include | Equipment | 46 | 2021-12-15 | 1794 | keep | 0 | Dec | 2021 | 0.0012219 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
FAJARDO | 2021-12-15 09:09 | 2021-12-15 09:10 | 3003 | 000:01 | T | DESGANCHE | RECIERRE | R21121500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-15 | 3003 | keep | 0 | Dec | 2021 | 0.0020453 | 0.0020453 | Momentary | FALSE | FALSE | Not_TMED_Event | 3003
FAJARDO | 2021-12-15 09:10 | 2021-12-15 10:51 | 80 | 001:41 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | R21121500019 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 101 | 2021-12-15 | 8080 | keep | 0 | Dec | 2021 | 0.0055033 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2021-12-15 09:11 | 2021-12-15 11:05 | 3 | 001:54 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REEMPLAZO PISTOLA EN PM NO ROTULADO | C21121500021 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 114 | 2021-12-15 | 342 | keep | 0 | Dec | 2021 | 0.00023293 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2021-12-15 09:25 | 2021-12-15 11:16 | 40 | 001:51 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21121500025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2021-12-15 | 4440 | keep | 0 | Dec | 2021 | 0.0030241 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-12-15 09:25 | 2021-12-15 11:21 | 35 | 001:56 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21121500027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2021-12-15 | 4060 | keep | 0 | Dec | 2021 | 0.0027652 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
GUAYAMA | 2021-12-15 09:37 | 2021-12-15 13:48 | 66 | 004:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P21121500020 | New_Event |  |  | Include | Wildlife | 251 | 2021-12-15 | 16566 | keep | 0 | Dec | 2021 | 0.011283 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
ARECIBO | 2021-12-15 09:38 | 2021-12-15 13:35 | 1 | 003:57 | P | OTRAS CAUSAS | 2 X 30 EN RISER PROBLEMA EN GABINETE DEL CLIENTE | A21121500032 | New_Event | Other Causes | Include | Include | Other | 237 | 2021-12-15 | 237 | keep | 0 | Dec | 2021 | 0.00016142 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-12-15 09:40 | 2021-12-15 10:22 | 6 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR BARRAS EN EL PEDESTAL | A21121300118 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2021-12-15 | 252 | keep | 0 | Dec | 2021 | 0.00017164 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-12-15 09:42 | 2021-12-15 13:36 | 842 | 003:54 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADORES ROTOS Y SE CERRO MACHETES | A21121500037 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 234 | 2021-12-15 | 197028 | keep | 0 | Dec | 2021 | 0.13419 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-12-15 09:47 | 2021-12-15 11:38 | 20 | 001:51 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21121500039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2021-12-15 | 2220 | keep | 0 | Dec | 2021 | 0.001512 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2021-12-15 09:50 | 2021-12-15 15:04 | 120 | 005:14 | P | HERRAJE ROTO O PODRIDO | SE ABRIO CORTE DE LINEA PARA REMPLAZAR CRUCETA PARTIDA | M21121500035 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 314 | 2021-12-15 | 37680 | keep | 0 | Dec | 2021 | 0.025664 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2021-12-15 09:58 | 2021-12-15 11:00 | 80 | 001:02 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L Y 1 X 50 EN OTRO C/L | S21121500025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 62 | 2021-12-15 | 4960 | keep | 0 | Dec | 2021 | 0.0033782 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-12-15 10:10 | 2021-12-15 13:52 | 100 | 003:42 | P | DESGANCHE | 2 X 65 EN C/L SE RETIRO BAMBUAS | B21121500031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2021-12-15 | 22200 | keep | 0 | Dec | 2021 | 0.01512 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-12-15 10:17 | 2021-12-15 11:33 | 40 | 001:16 | P | NO SE REPORTO CAUSA | 1 X 65 EN AEREO PROVISIONAL | B21121500033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 76 | 2021-12-15 | 3040 | keep | 0 | Dec | 2021 | 0.0020705 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2021-12-15 10:23 | 2021-12-15 11:33 | 1 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A21121500039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2021-12-15 | 70 | keep | 0 | Dec | 2021 | 4.7677e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-12-15 10:43 | 2021-12-15 14:59 | 18 | 004:16 | P | DESGANCHE | 1 X 40 EN C/L | R21121500028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 256 | 2021-12-15 | 4608 | keep | 0 | Dec | 2021 | 0.0031385 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CANOVANAS | 2021-12-15 11:06 | 2021-12-15 14:14 | 10 | 003:08 | P | DESGANCHE | 1 X 40 EN C/L | R21121500031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2021-12-15 | 1880 | keep | 0 | Dec | 2021 | 0.0012805 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-12-15 11:21 | 2021-12-15 11:23 | 2216 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE VERIFICO PERSONAL FUERA DE DESGANCHE Y SE CERRO POR SCADA | B21121500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-15 | 4432 | keep | 0 | Dec | 2021 | 0.0030186 | 0.0015093 | Momentary | FALSE | FALSE | Not_TMED_Event | 2216
VEGA BAJA | 2021-12-15 11:23 | 2021-12-15 21:13 | 35 | 009:50 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21121500027 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 590 | 2021-12-15 | 20650 | keep | 0 | Dec | 2021 | 0.014065 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2021-12-15 11:32 | 2021-12-15 11:33 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21121500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-15 | 2203 | keep | 0 | Dec | 2021 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2021-12-15 11:42 | 2021-12-15 12:03 | 1825 | 000:21 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2021-12-15 | 38325 | keep | 0 | Dec | 2021 | 0.026103 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2021-12-15 11:42 | 2021-12-15 12:03 | 47 | 000:21 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2021-12-15 | 987 | keep | 0 | Dec | 2021 | 0.00067224 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
SAN JUAN | 2021-12-15 11:42 | 2021-12-15 12:03 | 315 | 000:21 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2021-12-15 | 6615 | keep | 0 | Dec | 2021 | 0.0045054 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
SAN JUAN | 2021-12-15 11:42 | 2021-12-15 12:03 | 2 | 000:21 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2021-12-15 | 42 | keep | 0 | Dec | 2021 | 2.8606e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2021-12-15 11:42 | 2021-12-15 12:03 | 2391 | 000:21 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2021-12-15 | 50211 | keep | 0 | Dec | 2021 | 0.034198 | 0.0016285 | Sustained | FALSE | FALSE | Not_TMED_Event | 2391
CAGUAS | 2021-12-15 11:42 | 2021-12-15 12:05 | 1153 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE BAIROA A CAGUAS | C21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-12-15 | 26519 | keep | 0 | Dec | 2021 | 0.018062 | 0.0007853 | Sustained | FALSE | FALSE | Not_TMED_Event | 1153
CAGUAS | 2021-12-15 11:42 | 2021-12-15 12:05 | 1709 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE BAIROA A CAGUAS | C21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-12-15 | 39307 | keep | 0 | Dec | 2021 | 0.026772 | 0.001164 | Sustained | FALSE | FALSE | Not_TMED_Event | 1709
CAGUAS | 2021-12-15 11:42 | 2021-12-15 12:05 | 1320 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE BAIROA A CAGUAS | C21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-12-15 | 30360 | keep | 0 | Dec | 2021 | 0.020678 | 0.00089905 | Sustained | FALSE | FALSE | Not_TMED_Event | 1320
CAGUAS | 2021-12-15 11:42 | 2021-12-15 12:05 | 2276 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE BAIROA A CAGUAS | C21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-12-15 | 52348 | keep | 0 | Dec | 2021 | 0.035654 | 0.0015502 | Sustained | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2021-12-15 11:42 | 2021-12-15 12:05 | 777 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE BAIROA A CAGUAS | C21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-12-15 | 17871 | keep | 0 | Dec | 2021 | 0.012172 | 0.00052921 | Sustained | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2021-12-15 11:42 | 2021-12-15 12:05 | 12 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE BAIROA A CAGUAS | C21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-12-15 | 276 | keep | 0 | Dec | 2021 | 0.00018798 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-12-15 11:42 | 2021-12-15 12:05 | 1290 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE BAIROA A CAGUAS | C21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-12-15 | 29670 | keep | 0 | Dec | 2021 | 0.020208 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
BARRANQUITAS | 2021-12-15 12:08 | 2021-12-15 15:37 | 40 | 003:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21121500047 | New_Event | Bad Weather | Include | Include | Weather | 209 | 2021-12-15 | 8360 | keep | 0 | Dec | 2021 | 0.005694 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-12-15 12:10 | 2021-12-15 16:31 | 40 | 004:21 | P | DESGANCHE | 1 X 50 EN C/L | R21121500032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 261 | 2021-12-15 | 10440 | keep | 0 | Dec | 2021 | 0.0071106 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-12-15 12:20 | 2021-12-15 12:21 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-15 | 1617 | keep | 0 | Dec | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-12-15 12:20 | 2021-12-15 12:21 | 1017 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-15 | 1017 | keep | 0 | Dec | 2021 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-12-15 12:20 | 2021-12-15 12:21 | 828 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-15 | 828 | keep | 0 | Dec | 2021 | 0.00056395 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
MAYAGÃœEZ | 2021-12-15 12:20 | 2021-12-15 12:21 | 863 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-15 | 863 | keep | 0 | Dec | 2021 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2021-12-15 12:20 | 2021-12-15 12:21 | 309 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-15 | 309 | keep | 0 | Dec | 2021 | 0.00021046 | 0.00021046 | Momentary | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2021-12-15 12:20 | 2021-12-15 12:21 | 176 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-15 | 176 | keep | 0 | Dec | 2021 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
ARECIBO | 2021-12-15 12:38 | 2021-12-15 14:38 | 150 | 002:00 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA LINEAS CRUZADAS POR RAMA DE ARBOL | A21121500051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2021-12-15 | 18000 | keep | 0 | Dec | 2021 | 0.01226 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2021-12-15 12:44 | 2021-12-15 14:06 | 70 | 001:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21121500059 | New_Event | Bad Weather | Include | Include | Weather | 82 | 2021-12-15 | 5740 | keep | 0 | Dec | 2021 | 0.0039095 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2021-12-15 12:45 | 2021-12-15 12:47 | 1225 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA 1203-3 SE VERIFICO CON PERSONAL PRIVADO Y INDICARON ESTAN EN HORA ALMUERZO SE PROBO QUEDO EN SERVICIO | S21121500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-15 | 2450 | keep | 0 | Dec | 2021 | 0.0016687 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2021-12-15 12:45 | 2021-12-15 12:47 | 616 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SU CARGA POR 1203-1 SE VERIFICO CON PERSONAL PRIVADO EN ESTAN FUERA DE LINEA QUEDO EN SERVICIO | S21121500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-15 | 1232 | keep | 0 | Dec | 2021 | 0.00083911 | 0.00041955 | Momentary | FALSE | FALSE | Not_TMED_Event | 616
VEGA BAJA | 2021-12-15 12:55 | 2021-12-15 14:31 | 30 | 001:36 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B21121500047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2021-12-15 | 2880 | keep | 0 | Dec | 2021 | 0.0019616 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-15 12:57 | 2021-12-15 14:38 | 65 | 001:41 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B21121500048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 101 | 2021-12-15 | 6565 | keep | 0 | Dec | 2021 | 0.0044714 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2021-12-15 12:58 | 2021-12-15 15:10 | 60 | 002:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M21121500068 | New_Event | Bad Weather | Include | Include | Weather | 132 | 2021-12-15 | 7920 | keep | 0 | Dec | 2021 | 0.0053943 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2021-12-15 12:58 | 2021-12-15 16:53 | 10 | 003:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B21121500049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 235 | 2021-12-15 | 2350 | keep | 0 | Dec | 2021 | 0.0016006 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-15 13:02 | 2021-12-15 16:28 | 30 | 003:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21121500054 | New_Event | Bad Weather | Include | Include | Weather | 206 | 2021-12-15 | 6180 | keep | 0 | Dec | 2021 | 0.0042092 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-12-15 13:09 | 2021-12-15 16:15 | 100 | 003:06 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M21121500070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2021-12-15 | 18600 | keep | 0 | Dec | 2021 | 0.012668 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2021-12-15 13:15 | 2021-12-15 14:10 | 100 | 000:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA CERRAR PUENTE PRIMARIO | P21121500011 | New_Event | Wire Down | Include | Include | Equipment | 55 | 2021-12-15 | 5500 | keep | 0 | Dec | 2021 | 0.003746 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2021-12-15 13:15 | 2021-12-15 16:50 | 6 | 003:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B21121500052 | New_Event | Secondary Wire Down | Include | Include | Equipment | 215 | 2021-12-15 | 1290 | keep | 0 | Dec | 2021 | 0.00087861 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-12-15 13:16 | 2021-12-15 14:42 | 36 | 001:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L PAJARO SE RETIRO DE LINEA | S21121500043 | New_Event |  |  | Include | Wildlife | 86 | 2021-12-15 | 3096 | keep | 0 | Dec | 2021 | 0.0021087 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
BAYAMON | 2021-12-15 13:22 | 2021-12-15 16:17 | 25 | 002:55 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER Y 1 X 80 EN SU-1 | B21121500056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 175 | 2021-12-15 | 4375 | keep | 0 | Dec | 2021 | 0.0029798 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-12-15 13:22 | 2021-12-15 19:39 | 65 | 006:17 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 40 EN C/L | B21121500055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 377 | 2021-12-15 | 24505 | keep | 0 | Dec | 2021 | 0.01669 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2021-12-15 13:25 | 2021-12-15 18:19 | 24 | 004:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA RADIAL QUE DA SERVICIO A DOS TRANSFORMADORES | S21121500044 | New_Event | Wire Down | Include | Include | Equipment | 294 | 2021-12-15 | 7056 | keep | 0 | Dec | 2021 | 0.0048058 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
MAYAGÃœEZ | 2021-12-15 13:43 | 2021-12-15 13:44 | 4381 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21121500082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-15 | 4381 | keep | 0 | Dec | 2021 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
ARECIBO | 2021-12-15 13:44 | 2021-12-15 21:30 | 15 | 007:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA Y HERRAJE | A21121500114 | New_Event | Cutout Failure | Include | Include | Equipment | 466 | 2021-12-15 | 6990 | keep | 0 | Dec | 2021 | 0.0047609 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-12-15 13:48 | 2021-12-15 16:55 | 40 | 003:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21121500084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2021-12-15 | 7480 | keep | 0 | Dec | 2021 | 0.0050946 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-12-15 13:53 | 2021-12-15 16:18 | 11 | 002:25 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE DESGANCHO ENREDADERA | C21121500068 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 145 | 2021-12-15 | 1595 | keep | 0 | Dec | 2021 | 0.0010863 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
VEGA BAJA | 2021-12-15 13:53 | 2021-12-15 21:20 | 6 | 007:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B21121500059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 447 | 2021-12-15 | 2682 | keep | 0 | Dec | 2021 | 0.0018267 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-12-15 13:56 | 2021-12-15 17:20 | 36 | 003:24 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B21121500061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 204 | 2021-12-15 | 7344 | keep | 0 | Dec | 2021 | 0.005002 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
AGUADILLA | 2021-12-15 13:57 | 2021-12-15 14:20 | 1192 | 000:23 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON RECIERRE EN OFF SE VERIFICO PERSONAL FUERA DEL AREA | M21121500089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 23 | 2021-12-15 | 27416 | keep | 0 | Dec | 2021 | 0.018673 | 0.00081187 | Sustained | FALSE | FALSE | Not_TMED_Event | 1192
ARECIBO | 2021-12-15 13:59 | 2021-12-15 18:09 | 1 | 004:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES EN EL TRANSFORMADOR | A21121500068 | New_Event | Secondary Wire Down | Include | Include | Equipment | 250 | 2021-12-15 | 250 | keep | 0 | Dec | 2021 | 0.00017027 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-12-15 14:01 | 2021-12-15 20:53 | 25 | 006:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN C/L SE LLEVO LINEA A AISLADOR | B21121500069 | New_Event | Wire Down | Include | Include | Equipment | 412 | 2021-12-15 | 10300 | keep | 0 | Dec | 2021 | 0.0070153 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-12-15 14:01 | 2021-12-15 16:42 | 65 | 002:41 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B21121500063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 161 | 2021-12-15 | 10465 | keep | 0 | Dec | 2021 | 0.0071277 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
YAUCO | 2021-12-15 14:03 | 2021-12-15 17:21 | 101 | 003:18 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P21121500038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2021-12-15 | 19998 | keep | 0 | Dec | 2021 | 0.013621 | 6.8791e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 101
CANOVANAS | 2021-12-15 14:07 | 2021-12-15 14:27 | 30 | 000:20 | P | DESGANCHE | 1 X 30 EN C/L | R21121500038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 20 | 2021-12-15 | 600 | keep | 0 | Dec | 2021 | 0.00040866 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-12-15 14:07 | 2021-12-15 16:29 | 119 | 002:22 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21121500073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2021-12-15 | 16898 | keep | 0 | Dec | 2021 | 0.011509 | 8.105e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 119
SAN JUAN | 2021-12-15 14:10 | 2021-12-15 15:27 | 20 | 001:17 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L NO CAUSA | R21121500039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 77 | 2021-12-15 | 1540 | keep | 0 | Dec | 2021 | 0.0010489 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-12-15 14:10 | 2021-12-15 14:11 | 4381 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21121500092 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-15 | 4381 | keep | 0 | Dec | 2021 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
SAN JUAN | 2021-12-15 14:15 | 2021-12-15 14:16 | 552 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1206-04 QUE A SU VEZ LLEVA LA CARGA PARCIAL DE LOS ALIMENTADORES 1204-04 UN 40% Y 1204-03 UN 60% | S21121500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-15 | 552 | keep | 0 | Dec | 2021 | 0.00037596 | 0.00037596 | Momentary | FALSE | FALSE | Not_TMED_Event | 552
SAN JUAN | 2021-12-15 14:15 | 2021-12-15 14:16 | 2966 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1206-04 QUE A SU VEZ LLEVA LA CARGA PARCIAL DE LOS ALIMENTADORES 1204-04 UN 40% Y 1204-03 UN 60% | S21121500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-15 | 2966 | keep | 0 | Dec | 2021 | 0.0020201 | 0.0020201 | Momentary | FALSE | FALSE | Not_TMED_Event | 2966
SAN JUAN | 2021-12-15 14:15 | 2021-12-15 14:16 | 1799 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1206-04 QUE A SU VEZ LLEVA LA CARGA PARCIAL DE LOS ALIMENTADORES 1204-04 UN 40% Y 1204-03 UN 60% | S21121500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-15 | 1799 | keep | 0 | Dec | 2021 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
CAGUAS | 2021-12-15 14:37 | 2021-12-15 18:23 | 41 | 003:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | C21121500080 | New_Event | Bad Weather | Include | Include | Weather | 226 | 2021-12-15 | 9266 | keep | 0 | Dec | 2021 | 0.006311 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
CAGUAS | 2021-12-15 14:41 | 2021-12-15 15:36 | 84 | 000:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA CRUCE POR AVE | C21121500082 | New_Event |  |  | Include | Wildlife | 55 | 2021-12-15 | 4620 | keep | 0 | Dec | 2021 | 0.0031467 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
BAYAMON | 2021-12-15 14:52 | 2021-12-15 18:09 | 6 | 003:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21121500069 | New_Event | Secondary Wire Down | Include | Include | Equipment | 197 | 2021-12-15 | 1182 | keep | 0 | Dec | 2021 | 0.00080505 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-12-15 14:54 | 2021-12-15 17:00 | 50 | 002:06 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN C/L SE REMPLAZO PARARRAYO Y SE REALIZO PODA | B21121500072 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 126 | 2021-12-15 | 6300 | keep | 0 | Dec | 2021 | 0.0042909 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-12-15 15:10 | 2021-12-15 15:40 | 1 | 000:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN RISER AVE CRUZO FASE | P21121500045 | New_Event |  |  | Include | Wildlife | 30 | 2021-12-15 | 30 | keep | 0 | Dec | 2021 | 2.0433e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-12-15 15:15 | 2021-12-16 11:12 | 1 | 019:57 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21121500090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1197 | 2021-12-15 | 1197 | keep | 0 | Dec | 2021 | 0.00081527 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-12-15 15:20 | 2021-12-15 21:30 | 15 | 006:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | A21121500082 | New_Event | Cutout Failure | Include | Include | Equipment | 370 | 2021-12-15 | 5550 | keep | 0 | Dec | 2021 | 0.0037801 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-12-15 15:23 | 2021-12-15 16:28 | 40 | 001:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CRUCE X AVE | R21121500042 | New_Event |  |  | Include | Wildlife | 65 | 2021-12-15 | 2600 | keep | 0 | Dec | 2021 | 0.0017708 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-12-15 15:24 | 2021-12-15 18:35 | 50 | 003:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASES | M21121500108 | New_Event |  |  | Include | Wildlife | 191 | 2021-12-15 | 9550 | keep | 0 | Dec | 2021 | 0.0065045 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-12-15 15:39 | 2021-12-15 18:44 | 8 | 003:05 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21121500098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2021-12-15 | 1480 | keep | 0 | Dec | 2021 | 0.001008 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-12-15 15:44 | 2021-12-15 19:06 | 80 | 003:22 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA Y SE REALIZO DESGANCHE PRIMARIO | S21121500054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2021-12-15 | 16160 | keep | 0 | Dec | 2021 | 0.011007 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2021-12-15 16:01 | 2021-12-15 16:02 | 1397 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21121500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-15 | 1397 | keep | 0 | Dec | 2021 | 0.00095149 | 0.00095149 | Momentary | FALSE | FALSE | Not_TMED_Event | 1397
ARECIBO | 2021-12-15 16:04 | 2021-12-15 18:36 | 8 | 002:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA Y NEUTRAL | A21121500087 | New_Event | Secondary Wire Down | Include | Include | Equipment | 152 | 2021-12-15 | 1216 | keep | 0 | Dec | 2021 | 0.00082821 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2021-12-15 16:11 | 2021-12-16 12:28 | 172 | 020:17 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | P21121500049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1217 | 2021-12-15 | 209324 | keep | 0 | Dec | 2021 | 0.14257 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
BAYAMON | 2021-12-15 16:12 | 2021-12-15 16:15 | 948 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21121500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-12-15 | 2844 | keep | 0 | Dec | 2021 | 0.001937 | 0.00064568 | Momentary | FALSE | FALSE | Not_TMED_Event | 948
UTUADO | 2021-12-15 16:24 | 2021-12-15 17:20 | 60 | 000:56 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA RAMA CRUZO LINEAS PRIMARIAS | A21121500088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2021-12-15 | 3360 | keep | 0 | Dec | 2021 | 0.0022885 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-12-15 16:26 | 2021-12-15 17:33 | 12 | 001:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA RELOCALIZAR TOMA | R21121500043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 67 | 2021-12-15 | 804 | keep | 0 | Dec | 2021 | 0.0005476 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-12-15 16:30 | 2021-12-15 16:31 | 418 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | S21121500044 | New_Event |  |  | Include | Wildlife | 1 | 2021-12-15 | 418 | keep | 0 | Dec | 2021 | 0.0002847 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
CAGUAS | 2021-12-15 16:35 | 2021-12-15 17:07 | 60 | 000:32 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21121500108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 32 | 2021-12-15 | 1920 | keep | 0 | Dec | 2021 | 0.0013077 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-12-15 16:40 | 2021-12-15 16:42 | 418 | 000:02 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO INTERRUPTOR PARA RETIRAR GLOBO METALICO CRUZANDO LAS LINEAS | S21121500000 | 1st_after_momentary |  |  | Include | Wildlife | 2 | 2021-12-15 | 836 | keep | 0 | Dec | 2021 | 0.0005694 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
BAYAMON | 2021-12-15 16:40 | 2021-12-15 16:41 | 514 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1520-05 QUE LLEVA LA CARGA DEL 1520-01 Y 1520-04 | S21121500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-15 | 514 | keep | 0 | Dec | 2021 | 0.00035008 | 0.00035008 | Momentary | FALSE | FALSE | Not_TMED_Event | 514
BAYAMON | 2021-12-15 16:40 | 2021-12-15 16:41 | 752 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1520-05 QUE LLEVA LA CARGA DEL 1520-01 Y 1520-04 | S21121500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-15 | 752 | keep | 0 | Dec | 2021 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
BAYAMON | 2021-12-15 16:40 | 2021-12-15 16:41 | 68 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1520-05 QUE LLEVA LA CARGA DEL 1520-01 Y 1520-04 | S21121500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-15 | 68 | keep | 0 | Dec | 2021 | 4.6314e-05 | 4.6314e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 68
HUMACAO | 2021-12-15 16:50 | 2021-12-15 21:20 | 9 | 004:30 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO Y REPARARON NEUTRAL PRIMARIO | C21121500111 | New_Event | Service Transformer Failure | Include | Include | Equipment | 270 | 2021-12-15 | 2430 | keep | 0 | Dec | 2021 | 0.0016551 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
YAUCO | 2021-12-15 16:54 | 2021-12-15 19:27 | 140 | 002:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA EN CORTE DE LINEA | P21121500051 | New_Event | Cutout Failure | Include | Include | Equipment | 153 | 2021-12-15 | 21420 | keep | 0 | Dec | 2021 | 0.014589 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
ARECIBO | 2021-12-15 17:06 | 2021-12-15 19:05 | 25 | 001:59 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A21121500092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2021-12-15 | 2975 | keep | 0 | Dec | 2021 | 0.0020263 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-12-15 17:10 | 2021-12-15 17:36 | 15 | 000:26 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR Y SE REALIZO DESGANCHE PRIMARIO | S21121500009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 26 | 2021-12-15 | 390 | keep | 0 | Dec | 2021 | 0.00026563 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-12-15 17:12 | 2021-12-15 20:58 | 6 | 003:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21121500093 | New_Event | Bad Weather | Include | Include | Weather | 226 | 2021-12-15 | 1356 | keep | 0 | Dec | 2021 | 0.00092357 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-12-15 17:20 | 2021-12-15 19:08 | 20 | 001:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA LINEAS CRUZADAS | A21121500095 | New_Event | Wire Down | Include | Include | Equipment | 108 | 2021-12-15 | 2160 | keep | 0 | Dec | 2021 | 0.0014712 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-12-15 17:25 | 2021-12-16 10:47 | 8 | 017:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | A21121500096 | New_Event | Bad Weather | Include | Include | Weather | 1042 | 2021-12-15 | 8336 | keep | 0 | Dec | 2021 | 0.0056776 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-12-15 17:47 | 2021-12-15 20:10 | 80 | 002:23 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 40 EN CORTE DE LINEA SE REMPLAZARON AISLADORES | A21121500102 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 143 | 2021-12-15 | 11440 | keep | 0 | Dec | 2021 | 0.0077917 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-12-15 17:52 | 2021-12-16 09:20 | 25 | 015:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M21121500122 | New_Event | Bad Weather | Include | Include | Weather | 928 | 2021-12-15 | 23200 | keep | 0 | Dec | 2021 | 0.015801 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-12-15 17:54 | 2021-12-16 17:41 | 27 | 023:47 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN C/L SE REMPLAZO AISLADOR | B21121500089 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1427 | 2021-12-15 | 38529 | keep | 0 | Dec | 2021 | 0.026242 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
CAGUAS | 2021-12-15 17:55 | 2021-12-16 11:35 | 90 | 017:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | C21121500122 | New_Event |  |  | Include | Wildlife | 1060 | 2021-12-15 | 95400 | keep | 0 | Dec | 2021 | 0.064977 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2021-12-15 17:58 | 2021-12-15 21:46 | 80 | 003:48 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B21121500090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 228 | 2021-12-15 | 18240 | keep | 0 | Dec | 2021 | 0.012423 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2021-12-15 18:04 | 2021-12-15 18:05 | 551 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | C21121500123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-15 | 551 | keep | 0 | Dec | 2021 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
HUMACAO | 2021-12-15 18:05 | 2021-12-16 10:50 | 1 | 016:45 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21121600125 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1005 | 2021-12-15 | 1005 | keep | 0 | Dec | 2021 | 0.0006845 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-15 18:26 | 2021-12-15 22:38 | 30 | 004:12 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21121500081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 252 | 2021-12-15 | 7560 | keep | 0 | Dec | 2021 | 0.0051491 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-15 18:47 | 2021-12-16 10:49 | 30 | 016:02 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21121500133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 962 | 2021-12-15 | 28860 | keep | 0 | Dec | 2021 | 0.019656 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2021-12-15 19:18 | 2021-12-15 22:42 | 10 | 003:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN TRANSFORMADOR SE REPARO PUENTE DE LINEA A CAJA Y SE REALIZO DESGANCHE | B21121500010 | New_Event | Cutout Failure | Include | Include | Equipment | 204 | 2021-12-15 | 2040 | keep | 0 | Dec | 2021 | 0.0013894 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-15 19:24 | 2021-12-15 21:31 | 25 | 002:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21121500085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2021-12-15 | 3175 | keep | 0 | Dec | 2021 | 0.0021625 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2021-12-15 20:02 | 2021-12-15 20:03 | 1089 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A RIO BLANCO | C21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-15 | 1089 | keep | 0 | Dec | 2021 | 0.00074171 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2021-12-15 20:02 | 2021-12-15 20:03 | 3896 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A RIO BLANCO | C21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-15 | 3896 | keep | 0 | Dec | 2021 | 0.0026535 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2021-12-15 20:02 | 2021-12-15 20:03 | 1467 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A RIO BLANCO | C21121500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-15 | 1467 | keep | 0 | Dec | 2021 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
MAYAGÃœEZ | 2021-12-15 20:15 | 2021-12-15 22:29 | 2067 | 002:14 | T | CABLE SOTERRADO AVERIADO | AVERIA EN LA SALIDA DEL ALIMENTADOR SE TRANSFIRIO LA CARGA AL 6012-02 | M21121500134 | New_Event | UG Cable Fault | Include | Include | Equipment | 134 | 2021-12-15 | 276978 | keep | 0 | Dec | 2021 | 0.18865 | 0.0014078 | Sustained | FALSE | FALSE | Not_TMED_Event | 2067
HUMACAO | 2021-12-15 20:40 | 2021-12-16 12:23 | 100 | 015:43 | P | DESGANCHE | 2 X 50 EN CORTES DE LINEA | C21121500137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 943 | 2021-12-15 | 94300 | keep | 0 | Dec | 2021 | 0.064227 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-12-15 20:49 | 2021-12-16 00:21 | 10 | 003:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE LINEA A CAJA EN RISER | S21121500091 | New_Event | Wire Down | Include | Include | Equipment | 212 | 2021-12-15 | 2120 | keep | 0 | Dec | 2021 | 0.0014439 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-12-15 21:20 | 2021-12-15 22:08 | 8 | 000:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN XMR REMPLAZO PORTAFUSIBLE | R21121500049 | New_Event | Cutout Failure | Include | Include | Equipment | 48 | 2021-12-15 | 384 | keep | 0 | Dec | 2021 | 0.00026154 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2021-12-15 21:26 | 2021-12-16 16:13 | 397 | 018:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA Y SE INSTALO CORNED BRAKET | R21121500050 | New_Event | Wire Down | Include | Include | Equipment | 1127 | 2021-12-15 | 447419 | keep | 0 | Dec | 2021 | 0.30474 | 0.00027039 | Sustained | FALSE | FALSE | Not_TMED_Event | 397
ARECIBO | 2021-12-15 21:30 | 2021-12-15 22:46 | 1831 | 001:16 | T | HERRAJE ROTO O PODRIDO | SE ABRIO INTERRUPTOR A PETICION DEL JOURNEYMAN PARA REMPLAZO HERRAJE CORROIDO | A21121500119 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 76 | 2021-12-15 | 139156 | keep | 0 | Dec | 2021 | 0.094779 | 0.0012471 | Sustained | FALSE | FALSE | Not_TMED_Event | 1831
MAYAGÃœEZ | 2021-12-15 22:28 | 2021-12-15 22:29 | 4664 | 000:01 | T | CABLE SOTERRADO AVERIADO | SE ABRIO INTERRUPTOR A PETICION DEL JOURNEYMAN PARA CERRAR AMARRE CON EL 6012-03 | M21121500161 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2021-12-15 | 4664 | keep | 0 | Dec | 2021 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
BAYAMON | 2021-12-15 22:31 | 2021-12-15 23:47 | 40 | 001:16 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21121500107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 76 | 2021-12-15 | 3040 | keep | 0 | Dec | 2021 | 0.0020705 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-12-15 22:43 | 2021-12-16 15:58 | 12 | 017:15 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | S21121500102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1035 | 2021-12-15 | 12420 | keep | 0 | Dec | 2021 | 0.0084592 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-12-15 22:46 | 2021-12-16 10:19 | 15 | 011:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | A21121500082 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 693 | 2021-12-15 | 10395 | keep | 0 | Dec | 2021 | 0.00708 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-12-15 23:12 | 2021-12-15 23:28 | 20 | 000:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR NEUTRAL PRIMARIO | A21121500120 | New_Event | Wire Down | Include | Include | Equipment | 16 | 2021-12-15 | 320 | keep | 0 | Dec | 2021 | 0.00021795 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-12-15 23:49 | 2021-12-16 13:36 | 2 | 013:47 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | C21121500148 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 827 | 2021-12-15 | 1654 | keep | 0 | Dec | 2021 | 0.0011265 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2021-12-16 00:14 | 2021-12-16 15:25 | 100 | 015:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA DE CORTE DE LINEA | A21121600001 | New_Event | Cutout Failure | Include | Include | Equipment | 911 | 2021-12-16 | 91100 | keep | 0 | Dec | 2021 | 0.062048 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-12-16 02:11 | 2021-12-16 12:46 | 99 | 010:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIAS | C21121600003 | New_Event | Bad Weather | Include | Include | Weather | 635 | 2021-12-16 | 62865 | keep | 0 | Dec | 2021 | 0.042817 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
ARECIBO | 2021-12-16 02:38 | 2021-12-16 11:17 | 20 | 008:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 25 EN CORTE DE LINEA SE REPARO LINEAS PARTIDAS | A21121600003 | New_Event | Wire Down | Include | Include | Equipment | 519 | 2021-12-16 | 10380 | keep | 0 | Dec | 2021 | 0.0070698 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2021-12-16 03:42 | 2021-12-16 08:47 | 199 | 005:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | R21121600003 | New_Event | Bad Weather | Include | Include | Weather | 305 | 2021-12-16 | 60695 | keep | 0 | Dec | 2021 | 0.041339 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
VEGA BAJA | 2021-12-16 05:02 | 2021-12-16 15:10 | 16 | 010:08 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR 50KVA | B21121600008 | New_Event | Service Transformer Failure | Include | Include | Equipment | 608 | 2021-12-16 | 9728 | keep | 0 | Dec | 2021 | 0.0066257 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2021-12-16 05:04 | 2021-12-16 05:05 | 5961 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1713-05 LLEVANDO 95% 1717-02 | B21121600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-16 | 5961 | keep | 0 | Dec | 2021 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2021-12-16 05:04 | 2021-12-16 05:05 | 46 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1717-02 CON EL 95% DE SU CARGA TRANSFERIDA AL 1713-05 SE CERRO POR SCADA | B21121600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-16 | 46 | keep | 0 | Dec | 2021 | 3.133e-05 | 3.133e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 46
BARRANQUITAS | 2021-12-16 05:04 | 2021-12-16 18:31 | 150 | 013:27 | P | DESGANCHE | 2 X 65 EN C/L | C21121600004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 807 | 2021-12-16 | 121050 | keep | 0 | Dec | 2021 | 0.082447 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2021-12-16 05:05 | 2021-12-16 12:31 | 60 | 007:26 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 Y 1 X 30 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B21121600018 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 446 | 2021-12-16 | 26760 | keep | 0 | Dec | 2021 | 0.018226 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2021-12-16 05:26 | 2021-12-16 09:48 | 100 | 004:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | C21121600005 | New_Event |  |  | Include | Wildlife | 262 | 2021-12-16 | 26200 | keep | 0 | Dec | 2021 | 0.017845 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-12-16 05:29 | 2021-12-16 12:10 | 50 | 006:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA Y VIENTO | M21121600002 | New_Event | Bad Weather | Include | Include | Weather | 401 | 2021-12-16 | 20050 | keep | 0 | Dec | 2021 | 0.013656 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-12-16 05:41 | 2021-12-16 15:30 | 30 | 009:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21121600004 | New_Event | Bad Weather | Include | Include | Weather | 589 | 2021-12-16 | 17670 | keep | 0 | Dec | 2021 | 0.012035 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-12-16 06:16 | 2021-12-16 11:32 | 100 | 005:16 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21121600009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 316 | 2021-12-16 | 31600 | keep | 0 | Dec | 2021 | 0.021523 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-12-16 06:38 | 2021-12-16 11:32 | 304 | 004:54 | P | NO SE REPORTO CAUSA | 3 X 100 EN CORTE DE LINEA NO CAUSA | C21121600015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 294 | 2021-12-16 | 89376 | keep | 0 | Dec | 2021 | 0.060874 | 0.00020705 | Sustained | FALSE | FALSE | Not_TMED_Event | 304
HUMACAO | 2021-12-16 06:41 | 2021-12-16 11:51 | 60 | 005:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | C21121600016 | New_Event | Cutout Failure | Include | Include | Equipment | 310 | 2021-12-16 | 18600 | keep | 0 | Dec | 2021 | 0.012668 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-12-16 07:06 | 2021-12-16 13:30 | 150 | 006:24 | P | DESGANCHE | 3 X 65 EN CONVERTIDOR 3 X 80 Y 2 X 25 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | A21121600009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 384 | 2021-12-16 | 57600 | keep | 0 | Dec | 2021 | 0.039231 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
FAJARDO | 2021-12-16 07:08 | 2021-12-16 12:29 | 1 | 005:21 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA | R21121600008 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 321 | 2021-12-16 | 321 | keep | 0 | Dec | 2021 | 0.00021863 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-16 07:27 | 2021-12-22 19:55 | 1 | 156:28 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR JOURNEYMAN NO ENCONTRO CAUSA VERIFICADO EN BITACORA EVENTO DEL DIA 16 | M21121600008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9388 | 2021-12-16 | 9388 | keep | 0 | Dec | 2021 | 0.0063941 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-12-16 07:28 | 2021-12-16 11:42 | 3 | 004:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 8 EN TRANSFORMADOR SE LEVANTO SECUNDARIA | R21121600014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 254 | 2021-12-16 | 762 | keep | 0 | Dec | 2021 | 0.00051899 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2021-12-16 08:11 | 2021-12-16 10:30 | 14 | 002:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R21121600021 | New_Event |  |  | Include | Wildlife | 139 | 2021-12-16 | 1946 | keep | 0 | Dec | 2021 | 0.0013254 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2021-12-16 08:20 | 2021-12-16 08:21 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21121600016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-16 | 1097 | keep | 0 | Dec | 2021 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
MAYAGÃœEZ | 2021-12-16 08:20 | 2021-12-16 11:18 | 40 | 002:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y VIENTO | M21121600015 | New_Event | Bad Weather | Include | Include | Weather | 178 | 2021-12-16 | 7120 | keep | 0 | Dec | 2021 | 0.0048494 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-12-16 08:28 | 2021-12-16 13:39 | 250 | 005:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 80 EN CORTE DE LINEA SE RETEZARON LINEAS | C21121600027 | New_Event | Wire Down | Include | Include | Equipment | 311 | 2021-12-16 | 77750 | keep | 0 | Dec | 2021 | 0.052955 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BARRANQUITAS | 2021-12-16 08:33 | 2021-12-16 13:38 | 4 | 005:05 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIO XMR PARA REMPLAZAR POSTE PARTIDO | C21121600030 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 305 | 2021-12-16 | 1220 | keep | 0 | Dec | 2021 | 0.00083094 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2021-12-16 08:40 | 2021-12-16 13:06 | 4 | 004:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 Y 1 X 40 EN CORTES DE LINEA LLUVIAS | C21121600033 | New_Event | Bad Weather | Include | Include | Weather | 266 | 2021-12-16 | 1064 | keep | 0 | Dec | 2021 | 0.00072469 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2021-12-16 08:47 | 2021-12-16 12:12 | 54 | 003:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | R21121600027 | New_Event | Bad Weather | Include | Include | Weather | 205 | 2021-12-16 | 11070 | keep | 0 | Dec | 2021 | 0.0075397 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
HUMACAO | 2021-12-16 08:52 | 2021-12-16 12:42 | 1 | 003:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L REMPLAZO CAJA QUEMADA | C21121600038 | New_Event | Cutout Failure | Include | Include | Equipment | 230 | 2021-12-16 | 230 | keep | 0 | Dec | 2021 | 0.00015665 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-12-16 09:13 | 2021-12-16 18:09 | 9 | 008:56 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PRIMARIO A PUNTO DE CAER | R21121600032 | New_Event | Defective Pole | Include | Include | Equipment | 536 | 2021-12-16 | 4824 | keep | 0 | Dec | 2021 | 0.0032856 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
HUMACAO | 2021-12-16 09:14 | 2021-12-16 09:15 | 2450 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 12600 | C21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 2450 | keep | 0 | Dec | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2021-12-16 09:14 | 2021-12-16 09:15 | 640 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 12600 | C21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 640 | keep | 0 | Dec | 2021 | 0.0004359 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
CANOVANAS | 2021-12-16 09:23 | 2021-12-16 09:24 | 2708 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R21121600033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-16 | 2708 | keep | 0 | Dec | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
SAN JUAN | 2021-12-16 09:34 | 2021-12-16 10:49 | 1615 | 001:15 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO INTERRUPTOR POSTE IMPACTADO PARTIDO SE SECCIONALIZO CERRADO POR CONTROL | S21121600014 | New_Event |  |  | Include | Wildlife | 75 | 2021-12-16 | 121125 | keep | 0 | Dec | 2021 | 0.082498 | 0.0011 | Sustained | FALSE | FALSE | Not_TMED_Event | 1615
ARECIBO | 2021-12-16 09:41 | 2021-12-16 15:00 | 25 | 005:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21121600034 | New_Event | Bad Weather | Include | Include | Weather | 319 | 2021-12-16 | 7975 | keep | 0 | Dec | 2021 | 0.0054317 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2021-12-16 09:45 | 2021-12-16 12:46 | 20 | 003:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO PM Y SE REEMPLAZO CONEXIONES SOTERRADAS EN PEDESTAL | A21121600032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 181 | 2021-12-16 | 3620 | keep | 0 | Dec | 2021 | 0.0024656 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-12-16 09:45 | 2021-12-16 10:13 | 1 | 000:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | A21121500053 | New_Event | Secondary Wire Down | Include | Include | Equipment | 28 | 2021-12-16 | 28 | keep | 0 | Dec | 2021 | 1.9071e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-12-16 10:00 | 2021-12-16 10:52 | 3 | 000:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR CONEXIONES EN LINEA SECUNDARIA | P21121600015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 52 | 2021-12-16 | 156 | keep | 0 | Dec | 2021 | 0.00010625 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-12-16 10:21 | 2021-12-16 11:22 | 2 | 001:01 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR 50KVA | M21121600032 | New_Event | Service Transformer Failure | Include | Include | Equipment | 61 | 2021-12-16 | 122 | keep | 0 | Dec | 2021 | 8.3094e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2021-12-16 10:21 | 2021-12-16 15:37 | 100 | 005:16 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21121600033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 316 | 2021-12-16 | 31600 | keep | 0 | Dec | 2021 | 0.021523 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-12-16 10:35 | 2021-12-16 15:07 | 15 | 004:32 | P | DESGANCHE | SE ABRE MONTURA PARA RETIRAR ARBOL SOBRE FASE | S21121600075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 272 | 2021-12-16 | 4080 | keep | 0 | Dec | 2021 | 0.0027789 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-12-16 10:48 | 2021-12-16 12:44 | 12 | 001:56 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21121600019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2021-12-16 | 1392 | keep | 0 | Dec | 2021 | 0.00094808 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-12-16 10:48 | 2021-12-16 10:49 | 2147 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21121600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-16 | 2147 | keep | 0 | Dec | 2021 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
SAN JUAN | 2021-12-16 10:49 | 2021-12-16 11:21 | 830 | 000:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE TRANSFIRIO LA CARGA AL 1646-01 POR POSTE IMPACTADO PARTIDO DEL 1620-05 | S21121600014 | New_Event |  |  | Include | Wildlife | 32 | 2021-12-16 | 26560 | keep | 0 | Dec | 2021 | 0.01809 | 0.00056531 | Sustained | FALSE | FALSE | Not_TMED_Event | 830
BAYAMON | 2021-12-16 10:49 | 2021-12-18 09:19 | 2 | 046:30 | P | ESTRUCTURA AVERIADA | SE ABRIO PUENTE PARA SECCIONALIZAR POSTE PARTIDO Y SE REEMPLAZO 1 X 50 EN CORTE DE LINEA. SE QUEDARON SIN SERVICIO 2 CLIENTES | B21121400082 | Partial_restoration | Defective Pole | Include | Include | Equipment | 2790 | 2021-12-16 | 5580 | keep | 0 | Dec | 2021 | 0.0038005 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2021-12-16 10:53 | 2021-12-16 13:12 | 60 | 002:19 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21121600020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2021-12-16 | 8340 | keep | 0 | Dec | 2021 | 0.0056803 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-12-16 10:54 | 2021-12-16 10:55 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 1617 | keep | 0 | Dec | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-12-16 10:54 | 2021-12-16 10:55 | 1017 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 1017 | keep | 0 | Dec | 2021 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-12-16 10:54 | 2021-12-16 10:55 | 828 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 828 | keep | 0 | Dec | 2021 | 0.00056395 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
MAYAGÃœEZ | 2021-12-16 10:54 | 2021-12-16 10:55 | 863 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 863 | keep | 0 | Dec | 2021 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2021-12-16 10:54 | 2021-12-16 10:55 | 309 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 309 | keep | 0 | Dec | 2021 | 0.00021046 | 0.00021046 | Momentary | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2021-12-16 10:54 | 2021-12-16 10:55 | 176 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 176 | keep | 0 | Dec | 2021 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2021-12-16 10:55 | 2021-12-16 16:12 | 50 | 005:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21121600031 | New_Event | Bad Weather | Include | Include | Weather | 317 | 2021-12-16 | 15850 | keep | 0 | Dec | 2021 | 0.010795 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-12-16 11:13 | 2021-12-16 11:14 | 1648 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R21121600078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-16 | 1648 | keep | 0 | Dec | 2021 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CAGUAS | 2021-12-16 11:19 | 2021-12-16 18:48 | 40 | 007:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN C/L MAL TIEMPO | C21121600074 | New_Event | Bad Weather | Include | Include | Weather | 449 | 2021-12-16 | 17960 | keep | 0 | Dec | 2021 | 0.012232 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-12-16 11:21 | 2021-12-16 11:31 | 625 | 000:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE TRANSFIRIO LA CARGA AL 1620-02 POR POSTE IMPACTADO PARTIDO DEL 1620-05 | S21121600014 | Partial_restoration |  |  | Include | Wildlife | 10 | 2021-12-16 | 6250 | keep | 0 | Dec | 2021 | 0.0042568 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-16 11:22 | 2021-12-16 15:09 | 15 | 003:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO CONDUCTOR A CAJA PRIMARIA | B21121600037 | New_Event | Wire Down | Include | Include | Equipment | 227 | 2021-12-16 | 3405 | keep | 0 | Dec | 2021 | 0.0023191 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-12-16 11:31 | 2021-12-16 23:42 | 160 | 012:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REMPLAZO POSTE PARTIDO IMPACTADO POR VEHICULO | S21121600014 | Partial_restoration |  |  | Include | Wildlife | 731 | 2021-12-16 | 116960 | keep | 0 | Dec | 2021 | 0.079661 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-12-16 11:43 | 2021-12-16 12:35 | 4 | 000:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE X AVE | C21121600077 | New_Event |  |  | Include | Wildlife | 52 | 2021-12-16 | 208 | keep | 0 | Dec | 2021 | 0.00014167 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-12-16 11:48 | 2021-12-16 12:58 | 15 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21121600031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2021-12-16 | 1050 | keep | 0 | Dec | 2021 | 0.00071515 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-12-16 11:51 | 2021-12-16 16:10 | 40 | 004:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21121600042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2021-12-16 | 10360 | keep | 0 | Dec | 2021 | 0.0070561 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-16 11:58 | 2021-12-16 13:13 | 18 | 001:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21121600013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 75 | 2021-12-16 | 1350 | keep | 0 | Dec | 2021 | 0.00091948 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
UTUADO | 2021-12-16 12:02 | 2021-12-16 13:20 | 40 | 001:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CONVERTIDOR POR MAL TIEMPO | A21121600060 | New_Event | Bad Weather | Include | Include | Weather | 78 | 2021-12-16 | 3120 | keep | 0 | Dec | 2021 | 0.002125 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-12-16 12:28 | 2021-12-16 16:12 | 60 | 003:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MUCHA LLUVIA | S21121600038 | New_Event | Bad Weather | Include | Include | Weather | 224 | 2021-12-16 | 13440 | keep | 0 | Dec | 2021 | 0.0091539 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2021-12-16 12:31 | 2021-12-16 15:56 | 50 | 003:25 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M21121600048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2021-12-16 | 10250 | keep | 0 | Dec | 2021 | 0.0069812 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-12-16 12:42 | 2021-12-16 13:05 | 2126 | 000:23 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO SE VERIFICO PERSONAL FUERA | C21121600084 | New_Event | Cutout Failure | Include | Include | Equipment | 23 | 2021-12-16 | 48898 | keep | 0 | Dec | 2021 | 0.033304 | 0.001448 | Sustained | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2021-12-16 12:44 | 2021-12-16 16:28 | 40 | 003:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN C/L MAL TIEMPO | C21121600085 | New_Event | Bad Weather | Include | Include | Weather | 224 | 2021-12-16 | 8960 | keep | 0 | Dec | 2021 | 0.0061026 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-12-16 12:54 | 2021-12-16 16:35 | 1 | 003:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN RISER LLUVIA Y FUERTES VIENTOS | A21121600065 | New_Event | Bad Weather | Include | Include | Weather | 221 | 2021-12-16 | 221 | keep | 0 | Dec | 2021 | 0.00015052 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-16 12:57 | 2021-12-16 15:22 | 52 | 002:25 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21121600044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2021-12-16 | 7540 | keep | 0 | Dec | 2021 | 0.0051355 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
SAN JUAN | 2021-12-16 12:57 | 2021-12-16 13:58 | 3957 | 001:01 | T | DESGANCHE | DISPARO SE ABRIO MACHETE CAMINO LOS ROMEROS CARR.842 Y SE CERRO BKR. QUEDO EN SERVICIO 98% EN SERVICIO POR RAMA CRUZANDO LINEAS | S21121600045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2021-12-16 | 241377 | keep | 0 | Dec | 2021 | 0.1644 | 0.0026951 | Sustained | FALSE | FALSE | Not_TMED_Event | 3957
GUAYAMA | 2021-12-16 13:00 | 2021-12-16 13:45 | 4279 | 000:45 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR POR LINEA PRIMARIA PARTIDA SE ABRIERON PUENTES PRIMARIOS Y SE COLOCO INTERRUPTOR EN SERVICIO | P21121600028 | New_Event | Wire Down | Include | Include | Equipment | 45 | 2021-12-16 | 192555 | keep | 0 | Dec | 2021 | 0.13115 | 0.0029144 | Sustained | FALSE | FALSE | Not_TMED_Event | 4279
CAGUAS | 2021-12-16 13:04 | 2021-12-16 17:45 | 40 | 004:41 | P | DESGANCHE | 1 X 65 EN C/L | C21121600095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 281 | 2021-12-16 | 11240 | keep | 0 | Dec | 2021 | 0.0076555 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2021-12-16 13:05 | 2021-12-16 15:03 | 1 | 001:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L REMPLAZO CAJA QUEMADA | C21121600038 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 118 | 2021-12-16 | 118 | keep | 0 | Dec | 2021 | 8.0369e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-12-16 13:10 | 2021-12-16 14:32 | 15 | 001:22 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | B21121600046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2021-12-16 | 1230 | keep | 0 | Dec | 2021 | 0.00083775 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-12-16 13:16 | 2021-12-16 16:07 | 27 | 002:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21121600038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 171 | 2021-12-16 | 4617 | keep | 0 | Dec | 2021 | 0.0031446 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2021-12-16 13:20 | 2021-12-16 17:43 | 27 | 004:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B21121600047 | New_Event | Cutout Failure | Include | Include | Equipment | 263 | 2021-12-16 | 7101 | keep | 0 | Dec | 2021 | 0.0048365 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
PONCE | 2021-12-16 13:21 | 2021-12-16 13:22 | 1093 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE ENCONTRO CAUSA | P21121600039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-16 | 1093 | keep | 0 | Dec | 2021 | 0.00074444 | 0.00074444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1093
ARECIBO | 2021-12-16 13:21 | 2021-12-16 15:20 | 80 | 001:59 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A21121600069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2021-12-16 | 9520 | keep | 0 | Dec | 2021 | 0.006484 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-12-16 13:23 | 2021-12-16 13:25 | 500 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO 20% DE SU CARGA POR 1118-10 | S21121600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-16 | 1000 | keep | 0 | Dec | 2021 | 0.0006811 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2021-12-16 13:23 | 2021-12-16 13:25 | 2782 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 20% DEL 1111-1 | S21121600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-16 | 5564 | keep | 0 | Dec | 2021 | 0.0037896 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
HUMACAO | 2021-12-16 13:36 | 2021-12-16 14:48 | 50 | 001:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE X AVE | C21121600104 | New_Event |  |  | Include | Wildlife | 72 | 2021-12-16 | 3600 | keep | 0 | Dec | 2021 | 0.0024519 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2021-12-16 13:45 | 2021-12-16 19:37 | 50 | 005:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE CERRO PUENTES CON VOLTAJE SIN CARGA | P21121600074 | Partial_restoration | Wire Down | Include | Include | Equipment | 352 | 2021-12-16 | 17600 | keep | 0 | Dec | 2021 | 0.011987 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-16 13:58 | 2021-12-16 16:26 | 150 | 002:28 | P | DESGANCHE | SE RETIRO RAMA CRUZANDO FASE Y SE REMPLAZO MACHETE CON GOI SJ-211216-1 Y SE CERRO MACHETE 100% EN SERVICIO | S21121600045 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 148 | 2021-12-16 | 22200 | keep | 0 | Dec | 2021 | 0.01512 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2021-12-16 14:04 | 2021-12-16 15:09 | 133 | 001:05 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21121600052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 65 | 2021-12-16 | 8645 | keep | 0 | Dec | 2021 | 0.0058881 | 9.0586e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 133
CANOVANAS | 2021-12-16 14:05 | 2021-12-16 14:58 | 19 | 000:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR SECUNDARIA | R21121600029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 53 | 2021-12-16 | 1007 | keep | 0 | Dec | 2021 | 0.00068586 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2021-12-16 14:18 | 2021-12-16 14:47 | 225 | 000:29 | T | DESGANCHE | DISPARO SE RETIRO RAMA CRUZANDO FASE CAMINO PEDRO VIERA Y SE CERRO QUEDO EN SERVICIO SU CARGA POR 1303-5 | S21121600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 29 | 2021-12-16 | 6525 | keep | 0 | Dec | 2021 | 0.0044441 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-12-16 14:18 | 2021-12-16 14:47 | 870 | 000:29 | T | DESGANCHE | DISPARO SE RETIRO RAMA CRUZANDO FASE CAMINO PEDRO VIERA Y SE CERRO QUEDO EN SERVICIO LLEVA 1303-4 | S21121600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 29 | 2021-12-16 | 25230 | keep | 0 | Dec | 2021 | 0.017184 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2021-12-16 14:19 | 2021-12-16 17:52 | 52 | 003:33 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO | B21121600056 | New_Event | Switch Failure | Include | Include | Equipment | 213 | 2021-12-16 | 11076 | keep | 0 | Dec | 2021 | 0.0075438 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
BAYAMON | 2021-12-16 14:27 | 2021-12-16 16:49 | 52 | 002:22 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S21121600078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 142 | 2021-12-16 | 7384 | keep | 0 | Dec | 2021 | 0.0050292 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
CANOVANAS | 2021-12-16 14:29 | 2021-12-16 17:26 | 262 | 002:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | R21121600109 | New_Event | Bad Weather | Include | Include | Weather | 177 | 2021-12-16 | 46374 | keep | 0 | Dec | 2021 | 0.031585 | 0.00017845 | Sustained | FALSE | FALSE | Not_TMED_Event | 262
ARECIBO | 2021-12-16 14:35 | 2021-12-16 16:13 | 65 | 001:38 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A21121600083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 98 | 2021-12-16 | 6370 | keep | 0 | Dec | 2021 | 0.0043386 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2021-12-16 14:39 | 2021-12-16 17:01 | 5 | 002:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN XMR MAL TIEMPO | C21121600104 | New_Event | Bad Weather | Include | Include | Weather | 142 | 2021-12-16 | 710 | keep | 0 | Dec | 2021 | 0.00048358 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-12-16 14:45 | 2021-12-16 17:30 | 40 | 002:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO EN CORTE DE LINEA | A21121600085 | New_Event | Wire Down | Include | Include | Equipment | 165 | 2021-12-16 | 6600 | keep | 0 | Dec | 2021 | 0.0044952 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-12-16 14:54 | 2021-12-16 18:12 | 8 | 003:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA Y CONEXIONES SECUNDARIAS | M21121600064 | New_Event | Secondary Wire Down | Include | Include | Equipment | 198 | 2021-12-16 | 1584 | keep | 0 | Dec | 2021 | 0.0010789 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-12-16 14:57 | 2021-12-16 19:53 | 40 | 004:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21121600066 | New_Event | Bad Weather | Include | Include | Weather | 296 | 2021-12-16 | 11840 | keep | 0 | Dec | 2021 | 0.0080642 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2021-12-16 14:59 | 2021-12-16 15:00 | 2725 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8500 | C21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 2725 | keep | 0 | Dec | 2021 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2021-12-16 14:59 | 2021-12-16 15:00 | 1834 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8500 | C21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 1834 | keep | 0 | Dec | 2021 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2021-12-16 14:59 | 2021-12-16 15:00 | 1437 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8500 | C21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 1437 | keep | 0 | Dec | 2021 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2021-12-16 14:59 | 2021-12-16 15:00 | 2565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8500 | C21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 2565 | keep | 0 | Dec | 2021 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2021-12-16 14:59 | 2021-12-16 15:00 | 3565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8500 | C21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 3565 | keep | 0 | Dec | 2021 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
GUAYAMA | 2021-12-16 15:01 | 2021-12-16 15:53 | 60 | 000:52 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21121600055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 52 | 2021-12-16 | 3120 | keep | 0 | Dec | 2021 | 0.002125 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2021-12-16 15:08 | 2021-12-16 18:18 | 6 | 003:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | A21121600087 | New_Event | Bad Weather | Include | Include | Weather | 190 | 2021-12-16 | 1140 | keep | 0 | Dec | 2021 | 0.00077645 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-12-16 15:15 | 2021-12-16 16:18 | 8 | 001:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | A21121500098 | New_Event | Secondary Wire Down | Include | Include | Equipment | 63 | 2021-12-16 | 504 | keep | 0 | Dec | 2021 | 0.00034327 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-12-16 15:21 | 2021-12-16 15:54 | 1 | 000:33 | P | NO SE REPORTO CAUSA | 1 X 20 EN SU BOMBAS AAA NO CAUSA | C21121600082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 33 | 2021-12-16 | 33 | keep | 0 | Dec | 2021 | 2.2476e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-16 15:41 | 2021-12-16 17:19 | 12 | 001:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA | S21121500099 | New_Event | Cutout Failure | Include | Include | Equipment | 98 | 2021-12-16 | 1176 | keep | 0 | Dec | 2021 | 0.00080097 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-12-16 15:42 | 2021-12-16 15:43 | 3700 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21216000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-16 | 3700 | keep | 0 | Dec | 2021 | 0.0025201 | 0.0025201 | Momentary | FALSE | FALSE | Not_TMED_Event | 3700
AGUADILLA | 2021-12-16 15:42 | 2021-12-16 18:10 | 20 | 002:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21121600072 | New_Event | Secondary Wire Down | Include | Include | Equipment | 148 | 2021-12-16 | 2960 | keep | 0 | Dec | 2021 | 0.002016 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2021-12-16 15:48 | 2021-12-16 20:07 | 53 | 004:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REEMPLAZO POSTE PRIMARIO IMPACTADO PARTIDO SE CERRO CORTE DE LINEA NO FUNDIO | R21121600089 | New_Event |  |  | Include | Wildlife | 259 | 2021-12-16 | 13727 | keep | 0 | Dec | 2021 | 0.0093494 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
MAYAGÃœEZ | 2021-12-16 15:51 | 2021-12-16 17:31 | 15 | 001:40 | P | PARARRAYOS DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR PARARRAYOS DEFECTUOSOS EN TRANSFORMADOR | M21121600076 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 100 | 2021-12-16 | 1500 | keep | 0 | Dec | 2021 | 0.0010216 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-12-16 15:56 | 2021-12-16 15:57 | 2190 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21121600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-16 | 2190 | keep | 0 | Dec | 2021 | 0.0014916 | 0.0014916 | Momentary | FALSE | FALSE | Not_TMED_Event | 2190
BAYAMON | 2021-12-16 16:04 | 2021-12-16 16:08 | 878 | 000:04 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | B21121600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-12-16 | 3512 | keep | 0 | Dec | 2021 | 0.002392 | 0.000598 | Momentary | FALSE | FALSE | Not_TMED_Event | 878
VEGA BAJA | 2021-12-16 16:07 | 2021-12-16 16:09 | 2368 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | B21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-12-16 | 4736 | keep | 0 | Dec | 2021 | 0.0032257 | 0.0016128 | Momentary | FALSE | FALSE | Not_TMED_Event | 2368
VEGA BAJA | 2021-12-16 16:07 | 2021-12-16 16:09 | 538 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | B21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-12-16 | 1076 | keep | 0 | Dec | 2021 | 0.00073286 | 0.00036643 | Momentary | FALSE | FALSE | Not_TMED_Event | 538
VEGA BAJA | 2021-12-16 16:07 | 2021-12-16 16:09 | 1284 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | B21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-12-16 | 2568 | keep | 0 | Dec | 2021 | 0.0017491 | 0.00087453 | Momentary | FALSE | FALSE | Not_TMED_Event | 1284
VEGA BAJA | 2021-12-16 16:09 | 2021-12-16 19:18 | 27 | 003:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21121600038 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 189 | 2021-12-16 | 5103 | keep | 0 | Dec | 2021 | 0.0034756 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-12-16 16:10 | 2021-12-16 19:19 | 10 | 003:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS Y CONEXIONES | M21121600054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 189 | 2021-12-16 | 1890 | keep | 0 | Dec | 2021 | 0.0012873 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-16 16:14 | 2021-12-16 16:15 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21121600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-16 | 2605 | keep | 0 | Dec | 2021 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
ARECIBO | 2021-12-16 16:24 | 2021-12-16 17:18 | 2107 | 000:54 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO MACHETES PARA SECCIONALIZAR AISLADOR PARTIDO | A21121600096 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 54 | 2021-12-16 | 113778 | keep | 0 | Dec | 2021 | 0.077494 | 0.0014351 | Sustained | FALSE | FALSE | Not_TMED_Event | 2107
BAYAMON | 2021-12-16 16:34 | 2021-12-16 20:58 | 27 | 004:24 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21121600072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 264 | 2021-12-16 | 7128 | keep | 0 | Dec | 2021 | 0.0048548 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
HUMACAO | 2021-12-16 16:39 | 2021-12-16 17:54 | 75 | 001:15 | P | DESGANCHE | 2 X 50 EN C/L | C21121600131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2021-12-16 | 5625 | keep | 0 | Dec | 2021 | 0.0038312 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2021-12-16 16:40 | 2021-12-16 19:39 | 27 | 002:59 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21121600074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 179 | 2021-12-16 | 4833 | keep | 0 | Dec | 2021 | 0.0032917 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2021-12-16 16:41 | 2021-12-16 18:31 | 52 | 001:50 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B21121600075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 110 | 2021-12-16 | 5720 | keep | 0 | Dec | 2021 | 0.0038959 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
BAYAMON | 2021-12-16 16:42 | 2021-12-16 18:56 | 27 | 002:14 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B21121600076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 134 | 2021-12-16 | 3618 | keep | 0 | Dec | 2021 | 0.0024642 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
CAGUAS | 2021-12-16 16:59 | 2021-12-16 18:11 | 2092 | 001:12 | T | HERRAJE ROTO O PODRIDO | SE ABRIO INTERRUPTOR PARA REMPLAZAR CRUCETA ROTA | C21121600136 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 72 | 2021-12-16 | 150624 | keep | 0 | Dec | 2021 | 0.10259 | 0.0014249 | Sustained | FALSE | FALSE | Not_TMED_Event | 2092
ARECIBO | 2021-12-16 17:10 | 2021-12-16 17:45 | 15 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE ZAFADO EN TRANSFORMADOR | A21121600095 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2021-12-16 | 525 | keep | 0 | Dec | 2021 | 0.00035758 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-12-16 17:13 | 2021-12-16 18:29 | 32 | 001:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE AJUSTARON CONEXIONES EN CAJA PRIMARIA | P21121600062 | New_Event | Wire Down | Include | Include | Equipment | 76 | 2021-12-16 | 2432 | keep | 0 | Dec | 2021 | 0.0016564 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
ARECIBO | 2021-12-16 17:18 | 2021-12-16 18:39 | 1700 | 001:21 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR PARTIDO | A21121600108 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 81 | 2021-12-16 | 137700 | keep | 0 | Dec | 2021 | 0.093787 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2021-12-16 17:23 | 2021-12-16 17:42 | 1 | 000:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA CRUCE POR AVE | R21121600130 | New_Event |  |  | Include | Wildlife | 19 | 2021-12-16 | 19 | keep | 0 | Dec | 2021 | 1.2941e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-12-16 17:26 | 2021-12-16 19:10 | 8 | 001:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN XMR MAL TIEMPO | C21121600140 | New_Event | Bad Weather | Include | Include | Weather | 104 | 2021-12-16 | 832 | keep | 0 | Dec | 2021 | 0.00056667 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-12-16 17:46 | 2021-12-16 22:55 | 310 | 005:09 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | C21121600148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 309 | 2021-12-16 | 95790 | keep | 0 | Dec | 2021 | 0.065242 | 0.00021114 | Sustained | FALSE | FALSE | Not_TMED_Event | 310
ARECIBO | 2021-12-16 17:49 | 2021-12-16 21:44 | 75 | 003:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21121600111 | New_Event | Bad Weather | Include | Include | Weather | 235 | 2021-12-16 | 17625 | keep | 0 | Dec | 2021 | 0.012004 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
PONCE | 2021-12-16 17:58 | 2021-12-16 17:59 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE ENCONTRO CAUSA | P21121600069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-16 | 969 | keep | 0 | Dec | 2021 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
ARECIBO | 2021-12-16 18:03 | 2021-12-16 21:10 | 50 | 003:07 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21121600117 | New_Event | Bad Weather | Include | Include | Weather | 187 | 2021-12-16 | 9350 | keep | 0 | Dec | 2021 | 0.0063682 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-12-16 18:04 | 2021-12-16 18:05 | 2697 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21121600119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-16 | 2697 | keep | 0 | Dec | 2021 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
CAGUAS | 2021-12-16 18:27 | 2021-12-16 18:28 | 4390 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9300 | C21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 4390 | keep | 0 | Dec | 2021 | 0.00299 | 0.00299 | Momentary | FALSE | FALSE | Not_TMED_Event | 4390
CAGUAS | 2021-12-16 18:27 | 2021-12-16 18:28 | 2092 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9300 | C21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 2092 | keep | 0 | Dec | 2021 | 0.0014249 | 0.0014249 | Momentary | FALSE | FALSE | Not_TMED_Event | 2092
CAGUAS | 2021-12-16 18:27 | 2021-12-16 18:28 | 540 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9300 | C21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 540 | keep | 0 | Dec | 2021 | 0.00036779 | 0.00036779 | Momentary | FALSE | FALSE | Not_TMED_Event | 540
CAGUAS | 2021-12-16 18:27 | 2021-12-16 18:28 | 131 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9300 | C21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 131 | keep | 0 | Dec | 2021 | 8.9224e-05 | 8.9224e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 131
CAGUAS | 2021-12-16 18:27 | 2021-12-16 18:28 | 2281 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9300 | C21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 2281 | keep | 0 | Dec | 2021 | 0.0015536 | 0.0015536 | Momentary | FALSE | FALSE | Not_TMED_Event | 2281
CAGUAS | 2021-12-16 18:27 | 2021-12-16 18:28 | 1569 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9300 | C21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 1569 | keep | 0 | Dec | 2021 | 0.0010686 | 0.0010686 | Momentary | FALSE | FALSE | Not_TMED_Event | 1569
CAGUAS | 2021-12-16 18:27 | 2021-12-16 18:28 | 2417 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9300 | C21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 2417 | keep | 0 | Dec | 2021 | 0.0016462 | 0.0016462 | Momentary | FALSE | FALSE | Not_TMED_Event | 2417
ARECIBO | 2021-12-16 18:35 | 2021-12-16 18:36 | 1222 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2100 | A21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 1222 | keep | 0 | Dec | 2021 | 0.0008323 | 0.0008323 | Momentary | FALSE | FALSE | Not_TMED_Event | 1222
ARECIBO | 2021-12-16 18:35 | 2021-12-16 18:36 | 2756 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2100 | A21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 2756 | keep | 0 | Dec | 2021 | 0.0018771 | 0.0018771 | Momentary | FALSE | FALSE | Not_TMED_Event | 2756
ARECIBO | 2021-12-16 18:35 | 2021-12-16 18:36 | 2833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2100 | A21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 2833 | keep | 0 | Dec | 2021 | 0.0019295 | 0.0019295 | Momentary | FALSE | FALSE | Not_TMED_Event | 2833
ARECIBO | 2021-12-16 18:35 | 2021-12-16 18:36 | 1218 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2100 | A21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 1218 | keep | 0 | Dec | 2021 | 0.00082957 | 0.00082957 | Momentary | FALSE | FALSE | Not_TMED_Event | 1218
ARECIBO | 2021-12-16 18:35 | 2021-12-16 18:36 | 1345 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2100 | A21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 1345 | keep | 0 | Dec | 2021 | 0.00091607 | 0.00091607 | Momentary | FALSE | FALSE | Not_TMED_Event | 1345
ARECIBO | 2021-12-16 18:35 | 2021-12-16 18:36 | 1265 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2100 | A21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 1265 | keep | 0 | Dec | 2021 | 0.00086159 | 0.00086159 | Momentary | FALSE | FALSE | Not_TMED_Event | 1265
ARECIBO | 2021-12-16 18:35 | 2021-12-16 18:36 | 2071 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2100 | A21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 2071 | keep | 0 | Dec | 2021 | 0.0014105 | 0.0014105 | Momentary | FALSE | FALSE | Not_TMED_Event | 2071
ARECIBO | 2021-12-16 18:35 | 2021-12-16 18:36 | 760 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2100 | A21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 760 | keep | 0 | Dec | 2021 | 0.00051763 | 0.00051763 | Momentary | FALSE | FALSE | Not_TMED_Event | 760
ARECIBO | 2021-12-16 18:35 | 2021-12-16 18:36 | 509 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2100 | A21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 509 | keep | 0 | Dec | 2021 | 0.00034668 | 0.00034668 | Momentary | FALSE | FALSE | Not_TMED_Event | 509
ARECIBO | 2021-12-16 18:35 | 2021-12-16 18:36 | 2620 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2100 | A21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 2620 | keep | 0 | Dec | 2021 | 0.0017845 | 0.0017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 2620
ARECIBO | 2021-12-16 18:35 | 2021-12-16 18:36 | 1916 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2100 | A21121600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-16 | 1916 | keep | 0 | Dec | 2021 | 0.001305 | 0.001305 | Momentary | FALSE | FALSE | Not_TMED_Event | 1916
ARECIBO | 2021-12-16 18:36 | 2021-12-16 19:50 | 35 | 001:14 | P | LINEA DE TRANSMISION 38KV | SE ABRIO CORTE DE LINEA PARA SECCIONALIZAR POSTE EN FUEGO DE LINEA 2100 | A21121600114 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 74 | 2021-12-16 | 2590 | keep | 0 | Dec | 2021 | 0.001764 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2021-12-16 18:38 | 2021-12-17 11:14 | 7 | 016:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTE SECUNDARIO | M21121600091 | New_Event | Secondary Wire Down | Include | Include | Equipment | 996 | 2021-12-16 | 6972 | keep | 0 | Dec | 2021 | 0.0047486 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-12-16 18:39 | 2021-12-16 18:44 | 2107 | 000:05 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO INTERRUPTOR PARA CERRAR MACHETES | A21121600000 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 5 | 2021-12-16 | 10535 | keep | 0 | Dec | 2021 | 0.0071753 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-12-16 18:41 | 2021-12-16 19:23 | 23 | 000:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | R21121600141 | New_Event | Bad Weather | Include | Include | Weather | 42 | 2021-12-16 | 966 | keep | 0 | Dec | 2021 | 0.00065794 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
AGUADILLA | 2021-12-16 18:50 | 2021-12-16 19:50 | 4 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M21121600044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2021-12-16 | 240 | keep | 0 | Dec | 2021 | 0.00016346 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-12-16 18:56 | 2021-12-16 21:17 | 15 | 002:21 | P | NO SE REPORTO CAUSA | 1 X 15 EN C/L | B21121600099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 141 | 2021-12-16 | 2115 | keep | 0 | Dec | 2021 | 0.0014405 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-12-16 19:20 | 2021-12-17 17:15 | 20 | 021:55 | P | NO SE REPORTO CAUSA | 1 X 10 RISER | S21121600119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1315 | 2021-12-16 | 26300 | keep | 0 | Dec | 2021 | 0.017913 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-12-16 19:22 | 2021-12-16 22:20 | 4 | 002:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA LLUVIA Y VIENTO | A21121600136 | New_Event | Bad Weather | Include | Include | Weather | 178 | 2021-12-16 | 712 | keep | 0 | Dec | 2021 | 0.00048494 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-12-16 19:28 | 2021-12-17 16:37 | 25 | 021:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21121600137 | New_Event | Bad Weather | Include | Include | Weather | 1269 | 2021-12-16 | 31725 | keep | 0 | Dec | 2021 | 0.021608 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2021-12-16 19:49 | 2021-12-17 09:10 | 10 | 013:21 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | P21121600081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 801 | 2021-12-16 | 8010 | keep | 0 | Dec | 2021 | 0.0054556 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-12-16 19:51 | 2021-12-17 10:59 | 40 | 015:08 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | M21121600097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 908 | 2021-12-16 | 36320 | keep | 0 | Dec | 2021 | 0.024737 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2021-12-16 20:00 | 2021-12-17 10:20 | 386 | 014:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | P21121600085 | New_Event | Cutout Failure | Include | Include | Equipment | 860 | 2021-12-16 | 331960 | keep | 0 | Dec | 2021 | 0.2261 | 0.0002629 | Sustained | FALSE | FALSE | Not_TMED_Event | 386
FAJARDO | 2021-12-16 20:11 | 2021-12-16 22:43 | 10 | 002:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | R21121600149 | New_Event | Secondary Wire Down | Include | Include | Equipment | 152 | 2021-12-16 | 1520 | keep | 0 | Dec | 2021 | 0.0010353 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-16 20:17 | 2021-12-17 10:35 | 200 | 014:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 EN CORTE DE LINEA Y 1 X 6 EN TRANSFORMADOR SE REPARO NEUTRAL PARTIDO Y BAJANTE PRIMARIO | M21121600109 | New_Event | Wire Down | Include | Include | Equipment | 858 | 2021-12-16 | 171600 | keep | 0 | Dec | 2021 | 0.11688 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2021-12-16 20:55 | 2021-12-16 22:11 | 9 | 001:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR NEUTRAL SECUNDARIO | M21121600007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 76 | 2021-12-16 | 684 | keep | 0 | Dec | 2021 | 0.00046587 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2021-12-16 21:14 | 2021-12-16 22:51 | 60 | 001:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA Y VIENTO | M21121600112 | New_Event | Bad Weather | Include | Include | Weather | 97 | 2021-12-16 | 5820 | keep | 0 | Dec | 2021 | 0.003964 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2021-12-16 21:39 | 2021-12-17 10:31 | 9 | 012:52 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R21121600155 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 772 | 2021-12-16 | 6948 | keep | 0 | Dec | 2021 | 0.0047323 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2021-12-16 21:40 | 2021-12-17 11:00 | 40 | 013:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21121600145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 800 | 2021-12-16 | 32000 | keep | 0 | Dec | 2021 | 0.021795 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-12-16 22:55 | 2021-12-16 22:57 | 2900 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C21121600165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-16 | 5800 | keep | 0 | Dec | 2021 | 0.0039504 | 0.0019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 2900
CAGUAS | 2021-12-16 22:57 | 2021-12-17 16:14 | 310 | 017:17 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | C21121600148 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1037 | 2021-12-16 | 321470 | keep | 0 | Dec | 2021 | 0.21895 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-12-16 23:07 | 2021-12-17 01:22 | 10 | 002:15 | P | SECUNDARIA/DESGANCHE | SE REPARO SECUNDARIA ROTA Y REALIZO DESGANCHE | R21121600159 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 135 | 2021-12-16 | 1350 | keep | 0 | Dec | 2021 | 0.00091948 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-12-17 00:05 | 2021-12-17 12:28 | 50 | 012:23 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PARARRAYO | M21121700001 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 743 | 2021-12-17 | 37150 | keep | 0 | Dec | 2021 | 0.025303 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-12-17 02:15 | 2021-12-17 02:16 | 4188 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21121700006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-17 | 4188 | keep | 0 | Dec | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
MAYAGÃœEZ | 2021-12-17 02:40 | 2021-12-17 02:41 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21121700004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-17 | 108 | keep | 0 | Dec | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
MAYAGÃœEZ | 2021-12-17 04:03 | 2021-12-17 04:04 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21121700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-17 | 990 | keep | 0 | Dec | 2021 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
BAYAMON | 2021-12-17 04:43 | 2021-12-17 04:44 | 2858 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21121700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-17 | 2858 | keep | 0 | Dec | 2021 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
MAYAGÃœEZ | 2021-12-17 05:41 | 2021-12-17 05:42 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21121700009 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-17 | 990 | keep | 0 | Dec | 2021 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
FAJARDO | 2021-12-17 06:49 | 2021-12-17 08:44 | 8 | 001:55 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R21121700010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2021-12-17 | 920 | keep | 0 | Dec | 2021 | 0.00062661 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-12-17 07:01 | 2021-12-17 07:02 | 500 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO SU 20% POR 1118-10 | S21121700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-17 | 500 | keep | 0 | Dec | 2021 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2021-12-17 07:01 | 2021-12-17 07:02 | 2782 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 20% 1111-1 | S21121700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-17 | 2782 | keep | 0 | Dec | 2021 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
MAYAGÃœEZ | 2021-12-17 07:05 | 2021-12-17 12:25 | 150 | 005:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO DE CAJA PRIMARIA QUEMADA | M21121700014 | New_Event | Cutout Failure | Include | Include | Equipment | 320 | 2021-12-17 | 48000 | keep | 0 | Dec | 2021 | 0.032693 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2021-12-17 07:13 | 2021-12-17 07:14 | 308 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DE INTERRUPTOR | A21121700000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2021-12-17 | 308 | keep | 0 | Dec | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
ARECIBO | 2021-12-17 07:22 | 2021-12-17 07:23 | 308 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DE INTERRUPTOR | A21121700000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-12-17 | 308 | keep | 0 | Dec | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
CANOVANAS | 2021-12-17 07:38 | 2021-12-17 12:32 | 40 | 004:54 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | R21121700012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 294 | 2021-12-17 | 11760 | keep | 0 | Dec | 2021 | 0.0080097 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-17 07:40 | 2021-12-17 07:41 | 750 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO SOLO LLEVA 50% DE SU CARGA Y LLEVA LA CARGA DEL 1709-05 | S21121700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-17 | 750 | keep | 0 | Dec | 2021 | 0.00051082 | 0.00051082 | Momentary | FALSE | FALSE | Not_TMED_Event | 750
BAYAMON | 2021-12-17 07:40 | 2021-12-17 07:41 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 1709-03 Y LLEVA LA CARGA DEL 1709-05 | S21121700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-17 | 2364 | keep | 0 | Dec | 2021 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
VEGA BAJA | 2021-12-17 07:43 | 2021-12-17 19:25 | 100 | 011:42 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21121700006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 702 | 2021-12-17 | 70200 | keep | 0 | Dec | 2021 | 0.047813 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-12-17 07:44 | 2021-12-17 11:16 | 60 | 003:32 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A21121700007 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 212 | 2021-12-17 | 12720 | keep | 0 | Dec | 2021 | 0.0086635 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2021-12-17 07:54 | 2021-12-17 16:27 | 25 | 008:33 | P | DESGANCHE | 1 X 40 EN C/L | R21121700014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 513 | 2021-12-17 | 12825 | keep | 0 | Dec | 2021 | 0.008735 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2021-12-17 07:55 | 2021-12-17 07:56 | 464 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | P21121700006 | New_Event |  |  | Include | Wildlife | 1 | 2021-12-17 | 464 | keep | 0 | Dec | 2021 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2021-12-17 07:56 | 2021-12-17 08:19 | 100 | 000:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P21121700009 | 1st_after_momentary |  |  | Include | Wildlife | 23 | 2021-12-17 | 2300 | keep | 0 | Dec | 2021 | 0.0015665 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-12-17 07:59 | 2021-12-17 08:00 | 308 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DE INTERRUPTOR | A21121700000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-12-17 | 308 | keep | 0 | Dec | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
ARECIBO | 2021-12-17 08:01 | 2021-12-17 08:02 | 308 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DE INTERRUPTOR | A21121700000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-12-17 | 308 | keep | 0 | Dec | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
SAN JUAN | 2021-12-17 08:02 | 2021-12-17 17:23 | 15 | 009:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21121700007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 561 | 2021-12-17 | 8415 | keep | 0 | Dec | 2021 | 0.0057314 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-12-17 08:22 | 2021-12-17 08:27 | 1526 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17200 | B21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-17 | 7630 | keep | 0 | Dec | 2021 | 0.0051968 | 0.0010394 | Momentary | FALSE | FALSE | Not_TMED_Event | 1526
VEGA BAJA | 2021-12-17 08:22 | 2021-12-17 08:27 | 308 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17200 | B21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-17 | 1540 | keep | 0 | Dec | 2021 | 0.0010489 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2021-12-17 08:22 | 2021-12-17 08:27 | 1397 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17200 | B21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-17 | 6985 | keep | 0 | Dec | 2021 | 0.0047575 | 0.00095149 | Momentary | FALSE | FALSE | Not_TMED_Event | 1397
VEGA BAJA | 2021-12-17 08:22 | 2021-12-17 08:27 | 2926 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17200 | B21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-17 | 14630 | keep | 0 | Dec | 2021 | 0.0099644 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
VEGA BAJA | 2021-12-17 08:22 | 2021-12-17 08:37 | 27 | 000:15 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17200 | B21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-12-17 | 405 | keep | 0 | Dec | 2021 | 0.00027584 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
VEGA BAJA | 2021-12-17 08:22 | 2021-12-17 08:37 | 603 | 000:15 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17200 | B21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-12-17 | 9045 | keep | 0 | Dec | 2021 | 0.0061605 | 0.0004107 | Sustained | FALSE | FALSE | Not_TMED_Event | 603
VEGA BAJA | 2021-12-17 08:22 | 2021-12-17 08:37 | 6 | 000:15 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17200 | B21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-12-17 | 90 | keep | 0 | Dec | 2021 | 6.1299e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2021-12-17 08:22 | 2021-12-17 08:37 | 325 | 000:15 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17200 | B21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-12-17 | 4875 | keep | 0 | Dec | 2021 | 0.0033203 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
VEGA BAJA | 2021-12-17 08:22 | 2021-12-17 08:37 | 172 | 000:15 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17200 | B21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-12-17 | 2580 | keep | 0 | Dec | 2021 | 0.0017572 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
BARRANQUITAS | 2021-12-17 08:27 | 2021-12-17 08:28 | 1604 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C21121700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-17 | 1604 | keep | 0 | Dec | 2021 | 0.0010925 | 0.0010925 | Momentary | FALSE | FALSE | Not_TMED_Event | 1604
SAN JUAN | 2021-12-17 08:40 | 2021-12-17 12:09 | 12 | 003:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | S21121700012 | New_Event | Wire Down | Include | Include | Equipment | 209 | 2021-12-17 | 2508 | keep | 0 | Dec | 2021 | 0.0017082 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-12-17 08:42 | 2021-12-17 11:40 | 12 | 002:58 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA X 50 KVA | C21121700015 | New_Event | Service Transformer Failure | Include | Include | Equipment | 178 | 2021-12-17 | 2136 | keep | 0 | Dec | 2021 | 0.0014548 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-12-17 08:49 | 2021-12-17 12:17 | 10 | 003:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO CAJA QUEMADA EN TRANSFORMADOR | A21121700010 | New_Event | Cutout Failure | Include | Include | Equipment | 208 | 2021-12-17 | 2080 | keep | 0 | Dec | 2021 | 0.0014167 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-17 08:56 | 2021-12-17 16:33 | 1 | 007:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M21121700033 | New_Event | Bad Weather | Include | Include | Weather | 457 | 2021-12-17 | 457 | keep | 0 | Dec | 2021 | 0.00031126 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2021-12-17 08:57 | 2021-12-17 11:03 | 80 | 002:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA FUERTES VIENTOS | P21121700011 | New_Event | Bad Weather | Include | Include | Weather | 126 | 2021-12-17 | 10080 | keep | 0 | Dec | 2021 | 0.0068654 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-12-17 09:02 | 2021-12-17 09:07 | 10211 | 000:05 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1206-3 | S21121700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-12-17 | 51055 | keep | 0 | Dec | 2021 | 0.034773 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-12-17 09:02 | 2021-12-17 09:07 | 4133 | 000:05 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1204-5 | S21121700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-12-17 | 20665 | keep | 0 | Dec | 2021 | 0.014075 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
ARECIBO | 2021-12-17 09:08 | 2021-12-17 10:48 | 308 | 001:40 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETES QUEMADO DE 900AMP MARCA COOPER EN EL FID29833632 Y SE CERRO EL INTERRUPTOR NO HAY EVENTO RELACIONADO | A21121700000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 100 | 2021-12-17 | 30800 | keep | 0 | Dec | 2021 | 0.020978 | 0.00020978 | Sustained | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2021-12-17 09:18 | 2021-12-17 13:00 | 1 | 003:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA SE REMPLAZO CAJA | B21121700017 | New_Event | Cutout Failure | Include | Include | Equipment | 222 | 2021-12-17 | 222 | keep | 0 | Dec | 2021 | 0.0001512 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-12-17 09:27 | 2021-12-17 12:56 | 96 | 003:29 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTE DE LINEA | C21121700022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2021-12-17 | 20064 | keep | 0 | Dec | 2021 | 0.013665 | 6.5385e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 96
SAN JUAN | 2021-12-17 09:35 | 2021-12-17 15:23 | 15 | 005:48 | P | NO SE REPORTO CAUSA | 1 X 20 EN C/L | S21121700020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 348 | 2021-12-17 | 5220 | keep | 0 | Dec | 2021 | 0.0035553 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-12-17 09:42 | 2021-12-17 10:24 | 3 | 000:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR SE REPARO BARRA EN PEDESTAL | C21121600166 | New_Event | Wire Down | Include | Include | Equipment | 42 | 2021-12-17 | 126 | keep | 0 | Dec | 2021 | 8.5818e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2021-12-17 09:45 | 2021-12-17 10:25 | 14 | 000:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DIERON CONECTORES DE LINEA A CAJA | C21121700026 | New_Event | Wire Down | Include | Include | Equipment | 40 | 2021-12-17 | 560 | keep | 0 | Dec | 2021 | 0.00038141 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
VEGA BAJA | 2021-12-17 09:52 | 2021-12-17 10:18 | 1 | 000:26 | P | NO SE REPORTO CAUSA | 1 X 20 EN MONTURA DE TRANSFORMADORES | B21121700021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 26 | 2021-12-17 | 26 | keep | 0 | Dec | 2021 | 1.7708e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-17 09:54 | 2021-12-17 11:07 | 15 | 001:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21121700003 | New_Event | Secondary Wire Down | Include | Include | Equipment | 73 | 2021-12-17 | 1095 | keep | 0 | Dec | 2021 | 0.0007458 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-12-17 10:00 | 2021-12-17 15:12 | 7 | 005:12 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIO XMR PARA REMPLAZAR POSTE SECUNDARIO | R21121200032 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 312 | 2021-12-17 | 2184 | keep | 0 | Dec | 2021 | 0.0014875 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2021-12-17 10:01 | 2021-12-17 11:35 | 1 | 001:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R21121700025 | New_Event |  |  | Include | Wildlife | 94 | 2021-12-17 | 94 | keep | 0 | Dec | 2021 | 6.4023e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-12-17 10:03 | 2021-12-17 12:27 | 11 | 002:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR 150 PIES DE SECUNDARIA | C21121600108 | New_Event | Secondary Wire Down | Include | Include | Equipment | 144 | 2021-12-17 | 1584 | keep | 0 | Dec | 2021 | 0.0010789 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2021-12-17 10:07 | 2021-12-17 10:18 | 68 | 000:11 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1520-5 | S21121700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 11 | 2021-12-17 | 748 | keep | 0 | Dec | 2021 | 0.00050946 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
BAYAMON | 2021-12-17 10:07 | 2021-12-17 10:18 | 68 | 000:11 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1520-5 | S21121700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 11 | 2021-12-17 | 748 | keep | 0 | Dec | 2021 | 0.00050946 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
BAYAMON | 2021-12-17 10:07 | 2021-12-17 10:18 | 68 | 000:11 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO LLEVA 1520-1 Y 1520-4 | S21121700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 11 | 2021-12-17 | 748 | keep | 0 | Dec | 2021 | 0.00050946 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
MAYAGÃœEZ | 2021-12-17 10:07 | 2021-12-17 17:11 | 150 | 007:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | M21121700052 | New_Event | Wire Down | Include | Include | Equipment | 424 | 2021-12-17 | 63600 | keep | 0 | Dec | 2021 | 0.043318 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2021-12-17 10:14 | 2021-12-17 12:21 | 15 | 002:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21121700020 | New_Event | Secondary Wire Down | Include | Include | Equipment | 127 | 2021-12-17 | 1905 | keep | 0 | Dec | 2021 | 0.0012975 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-12-17 10:15 | 2021-12-17 10:18 | 1526 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17200 | B21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-17 | 4578 | keep | 0 | Dec | 2021 | 0.0031181 | 0.0010394 | Momentary | FALSE | FALSE | Not_TMED_Event | 1526
VEGA BAJA | 2021-12-17 10:15 | 2021-12-17 10:18 | 308 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17200 | B21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-17 | 924 | keep | 0 | Dec | 2021 | 0.00062933 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2021-12-17 10:15 | 2021-12-17 10:18 | 1397 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17200 | B21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-17 | 4191 | keep | 0 | Dec | 2021 | 0.0028545 | 0.00095149 | Momentary | FALSE | FALSE | Not_TMED_Event | 1397
VEGA BAJA | 2021-12-17 10:15 | 2021-12-17 10:18 | 2926 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17200 | B21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-17 | 8778 | keep | 0 | Dec | 2021 | 0.0059787 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
VEGA BAJA | 2021-12-17 10:15 | 2021-12-17 10:18 | 27 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17200 | B21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-17 | 81 | keep | 0 | Dec | 2021 | 5.5169e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
VEGA BAJA | 2021-12-17 10:15 | 2021-12-17 10:18 | 603 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17200 | B21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-17 | 1809 | keep | 0 | Dec | 2021 | 0.0012321 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
VEGA BAJA | 2021-12-17 10:15 | 2021-12-17 10:18 | 6 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17200 | B21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-17 | 18 | keep | 0 | Dec | 2021 | 1.226e-05 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2021-12-17 10:15 | 2021-12-17 10:18 | 325 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17200 | B21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-17 | 975 | keep | 0 | Dec | 2021 | 0.00066407 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
VEGA BAJA | 2021-12-17 10:15 | 2021-12-17 10:18 | 172 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17200 | B21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-12-17 | 516 | keep | 0 | Dec | 2021 | 0.00035145 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
CANOVANAS | 2021-12-17 10:17 | 2021-12-17 12:00 | 11 | 001:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO T-44 PARA REPARAR CONECTORES SULFATADOS EN BARRA DE PEDESTAL | R21121600007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 103 | 2021-12-17 | 1133 | keep | 0 | Dec | 2021 | 0.00077168 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2021-12-17 10:17 | 2021-12-17 14:49 | 29 | 004:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE FIJO CAJA PRIMARIA | C21121700031 | New_Event | Cutout Failure | Include | Include | Equipment | 272 | 2021-12-17 | 7888 | keep | 0 | Dec | 2021 | 0.0053725 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
BARRANQUITAS | 2021-12-17 10:17 | 2021-12-17 13:03 | 4 | 002:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA PARA REPARAR NEUTRAL SECUNDARIO | C21121600151 | New_Event | Secondary Wire Down | Include | Include | Equipment | 166 | 2021-12-17 | 664 | keep | 0 | Dec | 2021 | 0.00045225 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2021-12-17 10:22 | 2021-12-17 14:41 | 245 | 004:19 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21121700032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2021-12-17 | 63455 | keep | 0 | Dec | 2021 | 0.043219 | 0.00016687 | Sustained | FALSE | FALSE | Not_TMED_Event | 245
FAJARDO | 2021-12-17 10:52 | 2021-12-17 11:19 | 60 | 000:27 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO CAUSA | R21121700029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 27 | 2021-12-17 | 1620 | keep | 0 | Dec | 2021 | 0.0011034 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-12-17 10:53 | 2021-12-17 17:12 | 600 | 006:19 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PRIMARIO PARTIDO | A21121700032 | New_Event | Defective Pole | Include | Include | Equipment | 379 | 2021-12-17 | 227400 | keep | 0 | Dec | 2021 | 0.15488 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
ARECIBO | 2021-12-17 10:55 | 2021-12-17 10:56 | 3431 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | A21121700033 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-12-17 | 3431 | keep | 0 | Dec | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
BAYAMON | 2021-12-17 10:56 | 2021-12-17 12:13 | 80 | 001:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | S21121700000 | New_Event | Cutout Failure | Include | Include | Equipment | 77 | 2021-12-17 | 6160 | keep | 0 | Dec | 2021 | 0.0041955 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2021-12-17 10:56 | 2021-12-17 14:25 | 1 | 003:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN RISER MAL TIEMPO VIENTOS FUERTES | A21121700057 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 209 | 2021-12-17 | 209 | keep | 0 | Dec | 2021 | 0.00014235 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-12-17 10:57 | 2021-12-17 14:26 | 8 | 003:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C21121700029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 209 | 2021-12-17 | 1672 | keep | 0 | Dec | 2021 | 0.0011388 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-12-17 11:00 | 2021-12-17 12:59 | 12 | 001:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21121700029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 119 | 2021-12-17 | 1428 | keep | 0 | Dec | 2021 | 0.0009726 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-12-17 11:08 | 2021-12-17 11:59 | 15 | 000:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21121600100 | New_Event | Secondary Wire Down | Include | Include | Equipment | 51 | 2021-12-17 | 765 | keep | 0 | Dec | 2021 | 0.00052104 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2021-12-17 11:15 | 2021-12-17 12:09 | 10 | 000:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO EN XMR | R21121700030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 54 | 2021-12-17 | 540 | keep | 0 | Dec | 2021 | 0.00036779 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-12-17 11:55 | 2021-12-17 14:15 | 80 | 002:20 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | P21121700023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2021-12-17 | 11200 | keep | 0 | Dec | 2021 | 0.0076283 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-12-17 12:06 | 2021-12-17 16:30 | 3 | 004:24 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA POR 25 KVA | M21121700064 | New_Event | Service Transformer Failure | Include | Include | Equipment | 264 | 2021-12-17 | 792 | keep | 0 | Dec | 2021 | 0.00053943 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2021-12-17 12:15 | 2021-12-17 14:18 | 7 | 002:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR CRUCE X REPTIL | R21121700028 | New_Event |  |  | Include | Wildlife | 123 | 2021-12-17 | 861 | keep | 0 | Dec | 2021 | 0.00058642 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-12-17 12:28 | 2021-12-17 20:13 | 100 | 007:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINE PRIMARIA PARTIDA Y SE REMPLAZO HERRAJES PODRIDOS | A21121700046 | New_Event | Wire Down | Include | Include | Equipment | 465 | 2021-12-17 | 46500 | keep | 0 | Dec | 2021 | 0.031671 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-12-17 12:32 | 2021-12-17 12:33 | 500 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO NO RECERRO 20% POR 1118-10 | S21121700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-17 | 500 | keep | 0 | Dec | 2021 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2021-12-17 12:32 | 2021-12-17 12:33 | 2782 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO LLEVA 20% DEL 1111-1 | S21121700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-17 | 2782 | keep | 0 | Dec | 2021 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
FAJARDO | 2021-12-17 12:32 | 2021-12-17 12:49 | 40 | 000:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ABIERTO DE LINEA @ CAJA PRIMARIA | R21121700032 | New_Event | Wire Down | Include | Include | Equipment | 17 | 2021-12-17 | 680 | keep | 0 | Dec | 2021 | 0.00046314 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2021-12-17 12:34 | 2021-12-17 15:31 | 8 | 002:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR REMPLAZO CAJA QUEMADA | R21121700033 | New_Event | Cutout Failure | Include | Include | Equipment | 177 | 2021-12-17 | 1416 | keep | 0 | Dec | 2021 | 0.00096443 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2021-12-17 12:41 | 2021-12-18 09:16 | 60 | 020:35 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C21121700045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1235 | 2021-12-17 | 74100 | keep | 0 | Dec | 2021 | 0.050469 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2021-12-17 12:45 | 2021-12-17 12:50 | 2725 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LA LINEA 4800 DE SANTA ISABEL A CAYEY | C21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-17 | 13625 | keep | 0 | Dec | 2021 | 0.0092799 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2021-12-17 12:45 | 2021-12-17 12:50 | 1834 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LA LINEA 4800 DE SANTA ISABEL A CAYEY | C21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-17 | 9170 | keep | 0 | Dec | 2021 | 0.0062456 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2021-12-17 12:45 | 2021-12-17 12:50 | 1437 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LA LINEA 4800 DE SANTA ISABEL A CAYEY | C21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-17 | 7185 | keep | 0 | Dec | 2021 | 0.0048937 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2021-12-17 12:45 | 2021-12-17 12:50 | 2565 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LA LINEA 4800 DE SANTA ISABEL A CAYEY | C21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-17 | 12825 | keep | 0 | Dec | 2021 | 0.008735 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2021-12-17 12:45 | 2021-12-17 12:50 | 3565 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LA LINEA 4800 DE SANTA ISABEL A CAYEY | C21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-17 | 17825 | keep | 0 | Dec | 2021 | 0.012141 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
ARECIBO | 2021-12-17 12:45 | 2021-12-17 14:10 | 40 | 001:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO AISLADOR QUEMADO | A21121700048 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 85 | 2021-12-17 | 3400 | keep | 0 | Dec | 2021 | 0.0023157 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2021-12-17 12:46 | 2021-12-17 14:44 | 172 | 001:58 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21121700046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2021-12-17 | 20296 | keep | 0 | Dec | 2021 | 0.013824 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
BAYAMON | 2021-12-17 12:49 | 2021-12-17 16:47 | 12 | 003:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21121700037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 238 | 2021-12-17 | 2856 | keep | 0 | Dec | 2021 | 0.0019452 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-12-17 12:52 | 2021-12-17 12:53 | 2751 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P21121700030 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-17 | 2751 | keep | 0 | Dec | 2021 | 0.0018737 | 0.0018737 | Momentary | FALSE | FALSE | Not_TMED_Event | 2751
PONCE | 2021-12-17 12:52 | 2021-12-17 12:53 | 576 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P21121700030 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-17 | 576 | keep | 0 | Dec | 2021 | 0.00039231 | 0.00039231 | Momentary | FALSE | FALSE | Not_TMED_Event | 576
PONCE | 2021-12-17 12:52 | 2021-12-17 12:53 | 2584 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P21121700030 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-17 | 2584 | keep | 0 | Dec | 2021 | 0.00176 | 0.00176 | Momentary | FALSE | FALSE | Not_TMED_Event | 2584
PONCE | 2021-12-17 12:52 | 2021-12-17 12:53 | 1606 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P21121700030 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-17 | 1606 | keep | 0 | Dec | 2021 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
PONCE | 2021-12-17 12:52 | 2021-12-17 12:53 | 29 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P21121700030 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-17 | 29 | keep | 0 | Dec | 2021 | 1.9752e-05 | 1.9752e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 29
PONCE | 2021-12-17 12:52 | 2021-12-17 12:53 | 4035 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P21121700030 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-17 | 4035 | keep | 0 | Dec | 2021 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
PONCE | 2021-12-17 12:52 | 2021-12-17 12:53 | 3718 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P21121700030 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-17 | 3718 | keep | 0 | Dec | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
YAUCO | 2021-12-17 12:58 | 2021-12-17 17:00 | 50 | 004:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | P21121700029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2021-12-17 | 12100 | keep | 0 | Dec | 2021 | 0.0082413 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-12-17 13:04 | 2021-12-17 13:05 | 2126 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C21121700051 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-12-17 | 2126 | keep | 0 | Dec | 2021 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2021-12-17 13:05 | 2021-12-17 17:09 | 4 | 004:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C21121700053 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 244 | 2021-12-17 | 976 | keep | 0 | Dec | 2021 | 0.00066475 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-12-17 13:09 | 2021-12-17 16:56 | 10 | 003:47 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | S21121700044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2021-12-17 | 2270 | keep | 0 | Dec | 2021 | 0.0015461 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-12-17 13:35 | 2021-12-17 19:20 | 100 | 005:45 | P | LINEA DE TRANSMISION 38KV | SE ABRIO CORTE DE LINEA POR CRUCETA PARTIDA EN LINEA 2700 | M21121700078 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 345 | 2021-12-17 | 34500 | keep | 0 | Dec | 2021 | 0.023498 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2021-12-17 13:41 | 2021-12-17 13:42 | 1284 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21121700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-17 | 1284 | keep | 0 | Dec | 2021 | 0.00087453 | 0.00087453 | Momentary | FALSE | FALSE | Not_TMED_Event | 1284
BAYAMON | 2021-12-17 13:54 | 2021-12-17 13:56 | 599 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR CONTROL 20% DE LA CARGA TRANSFERIDA AL 1717-04 | B21121700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-17 | 1198 | keep | 0 | Dec | 2021 | 0.00081595 | 0.00040798 | Momentary | FALSE | FALSE | Not_TMED_Event | 599
MAYAGÃœEZ | 2021-12-17 13:57 | 2021-12-17 15:20 | 5 | 001:23 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA | M21121700092 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 83 | 2021-12-17 | 415 | keep | 0 | Dec | 2021 | 0.00028265 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2021-12-17 13:57 | 2021-12-17 15:53 | 30 | 001:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | B21121700030 | New_Event | Wire Down | Include | Include | Equipment | 116 | 2021-12-17 | 3480 | keep | 0 | Dec | 2021 | 0.0023702 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-12-17 13:58 | 2021-12-17 18:26 | 40 | 004:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE FIJO PISTOLA EN BUSHING PERSONAL DE AAA HALO LA LINEA HACIENDO EXCAVACION | R21121700035 | New_Event |  |  | Include | Wildlife | 268 | 2021-12-17 | 10720 | keep | 0 | Dec | 2021 | 0.0073013 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-12-17 14:14 | 2021-12-17 16:36 | 110 | 002:22 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 200 EN C/L REMPLAZO AISLADOR QUEMADO | R21121700038 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 142 | 2021-12-17 | 15620 | keep | 0 | Dec | 2021 | 0.010639 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
FAJARDO | 2021-12-17 14:16 | 2021-12-17 16:53 | 17 | 002:37 | P | AISLADOR ROTO, PARTIDO O SAFADO | ABRIO XMR PARA REMPLAZAR AISLACION Y RELOCALIZAR PARARRAYO DE XMR | R21121700039 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 157 | 2021-12-17 | 2669 | keep | 0 | Dec | 2021 | 0.0018178 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
MAYAGÃœEZ | 2021-12-17 14:17 | 2021-12-18 10:44 | 1 | 020:27 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR EL JOURNEYMAN NO ENCONTRO CAUSA PARA EL FUSIBLE FUNDIDO | M21121700094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1227 | 2021-12-17 | 1227 | keep | 0 | Dec | 2021 | 0.0008357 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-12-17 14:29 | 2021-12-17 17:05 | 39 | 002:36 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO ENCONTRO CAUSA | C21121700062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 156 | 2021-12-17 | 6084 | keep | 0 | Dec | 2021 | 0.0041438 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
HUMACAO | 2021-12-17 14:37 | 2021-12-17 14:38 | 1835 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C21121700065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-17 | 1835 | keep | 0 | Dec | 2021 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
PONCE | 2021-12-17 14:44 | 2021-12-17 15:45 | 1 | 001:01 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | P21121700043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2021-12-17 | 61 | keep | 0 | Dec | 2021 | 4.1547e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-17 14:44 | 2021-12-18 13:14 | 80 | 022:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA FUERTE VIENTO | M21121700097 | New_Event | Bad Weather | Include | Include | Weather | 1350 | 2021-12-17 | 108000 | keep | 0 | Dec | 2021 | 0.073558 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2021-12-17 14:54 | 2021-12-17 14:55 | 4390 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 9300 DE JUNCOS A SAN LORENZO | C21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-17 | 4390 | keep | 0 | Dec | 2021 | 0.00299 | 0.00299 | Momentary | FALSE | FALSE | Not_TMED_Event | 4390
CAGUAS | 2021-12-17 14:54 | 2021-12-17 14:55 | 2092 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 9300 DE JUNCOS A SAN LORENZO | C21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-17 | 2092 | keep | 0 | Dec | 2021 | 0.0014249 | 0.0014249 | Momentary | FALSE | FALSE | Not_TMED_Event | 2092
CAGUAS | 2021-12-17 14:54 | 2021-12-17 14:55 | 540 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 9300 DE JUNCOS A SAN LORENZO | C21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-17 | 540 | keep | 0 | Dec | 2021 | 0.00036779 | 0.00036779 | Momentary | FALSE | FALSE | Not_TMED_Event | 540
CAGUAS | 2021-12-17 14:54 | 2021-12-17 14:55 | 131 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 9300 DE JUNCOS A SAN LORENZO | C21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-17 | 131 | keep | 0 | Dec | 2021 | 8.9224e-05 | 8.9224e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 131
CAGUAS | 2021-12-17 14:54 | 2021-12-17 14:55 | 2281 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 9300 DE JUNCOS A SAN LORENZO | C21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-17 | 2281 | keep | 0 | Dec | 2021 | 0.0015536 | 0.0015536 | Momentary | FALSE | FALSE | Not_TMED_Event | 2281
CAGUAS | 2021-12-17 14:54 | 2021-12-17 14:55 | 1569 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 9300 DE JUNCOS A SAN LORENZO | C21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-17 | 1569 | keep | 0 | Dec | 2021 | 0.0010686 | 0.0010686 | Momentary | FALSE | FALSE | Not_TMED_Event | 1569
CAGUAS | 2021-12-17 14:54 | 2021-12-17 14:55 | 2417 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 9300 DE JUNCOS A SAN LORENZO | C21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-17 | 2417 | keep | 0 | Dec | 2021 | 0.0016462 | 0.0016462 | Momentary | FALSE | FALSE | Not_TMED_Event | 2417
YAUCO | 2021-12-17 15:05 | 2021-12-17 15:39 | 50 | 000:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE EN CORTE DE LINEA SAFADO NO SE REMPLAZO FUSIBLE | P21121700032 | New_Event | Wire Down | Include | Include | Equipment | 34 | 2021-12-17 | 1700 | keep | 0 | Dec | 2021 | 0.0011579 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-17 15:06 | 2021-12-17 21:17 | 6 | 006:11 | P | TRANSFORMADOR AVERIADO | SE PASO LA CARGA A OTRO TRANSFORMADOR | B21121700046 | New_Event | Service Transformer Failure | Include | Include | Equipment | 371 | 2021-12-17 | 2226 | keep | 0 | Dec | 2021 | 0.0015161 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2021-12-17 15:07 | 2021-12-17 17:41 | 5 | 002:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE TRANSFORMADOR | C21121700070 | New_Event | Wire Down | Include | Include | Equipment | 154 | 2021-12-17 | 770 | keep | 0 | Dec | 2021 | 0.00052444 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-12-17 15:15 | 2021-12-17 17:12 | 25 | 001:57 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21121700071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2021-12-17 | 2925 | keep | 0 | Dec | 2021 | 0.0019922 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2021-12-17 15:16 | 2021-12-17 17:13 | 117 | 001:57 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21121700072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2021-12-17 | 13689 | keep | 0 | Dec | 2021 | 0.0093235 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
SAN JUAN | 2021-12-17 15:24 | 2021-12-17 15:25 | 1066 | 000:01 | T | DESGANCHE | SE CERRO POR SCADA AMERITA DESGANCHE | S21121700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-17 | 1066 | keep | 0 | Dec | 2021 | 0.00072605 | 0.00072605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1066
CAGUAS | 2021-12-17 15:26 | 2021-12-18 10:15 | 80 | 018:49 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21121700074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1129 | 2021-12-17 | 90320 | keep | 0 | Dec | 2021 | 0.061517 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-12-17 15:27 | 2021-12-17 16:10 | 1066 | 000:43 | T | DESGANCHE | SE SECCIONALIZO ALIMENTADOR PARA REALIZAR DESGANCHE Y SE CERRO POR SCADA | S21121700054 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 43 | 2021-12-17 | 45838 | keep | 0 | Dec | 2021 | 0.03122 | 0.00072605 | Sustained | FALSE | FALSE | Not_TMED_Event | 1066
YAUCO | 2021-12-17 15:27 | 2021-12-17 18:14 | 80 | 002:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | P21121700052 | New_Event | Bad Weather | Include | Include | Weather | 167 | 2021-12-17 | 13360 | keep | 0 | Dec | 2021 | 0.0090994 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2021-12-17 15:35 | 2021-12-17 15:36 | 1105 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | A21121700000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-12-17 | 1105 | keep | 0 | Dec | 2021 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
ARECIBO | 2021-12-17 15:36 | 2021-12-17 18:31 | 200 | 002:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES Y DESGANCHE | A21121700065 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 175 | 2021-12-17 | 35000 | keep | 0 | Dec | 2021 | 0.023838 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2021-12-17 15:40 | 2021-12-17 17:42 | 30 | 002:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21121700081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2021-12-17 | 3660 | keep | 0 | Dec | 2021 | 0.0024928 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-12-17 15:44 | 2021-12-17 18:29 | 76 | 002:45 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | C21121700079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2021-12-17 | 12540 | keep | 0 | Dec | 2021 | 0.0085409 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
BARRANQUITAS | 2021-12-17 15:47 | 2021-12-17 15:48 | 2410 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 18400 DE BARRANQUITAS AL ABANICO | C21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-17 | 2410 | keep | 0 | Dec | 2021 | 0.0016414 | 0.0016414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2410
BARRANQUITAS | 2021-12-17 15:47 | 2021-12-17 15:48 | 2826 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 18400 DE BARRANQUITAS AL ABANICO | C21121700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-17 | 2826 | keep | 0 | Dec | 2021 | 0.0019248 | 0.0019248 | Momentary | FALSE | FALSE | Not_TMED_Event | 2826
BAYAMON | 2021-12-17 15:51 | 2021-12-17 19:57 | 40 | 004:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO CAJA | S21121711160 | New_Event | Cutout Failure | Include | Include | Equipment | 246 | 2021-12-17 | 9840 | keep | 0 | Dec | 2021 | 0.006702 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2021-12-17 15:52 | 2021-12-17 22:55 | 2410 | 007:03 | S | LINEA DE TRANSMISION 38KV | SE LEVANTO FASE DE LA LINEA 18400 | C21121700082 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 423 | 2021-12-17 | 1019430 | keep | 0 | Dec | 2021 | 0.69433 | 0.0016414 | Sustained | FALSE | FALSE | Not_TMED_Event | 2410
BARRANQUITAS | 2021-12-17 15:52 | 2021-12-17 22:55 | 2826 | 007:03 | S | LINEA DE TRANSMISION 38KV | SE LEVANTO FASE DE LA LINEA 18400 | C21121700082 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 423 | 2021-12-17 | 1195398 | keep | 0 | Dec | 2021 | 0.81418 | 0.0019248 | Sustained | FALSE | FALSE | Not_TMED_Event | 2826
ARECIBO | 2021-12-17 15:55 | 2021-12-17 21:17 | 80 | 005:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO | A21121700104 | New_Event | Wire Down | Include | Include | Equipment | 322 | 2021-12-17 | 25760 | keep | 0 | Dec | 2021 | 0.017545 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-12-17 15:57 | 2021-12-17 18:00 | 50 | 002:03 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S21121700061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 123 | 2021-12-17 | 6150 | keep | 0 | Dec | 2021 | 0.0041887 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-17 15:58 | 2021-12-17 16:53 | 40 | 000:55 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | S21121700062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 55 | 2021-12-17 | 2200 | keep | 0 | Dec | 2021 | 0.0014984 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2021-12-17 16:03 | 2021-12-17 16:04 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21121700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-17 | 3041 | keep | 0 | Dec | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
SAN JUAN | 2021-12-17 16:06 | 2021-12-17 19:11 | 32 | 003:05 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN C/L SE REMPLAZO AISLADOR | S21121700066 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 185 | 2021-12-17 | 5920 | keep | 0 | Dec | 2021 | 0.0040321 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
SAN JUAN | 2021-12-17 16:10 | 2021-12-17 16:56 | 256 | 000:46 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRARON MACHETES PREVIAMENTE ABIERTOS | S21161700054 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 46 | 2021-12-17 | 11776 | keep | 0 | Dec | 2021 | 0.0080206 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-17 16:18 | 2021-12-17 18:38 | 30 | 002:20 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21121700068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 140 | 2021-12-17 | 4200 | keep | 0 | Dec | 2021 | 0.0028606 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-12-17 16:28 | 2021-12-17 17:29 | 5 | 001:01 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA DESGANCHAR Y REPARAR SECUNDARIA | C21121700044 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 61 | 2021-12-17 | 305 | keep | 0 | Dec | 2021 | 0.00020773 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2021-12-17 16:36 | 2021-12-17 17:08 | 2708 | 000:32 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO NO RTU | R21121700055 | New_Event | Cutout Failure | Include | Include | Equipment | 32 | 2021-12-17 | 86656 | keep | 0 | Dec | 2021 | 0.059021 | 0.0018444 | Sustained | FALSE | FALSE | Not_TMED_Event | 2708
MAYAGÃœEZ | 2021-12-17 16:49 | 2021-12-17 18:57 | 1 | 002:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA DE TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | M21121700070 | New_Event | Secondary Wire Down | Include | Include | Equipment | 128 | 2021-12-17 | 128 | keep | 0 | Dec | 2021 | 8.718e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-12-17 17:08 | 2021-12-17 19:01 | 150 | 001:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 Y 3 X 40 EN CORTES DE LINEA REMPLAZO 2 CAJAS QUEMADAS | R21121700071 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 113 | 2021-12-17 | 16950 | keep | 0 | Dec | 2021 | 0.011545 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-17 17:09 | 2021-12-17 17:10 | 4089 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21121700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-17 | 4089 | keep | 0 | Dec | 2021 | 0.002785 | 0.002785 | Momentary | FALSE | FALSE | Not_TMED_Event | 4089
SAN JUAN | 2021-12-17 17:21 | 2021-12-17 19:25 | 25 | 002:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21121700056 | New_Event | Secondary Wire Down | Include | Include | Equipment | 124 | 2021-12-17 | 3100 | keep | 0 | Dec | 2021 | 0.0021114 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2021-12-17 17:26 | 2021-12-18 08:48 | 13 | 015:22 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE REALIZO DESGANCHE SECUNDARIO | P21121700063 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 922 | 2021-12-17 | 11986 | keep | 0 | Dec | 2021 | 0.0081636 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2021-12-17 17:28 | 2021-12-17 17:29 | 2610 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | B21121700000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-12-17 | 2610 | keep | 0 | Dec | 2021 | 0.0017777 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
VEGA BAJA | 2021-12-17 17:29 | 2021-12-18 00:21 | 40 | 006:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO CON GOI BY-211217-01 | B21121700103 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 412 | 2021-12-17 | 16480 | keep | 0 | Dec | 2021 | 0.011224 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-12-17 17:29 | 2021-12-17 17:30 | 3387 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21121700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-17 | 3387 | keep | 0 | Dec | 2021 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
MAYAGÃœEZ | 2021-12-17 17:36 | 2021-12-18 12:24 | 150 | 018:48 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21121700115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1128 | 2021-12-17 | 169200 | keep | 0 | Dec | 2021 | 0.11524 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2021-12-17 17:37 | 2021-12-17 19:06 | 80 | 001:29 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21121700092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 89 | 2021-12-17 | 7120 | keep | 0 | Dec | 2021 | 0.0048494 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2021-12-17 18:12 | 2021-12-17 19:24 | 10 | 001:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON 2 CAJAS PRIMARIAS AVERIADAS | A21121700082 | New_Event | Cutout Failure | Include | Include | Equipment | 72 | 2021-12-17 | 720 | keep | 0 | Dec | 2021 | 0.00049039 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-17 18:22 | 2021-12-17 19:30 | 5 | 001:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE TRANSFORMADOR | C21121700156 | New_Event | Wire Down | Include | Include | Equipment | 68 | 2021-12-17 | 340 | keep | 0 | Dec | 2021 | 0.00023157 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-12-17 18:22 | 2021-12-17 20:33 | 20 | 002:11 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21121700084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2021-12-17 | 2620 | keep | 0 | Dec | 2021 | 0.0017845 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-12-17 18:30 | 2021-12-18 10:00 | 80 | 015:30 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21121700125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 930 | 2021-12-17 | 74400 | keep | 0 | Dec | 2021 | 0.050674 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-12-17 18:31 | 2021-12-17 22:30 | 75 | 003:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR FUERTES VIENTOS | M21121700126 | New_Event | Bad Weather | Include | Include | Weather | 239 | 2021-12-17 | 17925 | keep | 0 | Dec | 2021 | 0.012209 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2021-12-17 18:32 | 2021-12-17 19:37 | 40 | 001:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21121700086 | New_Event | Bad Weather | Include | Include | Weather | 65 | 2021-12-17 | 2600 | keep | 0 | Dec | 2021 | 0.0017708 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-12-17 18:34 | 2021-12-18 13:04 | 50 | 018:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | C21121700164 | New_Event | Wire Down | Include | Include | Equipment | 1110 | 2021-12-17 | 55500 | keep | 0 | Dec | 2021 | 0.037801 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-17 18:36 | 2021-12-17 22:12 | 10 | 003:36 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | B21121700107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 216 | 2021-12-17 | 2160 | keep | 0 | Dec | 2021 | 0.0014712 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-17 19:19 | 2021-12-17 22:24 | 20 | 003:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | S21121700082 | New_Event | Cutout Failure | Include | Include | Equipment | 185 | 2021-12-17 | 3700 | keep | 0 | Dec | 2021 | 0.0025201 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2021-12-17 19:49 | 2021-12-17 21:41 | 6 | 001:52 | P | NO SE REPORTO CAUSA | 1 X 8 EN XMR NO CAUSA | R21121700089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2021-12-17 | 672 | keep | 0 | Dec | 2021 | 0.0004577 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2021-12-17 21:45 | 2021-12-17 22:00 | 10 | 000:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21121700114 | New_Event | Secondary Wire Down | Include | Include | Equipment | 15 | 2021-12-17 | 150 | keep | 0 | Dec | 2021 | 0.00010216 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-12-17 22:09 | 2021-12-18 15:00 | 20 | 016:51 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO Y SE CERRO PUENTES | M21121700143 | New_Event | Defective Pole | Include | Include | Equipment | 1011 | 2021-12-17 | 20220 | keep | 0 | Dec | 2021 | 0.013772 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-12-17 23:24 | 2021-12-18 09:59 | 40 | 010:35 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21121700128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 635 | 2021-12-17 | 25400 | keep | 0 | Dec | 2021 | 0.0173 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-12-17 23:47 | 2021-12-18 10:13 | 30 | 010:26 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | AVERIA NUEVA DE SU-2 @ T-8 SE CERRO N/O T-11 @ T-10 | B21121700130 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 626 | 2021-12-17 | 18780 | keep | 0 | Dec | 2021 | 0.012791 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2021-12-18 00:37 | 2021-12-18 02:24 | 10 | 001:47 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA SECCIONALIZAR POSTE SECUNDARIO PARTIDO | M21121800001 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 107 | 2021-12-18 | 1070 | keep | 0 | Dec | 2021 | 0.00072877 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-18 00:43 | 2021-12-18 01:45 | 820 | 001:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1303-02 LLEVANDO 20% 1204-02 SE CERRO POR SCADA NO SE ENCONTRO CAUSA | S21121800000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 62 | 2021-12-18 | 50840 | keep | 0 | Dec | 2021 | 0.034627 | 0.0005585 | Sustained | FALSE | FALSE | Not_TMED_Event | 820
SAN JUAN | 2021-12-18 00:43 | 2021-12-18 01:45 | 2435 | 001:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1303-02 LLEVANDO 20% 1204-02 SE CERRO POR SCADA NO SE ENCONTRO CAUSA | S21121800000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 62 | 2021-12-18 | 150970 | keep | 0 | Dec | 2021 | 0.10282 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
CANOVANAS | 2021-12-18 02:06 | 2021-12-18 02:08 | 3012 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | R21121800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-18 | 6024 | keep | 0 | Dec | 2021 | 0.0041029 | 0.0020515 | Momentary | FALSE | FALSE | Not_TMED_Event | 3012
SAN JUAN | 2021-12-18 02:10 | 2021-12-18 02:50 | 1050 | 000:40 | P | NO SE REPORTO CAUSA | DISPARO PORTATIL 8 LLEVANDO CARGA 1348-08 20% 1348-06 Y 20% 1336-08 SE CERRO EN SUBESTACION | S21121800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 40 | 2021-12-18 | 42000 | keep | 0 | Dec | 2021 | 0.028606 | 0.00071515 | Sustained | FALSE | FALSE | Not_TMED_Event | 1050
SAN JUAN | 2021-12-18 02:10 | 2021-12-18 02:50 | 251 | 000:40 | P | NO SE REPORTO CAUSA | DISPARO PORTATIL 8 LLEVANDO CARGA 1348-08 20% 1348-06 Y 20% 1336-08 SE CERRO EN SUBESTACION | S21121800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 40 | 2021-12-18 | 10040 | keep | 0 | Dec | 2021 | 0.0068382 | 0.00017095 | Sustained | FALSE | FALSE | Not_TMED_Event | 251
SAN JUAN | 2021-12-18 02:10 | 2021-12-18 02:50 | 1290 | 000:40 | T | NO SE REPORTO CAUSA | DISPARO PORTATIL 8 LLEVANDO CARGA 1348-08 20% 1348-06 Y 20% 1336-08 SE CERRO EN SUBESTACION | S21121800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 40 | 2021-12-18 | 51600 | keep | 0 | Dec | 2021 | 0.035145 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
BAYAMON | 2021-12-18 02:26 | 2021-12-18 03:43 | 4533 | 001:17 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1717-01 LLEVANDO CARGA 1717-05 SE CERRO POR SCADA PERSONAL DE SUBESTACIONES ENCONTRO EL SWITCH 69 ACTIVO | B21121800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 77 | 2021-12-18 | 349041 | keep | 0 | Dec | 2021 | 0.23773 | 0.0030874 | Sustained | FALSE | FALSE | Not_TMED_Event | 4533
BAYAMON | 2021-12-18 02:26 | 2021-12-18 03:43 | 341 | 001:17 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1717-01 LLEVANDO CARGA 1717-05 SE CERRO POR SCADA PERSONAL DE SUBESTACIONES ENCONTRO EL SWITCH 69 ACTIVO | B21121800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 77 | 2021-12-18 | 26257 | keep | 0 | Dec | 2021 | 0.017884 | 0.00023225 | Sustained | FALSE | FALSE | Not_TMED_Event | 341
SAN JUAN | 2021-12-18 02:52 | 2021-12-18 02:54 | 820 | 000:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1303-02 LLEVANDO 20% 1204-02 SE CERRO POR SCADA NO SE ENCONTRO CAUSA | S21121800000 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2021-12-18 | 1640 | keep | 0 | Dec | 2021 | 0.001117 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-18 02:52 | 2021-12-18 02:54 | 2435 | 000:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1303-02 LLEVANDO 20% 1204-02 SE CERRO POR SCADA NO SE ENCONTRO CAUSA | S21121800000 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2021-12-18 | 4870 | keep | 0 | Dec | 2021 | 0.0033169 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-18 03:33 | 2021-12-18 05:30 | 820 | 001:57 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1303-02 LLEVANDO 20% 1204-02 SE CERRO POR SCADA NO SE ENCONTRO CAUSA | S21121800000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 117 | 2021-12-18 | 95940 | keep | 0 | Dec | 2021 | 0.065344 | 0.0005585 | Sustained | FALSE | FALSE | Not_TMED_Event | 820
SAN JUAN | 2021-12-18 03:33 | 2021-12-18 05:30 | 2435 | 001:57 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1303-02 LLEVANDO 20% 1204-02 SE CERRO POR SCADA NO SE ENCONTRO CAUSA | S21121800000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 117 | 2021-12-18 | 284895 | keep | 0 | Dec | 2021 | 0.19404 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2021-12-18 04:43 | 2021-12-18 04:44 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21121800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-18 | 2203 | keep | 0 | Dec | 2021 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
FAJARDO | 2021-12-18 05:08 | 2021-12-18 05:09 | 970 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21121800002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-18 | 970 | keep | 0 | Dec | 2021 | 0.00066066 | 0.00066066 | Momentary | FALSE | FALSE | Not_TMED_Event | 970
SAN JUAN | 2021-12-18 05:36 | 2021-12-18 06:46 | 820 | 001:10 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRE MACHETE PARA SECCIONALIZAR AVERIA AISLADOR PARTIDO 20% DE LA CARGA DEL 1204-02 PARCIALMENTE TRANSFERIDA AL 1303-02 | S21121800060 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 70 | 2021-12-18 | 57400 | keep | 0 | Dec | 2021 | 0.039095 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-18 05:36 | 2021-12-18 06:46 | 2435 | 001:10 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO 1303-02 LLEVA 20% DEL 1204-2 Y SE ABRE MACHETE PARA SECCIOANLIZAR SE CERRO BKR. 70% EN SERVICIO | S21121800060 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 70 | 2021-12-18 | 170450 | keep | 0 | Dec | 2021 | 0.11609 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-18 05:45 | 2021-12-18 09:54 | 60 | 004:09 | P | NO SE REPORTO CAUSA | 1 X 50 EN PROVISIONAL AEREO | B21121800009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 249 | 2021-12-18 | 14940 | keep | 0 | Dec | 2021 | 0.010176 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2021-12-18 05:57 | 2021-12-18 05:58 | 1830 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R21121800003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-18 | 1830 | keep | 0 | Dec | 2021 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
AGUADILLA | 2021-12-18 05:58 | 2021-12-18 05:59 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21121800003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-18 | 3041 | keep | 0 | Dec | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
CAGUAS | 2021-12-18 06:00 | 2021-12-18 17:19 | 20 | 011:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE | C21121800003 | New_Event | Wire Down | Include | Include | Equipment | 679 | 2021-12-18 | 13580 | keep | 0 | Dec | 2021 | 0.0092493 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2021-12-18 06:02 | 2021-12-18 06:03 | 1830 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R21121800004 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-18 | 1830 | keep | 0 | Dec | 2021 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
SAN JUAN | 2021-12-18 06:03 | 2021-12-18 15:17 | 35 | 009:14 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S21121800055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 554 | 2021-12-18 | 19390 | keep | 0 | Dec | 2021 | 0.013206 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
FAJARDO | 2021-12-18 06:03 | 2021-12-18 06:04 | 710 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO INTERRUPTOR LLEVANDO LA CARGA DEL 2201-04 EN SERVICIO | R21121800005 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-12-18 | 710 | keep | 0 | Dec | 2021 | 0.00048358 | 0.00048358 | Momentary | FALSE | FALSE | Not_TMED_Event | 710
FAJARDO | 2021-12-18 06:03 | 2021-12-18 06:04 | 969 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO INTERRUPTOR CARGA POR EL 2201-03 EN SERVICIO | R21121800005 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-12-18 | 969 | keep | 0 | Dec | 2021 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
AGUADILLA | 2021-12-18 06:04 | 2021-12-18 06:05 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21121800005 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-18 | 3041 | keep | 0 | Dec | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
CANOVANAS | 2021-12-18 06:18 | 2021-12-18 09:39 | 70 | 003:21 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 30 EN CORTE DE LINEA SE REEMPLAZO AISLADOR ROTO | R21121800006 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 201 | 2021-12-18 | 14070 | keep | 0 | Dec | 2021 | 0.009583 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2021-12-18 06:20 | 2021-12-18 07:11 | 950 | 000:51 | P | DESGANCHE | DISPARO DE INTERRUPTOR. SE ENCONTRO BAMBUA SOBRE LINEA SE RETIRO CON VARETA EN AVE. SAN ROBERTO. CARGA PARCIAL A TRAVES DE LA PORTATIL #19 | S21121800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 51 | 2021-12-18 | 48450 | keep | 0 | Dec | 2021 | 0.032999 | 0.00064704 | Sustained | FALSE | FALSE | Not_TMED_Event | 950
YAUCO | 2021-12-18 06:35 | 2021-12-18 19:50 | 25 | 013:15 | P | ESTRUCTURA AVERIADA | 2 X 65 EN CORTE DE LINEA SE REMPLAZARON DOS POSTES PRIMARIOS Y SE LEVANTO LINEA | P21121800022 | New_Event | Defective Pole | Include | Include | Equipment | 795 | 2021-12-18 | 19875 | keep | 0 | Dec | 2021 | 0.013537 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-12-18 06:46 | 2021-12-18 07:13 | 1705 | 000:27 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REALIZARON OPERACIONES DE CAMPO SE ABRIO EN CUPEY BAJO Y SE CERRO EN CAMINO LOS ROMEROS 100% EN SERVICIO | S21121800060 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 27 | 2021-12-18 | 46035 | keep | 0 | Dec | 2021 | 0.031354 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2021-12-18 06:48 | 2021-12-18 06:49 | 710 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO INTERRUPTOR LLEVANDO LA CARGA DEL 2201-04 EN SERVICIO | R21121800007 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-12-18 | 710 | keep | 0 | Dec | 2021 | 0.00048358 | 0.00048358 | Momentary | FALSE | FALSE | Not_TMED_Event | 710
FAJARDO | 2021-12-18 06:48 | 2021-12-18 06:49 | 969 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO INTERRUPTOR CARGA POR EL 2201-03 EN SERVICIO | R21121800007 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-12-18 | 969 | keep | 0 | Dec | 2021 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
ARECIBO | 2021-12-18 06:49 | 2021-12-18 10:32 | 40 | 003:43 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS | A21121800001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 223 | 2021-12-18 | 8920 | keep | 0 | Dec | 2021 | 0.0060754 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2021-12-18 06:52 | 2021-12-18 07:57 | 710 | 001:05 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO INTERRUPTOR SE ABRIO AMARRE CON EL 2201-04 QUE TIENE AISLADOR ROTO PUENTE CRUZADO CERRADO POR CONTROL | R21121800008 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 65 | 2021-12-18 | 46150 | keep | 0 | Dec | 2021 | 0.031433 | 0.00048358 | Sustained | FALSE | FALSE | Not_TMED_Event | 710
FAJARDO | 2021-12-18 06:52 | 2021-12-18 08:30 | 969 | 001:38 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO AISLADOR ROTO SOBRE OTRA FASE SE CERRO AMARRE DEL 2201-04 CON 2201-03 FRENTE A LA SUBESTACION | R21121800029 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 98 | 2021-12-18 | 94962 | keep | 0 | Dec | 2021 | 0.064678 | 0.00065998 | Sustained | FALSE | FALSE | Not_TMED_Event | 969
CAGUAS | 2021-12-18 06:52 | 2021-12-18 11:01 | 10 | 004:09 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | C21121800004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 249 | 2021-12-18 | 2490 | keep | 0 | Dec | 2021 | 0.0016959 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-12-18 06:52 | 2021-12-18 06:53 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21121800000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-18 | 3041 | keep | 0 | Dec | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2021-12-18 06:54 | 2021-12-18 06:55 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21121800007 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-18 | 3041 | keep | 0 | Dec | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
SAN JUAN | 2021-12-18 07:08 | 2021-12-18 07:10 | 500 | 000:02 | P | DESCONECTIVO DEFECTUOSO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 20% POR 1118-10 | S21121800000 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2021-12-18 | 1000 | keep | 0 | Dec | 2021 | 0.0006811 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2021-12-18 07:08 | 2021-12-18 07:10 | 2782 | 000:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 20% 1111-1 | S21121800000 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2021-12-18 | 5564 | keep | 0 | Dec | 2021 | 0.0037896 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
MAYAGÃœEZ | 2021-12-18 07:12 | 2021-12-18 16:45 | 40 | 009:33 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSOS | M21121800009 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 573 | 2021-12-18 | 22920 | keep | 0 | Dec | 2021 | 0.015611 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-12-18 07:13 | 2021-12-18 07:18 | 820 | 000:05 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO 1303-02 Y SE CERRO A PETICION F.FEBRES 100% EN SERVICIO 1303-2 Y 20% 1204-2 | S21121800060 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 5 | 2021-12-18 | 4100 | keep | 0 | Dec | 2021 | 0.0027925 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-18 07:13 | 2021-12-18 07:18 | 2435 | 000:05 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO SE CERRO A PETICION F.FEBRES 100% EN SERVICIO 1303-2 Y 20% 1204-2 | S21121800060 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 5 | 2021-12-18 | 12175 | keep | 0 | Dec | 2021 | 0.0082923 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-12-18 07:22 | 2021-12-18 10:22 | 1 | 003:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 15 EN BANCO DE XMR CRUCE POR AVE | C21121800005 | New_Event |  |  | Include | Wildlife | 180 | 2021-12-18 | 180 | keep | 0 | Dec | 2021 | 0.0001226 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-18 07:29 | 2021-12-18 07:30 | 1417 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21121800010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-18 | 1417 | keep | 0 | Dec | 2021 | 0.00096511 | 0.00096511 | Momentary | FALSE | FALSE | Not_TMED_Event | 1417
SAN JUAN | 2021-12-18 07:32 | 2021-12-18 08:07 | 820 | 000:35 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO SE ABRIO MACHETE CALLE VICTOR LABIOSA 50% EN SERVICIO Y 20% 1204-02 | S21121800060 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 35 | 2021-12-18 | 28700 | keep | 0 | Dec | 2021 | 0.019547 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-18 07:32 | 2021-12-18 08:07 | 2435 | 000:35 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO SE ABRIO MACHETE CALLE VICTOR LABIOSA 50% EN SERVICIO Y 20% 1204-02 | S21121800060 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 35 | 2021-12-18 | 85225 | keep | 0 | Dec | 2021 | 0.058046 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-18 07:45 | 2021-12-18 07:46 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1206-03 LLEVANDO LA CARGA DEL 1204-05 | S21121800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-18 | 10211 | keep | 0 | Dec | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-12-18 07:45 | 2021-12-18 07:46 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1206-03 LLEVANDO LA CARGA DEL 1204-05 | S21121800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-18 | 4133 | keep | 0 | Dec | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
FAJARDO | 2021-12-18 07:48 | 2021-12-18 07:49 | 970 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R21121800025 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-18 | 970 | keep | 0 | Dec | 2021 | 0.00066066 | 0.00066066 | Momentary | FALSE | FALSE | Not_TMED_Event | 970
CANOVANAS | 2021-12-18 07:48 | 2021-12-18 11:10 | 53 | 003:22 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 SUM 20 DE 40 AMP. Y 1 X 80 EN RISER SE REPARO TERMINACION | R21121800024 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 202 | 2021-12-18 | 10706 | keep | 0 | Dec | 2021 | 0.0072918 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
MAYAGÃœEZ | 2021-12-18 07:54 | 2021-12-18 07:55 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21121800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-18 | 990 | keep | 0 | Dec | 2021 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
CAGUAS | 2021-12-18 08:01 | 2021-12-18 12:05 | 55 | 004:04 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21121800008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 244 | 2021-12-18 | 13420 | keep | 0 | Dec | 2021 | 0.0091403 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
SAN JUAN | 2021-12-18 08:07 | 2021-12-18 09:54 | 1200 | 001:47 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR CALLE ULALIA SAGRADO CORAZON 100% EN SERVICIO | S21121800060 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 107 | 2021-12-18 | 128400 | keep | 0 | Dec | 2021 | 0.087453 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-12-18 08:07 | 2021-12-18 13:47 | 70 | 005:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y VIENTO | M21121800017 | New_Event | Bad Weather | Include | Include | Weather | 340 | 2021-12-18 | 23800 | keep | 0 | Dec | 2021 | 0.01621 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
YAUCO | 2021-12-18 08:20 | 2021-12-18 11:25 | 173 | 003:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | P21121800010 | New_Event |  |  | Include | Wildlife | 185 | 2021-12-18 | 32005 | keep | 0 | Dec | 2021 | 0.021798 | 0.00011783 | Sustained | FALSE | FALSE | Not_TMED_Event | 173
ARECIBO | 2021-12-18 08:24 | 2021-12-18 11:41 | 15 | 003:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR POR FUERTES VIENTOS | A21121800006 | New_Event | Bad Weather | Include | Include | Weather | 197 | 2021-12-18 | 2955 | keep | 0 | Dec | 2021 | 0.0020126 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2021-12-18 08:30 | 2021-12-18 11:15 | 20 | 002:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE INSTALO RIGIDO Y SE FIJO PUENTE | R21121800029 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 165 | 2021-12-18 | 3300 | keep | 0 | Dec | 2021 | 0.0022476 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-18 08:33 | 2021-12-18 14:28 | 12 | 005:55 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO XMR | S21121800147 | New_Event | Vegetation Contact | Include | Include | Vegetation | 355 | 2021-12-18 | 4260 | keep | 0 | Dec | 2021 | 0.0029015 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-12-18 08:50 | 2021-12-18 10:15 | 5 | 001:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA Y SE AJUSTO TAP A AL B QUEDO EN 128 VOLTIOS POR FASE | S21121700026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 85 | 2021-12-18 | 425 | keep | 0 | Dec | 2021 | 0.00028947 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-12-18 09:01 | 2021-12-18 15:30 | 100 | 006:29 | P | DESGANCHE | 2 X 65 EN C/L SE RETIRARON BAMBUAS | S21121800163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 389 | 2021-12-18 | 38900 | keep | 0 | Dec | 2021 | 0.026495 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-12-18 09:02 | 2021-12-18 13:22 | 400 | 004:20 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE Y SE CERRO SU CARGA POR 1118-10 | S21121800174 | New_Event | Switch Failure | Include | Include | Equipment | 260 | 2021-12-18 | 104000 | keep | 0 | Dec | 2021 | 0.070834 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2021-12-18 09:02 | 2021-12-18 10:41 | 2782 | 001:39 | T | DESCONECTIVO DEFECTUOSO | DISPARO SE ABRE MACHETE EDUARDO ESQ. BARTOLOME DE LAS CASAS Y CALLE MEROFF 10% EN SERVICIO Y CARGA FUERA 1111-1 | S21121800174 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 99 | 2021-12-18 | 275418 | keep | 0 | Dec | 2021 | 0.18759 | 0.0018948 | Sustained | FALSE | FALSE | Not_TMED_Event | 2782
CAGUAS | 2021-12-18 09:03 | 2021-12-18 14:46 | 30 | 005:43 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO CAUSA | C21121800016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 343 | 2021-12-18 | 10290 | keep | 0 | Dec | 2021 | 0.0070085 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-18 09:05 | 2021-12-18 12:08 | 31 | 003:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA Y SE LEVANTO LINEA PRIMARIA | S21121800164 | New_Event | Wire Down | Include | Include | Equipment | 183 | 2021-12-18 | 5673 | keep | 0 | Dec | 2021 | 0.0038639 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
ARECIBO | 2021-12-18 09:10 | 2021-12-18 09:11 | 1227 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | A21121800010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-18 | 1227 | keep | 0 | Dec | 2021 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
BAYAMON | 2021-12-18 09:19 | 2021-12-18 19:21 | 12 | 010:02 | P | TRANSFORMADOR AVERIADO | SE REMPLAZARON DOS POSTES PARTIDOS Y UN XMR AVERIADO DE 37.5KVA POR UNO DE IGUAL CAPACIDAD | B21121800000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 602 | 2021-12-18 | 7224 | keep | 0 | Dec | 2021 | 0.0049202 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-12-18 09:38 | 2021-12-18 09:39 | 1222 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2100 | A21121800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-18 | 1222 | keep | 0 | Dec | 2021 | 0.0008323 | 0.0008323 | Momentary | FALSE | FALSE | Not_TMED_Event | 1222
ARECIBO | 2021-12-18 09:38 | 2021-12-18 09:39 | 2756 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2100 | A21121800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-18 | 2756 | keep | 0 | Dec | 2021 | 0.0018771 | 0.0018771 | Momentary | FALSE | FALSE | Not_TMED_Event | 2756
ARECIBO | 2021-12-18 09:38 | 2021-12-18 09:39 | 2833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2100 | A21121800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-18 | 2833 | keep | 0 | Dec | 2021 | 0.0019295 | 0.0019295 | Momentary | FALSE | FALSE | Not_TMED_Event | 2833
ARECIBO | 2021-12-18 09:38 | 2021-12-18 09:39 | 1218 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2100 | A21121800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-18 | 1218 | keep | 0 | Dec | 2021 | 0.00082957 | 0.00082957 | Momentary | FALSE | FALSE | Not_TMED_Event | 1218
ARECIBO | 2021-12-18 09:38 | 2021-12-18 09:39 | 509 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2100 | A21121800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-18 | 509 | keep | 0 | Dec | 2021 | 0.00034668 | 0.00034668 | Momentary | FALSE | FALSE | Not_TMED_Event | 509
ARECIBO | 2021-12-18 09:38 | 2021-12-18 09:39 | 2620 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2100 | A21121800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-18 | 2620 | keep | 0 | Dec | 2021 | 0.0017845 | 0.0017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 2620
ARECIBO | 2021-12-18 09:38 | 2021-12-18 09:39 | 1916 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2100 | A21121800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-18 | 1916 | keep | 0 | Dec | 2021 | 0.001305 | 0.001305 | Momentary | FALSE | FALSE | Not_TMED_Event | 1916
BARRANQUITAS | 2021-12-18 09:42 | 2021-12-18 17:29 | 60 | 007:47 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21121800017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 467 | 2021-12-18 | 28020 | keep | 0 | Dec | 2021 | 0.019084 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2021-12-18 10:02 | 2021-12-18 15:57 | 15 | 005:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21121800026 | New_Event | Bad Weather | Include | Include | Weather | 355 | 2021-12-18 | 5325 | keep | 0 | Dec | 2021 | 0.0036268 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-12-18 10:06 | 2021-12-18 12:35 | 40 | 002:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA SE RETIRO AVE | B21121800021 | New_Event |  |  | Include | Wildlife | 149 | 2021-12-18 | 5960 | keep | 0 | Dec | 2021 | 0.0040593 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-12-18 10:10 | 2021-12-18 12:12 | 6 | 002:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21121800039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 122 | 2021-12-18 | 732 | keep | 0 | Dec | 2021 | 0.00049856 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-12-18 10:19 | 2021-12-18 10:20 | 6481 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21121800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-18 | 6481 | keep | 0 | Dec | 2021 | 0.0044142 | 0.0044142 | Momentary | FALSE | FALSE | Not_TMED_Event | 6481
SAN JUAN | 2021-12-18 10:19 | 2021-12-18 11:55 | 6244 | 001:36 | T | DESGANCHE | DISPARO DE INTERRUPTOR. SE SECCIONALIZO AVERIA ARBOL SOBRE LAS LINEAS Y ENTRA UN 60% | S21121800222 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2021-12-18 | 599424 | keep | 0 | Dec | 2021 | 0.40826 | 0.0042528 | Sustained | FALSE | FALSE | Not_TMED_Event | 6244
BAYAMON | 2021-12-18 10:20 | 2021-12-18 12:48 | 12 | 002:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | S21121700053 | New_Event | Secondary Wire Down | Include | Include | Equipment | 148 | 2021-12-18 | 1776 | keep | 0 | Dec | 2021 | 0.0012096 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-12-18 10:26 | 2021-12-18 12:42 | 40 | 002:16 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21121800024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2021-12-18 | 5440 | keep | 0 | Dec | 2021 | 0.0037052 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-12-18 10:30 | 2021-12-18 14:52 | 23 | 004:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN TRANSFORMADOR MAL TIEMPO | A21121800036 | New_Event | Bad Weather | Include | Include | Weather | 262 | 2021-12-18 | 6026 | keep | 0 | Dec | 2021 | 0.0041043 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
SAN JUAN | 2021-12-18 10:41 | 2021-12-18 10:45 | 1350 | 000:04 | P | DESCONECTIVO DEFECTUOSO | SE CERRO EDUARDO CONDE ESQ. MORELL CAMPOS 50% EN SERVICIO CONTINUA FUERA 20% 1111-1 | S21121800174 | New_Event | Switch Failure | Include | Include | Equipment | 4 | 2021-12-18 | 5400 | keep | 0 | Dec | 2021 | 0.0036779 | 0.00091948 | Momentary | FALSE | FALSE | Not_TMED_Event | 1350
ARECIBO | 2021-12-18 10:41 | 2021-12-18 17:48 | 1222 | 007:07 | S | PARARRAYOS DEFECTUOSO | SE RETIRO CARGA DE LA SUBESTACION POR FUSIBLE FUNDIDO EN LA FASE B DE LA ALTA DEL TRANSFORMADOR SE REMPLAZO PARARRAYOS EN LA BARRA DE LA SUBESTACION, SE REMPLAZO EL FUSIBLE FUNDIDO EN LA ALTA DEL TRANSFORMADOR Y SE RESTABLECIO LA CARGA DE LA SUBESTACION | A21121800040 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 427 | 2021-12-18 | 521794 | keep | 0 | Dec | 2021 | 0.35539 | 0.0008323 | Sustained | FALSE | FALSE | Not_TMED_Event | 1222
ARECIBO | 2021-12-18 10:41 | 2021-12-18 17:48 | 2756 | 007:07 | S | PARARRAYOS DEFECTUOSO | SE RETIRO CARGA DE LA SUBESTACION POR FUSIBLE FUNDIDO EN LA FASE B DE LA ALTA DEL TRANSFORMADOR SE REMPLAZO PARARRAYOS EN LA BARRA DE LA SUBESTACION, SE REMPLAZO EL FUSIBLE FUNDIDO EN LA ALTA DEL TRANSFORMADOR Y SE RESTABLECIO LA CARGA DE LA SUBESTACION | A21121800040 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 427 | 2021-12-18 | 1176812 | keep | 0 | Dec | 2021 | 0.80152 | 0.0018771 | Sustained | FALSE | FALSE | Not_TMED_Event | 2756
ARECIBO | 2021-12-18 10:41 | 2021-12-18 17:48 | 2833 | 007:07 | S | PARARRAYOS DEFECTUOSO | SE RETIRO CARGA DE LA SUBESTACION POR FUSIBLE FUNDIDO EN LA FASE B DE LA ALTA DEL TRANSFORMADOR SE REMPLAZO PARARRAYOS EN LA BARRA DE LA SUBESTACION, SE REMPLAZO EL FUSIBLE FUNDIDO EN LA ALTA DEL TRANSFORMADOR Y SE RESTABLECIO LA CARGA DE LA SUBESTACION | A21121800040 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 427 | 2021-12-18 | 1209691 | keep | 0 | Dec | 2021 | 0.82392 | 0.0019295 | Sustained | FALSE | FALSE | Not_TMED_Event | 2833
SAN JUAN | 2021-12-18 10:45 | 2021-12-18 13:22 | 1350 | 002:37 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE 100% EN SERVICIO Y 20% DEL 1111-1 | S21121800174 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 157 | 2021-12-18 | 211950 | keep | 0 | Dec | 2021 | 0.14436 | 0.00091948 | Sustained | FALSE | FALSE | Not_TMED_Event | 1350
BAYAMON | 2021-12-18 10:46 | 2021-12-18 11:09 | 12 | 000:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21121800012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 23 | 2021-12-18 | 276 | keep | 0 | Dec | 2021 | 0.00018798 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2021-12-18 10:59 | 2021-12-18 15:40 | 36 | 004:41 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | B21121800026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 281 | 2021-12-18 | 10116 | keep | 0 | Dec | 2021 | 0.00689 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
HUMACAO | 2021-12-18 11:00 | 2021-12-18 11:54 | 11 | 000:54 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | C21121800031 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 54 | 2021-12-18 | 594 | keep | 0 | Dec | 2021 | 0.00040457 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2021-12-18 11:00 | 2021-12-18 15:34 | 60 | 004:34 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR | C21121800032 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 274 | 2021-12-18 | 16440 | keep | 0 | Dec | 2021 | 0.011197 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2021-12-18 11:02 | 2021-12-18 13:31 | 976 | 002:29 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO EN TRONCAL DEL ALIMENTADOR | M21121800013 | New_Event | Wire Down | Include | Include | Equipment | 149 | 2021-12-18 | 145424 | keep | 0 | Dec | 2021 | 0.099048 | 0.00066475 | Sustained | FALSE | FALSE | Not_TMED_Event | 976
BAYAMON | 2021-12-18 11:07 | 2021-12-18 16:00 | 35 | 004:53 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21121800027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 293 | 2021-12-18 | 10255 | keep | 0 | Dec | 2021 | 0.0069846 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2021-12-18 11:07 | 2021-12-18 14:53 | 50 | 003:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR SE RETIRO AVE | C21121800034 | New_Event |  |  | Include | Wildlife | 226 | 2021-12-18 | 11300 | keep | 0 | Dec | 2021 | 0.0076964 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-12-18 11:07 | 2021-12-18 19:07 | 30 | 008:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE LEVANTO CONDUCTOR | C21121800033 | New_Event | Wire Down | Include | Include | Equipment | 480 | 2021-12-18 | 14400 | keep | 0 | Dec | 2021 | 0.0098078 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2021-12-18 11:26 | 2021-12-18 15:08 | 80 | 003:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | R21121800058 | New_Event | Bad Weather | Include | Include | Weather | 222 | 2021-12-18 | 17760 | keep | 0 | Dec | 2021 | 0.012096 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2021-12-18 11:28 | 2021-12-18 15:05 | 66 | 003:37 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P21121800027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2021-12-18 | 14322 | keep | 0 | Dec | 2021 | 0.0097546 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
VEGA BAJA | 2021-12-18 11:32 | 2021-12-18 15:51 | 6 | 004:19 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B21121800031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 259 | 2021-12-18 | 1554 | keep | 0 | Dec | 2021 | 0.0010584 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2021-12-18 11:48 | 2021-12-18 13:40 | 201 | 001:52 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P21121800033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2021-12-18 | 22512 | keep | 0 | Dec | 2021 | 0.015333 | 0.0001369 | Sustained | FALSE | FALSE | Not_TMED_Event | 201
SAN JUAN | 2021-12-18 11:55 | 2021-12-18 12:55 | 3746 | 001:00 | P | DESGANCHE | SE RETIRO ARBOL Y SE CERRO 100% EN SERVICIO | S21121800222 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 60 | 2021-12-18 | 224760 | keep | 0 | Dec | 2021 | 0.15308 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-12-18 12:03 | 2021-12-18 17:30 | 50 | 005:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO BAJANTE CRUZANDO LAS LINEAS | M21121800062 | New_Event | Wire Down | Include | Include | Equipment | 327 | 2021-12-18 | 16350 | keep | 0 | Dec | 2021 | 0.011136 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-12-18 12:15 | 2021-12-18 16:37 | 60 | 004:22 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHO Y LEVANTO CONDUCTOR | C21121800043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 262 | 2021-12-18 | 15720 | keep | 0 | Dec | 2021 | 0.010707 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-12-18 12:15 | 2021-12-18 14:09 | 1 | 001:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN RISER AVE CRUZO FASE A TIERRA | M21121800072 | New_Event |  |  | Include | Wildlife | 114 | 2021-12-18 | 114 | keep | 0 | Dec | 2021 | 7.7645e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-12-18 12:32 | 2021-12-18 17:16 | 29 | 004:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 30 EN CORTE DE LINEA SE RETEZO LINEA | R21121800051 | New_Event | Wire Down | Include | Include | Equipment | 284 | 2021-12-18 | 8236 | keep | 0 | Dec | 2021 | 0.0056095 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
HUMACAO | 2021-12-18 12:34 | 2021-12-18 17:21 | 40 | 004:47 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C21121800051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 287 | 2021-12-18 | 11480 | keep | 0 | Dec | 2021 | 0.007819 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-12-18 12:37 | 2021-12-18 15:40 | 200 | 003:03 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | C21121800052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 183 | 2021-12-18 | 36600 | keep | 0 | Dec | 2021 | 0.024928 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2021-12-18 12:38 | 2021-12-19 13:06 | 10 | 024:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR REMPLAZO CAJA | C21121800053 | New_Event | Cutout Failure | Include | Include | Equipment | 1468 | 2021-12-18 | 14680 | keep | 0 | Dec | 2021 | 0.0099985 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-18 12:46 | 2021-12-18 18:35 | 5 | 005:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO EN PEDESTAL | S21121800312 | New_Event | Secondary Wire Down | Include | Include | Equipment | 349 | 2021-12-18 | 1745 | keep | 0 | Dec | 2021 | 0.0011885 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-12-18 12:52 | 2021-12-18 17:20 | 500 | 004:28 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M21121800084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2021-12-18 | 134000 | keep | 0 | Dec | 2021 | 0.091267 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2021-12-18 12:56 | 2021-12-18 12:57 | 1834 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21121800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-18 | 1834 | keep | 0 | Dec | 2021 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
ARECIBO | 2021-12-18 13:04 | 2021-12-18 18:18 | 300 | 005:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A21121800071 | New_Event | Cutout Failure | Include | Include | Equipment | 314 | 2021-12-18 | 94200 | keep | 0 | Dec | 2021 | 0.064159 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
PONCE | 2021-12-18 13:05 | 2021-12-18 13:06 | 1730 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21121800039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-18 | 1730 | keep | 0 | Dec | 2021 | 0.0011783 | 0.0011783 | Momentary | FALSE | FALSE | Not_TMED_Event | 1730
FAJARDO | 2021-12-18 13:18 | 2021-12-18 13:19 | 970 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R2121800054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-18 | 970 | keep | 0 | Dec | 2021 | 0.00066066 | 0.00066066 | Momentary | FALSE | FALSE | Not_TMED_Event | 970
AGUADILLA | 2021-12-18 13:31 | 2021-12-18 15:05 | 1024 | 001:34 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERUPTOR PARA REPARAR PUENTE ABIERTO EN TRONCAL DEL ALIMENTADOR | M21121800013 | Additional_clients | Wire Down | Include | Include | Equipment | 94 | 2021-12-18 | 96256 | keep | 0 | Dec | 2021 | 0.06556 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-12-18 13:32 | 2021-12-19 10:25 | 150 | 020:53 | P | DESGANCHE | 2 X 100 EN CONVERTIDOR DE VOLTAJE POR DESGANCHE | P21121800040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1253 | 2021-12-18 | 187950 | keep | 0 | Dec | 2021 | 0.12801 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2021-12-18 13:42 | 2021-12-18 18:52 | 65 | 005:10 | P | DESGANCHE | 1 X 100 Y 1 X 50 EN C/L SE REALIZO DESGANCHE | B21121800044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 310 | 2021-12-18 | 20150 | keep | 0 | Dec | 2021 | 0.013724 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2021-12-18 13:48 | 2021-12-18 21:17 | 1 | 007:29 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B21121800046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 449 | 2021-12-18 | 449 | keep | 0 | Dec | 2021 | 0.00030581 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-12-18 13:50 | 2021-12-18 16:08 | 1 | 002:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN RISER Y 1 X 15 EN TRANSFORMADOR SE FIJO BAJANTE AL PIN | R21121800056 | New_Event | Wire Down | Include | Include | Equipment | 138 | 2021-12-18 | 138 | keep | 0 | Dec | 2021 | 9.3991e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-12-18 13:52 | 2021-12-18 14:30 | 1 | 000:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN RISER MAL TIEMPO VIENTOS FUERTES | A21121800079 | New_Event | Bad Weather | Include | Include | Weather | 38 | 2021-12-18 | 38 | keep | 0 | Dec | 2021 | 2.5882e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-12-18 13:58 | 2021-12-18 13:59 | 658 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | P21121800048 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-12-18 | 658 | keep | 0 | Dec | 2021 | 0.00044816 | 0.00044816 | Momentary | FALSE | FALSE | Not_TMED_Event | 658
PONCE | 2021-12-18 13:59 | 2021-12-18 15:30 | 200 | 001:31 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | ALAMBRE PRIMARIO EN EL PISO | P21121800048 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 91 | 2021-12-18 | 18200 | keep | 0 | Dec | 2021 | 0.012396 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2021-12-18 14:00 | 2021-12-18 16:30 | 133 | 002:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21121800047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2021-12-18 | 19950 | keep | 0 | Dec | 2021 | 0.013588 | 9.0586e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 133
CANOVANAS | 2021-12-18 14:01 | 2021-12-18 15:28 | 112 | 001:27 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE Y REEMPLAZARON AISLADOR ROTO | R21121800057 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 87 | 2021-12-18 | 9744 | keep | 0 | Dec | 2021 | 0.0066366 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
UTUADO | 2021-12-18 14:03 | 2021-12-18 17:01 | 30 | 002:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21121800081 | New_Event | Bad Weather | Include | Include | Weather | 178 | 2021-12-18 | 5340 | keep | 0 | Dec | 2021 | 0.003637 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-18 14:04 | 2021-12-18 19:20 | 50 | 005:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN RISER MAL TIEMPO VIENTOS FUERTES | A21121800082 | New_Event | Bad Weather | Include | Include | Weather | 316 | 2021-12-18 | 15800 | keep | 0 | Dec | 2021 | 0.010761 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-12-18 14:12 | 2021-12-18 18:41 | 84 | 004:29 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER Y 1 X 40 EN SU-4 | S21121800327 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 269 | 2021-12-18 | 22596 | keep | 0 | Dec | 2021 | 0.01539 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
SAN JUAN | 2021-12-18 14:16 | 2021-12-18 14:17 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21121800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-18 | 2203 | keep | 0 | Dec | 2021 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
ARECIBO | 2021-12-18 14:18 | 2021-12-18 18:47 | 50 | 004:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21121800084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 269 | 2021-12-18 | 13450 | keep | 0 | Dec | 2021 | 0.0091607 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-18 14:20 | 2021-12-18 15:39 | 290 | 001:19 | T | DESGANCHE | DISPARO DE INTERRUPTOR. SE SECCIONALIZO AVERIA POR DESGANCHE Y SE CERRO POR SCADA | S21121800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2021-12-18 | 22910 | keep | 0 | Dec | 2021 | 0.015604 | 0.00019752 | Sustained | FALSE | FALSE | Not_TMED_Event | 290
BAYAMON | 2021-12-18 14:20 | 2021-12-18 15:38 | 150 | 001:18 | P | DESGANCHE | SE SECCIONALIZO Y SE CERRO POR SCADA CARGA PARCIAL POR EL 1526-03 | S21121800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2021-12-18 | 11700 | keep | 0 | Dec | 2021 | 0.0079688 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2021-12-18 14:24 | 2021-12-18 19:14 | 60 | 004:50 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 Y 1 X 50 EN CORTES DE LINEA SE REEMPLAZARON 2 AISLADORES | R21121800071 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 290 | 2021-12-18 | 17400 | keep | 0 | Dec | 2021 | 0.011851 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-12-18 14:28 | 2021-12-18 15:50 | 100 | 001:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21121800086 | New_Event | Bad Weather | Include | Include | Weather | 82 | 2021-12-18 | 8200 | keep | 0 | Dec | 2021 | 0.005585 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-12-18 14:39 | 2021-12-18 14:53 | 1105 | 000:14 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO INTERRUPTOR CON RECIERRE EN OFF SE VERIFICO PERSONAL FUERA DE LAS LINEA Y SE CERRO EL INTERRUPTOR | A21121800087 | New_Event | Bad Weather | Include | Include | Weather | 14 | 2021-12-18 | 15470 | keep | 0 | Dec | 2021 | 0.010537 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2021-12-18 14:42 | 2021-12-18 15:18 | 40 | 000:36 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 40 EN C/L | B21121800040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 36 | 2021-12-18 | 1440 | keep | 0 | Dec | 2021 | 0.00098078 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-12-18 14:46 | 2021-12-18 15:57 | 50 | 001:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA SE RETIRO AVE | C21121800067 | New_Event |  |  | Include | Wildlife | 71 | 2021-12-18 | 3550 | keep | 0 | Dec | 2021 | 0.0024179 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-12-18 14:50 | 2021-12-19 09:36 | 100 | 018:46 | P | NO SE REPORTO CAUSA | 1 X 140 EN C/L | S21121800336 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1126 | 2021-12-18 | 112600 | keep | 0 | Dec | 2021 | 0.076691 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-12-18 14:53 | 2021-12-18 16:34 | 120 | 001:41 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21121800092 | Partial_restoration | Bad Weather | Include | Include | Weather | 101 | 2021-12-18 | 12120 | keep | 0 | Dec | 2021 | 0.0082549 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-12-18 15:01 | 2021-12-18 17:50 | 60 | 002:49 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA 2 X 50 EN CORTE DE LINEA SE RETIRO RAMA CRUZANDO LINEAS PRIMARIAS | A21121800094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2021-12-18 | 10140 | keep | 0 | Dec | 2021 | 0.0069063 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2021-12-18 15:07 | 2021-12-18 16:25 | 45 | 001:18 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P21121800060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2021-12-18 | 3510 | keep | 0 | Dec | 2021 | 0.0023906 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2021-12-18 15:10 | 2021-12-18 15:11 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1907-03 QUE A SU VEZ LLEVA LA CARGA DEL 1909-09 | S21121800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-18 | 222 | keep | 0 | Dec | 2021 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2021-12-18 15:10 | 2021-12-18 15:11 | 4456 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1907-03 QUE A SU VEZ LLEVA LA CARGA DEL 1909-09 | S21121800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-18 | 4456 | keep | 0 | Dec | 2021 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
FAJARDO | 2021-12-18 15:12 | 2021-12-18 16:13 | 13 | 001:01 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R21121800075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2021-12-18 | 793 | keep | 0 | Dec | 2021 | 0.00054011 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
ARECIBO | 2021-12-18 15:17 | 2021-12-18 18:35 | 60 | 003:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN RISER MAL TIEMPO VIENTOS FUERTES | A21121800098 | New_Event | Bad Weather | Include | Include | Weather | 198 | 2021-12-18 | 11880 | keep | 0 | Dec | 2021 | 0.0080914 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-12-18 15:27 | 2021-12-18 16:35 | 12 | 001:08 | P | NO SE REPORTO CAUSA | 2 X 25 EN XMR | B21121800055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 68 | 2021-12-18 | 816 | keep | 0 | Dec | 2021 | 0.00055577 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-12-18 15:30 | 2021-12-18 16:20 | 658 | 000:50 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE ALIMENTADOR DE EMERGENCIA POR ALAMBRE PRIMARIO EN EL PISO | P21121800073 | Additional_clients | Wire Down | Include | Include | Equipment | 50 | 2021-12-18 | 32900 | keep | 0 | Dec | 2021 | 0.022408 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-12-18 15:31 | 2021-12-18 20:30 | 80 | 004:59 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M21121800121 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 299 | 2021-12-18 | 23920 | keep | 0 | Dec | 2021 | 0.016292 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-12-18 15:39 | 2021-12-18 15:56 | 150 | 000:17 | P | DESGANCHE | SE SECCIONALIZO Y SE CERRARON MACHETES PREVIAMENTE ABIERTO | S21121800000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 17 | 2021-12-18 | 2550 | keep | 0 | Dec | 2021 | 0.0017368 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-12-18 15:43 | 2021-12-18 17:45 | 976 | 002:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARAR PUENTE ABIERTO EN TROCAL DE ALIMENTADOR | M21121800013 | New_Event | Wire Down | Include | Include | Equipment | 122 | 2021-12-18 | 119072 | keep | 0 | Dec | 2021 | 0.081099 | 0.00066475 | Sustained | FALSE | FALSE | Not_TMED_Event | 976
SAN JUAN | 2021-12-18 15:47 | 2021-12-18 18:54 | 15 | 003:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | R21121800078 | New_Event | Bad Weather | Include | Include | Weather | 187 | 2021-12-18 | 2805 | keep | 0 | Dec | 2021 | 0.0019105 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-12-18 15:47 | 2021-12-18 19:25 | 32 | 003:38 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B21121800061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 218 | 2021-12-18 | 6976 | keep | 0 | Dec | 2021 | 0.0047513 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
BAYAMON | 2021-12-18 15:56 | 2021-12-18 18:50 | 50 | 002:54 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRARON MACHETES PREVIAMENTE ABIERTOS | S21121800000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 174 | 2021-12-18 | 8700 | keep | 0 | Dec | 2021 | 0.0059255 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-18 16:00 | 2021-12-18 18:41 | 6 | 002:41 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B21121800064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 161 | 2021-12-18 | 966 | keep | 0 | Dec | 2021 | 0.00065794 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-12-18 16:06 | 2021-12-18 16:08 | 837 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-07 SE CERRO POR SCADA LLEVA CARGA 1401-06 | S21121800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-18 | 1674 | keep | 0 | Dec | 2021 | 0.0011402 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2021-12-18 16:06 | 2021-12-18 16:08 | 908 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-07 SE CERRO POR SCADA LLEVA CARGA 1401-06 | S21121800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-18 | 1816 | keep | 0 | Dec | 2021 | 0.0012369 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
AGUADILLA | 2021-12-18 16:08 | 2021-12-18 17:40 | 15 | 001:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21121800093 | New_Event | Secondary Wire Down | Include | Include | Equipment | 92 | 2021-12-18 | 1380 | keep | 0 | Dec | 2021 | 0.00093991 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2021-12-18 16:09 | 2021-12-18 17:49 | 2635 | 001:40 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE RETIRO GLOBO EN LA SALIDA DEL ALIMENTADOR | C21121800000 | New_Event |  |  | Include | Wildlife | 100 | 2021-12-18 | 263500 | keep | 0 | Dec | 2021 | 0.17947 | 0.0017947 | Sustained | FALSE | FALSE | Not_TMED_Event | 2635
AGUADILLA | 2021-12-18 16:16 | 2021-12-19 16:35 | 200 | 024:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA IGUANA CRUZO LINEAS | M21121800137 | New_Event |  |  | Include | Wildlife | 1459 | 2021-12-18 | 291800 | keep | 0 | Dec | 2021 | 0.19874 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2021-12-18 16:20 | 2021-12-20 18:00 | 1 | 049:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA EN EL PISO Y SE CERRO PUENTE VERIFICADO EVENTO EN OMS | P21121800098 | Partial_restoration | Wire Down | Include | Include | Equipment | 2980 | 2021-12-18 | 2980 | keep | 0 | Dec | 2021 | 0.0020297 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-12-18 16:30 | 2021-12-19 14:36 | 15 | 022:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | M21121800139 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1326 | 2021-12-18 | 19890 | keep | 0 | Dec | 2021 | 0.013547 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2021-12-18 16:33 | 2021-12-18 18:00 | 58 | 001:27 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21121800078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2021-12-18 | 5046 | keep | 0 | Dec | 2021 | 0.0034368 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
FAJARDO | 2021-12-18 16:43 | 2021-12-18 19:18 | 13 | 002:35 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21121800082 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 155 | 2021-12-18 | 2015 | keep | 0 | Dec | 2021 | 0.0013724 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-18 16:44 | 2021-12-18 21:46 | 60 | 005:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO PORTAFUSIBLES | B21121800074 | New_Event | Cutout Failure | Include | Include | Equipment | 302 | 2021-12-18 | 18120 | keep | 0 | Dec | 2021 | 0.012341 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2021-12-18 16:51 | 2021-12-18 17:22 | 60 | 000:31 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21121800080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 31 | 2021-12-18 | 1860 | keep | 0 | Dec | 2021 | 0.0012668 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2021-12-18 16:55 | 2021-12-19 00:49 | 25 | 007:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA RAMAL | B21121800075 | New_Event | Wire Down | Include | Include | Equipment | 474 | 2021-12-18 | 11850 | keep | 0 | Dec | 2021 | 0.008071 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-12-18 17:19 | 2021-12-19 12:10 | 30 | 018:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE | M21121800149 | New_Event | Wire Down | Include | Include | Equipment | 1131 | 2021-12-18 | 33930 | keep | 0 | Dec | 2021 | 0.02311 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-12-18 17:30 | 2021-12-19 13:27 | 30 | 019:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR FUERTES VIENTOS | M21121800152 | New_Event | Bad Weather | Include | Include | Weather | 1197 | 2021-12-18 | 35910 | keep | 0 | Dec | 2021 | 0.024458 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-12-18 17:33 | 2021-12-18 17:34 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | C21121800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-18 | 2354 | keep | 0 | Dec | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
AGUADILLA | 2021-12-18 17:45 | 2021-12-18 17:46 | 1024 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DEL INTERRUPTOR PUENTE ABIERTO EN TRONCAL | M21121800000 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2021-12-18 | 1024 | keep | 0 | Dec | 2021 | 0.00069744 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-12-18 17:46 | 2021-12-18 17:56 | 976 | 000:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES PARA REPARAR PUENTE ABIERTO | M21121800123 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 10 | 2021-12-18 | 9760 | keep | 0 | Dec | 2021 | 0.0066475 | 0.00066475 | Sustained | FALSE | FALSE | Not_TMED_Event | 976
AGUADILLA | 2021-12-18 17:56 | 2021-12-19 09:07 | 1024 | 015:11 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO AVERIA DE AISLADORES PARTIDOS Y SE CERRO INTERRUPTOR | M21121800123 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 911 | 2021-12-18 | 932864 | keep | 0 | Dec | 2021 | 0.63537 | 0.00069744 | Sustained | FALSE | FALSE | Not_TMED_Event | 1024
CAGUAS | 2021-12-18 18:00 | 2021-12-19 11:58 | 50 | 017:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE LINEA A CAJA PRIMARIA | C21121800119 | New_Event | Wire Down | Include | Include | Equipment | 1078 | 2021-12-18 | 53900 | keep | 0 | Dec | 2021 | 0.036711 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-12-18 18:19 | 2021-12-18 20:16 | 50 | 001:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | R21121800087 | New_Event | Bad Weather | Include | Include | Weather | 117 | 2021-12-18 | 5850 | keep | 0 | Dec | 2021 | 0.0039844 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-18 19:08 | 2021-12-18 20:21 | 6 | 001:13 | P | DESGANCHE | 1 X 15 EN XMR SE RETIRO ENREDADERA | B21121800091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2021-12-18 | 438 | keep | 0 | Dec | 2021 | 0.00029832 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2021-12-18 19:44 | 2021-12-18 20:32 | 1943 | 000:48 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO NEUTRAL EN TRONCAL DEL ALIMENTADOR | M21121800000 | New_Event | Wire Down | Include | Include | Equipment | 48 | 2021-12-18 | 93264 | keep | 0 | Dec | 2021 | 0.063522 | 0.0013234 | Sustained | FALSE | FALSE | Not_TMED_Event | 1943
CAGUAS | 2021-12-18 20:05 | 2021-12-19 12:06 | 80 | 016:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE | C21121800138 | New_Event | Wire Down | Include | Include | Equipment | 961 | 2021-12-18 | 76880 | keep | 0 | Dec | 2021 | 0.052363 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2021-12-18 20:33 | 2021-12-19 15:05 | 20 | 018:32 | P | DESGANCHE | 1 X 20 EN C/L | C21121800140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1112 | 2021-12-18 | 22240 | keep | 0 | Dec | 2021 | 0.015148 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2021-12-18 20:38 | 2021-12-18 21:45 | 197 | 001:07 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 65 EN DISTINTOS CORTES DE LINEA NO SE ENCONTRO CAUSA | P21121800112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 67 | 2021-12-18 | 13199 | keep | 0 | Dec | 2021 | 0.0089898 | 0.00013418 | Sustained | FALSE | FALSE | Not_TMED_Event | 197
ARECIBO | 2021-12-18 20:40 | 2021-12-19 | 50 | 003:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA Y VIENTO | A21121800129 | New_Event | Bad Weather | Include | Include | Weather | 200 | 2021-12-18 | 10000 | keep | 0 | Dec | 2021 | 0.006811 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-12-18 20:47 | 2021-12-19 12:49 | 15 | 016:02 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R21121800094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 962 | 2021-12-18 | 14430 | keep | 0 | Dec | 2021 | 0.0098282 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-12-18 21:20 | 2021-12-19 11:12 | 9 | 013:52 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | C21121800141 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 832 | 2021-12-18 | 7488 | keep | 0 | Dec | 2021 | 0.0051 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
HUMACAO | 2021-12-18 21:38 | 2021-12-19 11:12 | 55 | 013:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE LINEA A CAJA PRIMARIA | C21121800145 | New_Event | Wire Down | Include | Include | Equipment | 814 | 2021-12-18 | 44770 | keep | 0 | Dec | 2021 | 0.030493 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
BAYAMON | 2021-12-18 22:49 | 2021-12-19 10:50 | 50 | 012:01 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE DE BAMBUAS | B21121800099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 721 | 2021-12-18 | 36050 | keep | 0 | Dec | 2021 | 0.024553 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-12-18 23:04 | 2021-12-19 10:15 | 250 | 011:11 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 100 EN C/L, 2 X 100 EN C/L, 2 X 80 EN C/L Y SE DEJO ABIERTO DE SU-2 @ SU-3 POR AVERIA EN TERMINACIONES DEL SU-3 | S21121800336 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 671 | 2021-12-18 | 167750 | keep | 0 | Dec | 2021 | 0.11425 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2021-12-18 23:20 | 2021-12-19 11:10 | 50 | 011:50 | P | NO SE REPORTO CAUSA | 1 X 40 EN PROVISIONAL AEREO | B21121800100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 710 | 2021-12-18 | 35500 | keep | 0 | Dec | 2021 | 0.024179 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-12-19 00:01 | 2021-12-19 09:32 | 20 | 009:31 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | R21121900001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 571 | 2021-12-19 | 11420 | keep | 0 | Dec | 2021 | 0.0077781 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-12-19 00:12 | 2021-12-19 06:37 | 3785 | 006:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | SECCIONALIZARON POSTE IMPACTADO POR AUTO Y CERRO INTELLIRUPTER 2603-8D | C21121900008 | New_Event |  |  | Include | Wildlife | 385 | 2021-12-19 | 1457225 | keep | 0 | Dec | 2021 | 0.99251 | 0.0025779 | Sustained | FALSE | FALSE | Not_TMED_Event | 3785
HUMACAO | 2021-12-19 00:12 | 2021-12-19 01:46 | 676 | 001:34 | S | ANIMAL U OBJETO EXTRAÃ‘O | POSTE DE LA LINEA 5300 PARTIDO POR IMPACTO DE AUTO | C21121900000 | New_Event |  |  | Include | Wildlife | 94 | 2021-12-19 | 63544 | keep | 0 | Dec | 2021 | 0.04328 | 0.00046042 | Sustained | FALSE | FALSE | Not_TMED_Event | 676
HUMACAO | 2021-12-19 00:12 | 2021-12-19 01:46 | 2873 | 001:34 | S | ANIMAL U OBJETO EXTRAÃ‘O | POSTE DE LA LINEA 5300 PARTIDO POR IMPACTO DE AUTO | C21121900000 | New_Event |  |  | Include | Wildlife | 94 | 2021-12-19 | 270062 | keep | 0 | Dec | 2021 | 0.18394 | 0.0019568 | Sustained | FALSE | FALSE | Not_TMED_Event | 2873
HUMACAO | 2021-12-19 00:12 | 2021-12-19 01:46 | 3902 | 001:34 | S | ANIMAL U OBJETO EXTRAÃ‘O | POSTE DE LA LINEA 5300 PARTIDO POR IMPACTO DE AUTO | C21121900000 | New_Event |  |  | Include | Wildlife | 94 | 2021-12-19 | 366788 | keep | 0 | Dec | 2021 | 0.24982 | 0.0026576 | Sustained | FALSE | FALSE | Not_TMED_Event | 3902
SAN JUAN | 2021-12-19 00:20 | 2021-12-19 02:15 | 10 | 001:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | S21121900002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 115 | 2021-12-19 | 1150 | keep | 0 | Dec | 2021 | 0.00078326 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-19 00:20 | 2021-12-19 00:21 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21121900001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-19 | 108 | keep | 0 | Dec | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
MAYAGÃœEZ | 2021-12-19 00:24 | 2021-12-19 00:25 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21121900002 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-19 | 108 | keep | 0 | Dec | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
UTUADO | 2021-12-19 02:01 | 2021-12-19 08:50 | 30 | 006:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA LLUVIA Y VIENTO | A21121900001 | New_Event | Bad Weather | Include | Include | Weather | 409 | 2021-12-19 | 12270 | keep | 0 | Dec | 2021 | 0.008357 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-12-19 02:15 | 2021-12-19 02:16 | 485 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1404-09 QUE A SU VEZ LLEVA LA CARGA DEL 1420-05 | S21121900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-19 | 485 | keep | 0 | Dec | 2021 | 0.00033033 | 0.00033033 | Momentary | FALSE | FALSE | Not_TMED_Event | 485
SAN JUAN | 2021-12-19 02:15 | 2021-12-19 02:16 | 4 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1404-09 QUE A SU VEZ LLEVA LA CARGA DEL 1420-05 | S21121900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-19 | 4 | keep | 0 | Dec | 2021 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-12-19 02:16 | 2021-12-19 10:31 | 10 | 008:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | S21121900002 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 495 | 2021-12-19 | 4950 | keep | 0 | Dec | 2021 | 0.0033714 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-19 03:05 | 2021-12-19 05:02 | 112 | 001:57 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ELIMINO PUENTE SAFADO DE PARARRAYO CRUZANDO LA LINEA PRIMARIA | B21121900002 | New_Event | Wire Down | Include | Include | Equipment | 117 | 2021-12-19 | 13104 | keep | 0 | Dec | 2021 | 0.0089251 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
BAYAMON | 2021-12-19 03:27 | 2021-12-19 03:28 | 2324 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21121900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-19 | 2324 | keep | 0 | Dec | 2021 | 0.0015829 | 0.0015829 | Momentary | FALSE | FALSE | Not_TMED_Event | 2324
CAGUAS | 2021-12-19 03:45 | 2021-12-19 21:12 | 216 | 017:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | SECCIONALIZO POSTE DE TRANSMISION PARTIDO POR VEHICULO LINEA 5300 | C21121900110 | New_Event |  |  | Include | Wildlife | 1047 | 2021-12-19 | 226152 | keep | 0 | Dec | 2021 | 0.15403 | 0.00014712 | Sustained | FALSE | FALSE | Not_TMED_Event | 216
VEGA BAJA | 2021-12-19 03:45 | 2021-12-19 16:39 | 48 | 012:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | B21121900006 | New_Event | Wire Down | Include | Include | Equipment | 774 | 2021-12-19 | 37152 | keep | 0 | Dec | 2021 | 0.025304 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
CANOVANAS | 2021-12-19 06:01 | 2021-12-19 09:17 | 25 | 003:16 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | R21121900004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 196 | 2021-12-19 | 4900 | keep | 0 | Dec | 2021 | 0.0033374 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2021-12-19 06:09 | 2021-12-19 06:10 | 725 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21121900106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-19 | 725 | keep | 0 | Dec | 2021 | 0.00049379 | 0.00049379 | Momentary | FALSE | FALSE | Not_TMED_Event | 725
AGUADILLA | 2021-12-19 06:28 | 2021-12-19 06:29 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21121900011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-19 | 1827 | keep | 0 | Dec | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
ARECIBO | 2021-12-19 06:37 | 2021-12-19 09:50 | 5 | 003:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | A21121900002 | New_Event | Cutout Failure | Include | Include | Equipment | 193 | 2021-12-19 | 965 | keep | 0 | Dec | 2021 | 0.00065726 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2021-12-19 06:39 | 2021-12-19 06:40 | 2926 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21121900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-19 | 2926 | keep | 0 | Dec | 2021 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
MAYAGÃœEZ | 2021-12-19 06:58 | 2021-12-19 16:02 | 2 | 009:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M21121900012 | New_Event | Bad Weather | Include | Include | Weather | 544 | 2021-12-19 | 1088 | keep | 0 | Dec | 2021 | 0.00074103 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2021-12-19 07:17 | 2021-12-19 11:18 | 50 | 004:01 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S21121900021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 241 | 2021-12-19 | 12050 | keep | 0 | Dec | 2021 | 0.0082072 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-12-19 07:33 | 2021-12-19 12:15 | 100 | 004:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR FUERTES VIENTOS | M21121900013 | New_Event | Bad Weather | Include | Include | Weather | 282 | 2021-12-19 | 28200 | keep | 0 | Dec | 2021 | 0.019207 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2021-12-19 07:38 | 2021-12-19 10:20 | 30 | 002:42 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | R21121900005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2021-12-19 | 4860 | keep | 0 | Dec | 2021 | 0.0033101 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-19 07:58 | 2021-12-19 12:30 | 50 | 004:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | A21121900004 | New_Event | Wire Down | Include | Include | Equipment | 272 | 2021-12-19 | 13600 | keep | 0 | Dec | 2021 | 0.0092629 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-12-19 08:03 | 2021-12-19 14:16 | 25 | 006:13 | P | DESGANCHE | 1 X 40 EN C/L | R21121900006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 373 | 2021-12-19 | 9325 | keep | 0 | Dec | 2021 | 0.0063512 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-12-19 08:16 | 2021-12-19 08:17 | 17 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S21121900029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-19 | 17 | keep | 0 | Dec | 2021 | 1.1579e-05 | 1.1579e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 17
SAN JUAN | 2021-12-19 08:20 | 2021-12-19 10:15 | 80 | 001:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L. SE RETIRO AVE | S21121900030 | New_Event |  |  | Include | Wildlife | 115 | 2021-12-19 | 9200 | keep | 0 | Dec | 2021 | 0.0062661 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2021-12-19 08:38 | 2021-12-19 08:39 | 1879 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA | C21121900110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-19 | 1879 | keep | 0 | Dec | 2021 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
SAN JUAN | 2021-12-19 08:41 | 2021-12-19 11:29 | 50 | 002:48 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU-15 | R21121900011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 168 | 2021-12-19 | 8400 | keep | 0 | Dec | 2021 | 0.0057212 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-12-19 08:58 | 2021-12-19 11:50 | 80 | 002:52 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L Y 1 X 40 EN RISER A SU-1 | R21121900014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 172 | 2021-12-19 | 13760 | keep | 0 | Dec | 2021 | 0.0093719 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-12-19 08:59 | 2021-12-19 17:10 | 40 | 008:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | M21121900030 | New_Event | Wire Down | Include | Include | Equipment | 491 | 2021-12-19 | 19640 | keep | 0 | Dec | 2021 | 0.013377 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-12-19 08:59 | 2021-12-19 16:41 | 7 | 007:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DE AISLADOR | M21121900023 | New_Event | Wire Down | Include | Include | Equipment | 462 | 2021-12-19 | 3234 | keep | 0 | Dec | 2021 | 0.0022027 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2021-12-19 09:00 | 2021-12-20 10:16 | 6 | 025:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | R21121900016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1516 | 2021-12-19 | 9096 | keep | 0 | Dec | 2021 | 0.0061952 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-12-19 09:02 | 2021-12-19 10:02 | 1812 | 001:00 | T | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO ALIMENTADOR 10% EN SERVICIO | B21121900010 | New_Event | Switch Failure | Include | Include | Equipment | 60 | 2021-12-19 | 108720 | keep | 0 | Dec | 2021 | 0.074049 | 0.0012341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1812
SAN JUAN | 2021-12-19 09:03 | 2021-12-19 10:15 | 50 | 001:12 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S21121900037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 72 | 2021-12-19 | 3600 | keep | 0 | Dec | 2021 | 0.0024519 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-12-19 09:07 | 2021-12-19 12:35 | 1000 | 003:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADORES PARTIDOS Y SE CERRO MACHETES | M21121900028 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 208 | 2021-12-19 | 208000 | keep | 0 | Dec | 2021 | 0.14167 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-12-19 09:10 | 2021-12-19 10:09 | 15 | 000:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21121800130 | New_Event | Secondary Wire Down | Include | Include | Equipment | 59 | 2021-12-19 | 885 | keep | 0 | Dec | 2021 | 0.00060277 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-12-19 09:13 | 2021-12-19 09:14 | 1983 | 000:01 | T | NO SE REPORTO CAUSA | CARGA TRANSFERIDA AL 1801-02 | B21121900011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-19 | 1983 | keep | 0 | Dec | 2021 | 0.0013506 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-12-19 09:13 | 2021-12-19 09:14 | 186 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA LA CARGA DEL 1711-04 | B21121900011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-19 | 186 | keep | 0 | Dec | 2021 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
SAN JUAN | 2021-12-19 09:22 | 2021-12-19 12:09 | 30 | 002:47 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | R21112190001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 167 | 2021-12-19 | 5010 | keep | 0 | Dec | 2021 | 0.0034123 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-12-19 09:41 | 2021-12-19 15:50 | 40 | 006:09 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER NO CAUSA | C21121900134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 369 | 2021-12-19 | 14760 | keep | 0 | Dec | 2021 | 0.010053 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2021-12-19 09:52 | 2021-12-19 09:53 | 1467 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA | C21121900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-19 | 1467 | keep | 0 | Dec | 2021 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
GUAYAMA | 2021-12-19 09:57 | 2021-12-19 09:58 | 1945 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | P21121900031 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-12-19 | 1945 | keep | 0 | Dec | 2021 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
GUAYAMA | 2021-12-19 09:58 | 2021-12-19 12:45 | 75 | 002:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 100 EN CORTE DE LINEA SE REMPLAZARON TRES CAJAS PRIMARIAS EN CORTE DE LINEA | P21121900032 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 167 | 2021-12-19 | 12525 | keep | 0 | Dec | 2021 | 0.0085307 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2021-12-19 09:59 | 2021-12-19 17:33 | 1105 | 007:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN SALIDA DE CONVERTIDOR REMPLAZO CAJA QUEMADA | C21121900141 | New_Event | Cutout Failure | Include | Include | Equipment | 454 | 2021-12-19 | 501670 | keep | 0 | Dec | 2021 | 0.34169 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
SAN JUAN | 2021-12-19 10:01 | 2021-12-19 10:35 | 80 | 000:34 | P | DESGANCHE | 1 X 100 EN C/L. HAY QUE REALIZAR DESGANCHE DE BAMBUAS | S21121900048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 34 | 2021-12-19 | 2720 | keep | 0 | Dec | 2021 | 0.0018526 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-12-19 10:02 | 2021-12-19 12:40 | 1630 | 002:38 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO | B21121900010 | New_Event | Switch Failure | Include | Include | Equipment | 158 | 2021-12-19 | 257540 | keep | 0 | Dec | 2021 | 0.17541 | 0.0011102 | Sustained | FALSE | FALSE | Not_TMED_Event | 1630
MAYAGÃœEZ | 2021-12-19 10:08 | 2021-12-19 14:54 | 10 | 004:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M21121900033 | New_Event | Bad Weather | Include | Include | Weather | 286 | 2021-12-19 | 2860 | keep | 0 | Dec | 2021 | 0.0019479 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-19 10:15 | 2021-12-19 10:20 | 10211 | 000:05 | T | NO SE REPORTO CAUSA | SE ABRIO INTERRUPTOR 1206-03 A PETICION DE JESUS MARRERO POR FUEGO EN CORTE DE LINEA QUE DA SERVICIO A HOSPITAL TRUJILLO ALTO. SE ABRIO C/L Y SE CERRO NUEVAMENTE INTERRUPTOR.CARGA POR EL 1206-03 | S21121900050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-12-19 | 51055 | keep | 0 | Dec | 2021 | 0.034773 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-12-19 10:15 | 2021-12-19 10:20 | 4133 | 000:05 | T | NO SE REPORTO CAUSA | SE ABRIO INTERRUPTOR A PETICION DE JESUS MARRERO POR FUEGO EN CORTE DE LINEA QUE DA SERVICIO A HOSPITAL TRUJILLO ALTO. SE ABRIO C/L Y SE CERRO NUEVAMENTE INTERRUPTOR. LLEVA LA CARGA DEL 1204-05 | S21121900050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-12-19 | 20665 | keep | 0 | Dec | 2021 | 0.014075 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-12-19 10:20 | 2021-12-19 11:36 | 50 | 001:16 | P | NO SE REPORTO CAUSA | 1 X65 EN C/L | S21121900037 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 76 | 2021-12-19 | 3800 | keep | 0 | Dec | 2021 | 0.0025882 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-19 10:20 | 2021-12-19 12:45 | 250 | 002:25 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 100 EN C/L, 2 X 100 EN C/L, 2 X 80 EN C/L Y SE DEJO ABIERTO DE SU-2 @ SU-3 POR AVERIA EN TERMINACIONES DEL SU-3 | S21121800336 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 145 | 2021-12-19 | 36250 | keep | 0 | Dec | 2021 | 0.02469 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-12-19 10:25 | 2021-12-19 10:26 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21121900034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-19 | 1827 | keep | 0 | Dec | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
PONCE | 2021-12-19 10:27 | 2021-12-19 12:57 | 2113 | 002:30 | T | DESGANCHE | DISPARO DEL ALIMENTADOR POR DESGANCHE | P21121900039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2021-12-19 | 316950 | keep | 0 | Dec | 2021 | 0.21587 | 0.0014392 | Sustained | FALSE | FALSE | Not_TMED_Event | 2113
UTUADO | 2021-12-19 10:33 | 2021-12-19 14:03 | 150 | 003:30 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A21121900006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2021-12-19 | 31500 | keep | 0 | Dec | 2021 | 0.021455 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2021-12-19 10:37 | 2021-12-19 15:44 | 6136 | 005:07 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETES Y AISLADORES Y SE CERRO MACHETES | B21121900000 | New_Event | Switch Failure | Include | Include | Equipment | 307 | 2021-12-19 | 1883752 | keep | 0 | Dec | 2021 | 1.283 | 0.0041792 | Sustained | FALSE | FALSE | Not_TMED_Event | 6136
HUMACAO | 2021-12-19 11:04 | 2021-12-19 13:36 | 50 | 002:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN C/L LEVANTO CONDUCTOR | C21121900154 | New_Event | Wire Down | Include | Include | Equipment | 152 | 2021-12-19 | 7600 | keep | 0 | Dec | 2021 | 0.0051763 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-12-19 11:22 | 2021-12-19 15:54 | 10 | 004:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN XMR REMPLAZO CAJA | R21121900027 | New_Event | Cutout Failure | Include | Include | Equipment | 272 | 2021-12-19 | 2720 | keep | 0 | Dec | 2021 | 0.0018526 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-19 11:25 | 2021-12-19 17:30 | 10 | 006:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A21121900013 | New_Event | Wire Down | Include | Include | Equipment | 365 | 2021-12-19 | 3650 | keep | 0 | Dec | 2021 | 0.002486 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-19 11:33 | 2021-12-19 11:34 | 436 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO | C21121900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-19 | 436 | keep | 0 | Dec | 2021 | 0.00029696 | 0.00029696 | Momentary | FALSE | FALSE | Not_TMED_Event | 436
ARECIBO | 2021-12-19 11:38 | 2021-12-19 13:00 | 6 | 001:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A21121900015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 82 | 2021-12-19 | 492 | keep | 0 | Dec | 2021 | 0.0003351 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-12-19 11:59 | 2021-12-19 14:13 | 1825 | 002:14 | T | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO POR SCADA | S21121900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2021-12-19 | 244550 | keep | 0 | Dec | 2021 | 0.16656 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2021-12-19 11:59 | 2021-12-19 14:13 | 3957 | 002:14 | T | DESGANCHE | SE RETIRO ARBOL DE LA LINEA Y SE CERRO POR SCADA | S21121900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2021-12-19 | 530238 | keep | 0 | Dec | 2021 | 0.36114 | 0.0026951 | Sustained | FALSE | FALSE | Not_TMED_Event | 3957
BAYAMON | 2021-12-19 12:04 | 2021-12-19 16:37 | 30 | 004:33 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 50 EN C/L SE REPARO TERMINACION | B21121900108 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 273 | 2021-12-19 | 8190 | keep | 0 | Dec | 2021 | 0.0055782 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-12-19 12:06 | 2021-12-19 12:07 | 476 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3000 | C21121900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-19 | 476 | keep | 0 | Dec | 2021 | 0.0003242 | 0.0003242 | Momentary | FALSE | FALSE | Not_TMED_Event | 476
CAGUAS | 2021-12-19 12:06 | 2021-12-19 12:07 | 1655 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3000 | C21121900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-19 | 1655 | keep | 0 | Dec | 2021 | 0.0011272 | 0.0011272 | Momentary | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2021-12-19 12:06 | 2021-12-19 12:07 | 361 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3000 | C21121900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-19 | 361 | keep | 0 | Dec | 2021 | 0.00024588 | 0.00024588 | Momentary | FALSE | FALSE | Not_TMED_Event | 361
CAGUAS | 2021-12-19 12:06 | 2021-12-19 12:07 | 2842 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3000 | C21121900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-19 | 2842 | keep | 0 | Dec | 2021 | 0.0019357 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
CAGUAS | 2021-12-19 12:06 | 2021-12-19 12:07 | 1702 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3000 | C21121900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-19 | 1702 | keep | 0 | Dec | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2021-12-19 12:06 | 2021-12-19 12:07 | 918 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3000 | C21121900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-12-19 | 918 | keep | 0 | Dec | 2021 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2021-12-19 12:06 | 2021-12-19 12:07 | 1922 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO | C21121900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-19 | 1922 | keep | 0 | Dec | 2021 | 0.0013091 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
CAGUAS | 2021-12-19 12:07 | 2021-12-19 12:49 | 80 | 000:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE | C21121800138 | Partial_restoration | Wire Down | Include | Include | Equipment | 42 | 2021-12-19 | 3360 | keep | 0 | Dec | 2021 | 0.0022885 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-12-19 12:09 | 2021-12-19 20:29 | 40 | 008:20 | P | DESGANCHE | 1 X 40 EN C/L | C21121900167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 500 | 2021-12-19 | 20000 | keep | 0 | Dec | 2021 | 0.013622 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2021-12-19 12:09 | 2021-12-19 13:49 | 1 | 001:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO DE CAJA PRIMARIA Y 1 X 100 EN CORTE DE LINEA | P21121900058 | New_Event | Cutout Failure | Include | Include | Equipment | 100 | 2021-12-19 | 100 | keep | 0 | Dec | 2021 | 6.811e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-12-19 12:17 | 2021-12-19 13:00 | 60 | 000:43 | P | DESGANCHE | 1 X 50 EN C/L | C21121900168 | New_Event | Vegetation Contact | Include | Include | Vegetation | 43 | 2021-12-19 | 2580 | keep | 0 | Dec | 2021 | 0.0017572 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-12-19 12:22 | 2021-12-19 15:55 | 30 | 003:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN C/L SE RETEZO LINEA | B21121900113 | New_Event | Wire Down | Include | Include | Equipment | 213 | 2021-12-19 | 6390 | keep | 0 | Dec | 2021 | 0.0043522 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-19 12:24 | 2021-12-20 11:02 | 30 | 022:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REMPLAZO BAJANTE PRIMARIO | A21121900020 | New_Event | Wire Down | Include | Include | Equipment | 1358 | 2021-12-19 | 40740 | keep | 0 | Dec | 2021 | 0.027748 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-19 12:26 | 2021-12-19 15:19 | 50 | 002:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21121900023 | New_Event | Bad Weather | Include | Include | Weather | 173 | 2021-12-19 | 8650 | keep | 0 | Dec | 2021 | 0.0058915 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-12-19 12:31 | 2021-12-19 16:27 | 25 | 003:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L MAL TIEMPO | C21121900173 | New_Event | Bad Weather | Include | Include | Weather | 236 | 2021-12-19 | 5900 | keep | 0 | Dec | 2021 | 0.0040185 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-12-19 12:38 | 2021-12-19 15:19 | 32 | 002:41 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S21121900108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 161 | 2021-12-19 | 5152 | keep | 0 | Dec | 2021 | 0.003509 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
CAGUAS | 2021-12-19 12:38 | 2021-12-19 15:52 | 10 | 003:14 | P | SECUNDARIA/DESGANCHE | ABRIO XMR PARA DESGANCHAR Y REPARAR SECUNDARIA | C21121900053 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 194 | 2021-12-19 | 1940 | keep | 0 | Dec | 2021 | 0.0013213 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2021-12-19 12:50 | 2021-12-19 15:40 | 131 | 002:50 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE REPORTO LA CAUSA | P21121900062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 170 | 2021-12-19 | 22270 | keep | 0 | Dec | 2021 | 0.015168 | 8.9224e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 131
BAYAMON | 2021-12-19 12:53 | 2021-12-19 14:54 | 50 | 002:01 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B21121900127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 121 | 2021-12-19 | 6050 | keep | 0 | Dec | 2021 | 0.0041206 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-12-19 12:58 | 2021-12-19 12:59 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21121900043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-19 | 3041 | keep | 0 | Dec | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2021-12-19 13:00 | 2021-12-19 13:01 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21121900044 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-19 | 3041 | keep | 0 | Dec | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
SAN JUAN | 2021-12-19 13:01 | 2021-12-19 15:51 | 15 | 002:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REMPLAZO CAJA QUEMADA | S21121900116 | New_Event | Cutout Failure | Include | Include | Equipment | 170 | 2021-12-19 | 2550 | keep | 0 | Dec | 2021 | 0.0017368 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2021-12-19 13:04 | 2021-12-19 13:45 | 1 | 000:41 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P21121900063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 41 | 2021-12-19 | 41 | keep | 0 | Dec | 2021 | 2.7925e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-19 13:09 | 2021-12-19 16:16 | 10 | 003:07 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | S21121900120 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 187 | 2021-12-19 | 1870 | keep | 0 | Dec | 2021 | 0.0012736 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-19 13:22 | 2021-12-19 17:15 | 75 | 003:53 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21121900028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2021-12-19 | 17475 | keep | 0 | Dec | 2021 | 0.011902 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2021-12-19 13:24 | 2021-12-19 17:03 | 40 | 003:39 | P | HERRAJE ROTO O PODRIDO | 1 X 50 EN C/L REMPLAZO HARRAJE DE CAJA | C21121900177 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 219 | 2021-12-19 | 8760 | keep | 0 | Dec | 2021 | 0.0059664 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2021-12-19 13:35 | 2021-12-20 11:30 | 1 | 021:55 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C21121900179 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1315 | 2021-12-19 | 1315 | keep | 0 | Dec | 2021 | 0.00089564 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-12-19 13:35 | 2021-12-19 15:38 | 105 | 002:03 | P | DESGANCHE | 2 X 50 EN C/L | C21121900179 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2021-12-19 | 12915 | keep | 0 | Dec | 2021 | 0.0087963 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
AGUADILLA | 2021-12-19 13:36 | 2021-12-19 17:29 | 5 | 003:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M21121900050 | New_Event | Bad Weather | Include | Include | Weather | 233 | 2021-12-19 | 1165 | keep | 0 | Dec | 2021 | 0.00079348 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-12-19 13:38 | 2021-12-19 13:39 | 1085 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21121900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-19 | 1085 | keep | 0 | Dec | 2021 | 0.00073899 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
CANOVANAS | 2021-12-19 13:40 | 2021-12-19 16:05 | 40 | 002:25 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER @ SU - 2 NO CAUSA | R21121900033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2021-12-19 | 5800 | keep | 0 | Dec | 2021 | 0.0039504 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2021-12-19 13:43 | 2021-12-19 17:23 | 88 | 003:40 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO NADA | P21121900066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 220 | 2021-12-19 | 19360 | keep | 0 | Dec | 2021 | 0.013186 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
BARRANQUITAS | 2021-12-19 13:57 | 2021-12-19 15:13 | 50 | 001:16 | P | DESGANCHE | 1 X 50 EN C/L | C21121900182 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2021-12-19 | 3800 | keep | 0 | Dec | 2021 | 0.0025882 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2021-12-19 14:02 | 2021-12-20 11:44 | 6 | 021:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO NEUTRAL | R21121900035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1302 | 2021-12-19 | 7812 | keep | 0 | Dec | 2021 | 0.0053207 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-12-19 14:15 | 2021-12-19 15:00 | 1825 | 000:45 | T | DESGANCHE | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA | S21121900000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 45 | 2021-12-19 | 82125 | keep | 0 | Dec | 2021 | 0.055935 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-12-19 14:28 | 2021-12-20 13:18 | 10 | 022:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN XMR | C21121900186 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1370 | 2021-12-19 | 13700 | keep | 0 | Dec | 2021 | 0.009331 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-12-19 14:45 | 2021-12-19 15:16 | 8 | 000:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR CONEXIONES EN LINEA SECUNDARIA | P21121900030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 31 | 2021-12-19 | 248 | keep | 0 | Dec | 2021 | 0.00016891 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-12-19 14:45 | 2021-12-19 15:06 | 8 | 000:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | M21121900055 | New_Event | Secondary Wire Down | Include | Include | Equipment | 21 | 2021-12-19 | 168 | keep | 0 | Dec | 2021 | 0.00011442 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2021-12-19 14:57 | 2021-12-19 18:09 | 40 | 003:12 | P | DESGANCHE | 1 X 40 EN C/L | R21121900040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2021-12-19 | 7680 | keep | 0 | Dec | 2021 | 0.0052308 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-12-19 15:00 | 2021-12-19 15:52 | 600 | 000:52 | P | DESGANCHE | SE SECCIONALIZO Y SE CERRARON MACHETES PREVIAMENTE ABIERTOS | S21121900000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 52 | 2021-12-19 | 31200 | keep | 0 | Dec | 2021 | 0.02125 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-12-19 15:06 | 2021-12-20 09:23 | 40 | 018:17 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | C21121900190 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1097 | 2021-12-19 | 43880 | keep | 0 | Dec | 2021 | 0.029886 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2021-12-19 15:14 | 2021-12-19 17:15 | 10 | 002:01 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | P21121900075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2021-12-19 | 1210 | keep | 0 | Dec | 2021 | 0.00082413 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-19 15:23 | 2021-12-19 17:39 | 8 | 002:16 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR SE REPARO SECUNDARIA Y SE DESGANCHO | B21121900000 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 136 | 2021-12-19 | 1088 | keep | 0 | Dec | 2021 | 0.00074103 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-12-19 15:25 | 2021-12-19 17:07 | 50 | 001:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE X AVE | C21121900192 | New_Event |  |  | Include | Wildlife | 102 | 2021-12-19 | 5100 | keep | 0 | Dec | 2021 | 0.0034736 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2021-12-19 15:29 | 2021-12-19 20:00 | 80 | 004:31 | P | DESGANCHE | 2 X 50 EN C/L | R21121900041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 271 | 2021-12-19 | 21680 | keep | 0 | Dec | 2021 | 0.014766 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-12-19 15:47 | 2021-12-19 18:52 | 30 | 003:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L Y 1 X 15 EN XMR SE RETIRO CULEBRA | B21121900191 | New_Event |  |  | Include | Wildlife | 185 | 2021-12-19 | 5550 | keep | 0 | Dec | 2021 | 0.0037801 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-12-19 15:52 | 2021-12-19 16:57 | 300 | 001:05 | P | DESGANCHE | SE SECCIONALIZO Y SE CERRARON MACHETES PREVIAMENTE ABIERTOS | S21121900000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 65 | 2021-12-19 | 19500 | keep | 0 | Dec | 2021 | 0.013281 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-19 15:59 | 2021-12-19 17:11 | 1 | 001:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE X REPTIL | R21121900042 | New_Event |  |  | Include | Wildlife | 72 | 2021-12-19 | 72 | keep | 0 | Dec | 2021 | 4.9039e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-19 16:22 | 2021-12-19 20:31 | 36 | 004:09 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 40 EN C/L | B21121900196 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 249 | 2021-12-19 | 8964 | keep | 0 | Dec | 2021 | 0.0061053 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
AGUADILLA | 2021-12-19 16:28 | 2021-12-19 19:01 | 80 | 002:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M21121900064 | New_Event | Bad Weather | Include | Include | Weather | 153 | 2021-12-19 | 12240 | keep | 0 | Dec | 2021 | 0.0083366 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2021-12-19 16:29 | 2021-12-19 18:21 | 130 | 001:52 | P | DESGANCHE | 2 X 65 EN C/L | C21121900200 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2021-12-19 | 14560 | keep | 0 | Dec | 2021 | 0.0099167 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
BAYAMON | 2021-12-19 16:32 | 2021-12-19 19:27 | 6 | 002:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S21121900166 | New_Event | Secondary Wire Down | Include | Include | Equipment | 175 | 2021-12-19 | 1050 | keep | 0 | Dec | 2021 | 0.00071515 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-12-19 16:41 | 2021-12-20 10:00 | 10 | 017:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN XMR CRUCE POR AVE | C21121900202 | New_Event |  |  | Include | Wildlife | 1039 | 2021-12-19 | 10390 | keep | 0 | Dec | 2021 | 0.0070766 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-19 16:51 | 2021-12-19 17:12 | 1 | 000:21 | P | OTRAS CAUSAS | 1 X 20 EN BANCO DE TRANSFORMADORES PROA | C21121900204 | New_Event | Other Causes | Include | Include | Other | 21 | 2021-12-19 | 21 | keep | 0 | Dec | 2021 | 1.4303e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2021-12-19 16:53 | 2021-12-20 11:11 | 10 | 018:18 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR | C21121900205 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1098 | 2021-12-19 | 10980 | keep | 0 | Dec | 2021 | 0.0074784 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-19 16:57 | 2021-12-19 16:59 | 1825 | 000:02 | T | DESGANCHE | SE CERRO POR SCADA | S21121900000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-12-19 | 3650 | keep | 0 | Dec | 2021 | 0.002486 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-19 16:59 | 2021-12-19 22:47 | 175 | 005:48 | P | DESGANCHE | SE REALIZO REEMPLAZO DE AISLADOR Y PODA DE BAMBUAS | S21121900000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 348 | 2021-12-19 | 60900 | keep | 0 | Dec | 2021 | 0.041479 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
MAYAGÃœEZ | 2021-12-19 17:12 | 2021-12-19 19:16 | 1597 | 002:04 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE RETIRO GLOBO CRUZANDO LINEAS PRIMARIAS | M21121900069 | New_Event |  |  | Include | Wildlife | 124 | 2021-12-19 | 198028 | keep | 0 | Dec | 2021 | 0.13488 | 0.0010877 | Sustained | FALSE | FALSE | Not_TMED_Event | 1597
MAYAGÃœEZ | 2021-12-19 17:38 | 2021-12-20 11:20 | 100 | 017:42 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M21121900074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1062 | 2021-12-19 | 106200 | keep | 0 | Dec | 2021 | 0.072332 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-12-19 17:47 | 2021-12-19 17:52 | 1935 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9800 | B21121900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-19 | 9675 | keep | 0 | Dec | 2021 | 0.0065896 | 0.0013179 | Momentary | FALSE | FALSE | Not_TMED_Event | 1935
BAYAMON | 2021-12-19 17:47 | 2021-12-19 17:52 | 3 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9800 | B21121900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-19 | 15 | keep | 0 | Dec | 2021 | 1.0216e-05 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-12-19 17:47 | 2021-12-19 17:52 | 61 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9800 | B21121900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-19 | 305 | keep | 0 | Dec | 2021 | 0.00020773 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2021-12-19 17:47 | 2021-12-19 17:52 | 1501 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9800 | B21121900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-19 | 7505 | keep | 0 | Dec | 2021 | 0.0051116 | 0.0010223 | Momentary | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2021-12-19 17:47 | 2021-12-19 17:52 | 546 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9800 | B21121900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-19 | 2730 | keep | 0 | Dec | 2021 | 0.0018594 | 0.00037188 | Momentary | FALSE | FALSE | Not_TMED_Event | 546
BAYAMON | 2021-12-19 17:47 | 2021-12-19 17:52 | 959 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9800 CARGA DEL 1901-01 POR 1904-07 | S21121900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-19 | 4795 | keep | 0 | Dec | 2021 | 0.0032659 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2021-12-19 17:47 | 2021-12-19 17:52 | 1297 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9800 CARGA DEL 1901-02 POR 1904-06 | S21121900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-19 | 6485 | keep | 0 | Dec | 2021 | 0.0044169 | 0.00088338 | Momentary | FALSE | FALSE | Not_TMED_Event | 1297
BAYAMON | 2021-12-19 17:47 | 2021-12-19 17:52 | 451 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9800 CARGA DEL 1901-03 POR 1904-06 | S21121900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-19 | 2255 | keep | 0 | Dec | 2021 | 0.0015359 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
BAYAMON | 2021-12-19 17:47 | 2021-12-19 17:52 | 1264 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9800 CARGA DEL 1901-04 POR 1904-07 | S21121900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-19 | 6320 | keep | 0 | Dec | 2021 | 0.0043045 | 0.0008609 | Momentary | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2021-12-19 17:47 | 2021-12-19 17:52 | 620 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9800 | S21121900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-12-19 | 3100 | keep | 0 | Dec | 2021 | 0.0021114 | 0.00042228 | Momentary | FALSE | FALSE | Not_TMED_Event | 620
CAGUAS | 2021-12-19 18:06 | 2021-12-19 18:08 | 436 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO | C21121900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-19 | 872 | keep | 0 | Dec | 2021 | 0.00059392 | 0.00029696 | Momentary | FALSE | FALSE | Not_TMED_Event | 436
AGUADILLA | 2021-12-19 18:25 | 2021-12-20 10:56 | 35 | 016:31 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M21121900084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 991 | 2021-12-19 | 34685 | keep | 0 | Dec | 2021 | 0.023624 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2021-12-19 18:37 | 2021-12-19 20:23 | 40 | 001:46 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 65 EN RISER CONTAMINACION EN SU - 11 | C21121900162 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 106 | 2021-12-19 | 4240 | keep | 0 | Dec | 2021 | 0.0028878 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-12-19 18:54 | 2021-12-19 20:36 | 40 | 001:42 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 80 SMU 20 EN SU 1 J C CONTAMINACION | R21121900050 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 102 | 2021-12-19 | 4080 | keep | 0 | Dec | 2021 | 0.0027789 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-12-19 19:08 | 2021-12-19 21:43 | 50 | 002:35 | P | DESGANCHE | 1 X 50 EN C/L | R21121900055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2021-12-19 | 7750 | keep | 0 | Dec | 2021 | 0.0052785 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-12-19 19:18 | 2021-12-20 13:03 | 50 | 017:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS | A21121900046 | New_Event | Wire Down | Include | Include | Equipment | 1065 | 2021-12-19 | 53250 | keep | 0 | Dec | 2021 | 0.036268 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-12-19 19:38 | 2021-12-20 00:04 | 80 | 004:26 | P | TRANSFORMADOR AVERIADO | 2 X 100 Y 2 X 40 EN CORTE DE LINEA TRANSFORMADOR T4 QUEMADO | R21121900060 | New_Event | Service Transformer Failure | Include | Include | Equipment | 266 | 2021-12-19 | 21280 | keep | 0 | Dec | 2021 | 0.014494 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2021-12-19 19:53 | 2021-12-20 12:01 | 8 | 016:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO LINEA SECUNDARIA | A21121900050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 968 | 2021-12-19 | 7744 | keep | 0 | Dec | 2021 | 0.0052744 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-12-19 20:12 | 2021-12-20 09:58 | 100 | 013:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M21121900097 | New_Event |  |  | Include | Wildlife | 826 | 2021-12-19 | 82600 | keep | 0 | Dec | 2021 | 0.056258 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-12-19 20:14 | 2021-12-20 13:47 | 14 | 017:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN XMR | C21121900211 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1053 | 2021-12-19 | 14742 | keep | 0 | Dec | 2021 | 0.010041 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
UTUADO | 2021-12-19 21:20 | 2021-12-19 21:21 | 1405 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21121900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-19 | 1405 | keep | 0 | Dec | 2021 | 0.00095694 | 0.00095694 | Momentary | FALSE | FALSE | Not_TMED_Event | 1405
MAYAGÃœEZ | 2021-12-19 21:21 | 2021-12-19 21:22 | 4304 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21121900101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-19 | 4304 | keep | 0 | Dec | 2021 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
MAYAGÃœEZ | 2021-12-19 21:25 | 2021-12-19 21:26 | 4304 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21121900102 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-19 | 4304 | keep | 0 | Dec | 2021 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
BAYAMON | 2021-12-19 21:28 | 2021-12-20 04:26 | 25 | 006:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21121900199 | New_Event | Secondary Wire Down | Include | Include | Equipment | 418 | 2021-12-19 | 10450 | keep | 0 | Dec | 2021 | 0.0071174 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-12-19 21:53 | 2021-12-20 10:07 | 70 | 012:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L. SE REEMPLAZO CAJA AVERIADA | S21121900201 | New_Event | Cutout Failure | Include | Include | Equipment | 734 | 2021-12-19 | 51380 | keep | 0 | Dec | 2021 | 0.034995 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2021-12-19 21:53 | 2021-12-20 09:19 | 20 | 011:26 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | R21121900073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 686 | 2021-12-19 | 13720 | keep | 0 | Dec | 2021 | 0.0093446 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2021-12-19 21:53 | 2021-12-20 11:24 | 60 | 013:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PARTIDA Y SE CERRO MACHETES | A21121900056 | New_Event | Wire Down | Include | Include | Equipment | 811 | 2021-12-19 | 48660 | keep | 0 | Dec | 2021 | 0.033142 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2021-12-19 22:14 | 2021-12-21 11:19 | 20 | 037:05 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN C/L REPARO TRAMO ENTRE T-5 Y T-6 | C21121900217 | New_Event | UG Cable Fault | Include | Include | Equipment | 2225 | 2021-12-19 | 44500 | keep | 0 | Dec | 2021 | 0.030309 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-12-19 22:14 | 2021-12-20 13:28 | 60 | 015:14 | P | CABLE SOTERRADO AVERIADO | 1 X 65 EN RISER Y 1 X 50 EN SU-11 @ T-4. AVERIA EN T-5 @ T-6 | C21121900217 | New_Event | UG Cable Fault | Include | Include | Equipment | 914 | 2021-12-19 | 54840 | keep | 0 | Dec | 2021 | 0.037351 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2021-12-19 22:16 | 2021-12-20 00:06 | 2410 | 001:50 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 18400 | C21121900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 110 | 2021-12-19 | 265100 | keep | 0 | Dec | 2021 | 0.18056 | 0.0016414 | Sustained | FALSE | FALSE | Not_TMED_Event | 2410
BARRANQUITAS | 2021-12-19 22:16 | 2021-12-20 00:06 | 2826 | 001:50 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 18400 | C21121900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 110 | 2021-12-19 | 310860 | keep | 0 | Dec | 2021 | 0.21173 | 0.0019248 | Sustained | FALSE | FALSE | Not_TMED_Event | 2826
BAYAMON | 2021-12-19 23:21 | 2021-12-19 23:22 | 1834 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERUPTOR | B21121900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-19 | 1834 | keep | 0 | Dec | 2021 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
CANOVANAS | 2021-12-20 00:04 | 2021-12-20 11:32 | 9 | 011:28 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 75KVA POR UNO DE IGUAL CAPACIDAD | R21122000001 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 688 | 2021-12-20 | 6192 | keep | 0 | Dec | 2021 | 0.0042173 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-12-20 00:09 | 2021-12-20 00:40 | 1160 | 000:31 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR Y SE CERRO PUENTE EN TRONCAL, NO HAY EVENTO DE PARCIAL | A21122000001 | New_Event | Wire Down | Include | Include | Equipment | 31 | 2021-12-20 | 35960 | keep | 0 | Dec | 2021 | 0.024492 | 0.00079007 | Sustained | FALSE | FALSE | Not_TMED_Event | 1160
SAN JUAN | 2021-12-20 01:42 | 2021-12-20 17:28 | 1 | 015:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | S21122000058 | New_Event | Wire Down | Include | Include | Equipment | 946 | 2021-12-20 | 946 | keep | 0 | Dec | 2021 | 0.00064432 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-20 01:43 | 2021-12-20 12:07 | 20 | 010:24 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REMPLAZO BASE EN SU-1 | R21122000002 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 624 | 2021-12-20 | 12480 | keep | 0 | Dec | 2021 | 0.0085001 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-12-20 02:02 | 2021-12-20 02:10 | 10211 | 000:08 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRPTOR 1206-03 QUE A SU VEZ LLEVA LA CARGA DEL 1204-05 | S21122000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2021-12-20 | 81688 | keep | 0 | Dec | 2021 | 0.055637 | 0.0069547 | Sustained | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-12-20 02:02 | 2021-12-20 02:10 | 4133 | 000:08 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRPTOR 1206-03 QUE A SU VEZ LLEVA LA CARGA DEL 1204-05 | S21122000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2021-12-20 | 33064 | keep | 0 | Dec | 2021 | 0.02252 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-12-20 02:36 | 2021-12-20 11:52 | 45 | 009:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L. SE REEMPLAZO CAJA AVERIADA | S21122000005 | New_Event | Cutout Failure | Include | Include | Equipment | 556 | 2021-12-20 | 25020 | keep | 0 | Dec | 2021 | 0.017041 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
HUMACAO | 2021-12-20 03:31 | 2021-12-20 10:16 | 45 | 006:45 | P | DESGANCHE | 1 X 65 EN RISER | C21122000001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 405 | 2021-12-20 | 18225 | keep | 0 | Dec | 2021 | 0.012413 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2021-12-20 06:24 | 2021-12-20 06:25 | 990 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21122000002 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-12-20 | 990 | keep | 0 | Dec | 2021 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
MAYAGÃœEZ | 2021-12-20 06:25 | 2021-12-20 11:01 | 1 | 004:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | M21122000003 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 276 | 2021-12-20 | 276 | keep | 0 | Dec | 2021 | 0.00018798 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-12-20 07:13 | 2021-12-20 11:59 | 50 | 004:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21122000013 | New_Event | Bad Weather | Include | Include | Weather | 286 | 2021-12-20 | 14300 | keep | 0 | Dec | 2021 | 0.0097397 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2021-12-20 07:28 | 2021-12-20 11:54 | 12 | 004:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO BAJANTE PRIMARIO | A21122000015 | New_Event | Wire Down | Include | Include | Equipment | 266 | 2021-12-20 | 3192 | keep | 0 | Dec | 2021 | 0.0021741 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-12-20 07:43 | 2021-12-20 10:13 | 45 | 002:30 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA Y 1 X 10 XMR REPARO AISLADOR SAFADO | C21122000008 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 150 | 2021-12-20 | 6750 | keep | 0 | Dec | 2021 | 0.0045974 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2021-12-20 07:53 | 2021-12-20 10:02 | 45 | 002:09 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21122000011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2021-12-20 | 5805 | keep | 0 | Dec | 2021 | 0.0039538 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2021-12-20 08:00 | 2021-12-20 12:34 | 11 | 004:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN XMR RETEZO LINEA SECUNDARIA | C21122000012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 274 | 2021-12-20 | 3014 | keep | 0 | Dec | 2021 | 0.0020528 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2021-12-20 08:00 | 2021-12-20 17:15 | 1 | 009:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | M21122000005 | New_Event | Bad Weather | Include | Include | Weather | 555 | 2021-12-20 | 555 | keep | 0 | Dec | 2021 | 0.00037801 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-12-20 08:04 | 2021-12-20 10:15 | 112 | 002:11 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER Y 1 X 15 EN SU-9 NO SE REPORTO LA CAUSA | P21122000006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 131 | 2021-12-20 | 14672 | keep | 0 | Dec | 2021 | 0.009993 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
MAYAGÃœEZ | 2021-12-20 08:04 | 2021-12-20 14:49 | 50 | 006:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA IGUANA CRUZO LINEAS | M21122000007 | New_Event |  |  | Include | Wildlife | 405 | 2021-12-20 | 20250 | keep | 0 | Dec | 2021 | 0.013792 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-12-20 08:16 | 2021-12-20 13:29 | 14 | 005:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REEMPLAZAR BARRA EN PEDESTAL | C21122000015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 313 | 2021-12-20 | 4382 | keep | 0 | Dec | 2021 | 0.0029846 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
PONCE | 2021-12-20 08:23 | 2021-12-20 12:25 | 1 | 004:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN CORTE DE LINEA SE REEMPLAZO AISLADOR ROTO | P21122000010 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 242 | 2021-12-20 | 242 | keep | 0 | Dec | 2021 | 0.00016483 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-20 08:28 | 2021-12-20 08:29 | 1297 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO INTERRUPTOR A SOLICITUD DE ELVIN MORALES POR CAJA EN FUEGO CARGA POR BKR 1904-6 | S21122000007 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-12-20 | 1297 | keep | 0 | Dec | 2021 | 0.00088338 | 0.00088338 | Momentary | FALSE | FALSE | Not_TMED_Event | 1297
BAYAMON | 2021-12-20 08:28 | 2021-12-20 08:29 | 451 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO INTERRUPTOR A PETICION DE ELVIN MORALES POR CAJA EN FUEGO. CARGA POR BKR 1904-06 | S21122000007 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-12-20 | 451 | keep | 0 | Dec | 2021 | 0.00030717 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
BAYAMON | 2021-12-20 08:29 | 2021-12-20 09:45 | 15 | 001:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA | S21122000007 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 76 | 2021-12-20 | 1140 | keep | 0 | Dec | 2021 | 0.00077645 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-12-20 08:49 | 2021-12-20 12:55 | 1 | 004:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REMPLAZO PORTAFUSIBLES Y SE DESGANCHO | R21122000014 | New_Event | Cutout Failure | Include | Include | Equipment | 246 | 2021-12-20 | 246 | keep | 0 | Dec | 2021 | 0.00016755 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-12-20 08:51 | 2021-12-20 14:51 | 1 | 006:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA EN EL PISO | P21122000013 | New_Event | Wire Down | Include | Include | Equipment | 360 | 2021-12-20 | 360 | keep | 0 | Dec | 2021 | 0.00024519 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-20 08:53 | 2021-12-20 19:35 | 5 | 010:42 | P | ESTRUCTURA AVERIADA | 3 X 40 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO | M21122000015 | New_Event | Defective Pole | Include | Include | Equipment | 642 | 2021-12-20 | 3210 | keep | 0 | Dec | 2021 | 0.0021863 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-12-20 09:00 | 2021-12-20 12:24 | 41 | 003:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO A CAJA EN CORTE DE LINEA | P21122000015 | New_Event | Wire Down | Include | Include | Equipment | 204 | 2021-12-20 | 8364 | keep | 0 | Dec | 2021 | 0.0056967 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
BAYAMON | 2021-12-20 09:01 | 2021-12-20 11:51 | 27 | 002:50 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B21122000009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 170 | 2021-12-20 | 4590 | keep | 0 | Dec | 2021 | 0.0031262 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
ARECIBO | 2021-12-20 09:03 | 2021-12-20 09:04 | 1227 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | A21122000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-20 | 1227 | keep | 0 | Dec | 2021 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
GUAYAMA | 2021-12-20 09:22 | 2021-12-20 12:16 | 1 | 002:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 40 EN RISER AVE CRUZO FASE | P21122000017 | New_Event |  |  | Include | Wildlife | 174 | 2021-12-20 | 174 | keep | 0 | Dec | 2021 | 0.00011851 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-12-20 09:30 | 2021-12-20 17:50 | 6 | 008:20 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REEMPLAZO 3 MACHETES EN SU-1 3 X 40 EN RISER Y 1 X 25 EN OTRO RISER | R21122000018 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 500 | 2021-12-20 | 3000 | keep | 0 | Dec | 2021 | 0.0020433 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-12-20 09:31 | 2021-12-20 16:11 | 2 | 006:40 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SECTOR REQUIERE DESGANCHE PRIMARIO | M21122000020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 400 | 2021-12-20 | 800 | keep | 0 | Dec | 2021 | 0.00054488 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2021-12-20 09:40 | 2021-12-20 13:10 | 15 | 003:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR LA MISMA CAPACIDAD | M21122000004 | New_Event | Service Transformer Failure | Include | Include | Equipment | 210 | 2021-12-20 | 3150 | keep | 0 | Dec | 2021 | 0.0021455 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-12-20 09:40 | 2021-12-20 15:35 | 80 | 005:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M21122000022 | New_Event | Cutout Failure | Include | Include | Equipment | 355 | 2021-12-20 | 28400 | keep | 0 | Dec | 2021 | 0.019343 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2021-12-20 09:41 | 2021-12-20 13:11 | 50 | 003:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | P21122000022 | New_Event |  |  | Include | Wildlife | 210 | 2021-12-20 | 10500 | keep | 0 | Dec | 2021 | 0.0071515 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-20 09:52 | 2021-12-20 19:47 | 50 | 009:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR PRIMARIO | B21122000011 | New_Event | Wire Down | Include | Include | Equipment | 595 | 2021-12-20 | 29750 | keep | 0 | Dec | 2021 | 0.020263 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-12-20 10:02 | 2021-12-20 12:11 | 2 | 002:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE RETESO LINEA PRIMARIA | M21122000026 | New_Event | Wire Down | Include | Include | Equipment | 129 | 2021-12-20 | 258 | keep | 0 | Dec | 2021 | 0.00017572 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2021-12-20 10:25 | 2021-12-20 15:07 | 9 | 004:42 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50 KVA X 50 KVA | R21122000024 | New_Event | Service Transformer Failure | Include | Include | Equipment | 282 | 2021-12-20 | 2538 | keep | 0 | Dec | 2021 | 0.0017286 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-12-20 10:29 | 2021-12-20 13:24 | 10 | 002:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S21122000016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 175 | 2021-12-20 | 1750 | keep | 0 | Dec | 2021 | 0.0011919 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-12-20 10:34 | 2021-12-20 16:04 | 20 | 005:30 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | C21122000029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 330 | 2021-12-20 | 6600 | keep | 0 | Dec | 2021 | 0.0044952 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-12-20 10:41 | 2021-12-20 12:12 | 10 | 001:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21122000025 | New_Event | Bad Weather | Include | Include | Weather | 91 | 2021-12-20 | 910 | keep | 0 | Dec | 2021 | 0.0006198 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-20 10:54 | 2021-12-20 15:03 | 1 | 004:09 | P | NO SE REPORTO CAUSA | 2 X 25 EN CORTE DE LINEA | S21122000045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 249 | 2021-12-20 | 249 | keep | 0 | Dec | 2021 | 0.00016959 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-12-20 10:55 | 2021-12-20 12:02 | 14 | 001:07 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA A 4.16KV POR UNO DE IGUAL CAPACIDAD | P21122000041 | New_Event | Service Transformer Failure | Include | Include | Equipment | 67 | 2021-12-20 | 938 | keep | 0 | Dec | 2021 | 0.00063887 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2021-12-20 10:56 | 2021-12-20 17:00 | 5 | 006:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S21122000047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 364 | 2021-12-20 | 1820 | keep | 0 | Dec | 2021 | 0.0012396 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-12-20 11:13 | 2021-12-20 11:14 | 828 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1206-04 LLEVANDO 60% DEL 1204-03 Y 40% DEL 1204-04 | S21122000051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-20 | 828 | keep | 0 | Dec | 2021 | 0.00056395 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
SAN JUAN | 2021-12-20 11:13 | 2021-12-20 11:14 | 1977 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1206-04 LLEVANDO 60% DEL 1204-03 Y 40% DEL 1204-04 | S21122000051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-20 | 1977 | keep | 0 | Dec | 2021 | 0.0013465 | 0.0013465 | Momentary | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2021-12-20 11:13 | 2021-12-20 11:14 | 1799 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1206-04 LLEVANDO 60% DEL 1204-03 Y 40% DEL 1204-04 | S21122000051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-20 | 1799 | keep | 0 | Dec | 2021 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
BAYAMON | 2021-12-20 11:25 | 2021-12-20 13:12 | 10 | 001:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S21122000037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 107 | 2021-12-20 | 1070 | keep | 0 | Dec | 2021 | 0.00072877 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-12-20 11:25 | 2021-12-20 19:12 | 30 | 007:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | R21122000027 | New_Event | Bad Weather | Include | Include | Weather | 467 | 2021-12-20 | 14010 | keep | 0 | Dec | 2021 | 0.0095421 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-20 11:28 | 2021-12-20 18:29 | 1 | 007:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN C/L Y SE REMPLAZO PORTAFUSIBLES | S21122000053 | New_Event | Cutout Failure | Include | Include | Equipment | 421 | 2021-12-20 | 421 | keep | 0 | Dec | 2021 | 0.00028674 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-12-20 11:28 | 2021-12-20 14:52 | 1 | 003:24 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M21122000036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2021-12-20 | 204 | keep | 0 | Dec | 2021 | 0.00013894 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-20 11:29 | 2021-12-20 19:06 | 18 | 007:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO Y SE REMPLAZO CAJA PRIMARIA | S21122000054 | New_Event | Wire Down | Include | Include | Equipment | 457 | 2021-12-20 | 8226 | keep | 0 | Dec | 2021 | 0.0056027 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
ARECIBO | 2021-12-20 11:29 | 2021-12-20 13:37 | 140 | 002:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA | A21122000051 | New_Event | Cutout Failure | Include | Include | Equipment | 128 | 2021-12-20 | 17920 | keep | 0 | Dec | 2021 | 0.012205 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
CAGUAS | 2021-12-20 11:30 | 2021-12-20 15:19 | 90 | 003:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA | C21122000033 | New_Event | Cutout Failure | Include | Include | Equipment | 229 | 2021-12-20 | 20610 | keep | 0 | Dec | 2021 | 0.014037 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2021-12-20 11:31 | 2021-12-20 11:42 | 959 | 000:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9800 | B21122000032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2021-12-20 | 10549 | keep | 0 | Dec | 2021 | 0.0071849 | 0.00065317 | Sustained | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2021-12-20 11:31 | 2021-12-20 11:42 | 1382 | 000:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9800 | B21122000032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2021-12-20 | 15202 | keep | 0 | Dec | 2021 | 0.010354 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2021-12-20 11:31 | 2021-12-20 11:42 | 663 | 000:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9800 | B21122000032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2021-12-20 | 7293 | keep | 0 | Dec | 2021 | 0.0049672 | 0.00045157 | Sustained | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2021-12-20 11:31 | 2021-12-20 11:42 | 1514 | 000:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21122000030 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2021-12-20 | 16654 | keep | 0 | Dec | 2021 | 0.011343 | 0.0010312 | Sustained | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2021-12-20 11:31 | 2021-12-20 11:42 | 1105 | 000:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21122000030 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2021-12-20 | 12155 | keep | 0 | Dec | 2021 | 0.0082787 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2021-12-20 11:31 | 2021-12-20 11:42 | 4176 | 000:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21122000034 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2021-12-20 | 45936 | keep | 0 | Dec | 2021 | 0.031287 | 0.0028443 | Sustained | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2021-12-20 11:31 | 2021-12-20 11:42 | 252 | 000:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21122000034 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2021-12-20 | 2772 | keep | 0 | Dec | 2021 | 0.001888 | 0.00017164 | Sustained | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2021-12-20 11:31 | 2021-12-20 11:42 | 2147 | 000:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21122000034 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2021-12-20 | 23617 | keep | 0 | Dec | 2021 | 0.016085 | 0.0014623 | Sustained | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2021-12-20 11:31 | 2021-12-20 11:42 | 2858 | 000:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21122000034 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2021-12-20 | 31438 | keep | 0 | Dec | 2021 | 0.021412 | 0.0019466 | Sustained | FALSE | FALSE | Not_TMED_Event | 2858
SAN JUAN | 2021-12-20 11:42 | 2021-12-20 14:30 | 26 | 002:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L SE REMPLAZO PORTAFUSIBLES | S21122000057 | New_Event | Cutout Failure | Include | Include | Equipment | 168 | 2021-12-20 | 4368 | keep | 0 | Dec | 2021 | 0.002975 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
ARECIBO | 2021-12-20 11:50 | 2021-12-20 15:30 | 5 | 003:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A21122000054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 220 | 2021-12-20 | 1100 | keep | 0 | Dec | 2021 | 0.0007492 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2021-12-20 11:53 | 2021-12-20 18:56 | 1 | 007:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN BANCO DE TRANSFORMADORES CRUCE POR AVE | R21122000030 | New_Event |  |  | Include | Wildlife | 423 | 2021-12-20 | 423 | keep | 0 | Dec | 2021 | 0.0002881 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-12-20 12:07 | 2021-12-20 16:02 | 60 | 003:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA DEFECTUOSA | R21122000031 | New_Event | Cutout Failure | Include | Include | Equipment | 235 | 2021-12-20 | 14100 | keep | 0 | Dec | 2021 | 0.0096034 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-12-20 12:25 | 2021-12-20 14:11 | 1 | 001:46 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 SUM 20 DE 25 AMP. EN SU-2 CONTAMINACION | R21122000032 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 106 | 2021-12-20 | 106 | keep | 0 | Dec | 2021 | 7.2196e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-20 12:35 | 2021-12-20 16:30 | 30 | 003:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21122000040 | New_Event | Bad Weather | Include | Include | Weather | 235 | 2021-12-20 | 7050 | keep | 0 | Dec | 2021 | 0.0048017 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2021-12-20 12:37 | 2021-12-20 16:13 | 35 | 003:36 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO DISCO | R21122000033 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 216 | 2021-12-20 | 7560 | keep | 0 | Dec | 2021 | 0.0051491 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2021-12-20 12:38 | 2021-12-20 12:40 | 725 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO RR/OFF | C21122000041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-20 | 1450 | keep | 0 | Dec | 2021 | 0.00098759 | 0.00049379 | Momentary | FALSE | FALSE | Not_TMED_Event | 725
CAGUAS | 2021-12-20 12:44 | 2021-12-20 14:55 | 45 | 002:11 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | C21122000042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 131 | 2021-12-20 | 5895 | keep | 0 | Dec | 2021 | 0.0040151 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2021-12-20 13:04 | 2021-12-20 13:07 | 2900 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO RR/OFF | C21122000047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-12-20 | 8700 | keep | 0 | Dec | 2021 | 0.0059255 | 0.0019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 2900
CAGUAS | 2021-12-20 13:07 | 2021-12-20 17:19 | 70 | 004:12 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | C21122000077 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 252 | 2021-12-20 | 17640 | keep | 0 | Dec | 2021 | 0.012015 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2021-12-20 13:11 | 2021-12-20 14:39 | 15 | 001:28 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21122000044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 88 | 2021-12-20 | 1320 | keep | 0 | Dec | 2021 | 0.00089905 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-12-20 13:28 | 2021-12-20 13:29 | 7621 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21122000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-20 | 7621 | keep | 0 | Dec | 2021 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
HUMACAO | 2021-12-20 13:38 | 2021-12-20 18:30 | 8 | 004:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA ABIERTA | C21122000055 | New_Event | Secondary Wire Down | Include | Include | Equipment | 292 | 2021-12-20 | 2336 | keep | 0 | Dec | 2021 | 0.001591 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2021-12-20 13:51 | 2021-12-20 16:49 | 197 | 002:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 Y 2 X 40 EN CORTES DE LINEA CAMION IMPACTO POSTE Y MOVIO LAS LINEAS | R21122000040 | New_Event |  |  | Include | Wildlife | 178 | 2021-12-20 | 35066 | keep | 0 | Dec | 2021 | 0.023883 | 0.00013418 | Sustained | FALSE | FALSE | Not_TMED_Event | 197
ARECIBO | 2021-12-20 13:53 | 2021-12-20 14:26 | 14 | 000:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A21122000059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 33 | 2021-12-20 | 462 | keep | 0 | Dec | 2021 | 0.00031467 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2021-12-20 13:59 | 2021-12-20 19:31 | 100 | 005:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REMPLAZO CAJA Y SE CERRO PUENTE | S21122000068 | New_Event | Cutout Failure | Include | Include | Equipment | 332 | 2021-12-20 | 33200 | keep | 0 | Dec | 2021 | 0.022612 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2021-12-20 14:20 | 2021-12-20 16:45 | 12 | 002:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CAJAS DE TRANSFORMADOR PARA RETESAR LINEAS PRIMARIAS | M21122000051 | New_Event | Wire Down | Include | Include | Equipment | 145 | 2021-12-20 | 1740 | keep | 0 | Dec | 2021 | 0.0011851 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-12-20 14:21 | 2021-12-20 16:17 | 5 | 001:56 | P | NO SE REPORTO CAUSA | SE SUBIO XMR AUTOPROTEGIDO | C21122000060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2021-12-20 | 580 | keep | 0 | Dec | 2021 | 0.00039504 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2021-12-20 14:37 | 2021-12-20 15:50 | 1 | 001:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE CERRO PUENTE DE CAJA A CARGA | R21122000042 | New_Event | Wire Down | Include | Include | Equipment | 73 | 2021-12-20 | 73 | keep | 0 | Dec | 2021 | 4.972e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-12-20 14:40 | 2021-12-20 15:39 | 3 | 000:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA Y ENDEREZAR POSTE SECUNDARIO | A21121900007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 59 | 2021-12-20 | 177 | keep | 0 | Dec | 2021 | 0.00012055 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-12-20 14:43 | 2021-12-20 22:19 | 50 | 007:36 | P | ESTRUCTURA AVERIADA | 2 X 50 EN CORTE DE LINEA Y SE REEMPLAZO POSTE PRIMARIO | S21122000075 | New_Event | Defective Pole | Include | Include | Equipment | 456 | 2021-12-20 | 22800 | keep | 0 | Dec | 2021 | 0.015529 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-12-20 14:44 | 2021-12-20 18:30 | 25 | 003:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21122000068 | New_Event | Bad Weather | Include | Include | Weather | 226 | 2021-12-20 | 5650 | keep | 0 | Dec | 2021 | 0.0038482 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2021-12-20 14:51 | 2021-12-21 07:57 | 30 | 017:06 | P | DESGANCHE | 1 X 30 EN C/L | C21122000062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1026 | 2021-12-20 | 30780 | keep | 0 | Dec | 2021 | 0.020964 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-20 15:00 | 2021-12-20 16:23 | 7 | 001:23 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE 37.5 KVA X 37.5 KVA | A21122000073 | New_Event | Service Transformer Failure | Include | Include | Equipment | 83 | 2021-12-20 | 581 | keep | 0 | Dec | 2021 | 0.00039572 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-12-20 15:01 | 2021-12-20 15:22 | 6 | 000:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR CHANGO Y SE RETIRO PENCA DE LA LINEA | R21122000044 | New_Event |  |  | Include | Wildlife | 21 | 2021-12-20 | 126 | keep | 0 | Dec | 2021 | 8.5818e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-12-20 15:01 | 2021-12-20 18:58 | 20 | 003:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | S21122000080 | New_Event | Cutout Failure | Include | Include | Equipment | 237 | 2021-12-20 | 4740 | keep | 0 | Dec | 2021 | 0.0032284 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-12-20 15:06 | 2021-12-20 20:13 | 50 | 005:07 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PARARAYO | S21122000082 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 307 | 2021-12-20 | 15350 | keep | 0 | Dec | 2021 | 0.010455 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-12-20 15:10 | 2021-12-20 15:59 | 300 | 000:49 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ESTABLECIO GOI BY-211220-01 PARA REMPLAZO DE AISLADOR | B21122000050 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 49 | 2021-12-20 | 14700 | keep | 0 | Dec | 2021 | 0.010012 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2021-12-20 15:32 | 2021-12-20 17:50 | 126 | 002:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | R21122000046 | New_Event | Bad Weather | Include | Include | Weather | 138 | 2021-12-20 | 17388 | keep | 0 | Dec | 2021 | 0.011843 | 8.5818e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 126
CAGUAS | 2021-12-20 15:42 | 2021-12-20 17:08 | 60 | 001:26 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21122000070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2021-12-20 | 5160 | keep | 0 | Dec | 2021 | 0.0035145 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2021-12-20 16:05 | 2021-12-20 17:44 | 30 | 001:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | R21122000049 | New_Event | Bad Weather | Include | Include | Weather | 99 | 2021-12-20 | 2970 | keep | 0 | Dec | 2021 | 0.0020229 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-20 16:08 | 2021-12-20 19:03 | 1588 | 002:55 | T | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR CONTROL | B21122000065 | New_Event | UG Cable Fault | Include | Include | Equipment | 175 | 2021-12-20 | 277900 | keep | 0 | Dec | 2021 | 0.18928 | 0.0010816 | Sustained | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2021-12-20 16:08 | 2021-12-20 21:10 | 13 | 005:02 | T | CABLE SOTERRADO AVERIADO | CARGA TRANSFERIDA AL 1711-01 SE TRANSFIRIO LA CARGA AL 1716-03 POR AVERIA SOTERRADA EN CORRIDA DEL 1711-01 | B21122000065 | New_Event | UG Cable Fault | Include | Include | Equipment | 302 | 2021-12-20 | 3926 | keep | 0 | Dec | 2021 | 0.002674 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
PONCE | 2021-12-20 16:50 | 2021-12-20 17:10 | 8 | 000:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P21122000038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 20 | 2021-12-20 | 160 | keep | 0 | Dec | 2021 | 0.00010898 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-12-20 17:02 | 2021-12-20 17:03 | 4381 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21122000073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-20 | 4381 | keep | 0 | Dec | 2021 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
ARECIBO | 2021-12-20 17:25 | 2021-12-20 19:08 | 5 | 001:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A21122000030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 103 | 2021-12-20 | 515 | keep | 0 | Dec | 2021 | 0.00035076 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-12-20 17:33 | 2021-12-21 11:09 | 10 | 017:36 | P | TRANSFORMADOR AVERIADO | 1 X 15 EN TRANSFORMADOR SE REMPLAZO TRANSFORMADOR AVERIADO 25 KVA | B21122000079 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1056 | 2021-12-20 | 10560 | keep | 0 | Dec | 2021 | 0.0071924 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-20 17:40 | 2021-12-20 17:41 | 1342 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21122000086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-20 | 1342 | keep | 0 | Dec | 2021 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
MAYAGÃœEZ | 2021-12-20 18:29 | 2021-12-20 18:30 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21122000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-20 | 1352 | keep | 0 | Dec | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
BARRANQUITAS | 2021-12-20 18:29 | 2021-12-20 19:35 | 2280 | 001:06 | T | DESGANCHE | DISPARO 9902-03 RR/OFF LLEVANDO LA CARGA DEL 9902-02 | C21122000094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2021-12-20 | 150480 | keep | 0 | Dec | 2021 | 0.10249 | 0.0015529 | Sustained | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2021-12-20 18:29 | 2021-12-20 19:35 | 1617 | 001:06 | T | DESGANCHE | DISPARO 9902-03 RR/OFF LLEVANDO LA CARGA DEL 9902-02 | C21122000094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2021-12-20 | 106722 | keep | 0 | Dec | 2021 | 0.072688 | 0.0011013 | Sustained | FALSE | FALSE | Not_TMED_Event | 1617
ARECIBO | 2021-12-20 18:30 | 2021-12-20 21:39 | 3 | 003:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A21122000084 | New_Event | Wire Down | Include | Include | Equipment | 189 | 2021-12-20 | 567 | keep | 0 | Dec | 2021 | 0.00038618 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2021-12-20 18:33 | 2021-12-20 18:55 | 1 | 000:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN BANCO DE TRANSFORMADORES CRUCE POR AVE | R21122000064 | New_Event |  |  | Include | Wildlife | 22 | 2021-12-20 | 22 | keep | 0 | Dec | 2021 | 1.4984e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-20 18:36 | 2021-12-20 19:02 | 16 | 000:26 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA DESGANCHAR Y REPARAR SECUNDARIA | R21122000065 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 26 | 2021-12-20 | 416 | keep | 0 | Dec | 2021 | 0.00028334 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2021-12-20 18:45 | 2021-12-20 21:15 | 50 | 002:30 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S21122000101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 150 | 2021-12-20 | 7500 | keep | 0 | Dec | 2021 | 0.0051082 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-20 19:03 | 2021-12-20 21:10 | 1200 | 002:07 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO TRAMO SOTERRADO Y SE TRANSFIRIO LA CARGA AL 1716-03 LLEVA LA CARGA DEL 1711-03 | B21122000065 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 127 | 2021-12-20 | 152400 | keep | 0 | Dec | 2021 | 0.1038 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-12-20 19:18 | 2021-12-20 19:19 | 485 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21122000077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-20 | 485 | keep | 0 | Dec | 2021 | 0.00033033 | 0.00033033 | Momentary | FALSE | FALSE | Not_TMED_Event | 485
BAYAMON | 2021-12-20 19:31 | 2021-12-20 20:39 | 68 | 001:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 SE CERRO POR SCADA 1102-01 LLEVA 1102-04, 1102-05, 1105-04, 1105-05 | S21122000068 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 68 | 2021-12-20 | 4624 | keep | 0 | Dec | 2021 | 0.0031494 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
SAN JUAN | 2021-12-20 19:31 | 2021-12-20 20:10 | 171 | 000:39 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 LLEVA 1110-02 Y 1110-05 | S21122000068 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 39 | 2021-12-20 | 6669 | keep | 0 | Dec | 2021 | 0.0045422 | 0.00011647 | Sustained | FALSE | FALSE | Not_TMED_Event | 171
SAN JUAN | 2021-12-20 19:31 | 2021-12-20 20:10 | 1837 | 000:39 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 | S21122000068 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 39 | 2021-12-20 | 71643 | keep | 0 | Dec | 2021 | 0.048796 | 0.0012512 | Sustained | FALSE | FALSE | Not_TMED_Event | 1837
BAYAMON | 2021-12-20 19:31 | 2021-12-20 20:39 | 536 | 001:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 CARGA DEL 1102-04 POR 1102-01 | S21122000068 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 68 | 2021-12-20 | 36448 | keep | 0 | Dec | 2021 | 0.024825 | 0.00036507 | Sustained | FALSE | FALSE | Not_TMED_Event | 536
BAYAMON | 2021-12-20 19:31 | 2021-12-20 20:39 | 348 | 001:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 CARGA DEL 1102-05 POR 1102-01 | S21122000068 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 68 | 2021-12-20 | 23664 | keep | 0 | Dec | 2021 | 0.016117 | 0.00023702 | Sustained | FALSE | FALSE | Not_TMED_Event | 348
SAN JUAN | 2021-12-20 19:31 | 2021-12-20 20:10 | 455 | 000:39 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 CARGA DEL 1110-02 POR 1102-02 | S21122000105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 39 | 2021-12-20 | 17745 | keep | 0 | Dec | 2021 | 0.012086 | 0.0003099 | Sustained | FALSE | FALSE | Not_TMED_Event | 455
SAN JUAN | 2021-12-20 19:31 | 2021-12-20 20:10 | 283 | 000:39 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 CARGA DEL 1110-05 POR 1102-02 | S21122000105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 39 | 2021-12-20 | 11037 | keep | 0 | Dec | 2021 | 0.0075173 | 0.00019275 | Sustained | FALSE | FALSE | Not_TMED_Event | 283
BARRANQUITAS | 2021-12-20 19:32 | 2021-12-20 20:39 | 1 | 001:07 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | C21122000108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2021-12-20 | 67 | keep | 0 | Dec | 2021 | 4.5633e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-20 19:33 | 2021-12-21 09:52 | 6 | 014:19 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA INFORMA JOURNEYMAN NO IDENTIFICO CAUSA | M21122000084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 859 | 2021-12-20 | 5154 | keep | 0 | Dec | 2021 | 0.0035104 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2021-12-20 19:35 | 2021-12-20 20:31 | 1596 | 000:56 | P | DESGANCHE | SE SECCIONALIZO TRAMO CON BAMBUAS | C21122000094 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 56 | 2021-12-20 | 89376 | keep | 0 | Dec | 2021 | 0.060874 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-12-20 19:35 | 2021-12-20 20:31 | 1000 | 000:56 | P | DESGANCHE | SE SECCIONALIZARON BAMBUAS SOBRE LINEAS | C21122000095 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 56 | 2021-12-20 | 56000 | keep | 0 | Dec | 2021 | 0.038141 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-20 20:09 | 2021-12-20 20:14 | 36 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA CARGA POR 1620-04 POR BARRA DE INSPECCION | S21122000175 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-12-20 | 180 | keep | 0 | Dec | 2021 | 0.0001226 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-12-20 20:09 | 2021-12-20 20:14 | 172 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA LLEVA 1620-01 | S21122000175 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-12-20 | 860 | keep | 0 | Dec | 2021 | 0.00058574 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
BAYAMON | 2021-12-20 20:28 | 2021-12-20 20:30 | 1812 | 000:02 | T | CABLE SOTERRADO AVERIADO | EN TRANSFERENCIA DE CARGA INTERRUPTOR DISPARO SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL | B21122000000 | New_Event | UG Cable Fault | Include | Include | Equipment | 2 | 2021-12-20 | 3624 | keep | 0 | Dec | 2021 | 0.0024683 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
BARRANQUITAS | 2021-12-20 20:31 | 2021-12-20 23:32 | 2280 | 003:01 | T | BREAKER DEFECTUOSO O NO OPERA | INTERRUPTOR 9902-3 AVERIADO SE TRANSFIRIO POR BARRA DE INSPECCION AL 9902-01 | C21122000095 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 181 | 2021-12-20 | 412680 | keep | 0 | Dec | 2021 | 0.28107 | 0.0015529 | Sustained | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2021-12-20 20:31 | 2021-12-20 23:45 | 1617 | 003:14 | T | BREAKER DEFECTUOSO O NO OPERA | INTERRUPTOR 9902-3 AVERIADO SE TRANSFIRIO POR BARRA DE INSPECCION AL 9902-01 | C21122000095 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 194 | 2021-12-20 | 313698 | keep | 0 | Dec | 2021 | 0.21366 | 0.0011013 | Sustained | FALSE | FALSE | Not_TMED_Event | 1617
HUMACAO | 2021-12-20 20:37 | 2021-12-20 20:38 | 2126 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA | C21122000151 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-20 | 2126 | keep | 0 | Dec | 2021 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
SAN JUAN | 2021-12-20 20:38 | 2021-12-20 22:19 | 90 | 001:41 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21122000072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2021-12-20 | 9090 | keep | 0 | Dec | 2021 | 0.0061912 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2021-12-20 20:46 | 2021-12-20 22:23 | 50 | 001:37 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21122000197 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2021-12-20 | 4850 | keep | 0 | Dec | 2021 | 0.0033033 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-12-20 20:46 | 2021-12-20 23:21 | 85 | 002:35 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21122000197 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 155 | 2021-12-20 | 13175 | keep | 0 | Dec | 2021 | 0.0089734 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
CANOVANAS | 2021-12-20 20:46 | 2021-12-21 13:46 | 70 | 017:00 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 40 EN SU-5 Y 1 X 25 EN RISER REPARO TERMINACION EN T-96 | R21122000074 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1020 | 2021-12-20 | 71400 | keep | 0 | Dec | 2021 | 0.04863 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2021-12-20 20:48 | 2021-12-21 09:20 | 50 | 012:32 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21122000087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 752 | 2021-12-20 | 37600 | keep | 0 | Dec | 2021 | 0.025609 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-12-20 20:53 | 2021-12-21 11:01 | 40 | 014:08 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M21122000086 | New_Event | Bad Weather | Include | Include | Weather | 848 | 2021-12-20 | 33920 | keep | 0 | Dec | 2021 | 0.023103 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-12-20 21:01 | 2021-12-21 12:54 | 6 | 015:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C21122000158 | New_Event | Secondary Wire Down | Include | Include | Equipment | 953 | 2021-12-20 | 5718 | keep | 0 | Dec | 2021 | 0.0038945 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-12-20 21:23 | 2021-12-21 02:07 | 2302 | 004:44 | S | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO A LOCKOUT DE LA SUBESTACION CONTAMINACION DE LA BARRA DE DISTRIBUCION Y AISLADORES | C21122000000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 284 | 2021-12-20 | 653768 | keep | 0 | Dec | 2021 | 0.44528 | 0.0015679 | Sustained | FALSE | FALSE | Not_TMED_Event | 2302
CAGUAS | 2021-12-20 21:23 | 2021-12-21 02:07 | 1342 | 004:44 | S | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO A LOCKOUT DE LA SUBESTACION CONTAMINACION DE LA BARRA DE DISTRIBUCION Y AISLADORES | C21122000000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 284 | 2021-12-20 | 381128 | keep | 0 | Dec | 2021 | 0.25958 | 0.00091403 | Sustained | FALSE | FALSE | Not_TMED_Event | 1342
CAGUAS | 2021-12-20 21:23 | 2021-12-21 02:07 | 34 | 004:44 | S | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO A LOCKOUT DE LA SUBESTACION CONTAMINACION DE LA BARRA DE DISTRIBUCION Y AISLADORES | C21122000000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 284 | 2021-12-20 | 9656 | keep | 0 | Dec | 2021 | 0.0065767 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
CAGUAS | 2021-12-20 21:23 | 2021-12-21 00:26 | 1742 | 003:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO A LOCKOUT DE LA SUBESTACION CONTAMINACION DE LA BARRA DE DISTRIBUCION Y AISLADORES DE LA 3015 | C21122000000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 183 | 2021-12-20 | 318786 | keep | 0 | Dec | 2021 | 0.21712 | 0.0011865 | Sustained | FALSE | FALSE | Not_TMED_Event | 1742
AGUADILLA | 2021-12-20 22:32 | 2021-12-21 10:37 | 6 | 012:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | M21122000091 | New_Event | Wire Down | Include | Include | Equipment | 725 | 2021-12-20 | 4350 | keep | 0 | Dec | 2021 | 0.0029628 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2021-12-20 22:43 | 2021-12-21 10:54 | 30 | 012:11 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21122000144 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 731 | 2021-12-20 | 21930 | keep | 0 | Dec | 2021 | 0.014936 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2021-12-20 22:50 | 2021-12-21 18:01 | 20 | 019:11 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 37.5 KVA X 37.5 KVA | M21122000093 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1151 | 2021-12-20 | 23020 | keep | 0 | Dec | 2021 | 0.015679 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-12-20 23:07 | 2021-12-20 23:08 | 1681 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-01 CARGA POR 1303-04 | S21122000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-20 | 1681 | keep | 0 | Dec | 2021 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-12-20 23:07 | 2021-12-20 23:08 | 1598 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1346-06 CARGA POR 1303-04 | S21122000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-20 | 1598 | keep | 0 | Dec | 2021 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2021-12-20 23:21 | 2021-12-20 23:22 | 1681 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-01 CARGA POR 1303-04 | S21122000000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-20 | 1681 | keep | 0 | Dec | 2021 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-12-20 23:21 | 2021-12-20 23:22 | 1598 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1346-06 CARGA POR 1303-04 | S21122000000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-20 | 1598 | keep | 0 | Dec | 2021 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2021-12-21 00:18 | 2021-12-21 01:02 | 1681 | 000:44 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-04 LLEVANDO 1303-01 SE SECCIONALIZO EN CARR 176 SECTOR LOS GUANOS Y SE CERRO POR SCADA. ENTRA UN 75% | S21121000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 44 | 2021-12-21 | 73964 | keep | 0 | Dec | 2021 | 0.050377 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-12-21 00:18 | 2021-12-21 01:02 | 1598 | 000:44 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-04 LLEVANDO LA CARGA DEL 1346-06. SE SECCIONALIZO SECTOR LOS GUANOS CORRIDA DEL 1303-01 Y SE CERRO INTERRUPTOR. ENTRA 100% EL 1346-06 | S21121000001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 44 | 2021-12-21 | 70312 | keep | 0 | Dec | 2021 | 0.047889 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2021-12-21 01:02 | 2021-12-21 08:23 | 421 | 007:21 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETES PERO DISPARO | S21122100001 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 441 | 2021-12-21 | 185661 | keep | 0 | Dec | 2021 | 0.12645 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-12-21 01:02 | 2021-12-21 03:54 | 2926 | 002:52 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 9202-04 SE REALIZARON OPERACIONES DE CAMPO Y SE SECCIONALIZO ALIMETADOR Y SE CERRO POR SCADA. ENTRA UN 70% | B21122100009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 172 | 2021-12-21 | 503272 | keep | 0 | Dec | 2021 | 0.34278 | 0.0019929 | Sustained | FALSE | FALSE | Not_TMED_Event | 2926
CANOVANAS | 2021-12-21 01:17 | 2021-12-21 12:04 | 75 | 010:47 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN CORTES DE LINEAS | R21122100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 647 | 2021-12-21 | 48525 | keep | 0 | Dec | 2021 | 0.03305 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2021-12-21 01:32 | 2021-12-21 01:33 | 2450 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C21122100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-21 | 2450 | keep | 0 | Dec | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
BAYAMON | 2021-12-21 02:35 | 2021-12-21 02:36 | 1834 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | B21122100000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-12-21 | 1834 | keep | 0 | Dec | 2021 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BAYAMON | 2021-12-21 02:36 | 2021-12-21 13:09 | 1 | 010:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO | B21122100028 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 633 | 2021-12-21 | 633 | keep | 0 | Dec | 2021 | 0.00043113 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-12-21 03:54 | 2021-12-21 06:21 | 870 | 002:27 | P | NO SE REPORTO CAUSA | SE CERRO MACHETES EN CARRETERA 693 FRENTE A URBANIZACION QUINTAS DE DORADO 100% EN SERVICIO. NO SE ENCONTRO CAUSA | B21122100009 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 147 | 2021-12-21 | 127890 | keep | 0 | Dec | 2021 | 0.087105 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-12-21 04:04 | 2021-12-21 11:52 | 10 | 007:48 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B21122100015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 468 | 2021-12-21 | 4680 | keep | 0 | Dec | 2021 | 0.0031875 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-21 04:15 | 2021-12-21 10:14 | 60 | 005:59 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | B21122100016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 359 | 2021-12-21 | 21540 | keep | 0 | Dec | 2021 | 0.014671 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2021-12-21 04:21 | 2021-12-21 04:22 | 293 | 000:01 | T | DESGANCHE | RECIERRE | C21122100011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-21 | 293 | keep | 0 | Dec | 2021 | 0.00019956 | 0.00019956 | Momentary | FALSE | FALSE | Not_TMED_Event | 293
CAGUAS | 2021-12-21 04:22 | 2021-12-21 18:12 | 100 | 013:50 | P | DESGANCHE | 2 X 65 C/L | C21122100013 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 830 | 2021-12-21 | 83000 | keep | 0 | Dec | 2021 | 0.056531 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-12-21 04:34 | 2021-12-21 11:19 | 50 | 006:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA EN PROVISIONAL | S21122100022 | New_Event | Cutout Failure | Include | Include | Equipment | 405 | 2021-12-21 | 20250 | keep | 0 | Dec | 2021 | 0.013792 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-12-21 05:41 | 2021-12-21 10:02 | 15 | 004:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M21122100004 | New_Event | Bad Weather | Include | Include | Weather | 261 | 2021-12-21 | 3915 | keep | 0 | Dec | 2021 | 0.0026665 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-12-21 06:04 | 2021-12-21 10:05 | 80 | 004:01 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN C/L'S | C21122100019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2021-12-21 | 19280 | keep | 0 | Dec | 2021 | 0.013132 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-12-21 06:06 | 2021-12-21 15:29 | 16 | 009:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN TRANSFORMADOR SE CERRO PUENTE | S21122100025 | New_Event | Wire Down | Include | Include | Equipment | 563 | 2021-12-21 | 9008 | keep | 0 | Dec | 2021 | 0.0061353 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2021-12-21 06:27 | 2021-12-21 06:28 | 418 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S21122100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-21 | 418 | keep | 0 | Dec | 2021 | 0.0002847 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
SAN JUAN | 2021-12-21 07:03 | 2021-12-21 07:04 | 2000 | 000:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO NO RECERRO 1619-02 LLEVANDO PARTE DE LA CARGA 1336-06 | R21122100000 | New_Event |  |  | Include | Wildlife | 1 | 2021-12-21 | 2000 | keep | 0 | Dec | 2021 | 0.0013622 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
SAN JUAN | 2021-12-21 07:04 | 2021-12-21 09:23 | 20 | 002:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA SE RETIRO TAPA DE ALUMBRADO HACIENDO CONTACTO CON PROVISIONAL AEREO Y SE REMPLAZO CAJA PRIMARIA | R21122100005 | 1st_after_momentary |  |  | Include | Wildlife | 139 | 2021-12-21 | 2780 | keep | 0 | Dec | 2021 | 0.0018934 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-12-21 07:15 | 2021-12-21 07:16 | 2076 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR 1718-03 LLEVANDO 40% DEL 1710-05 | B21122100000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-12-21 | 2076 | keep | 0 | Dec | 2021 | 0.001414 | 0.001414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2076
BAYAMON | 2021-12-21 07:15 | 2021-12-21 07:16 | 2605 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR 1718-03 LLEVANDO 40% DEL 1710-05 | B21122100000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-12-21 | 2605 | keep | 0 | Dec | 2021 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2021-12-21 07:16 | 2021-12-21 16:17 | 4 | 009:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CONDUCTOR PARTIDO. RELACIONADO AL GOI-BY211221-03 | B21122100027 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 541 | 2021-12-21 | 2164 | keep | 0 | Dec | 2021 | 0.0014739 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2021-12-21 07:35 | 2021-12-21 15:09 | 100 | 007:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN C/L CRUCE POR AVE | C21122100024 | New_Event |  |  | Include | Wildlife | 454 | 2021-12-21 | 45400 | keep | 0 | Dec | 2021 | 0.030922 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2021-12-21 07:39 | 2021-12-21 07:40 | 2635 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO LLEVA LA CARGA DEL 9902-02 Y 03 | C21122100089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-21 | 2635 | keep | 0 | Dec | 2021 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2021-12-21 07:39 | 2021-12-21 07:40 | 2280 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL 9902-01 | C21122100089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-21 | 2280 | keep | 0 | Dec | 2021 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2021-12-21 07:39 | 2021-12-21 07:40 | 1617 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL 9902-01 | C21122100089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-21 | 1617 | keep | 0 | Dec | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
SAN JUAN | 2021-12-21 07:42 | 2021-12-21 07:43 | 1026 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21122100006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-21 | 1026 | keep | 0 | Dec | 2021 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
SAN JUAN | 2021-12-21 07:44 | 2021-12-21 12:05 | 6 | 004:21 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE DESGANCHO Y SE REPARO SECUNDARIA | S21122100017 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 261 | 2021-12-21 | 1566 | keep | 0 | Dec | 2021 | 0.0010666 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-12-21 07:51 | 2021-12-21 22:17 | 80 | 014:26 | P | ESTRUCTURA AVERIADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO POSTE PARTIDO | C21122100027 | New_Event | Defective Pole | Include | Include | Equipment | 866 | 2021-12-21 | 69280 | keep | 0 | Dec | 2021 | 0.047186 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-12-21 07:52 | 2021-12-21 10:39 | 514 | 002:47 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO 2 MACHETES Y SE CERRO 10% EN SERVICIO SU CARGA POR 1118-10 | S21122100038 | New_Event | Switch Failure | Include | Include | Equipment | 167 | 2021-12-21 | 85838 | keep | 0 | Dec | 2021 | 0.058464 | 0.00035008 | Sustained | FALSE | FALSE | Not_TMED_Event | 514
SAN JUAN | 2021-12-21 07:52 | 2021-12-21 10:32 | 2782 | 002:40 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR SE ABRIO MACHETE N/O CONTRA EL 1111-01 Y SE CERRO INTERRUPTOR POR SCADA QUEDO FUERA EL 20% DEL 1111-01 | S21122100038 | New_Event | Switch Failure | Include | Include | Equipment | 160 | 2021-12-21 | 445120 | keep | 0 | Dec | 2021 | 0.30317 | 0.0018948 | Sustained | FALSE | FALSE | Not_TMED_Event | 2782
BAYAMON | 2021-12-21 08:22 | 2021-12-21 08:23 | 317 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21122100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-21 | 317 | keep | 0 | Dec | 2021 | 0.00021591 | 0.00021591 | Momentary | FALSE | FALSE | Not_TMED_Event | 317
SAN JUAN | 2021-12-21 08:23 | 2021-12-21 08:24 | 1681 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-04 LLEVANDO 1303-01 SE SECCIONALIZO EN CARR 176 SECTOR LOS GUANOS Y SE CERRO POR SCADA. ENTRA UN 75% | S21121000001 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-21 | 1681 | keep | 0 | Dec | 2021 | 0.0011449 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-21 08:23 | 2021-12-21 08:24 | 1598 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-04 LLEVANDO LA CARGA DEL 1346-06. SE SECCIONALIZO SECTOR LOS GUANOS CORRIDA DEL 1303-01 Y SE CERRO INTERRUPTOR. ENTRA 100% EL 1346-06 | S21121000001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-21 | 1598 | keep | 0 | Dec | 2021 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2021-12-21 08:24 | 2021-12-21 08:34 | 421 | 000:10 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETES | S21122100001 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 10 | 2021-12-21 | 4210 | keep | 0 | Dec | 2021 | 0.0028674 | 0.00028674 | Sustained | FALSE | FALSE | Not_TMED_Event | 421
MAYAGÃœEZ | 2021-12-21 08:32 | 2021-12-21 11:50 | 4 | 003:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M21122100011 | New_Event | Wire Down | Include | Include | Equipment | 198 | 2021-12-21 | 792 | keep | 0 | Dec | 2021 | 0.00053943 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-12-21 08:34 | 2021-12-21 08:35 | 418 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S21122100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-21 | 418 | keep | 0 | Dec | 2021 | 0.0002847 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
ARECIBO | 2021-12-21 08:39 | 2021-12-21 17:36 | 12 | 008:57 | P | OTRAS CAUSAS | 1 X 10 EN TRANSFORMADOR POR CONTAMINACION DE SALITRE | A21122100005 | New_Event | Other Causes | Include | Include | Other | 537 | 2021-12-21 | 6444 | keep | 0 | Dec | 2021 | 0.004389 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-12-21 08:43 | 2021-12-21 08:44 | 199 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S21122100060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-21 | 199 | keep | 0 | Dec | 2021 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2021-12-21 08:46 | 2021-12-21 10:29 | 50 | 001:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | A21122100006 | New_Event |  |  | Include | Wildlife | 103 | 2021-12-21 | 5150 | keep | 0 | Dec | 2021 | 0.0035076 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2021-12-21 08:59 | 2021-12-21 11:42 | 1 | 002:43 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER @ PM LIBERTY | R21122100011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 163 | 2021-12-21 | 163 | keep | 0 | Dec | 2021 | 0.00011102 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-21 09:04 | 2021-12-21 11:43 | 80 | 002:39 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA Y 2 X 25 EN SU-A | R21122100012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 159 | 2021-12-21 | 12720 | keep | 0 | Dec | 2021 | 0.0086635 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-12-21 09:16 | 2021-12-22 12:24 | 1 | 027:08 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU-1 | S21122100073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1628 | 2021-12-21 | 1628 | keep | 0 | Dec | 2021 | 0.0011088 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-21 09:23 | 2021-12-21 09:24 | 2000 | 000:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO NO RECERRO 1619-02 LLEVANDO PARTE DE LA CARGA 1336-06 | R21122100000 | Additional_clients |  |  | Include | Wildlife | 1 | 2021-12-21 | 2000 | keep | 0 | Dec | 2021 | 0.0013622 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-21 09:24 | 2021-12-21 15:14 | 20 | 005:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA SE RETIRO TAPA DE ALUMBRADO HACIENDO CONTACTO CON PROVISIONAL AEREO Y SE REMPLAZO CAJA PRIMARIA | R21122100005 | 1st_after_momentary |  |  | Include | Wildlife | 350 | 2021-12-21 | 7000 | keep | 0 | Dec | 2021 | 0.0047677 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-12-21 09:24 | 2021-12-21 17:01 | 52 | 007:37 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU 1 Y 1 X 40 EN SU 2 | R21122100017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 457 | 2021-12-21 | 23764 | keep | 0 | Dec | 2021 | 0.016186 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
MAYAGÃœEZ | 2021-12-21 09:25 | 2021-12-21 14:26 | 12 | 005:01 | P | HERRAJE ROTO O PODRIDO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZO DE CRUCETA PARTIDA | M21122100006 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 301 | 2021-12-21 | 3612 | keep | 0 | Dec | 2021 | 0.0024601 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-12-21 09:27 | 2021-12-21 14:22 | 30 | 004:55 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR QUEMADO DE 50 KVA X 50 KVA | C21122100061 | New_Event | Service Transformer Failure | Include | Include | Equipment | 295 | 2021-12-21 | 8850 | keep | 0 | Dec | 2021 | 0.0060277 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2021-12-21 09:35 | 2021-12-21 09:36 | 1494 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA LA CARGA DEL 9101-04 | B21122100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-21 | 1494 | keep | 0 | Dec | 2021 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
BAYAMON | 2021-12-21 09:35 | 2021-12-21 23:10 | 25 | 013:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA Y SE REEMPLAZO CAJA QUEMADA | B21122100266 | New_Event | Cutout Failure | Include | Include | Equipment | 815 | 2021-12-21 | 20375 | keep | 0 | Dec | 2021 | 0.013877 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-12-21 09:50 | 2021-12-21 09:54 | 315 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B21122100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-12-21 | 1260 | keep | 0 | Dec | 2021 | 0.00085818 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
BAYAMON | 2021-12-21 09:55 | 2021-12-21 14:30 | 30 | 004:35 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN C/L. SE REEMPLAZARON DOS PARARRAYOS | B21122100041 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 275 | 2021-12-21 | 8250 | keep | 0 | Dec | 2021 | 0.005619 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2021-12-21 10:03 | 2021-12-21 11:49 | 10 | 001:46 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 25 KVA X 25 KVA | C21122100062 | New_Event | Service Transformer Failure | Include | Include | Equipment | 106 | 2021-12-21 | 1060 | keep | 0 | Dec | 2021 | 0.00072196 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-21 10:04 | 2021-12-21 12:00 | 20 | 001:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PM PARA REMPLAZAR BARRAS SECUNDARIAS | A21122100014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 116 | 2021-12-21 | 2320 | keep | 0 | Dec | 2021 | 0.0015801 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-12-21 10:07 | 2021-12-21 18:34 | 50 | 008:27 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA Y 2 X 40 EN RISER | S21122100091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 507 | 2021-12-21 | 25350 | keep | 0 | Dec | 2021 | 0.017266 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-21 10:12 | 2021-12-21 12:42 | 10 | 002:30 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21122100045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 150 | 2021-12-21 | 1500 | keep | 0 | Dec | 2021 | 0.0010216 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-21 10:15 | 2021-12-21 17:54 | 150 | 007:39 | P | DESGANCHE | 2 X 65 EN C/L | C21122100066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 459 | 2021-12-21 | 68850 | keep | 0 | Dec | 2021 | 0.046893 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2021-12-21 10:20 | 2021-12-21 10:23 | 4702 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA TRANSFERIDA LA CARGA DEL 9105-07 | B21122100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-12-21 | 14106 | keep | 0 | Dec | 2021 | 0.0096075 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2021-12-21 10:20 | 2021-12-21 10:23 | 215 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA TRANSFERIDA AL 9004-10 | B21122100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-12-21 | 645 | keep | 0 | Dec | 2021 | 0.00043931 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
CAGUAS | 2021-12-21 10:26 | 2021-12-21 13:03 | 50 | 002:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN RISER MAL TIEMPO | C21122100071 | New_Event | Bad Weather | Include | Include | Weather | 157 | 2021-12-21 | 7850 | keep | 0 | Dec | 2021 | 0.0053466 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-12-21 10:28 | 2021-12-21 12:50 | 40 | 002:22 | P | DESGANCHE | 1 X 40 EN C/L | C21122100073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2021-12-21 | 5680 | keep | 0 | Dec | 2021 | 0.0038686 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-12-21 10:39 | 2021-12-21 14:05 | 256 | 003:26 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO 2 MACHETES Y SE CERRO 20% EN SERVICIO SU CARGA POR 1118-10 | S21122100038 | New_Event | Switch Failure | Include | Include | Equipment | 206 | 2021-12-21 | 52736 | keep | 0 | Dec | 2021 | 0.035918 | 0.00017436 | Sustained | FALSE | FALSE | Not_TMED_Event | 256
HUMACAO | 2021-12-21 10:43 | 2021-12-21 14:31 | 15 | 003:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L C RUCE X AVE | C21122100080 | New_Event |  |  | Include | Wildlife | 228 | 2021-12-21 | 3420 | keep | 0 | Dec | 2021 | 0.0023293 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-12-21 10:53 | 2021-12-21 16:30 | 40 | 005:37 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B21122100099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 337 | 2021-12-21 | 13480 | keep | 0 | Dec | 2021 | 0.0091812 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2021-12-21 10:55 | 2021-12-21 16:01 | 8 | 005:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR BARRAS DE PEDESTAL | C21122100084 | New_Event | Secondary Wire Down | Include | Include | Equipment | 306 | 2021-12-21 | 2448 | keep | 0 | Dec | 2021 | 0.0016673 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-12-21 10:55 | 2021-12-21 16:41 | 10 | 005:46 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 50 X 50 KVA | B21122100050 | New_Event | Service Transformer Failure | Include | Include | Equipment | 346 | 2021-12-21 | 3460 | keep | 0 | Dec | 2021 | 0.0023566 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-12-21 11:07 | 2021-12-21 12:21 | 5 | 001:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C21122100086 | New_Event | Secondary Wire Down | Include | Include | Equipment | 74 | 2021-12-21 | 370 | keep | 0 | Dec | 2021 | 0.00025201 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-12-21 11:15 | 2021-12-21 11:16 | 1860 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S21122100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-21 | 1860 | keep | 0 | Dec | 2021 | 0.0012668 | 0.0012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 1860
SAN JUAN | 2021-12-21 11:19 | 2021-12-21 12:26 | 1964 | 001:07 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO 1106-04 AL PERSONAL HACER PRUEBA EN PROVISIONAL LLEVA 60% DEL 1110-03 | S21122100000 | New_Event | Cutout Failure | Include | Include | Equipment | 67 | 2021-12-21 | 131588 | keep | 0 | Dec | 2021 | 0.089624 | 0.0013377 | Sustained | FALSE | FALSE | Not_TMED_Event | 1964
SAN JUAN | 2021-12-21 11:19 | 2021-12-21 12:26 | 916 | 001:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO 1106-04 AL PERSONAL HACER PRUEBA EN PROVISIONAL LLEVA 60% DEL 1110-03 | S21122100000 | New_Event | Cutout Failure | Include | Include | Equipment | 67 | 2021-12-21 | 61372 | keep | 0 | Dec | 2021 | 0.0418 | 0.00062388 | Sustained | FALSE | FALSE | Not_TMED_Event | 916
FAJARDO | 2021-12-21 11:39 | 2021-12-21 11:40 | 76 | 000:01 | T | DESGANCHE | RECIERRE | R21122100028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-21 | 76 | keep | 0 | Dec | 2021 | 5.1763e-05 | 5.1763e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 76
BAYAMON | 2021-12-21 11:40 | 2021-12-21 11:41 | 222 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR 1907-03 LLEVANDO 1909-09 | S21122100000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2021-12-21 | 222 | keep | 0 | Dec | 2021 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2021-12-21 11:40 | 2021-12-21 11:41 | 4456 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR 1907-03 LLEVANDO 1909-09 | S21122100000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2021-12-21 | 4456 | keep | 0 | Dec | 2021 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
FAJARDO | 2021-12-21 11:40 | 2021-12-21 12:34 | 30 | 000:54 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21122100029 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 54 | 2021-12-21 | 1620 | keep | 0 | Dec | 2021 | 0.0011034 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-21 11:41 | 2021-12-21 17:34 | 150 | 005:53 | P | DESCONECTIVO DEFECTUOSO | MACHETE QUEMADO DEL 1907-03. LLEVANDO LA CARGA DEL 1909-09 | S21122100000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 353 | 2021-12-21 | 52950 | keep | 0 | Dec | 2021 | 0.036064 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2021-12-21 11:41 | 2021-12-21 17:34 | 2500 | 005:53 | P | DESCONECTIVO DEFECTUOSO | MACHETE QUEMADO DEL 1907-03. CARGAR POR EL 1907-03 | S21122100000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 353 | 2021-12-21 | 882500 | keep | 0 | Dec | 2021 | 0.60107 | 0.0017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 2500
SAN JUAN | 2021-12-21 12:26 | 2021-12-21 12:37 | 50 | 000:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA EN PROVISIONAL | S21122100022 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 11 | 2021-12-21 | 550 | keep | 0 | Dec | 2021 | 0.0003746 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-12-21 12:30 | 2021-12-21 12:31 | 4381 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR BAJANTE DE LINEA A MACHETE ZAFADO | M21122100019 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-12-21 | 4381 | keep | 0 | Dec | 2021 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
MAYAGÃœEZ | 2021-12-21 12:31 | 2021-12-21 18:38 | 500 | 006:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE LINEA A MACHETE | M21122100029 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 367 | 2021-12-21 | 183500 | keep | 0 | Dec | 2021 | 0.12498 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2021-12-21 13:18 | 2021-12-21 13:20 | 1200 | 000:02 | P | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR 1716-03 LLEVANDO 80% 1711-01 Y 100%1711-03 | B21122100000 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2021-12-21 | 2400 | keep | 0 | Dec | 2021 | 0.0016346 | 0.00081731 | Momentary | FALSE | FALSE | Not_TMED_Event | 1200
BAYAMON | 2021-12-21 13:18 | 2021-12-21 13:20 | 13 | 000:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR 1716-03 LLEVANDO 80% 1711-01 Y 100%1711-03 | B21122100000 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2021-12-21 | 26 | keep | 0 | Dec | 2021 | 1.7708e-05 | 8.8542e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2021-12-21 13:18 | 2021-12-21 13:20 | 1812 | 000:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR 1716-03 LLEVANDO 80% 1711-01 Y 100%1711-03 | B21122100000 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2021-12-21 | 3624 | keep | 0 | Dec | 2021 | 0.0024683 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
BAYAMON | 2021-12-21 13:20 | 2021-12-21 18:57 | 500 | 005:37 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE AVERIADO EN VIVO | B21122100057 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 337 | 2021-12-21 | 168500 | keep | 0 | Dec | 2021 | 0.11476 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
ARECIBO | 2021-12-21 13:34 | 2021-12-21 13:47 | 4 | 000:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21122100022 | New_Event | Bad Weather | Include | Include | Weather | 13 | 2021-12-21 | 52 | keep | 0 | Dec | 2021 | 3.5417e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2021-12-21 13:57 | 2021-12-21 16:05 | 10 | 002:08 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA BAJAR TAPS REALIZAR DESGANCHE Y REMPLAZAR TOMA | R21122100030 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 128 | 2021-12-21 | 1280 | keep | 0 | Dec | 2021 | 0.0008718 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-21 14:00 | 2021-12-21 16:29 | 4 | 002:29 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR ROTO | A21122100023 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 149 | 2021-12-21 | 596 | keep | 0 | Dec | 2021 | 0.00040593 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2021-12-21 14:37 | 2021-12-21 15:08 | 16 | 000:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CONTRATISTA REALIZANDO EXCAVACION CRUZO SECUNDARIA | P21122100014 | New_Event |  |  | Include | Wildlife | 31 | 2021-12-21 | 496 | keep | 0 | Dec | 2021 | 0.00033782 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2021-12-21 14:38 | 2021-12-21 14:53 | 1 | 000:15 | P | NO SE REPORTO CAUSA | 1 SMU 20 DE 80 AMPS NO CAUSA | C21122100041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2021-12-21 | 15 | keep | 0 | Dec | 2021 | 1.0216e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-21 14:44 | 2021-12-21 14:45 | 2713 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21122100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-21 | 2713 | keep | 0 | Dec | 2021 | 0.0018478 | 0.0018478 | Momentary | FALSE | FALSE | Not_TMED_Event | 2713
FAJARDO | 2021-12-21 15:07 | 2021-12-21 15:12 | 4098 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DAGUAO | R21122100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2021-12-21 | 20490 | keep | 0 | Dec | 2021 | 0.013956 | 0.0027911 | Momentary | FALSE | FALSE | Not_TMED_Event | 4098
FAJARDO | 2021-12-21 15:07 | 2021-12-21 15:12 | 956 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DAGUAO | R21122100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2021-12-21 | 4780 | keep | 0 | Dec | 2021 | 0.0032556 | 0.00065113 | Momentary | FALSE | FALSE | Not_TMED_Event | 956
FAJARDO | 2021-12-21 15:07 | 2021-12-21 15:12 | 1839 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DAGUAO | R21122100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2021-12-21 | 9195 | keep | 0 | Dec | 2021 | 0.0062627 | 0.0012525 | Momentary | FALSE | FALSE | Not_TMED_Event | 1839
FAJARDO | 2021-12-21 15:07 | 2021-12-21 15:12 | 1778 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DAGUAO | R21122100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2021-12-21 | 8890 | keep | 0 | Dec | 2021 | 0.0060549 | 0.001211 | Momentary | FALSE | FALSE | Not_TMED_Event | 1778
FAJARDO | 2021-12-21 15:07 | 2021-12-21 15:12 | 1376 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DAGUAO | R21122100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2021-12-21 | 6880 | keep | 0 | Dec | 2021 | 0.0046859 | 0.00093719 | Momentary | FALSE | FALSE | Not_TMED_Event | 1376
FAJARDO | 2021-12-21 15:07 | 2021-12-21 15:12 | 293 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DAGUAO | R21122100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2021-12-21 | 1465 | keep | 0 | Dec | 2021 | 0.0009978 | 0.00019956 | Momentary | FALSE | FALSE | Not_TMED_Event | 293
FAJARDO | 2021-12-21 15:07 | 2021-12-21 15:12 | 1215 | 000:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DAGUAO | R21122100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2021-12-21 | 6075 | keep | 0 | Dec | 2021 | 0.0041377 | 0.00082753 | Momentary | FALSE | FALSE | Not_TMED_Event | 1215
BAYAMON | 2021-12-21 15:20 | 2021-12-22 11:30 | 70 | 020:10 | P | ERROR HUMANO | SE CERRO MACHETES EN CARRETERA 2 MARGINAL COVADONGA SE QUEDARON ABIERTOS AL REALIZAR OPERACIONES BAJO SWITCHING FORM BY-211221-03 | B21122100034 | New_Event | Human Error | Include | Include | Other | 1210 | 2021-12-21 | 84700 | keep | 0 | Dec | 2021 | 0.057689 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2021-12-21 15:21 | 2021-12-21 15:38 | 30 | 000:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN C/L MAL TIEMPO | C21122100091 | New_Event | Bad Weather | Include | Include | Weather | 17 | 2021-12-21 | 510 | keep | 0 | Dec | 2021 | 0.00034736 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-12-21 15:27 | 2021-12-21 18:57 | 10 | 003:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 37.5 KVA | S21122100106 | New_Event | Service Transformer Failure | Include | Include | Equipment | 210 | 2021-12-21 | 2100 | keep | 0 | Dec | 2021 | 0.0014303 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-12-21 15:29 | 2021-12-21 17:34 | 8 | 002:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARA LINEA SECUNDARIA | P21122100015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 125 | 2021-12-21 | 1000 | keep | 0 | Dec | 2021 | 0.0006811 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-12-21 15:30 | 2021-12-21 16:17 | 2076 | 000:47 | P | ERROR HUMANO | SE CERRO MACHETES EN CARRETRA 863 ESQUINA 2 QUE AL REALIZAR OPERACIONES EN SWITCHING FORM BY-211221-03 NO SE CERRARON | B21122100040 | New_Event | Human Error | Include | Include | Other | 47 | 2021-12-21 | 97572 | keep | 0 | Dec | 2021 | 0.066456 | 0.001414 | Sustained | FALSE | FALSE | Not_TMED_Event | 2076
CAGUAS | 2021-12-21 16:04 | 2021-12-21 16:17 | 1 | 000:13 | P | DESGANCHE | 1 X 100 EN C/L | C21122100092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 13 | 2021-12-21 | 13 | keep | 0 | Dec | 2021 | 8.8542e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-21 16:10 | 2021-12-21 16:17 | 1633 | 000:07 | T | ERROR HUMANO | SE ABRIO INTERRUPTOR 1703-01 ERRONEAMENTE PARA ESTABLECER GOI POR CONDUCTOR EN EL SUELO A PETICION DE PEDRO VEGA PERO ERA EL 1718-03. LLEVANDO CARGA PARCIAL DEL 1703-05. | B21122100000 | New_Event | Human Error | Include | Include | Other | 7 | 2021-12-21 | 11431 | keep | 0 | Dec | 2021 | 0.0077856 | 0.0011122 | Sustained | FALSE | FALSE | Not_TMED_Event | 1633
BAYAMON | 2021-12-21 16:10 | 2021-12-21 16:17 | 30 | 000:07 | P | ERROR HUMANO | SE ABRIO INTERRUPTOR 1703-01 ERRONEAMENTE PARA ESTABLECER GOI POR CONDUCTOR EN EL SUELO A PETICION DE PEDRO VEGA PERO ERA EL 1718-03. LLEVANDO CARGA PARCIAL DEL 1703-05. | B21122100000 | New_Event | Human Error | Include | Include | Other | 7 | 2021-12-21 | 210 | keep | 0 | Dec | 2021 | 0.00014303 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-21 16:10 | 2021-12-21 17:20 | 6 | 001:10 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BARRAS SECUNDARIAS SOTERRADAS | A21122100024 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 70 | 2021-12-21 | 420 | keep | 0 | Dec | 2021 | 0.00028606 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-12-21 16:17 | 2021-12-21 23:26 | 2076 | 007:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1718-03 PARA LEVANTAR LINEA PRIMARIA. ADEMAS LLEVA EL 40% DEL 1710-05. RELACIONADO AL GOI-BY211221-03 | B21122100069 | New_Event | Wire Down | Include | Include | Equipment | 429 | 2021-12-21 | 890604 | keep | 0 | Dec | 2021 | 0.60659 | 0.001414 | Sustained | FALSE | FALSE | Not_TMED_Event | 2076
BAYAMON | 2021-12-21 16:17 | 2021-12-21 23:26 | 2605 | 007:09 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA LEVANTAR LINEA PRIMARIA. ADEMAS LLEVA EL 40% DEL 1710-05. RELACIONADO AL GOI-BY211221-03 | B21122100069 | New_Event | Wire Down | Include | Include | Equipment | 429 | 2021-12-21 | 1117545 | keep | 0 | Dec | 2021 | 0.76115 | 0.0017743 | Sustained | FALSE | FALSE | Not_TMED_Event | 2605
AGUADILLA | 2021-12-21 16:25 | 2021-12-21 16:35 | 1192 | 000:10 | T | TRANSFORMADOR AVERIADO | SE ABRIO INTERRUPTOR DE EMERGENCIA POR CONVERTIDOR BOTANDO HUMO Y ACEITE | M21122100027 | New_Event | Service Transformer Failure | Include | Include | Equipment | 10 | 2021-12-21 | 11920 | keep | 0 | Dec | 2021 | 0.0081187 | 0.00081187 | Sustained | FALSE | FALSE | Not_TMED_Event | 1192
PONCE | 2021-12-21 16:29 | 2021-12-21 16:43 | 1 | 000:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA EN CORTE DE LINEA | P21122100016 | New_Event | Cutout Failure | Include | Include | Equipment | 14 | 2021-12-21 | 14 | keep | 0 | Dec | 2021 | 9.5353e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-12-21 16:35 | 2021-12-21 18:15 | 80 | 001:40 | P | TRANSFORMADOR AVERIADO | SE SECCIONALIZO ALIMENTADOR Y SE CERRO N/O CON 7101-03 | M21122100056 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 100 | 2021-12-21 | 8000 | keep | 0 | Dec | 2021 | 0.0054488 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-12-21 16:35 | 2021-12-22 08:03 | 299 | 015:28 | P | TRANSFORMADOR AVERIADO | CONVERTIDOR AVERIADO SE ABRIO INTERRUPTOR PARA REMPLAZARLO | M21122100028 | New_Event | Service Transformer Failure | Include | Include | Equipment | 928 | 2021-12-21 | 277472 | keep | 0 | Dec | 2021 | 0.18898 | 0.00020365 | Sustained | FALSE | FALSE | Not_TMED_Event | 299
AGUADILLA | 2021-12-21 16:35 | 2021-12-21 17:48 | 299 | 001:13 | P | TRANSFORMADOR AVERIADO | 1 X 140 EN CORTE DE LINEA CONVERTIDOR AVERIADO | M21122100050 | New_Event | Service Transformer Failure | Include | Include | Equipment | 73 | 2021-12-21 | 21827 | keep | 0 | Dec | 2021 | 0.014866 | 0.00020365 | Sustained | FALSE | FALSE | Not_TMED_Event | 299
SAN JUAN | 2021-12-21 16:50 | 2021-12-21 17:48 | 12 | 000:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE T-17 PARA REMPLAZO BARRA PEDESTAL | S21122000025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 58 | 2021-12-21 | 696 | keep | 0 | Dec | 2021 | 0.00047404 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2021-12-21 16:50 | 2021-12-21 17:23 | 2 | 000:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | M21122100030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 33 | 2021-12-21 | 66 | keep | 0 | Dec | 2021 | 4.4952e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2021-12-21 17:09 | 2021-12-21 19:10 | 3438 | 002:01 | T | ERROR HUMANO | PERSONAL EN OPERACIONES PARA ESTABLECER GOI BY-211221-03 EN EL 1718-03, ABRIO INCORRECTAMENTE RISER DEL 1718-02 EN VEZ DEL 1718-03. | B21122100000 | New_Event | Human Error | Include | Include | Other | 121 | 2021-12-21 | 415998 | keep | 0 | Dec | 2021 | 0.28333 | 0.0023416 | Sustained | FALSE | FALSE | Not_TMED_Event | 3438
CAGUAS | 2021-12-21 17:19 | 2021-12-21 17:22 | 2178 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO | C21122100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-12-21 | 6534 | keep | 0 | Dec | 2021 | 0.0044503 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
CAGUAS | 2021-12-21 17:22 | 2021-12-21 19:31 | 40 | 002:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN C/L SECCIONALIZO CONDUCTOR EN EL SUELO | C21122100095 | New_Event | Wire Down | Include | Include | Equipment | 129 | 2021-12-21 | 5160 | keep | 0 | Dec | 2021 | 0.0035145 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2021-12-21 17:25 | 2021-12-22 09:36 | 71 | 016:11 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | C21122100107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 971 | 2021-12-21 | 68941 | keep | 0 | Dec | 2021 | 0.046955 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
CAGUAS | 2021-12-21 17:27 | 2021-12-21 19:37 | 7 | 002:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR REMPLAZO CAJA AVERIADA | C21122100108 | New_Event | Cutout Failure | Include | Include | Equipment | 130 | 2021-12-21 | 910 | keep | 0 | Dec | 2021 | 0.0006198 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-12-21 17:27 | 2021-12-21 23:50 | 200 | 006:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 Y 1 X 65 EN DIFERENTES CORTES DE LINEAS LLUVIA Y FUERTES VIENTOS | M21122100057 | New_Event | Bad Weather | Include | Include | Weather | 383 | 2021-12-21 | 76600 | keep | 0 | Dec | 2021 | 0.052172 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2021-12-21 17:28 | 2021-12-22 07:56 | 6 | 014:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR AVE CRUZO LINEAS | A21122100034 | New_Event |  |  | Include | Wildlife | 868 | 2021-12-21 | 5208 | keep | 0 | Dec | 2021 | 0.0035471 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-12-21 17:34 | 2021-12-21 19:32 | 222 | 001:58 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR 1907-03 PARA REEMPLAZAR MACHETES AVERIADOS MEDIANTE GOI BY-211221-04. LLEVANDO EL 1909-09 | S21122100000 | Additional_clients | Switch Failure | Include | Include | Equipment | 118 | 2021-12-21 | 26196 | keep | 0 | Dec | 2021 | 0.017842 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-21 17:34 | 2021-12-21 19:32 | 4456 | 001:58 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR 1907-03 PARA REEMPLAZAR MACHETES AVERIADOS MEDIANTE GOI BY-211221-04. LLEVANDO EL 1909-09 | S21122100000 | Additional_clients | Switch Failure | Include | Include | Equipment | 118 | 2021-12-21 | 525808 | keep | 0 | Dec | 2021 | 0.35813 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-21 17:58 | 2021-12-21 18:36 | 10 | 000:38 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REPARAR SECUNDARIA Y SE REALIZO DESGANCHE | B21122100117 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 38 | 2021-12-21 | 380 | keep | 0 | Dec | 2021 | 0.00025882 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-12-21 18:13 | 2021-12-21 22:49 | 35 | 004:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA Y SE REEMPLAZO CAJA QUEMADA | B21122100150 | New_Event | Cutout Failure | Include | Include | Equipment | 276 | 2021-12-21 | 9660 | keep | 0 | Dec | 2021 | 0.0065794 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2021-12-21 18:16 | 2021-12-21 18:39 | 10 | 000:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONECTORES SECUNDARIOS | R21122000034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 23 | 2021-12-21 | 230 | keep | 0 | Dec | 2021 | 0.00015665 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-21 18:16 | 2021-12-21 18:41 | 10 | 000:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A21122100040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 25 | 2021-12-21 | 250 | keep | 0 | Dec | 2021 | 0.00017027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-21 18:17 | 2021-12-21 22:00 | 40 | 003:43 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO RISER PARA REPARAR PISTOLA QUEMADA EN PM | A21122100041 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 223 | 2021-12-21 | 8920 | keep | 0 | Dec | 2021 | 0.0060754 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-12-21 18:26 | 2021-12-21 20:19 | 10 | 001:53 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R21122100036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 113 | 2021-12-21 | 1130 | keep | 0 | Dec | 2021 | 0.00076964 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-21 18:30 | 2021-12-21 19:37 | 2 | 001:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BARRA SOTERRADA SULFATADA | M21122000072 | New_Event | Secondary Wire Down | Include | Include | Equipment | 67 | 2021-12-21 | 134 | keep | 0 | Dec | 2021 | 9.1267e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2021-12-21 18:33 | 2021-12-22 12:22 | 6 | 017:49 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 50 KVA POR 50 KVA | C21122100123 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1069 | 2021-12-21 | 6414 | keep | 0 | Dec | 2021 | 0.0043685 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-12-21 18:41 | 2021-12-21 23:35 | 15 | 004:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CAJA A TRANSFORMADOR | R21122100039 | New_Event | Wire Down | Include | Include | Equipment | 294 | 2021-12-21 | 4410 | keep | 0 | Dec | 2021 | 0.0030036 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-12-21 18:53 | 2021-12-22 10:03 | 10 | 015:10 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B21122100229 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 910 | 2021-12-21 | 9100 | keep | 0 | Dec | 2021 | 0.006198 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-12-21 19:14 | 2021-12-22 14:25 | 1 | 019:11 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C21122100139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1151 | 2021-12-21 | 1151 | keep | 0 | Dec | 2021 | 0.00078394 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-12-21 19:31 | 2021-12-22 16:38 | 200 | 021:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO PRIMARIA Y SE CERRO C/L | C21122200059 | Additional_clients | Wire Down | Include | Include | Equipment | 1267 | 2021-12-21 | 253400 | keep | 0 | Dec | 2021 | 0.17259 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-21 19:42 | 2021-12-21 23:32 | 40 | 003:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA Y SE LEVANTO LINEA PRIMARIA | S21122100200 | New_Event | Wire Down | Include | Include | Equipment | 230 | 2021-12-21 | 9200 | keep | 0 | Dec | 2021 | 0.0062661 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-12-21 19:50 | 2021-12-22 08:50 | 25 | 013:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | C21122100143 | New_Event |  |  | Include | Wildlife | 780 | 2021-12-21 | 19500 | keep | 0 | Dec | 2021 | 0.013281 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2021-12-21 20:08 | 2021-12-22 14:34 | 6 | 018:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | C21122100147 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1106 | 2021-12-21 | 6636 | keep | 0 | Dec | 2021 | 0.0045197 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2021-12-21 20:11 | 2021-12-21 20:46 | 10 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR SECUNDARIA | R21122100202 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2021-12-21 | 350 | keep | 0 | Dec | 2021 | 0.00023838 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-21 20:27 | 2021-12-21 20:46 | 8 | 000:19 | P | HERRAJE ROTO O PODRIDO | SE REEMPLAZO CRUCETA PARTIDA | R21122100051 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 19 | 2021-12-21 | 152 | keep | 0 | Dec | 2021 | 0.00010353 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-12-21 20:50 | 2021-12-22 10:10 | 10 | 013:20 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S21122100024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 800 | 2021-12-21 | 8000 | keep | 0 | Dec | 2021 | 0.0054488 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-12-21 21:31 | 2021-12-21 22:27 | 10 | 000:56 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | R21122100057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 56 | 2021-12-21 | 560 | keep | 0 | Dec | 2021 | 0.00038141 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-21 23:26 | 2021-12-22 11:26 | 2076 | 012:00 | P | ERROR HUMANO | SE CERRO MACHETES EN CARRETRA 863 ESQUINA 2 QUE AL REALIZAR OPERACIONES EN SWITCHING FORM BY-211221-03 NO SE CERRARON | B21122100040 | New_Event | Human Error | Include | Include | Other | 720 | 2021-12-21 | 1494720 | keep | 0 | Dec | 2021 | 1.018 | 0.001414 | Sustained | FALSE | FALSE | Not_TMED_Event | 2076
BAYAMON | 2021-12-21 23:26 | 2021-12-22 11:30 | 700 | 012:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES Y PERMANECIERON ABIERTOS POR ERROR HASTA EL PROXIMO DIA. RELACIONADO AL GOI-BY211221-03 | B21122100069 | Partial_restoration | Wire Down | Include | Include | Equipment | 724 | 2021-12-21 | 506800 | keep | 0 | Dec | 2021 | 0.34518 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-12-22 01:03 | 2021-12-22 01:04 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21122200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-22 | 1097 | keep | 0 | Dec | 2021 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
HUMACAO | 2021-12-22 02:02 | 2021-12-22 11:43 | 125 | 009:41 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C21122200002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 581 | 2021-12-22 | 72625 | keep | 0 | Dec | 2021 | 0.049465 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
CANOVANAS | 2021-12-22 03:01 | 2021-12-22 09:37 | 50 | 006:36 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L REMPLAZO AISLADOR | R21122200001 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 396 | 2021-12-22 | 19800 | keep | 0 | Dec | 2021 | 0.013486 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-12-22 03:42 | 2021-12-22 03:43 | 4381 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21122200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-22 | 4381 | keep | 0 | Dec | 2021 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
CAGUAS | 2021-12-22 05:17 | 2021-12-22 12:04 | 5 | 006:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | C21122000004 | New_Event | Secondary Wire Down | Include | Include | Equipment | 407 | 2021-12-22 | 2035 | keep | 0 | Dec | 2021 | 0.001386 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2021-12-22 05:23 | 2021-12-22 09:14 | 50 | 003:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE X AVE | R21122200002 | New_Event |  |  | Include | Wildlife | 231 | 2021-12-22 | 11550 | keep | 0 | Dec | 2021 | 0.0078667 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-22 06:06 | 2021-12-22 16:50 | 199 | 010:44 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | SUBESTACION SE FUE A LOCK-OUT DEBIDO A QUE SE DISPARO EL INTERRUPTOR 1529-13 Y AL INTENTAR PROBARLO SE FUE A LOCK-OUT SE SECCIONALIZO AVERIA DEL 1924-02 POR ALAMBRE EN EL PISO LLEVANDO PARCIAL DE 1911-07 | S21122200062 | New_Event | Wire Down | Include | Include | Equipment | 644 | 2021-12-22 | 128156 | keep | 0 | Dec | 2021 | 0.087286 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
BAYAMON | 2021-12-22 06:06 | 2021-12-22 17:24 | 72 | 011:18 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO 3 VECES Y SE ENCONTRO LINEA EN EL PISO CRUZADO CON 1529-13 | S21122200062 | New_Event | Wire Down | Include | Include | Equipment | 678 | 2021-12-22 | 48816 | keep | 0 | Dec | 2021 | 0.033248 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
BAYAMON | 2021-12-22 06:06 | 2021-12-22 11:41 | 5 | 005:35 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO ALIMENTADOR 1924-02 LLEVANDO LA CARGA DEL 1924-03 DEBIDO A CONDUCTOR EN EL SUELO ENREDADO EN EL 1529-13. SE ABRIO N/O Y SE NORMALIZO LA CARGA DEL 1924-03 POR SU INTERRUPTOR. | S21122200011 | New_Event | Wire Down | Include | Include | Equipment | 335 | 2021-12-22 | 1675 | keep | 0 | Dec | 2021 | 0.0011408 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-12-22 06:08 | 2021-12-22 11:15 | 1844 | 005:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SUBESTACION 1529 EN LOCK OUT POR CONDUCTOR EN EL SUELO DEL 1529-13 Y 1924-02. 30% POR EL 1529-15. AL CERRAR EL 1529-15 PROBO MALO Y SE PATRULLO DEJANDO FUERA FUSIBLES HACIA PISCINA SANTA MARIA FID 33565087 | S21122200003 | New_Event | Wire Down | Include | Include | Equipment | 307 | 2021-12-22 | 566108 | keep | 0 | Dec | 2021 | 0.38557 | 0.0012559 | Sustained | FALSE | FALSE | Not_TMED_Event | 1844
BAYAMON | 2021-12-22 06:08 | 2021-12-22 09:37 | 1370 | 003:29 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO EL 1529-13 Y AL CERRARLO SE FUE A LOCK-OUT SUBESTACION DEBIDO A CONDUCTOR EN EL SUELO A LA SALIDA EN LA CARR 2 Y AFECTANDO TAMBIEN EL 1924-02. | S21122200003 | New_Event | Wire Down | Include | Include | Equipment | 209 | 2021-12-22 | 286330 | keep | 0 | Dec | 2021 | 0.19502 | 0.0009331 | Sustained | FALSE | FALSE | Not_TMED_Event | 1370
BAYAMON | 2021-12-22 06:08 | 2021-12-22 14:10 | 1984 | 008:02 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | SUBESTACION SE FUE A LOCK-OUT DEBIDO A QUE SE DISPARO EL INTERRUPTOR 1529-13 Y AL INTENTAR PROBARLO SE FUE A LOCK-OUT SE SECCIONALIZO AVERIA DEL 1924-02 POR ALAMBRE EN EL PISO LLEVANDO PARCIAL DE 1911-07 | S21122200062 | New_Event | Wire Down | Include | Include | Equipment | 482 | 2021-12-22 | 956288 | keep | 0 | Dec | 2021 | 0.65132 | 0.0013513 | Sustained | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2021-12-22 06:08 | 2021-12-22 10:15 | 1802 | 004:07 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO EL 1529-13 Y AL CERRARLO SE FUE A LOCK-OUT SUBESTACION DEBIDO A CONDUCTOR EN EL SUELO A LA SALIDA EN LA CARR 2 Y AFECTANDO TAMBIEN EL 1924-02. AL CERRARLO PROBO MALO Y SE ENVIO A PATRULLAR. LLEVA 30% 1346-02 | S21122200003 | New_Event | Wire Down | Include | Include | Equipment | 247 | 2021-12-22 | 445094 | keep | 0 | Dec | 2021 | 0.30315 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
BAYAMON | 2021-12-22 06:08 | 2021-12-22 14:10 | 250 | 008:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SUBESTACION SE FUE A LOCK-OUT DEBIDO A QUE SE DISPARO EL INTERRUPTOR 1529-13 Y AL INTENTAR PROBARLO SE FUE A LOCK-OUT SE SECCIONALIZO AVERIA DEL 1924-02 POR ALAMBRE EN EL PISO SU CARGA POR EL 1529-13 | S21122200062 | New_Event | Wire Down | Include | Include | Equipment | 482 | 2021-12-22 | 120500 | keep | 0 | Dec | 2021 | 0.082072 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
ARECIBO | 2021-12-22 06:13 | 2021-12-22 10:31 | 25 | 004:18 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR INFORMA JOURNEYMAN NO IDENTIFICO CAUSA | A21122200001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 258 | 2021-12-22 | 6450 | keep | 0 | Dec | 2021 | 0.0043931 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-12-22 06:29 | 2021-12-22 17:00 | 6 | 010:31 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA POR UNO DE 25 KVA | M21122200044 | New_Event | Service Transformer Failure | Include | Include | Equipment | 631 | 2021-12-22 | 3786 | keep | 0 | Dec | 2021 | 0.0025786 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-12-22 06:57 | 2021-12-22 12:30 | 20 | 005:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B21122200014 | New_Event | Cutout Failure | Include | Include | Equipment | 333 | 2021-12-22 | 6660 | keep | 0 | Dec | 2021 | 0.0045361 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-12-22 06:58 | 2021-12-22 15:14 | 12 | 008:16 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 50 KVA POR 50 KVA | C21122200009 | New_Event | Service Transformer Failure | Include | Include | Equipment | 496 | 2021-12-22 | 5952 | keep | 0 | Dec | 2021 | 0.0040539 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-12-22 07:21 | 2021-12-22 09:12 | 40 | 001:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CRUCE X AVE | R21122200004 | New_Event |  |  | Include | Wildlife | 111 | 2021-12-22 | 4440 | keep | 0 | Dec | 2021 | 0.0030241 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-12-22 07:56 | 2021-12-22 07:57 | 2888 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DEL INTERRUPTOR | A21122200003 | New_Event |  |  | Include | Wildlife | 1 | 2021-12-22 | 2888 | keep | 0 | Dec | 2021 | 0.001967 | 0.001967 | Momentary | FALSE | FALSE | Not_TMED_Event | 2888
ARECIBO | 2021-12-22 07:57 | 2021-12-22 08:30 | 6 | 000:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR AVE CRUZO LINEAS | A21122100034 | 1st_after_momentary |  |  | Include | Wildlife | 33 | 2021-12-22 | 198 | keep | 0 | Dec | 2021 | 0.00013486 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-12-22 07:58 | 2021-12-22 14:40 | 6 | 006:42 | P | DESGANCHE | 1 X 15 EN XMR SE REALIZO DESGANCHE | C21122200015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 402 | 2021-12-22 | 2412 | keep | 0 | Dec | 2021 | 0.0016428 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2021-12-22 08:03 | 2021-12-22 14:04 | 1192 | 006:01 | T | TRANSFORMADOR AVERIADO | SE ABRIO INTERRUPTOR PARA REMPLAZAR CONVERTIDOR | M21122200007 | New_Event | Service Transformer Failure | Include | Include | Equipment | 361 | 2021-12-22 | 430312 | keep | 0 | Dec | 2021 | 0.29308 | 0.00081187 | Sustained | FALSE | FALSE | Not_TMED_Event | 1192
MAYAGÃœEZ | 2021-12-22 08:18 | 2021-12-22 12:20 | 60 | 004:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | M21122200011 | New_Event |  |  | Include | Wildlife | 242 | 2021-12-22 | 14520 | keep | 0 | Dec | 2021 | 0.0098895 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2021-12-22 08:29 | 2021-12-22 10:05 | 10 | 001:36 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA | B21122200047 | New_Event | Service Transformer Failure | Include | Include | Equipment | 96 | 2021-12-22 | 960 | keep | 0 | Dec | 2021 | 0.00065385 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-22 08:31 | 2021-12-22 11:29 | 5 | 002:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR PALOMA | C21122200018 | New_Event |  |  | Include | Wildlife | 178 | 2021-12-22 | 890 | keep | 0 | Dec | 2021 | 0.00060617 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2021-12-22 08:31 | 2021-12-22 10:15 | 75 | 001:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | P21122200006 | New_Event |  |  | Include | Wildlife | 104 | 2021-12-22 | 7800 | keep | 0 | Dec | 2021 | 0.0053125 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BARRANQUITAS | 2021-12-22 08:34 | 2021-12-22 16:23 | 1 | 007:49 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L | C21122200021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 469 | 2021-12-22 | 469 | keep | 0 | Dec | 2021 | 0.00031943 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-22 08:42 | 2021-12-22 15:49 | 6 | 007:07 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21122200092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 427 | 2021-12-22 | 2562 | keep | 0 | Dec | 2021 | 0.001745 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2021-12-22 08:50 | 2021-12-22 08:51 | 1173 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P21122200008 | New_Event |  |  | Include | Wildlife | 1 | 2021-12-22 | 1173 | keep | 0 | Dec | 2021 | 0.00079892 | 0.00079892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1173
GUAYAMA | 2021-12-22 08:50 | 2021-12-22 08:51 | 215 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P21122200008 | New_Event |  |  | Include | Wildlife | 1 | 2021-12-22 | 215 | keep | 0 | Dec | 2021 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
GUAYAMA | 2021-12-22 08:51 | 2021-12-22 09:50 | 50 | 000:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | P21122200003 | 1st_after_momentary |  |  | Include | Wildlife | 59 | 2021-12-22 | 2950 | keep | 0 | Dec | 2021 | 0.0020092 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-22 09:07 | 2021-12-22 14:49 | 478 | 005:42 | S | LINEA DE TRANSMISION | DISPARO LINEA DE TRANSMISION 10700 | B21122200000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 342 | 2021-12-22 | 163476 | keep | 0 | Dec | 2021 | 0.11134 | 0.00032556 | Sustained | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2021-12-22 09:07 | 2021-12-22 14:49 | 679 | 005:42 | S | LINEA DE TRANSMISION | DISPARO LINEA DE TRANSMISION 10700 | B21122200000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 342 | 2021-12-22 | 232218 | keep | 0 | Dec | 2021 | 0.15816 | 0.00046246 | Sustained | FALSE | FALSE | Not_TMED_Event | 679
BAYAMON | 2021-12-22 09:07 | 2021-12-22 14:49 | 949 | 005:42 | S | LINEA DE TRANSMISION | DISPARO LINEA DE TRANSMISION 10700 | B21122200000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 342 | 2021-12-22 | 324558 | keep | 0 | Dec | 2021 | 0.22105 | 0.00064636 | Sustained | FALSE | FALSE | Not_TMED_Event | 949
BAYAMON | 2021-12-22 09:07 | 2021-12-22 14:49 | 67 | 005:42 | S | LINEA DE TRANSMISION | DISPARO LINEA DE TRANSMISION 10700 | B21122200000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 342 | 2021-12-22 | 22914 | keep | 0 | Dec | 2021 | 0.015607 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2021-12-22 09:07 | 2021-12-22 14:49 | 637 | 005:42 | S | LINEA DE TRANSMISION | DISPARO LINEA DE TRANSMISION 10700 | B21122200000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 342 | 2021-12-22 | 217854 | keep | 0 | Dec | 2021 | 0.14838 | 0.00043386 | Sustained | FALSE | FALSE | Not_TMED_Event | 637
BARRANQUITAS | 2021-12-22 09:19 | 2021-12-22 19:30 | 4 | 010:11 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C21122200031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 611 | 2021-12-22 | 2444 | keep | 0 | Dec | 2021 | 0.0016646 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-12-22 09:25 | 2021-12-22 09:26 | 766 | 000:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO 1709-03 LLEVANDO EL 1709-05 Y 50% ESTA TRANSFERIDO AL 1909-07 | S21122200000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-12-22 | 766 | keep | 0 | Dec | 2021 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2021-12-22 09:25 | 2021-12-22 09:26 | 2364 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO 1709-03 LLEVANDO EL 1709-05 | S21122200000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-12-22 | 2364 | keep | 0 | Dec | 2021 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
BAYAMON | 2021-12-22 09:26 | 2021-12-22 16:55 | 10 | 007:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 Y 1 X 80 EN CORTES DE LINEA SE REMPLAZO PORTAFUSIBLE | S21122200219 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 449 | 2021-12-22 | 4490 | keep | 0 | Dec | 2021 | 0.0030581 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-22 09:59 | 2021-12-22 10:23 | 7 | 000:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA ENCABEZAR SECUNDARIA | R21122200014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 24 | 2021-12-22 | 168 | keep | 0 | Dec | 2021 | 0.00011442 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2021-12-22 10:00 | 2021-12-22 18:10 | 1 | 008:10 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 100 EN SU-1 RAYOS | C21122200043 | New_Event | Bad Weather | Include | Include | Weather | 490 | 2021-12-22 | 490 | keep | 0 | Dec | 2021 | 0.00033374 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-12-22 10:02 | 2021-12-22 15:40 | 1 | 005:38 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA POR UNO DE 25 KVA | A21122200011 | New_Event | Service Transformer Failure | Include | Include | Equipment | 338 | 2021-12-22 | 338 | keep | 0 | Dec | 2021 | 0.00023021 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-22 10:05 | 2021-12-22 16:26 | 1 | 006:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M21122200021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 381 | 2021-12-22 | 381 | keep | 0 | Dec | 2021 | 0.0002595 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-22 10:15 | 2021-12-22 10:42 | 302 | 000:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO AMARRE CONTRA EL 1346-02 Y SE CERRO MACHETES EN 17435640 ENTRANDO 100% DEL 1529-15. QUEDA FUERA EL 30% DEL 1346-02. | S21122200003 | New_Event | Wire Down | Include | Include | Equipment | 27 | 2021-12-22 | 8154 | keep | 0 | Dec | 2021 | 0.0055537 | 0.00020569 | Sustained | FALSE | FALSE | Not_TMED_Event | 302
ARECIBO | 2021-12-22 10:25 | 2021-12-22 11:40 | 4 | 001:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21122200012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 75 | 2021-12-22 | 300 | keep | 0 | Dec | 2021 | 0.00020433 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2021-12-22 10:25 | 2021-12-22 17:03 | 4 | 006:38 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C21122200045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 398 | 2021-12-22 | 1592 | keep | 0 | Dec | 2021 | 0.0010843 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-12-22 10:27 | 2021-12-22 11:25 | 20 | 000:58 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21122100096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 58 | 2021-12-22 | 1160 | keep | 0 | Dec | 2021 | 0.00079007 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-12-22 11:07 | 2021-12-22 14:59 | 922 | 003:52 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO MH-1 A MH-2 AVERIA TERMINACION RISER DEALER HYUNDAI 99% EN SERVICIO | S21122200164 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 232 | 2021-12-22 | 213904 | keep | 0 | Dec | 2021 | 0.14569 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
HUMACAO | 2021-12-22 11:10 | 2021-12-22 17:58 | 6 | 006:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | C21122200050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 408 | 2021-12-22 | 2448 | keep | 0 | Dec | 2021 | 0.0016673 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-12-22 11:40 | 2021-12-22 17:03 | 3 | 005:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 5 EN TRANSFORMADOR AVE CRUZO LINEAS | M21122200029 | New_Event |  |  | Include | Wildlife | 323 | 2021-12-22 | 969 | keep | 0 | Dec | 2021 | 0.00065998 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
UTUADO | 2021-12-22 11:58 | 2021-12-22 11:59 | 932 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA | A21122200020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-22 | 932 | keep | 0 | Dec | 2021 | 0.00063478 | 0.00063478 | Momentary | FALSE | FALSE | Not_TMED_Event | 932
ARECIBO | 2021-12-22 12:23 | 2021-12-22 14:12 | 4 | 001:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21122200022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2021-12-22 | 436 | keep | 0 | Dec | 2021 | 0.00029696 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2021-12-22 12:25 | 2021-12-22 13:30 | 10 | 001:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA SE RETIRO CULEBRA | B21122200146 | New_Event |  |  | Include | Wildlife | 65 | 2021-12-22 | 650 | keep | 0 | Dec | 2021 | 0.00044271 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-12-22 12:36 | 2021-12-22 15:14 | 1 | 002:38 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | P21122200028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2021-12-22 | 158 | keep | 0 | Dec | 2021 | 0.00010761 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-22 12:39 | 2021-12-22 12:42 | 3 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL BREAKER PROVISIONAL #6 DE LA PORTATIL #7 LLEVA TRANSFERIDA LA CARGA DE 1707-02, 1707-03, 1707-04 Y 1707-05 | B21122200000 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2021-12-22 | 9 | keep | 0 | Dec | 2021 | 6.1299e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-12-22 12:39 | 2021-12-22 12:42 | 61 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL BREAKER PROVISIONAL #6 DE LA PORTATIL #7 LLEVA TRANSFERIDA LA CARGA DE 1707-02, 1707-03, 1707-04 Y 1707-05 | B21122200000 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2021-12-22 | 183 | keep | 0 | Dec | 2021 | 0.00012464 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2021-12-22 12:39 | 2021-12-22 12:42 | 1501 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL BREAKER PROVISIONAL #6 DE LA PORTATIL #7 LLEVA TRANSFERIDA LA CARGA DE 1707-02, 1707-03, 1707-04 Y 1707-05 | B21122200000 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2021-12-22 | 4503 | keep | 0 | Dec | 2021 | 0.003067 | 0.0010223 | Momentary | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2021-12-22 12:39 | 2021-12-22 12:42 | 546 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL BREAKER PROVISIONAL #6 DE LA PORTATIL #7 LLEVA TRANSFERIDA LA CARGA DE 1707-02, 1707-03, 1707-04 Y 1707-05 | B21122200000 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2021-12-22 | 1638 | keep | 0 | Dec | 2021 | 0.0011156 | 0.00037188 | Momentary | FALSE | FALSE | Not_TMED_Event | 546
BAYAMON | 2021-12-22 12:42 | 2021-12-22 13:37 | 7 | 000:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN TRANSFORMADOR SE RETIRO BAJANTE DE LINEA A PARARRAYO | B21122200162 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 55 | 2021-12-22 | 385 | keep | 0 | Dec | 2021 | 0.00026222 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
GUAYAMA | 2021-12-22 13:06 | 2021-12-22 15:41 | 1 | 002:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 20 EN MONTURA TRIFASICA AVE CRUZO FASE | P21122200029 | New_Event |  |  | Include | Wildlife | 155 | 2021-12-22 | 155 | keep | 0 | Dec | 2021 | 0.00010557 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-12-22 13:31 | 2021-12-22 14:49 | 39 | 001:18 | P | AISLADOR ROTO, PARTIDO O SAFADO | ABRIO C/L PARA REMPLAZAR AISLADOR Y RETEZAR LINEA | R21122200017 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 78 | 2021-12-22 | 3042 | keep | 0 | Dec | 2021 | 0.0020719 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
CAGUAS | 2021-12-22 13:31 | 2021-12-22 15:14 | 32 | 001:43 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | C21122200074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2021-12-22 | 3296 | keep | 0 | Dec | 2021 | 0.0022449 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
BAYAMON | 2021-12-22 13:37 | 2021-12-22 14:25 | 3 | 000:48 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL BREAKER PROVISIONAL #6 DE LA PORTATIL #7 LLEVA TRANSFERIDA LA CARGA DE 1707-02, 1707-03, 1707-04 Y 1707-05 SE RETIRO PUENTE DE LINEA A PARARRAYO | B21122200000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 48 | 2021-12-22 | 144 | keep | 0 | Dec | 2021 | 9.8078e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-12-22 13:37 | 2021-12-22 14:25 | 61 | 000:48 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL BREAKER PROVISIONAL #6 DE LA PORTATIL #7 LLEVA TRANSFERIDA LA CARGA DE 1707-02, 1707-03, 1707-04 Y 1707-05 SE RETIRO PUENTE DE LINEA A PARARRAYO | B21122200000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 48 | 2021-12-22 | 2928 | keep | 0 | Dec | 2021 | 0.0019942 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2021-12-22 13:37 | 2021-12-22 14:25 | 1501 | 000:48 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL BREAKER PROVISIONAL #6 DE LA PORTATIL #7 LLEVA TRANSFERIDA LA CARGA DE 1707-02, 1707-03, 1707-04 Y 1707-05 SE RETIRO PUENTE DE LINEA A PARARRAYO | B21122200000 | Additional_clients | Wire Down | Include | Include | Equipment | 48 | 2021-12-22 | 72048 | keep | 0 | Dec | 2021 | 0.049072 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-22 13:37 | 2021-12-22 14:25 | 546 | 000:48 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL BREAKER PROVISIONAL #6 DE LA PORTATIL #7 LLEVA TRANSFERIDA LA CARGA DE 1707-02, 1707-03, 1707-04 Y 1707-05 SE RETIRO PUENTE DE LINEA A PARARRAYO | B21122200000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 48 | 2021-12-22 | 26208 | keep | 0 | Dec | 2021 | 0.01785 | 0.00037188 | Sustained | FALSE | FALSE | Not_TMED_Event | 546
BAYAMON | 2021-12-22 14:02 | 2021-12-22 22:35 | 100 | 008:33 | P | NO SE REPORTO CAUSA | 2 X 100 EN SU-1 HACIA SU-2 | S21122200225 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 513 | 2021-12-22 | 51300 | keep | 0 | Dec | 2021 | 0.03494 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2021-12-22 14:04 | 2021-12-22 17:25 | 299 | 003:21 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO CONVERTIDOR AVERIADO | M21122200043 | New_Event | Service Transformer Failure | Include | Include | Equipment | 201 | 2021-12-22 | 60099 | keep | 0 | Dec | 2021 | 0.040933 | 0.00020365 | Sustained | FALSE | FALSE | Not_TMED_Event | 299
HUMACAO | 2021-12-22 14:18 | 2021-12-22 22:55 | 10 | 008:37 | P | SECUNDARIA/ESTRUCTURA AVERIADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZARON 2 POSTES PARTIDOS | C21122200083 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 517 | 2021-12-22 | 5170 | keep | 0 | Dec | 2021 | 0.0035213 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-22 14:25 | 2021-12-22 15:53 | 7 | 001:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN TRANSFORMADOR SE RETIRO BAJANTE DE LINEA A PARARRAYO | B21122200162 | Partial_restoration | Wire Down | Include | Include | Equipment | 88 | 2021-12-22 | 616 | keep | 0 | Dec | 2021 | 0.00041955 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-22 14:35 | 2021-12-22 14:59 | 135 | 000:24 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO AL CERRAR MH-1 A MH-2 SE RESETEO BANDERAS Y SE CERRO INTERRUPTOR 100% 1401-8 Y 99% DEL 1346-5 SE ENCONTRO TERMINACION AVERIADA V.S. 2 A RISER | S21122200164 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 24 | 2021-12-22 | 3240 | keep | 0 | Dec | 2021 | 0.0022067 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2021-12-22 14:41 | 2021-12-23 11:07 | 12 | 020:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR BAJANTE | S21122200237 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1226 | 2021-12-22 | 14712 | keep | 0 | Dec | 2021 | 0.01002 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-12-22 14:44 | 2021-12-22 18:00 | 40 | 003:16 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21122200047 | New_Event | Bad Weather | Include | Include | Weather | 196 | 2021-12-22 | 7840 | keep | 0 | Dec | 2021 | 0.0053398 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-12-22 14:52 | 2021-12-22 16:27 | 36 | 001:35 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO CAUSA | R21122200020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 95 | 2021-12-22 | 3420 | keep | 0 | Dec | 2021 | 0.0023293 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-12-22 14:59 | 2021-12-22 17:33 | 1 | 002:34 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 2 X 30 EN RISER SE REPARO TERMINACION SU CARGA POR 1401-8 | S21122200164 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 154 | 2021-12-22 | 154 | keep | 0 | Dec | 2021 | 0.00010489 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-12-22 15:02 | 2021-12-22 16:36 | 20 | 001:34 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR SECTOR REQUIERE DESGANCHE | M21122200049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2021-12-22 | 1880 | keep | 0 | Dec | 2021 | 0.0012805 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-12-22 15:03 | 2021-12-22 18:21 | 100 | 003:18 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21122200243 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2021-12-22 | 19800 | keep | 0 | Dec | 2021 | 0.013486 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2021-12-22 15:12 | 2021-12-22 15:53 | 10 | 000:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21122200038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 41 | 2021-12-22 | 410 | keep | 0 | Dec | 2021 | 0.00027925 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-12-22 15:26 | 2021-12-22 17:34 | 100 | 002:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | P21122200035 | New_Event | Cutout Failure | Include | Include | Equipment | 128 | 2021-12-22 | 12800 | keep | 0 | Dec | 2021 | 0.008718 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-12-22 15:46 | 2021-12-22 18:24 | 2450 | 002:38 | T | BREAKER DEFECTUOSO O NO OPERA | SE TRANSFIRIO LA CARGA AL 2605-02 POR BOBINA DE CLOSE QUEMADA DEL 2605-01 | C21122200101 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 158 | 2021-12-22 | 387100 | keep | 0 | Dec | 2021 | 0.26365 | 0.0016687 | Sustained | FALSE | FALSE | Not_TMED_Event | 2450
UTUADO | 2021-12-22 15:47 | 2021-12-22 16:28 | 2 | 000:41 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS | A21122200029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 41 | 2021-12-22 | 82 | keep | 0 | Dec | 2021 | 5.585e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2021-12-22 15:47 | 2021-12-22 19:36 | 10 | 003:49 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | B21122200207 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 229 | 2021-12-22 | 2290 | keep | 0 | Dec | 2021 | 0.0015597 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-22 16:05 | 2021-12-22 16:54 | 27 | 000:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | R21122200023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 49 | 2021-12-22 | 1323 | keep | 0 | Dec | 2021 | 0.00090109 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
SAN JUAN | 2021-12-22 16:20 | 2021-12-22 18:30 | 85 | 002:10 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21222000259 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2021-12-22 | 11050 | keep | 0 | Dec | 2021 | 0.0075261 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
BAYAMON | 2021-12-22 16:21 | 2021-12-22 18:11 | 40 | 001:50 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21122200215 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 110 | 2021-12-22 | 4400 | keep | 0 | Dec | 2021 | 0.0029968 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-12-22 16:29 | 2021-12-22 21:05 | 10 | 004:36 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21122200216 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 276 | 2021-12-22 | 2760 | keep | 0 | Dec | 2021 | 0.0018798 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-12-22 16:49 | 2021-12-22 21:38 | 40 | 004:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE X AVE | R21122200025 | New_Event |  |  | Include | Wildlife | 289 | 2021-12-22 | 11560 | keep | 0 | Dec | 2021 | 0.0078735 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-12-22 17:02 | 2021-12-23 13:00 | 10 | 019:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C21122200118 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1198 | 2021-12-22 | 11980 | keep | 0 | Dec | 2021 | 0.0081595 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-22 17:04 | 2021-12-22 19:41 | 500 | 002:37 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21122200037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2021-12-22 | 78500 | keep | 0 | Dec | 2021 | 0.053466 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2021-12-22 17:16 | 2021-12-22 17:18 | 2234 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B21122200219 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-22 | 4468 | keep | 0 | Dec | 2021 | 0.0030431 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
SAN JUAN | 2021-12-22 17:17 | 2021-12-22 20:18 | 12 | 003:01 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21122200217 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 181 | 2021-12-22 | 2172 | keep | 0 | Dec | 2021 | 0.0014793 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-12-22 17:18 | 2021-12-22 21:24 | 150 | 004:06 | P | NO SE REPORTO CAUSA | 1 X 200 EN CONVERTIDOR | B21122200237 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 246 | 2021-12-22 | 36900 | keep | 0 | Dec | 2021 | 0.025132 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2021-12-22 17:39 | 2021-12-22 18:00 | 1 | 000:21 | P | NO SE REPORTO CAUSA | 1 X 10 EN MONTURA TRIFASICA NO SE REPORTO LA CAUSA | P21122200045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 21 | 2021-12-22 | 21 | keep | 0 | Dec | 2021 | 1.4303e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-12-22 17:42 | 2021-12-22 21:20 | 30 | 003:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN C/L SE REPARO LINEA CRUZADA | C21122200122 | New_Event | Wire Down | Include | Include | Equipment | 218 | 2021-12-22 | 6540 | keep | 0 | Dec | 2021 | 0.0044544 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2021-12-22 17:50 | 2021-12-22 18:33 | 6 | 000:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | R21122200030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 43 | 2021-12-22 | 258 | keep | 0 | Dec | 2021 | 0.00017572 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2021-12-22 17:51 | 2021-12-23 14:17 | 20 | 020:26 | P | DESGANCHE | 1 X 15 EN C/L SE REALIZO DESGANCHE | R21122200031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1226 | 2021-12-22 | 24520 | keep | 0 | Dec | 2021 | 0.0167 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2021-12-22 17:51 | 2021-12-22 21:51 | 40 | 004:00 | P | NO SE REPORTO CAUSA | 1 X 15 Y 1 X 40 EN CORTES DE LINEA NO CAUSA | R21122200031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 240 | 2021-12-22 | 9600 | keep | 0 | Dec | 2021 | 0.0065385 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-22 18:12 | 2021-12-22 19:04 | 10 | 000:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA Y TOMA | B21122200218 | New_Event | Secondary Wire Down | Include | Include | Equipment | 52 | 2021-12-22 | 520 | keep | 0 | Dec | 2021 | 0.00035417 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-22 18:18 | 2021-12-22 20:58 | 100 | 002:40 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21122200280 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2021-12-22 | 16000 | keep | 0 | Dec | 2021 | 0.010898 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-12-22 18:20 | 2021-12-22 18:30 | 12 | 000:10 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR POSTES SECUNDARIOS PARTIDOS | M21122200012 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 10 | 2021-12-22 | 120 | keep | 0 | Dec | 2021 | 8.1731e-05 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-12-22 18:21 | 2021-12-22 18:23 | 320 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B21122200226 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-22 | 640 | keep | 0 | Dec | 2021 | 0.0004359 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2021-12-22 18:23 | 2021-12-22 19:57 | 30 | 001:34 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21122200227 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 94 | 2021-12-22 | 2820 | keep | 0 | Dec | 2021 | 0.0019207 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-12-22 18:26 | 2021-12-22 21:26 | 50 | 003:00 | P | DESGANCHE | 1 X 80 EN C.L SE REALIZO DESGANCHE | C21122200133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2021-12-22 | 9000 | keep | 0 | Dec | 2021 | 0.0061299 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2021-12-22 18:26 | 2021-12-22 18:27 | 4132 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21122200047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-22 | 4132 | keep | 0 | Dec | 2021 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
SAN JUAN | 2021-12-22 18:30 | 2021-12-22 21:09 | 7 | 002:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN XMR REPARO SECUNDARIA | R21122200033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 159 | 2021-12-22 | 1113 | keep | 0 | Dec | 2021 | 0.00075806 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2021-12-22 18:31 | 2021-12-23 17:25 | 10 | 022:54 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR DE 50 KVA X 50 KVA | C21122200136 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1374 | 2021-12-22 | 13740 | keep | 0 | Dec | 2021 | 0.0093583 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-22 18:48 | 2021-12-22 20:47 | 30 | 001:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BARRAS SECUNDARIAS SOTERRADAS | A21122200051 | New_Event | Secondary Wire Down | Include | Include | Equipment | 119 | 2021-12-22 | 3570 | keep | 0 | Dec | 2021 | 0.0024315 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-12-22 18:50 | 2021-12-22 22:08 | 13 | 003:18 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | R21122200037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 198 | 2021-12-22 | 2574 | keep | 0 | Dec | 2021 | 0.0017531 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
HUMACAO | 2021-12-22 19:09 | 2021-12-22 22:22 | 130 | 003:13 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21122200141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2021-12-22 | 25090 | keep | 0 | Dec | 2021 | 0.017089 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
CAGUAS | 2021-12-22 19:49 | 2021-12-23 11:27 | 30 | 015:38 | P | DESGANCHE | 1 X 30 EN C/L | C21122200157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 938 | 2021-12-22 | 28140 | keep | 0 | Dec | 2021 | 0.019166 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-22 20:16 | 2021-12-22 21:20 | 100 | 001:04 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21122200055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2021-12-22 | 6400 | keep | 0 | Dec | 2021 | 0.004359 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2021-12-22 20:50 | 2021-12-22 21:40 | 8 | 000:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21122200042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 50 | 2021-12-22 | 400 | keep | 0 | Dec | 2021 | 0.00027244 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-12-22 22:05 | 2021-12-23 13:29 | 26 | 015:24 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REMPLAZO PISTOLA EN EL T - 15 | C21122200166 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 924 | 2021-12-22 | 24024 | keep | 0 | Dec | 2021 | 0.016363 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
ARECIBO | 2021-12-22 22:13 | 2021-12-23 00:25 | 200 | 002:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA 100 AMP | A21122200062 | New_Event | Cutout Failure | Include | Include | Equipment | 132 | 2021-12-22 | 26400 | keep | 0 | Dec | 2021 | 0.017981 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2021-12-22 22:21 | 2021-12-23 11:16 | 35 | 012:55 | P | DESGANCHE | 1 X 50 EN C/L | C21122200167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 775 | 2021-12-22 | 27125 | keep | 0 | Dec | 2021 | 0.018475 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
HUMACAO | 2021-12-22 22:43 | 2021-12-23 12:50 | 50 | 014:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L REMPLAZO CAJA AVERIADA | C21122200160 | New_Event | Cutout Failure | Include | Include | Equipment | 847 | 2021-12-22 | 42350 | keep | 0 | Dec | 2021 | 0.028844 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-12-22 23:00 | 2021-12-22 23:01 | 602 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DE INTERRUPTOR | S21122200000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2021-12-22 | 602 | keep | 0 | Dec | 2021 | 0.00041002 | 0.00041002 | Momentary | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2021-12-22 23:01 | 2021-12-22 23:50 | 100 | 000:49 | P | DESCONECTIVO DEFECTUOSO | SE ENCONTRO UN MACHETE ABIERTO Y SE PROCEDIO A CERRARLO. SE REFIERE PARA REEMPLAZO DE EL JUEGO DE MACHETES DE SALIDA | S21122200291 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 49 | 2021-12-22 | 4900 | keep | 0 | Dec | 2021 | 0.0033374 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-12-22 23:32 | 2021-12-22 23:33 | 2126 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C21122200170 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-22 | 2126 | keep | 0 | Dec | 2021 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
SAN JUAN | 2021-12-23 | 2021-12-23 12:34 | 30 | 012:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA | S21122300001 | New_Event | Cutout Failure | Include | Include | Equipment | 754 | 2021-12-23 | 22620 | keep | 0 | Dec | 2021 | 0.015406 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-23 00:21 | 2021-12-23 17:06 | 100 | 016:45 | P | LINEA DE TRANSMISION 38KV | SE RETIRO OVERHEAD CAIDO SOBRE EL ALIMENTADOR Y SE REMPLAZO AISLADOR ROTO | A21122300001 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1005 | 2021-12-23 | 100500 | keep | 0 | Dec | 2021 | 0.06845 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-12-23 02:16 | 2021-12-23 10:57 | 4 | 008:41 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | S21122300003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 521 | 2021-12-23 | 2084 | keep | 0 | Dec | 2021 | 0.0014194 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-12-23 04:01 | 2021-12-23 07:17 | 2000 | 003:16 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO CONVERTIDOR QUEMADO | B21122300004 | New_Event | Service Transformer Failure | Include | Include | Equipment | 196 | 2021-12-23 | 392000 | keep | 0 | Dec | 2021 | 0.26699 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
BAYAMON | 2021-12-23 04:24 | 2021-12-23 10:46 | 40 | 006:22 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA PRINCIPAL Y 1 X 40 EN CORTE DE LINEA INTERMEDIO SE REALIZO DESGANCHE | B21122300007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 382 | 2021-12-23 | 15280 | keep | 0 | Dec | 2021 | 0.010407 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-12-23 07:09 | 2021-12-23 17:19 | 40 | 010:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | B21122300016 | New_Event | Wire Down | Include | Include | Equipment | 610 | 2021-12-23 | 24400 | keep | 0 | Dec | 2021 | 0.016619 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2021-12-23 07:13 | 2021-12-23 13:28 | 30 | 006:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21122300007 | New_Event | Bad Weather | Include | Include | Weather | 375 | 2021-12-23 | 11250 | keep | 0 | Dec | 2021 | 0.0076623 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-12-23 07:15 | 2021-12-23 15:01 | 200 | 007:46 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S21122300008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 466 | 2021-12-23 | 93200 | keep | 0 | Dec | 2021 | 0.063478 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2021-12-23 07:15 | 2021-12-24 03:20 | 60 | 020:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21122300079 | New_Event | Bad Weather | Include | Include | Weather | 1205 | 2021-12-23 | 72300 | keep | 0 | Dec | 2021 | 0.049243 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-12-23 07:16 | 2021-12-24 11:24 | 25 | 028:08 | P | NO SE REPORTO CAUSA | SE REPARO BAJANTE SECUNDARIO | S21122300009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1688 | 2021-12-23 | 42200 | keep | 0 | Dec | 2021 | 0.028742 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-12-23 07:17 | 2021-12-23 07:18 | 5809 | 000:01 | T | TRANSFORMADOR AVERIADO | SE REMPLAZO CONVERTIDOR QUEMADO | B21122300004 | Additional_clients | Service Transformer Failure | Include | Include | Equipment | 1 | 2021-12-23 | 5809 | keep | 0 | Dec | 2021 | 0.0039565 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-23 07:18 | 2021-12-23 12:40 | 2000 | 005:22 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO CONVERTIDOR AVERIADO | B21122300004 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 322 | 2021-12-23 | 644000 | keep | 0 | Dec | 2021 | 0.43863 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
BARRANQUITAS | 2021-12-23 07:25 | 2021-12-23 13:25 | 40 | 006:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA AVERIADA NO FUNDIO | C21122300006 | New_Event | Cutout Failure | Include | Include | Equipment | 360 | 2021-12-23 | 14400 | keep | 0 | Dec | 2021 | 0.0098078 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2021-12-23 07:35 | 2021-12-23 07:36 | 1475 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UN OPERACION Y QUEDA EN SERVICIO | P21122300001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-23 | 1475 | keep | 0 | Dec | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
ARECIBO | 2021-12-23 07:36 | 2021-12-23 07:37 | 199 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR CARGA POR 8013-04 | A21122300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-12-23 | 199 | keep | 0 | Dec | 2021 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2021-12-23 07:36 | 2021-12-23 07:37 | 24 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA ALGUNA | A21122300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-12-23 | 24 | keep | 0 | Dec | 2021 | 1.6346e-05 | 1.6346e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 24
ARECIBO | 2021-12-23 07:37 | 2021-12-23 11:52 | 50 | 004:15 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA POR VIENTOS | A21122300035 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 255 | 2021-12-23 | 12750 | keep | 0 | Dec | 2021 | 0.008684 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-12-23 07:57 | 2021-12-23 10:00 | 30 | 002:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | M21122300003 | New_Event |  |  | Include | Wildlife | 123 | 2021-12-23 | 3690 | keep | 0 | Dec | 2021 | 0.0025132 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2021-12-23 08:03 | 2021-12-23 08:04 | 2524 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | R21122300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-23 | 2524 | keep | 0 | Dec | 2021 | 0.0017191 | 0.0017191 | Momentary | FALSE | FALSE | Not_TMED_Event | 2524
MAYAGÃœEZ | 2021-12-23 08:03 | 2021-12-23 13:44 | 20 | 005:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21122300004 | New_Event | Bad Weather | Include | Include | Weather | 341 | 2021-12-23 | 6820 | keep | 0 | Dec | 2021 | 0.0046451 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-12-23 08:08 | 2021-12-23 14:55 | 20 | 006:47 | P | DESGANCHE | 1 X 50 C/L SE REALIZO DESGANCHE | R21122300005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 407 | 2021-12-23 | 8140 | keep | 0 | Dec | 2021 | 0.0055441 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-12-23 08:15 | 2021-12-23 22:37 | 1 | 014:22 | P | NO SE REPORTO CAUSA | 2 X 40 EN TRANSCLOSURE | S21122300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 862 | 2021-12-23 | 862 | keep | 0 | Dec | 2021 | 0.0005871 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2021-12-23 08:17 | 2021-12-23 17:13 | 10 | 008:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C21122300013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 536 | 2021-12-23 | 5360 | keep | 0 | Dec | 2021 | 0.0036507 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-12-23 08:31 | 2021-12-23 10:09 | 65 | 001:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L. SE REEMPLAZO PORTAFUSIBLES | R21122300007 | New_Event | Cutout Failure | Include | Include | Equipment | 98 | 2021-12-23 | 6370 | keep | 0 | Dec | 2021 | 0.0043386 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2021-12-23 08:44 | 2021-12-24 10:04 | 15 | 025:20 | P | DESGANCHE | DESGANCHE Y SE REPARO SECUNDARIA | S21122300014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1520 | 2021-12-23 | 22800 | keep | 0 | Dec | 2021 | 0.015529 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-12-23 08:46 | 2021-12-23 11:48 | 40 | 003:02 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21122300046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 182 | 2021-12-23 | 7280 | keep | 0 | Dec | 2021 | 0.0049584 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-12-23 08:54 | 2021-12-23 11:19 | 10 | 002:25 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR NO CAUSA | C21122300015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2021-12-23 | 1450 | keep | 0 | Dec | 2021 | 0.00098759 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-23 08:57 | 2021-12-23 09:28 | 10 | 000:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA Y CONEXIONES | B21122200218 | New_Event | Secondary Wire Down | Include | Include | Equipment | 31 | 2021-12-23 | 310 | keep | 0 | Dec | 2021 | 0.00021114 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-23 09:00 | 2021-12-23 09:36 | 10 | 000:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA Y CONECTORES SECUNDARIOS | S21122100206 | New_Event | Secondary Wire Down | Include | Include | Equipment | 36 | 2021-12-23 | 360 | keep | 0 | Dec | 2021 | 0.00024519 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-12-23 09:05 | 2021-12-23 12:03 | 10 | 002:58 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 25 X 25KVA | R21122300010 | New_Event | Service Transformer Failure | Include | Include | Equipment | 178 | 2021-12-23 | 1780 | keep | 0 | Dec | 2021 | 0.0012123 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-23 09:12 | 2021-12-23 10:33 | 10 | 001:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | R21122200044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 81 | 2021-12-23 | 810 | keep | 0 | Dec | 2021 | 0.00055169 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-12-23 09:12 | 2021-12-23 16:53 | 20 | 007:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | R21122300011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 461 | 2021-12-23 | 9220 | keep | 0 | Dec | 2021 | 0.0062797 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-12-23 09:14 | 2021-12-23 10:34 | 10 | 001:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTE SECUNDARIO Y CONEXIONES | B21122200252 | New_Event | Secondary Wire Down | Include | Include | Equipment | 80 | 2021-12-23 | 800 | keep | 0 | Dec | 2021 | 0.00054488 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-23 09:27 | 2021-12-23 14:47 | 30 | 005:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LUVIA Y VIENTO | A21122300019 | New_Event | Bad Weather | Include | Include | Weather | 320 | 2021-12-23 | 9600 | keep | 0 | Dec | 2021 | 0.0065385 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-12-23 09:28 | 2021-12-23 14:18 | 1 | 004:50 | P | NO SE REPORTO CAUSA | 1 X 30 EN XMR Y 1 X 20 EN TRANSCLOSURE NO CAUSA | C21122300019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 290 | 2021-12-23 | 290 | keep | 0 | Dec | 2021 | 0.00019752 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-12-23 09:30 | 2021-12-23 17:15 | 85 | 007:45 | P | DESGANCHE | 2 X 50 EN C/L | C21122320002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 465 | 2021-12-23 | 39525 | keep | 0 | Dec | 2021 | 0.02692 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
CAGUAS | 2021-12-23 10:00 | 2021-12-23 10:01 | 1342 | 000:01 | T | OTRAS CAUSAS | PERSONAL REALIZANDO PRUEBAS A RISER DE EDIFICIO ANGORA PROA | C21122300055 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-12-23 | 1342 | keep | 0 | Dec | 2021 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
MAYAGÃœEZ | 2021-12-23 10:00 | 2021-12-23 12:34 | 100 | 002:34 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M21122300023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2021-12-23 | 15400 | keep | 0 | Dec | 2021 | 0.010489 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-12-23 10:01 | 2021-12-23 12:01 | 1 | 002:00 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L NO CAUSA | C21122300015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2021-12-23 | 120 | keep | 0 | Dec | 2021 | 8.1731e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-12-23 10:15 | 2021-12-23 10:55 | 20 | 000:40 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A21122300022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 40 | 2021-12-23 | 800 | keep | 0 | Dec | 2021 | 0.00054488 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-12-23 10:21 | 2021-12-23 11:11 | 10 | 000:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES EN PEDESTAL | S21122200239 | New_Event | Secondary Wire Down | Include | Include | Equipment | 50 | 2021-12-23 | 500 | keep | 0 | Dec | 2021 | 0.00034055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-23 10:41 | 2021-12-23 11:51 | 10 | 001:10 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR | B21122300083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 70 | 2021-12-23 | 700 | keep | 0 | Dec | 2021 | 0.00047677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-23 10:49 | 2021-12-23 15:09 | 25 | 004:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN RISER SE REMPLAZO CAJA | S21122300033 | New_Event | Cutout Failure | Include | Include | Equipment | 260 | 2021-12-23 | 6500 | keep | 0 | Dec | 2021 | 0.0044271 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2021-12-23 10:53 | 2021-12-23 16:04 | 50 | 005:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA Y VIENTO | A21122300027 | New_Event | Bad Weather | Include | Include | Weather | 311 | 2021-12-23 | 15550 | keep | 0 | Dec | 2021 | 0.010591 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2021-12-23 11:07 | 2021-12-23 16:53 | 1 | 005:46 | P | NO SE REPORTO CAUSA | 1 X 20 EN C/L | R21122300022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 346 | 2021-12-23 | 346 | keep | 0 | Dec | 2021 | 0.00023566 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-12-23 11:47 | 2021-12-23 16:19 | 1 | 004:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | A21122300034 | New_Event | Wire Down | Include | Include | Equipment | 272 | 2021-12-23 | 272 | keep | 0 | Dec | 2021 | 0.00018526 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-12-23 11:55 | 2021-12-23 15:37 | 25 | 003:42 | P | DESGANCHE | 1X 80 EN C/L SE REALIZO DESGANCHE | R21122300032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2021-12-23 | 5550 | keep | 0 | Dec | 2021 | 0.0037801 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2021-12-23 12:07 | 2021-12-23 13:47 | 3 | 001:40 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 50 EN SU 1 SE REMPLAZO PORTAFUSIBLE RBA EN SU | B21122300103 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 100 | 2021-12-23 | 300 | keep | 0 | Dec | 2021 | 0.00020433 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-12-23 12:19 | 2021-12-23 12:20 | 600 | 000:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO NO RECERRO INFORMARON GLOBO CRUZANDO FASE CALLE FELIPE GUTIERREZ PARTE DE SU CARGA POR 1336-8 | S21122300000 | New_Event |  |  | Include | Wildlife | 1 | 2021-12-23 | 600 | keep | 0 | Dec | 2021 | 0.00040866 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2021-12-23 12:19 | 2021-12-23 12:20 | 5290 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO NO RECERRO SE CERRO POR CONTROL LLEVA 1336-9 Y 30% 1204-04 | S21122300000 | New_Event |  |  | Include | Wildlife | 1 | 2021-12-23 | 5290 | keep | 0 | Dec | 2021 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2021-12-23 12:19 | 2021-12-23 12:20 | 207 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO NO RECERRO SE CERRO POR CONTROL LLEVA 1336-9 Y 30% 1204-04 | S21122300000 | New_Event |  |  | Include | Wildlife | 1 | 2021-12-23 | 207 | keep | 0 | Dec | 2021 | 0.00014099 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
VEGA BAJA | 2021-12-23 12:33 | 2021-12-23 16:48 | 30 | 004:15 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21122300108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 255 | 2021-12-23 | 7650 | keep | 0 | Dec | 2021 | 0.0052104 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2021-12-23 12:35 | 2021-12-23 13:21 | 10 | 000:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO MXR Y SE REPARO SECUNDARIA | R21122300034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 46 | 2021-12-23 | 460 | keep | 0 | Dec | 2021 | 0.0003133 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-23 12:40 | 2021-12-23 12:41 | 5809 | 000:01 | T | TRANSFORMADOR AVERIADO | SE ABRIO INTERRUPTOR A PETICION PERSONAL DE CAMPO PARA PODER ABRIR CAJA PRIMARIA EN CONVERTIDOR AVERIADO | B21122300000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1 | 2021-12-23 | 5809 | keep | 0 | Dec | 2021 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
BAYAMON | 2021-12-23 12:41 | 2021-12-24 03:07 | 2000 | 014:26 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO CONVERTIDOR | B21122300004 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 866 | 2021-12-23 | 1732000 | keep | 0 | Dec | 2021 | 1.1797 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
CAGUAS | 2021-12-23 12:45 | 2021-12-23 12:46 | 2302 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21122300096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-23 | 2302 | keep | 0 | Dec | 2021 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
SAN JUAN | 2021-12-23 12:47 | 2021-12-23 12:48 | 600 | 000:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO NO RECERRO INFORMARON GLOBO CRUZANDO FASE CALLE FELIPE GUTIERREZ PARTE DE SU CARGA POR 1336-8 | S21122300000 | 1st_after_momentary |  |  | Include | Wildlife | 1 | 2021-12-23 | 600 | keep | 0 | Dec | 2021 | 0.00040866 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2021-12-23 12:47 | 2021-12-23 12:48 | 5290 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO NO RECERRO SE CERRO POR CONTROL LLEVA 1336-9 Y 30% 1204-04 | S21122300000 | 1st_after_momentary |  |  | Include | Wildlife | 1 | 2021-12-23 | 5290 | keep | 0 | Dec | 2021 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2021-12-23 12:47 | 2021-12-23 12:48 | 207 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO NO RECERRO SE CERRO POR CONTROL LLEVA 1336-9 Y 30% 1204-04 | S21122300000 | 1st_after_momentary |  |  | Include | Wildlife | 1 | 2021-12-23 | 207 | keep | 0 | Dec | 2021 | 0.00014099 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
ARECIBO | 2021-12-23 12:50 | 2021-12-23 12:51 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | A21122300044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-23 | 3431 | keep | 0 | Dec | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
SAN JUAN | 2021-12-23 12:51 | 2021-12-23 12:52 | 600 | 000:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO NO RECERRO INFORMARON GLOBO CRUZANDO FASE CALLE FELIPE GUTIERREZ PARTE DE SU CARGA POR 1336-8 | S21122300000 | 1st_after_momentary |  |  | Include | Wildlife | 1 | 2021-12-23 | 600 | keep | 0 | Dec | 2021 | 0.00040866 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2021-12-23 12:51 | 2021-12-23 12:52 | 5290 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO NO RECERRO INFORMARON GLOBO CRUZANDO FASE CALLE FELIPE GUTIERREZ LLEVANDO 1336-9 Y 30% 1204-4 | S21122300000 | 1st_after_momentary |  |  | Include | Wildlife | 1 | 2021-12-23 | 5290 | keep | 0 | Dec | 2021 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2021-12-23 12:51 | 2021-12-23 12:52 | 207 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO NO RECERRO INFORMARON GLOBO CRUZANDO FASE CALLE FELIPE GUTIERREZ SU CARGA POR 1336-8 Y 30% 1204-4 | S21122300000 | 1st_after_momentary |  |  | Include | Wildlife | 1 | 2021-12-23 | 207 | keep | 0 | Dec | 2021 | 0.00014099 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
PONCE | 2021-12-23 13:03 | 2021-12-23 16:17 | 50 | 003:14 | P | NO SE REPORTO CAUSA | 1 X 40 EN SWITCH UNIT NO SE REPORTO CAUSA | P21122300020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 194 | 2021-12-23 | 9700 | keep | 0 | Dec | 2021 | 0.0066066 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-12-23 13:13 | 2021-12-23 17:30 | 5 | 004:17 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHO | C21122300052 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 257 | 2021-12-23 | 1285 | keep | 0 | Dec | 2021 | 0.00087521 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-12-23 13:13 | 2021-12-23 20:12 | 12 | 006:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M21122300041 | New_Event | Bad Weather | Include | Include | Weather | 419 | 2021-12-23 | 5028 | keep | 0 | Dec | 2021 | 0.0034245 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-12-23 13:22 | 2021-12-23 14:06 | 12 | 000:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21122300024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 44 | 2021-12-23 | 528 | keep | 0 | Dec | 2021 | 0.00035962 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2021-12-23 13:27 | 2021-12-23 14:50 | 1 | 001:23 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | P21122300027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2021-12-23 | 83 | keep | 0 | Dec | 2021 | 5.6531e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-23 13:29 | 2021-12-23 16:58 | 5 | 003:29 | P | DESGANCHE | 1 X 50 EN RISER 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21122300119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2021-12-23 | 1045 | keep | 0 | Dec | 2021 | 0.00071174 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-12-23 13:34 | 2021-12-23 14:45 | 50 | 001:11 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR | B21122300122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 71 | 2021-12-23 | 3550 | keep | 0 | Dec | 2021 | 0.0024179 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2021-12-23 14:12 | 2021-12-23 16:18 | 25 | 002:06 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | R21122300039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2021-12-23 | 3150 | keep | 0 | Dec | 2021 | 0.0021455 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-12-23 14:24 | 2021-12-23 18:56 | 20 | 004:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | S21122300061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 272 | 2021-12-23 | 5440 | keep | 0 | Dec | 2021 | 0.0037052 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-12-23 14:29 | 2021-12-23 18:28 | 50 | 003:59 | P | DESGANCHE | 1 X 50 EN C/L | C21122300061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2021-12-23 | 11950 | keep | 0 | Dec | 2021 | 0.0081391 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-12-23 15:01 | 2021-12-23 15:28 | 225 | 000:27 | T | NO SE REPORTO CAUSA | DISPARO CON R/R ON SE PROBO POR CONTROL DIO FAIL TO OPERATE SE CERRO LOCALMENTE EN COORDINACION GRUPO PATRULLANDO LINEA SU CARGA 1303-5 | S21122300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 27 | 2021-12-23 | 6075 | keep | 0 | Dec | 2021 | 0.0041377 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-12-23 15:01 | 2021-12-23 15:28 | 870 | 000:27 | T | NO SE REPORTO CAUSA | DISPARO CON R/R ON SE PROBO POR CONTROL DIO FAIL TO OPERATE SE CERRO LOCALMENTE EN COORDINACION GRUPO PATRULLANDO LINEA LLEVA CARGA 1303-4 | S21122300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 27 | 2021-12-23 | 23490 | keep | 0 | Dec | 2021 | 0.015999 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
BARRANQUITAS | 2021-12-23 15:01 | 2021-12-23 18:28 | 200 | 003:27 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA NO CERRO ORDENES | C21122300067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2021-12-23 | 41400 | keep | 0 | Dec | 2021 | 0.028197 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2021-12-23 15:10 | 2021-12-23 15:39 | 4 | 000:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21122300053 | New_Event | Secondary Wire Down | Include | Include | Equipment | 29 | 2021-12-23 | 116 | keep | 0 | Dec | 2021 | 7.9007e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-12-23 15:16 | 2021-12-23 17:36 | 70 | 002:20 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | A21122300055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2021-12-23 | 9800 | keep | 0 | Dec | 2021 | 0.0066747 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2021-12-23 15:28 | 2021-12-23 16:31 | 200 | 001:03 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S21122300008 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 63 | 2021-12-23 | 12600 | keep | 0 | Dec | 2021 | 0.0085818 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-12-23 15:56 | 2021-12-24 13:16 | 1 | 021:20 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | R21122300061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1280 | 2021-12-23 | 1280 | keep | 0 | Dec | 2021 | 0.0008718 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-23 16:10 | 2021-12-23 16:36 | 8 | 000:26 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA PODER RETIRAR ARBOL SOBRE LAS LINEAS PRIMARIAS | M21122300057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 26 | 2021-12-23 | 208 | keep | 0 | Dec | 2021 | 0.00014167 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-12-23 16:14 | 2021-12-23 18:02 | 10 | 001:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BARRAS DE PEDESTAL | S21122300062 | New_Event | Secondary Wire Down | Include | Include | Equipment | 108 | 2021-12-23 | 1080 | keep | 0 | Dec | 2021 | 0.00073558 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-23 16:15 | 2021-12-23 17:16 | 12 | 001:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21122300134 | New_Event | Secondary Wire Down | Include | Include | Equipment | 61 | 2021-12-23 | 732 | keep | 0 | Dec | 2021 | 0.00049856 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2021-12-23 16:18 | 2021-12-23 17:47 | 55 | 001:29 | P | DESGANCHE | 1 X 65 EN C/L | C21122300083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2021-12-23 | 4895 | keep | 0 | Dec | 2021 | 0.003334 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
ARECIBO | 2021-12-23 16:19 | 2021-12-24 12:09 | 8 | 019:50 | P | HERRAJE ROTO O PODRIDO | 2 X 10 EN TRANSFORMADOR SE REMPLAZO CRUCETA PARTIDA | A21122300064 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 1190 | 2021-12-23 | 9520 | keep | 0 | Dec | 2021 | 0.006484 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-12-23 16:25 | 2021-12-23 16:26 | 271 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21122300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-23 | 271 | keep | 0 | Dec | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
AGUADILLA | 2021-12-23 16:31 | 2021-12-24 11:50 | 200 | 019:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO ABIERTO SE RETEZO LINEA PRIMARIA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | M21122300058 | New_Event | Wire Down | Include | Include | Equipment | 1159 | 2021-12-23 | 231800 | keep | 0 | Dec | 2021 | 0.15788 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
UTUADO | 2021-12-23 16:35 | 2021-12-23 18:52 | 6 | 002:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA INSTALAR TENSOR ENDEREZAR POSTE Y RETEZAR LINEA PRIMARIA | A21122300066 | New_Event | Wire Down | Include | Include | Equipment | 137 | 2021-12-23 | 822 | keep | 0 | Dec | 2021 | 0.00055986 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-12-23 16:43 | 2021-12-23 19:43 | 25 | 003:00 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 25 X 25 KVA | R21122300063 | New_Event | Service Transformer Failure | Include | Include | Equipment | 180 | 2021-12-23 | 4500 | keep | 0 | Dec | 2021 | 0.0030649 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2021-12-23 16:49 | 2021-12-23 17:01 | 40 | 000:12 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | P21122300041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 12 | 2021-12-23 | 480 | keep | 0 | Dec | 2021 | 0.00032693 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-12-23 16:58 | 2021-12-23 16:59 | 5062 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21122300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-23 | 5062 | keep | 0 | Dec | 2021 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
CAGUAS | 2021-12-23 17:10 | 2021-12-24 17:32 | 113 | 024:22 | P | DESGANCHE | ABRIO C/L PARA DESGANCHAR | C21122300094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1462 | 2021-12-23 | 165206 | keep | 0 | Dec | 2021 | 0.11252 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
MAYAGÃœEZ | 2021-12-23 17:21 | 2021-12-23 17:22 | 4381 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21122300067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-23 | 4381 | keep | 0 | Dec | 2021 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
VEGA BAJA | 2021-12-23 17:30 | 2021-12-23 18:52 | 10 | 001:22 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B21122300153 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 82 | 2021-12-23 | 820 | keep | 0 | Dec | 2021 | 0.0005585 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-23 17:46 | 2021-12-23 18:47 | 12 | 001:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21122200209 | New_Event | Secondary Wire Down | Include | Include | Equipment | 61 | 2021-12-23 | 732 | keep | 0 | Dec | 2021 | 0.00049856 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2021-12-23 17:59 | 2021-12-23 21:00 | 150 | 003:01 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA POR DESGANCHE | P21122300044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2021-12-23 | 27150 | keep | 0 | Dec | 2021 | 0.018492 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-12-23 18:35 | 2021-12-23 21:00 | 40 | 002:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21122300074 | New_Event | Bad Weather | Include | Include | Weather | 145 | 2021-12-23 | 5800 | keep | 0 | Dec | 2021 | 0.0039504 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-12-23 18:47 | 2021-12-23 21:39 | 10 | 002:52 | P | OTRAS CAUSAS | 1 X 15 EN TRANSFORMADOR EL FUSIBLE ESTABA PODRIDO(OXIDADO) | A21122300069 | New_Event | Other Causes | Include | Include | Other | 172 | 2021-12-23 | 1720 | keep | 0 | Dec | 2021 | 0.0011715 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-23 19:55 | 2021-12-23 19:56 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21122300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-23 | 312 | keep | 0 | Dec | 2021 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2021-12-23 20:17 | 2021-12-23 20:54 | 15 | 000:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | R21122300066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 37 | 2021-12-23 | 555 | keep | 0 | Dec | 2021 | 0.00037801 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-12-23 21:20 | 2021-12-23 23:20 | 150 | 002:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M21122300095 | New_Event | Bad Weather | Include | Include | Weather | 120 | 2021-12-23 | 18000 | keep | 0 | Dec | 2021 | 0.01226 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2021-12-23 22:07 | 2021-12-24 08:36 | 1 | 010:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA SE RETIRO RATON CRUZANDO LINEA | B21122300171 | New_Event |  |  | Include | Wildlife | 629 | 2021-12-23 | 629 | keep | 0 | Dec | 2021 | 0.00042841 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-12-23 22:45 | 2021-12-23 22:47 | 2126 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C21122300112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-23 | 4252 | keep | 0 | Dec | 2021 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
ARECIBO | 2021-12-23 23:09 | 2021-12-24 14:59 | 20 | 015:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A21122300072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 950 | 2021-12-23 | 19000 | keep | 0 | Dec | 2021 | 0.012941 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-12-24 00:04 | 2021-12-24 10:35 | 50 | 010:31 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO CAUSA | C21122400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 631 | 2021-12-24 | 31550 | keep | 0 | Dec | 2021 | 0.021489 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-12-24 00:29 | 2021-12-24 02:11 | 2566 | 001:42 | T | DESCONECTIVO DEFECTUOSO | DISPARO SE ABRIO SU-14 A SU-12 AVE. PONCE DE LEON SE CERRO INTERRUPTOR 20% EN SERVICIO Y FUERA 5%CARGA 1115-5 | S21122400001 | New_Event | Switch Failure | Include | Include | Equipment | 102 | 2021-12-24 | 261732 | keep | 0 | Dec | 2021 | 0.17826 | 0.0017477 | Sustained | FALSE | FALSE | Not_TMED_Event | 2566
BAYAMON | 2021-12-24 00:29 | 2021-12-24 02:51 | 40 | 002:22 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO POR TOMA AVERIADA DE CLIENTE FIRST BANK | S21122400001 | New_Event | UG Cable Fault | Include | Include | Equipment | 142 | 2021-12-24 | 5680 | keep | 0 | Dec | 2021 | 0.0038686 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-12-24 02:11 | 2021-12-24 02:39 | 1300 | 000:28 | P | CABLE SOTERRADO AVERIADO | SE ABRIO V.S.MH-3 TODAS LAS VIAS Y SE CERRO SU-14 AVE. PONCE DE LEON 50% EN SERVICIO | S21122400001 | New_Event | UG Cable Fault | Include | Include | Equipment | 28 | 2021-12-24 | 36400 | keep | 0 | Dec | 2021 | 0.024792 | 0.00088542 | Sustained | FALSE | FALSE | Not_TMED_Event | 1300
MAYAGÃœEZ | 2021-12-24 02:26 | 2021-12-25 14:14 | 4 | 035:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN RISER POR MAL TIEMPO | M21122400001 | New_Event | Bad Weather | Include | Include | Weather | 2148 | 2021-12-24 | 8592 | keep | 0 | Dec | 2021 | 0.005852 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-12-24 02:39 | 2021-12-24 02:50 | 390 | 000:11 | P | CABLE SOTERRADO AVERIADO | SE CERRO V.S. MH-3 A SU-23 80% EN SERVICIO | S21122400001 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 11 | 2021-12-24 | 4290 | keep | 0 | Dec | 2021 | 0.0029219 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-24 02:50 | 2021-12-24 02:51 | 2566 | 000:01 | T | CABLE SOTERRADO AVERIADO | DISPARO AL CERRAR V.S. MH-3 A MH-5 | S21122400001 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1 | 2021-12-24 | 2566 | keep | 0 | Dec | 2021 | 0.0017477 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-24 02:51 | 2021-12-24 03:32 | 507 | 000:41 | P | CABLE SOTERRADO AVERIADO | SE ABRIO MH-11A A MH-5 CIUDADELA 95% EN SERVICIO | S21122400001 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 41 | 2021-12-24 | 20787 | keep | 0 | Dec | 2021 | 0.014158 | 0.00034532 | Sustained | FALSE | FALSE | Not_TMED_Event | 507
AGUADILLA | 2021-12-24 03:20 | 2021-12-24 03:21 | 1192 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERE DE INTERRUPTOR | M21122400002 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-12-24 | 1192 | keep | 0 | Dec | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2021-12-24 03:21 | 2021-12-24 09:29 | 60 | 006:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21122300079 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 368 | 2021-12-24 | 22080 | keep | 0 | Dec | 2021 | 0.015039 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-12-24 03:32 | 2021-12-24 03:33 | 2566 | 000:01 | T | CABLE SOTERRADO AVERIADO | DISPARO AL CERRA DE V.S. 11A A MH-11B Y SE ABRIO Y SE CERRO INTERRUPTOR 95% EN SERVICIO | S21122400001 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1 | 2021-12-24 | 2566 | keep | 0 | Dec | 2021 | 0.0017477 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-24 03:33 | 2021-12-24 11:05 | 40 | 007:32 | P | CABLE SOTERRADO AVERIADO | DISPARO AL CERRAR V.S. 11 A MH-11B SE ENCONTRO TOMA AVERIA DE BANCO FIRST BANK SE ORIENTO A CLIENTE | S21122400001 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 452 | 2021-12-24 | 18080 | keep | 0 | Dec | 2021 | 0.012314 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-12-24 05:08 | 2021-12-24 11:51 | 1 | 006:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR PEDESTAL SECUNDARIO | M21122400003 | New_Event | Secondary Wire Down | Include | Include | Equipment | 403 | 2021-12-24 | 403 | keep | 0 | Dec | 2021 | 0.00027448 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-24 06:39 | 2021-12-24 11:45 | 20 | 005:06 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 75 KVA X 100 KVA | R21122400002 | New_Event | Service Transformer Failure | Include | Include | Equipment | 306 | 2021-12-24 | 6120 | keep | 0 | Dec | 2021 | 0.0041683 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-12-24 07:18 | 2021-12-24 10:42 | 10 | 003:24 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | B21122400004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 204 | 2021-12-24 | 2040 | keep | 0 | Dec | 2021 | 0.0013894 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-12-24 07:28 | 2021-12-24 14:10 | 50 | 006:42 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN C/L REMPLAZO 3 PARARRAYOS Y INSTALO C/L | C21122400010 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 402 | 2021-12-24 | 20100 | keep | 0 | Dec | 2021 | 0.01369 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2021-12-24 07:38 | 2021-12-24 07:39 | 2635 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21122400013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-24 | 2635 | keep | 0 | Dec | 2021 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
SAN JUAN | 2021-12-24 08:37 | 2021-12-24 11:54 | 35 | 003:17 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S21122400018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 197 | 2021-12-24 | 6895 | keep | 0 | Dec | 2021 | 0.0046962 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
HUMACAO | 2021-12-24 08:57 | 2021-12-24 08:58 | 3902 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21122400023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-24 | 3902 | keep | 0 | Dec | 2021 | 0.0026576 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
SAN JUAN | 2021-12-24 09:02 | 2021-12-24 12:19 | 10 | 003:17 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S21122400021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 197 | 2021-12-24 | 1970 | keep | 0 | Dec | 2021 | 0.0013418 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2021-12-24 09:06 | 2021-12-24 12:01 | 1 | 002:55 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21122400001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2021-12-24 | 175 | keep | 0 | Dec | 2021 | 0.00011919 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-24 09:08 | 2021-12-24 11:44 | 100 | 002:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | S21122400023 | New_Event |  |  | Include | Wildlife | 156 | 2021-12-24 | 15600 | keep | 0 | Dec | 2021 | 0.010625 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2021-12-24 09:08 | 2021-12-24 17:54 | 6 | 008:46 | P | ESTRUCTURA AVERIADA | 1 X 15 EN XMR REMPLAZO POSTE PARTIDO Y CRUCETA | R21122400006 | New_Event | Defective Pole | Include | Include | Equipment | 526 | 2021-12-24 | 3156 | keep | 0 | Dec | 2021 | 0.0021495 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-12-24 09:16 | 2021-12-24 10:39 | 10 | 001:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 10 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA PARTIDA POR CAMION | P21122400004 | New_Event |  |  | Include | Wildlife | 83 | 2021-12-24 | 830 | keep | 0 | Dec | 2021 | 0.00056531 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-12-24 09:22 | 2021-12-24 13:00 | 30 | 003:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEAS CRUCE DE FASE PRIMARIA POR AVE | P21122400005 | New_Event |  |  | Include | Wildlife | 218 | 2021-12-24 | 6540 | keep | 0 | Dec | 2021 | 0.0044544 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-24 09:29 | 2021-12-24 15:00 | 15 | 005:31 | P | PARARRAYOS DEFECTUOSO | 2 X 15 EN TRANSFORMADOR SE ELIMINO PARARRAYO | B21122400010 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 331 | 2021-12-24 | 4965 | keep | 0 | Dec | 2021 | 0.0033816 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-12-24 09:30 | 2021-12-24 12:16 | 40 | 002:46 | P | DESGANCHE | 1 X 80 EN C/L | R21122400007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2021-12-24 | 6640 | keep | 0 | Dec | 2021 | 0.0045225 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-24 09:37 | 2021-12-24 09:39 | 462 | 000:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1716-03 LLEVANDO 80% 1711-01 Y EL 100% 1711-03 PUENTE ABIERTO EN MACHETE | B21122400012 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2021-12-24 | 924 | keep | 0 | Dec | 2021 | 0.00062933 | 0.00031467 | Momentary | FALSE | FALSE | Not_TMED_Event | 462
BAYAMON | 2021-12-24 09:37 | 2021-12-24 09:39 | 13 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1716-03 LLEVANDO 80% DEL 1711-01 Y EL 100% 1711-03 PUENTE ABIERTO EN MACHETE | B21122400012 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2021-12-24 | 26 | keep | 0 | Dec | 2021 | 1.7708e-05 | 8.8542e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2021-12-24 09:37 | 2021-12-24 09:39 | 1812 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1716-03 LLEVANDO 80% 1711-01 Y EL 100% DE LA CARGA DEL 1711-03 PUENTE ABIERTO EN MACHETE | B21122400012 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2021-12-24 | 3624 | keep | 0 | Dec | 2021 | 0.0024683 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
BAYAMON | 2021-12-24 09:39 | 2021-12-24 12:50 | 300 | 003:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO EN MACHETE CARR PR-177 EN PUENTE ROSSO | B21122400018 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 191 | 2021-12-24 | 57300 | keep | 0 | Dec | 2021 | 0.039027 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
GUAYAMA | 2021-12-24 09:39 | 2021-12-24 10:47 | 173 | 001:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P21122400010 | New_Event |  |  | Include | Wildlife | 68 | 2021-12-24 | 11764 | keep | 0 | Dec | 2021 | 0.0080124 | 0.00011783 | Sustained | FALSE | FALSE | Not_TMED_Event | 173
HUMACAO | 2021-12-24 09:46 | 2021-12-24 10:27 | 6 | 000:41 | P | TRANSFORMADOR AVERIADO | ABRIO XMR PARA REMPLAZAR BUSHING DEL NEUTRAL PRIMARIO | C21122400006 | New_Event | Service Transformer Failure | Include | Include | Equipment | 41 | 2021-12-24 | 246 | keep | 0 | Dec | 2021 | 0.00016755 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2021-12-24 09:48 | 2021-12-24 17:04 | 15 | 007:16 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO | P21122400011 | New_Event | Service Transformer Failure | Include | Include | Equipment | 436 | 2021-12-24 | 6540 | keep | 0 | Dec | 2021 | 0.0044544 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-12-24 09:54 | 2021-12-24 11:54 | 100 | 002:00 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21122400028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2021-12-24 | 12000 | keep | 0 | Dec | 2021 | 0.0081731 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-12-24 09:55 | 2021-12-24 10:11 | 2 | 000:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR REMPLAZAR CONECTORES | M21122400021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 16 | 2021-12-24 | 32 | keep | 0 | Dec | 2021 | 2.1795e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2021-12-24 10:15 | 2021-12-24 11:48 | 18 | 001:33 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50KVA A 2.4KV POR ESCAPE DE ACEITE | P21122400012 | New_Event | Service Transformer Failure | Include | Include | Equipment | 93 | 2021-12-24 | 1674 | keep | 0 | Dec | 2021 | 0.0011402 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
HUMACAO | 2021-12-24 10:21 | 2021-12-24 12:55 | 30 | 002:34 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L NO CAUSA | C21122400029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 154 | 2021-12-24 | 4620 | keep | 0 | Dec | 2021 | 0.0031467 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-24 10:22 | 2021-12-24 16:24 | 25 | 006:02 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S21122400037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 362 | 2021-12-24 | 9050 | keep | 0 | Dec | 2021 | 0.0061639 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2021-12-24 10:24 | 2021-12-24 12:08 | 5 | 001:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO SECUNDARIA Y REGULO XMR BAJO TAP 3 AL 2 QUEDO 121/242 | C21122400030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 104 | 2021-12-24 | 520 | keep | 0 | Dec | 2021 | 0.00035417 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2021-12-24 10:30 | 2021-12-24 11:43 | 6 | 001:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | M21122400026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 73 | 2021-12-24 | 438 | keep | 0 | Dec | 2021 | 0.00029832 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-12-24 10:35 | 2021-12-24 11:25 | 7 | 000:50 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5KVA A 2.4 KV AVERIADO | P21122400014 | New_Event | Service Transformer Failure | Include | Include | Equipment | 50 | 2021-12-24 | 350 | keep | 0 | Dec | 2021 | 0.00023838 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2021-12-24 10:48 | 2021-12-24 12:19 | 1 | 001:31 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21122400050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 91 | 2021-12-24 | 91 | keep | 0 | Dec | 2021 | 6.198e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-24 11:05 | 2021-12-24 11:06 | 2566 | 000:01 | T | CABLE SOTERRADO AVERIADO | DISPARO TOMA AVERIADA DE V.S. MH-11B A FIRST BANK | S21122400001 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2021-12-24 | 2566 | keep | 0 | Dec | 2021 | 0.0017477 | 0.0017477 | Momentary | FALSE | FALSE | Not_TMED_Event | 2566
SAN JUAN | 2021-12-24 11:06 | 2021-12-24 12:47 | 10 | 001:41 | P | CABLE SOTERRADO AVERIADO | SE CERRO V.S.11A MH-11B 100% EN SERVICIO SE DESCONECTO TOMA CLIENTE | S21122400001 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 101 | 2021-12-24 | 1010 | keep | 0 | Dec | 2021 | 0.00068791 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-24 11:28 | 2021-12-25 10:35 | 100 | 023:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN C/L REMPLAZO PORTAFUSIBLE QUEMADO | R21122400035 | New_Event | Cutout Failure | Include | Include | Equipment | 1387 | 2021-12-24 | 138700 | keep | 0 | Dec | 2021 | 0.094468 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-12-24 11:52 | 2021-12-24 15:45 | 15 | 003:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA EN TRANSFORMADOR QUEMADA | A21122400013 | New_Event | Cutout Failure | Include | Include | Equipment | 233 | 2021-12-24 | 3495 | keep | 0 | Dec | 2021 | 0.0023804 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-12-24 11:55 | 2021-12-24 15:28 | 7 | 003:33 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 37.5 KVA X 37.5 KVA | C21122400035 | New_Event | Service Transformer Failure | Include | Include | Equipment | 213 | 2021-12-24 | 1491 | keep | 0 | Dec | 2021 | 0.0010155 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-12-24 12:00 | 2021-12-24 16:13 | 20 | 004:13 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO DE 45' MADERA POR UNO DE 45' METAL | M21122400034 | New_Event | Defective Pole | Include | Include | Equipment | 253 | 2021-12-24 | 5060 | keep | 0 | Dec | 2021 | 0.0034463 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2021-12-24 12:11 | 2021-12-24 12:12 | 2844 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR REALIZA TRES OPERACIONES Y QUEDA EN SERVICIO | P21122400021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-24 | 2844 | keep | 0 | Dec | 2021 | 0.001937 | 0.001937 | Momentary | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2021-12-24 12:12 | 2021-12-24 13:57 | 300 | 001:45 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P21122400022 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 105 | 2021-12-24 | 31500 | keep | 0 | Dec | 2021 | 0.021455 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2021-12-24 12:19 | 2021-12-24 14:48 | 11 | 002:29 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 50 KVA X 50 KVA | C21122400036 | New_Event | Service Transformer Failure | Include | Include | Equipment | 149 | 2021-12-24 | 1639 | keep | 0 | Dec | 2021 | 0.0011163 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
ARECIBO | 2021-12-24 12:30 | 2021-12-24 14:38 | 5 | 002:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | A21122400015 | New_Event | Bad Weather | Include | Include | Weather | 128 | 2021-12-24 | 640 | keep | 0 | Dec | 2021 | 0.0004359 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2021-12-24 12:51 | 2021-12-24 18:43 | 1 | 005:52 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21122400098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 352 | 2021-12-24 | 352 | keep | 0 | Dec | 2021 | 0.00023975 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-24 13:12 | 2021-12-24 16:54 | 25 | 003:42 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B21122400101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 222 | 2021-12-24 | 5550 | keep | 0 | Dec | 2021 | 0.0037801 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-12-24 13:26 | 2021-12-24 16:24 | 1 | 002:58 | P | DESGANCHE | 1 X 80 EN C/L SE REALIZO DESGANCHE | B21122400105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2021-12-24 | 178 | keep | 0 | Dec | 2021 | 0.00012123 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-24 13:27 | 2021-12-24 16:04 | 573 | 002:37 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE RETEZO LINEA Y SE ELIMINO PUENTE PARTIDO SE CERRO POR SCADA LLEVA TRANSFERIDA LA CARGA DEL 1704-05 | B21122400000 | New_Event |  |  | Include | Wildlife | 157 | 2021-12-24 | 89961 | keep | 0 | Dec | 2021 | 0.061272 | 0.00039027 | Sustained | FALSE | FALSE | Not_TMED_Event | 573
BAYAMON | 2021-12-24 13:27 | 2021-12-24 16:04 | 1313 | 002:37 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE RETEZO LINEA Y SE ELIMINO PUENTE PARTIDO SE CERRO POR SCADA CARGA POR EL 1704-04 | B21122400000 | New_Event |  |  | Include | Wildlife | 157 | 2021-12-24 | 206141 | keep | 0 | Dec | 2021 | 0.1404 | 0.00089428 | Sustained | FALSE | FALSE | Not_TMED_Event | 1313
HUMACAO | 2021-12-24 13:31 | 2021-12-24 14:48 | 50 | 001:17 | P | DESGANCHE | 1 X 100 EN C/L | C21122400038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2021-12-24 | 3850 | keep | 0 | Dec | 2021 | 0.0026222 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-24 13:46 | 2021-12-24 17:49 | 20 | 004:03 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B21122400114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 243 | 2021-12-24 | 4860 | keep | 0 | Dec | 2021 | 0.0033101 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-12-24 13:58 | 2021-12-24 15:31 | 80 | 001:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE CRUZO LINEAS | P21122400042 | New_Event |  |  | Include | Wildlife | 93 | 2021-12-24 | 7440 | keep | 0 | Dec | 2021 | 0.0050674 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2021-12-24 14:05 | 2021-12-24 14:06 | 26 | 000:01 | P | CABLE SOTERRADO AVERIADO | CONSTUYO PROVICIONAL AEREO DEL SU - 8 AL SU - 9 | C21122300104 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2021-12-24 | 26 | keep | 0 | Dec | 2021 | 1.7708e-05 | 1.7708e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 26
AGUADILLA | 2021-12-24 14:17 | 2021-12-24 16:45 | 1 | 002:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN RISER LLUVIA | M21122400037 | New_Event | Bad Weather | Include | Include | Weather | 148 | 2021-12-24 | 148 | keep | 0 | Dec | 2021 | 0.0001008 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-12-24 14:20 | 2021-12-25 00:56 | 15 | 010:36 | P | CABLE SOTERRADO AVERIADO | SE PREPARO PROVISIONAL AEREO HACIA T-5 | B21122400131 | New_Event | UG Cable Fault | Include | Include | Equipment | 636 | 2021-12-24 | 9540 | keep | 0 | Dec | 2021 | 0.0064977 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-12-24 14:27 | 2021-12-24 18:08 | 10 | 003:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REMPLAZO BAJANTE SECUNDARIO | A21122400020 | New_Event | Secondary Wire Down | Include | Include | Equipment | 221 | 2021-12-24 | 2210 | keep | 0 | Dec | 2021 | 0.0015052 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-24 14:31 | 2021-12-24 17:50 | 20 | 003:19 | P | NO SE REPORTO CAUSA | 1 X 15 EN RISER | B21122400133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 199 | 2021-12-24 | 3980 | keep | 0 | Dec | 2021 | 0.0027108 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-12-24 15:31 | 2021-12-24 21:26 | 8 | 005:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REMPLAZO BARRA EN PEDESTAL | A21122400024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 355 | 2021-12-24 | 2840 | keep | 0 | Dec | 2021 | 0.0019343 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2021-12-24 15:38 | 2021-12-24 17:00 | 100 | 001:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | P21122400052 | New_Event |  |  | Include | Wildlife | 82 | 2021-12-24 | 8200 | keep | 0 | Dec | 2021 | 0.005585 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2021-12-24 15:49 | 2021-12-24 19:30 | 15 | 003:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ABIERTO | P21122400054 | New_Event | Wire Down | Include | Include | Equipment | 221 | 2021-12-24 | 3315 | keep | 0 | Dec | 2021 | 0.0022578 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-12-24 16:09 | 2021-12-24 16:10 | 6481 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21122400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-24 | 6481 | keep | 0 | Dec | 2021 | 0.0044142 | 0.0044142 | Momentary | FALSE | FALSE | Not_TMED_Event | 6481
SAN JUAN | 2021-12-24 16:09 | 2021-12-24 16:10 | 60 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 85% X 1620-1 | S21122400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-24 | 60 | keep | 0 | Dec | 2021 | 4.0866e-05 | 4.0866e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2021-12-24 16:16 | 2021-12-24 17:57 | 6 | 001:41 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | C21122400042 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 101 | 2021-12-24 | 606 | keep | 0 | Dec | 2021 | 0.00041274 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-12-24 16:18 | 2021-12-24 18:39 | 5 | 002:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR NEUTRAL SECUNDARIO | C21122400043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 141 | 2021-12-24 | 705 | keep | 0 | Dec | 2021 | 0.00048017 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2021-12-24 16:42 | 2021-12-24 16:43 | 1648 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21122400019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-24 | 1648 | keep | 0 | Dec | 2021 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
ARECIBO | 2021-12-24 17:20 | 2021-12-24 21:23 | 100 | 004:03 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | A21122400027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2021-12-24 | 24300 | keep | 0 | Dec | 2021 | 0.016551 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-12-24 17:35 | 2021-12-24 19:36 | 5 | 002:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA QUEMADA | A21122400028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 121 | 2021-12-24 | 605 | keep | 0 | Dec | 2021 | 0.00041206 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-12-24 17:55 | 2021-12-24 21:49 | 40 | 003:54 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO CAUSA | R21122400022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 234 | 2021-12-24 | 9360 | keep | 0 | Dec | 2021 | 0.0063751 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-24 18:38 | 2021-12-24 18:40 | 1040 | 000:02 | P | NO SE REPORTO CAUSA | SE CERRO POR SCADA 80% DEL 1711-01 ESTA TRANSFERIDO AL 1716-03 | B21122400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-24 | 2080 | keep | 0 | Dec | 2021 | 0.0014167 | 0.00070834 | Momentary | FALSE | FALSE | Not_TMED_Event | 1040
BAYAMON | 2021-12-24 18:38 | 2021-12-24 18:40 | 13 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1716-03 | B21122400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-24 | 26 | keep | 0 | Dec | 2021 | 1.7708e-05 | 8.8542e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2021-12-24 18:38 | 2021-12-24 18:40 | 1812 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA LA CARGA TOTAL DEL 1711-03 Y 80% DE LA CARGA DEL 1711-01 | B21122400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-24 | 3624 | keep | 0 | Dec | 2021 | 0.0024683 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
CAGUAS | 2021-12-24 20:11 | 2021-12-25 12:07 | 30 | 015:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA PARTIDA NO FUNDIO | C21122400048 | New_Event | Cutout Failure | Include | Include | Equipment | 956 | 2021-12-24 | 28680 | keep | 0 | Dec | 2021 | 0.019534 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-24 20:34 | 2021-12-24 21:34 | 20 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B21122300167 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2021-12-24 | 1200 | keep | 0 | Dec | 2021 | 0.00081731 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-12-24 21:02 | 2021-12-24 23:13 | 60 | 002:11 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21122400170 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2021-12-24 | 7860 | keep | 0 | Dec | 2021 | 0.0053534 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-12-24 21:17 | 2021-12-25 09:46 | 120 | 012:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21122400034 | New_Event | Bad Weather | Include | Include | Weather | 749 | 2021-12-24 | 89880 | keep | 0 | Dec | 2021 | 0.061217 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2021-12-24 21:30 | 2021-12-25 08:01 | 25 | 010:31 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S21122400041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 631 | 2021-12-24 | 15775 | keep | 0 | Dec | 2021 | 0.010744 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-12-24 22:16 | 2021-12-25 13:35 | 30 | 015:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS PARTIDAS Y REPARAR CONEXIONES SECUNDARIAS | M21122400047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 919 | 2021-12-24 | 27570 | keep | 0 | Dec | 2021 | 0.018778 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2021-12-24 22:24 | 2021-12-24 22:47 | 60 | 000:23 | P | DESGANCHE | SE ABRIO CORTE DE LINEA DE EMERGENCIA PARA RETIRAR ARBOL SOBRE LA LINEA | B21122400171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 23 | 2021-12-24 | 1380 | keep | 0 | Dec | 2021 | 0.00093991 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2021-12-24 23:14 | 2021-12-25 11:36 | 40 | 012:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN C/L Y 1 X 10 EN XMR REPARO BAJANTE DE CAJA A XMR | R21122400036 | New_Event | Wire Down | Include | Include | Equipment | 742 | 2021-12-24 | 29680 | keep | 0 | Dec | 2021 | 0.020215 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-24 23:22 | 2021-12-25 09:35 | 20 | 010:13 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21122400178 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 613 | 2021-12-24 | 12260 | keep | 0 | Dec | 2021 | 0.0083502 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-12-25 00:51 | 2021-12-25 10:00 | 4946 | 009:09 | P | NO SE REPORTO CAUSA | CERRO EL IR 2603-8F NO CAUSA | C21122500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 549 | 2021-12-25 | 2715354 | keep | 0 | Dec | 2021 | 1.8494 | 0.0033687 | Sustained | FALSE | FALSE | Not_TMED_Event | 4946
AGUADILLA | 2021-12-25 00:52 | 2021-12-25 11:18 | 45 | 010:26 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21122500002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 626 | 2021-12-25 | 28170 | keep | 0 | Dec | 2021 | 0.019186 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2021-12-25 01:10 | 2021-12-25 01:11 | 4533 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21122500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-25 | 4533 | keep | 0 | Dec | 2021 | 0.0030874 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
VEGA BAJA | 2021-12-25 01:30 | 2021-12-25 01:37 | 776 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV EN VEGA BAJA TC | B21122500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2021-12-25 | 5432 | keep | 0 | Dec | 2021 | 0.0036997 | 0.00052853 | Sustained | FALSE | FALSE | Not_TMED_Event | 776
VEGA BAJA | 2021-12-25 01:30 | 2021-12-25 01:37 | 2216 | 000:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV EN VEGA BAJA TC | B21122500000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2021-12-25 | 15512 | keep | 0 | Dec | 2021 | 0.010565 | 0.0015093 | Sustained | FALSE | FALSE | Not_TMED_Event | 2216
VEGA BAJA | 2021-12-25 01:30 | 2021-12-25 01:34 | 4702 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA LA CARGA DEL 9105-07 | B21122500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-12-25 | 18808 | keep | 0 | Dec | 2021 | 0.01281 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2021-12-25 01:30 | 2021-12-25 01:34 | 215 | 000:04 | T | NO SE REPORTO CAUSA | CARGA TRANSFERIDA AL 9004-10 | B21122500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-12-25 | 860 | keep | 0 | Dec | 2021 | 0.00058574 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
HUMACAO | 2021-12-25 01:48 | 2021-12-25 11:20 | 60 | 009:32 | P | DESGANCHE | 1 X 65 EN C/L | C21122500003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 572 | 2021-12-25 | 34320 | keep | 0 | Dec | 2021 | 0.023375 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2021-12-25 02:10 | 2021-12-25 02:11 | 2450 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO 2605-01 | C21122500005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-25 | 2450 | keep | 0 | Dec | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
BAYAMON | 2021-12-25 03:09 | 2021-12-25 09:39 | 20 | 006:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA CRUZANDO LINEAS | B21122500007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 390 | 2021-12-25 | 7800 | keep | 0 | Dec | 2021 | 0.0053125 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-12-25 03:21 | 2021-12-25 11:40 | 30 | 008:19 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN C/L REMPLAZO AISLADOR Y LEVANTO CONDUCTOR | C21122500008 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 499 | 2021-12-25 | 14970 | keep | 0 | Dec | 2021 | 0.010196 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2021-12-25 03:34 | 2021-12-25 03:35 | 4085 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21122500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-25 | 4085 | keep | 0 | Dec | 2021 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
AGUADILLA | 2021-12-25 03:47 | 2021-12-25 03:48 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21122500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-25 | 3041 | keep | 0 | Dec | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
CAGUAS | 2021-12-25 04:12 | 2021-12-25 04:13 | 1590 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21122500009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-25 | 1590 | keep | 0 | Dec | 2021 | 0.0010829 | 0.0010829 | Momentary | FALSE | FALSE | Not_TMED_Event | 1590
SAN JUAN | 2021-12-25 04:18 | 2021-12-25 04:20 | 143 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA 80% 1404-07 | S21122500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-25 | 286 | keep | 0 | Dec | 2021 | 0.00019479 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2021-12-25 04:18 | 2021-12-25 04:20 | 1000 | 000:02 | P | NO SE REPORTO CAUSA | 80% DE LA CARGA TRANSFERIDA AL 1404-06 | S21122500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-25 | 2000 | keep | 0 | Dec | 2021 | 0.0013622 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2021-12-25 04:20 | 2021-12-25 11:09 | 30 | 006:49 | P | NO SE REPORTO CAUSA | 2 X 50 EN C/L | S21122500005 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 409 | 2021-12-25 | 12270 | keep | 0 | Dec | 2021 | 0.008357 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2021-12-25 04:34 | 2021-12-25 04:35 | 4702 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA LA CARGA DEL 9105-07 | B21122500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-25 | 4702 | keep | 0 | Dec | 2021 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2021-12-25 04:34 | 2021-12-25 04:35 | 215 | 000:01 | T | NO SE REPORTO CAUSA | CARGA TRANSFERIDA AL 9004-10 | B21122500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-25 | 215 | keep | 0 | Dec | 2021 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2021-12-25 04:36 | 2021-12-25 07:05 | 4702 | 002:29 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 9004-10 LLEVANDO CARGA 9105-07 SE CERRO POR SCADA ABRIENDO MACHETES DE AMARRE | B21122500013 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 149 | 2021-12-25 | 700598 | keep | 0 | Dec | 2021 | 0.47717 | 0.0032025 | Sustained | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2021-12-25 04:36 | 2021-12-25 08:17 | 215 | 003:41 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 9004-10 LLEVANDO CARGA 9105-07 SE CERRO MACHETES DE AMARRE NO SE ENCONTRO CAUSA | B21122500013 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 221 | 2021-12-25 | 47515 | keep | 0 | Dec | 2021 | 0.032362 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2021-12-25 04:39 | 2021-12-25 04:40 | 1494 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO | B21122500000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-12-25 | 1494 | keep | 0 | Dec | 2021 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
VEGA BAJA | 2021-12-25 04:41 | 2021-12-25 04:42 | 1494 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO | B21122500000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-12-25 | 1494 | keep | 0 | Dec | 2021 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
VEGA BAJA | 2021-12-25 04:44 | 2021-12-25 04:45 | 1494 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO | B21122500000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-12-25 | 1494 | keep | 0 | Dec | 2021 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
VEGA BAJA | 2021-12-25 04:49 | 2021-12-25 11:10 | 1494 | 006:21 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 9101-02 LLEVANDO CARGA 9101-04 SE CERRO POR SCADA SE LEVANTO NEUTRAL PRIMARIO | B21122500118 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 381 | 2021-12-25 | 569214 | keep | 0 | Dec | 2021 | 0.38769 | 0.0010176 | Sustained | FALSE | FALSE | Not_TMED_Event | 1494
CAGUAS | 2021-12-25 05:41 | 2021-12-25 09:04 | 3005 | 003:23 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO EL ALIMENTADOR | C21122500011 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 203 | 2021-12-25 | 610015 | keep | 0 | Dec | 2021 | 0.41548 | 0.0020467 | Sustained | FALSE | FALSE | Not_TMED_Event | 3005
BAYAMON | 2021-12-25 05:43 | 2021-12-25 11:13 | 30 | 005:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | S21122500004 | New_Event | Wire Down | Include | Include | Equipment | 330 | 2021-12-25 | 9900 | keep | 0 | Dec | 2021 | 0.0067428 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-12-25 05:54 | 2021-12-25 05:55 | 1320 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21122500000 | New_Event |  |  | Include | Wildlife | 1 | 2021-12-25 | 1320 | keep | 0 | Dec | 2021 | 0.00089905 | 0.00089905 | Momentary | FALSE | FALSE | Not_TMED_Event | 1320
CAGUAS | 2021-12-25 05:55 | 2021-12-25 12:12 | 9 | 006:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 50 EN C/L REMPLAZO POSTE PARTIDO POR VEHICULO | C21122500063 | 1st_after_momentary |  |  | Include | Wildlife | 377 | 2021-12-25 | 3393 | keep | 0 | Dec | 2021 | 0.002311 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-12-25 06:09 | 2021-12-25 06:10 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1909-08 LLEVANDO CARGA 1907-05 | S21122500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-25 | 2435 | keep | 0 | Dec | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-12-25 06:09 | 2021-12-25 06:10 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1909-08 LLEVANDO CARGA 1907-05 | S21122500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-25 | 2956 | keep | 0 | Dec | 2021 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
SAN JUAN | 2021-12-25 06:33 | 2021-12-25 11:39 | 150 | 005:06 | P | NO SE REPORTO CAUSA | 2 X 80 EN C/L NO CAUSA | R21122500005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 306 | 2021-12-25 | 45900 | keep | 0 | Dec | 2021 | 0.031262 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2021-12-25 06:37 | 2021-12-25 06:40 | 350 | 000:03 | P | NO SE REPORTO CAUSA | SE CERRO POR SCADA 30% POR EL 1529-15 | S21122500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-12-25 | 1050 | keep | 0 | Dec | 2021 | 0.00071515 | 0.00023838 | Momentary | FALSE | FALSE | Not_TMED_Event | 350
BAYAMON | 2021-12-25 06:37 | 2021-12-25 06:40 | 1802 | 000:03 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA 30% DEL 1346-02 | S21122500008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-12-25 | 5406 | keep | 0 | Dec | 2021 | 0.003682 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
FAJARDO | 2021-12-25 06:47 | 2021-12-25 10:06 | 40 | 003:19 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 Y 1 X 20 EN C/LS REMPLAZO AISLADOR ROTO | R21122500006 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 199 | 2021-12-25 | 7960 | keep | 0 | Dec | 2021 | 0.0054215 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2021-12-25 07:04 | 2021-12-25 07:05 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO | P21122500002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-25 | 3744 | keep | 0 | Dec | 2021 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
CANOVANAS | 2021-12-25 07:30 | 2021-12-25 07:43 | 2580 | 000:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11100 | R21122500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 13 | 2021-12-25 | 33540 | keep | 0 | Dec | 2021 | 0.022844 | 0.0017572 | Sustained | FALSE | FALSE | Not_TMED_Event | 2580
CANOVANAS | 2021-12-25 07:30 | 2021-12-25 07:43 | 500 | 000:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11100 | R21122500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 13 | 2021-12-25 | 6500 | keep | 0 | Dec | 2021 | 0.0044271 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CANOVANAS | 2021-12-25 07:44 | 2021-12-25 08:50 | 2580 | 001:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11100 | R21122500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 66 | 2021-12-25 | 170280 | keep | 0 | Dec | 2021 | 0.11598 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-12-25 07:44 | 2021-12-25 08:50 | 500 | 001:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11100 | R21122500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 66 | 2021-12-25 | 33000 | keep | 0 | Dec | 2021 | 0.022476 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-25 07:49 | 2021-12-25 09:46 | 1085 | 001:57 | T | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO POR SCADA | S21122500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2021-12-25 | 126945 | keep | 0 | Dec | 2021 | 0.086462 | 0.00073899 | Sustained | FALSE | FALSE | Not_TMED_Event | 1085
SAN JUAN | 2021-12-25 07:50 | 2021-12-25 12:06 | 40 | 004:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN C/L REMPLAZO CONECTOR QUEMADO EN BAJANTE PRIMARIO | R21122500012 | New_Event | Wire Down | Include | Include | Equipment | 256 | 2021-12-25 | 10240 | keep | 0 | Dec | 2021 | 0.0069744 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-25 07:59 | 2021-12-25 08:00 | 534 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1519-05 | S21122500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-25 | 534 | keep | 0 | Dec | 2021 | 0.0003637 | 0.0003637 | Momentary | FALSE | FALSE | Not_TMED_Event | 534
BAYAMON | 2021-12-25 07:59 | 2021-12-25 08:00 | 558 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA CARGA DEL 1519-01 | S21122500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-25 | 558 | keep | 0 | Dec | 2021 | 0.00038005 | 0.00038005 | Momentary | FALSE | FALSE | Not_TMED_Event | 558
SAN JUAN | 2021-12-25 08:00 | 2021-12-25 08:01 | 4291 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21122500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-25 | 4291 | keep | 0 | Dec | 2021 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
SAN JUAN | 2021-12-25 08:01 | 2021-12-25 09:58 | 20 | 001:57 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S21122500041 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 117 | 2021-12-25 | 2340 | keep | 0 | Dec | 2021 | 0.0015938 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-12-25 08:04 | 2021-12-25 09:24 | 3114 | 001:20 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR REALIZA TRES OPERACIONES SE ABRIO MACHETES EN PARCELAS MAGUEYES DEBIDO A POSTE PRIMARIO AVERIADO POR IMPACTO VEHICULO DE MOTOR | P21122500008 | New_Event |  |  | Include | Wildlife | 80 | 2021-12-25 | 249120 | keep | 0 | Dec | 2021 | 0.16967 | 0.0021209 | Sustained | FALSE | FALSE | Not_TMED_Event | 3114
CANOVANAS | 2021-12-25 08:13 | 2021-12-25 10:10 | 60 | 001:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 Y 1 X 50 EN C/L CRUCE X AVE | R21122500017 | New_Event |  |  | Include | Wildlife | 117 | 2021-12-25 | 7020 | keep | 0 | Dec | 2021 | 0.0047813 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-12-25 08:46 | 2021-12-25 11:05 | 3 | 002:19 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PARARRAYO EN MONTURA DE TRANSFORMADORES | B21122500123 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 139 | 2021-12-25 | 417 | keep | 0 | Dec | 2021 | 0.00028402 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-12-25 08:49 | 2021-12-25 13:59 | 2 | 005:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO CONEXIONES SECUNDARIAS | M21122500009 | New_Event | Secondary Wire Down | Include | Include | Equipment | 310 | 2021-12-25 | 620 | keep | 0 | Dec | 2021 | 0.00042228 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2021-12-25 09:04 | 2021-12-25 09:06 | 36 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR EL 1620-04 | S21122500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-25 | 72 | keep | 0 | Dec | 2021 | 4.9039e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-12-25 09:04 | 2021-12-25 09:06 | 172 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA 1620-01 | S21122500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-25 | 344 | keep | 0 | Dec | 2021 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
CAGUAS | 2021-12-25 09:04 | 2021-12-25 10:24 | 1000 | 001:20 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO NO CAUSA | C21122500117 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 80 | 2021-12-25 | 80000 | keep | 0 | Dec | 2021 | 0.054488 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-12-25 09:08 | 2021-12-25 11:32 | 1 | 002:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REMPLAZO PORTAFUSIBLE | C21122500059 | New_Event | Cutout Failure | Include | Include | Equipment | 144 | 2021-12-25 | 144 | keep | 0 | Dec | 2021 | 9.8078e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2021-12-25 09:09 | 2021-12-25 10:50 | 20 | 001:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR BAJANTES Y CONECTORES SECUNDARIOS | P21122500025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 101 | 2021-12-25 | 2020 | keep | 0 | Dec | 2021 | 0.0013758 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2021-12-25 09:22 | 2021-12-25 13:55 | 4 | 004:33 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO 37.5 KVA A 4.16 KV | P21122500028 | New_Event | Service Transformer Failure | Include | Include | Equipment | 273 | 2021-12-25 | 1092 | keep | 0 | Dec | 2021 | 0.00074376 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2021-12-25 09:24 | 2021-12-25 14:00 | 31 | 004:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REMPLAZO POSTE PRIMARIO PARTIDO POR IMPACTO DE VEHICULO Y SE CERRO MACHETES | P21122500037 | Partial_restoration |  |  | Include | Wildlife | 276 | 2021-12-25 | 8556 | keep | 0 | Dec | 2021 | 0.0058275 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-12-25 09:29 | 2021-12-25 09:30 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21122500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-25 | 1827 | keep | 0 | Dec | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
VEGA BAJA | 2021-12-25 09:30 | 2021-12-25 20:25 | 1 | 010:55 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21122500146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 655 | 2021-12-25 | 655 | keep | 0 | Dec | 2021 | 0.00044612 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-25 09:47 | 2021-12-25 15:22 | 60 | 005:35 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR POSTE PARTIDO | B21122500001 | New_Event | Defective Pole | Include | Include | Equipment | 335 | 2021-12-25 | 20100 | keep | 0 | Dec | 2021 | 0.01369 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-12-25 10:00 | 2021-12-25 10:18 | 15 | 000:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21122400045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 18 | 2021-12-25 | 270 | keep | 0 | Dec | 2021 | 0.0001839 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-12-25 10:15 | 2021-12-25 16:09 | 15 | 005:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | M21122500013 | New_Event | Bad Weather | Include | Include | Weather | 354 | 2021-12-25 | 5310 | keep | 0 | Dec | 2021 | 0.0036166 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-12-25 10:24 | 2021-12-25 11:04 | 1000 | 000:40 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR ROTO | C21122500011 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 40 | 2021-12-25 | 40000 | keep | 0 | Dec | 2021 | 0.027244 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
PONCE | 2021-12-25 10:27 | 2021-12-25 10:28 | 4035 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21122500044 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-12-25 | 4035 | keep | 0 | Dec | 2021 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
PONCE | 2021-12-25 10:28 | 2021-12-25 12:43 | 800 | 002:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CAJA DE SALIDA DE CONVERTIDOR Y SE REMPLAZO CAJA AVERIADA EN UNA SEGUNDA FASE PRIMARIA DE LA SALIDA DEL CONVERTIDOR | P21122500057 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 135 | 2021-12-25 | 108000 | keep | 0 | Dec | 2021 | 0.073558 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
SAN JUAN | 2021-12-25 10:37 | 2021-12-25 12:32 | 25 | 001:55 | P | NO SE REPORTO CAUSA | 2 X 15 EN XMR | S21122500062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2021-12-25 | 2875 | keep | 0 | Dec | 2021 | 0.0019581 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2021-12-25 10:47 | 2021-12-25 12:57 | 40 | 002:10 | P | DESGANCHE | ABRIO C/L PARA RETIRAR ARBOL DE LA LINEA | R21122500011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2021-12-25 | 5200 | keep | 0 | Dec | 2021 | 0.0035417 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-12-25 10:48 | 2021-12-25 16:35 | 70 | 005:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21122500007 | New_Event | Wire Down | Include | Include | Equipment | 347 | 2021-12-25 | 24290 | keep | 0 | Dec | 2021 | 0.016544 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2021-12-25 11:04 | 2021-12-25 13:27 | 2005 | 002:23 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR QUEMADO Y CAJA AVERIADA | C21122500011 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 143 | 2021-12-25 | 286715 | keep | 0 | Dec | 2021 | 0.19528 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-12-25 11:07 | 2021-12-25 11:08 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21122500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-25 | 1702 | keep | 0 | Dec | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2021-12-25 11:08 | 2021-12-25 16:49 | 5 | 005:41 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | C21122500199 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 341 | 2021-12-25 | 1705 | keep | 0 | Dec | 2021 | 0.0011613 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-12-25 11:15 | 2021-12-25 13:26 | 20 | 002:11 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S21122500065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 131 | 2021-12-25 | 2620 | keep | 0 | Dec | 2021 | 0.0017845 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-12-25 11:53 | 2021-12-25 18:26 | 45 | 006:33 | P | CABLE SOTERRADO AVERIADO | AVERIA NUEVA T-2 A SU-4 AVERIA VIEJA T-3 SE DEJO EN PARKING BUSHING SE CERRO N/O T-7 A T-8 1 X 25 SUM-20 | S21122500067 | New_Event | UG Cable Fault | Include | Include | Equipment | 393 | 2021-12-25 | 17685 | keep | 0 | Dec | 2021 | 0.012045 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
VEGA BAJA | 2021-12-25 12:08 | 2021-12-25 18:39 | 50 | 006:31 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21122500192 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 391 | 2021-12-25 | 19550 | keep | 0 | Dec | 2021 | 0.013315 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-12-25 12:10 | 2021-12-25 12:29 | 5 | 000:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | A21122500002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 19 | 2021-12-25 | 95 | keep | 0 | Dec | 2021 | 6.4704e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2021-12-25 12:18 | 2021-12-25 13:37 | 40 | 001:19 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER NO CAUSA | C21122500183 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 79 | 2021-12-25 | 3160 | keep | 0 | Dec | 2021 | 0.0021523 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-12-25 13:06 | 2021-12-25 14:07 | 15 | 001:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21122400099 | New_Event | Secondary Wire Down | Include | Include | Equipment | 61 | 2021-12-25 | 915 | keep | 0 | Dec | 2021 | 0.0006232 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-12-25 13:07 | 2021-12-25 16:17 | 30 | 003:10 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21122500070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2021-12-25 | 5700 | keep | 0 | Dec | 2021 | 0.0038822 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-25 13:10 | 2021-12-25 17:11 | 120 | 004:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A21122500012 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 241 | 2021-12-25 | 28920 | keep | 0 | Dec | 2021 | 0.019697 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2021-12-25 13:25 | 2021-12-25 17:51 | 50 | 004:26 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | S21122500073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2021-12-25 | 13300 | keep | 0 | Dec | 2021 | 0.0090586 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2021-12-25 13:26 | 2021-12-25 16:59 | 40 | 003:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO BAJANTE DE CAJA A LINEA NO FUNDIO | C21122500198 | New_Event | Wire Down | Include | Include | Equipment | 213 | 2021-12-25 | 8520 | keep | 0 | Dec | 2021 | 0.0058029 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-25 13:32 | 2021-12-25 18:43 | 100 | 005:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTE DE LINEA IGUANA CRUZO FASE | S21122500075 | New_Event |  |  | Include | Wildlife | 311 | 2021-12-25 | 31100 | keep | 0 | Dec | 2021 | 0.021182 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-12-25 13:50 | 2021-12-25 13:52 | 3005 | 000:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO | C21122500200 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2021-12-25 | 6010 | keep | 0 | Dec | 2021 | 0.0040934 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
SAN JUAN | 2021-12-25 13:52 | 2021-12-25 13:53 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21122500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-25 | 2203 | keep | 0 | Dec | 2021 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
BAYAMON | 2021-12-25 13:55 | 2021-12-25 15:27 | 60 | 001:32 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B21122500201 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 92 | 2021-12-25 | 5520 | keep | 0 | Dec | 2021 | 0.0037596 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-12-25 14:01 | 2021-12-25 19:58 | 100 | 005:57 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M21122500021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 357 | 2021-12-25 | 35700 | keep | 0 | Dec | 2021 | 0.024315 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2021-12-25 14:07 | 2021-12-25 17:40 | 15 | 003:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21122500194 | New_Event | Secondary Wire Down | Include | Include | Equipment | 213 | 2021-12-25 | 3195 | keep | 0 | Dec | 2021 | 0.0021761 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-12-25 14:45 | 2021-12-25 17:35 | 30 | 002:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO | M21122500025 | New_Event | Wire Down | Include | Include | Equipment | 170 | 2021-12-25 | 5100 | keep | 0 | Dec | 2021 | 0.0034736 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-12-25 14:55 | 2021-12-25 14:57 | 600 | 000:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO PARTE DE SU CARGA POR 1336-8 | S21122500000 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2021-12-25 | 1200 | keep | 0 | Dec | 2021 | 0.00081731 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2021-12-25 14:55 | 2021-12-25 14:57 | 5290 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1336-9 Y 30% DEL 1204-4 | S21122500000 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2021-12-25 | 10580 | keep | 0 | Dec | 2021 | 0.007206 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2021-12-25 14:55 | 2021-12-25 14:57 | 207 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1336-8 Y 30% DEL 1204-4 | S21122500000 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2021-12-25 | 414 | keep | 0 | Dec | 2021 | 0.00028197 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2021-12-25 14:57 | 2021-12-25 18:07 | 145 | 003:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | S21122500086 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 190 | 2021-12-25 | 27550 | keep | 0 | Dec | 2021 | 0.018764 | 9.8759e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 145
CANOVANAS | 2021-12-25 15:10 | 2021-12-25 16:27 | 8 | 001:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | R21122500039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 77 | 2021-12-25 | 616 | keep | 0 | Dec | 2021 | 0.00041955 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-12-25 15:42 | 2021-12-25 17:32 | 3005 | 001:50 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO EL BKR PARA REMPLAZAR AISLADOR ROTO EN LA SALIDA DEL ALIMENTADOR | C21122500205 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 110 | 2021-12-25 | 330550 | keep | 0 | Dec | 2021 | 0.22514 | 0.0020467 | Sustained | FALSE | FALSE | Not_TMED_Event | 3005
CANOVANAS | 2021-12-25 15:55 | 2021-12-25 17:44 | 150 | 001:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 Y 1 X 100 EN C/LS 1X 10 EN XMR REMPLAZO CAJA AVERIADA | R21122500044 | New_Event | Cutout Failure | Include | Include | Equipment | 109 | 2021-12-25 | 16350 | keep | 0 | Dec | 2021 | 0.011136 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2021-12-25 16:07 | 2021-12-25 16:08 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21122500087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-25 | 2113 | keep | 0 | Dec | 2021 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
CANOVANAS | 2021-12-25 16:19 | 2021-12-25 20:35 | 100 | 004:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | ELIMINO POSTE PARTIDO POR VEHICULO Y RETEZO LINEAS | R21122500049 | New_Event |  |  | Include | Wildlife | 256 | 2021-12-25 | 25600 | keep | 0 | Dec | 2021 | 0.017436 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2021-12-25 16:20 | 2021-12-25 19:39 | 75 | 003:19 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21122500209 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 199 | 2021-12-25 | 14925 | keep | 0 | Dec | 2021 | 0.010165 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2021-12-25 16:59 | 2021-12-25 21:11 | 100 | 004:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A21122500025 | New_Event |  |  | Include | Wildlife | 252 | 2021-12-25 | 25200 | keep | 0 | Dec | 2021 | 0.017164 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-12-25 18:08 | 2021-12-25 18:09 | 643 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21122500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-25 | 643 | keep | 0 | Dec | 2021 | 0.00043794 | 0.00043794 | Momentary | FALSE | FALSE | Not_TMED_Event | 643
ARECIBO | 2021-12-25 18:21 | 2021-12-26 09:53 | 4 | 015:32 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | A21122500029 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 932 | 2021-12-25 | 3728 | keep | 0 | Dec | 2021 | 0.0025391 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2021-12-25 18:36 | 2021-12-26 09:44 | 20 | 015:08 | P | DESGANCHE | 1 X 30 EN C/L | R21122500063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 908 | 2021-12-25 | 18160 | keep | 0 | Dec | 2021 | 0.012369 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2021-12-25 18:39 | 2021-12-25 21:50 | 480 | 003:11 | P | DESGANCHE | 2 X 140 EN CORTE DE LINEA SE REMOVIO ARBOL SOBRE LINEA | P21122500090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2021-12-25 | 91680 | keep | 0 | Dec | 2021 | 0.062443 | 0.00032693 | Sustained | FALSE | FALSE | Not_TMED_Event | 480
CANOVANAS | 2021-12-25 19:00 | 2021-12-25 19:53 | 1 | 000:53 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | R21122500066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 53 | 2021-12-25 | 53 | keep | 0 | Dec | 2021 | 3.6098e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-12-25 20:30 | 2021-12-25 21:02 | 15 | 000:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21122500026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 32 | 2021-12-25 | 480 | keep | 0 | Dec | 2021 | 0.00032693 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-12-25 20:31 | 2021-12-26 14:31 | 1 | 018:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA | S21122500102 | New_Event | Cutout Failure | Include | Include | Equipment | 1080 | 2021-12-25 | 1080 | keep | 0 | Dec | 2021 | 0.00073558 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-12-25 20:36 | 2021-12-26 11:09 | 60 | 014:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L SE RETIRO IGUANA | B21122500219 | New_Event |  |  | Include | Wildlife | 873 | 2021-12-25 | 52380 | keep | 0 | Dec | 2021 | 0.035676 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2021-12-25 20:40 | 2021-12-25 22:11 | 30 | 001:31 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21122500220 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 91 | 2021-12-25 | 2730 | keep | 0 | Dec | 2021 | 0.0018594 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2021-12-25 20:53 | 2021-12-26 17:04 | 5 | 020:11 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | R21122500069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1211 | 2021-12-25 | 6055 | keep | 0 | Dec | 2021 | 0.004124 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2021-12-25 21:10 | 2021-12-26 00:33 | 2366 | 003:23 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO LINEA PRIMARIA PARTIDA SE CERRO INTERRUPTOR | M21122500043 | New_Event | Wire Down | Include | Include | Equipment | 203 | 2021-12-25 | 480298 | keep | 0 | Dec | 2021 | 0.32713 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
VEGA BAJA | 2021-12-25 21:10 | 2021-12-25 21:56 | 15 | 000:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21122500146 | New_Event | Secondary Wire Down | Include | Include | Equipment | 46 | 2021-12-25 | 690 | keep | 0 | Dec | 2021 | 0.00046996 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-12-25 22:26 | 2021-12-25 22:27 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21122500059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-25 | 1097 | keep | 0 | Dec | 2021 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
BAYAMON | 2021-12-25 23:00 | 2021-12-26 09:38 | 6 | 010:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S21122500109 | New_Event | Secondary Wire Down | Include | Include | Equipment | 638 | 2021-12-25 | 3828 | keep | 0 | Dec | 2021 | 0.0026072 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-12-25 23:59 | 2021-12-26 10:40 | 50 | 010:41 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21122500110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 641 | 2021-12-25 | 32050 | keep | 0 | Dec | 2021 | 0.021829 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-12-26 00:33 | 2021-12-26 03:04 | 250 | 002:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PARTIDA SE CERRO EN REGULADORES | M21122600001 | Partial_restoration | Wire Down | Include | Include | Equipment | 151 | 2021-12-26 | 37750 | keep | 0 | Dec | 2021 | 0.025711 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-26 00:40 | 2021-12-26 00:41 | 1370 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21122600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-26 | 1370 | keep | 0 | Dec | 2021 | 0.0009331 | 0.0009331 | Momentary | FALSE | FALSE | Not_TMED_Event | 1370
BAYAMON | 2021-12-26 02:35 | 2021-12-26 09:47 | 6 | 007:12 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B21122600001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 432 | 2021-12-26 | 2592 | keep | 0 | Dec | 2021 | 0.0017654 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-12-26 02:42 | 2021-12-26 11:59 | 67 | 009:17 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 65 EN SU - 2 Y 1 X 50 EN C/L REMPLAZO STRESS CONE Y INSTALO UN C/L | C21122600003 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 557 | 2021-12-26 | 37319 | keep | 0 | Dec | 2021 | 0.025418 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
ARECIBO | 2021-12-26 05:34 | 2021-12-26 05:35 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21122600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-26 | 308 | keep | 0 | Dec | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
MAYAGÃœEZ | 2021-12-26 06:13 | 2021-12-26 12:20 | 150 | 006:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE REALIZO DESGANCHE | M21122600003 | New_Event | Wire Down | Include | Include | Equipment | 367 | 2021-12-26 | 55050 | keep | 0 | Dec | 2021 | 0.037494 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2021-12-26 06:49 | 2021-12-26 12:06 | 60 | 005:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN RISER SE REEMPLAZARON DOS CAJAS QUEMADAS EN RISER | P21122600003 | New_Event | Cutout Failure | Include | Include | Equipment | 317 | 2021-12-26 | 19020 | keep | 0 | Dec | 2021 | 0.012954 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-12-26 06:59 | 2021-12-26 08:08 | 50 | 001:09 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B21122600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 69 | 2021-12-26 | 3450 | keep | 0 | Dec | 2021 | 0.0023498 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-12-26 07:02 | 2021-12-26 07:03 | 2859 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21122600005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-26 | 2859 | keep | 0 | Dec | 2021 | 0.0019473 | 0.0019473 | Momentary | FALSE | FALSE | Not_TMED_Event | 2859
CANOVANAS | 2021-12-26 07:16 | 2021-12-26 07:17 | 1894 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21122600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-26 | 1894 | keep | 0 | Dec | 2021 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
VEGA BAJA | 2021-12-26 07:51 | 2021-12-26 10:05 | 75 | 002:14 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE AVERIADO | B21122600003 | New_Event | Switch Failure | Include | Include | Equipment | 134 | 2021-12-26 | 10050 | keep | 0 | Dec | 2021 | 0.006845 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2021-12-26 08:07 | 2021-12-27 10:44 | 6 | 026:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S21122600004 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1597 | 2021-12-26 | 9582 | keep | 0 | Dec | 2021 | 0.0065263 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-12-26 08:10 | 2021-12-26 12:19 | 65 | 004:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE DE LINEA Y SE REEMPLAZARON DOS CAJAS | S21122600003 | New_Event | Cutout Failure | Include | Include | Equipment | 249 | 2021-12-26 | 16185 | keep | 0 | Dec | 2021 | 0.011024 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
HUMACAO | 2021-12-26 08:12 | 2021-12-26 10:31 | 20 | 002:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CRUCE X AVE | C21122600006 | New_Event |  |  | Include | Wildlife | 139 | 2021-12-26 | 2780 | keep | 0 | Dec | 2021 | 0.0018934 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-12-26 08:34 | 2021-12-26 08:35 | 1983 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1801-02 Y SE CERRO POR SCADA LLEVA 1711-04 | B21122600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-26 | 1983 | keep | 0 | Dec | 2021 | 0.0013506 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-12-26 08:34 | 2021-12-26 08:35 | 260 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1801-02 Y SE CERRO POR SCADA LLEVA PARTE DEL 1717-01 | B21122600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-26 | 260 | keep | 0 | Dec | 2021 | 0.00017708 | 0.00017708 | Momentary | FALSE | FALSE | Not_TMED_Event | 260
BAYAMON | 2021-12-26 08:34 | 2021-12-26 08:35 | 186 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1801-02 Y SE CERRO POR SCADA LLEVA 1711-04 Y PARTE DEL 1717-01 | B21122600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-26 | 186 | keep | 0 | Dec | 2021 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2021-12-26 08:34 | 2021-12-26 08:35 | 3798 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21122600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-26 | 3798 | keep | 0 | Dec | 2021 | 0.0025868 | 0.0025868 | Momentary | FALSE | FALSE | Not_TMED_Event | 3798
HUMACAO | 2021-12-26 08:42 | 2021-12-26 08:43 | 2450 | 000:01 | T | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | DISPARO | C21122600010 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1 | 2021-12-26 | 2450 | keep | 0 | Dec | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2021-12-26 08:43 | 2021-12-26 11:04 | 6 | 002:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN XMR REPARO SECUNDARIA | C21122600011 | 1st_after_momentary | Secondary Wire Down | Include | Include | Equipment | 141 | 2021-12-26 | 846 | keep | 0 | Dec | 2021 | 0.00057621 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-12-26 08:54 | 2021-12-26 13:45 | 12 | 004:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CULEBRA CRUZO LINEAS | M21122600010 | New_Event |  |  | Include | Wildlife | 291 | 2021-12-26 | 3492 | keep | 0 | Dec | 2021 | 0.0023784 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2021-12-26 09:09 | 2021-12-26 12:15 | 40 | 003:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO FASE | P21122600007 | New_Event |  |  | Include | Wildlife | 186 | 2021-12-26 | 7440 | keep | 0 | Dec | 2021 | 0.0050674 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-12-26 09:21 | 2021-12-26 10:49 | 1 | 001:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 25 EN CORTE DE LINEA AVE CRUZO LINEAS | A21122600002 | New_Event |  |  | Include | Wildlife | 88 | 2021-12-26 | 88 | keep | 0 | Dec | 2021 | 5.9936e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2021-12-26 09:23 | 2021-12-26 10:40 | 65 | 001:17 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | P21122600008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 77 | 2021-12-26 | 5005 | keep | 0 | Dec | 2021 | 0.0034089 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2021-12-26 09:26 | 2021-12-26 12:30 | 20 | 003:04 | P | SECUNDARIA/DESGANCHE | 1 X 40 EN TRANSFORMADOR Y SE REALIZO DESGANCHE SECUNDARIO | S21122600000 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 184 | 2021-12-26 | 3680 | keep | 0 | Dec | 2021 | 0.0025064 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-12-26 09:34 | 2021-12-26 10:29 | 602 | 000:55 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA REEMPLAZO DE MACHETE DE SALIDA DEFECTUOSO | S21122600087 | New_Event | Switch Failure | Include | Include | Equipment | 55 | 2021-12-26 | 33110 | keep | 0 | Dec | 2021 | 0.022551 | 0.00041002 | Sustained | FALSE | FALSE | Not_TMED_Event | 602
GUAYAMA | 2021-12-26 09:35 | 2021-12-26 10:10 | 8 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | P21122600009 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2021-12-26 | 280 | keep | 0 | Dec | 2021 | 0.00019071 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2021-12-26 09:47 | 2021-12-26 11:29 | 8 | 001:42 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIDO DE 15 KVA X 25 KVA | C21122500013 | New_Event | Service Transformer Failure | Include | Include | Equipment | 102 | 2021-12-26 | 816 | keep | 0 | Dec | 2021 | 0.00055577 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-12-26 09:53 | 2021-12-26 14:45 | 1 | 004:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE TRANSFORMADOR | S21122600012 | New_Event | Wire Down | Include | Include | Equipment | 292 | 2021-12-26 | 292 | keep | 0 | Dec | 2021 | 0.00019888 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-12-26 10:05 | 2021-12-26 10:06 | 4702 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO 9004-10 Y SE CERRO POR SCADA LLEVA 9105-07 | B21122600000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2021-12-26 | 4702 | keep | 0 | Dec | 2021 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2021-12-26 10:05 | 2021-12-26 10:06 | 215 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO 9004-10 Y SE CERRO POR SCADA LLEVA 9105-07 | B21122600000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2021-12-26 | 215 | keep | 0 | Dec | 2021 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2021-12-26 10:06 | 2021-12-26 12:31 | 75 | 002:25 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE AVERIADO | B21122600003 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 145 | 2021-12-26 | 10875 | keep | 0 | Dec | 2021 | 0.0074069 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2021-12-26 10:08 | 2021-12-26 14:03 | 6 | 003:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR SECUNDARIA | C21122600016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 235 | 2021-12-26 | 1410 | keep | 0 | Dec | 2021 | 0.00096034 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2021-12-26 10:13 | 2021-12-26 10:56 | 30 | 000:43 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO CAUSA | R21122600005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 43 | 2021-12-26 | 1290 | keep | 0 | Dec | 2021 | 0.00087861 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-12-26 10:18 | 2021-12-26 11:50 | 1 | 001:32 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | C21122600017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 92 | 2021-12-26 | 92 | keep | 0 | Dec | 2021 | 6.2661e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-12-26 10:18 | 2021-12-26 12:59 | 65 | 002:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | P21122600010 | New_Event |  |  | Include | Wildlife | 161 | 2021-12-26 | 10465 | keep | 0 | Dec | 2021 | 0.0071277 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
ARECIBO | 2021-12-26 10:50 | 2021-12-26 10:58 | 2694 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE INTERRUPTORES 6930 Y 13630 PARA HACER OPERACIONES EN EL 18350 | A21122600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-12-26 | 21552 | keep | 0 | Dec | 2021 | 0.014679 | 0.0018349 | Sustained | FALSE | FALSE | Not_TMED_Event | 2694
ARECIBO | 2021-12-26 10:50 | 2021-12-26 10:58 | 2228 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE INTERRUPTORES 6930 Y 13630 PARA HACER OPERACIONES EN EL 18350 | A21122600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-12-26 | 17824 | keep | 0 | Dec | 2021 | 0.01214 | 0.0015175 | Sustained | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2021-12-26 10:50 | 2021-12-26 10:58 | 438 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE INTERRUPTORES 6930 Y 13630 PARA HACER OPERACIONES EN EL 18350 EL 8007-04 LLEVA LA CARGA DEL 8007-03 | A21122600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-12-26 | 3504 | keep | 0 | Dec | 2021 | 0.0023866 | 0.00029832 | Sustained | FALSE | FALSE | Not_TMED_Event | 438
ARECIBO | 2021-12-26 10:50 | 2021-12-26 10:58 | 2201 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE INTERRUPTORES 6930 Y 13630 PARA HACER OPERACIONES EN EL 18350 | A21122600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-12-26 | 17608 | keep | 0 | Dec | 2021 | 0.011993 | 0.0014991 | Sustained | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2021-12-26 10:50 | 2021-12-26 10:58 | 1986 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE INTERRUPTORES 6930 Y 13630 PARA HACER OPERACIONES EN EL 18350 | A21122600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-12-26 | 15888 | keep | 0 | Dec | 2021 | 0.010821 | 0.0013527 | Sustained | FALSE | FALSE | Not_TMED_Event | 1986
ARECIBO | 2021-12-26 10:50 | 2021-12-26 10:58 | 199 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE INTERRUPTORES 6930 Y 13630 PARA HACER OPERACIONES EN EL 18350 | A21122600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-12-26 | 1592 | keep | 0 | Dec | 2021 | 0.0010843 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2021-12-26 10:50 | 2021-12-26 10:58 | 24 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE INTERRUPTORES 6930 Y 13630 PARA HACER OPERACIONES EN EL 18350 EL 8013-04 LLEVA LA CARGA DEL 8013-03 | A21122600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-12-26 | 192 | keep | 0 | Dec | 2021 | 0.00013077 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
MAYAGÃœEZ | 2021-12-26 11:12 | 2021-12-26 14:26 | 150 | 003:14 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M21122600017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2021-12-26 | 29100 | keep | 0 | Dec | 2021 | 0.01982 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2021-12-26 11:33 | 2021-12-26 11:34 | 1000 | 000:01 | P | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% 1348-07 Y 80% 1348-06 | S21122600000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2021-12-26 | 1000 | keep | 0 | Dec | 2021 | 0.0006811 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2021-12-26 11:33 | 2021-12-26 11:34 | 278 | 000:01 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% 1348-07 Y 80% 1348-06 | S21122600000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2021-12-26 | 278 | keep | 0 | Dec | 2021 | 0.00018934 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2021-12-26 11:33 | 2021-12-26 11:34 | 9 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% 1348-07 Y 80% 1348-06 | S21122600000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-12-26 | 9 | keep | 0 | Dec | 2021 | 6.1299e-06 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2021-12-26 11:33 | 2021-12-26 13:36 | 6 | 002:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 30 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M21122600020 | New_Event | Wire Down | Include | Include | Equipment | 123 | 2021-12-26 | 738 | keep | 0 | Dec | 2021 | 0.00050265 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-12-26 11:45 | 2021-12-26 14:00 | 10 | 002:15 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | C21122600021 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 135 | 2021-12-26 | 1350 | keep | 0 | Dec | 2021 | 0.00091948 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-26 11:48 | 2021-12-26 14:07 | 30 | 002:19 | P | DESGANCHE | 2 X 40 EN C/L SE REALIZO DESGANCHE | B21122600014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2021-12-26 | 4170 | keep | 0 | Dec | 2021 | 0.0028402 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-12-26 11:49 | 2021-12-26 12:24 | 12 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO PM-12 PARA REPARAR MOLE SECUNDARIA | S21122600002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2021-12-26 | 420 | keep | 0 | Dec | 2021 | 0.00028606 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-12-26 12:00 | 2021-12-26 15:20 | 10 | 003:20 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P21122600014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2021-12-26 | 2000 | keep | 0 | Dec | 2021 | 0.0013622 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-26 12:03 | 2021-12-26 12:04 | 1000 | 000:01 | P | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% 1348-07 Y 80% 1348-06 | S21122600000 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 1 | 2021-12-26 | 1000 | keep | 0 | Dec | 2021 | 0.0006811 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2021-12-26 12:03 | 2021-12-26 12:04 | 278 | 000:01 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% 1348-07 Y 80% 1348-06 | S21122600000 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 1 | 2021-12-26 | 278 | keep | 0 | Dec | 2021 | 0.00018934 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2021-12-26 12:03 | 2021-12-26 12:04 | 9 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% 1348-07 Y 80% 1348-06 | S21122600000 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-12-26 | 9 | keep | 0 | Dec | 2021 | 6.1299e-06 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2021-12-26 12:04 | 2021-12-26 12:09 | 139 | 000:05 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO ALIMENTADOR CARGA TRANSFERIDA AL 1424-08 | S21122600021 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 5 | 2021-12-26 | 695 | keep | 0 | Dec | 2021 | 0.00047336 | 9.4672e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 139
SAN JUAN | 2021-12-26 12:09 | 2021-12-26 14:25 | 1000 | 002:16 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO ALIMENTADOR ESTA CARGA ESTA TRANSFERIDA AL 1424-08 | S21122600021 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 136 | 2021-12-26 | 136000 | keep | 0 | Dec | 2021 | 0.092629 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2021-12-26 12:09 | 2021-12-26 13:19 | 278 | 001:10 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% 1348-07 Y 80% 1348-06 SE SECCIONALIZO ABRIENDO N/O CONTRA EL 1424-08 | S21122600000 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 70 | 2021-12-26 | 19460 | keep | 0 | Dec | 2021 | 0.013254 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-26 12:09 | 2021-12-26 12:35 | 9 | 000:26 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% 1348-07 Y 80% 1348-06 | S21122600000 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 26 | 2021-12-26 | 234 | keep | 0 | Dec | 2021 | 0.00015938 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2021-12-26 12:15 | 2021-12-26 13:56 | 12 | 001:41 | P | DESGANCHE | 1 X 25 EN C/L | C21122600023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2021-12-26 | 1212 | keep | 0 | Dec | 2021 | 0.00082549 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-12-26 12:21 | 2021-12-26 12:22 | 36 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04 QUE A SU VEZ LLEVA LA CARGA DEL 1620-01 | S21122600025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-26 | 36 | keep | 0 | Dec | 2021 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-12-26 12:21 | 2021-12-26 12:22 | 172 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04 QUE A SU VEZ LLEVA LA CARGA DEL 1620-01 | S21122600025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-26 | 172 | keep | 0 | Dec | 2021 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
ARECIBO | 2021-12-26 12:22 | 2021-12-26 13:31 | 4 | 001:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A21122500031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 69 | 2021-12-26 | 276 | keep | 0 | Dec | 2021 | 0.00018798 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2021-12-26 12:31 | 2021-12-26 12:34 | 4702 | 000:03 | T | DESCONECTIVO DEFECTUOSO | DISPARO 9004-10 Y SE CERRO POR SCADA LLEVA 9105-07 | B21122600000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 3 | 2021-12-26 | 14106 | keep | 0 | Dec | 2021 | 0.0096075 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2021-12-26 12:31 | 2021-12-26 12:34 | 215 | 000:03 | T | DESCONECTIVO DEFECTUOSO | DISPARO 9004-10 Y SE CERRO POR SCADA LLEVA 9105-07 | B21122600000 | Additional_clients | Switch Failure | Include | Include | Equipment | 3 | 2021-12-26 | 645 | keep | 0 | Dec | 2021 | 0.00043931 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-26 12:33 | 2021-12-26 12:34 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1907-03 LLEVA 1909-09 | S21122600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-26 | 222 | keep | 0 | Dec | 2021 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2021-12-26 12:33 | 2021-12-26 12:34 | 4456 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1907-03 LLEVA 1909-09 | S21122600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-26 | 4456 | keep | 0 | Dec | 2021 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
VEGA BAJA | 2021-12-26 12:34 | 2021-12-26 12:59 | 75 | 000:25 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE AVERIADO | B21122600003 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 25 | 2021-12-26 | 1875 | keep | 0 | Dec | 2021 | 0.0012771 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2021-12-26 12:59 | 2021-12-26 13:01 | 4702 | 000:02 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO BKR 9004-10 POR MACHETE DEL 9105-07 EN FUEGO SE SECCIONALIZO Y 9004-10 SE CERRO POR SCADA LLEVA 9105-07 | B21122600000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 2 | 2021-12-26 | 9404 | keep | 0 | Dec | 2021 | 0.006405 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2021-12-26 12:59 | 2021-12-26 13:01 | 215 | 000:02 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO 9004-10 Y SE CERRO POR SCADA LLEVA 9105-07 PARA SECCIONALIZAR MACHETE EN FUEGO DEL 9105-07 | B21122600000 | Additional_clients | Switch Failure | Include | Include | Equipment | 2 | 2021-12-26 | 430 | keep | 0 | Dec | 2021 | 0.00029287 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-12-26 13:01 | 2021-12-26 14:57 | 75 | 001:56 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE AVERIADO Y SE CERRO MACHETE | B21122600003 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 116 | 2021-12-26 | 8700 | keep | 0 | Dec | 2021 | 0.0059255 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2021-12-26 13:19 | 2021-12-26 13:21 | 278 | 000:02 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% 1348-07 Y 80% 1348-06 | S21122600000 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 2 | 2021-12-26 | 556 | keep | 0 | Dec | 2021 | 0.00037869 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-26 13:19 | 2021-12-26 13:21 | 9 | 000:02 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR 1424-08. SE REALIZARON OPERACIONES DE CAMPO Y SE CERRO AMARRE EN SU-3909 PROBANDO MALO LA LINEA | S21122600021 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 2 | 2021-12-26 | 18 | keep | 0 | Dec | 2021 | 1.226e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-26 13:21 | 2021-12-26 13:52 | 139 | 000:31 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO ALIMENTADOR CARGA TRANSFERIDA AL 1424-08 50% EN SERVICIO | S21122600000 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 31 | 2021-12-26 | 4309 | keep | 0 | Dec | 2021 | 0.0029348 | 9.4672e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 139
FAJARDO | 2021-12-26 13:46 | 2021-12-26 18:08 | 50 | 004:22 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO CAUSA | R21122600019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 262 | 2021-12-26 | 13100 | keep | 0 | Dec | 2021 | 0.0089224 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-12-26 13:51 | 2021-12-26 13:52 | 922 | 000:01 | T | NO SE REPORTO CAUSA | CARGA TRANSFERIDA AL 1401-08 | S21122600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-26 | 922 | keep | 0 | Dec | 2021 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-12-26 13:51 | 2021-12-26 13:52 | 135 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA LA CARGA DEL 1346-05 | S21122600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-26 | 135 | keep | 0 | Dec | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2021-12-26 13:52 | 2021-12-26 13:55 | 278 | 000:03 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% 1348-07 Y 80% 1348-06 | S21122600000 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 3 | 2021-12-26 | 834 | keep | 0 | Dec | 2021 | 0.00056803 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-26 13:52 | 2021-12-26 13:55 | 9 | 000:03 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR 1424-08. SE REALIZARON OPERACIONES DE CAMPO Y SE CERRO AMARRE EN SU-3909 PROBANDO MALO LA LINEA | S21122600021 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 3 | 2021-12-26 | 27 | keep | 0 | Dec | 2021 | 1.839e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2021-12-26 13:53 | 2021-12-26 16:22 | 12 | 002:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO CONEXIONES SECUNDARIAS | A21122600014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 149 | 2021-12-26 | 1788 | keep | 0 | Dec | 2021 | 0.0012178 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-12-26 13:55 | 2021-12-26 14:35 | 139 | 000:40 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO ALIMENTADOR CARGA TRANSFERIDA AL 1424-08 50% EN SERVICIO | S21122600000 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 40 | 2021-12-26 | 5560 | keep | 0 | Dec | 2021 | 0.0037869 | 9.4672e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 139
HUMACAO | 2021-12-26 14:13 | 2021-12-26 15:09 | 1 | 000:56 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | C21122600027 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 56 | 2021-12-26 | 56 | keep | 0 | Dec | 2021 | 3.8141e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-26 14:35 | 2021-12-26 15:30 | 69 | 000:55 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO ALIMENTADOR CARGA TRANSFERIDA AL 1424-08 75% EN SERVICIO | S21122600021 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 55 | 2021-12-26 | 3795 | keep | 0 | Dec | 2021 | 0.0025848 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-12-26 14:56 | 2021-12-26 15:28 | 1 | 000:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y VIENTO | M21122600039 | New_Event | Bad Weather | Include | Include | Weather | 32 | 2021-12-26 | 32 | keep | 0 | Dec | 2021 | 2.1795e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-26 15:28 | 2021-12-26 15:29 | 990 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M21122600000 | Additional_clients | Bad Weather | Include | Include | Weather | 1 | 2021-12-26 | 990 | keep | 0 | Dec | 2021 | 0.00067428 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-12-26 15:29 | 2021-12-26 17:30 | 1 | 002:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y VIENTO | M21122600039 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 121 | 2021-12-26 | 121 | keep | 0 | Dec | 2021 | 8.2413e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-26 15:30 | 2021-12-26 17:12 | 50 | 001:42 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO ALIMENTADOR CARGA TRANSFERIDA AL 1424-08 | S21122600021 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 102 | 2021-12-26 | 5100 | keep | 0 | Dec | 2021 | 0.0034736 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-12-26 15:32 | 2021-12-26 16:34 | 29 | 001:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR LINEA ZAFADA DE AISLADOR Y SE AJUSTO VOLTAJE SECUNDARIO A TRANSFORMADOR | M21122600040 | New_Event | Wire Down | Include | Include | Equipment | 62 | 2021-12-26 | 1798 | keep | 0 | Dec | 2021 | 0.0012246 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
ARECIBO | 2021-12-26 15:47 | 2021-12-26 21:47 | 60 | 006:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A21122600020 | New_Event | Bad Weather | Include | Include | Weather | 360 | 2021-12-26 | 21600 | keep | 0 | Dec | 2021 | 0.014712 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-12-26 15:58 | 2021-12-26 17:32 | 40 | 001:34 | P | DESGANCHE | 1 X 50 EN C/L | R21122600024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2021-12-26 | 3760 | keep | 0 | Dec | 2021 | 0.0025609 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-12-26 15:58 | 2021-12-26 18:03 | 3 | 002:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN XMR CRUCE X AVE | R21122600023 | New_Event |  |  | Include | Wildlife | 125 | 2021-12-26 | 375 | keep | 0 | Dec | 2021 | 0.00025541 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2021-12-26 16:01 | 2021-12-26 17:25 | 6 | 001:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE XMR Y SE REPARO BARRA EN PEDESTAL | B21122600027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 84 | 2021-12-26 | 504 | keep | 0 | Dec | 2021 | 0.00034327 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-12-26 16:17 | 2021-12-26 17:40 | 100 | 001:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A21122600022 | New_Event | Bad Weather | Include | Include | Weather | 83 | 2021-12-26 | 8300 | keep | 0 | Dec | 2021 | 0.0056531 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-12-26 16:28 | 2021-12-26 17:08 | 7 | 000:40 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | C21122600027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 40 | 2021-12-26 | 280 | keep | 0 | Dec | 2021 | 0.00019071 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-12-26 16:34 | 2021-12-27 12:17 | 60 | 019:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 200 SE LEVANTO PRIMARIA | B21122600029 | New_Event | Wire Down | Include | Include | Equipment | 1183 | 2021-12-26 | 70980 | keep | 0 | Dec | 2021 | 0.048344 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-12-26 16:42 | 2021-12-26 17:28 | 100 | 000:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y VIENTO | M21122600044 | New_Event | Bad Weather | Include | Include | Weather | 46 | 2021-12-26 | 4600 | keep | 0 | Dec | 2021 | 0.003133 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-12-26 16:48 | 2021-12-26 18:14 | 12 | 001:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN C/L CRUCE X AVE | C21122600030 | New_Event |  |  | Include | Wildlife | 86 | 2021-12-26 | 1032 | keep | 0 | Dec | 2021 | 0.00070289 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-12-26 17:07 | 2021-12-26 19:11 | 36 | 002:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REMPLAZO CAJA PRIMARIA | B21122600030 | New_Event | Cutout Failure | Include | Include | Equipment | 124 | 2021-12-26 | 4464 | keep | 0 | Dec | 2021 | 0.0030404 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-12-26 17:12 | 2021-12-26 17:15 | 1000 | 000:03 | P | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% 1348-07 Y 80% 1348-06 | S21122600000 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 3 | 2021-12-26 | 3000 | keep | 0 | Dec | 2021 | 0.0020433 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-26 17:12 | 2021-12-26 17:15 | 278 | 000:03 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% 1348-07 Y 80% 1348-06 | S21122600000 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 3 | 2021-12-26 | 834 | keep | 0 | Dec | 2021 | 0.00056803 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-26 17:12 | 2021-12-26 17:15 | 9 | 000:03 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% 1348-07 Y 80% 1348-06 | S21122600021 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 3 | 2021-12-26 | 27 | keep | 0 | Dec | 2021 | 1.839e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2021-12-26 17:15 | 2021-12-28 13:07 | 1000 | 043:52 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ELIMINO TOMA EN CAJAS SECAS HACIA SUBESTACION ABANDONADA Y SE CERRO EN MH-6 HACIA CAJAS SECAS CARGA POR EL 1348-07 80% POR EL 1424-08 | S21122600021 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 2632 | 2021-12-26 | 2632000 | keep | 0 | Dec | 2021 | 1.7926 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2021-12-26 17:15 | 2021-12-28 13:07 | 278 | 043:52 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ELIMINO TOMA EN CAJAS SECAS HACIA SUBESTACION ABANDONADA Y SE CERRO EN MH-6 HACIA CAJAS SECAS CARGA POR EL 1348-07 | S21122600021 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 2632 | 2021-12-26 | 731696 | keep | 0 | Dec | 2021 | 0.49835 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2021-12-26 17:15 | 2021-12-28 13:07 | 9 | 043:52 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ELIMINO TOMA EN CAJAS SECAS HACIA SUBESTACION ABANDONADA Y SE CERRO EN MH-6 HACIA CAJAS SECAS | S21122600021 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 2632 | 2021-12-26 | 23688 | keep | 0 | Dec | 2021 | 0.016134 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2021-12-26 17:25 | 2021-12-26 17:26 | 4634 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21122600034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-26 | 4634 | keep | 0 | Dec | 2021 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
MAYAGÃœEZ | 2021-12-26 17:38 | 2021-12-27 17:34 | 125 | 023:56 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO Y SE CERRO CORTE DE LINEA | M21122600047 | New_Event | UG Cable Fault | Include | Include | Equipment | 1436 | 2021-12-26 | 179500 | keep | 0 | Dec | 2021 | 0.12226 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
VEGA BAJA | 2021-12-26 17:44 | 2021-12-26 20:41 | 36 | 002:57 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 40 EN C/L | B21122600031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 177 | 2021-12-26 | 6372 | keep | 0 | Dec | 2021 | 0.0043399 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
ARECIBO | 2021-12-26 17:55 | 2021-12-26 20:51 | 30 | 002:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A21122600024 | New_Event | Bad Weather | Include | Include | Weather | 176 | 2021-12-26 | 5280 | keep | 0 | Dec | 2021 | 0.0035962 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-12-26 17:56 | 2021-12-26 21:43 | 30 | 003:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y VIENTO | M21122600050 | New_Event | Bad Weather | Include | Include | Weather | 227 | 2021-12-26 | 6810 | keep | 0 | Dec | 2021 | 0.0046383 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2021-12-26 18:07 | 2021-12-27 09:45 | 25 | 015:38 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21122600026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 938 | 2021-12-26 | 23450 | keep | 0 | Dec | 2021 | 0.015972 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-12-26 18:11 | 2021-12-26 20:25 | 5 | 002:14 | T | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA LLEVA LA CARGA DEL 1116-04 Y 1117-08 | S21122600053 | New_Event | UG Cable Fault | Include | Include | Equipment | 134 | 2021-12-26 | 670 | keep | 0 | Dec | 2021 | 0.00045633 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-12-26 18:13 | 2021-12-27 09:45 | 50 | 015:32 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE RETIRO PARARRAYOS DEFECTUOSO | M21122600052 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 932 | 2021-12-26 | 46600 | keep | 0 | Dec | 2021 | 0.031739 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-12-26 18:41 | 2021-12-26 22:41 | 25 | 004:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M21122600054 | New_Event | Wire Down | Include | Include | Equipment | 240 | 2021-12-26 | 6000 | keep | 0 | Dec | 2021 | 0.0040866 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2021-12-26 18:42 | 2021-12-26 21:18 | 60 | 002:36 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE | B21122600035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2021-12-26 | 9360 | keep | 0 | Dec | 2021 | 0.0063751 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-12-26 21:10 | 2021-12-26 21:11 | 5 | 000:01 | T | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA LLEVA LA CARGA DEL 1116-04 Y 1117-08 | S21122600053 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1 | 2021-12-26 | 5 | keep | 0 | Dec | 2021 | 3.4055e-06 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-26 21:11 | 2021-12-26 21:31 | 466 | 000:20 | T | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO ALIMENTADOR Y SE CERRO N/O CON 1116-05 | S21122600053 | New_Event | UG Cable Fault | Include | Include | Equipment | 20 | 2021-12-26 | 9320 | keep | 0 | Dec | 2021 | 0.0063478 | 0.00031739 | Sustained | FALSE | FALSE | Not_TMED_Event | 466
VEGA BAJA | 2021-12-26 21:15 | 2021-12-27 10:08 | 10 | 012:53 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | B21122600042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 773 | 2021-12-26 | 7730 | keep | 0 | Dec | 2021 | 0.0052649 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-26 21:31 | 2021-12-27 09:34 | 233 | 012:03 | P | CABLE SOTERRADO AVERIADO | SE NORAMALIZO INTERRUPTOR NORMALIZO INTERRUPTOR 1116-04 PARA DAR SERVICIO A LAS CARGA TRANSFERIDAS AL 1116-05. SE REPORTO AVERIA TRAMO AVERIADO DEL MH-19 AL MH-20 | S21122600053 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 723 | 2021-12-26 | 168459 | keep | 0 | Dec | 2021 | 0.11474 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-12-26 22:01 | 2021-12-27 10:14 | 30 | 012:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21122600041 | New_Event | Bad Weather | Include | Include | Weather | 733 | 2021-12-26 | 21990 | keep | 0 | Dec | 2021 | 0.014977 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-26 22:21 | 2021-12-27 08:57 | 6 | 010:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S21122600078 | New_Event | Secondary Wire Down | Include | Include | Equipment | 636 | 2021-12-26 | 3816 | keep | 0 | Dec | 2021 | 0.0025991 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-12-27 00:08 | 2021-12-27 00:09 | 1250 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21122700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-27 | 1250 | keep | 0 | Dec | 2021 | 0.00085137 | 0.00085137 | Momentary | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2021-12-27 00:09 | 2021-12-27 09:07 | 100 | 008:58 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO CAUSA | C21122700002 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 538 | 2021-12-27 | 53800 | keep | 0 | Dec | 2021 | 0.036643 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-12-27 01:15 | 2021-12-27 22:26 | 60 | 021:11 | P | ESTRUCTURA AVERIADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO | M21122700001 | New_Event | Defective Pole | Include | Include | Equipment | 1271 | 2021-12-27 | 76260 | keep | 0 | Dec | 2021 | 0.05194 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-12-27 04:14 | 2021-12-27 04:15 | 2888 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA | A21122700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-27 | 2888 | keep | 0 | Dec | 2021 | 0.001967 | 0.001967 | Momentary | FALSE | FALSE | Not_TMED_Event | 2888
PONCE | 2021-12-27 04:53 | 2021-12-27 04:54 | 449 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21122700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-27 | 449 | keep | 0 | Dec | 2021 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
HUMACAO | 2021-12-27 06:32 | 2021-12-27 06:33 | 2354 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | C21122700000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-12-27 | 2354 | keep | 0 | Dec | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
HUMACAO | 2021-12-27 06:33 | 2021-12-27 17:53 | 14 | 011:20 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 20 EN SMU DE 20 SE REEMPLAZO PANEL DE MICARTA | C21122700052 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 680 | 2021-12-27 | 9520 | keep | 0 | Dec | 2021 | 0.006484 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
FAJARDO | 2021-12-27 06:38 | 2021-12-27 10:43 | 55 | 004:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA DEFECTUOSA | R21122700002 | New_Event | Cutout Failure | Include | Include | Equipment | 245 | 2021-12-27 | 13475 | keep | 0 | Dec | 2021 | 0.0091778 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CAGUAS | 2021-12-27 07:10 | 2021-12-27 07:11 | 1307 | 000:01 | T | DESGANCHE | RECIERRE | C21122700009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-27 | 1307 | keep | 0 | Dec | 2021 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
CAGUAS | 2021-12-27 07:11 | 2021-12-27 12:20 | 100 | 005:09 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21122700025 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 309 | 2021-12-27 | 30900 | keep | 0 | Dec | 2021 | 0.021046 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-12-27 07:43 | 2021-12-27 09:31 | 3 | 001:48 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO CAUSA | C21122700011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 108 | 2021-12-27 | 324 | keep | 0 | Dec | 2021 | 0.00022067 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-12-27 07:45 | 2021-12-27 10:51 | 6 | 003:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S21122700004 | New_Event | Secondary Wire Down | Include | Include | Equipment | 186 | 2021-12-27 | 1116 | keep | 0 | Dec | 2021 | 0.0007601 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-12-27 08:19 | 2021-12-27 15:23 | 10 | 007:04 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE TRANSFORMADOR 37.5 KVA A 4160 VOLTS AVERIADO POR OTRO IGUAL CAPACIDAD Y VOLTAJE | P21122700002 | New_Event | Service Transformer Failure | Include | Include | Equipment | 424 | 2021-12-27 | 4240 | keep | 0 | Dec | 2021 | 0.0028878 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-27 08:23 | 2021-12-27 12:49 | 20 | 004:26 | P | NO SE REPORTO CAUSA | 4 X 100 EN RISER Y CORTE DE LINEA | C21122700015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 266 | 2021-12-27 | 5320 | keep | 0 | Dec | 2021 | 0.0036234 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-12-27 08:32 | 2021-12-27 13:30 | 15 | 004:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA CRUCE POR AVE | R21122700006 | New_Event |  |  | Include | Wildlife | 298 | 2021-12-27 | 4470 | keep | 0 | Dec | 2021 | 0.0030445 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-12-27 08:47 | 2021-12-27 09:22 | 20 | 000:35 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21122700009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 35 | 2021-12-27 | 700 | keep | 0 | Dec | 2021 | 0.00047677 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-12-27 08:47 | 2021-12-27 09:33 | 50 | 000:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | A21122700009 | New_Event |  |  | Include | Wildlife | 46 | 2021-12-27 | 2300 | keep | 0 | Dec | 2021 | 0.0015665 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-27 08:48 | 2021-12-27 11:27 | 7 | 002:39 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 25KVA POR UNO DE IGUAL CAPACIDAD | B21122700006 | New_Event | Service Transformer Failure | Include | Include | Equipment | 159 | 2021-12-27 | 1113 | keep | 0 | Dec | 2021 | 0.00075806 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-12-27 08:54 | 2021-12-27 12:32 | 10 | 003:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR CONECTORES SECUNDARIO | A21122700010 | New_Event | Secondary Wire Down | Include | Include | Equipment | 218 | 2021-12-27 | 2180 | keep | 0 | Dec | 2021 | 0.0014848 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2021-12-27 08:55 | 2021-12-27 10:22 | 100 | 001:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO FASE | P21122700005 | New_Event |  |  | Include | Wildlife | 87 | 2021-12-27 | 8700 | keep | 0 | Dec | 2021 | 0.0059255 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2021-12-27 09:31 | 2021-12-27 11:09 | 60 | 001:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21122700012 | New_Event | Bad Weather | Include | Include | Weather | 98 | 2021-12-27 | 5880 | keep | 0 | Dec | 2021 | 0.0040048 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-12-27 09:34 | 2021-12-27 09:35 | 5 | 000:01 | T | CABLE SOTERRADO AVERIADO | SE REALIZARON OPERACIONES DE CAMPO Y PROBO AVERIADO TRAMO DEL MH-18 AL SU-21. SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA LLEVA LA CARGA DEL 1116-04 Y 1117-08 | S21122600053 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2021-12-27 | 5 | keep | 0 | Dec | 2021 | 3.4055e-06 | 3.4055e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-12-27 09:34 | 2021-12-27 09:35 | 466 | 000:01 | T | CABLE SOTERRADO AVERIADO | SE REALIZARON OPERACIONES DE CAMPO Y PROBO AVERIADO DEL MH-18 AL SU-21. SE SECCIONALIZO ALIMENTADOR Y SE CERRO N/O CON 1116-05 | S21122600053 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1 | 2021-12-27 | 466 | keep | 0 | Dec | 2021 | 0.00031739 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-27 09:35 | 2021-12-27 17:03 | 169 | 007:28 | T | CABLE SOTERRADO AVERIADO | SE NORAMALIZO INTERRUPTOR NORMALIZO INTERRUPTOR 1116-04 PARA DAR SERVICIO A LAS CARGA TRANSFERIDAS AL 1116-05. SE REPORTO AVERIA TRAMO AVERIADO DEL MH-19 AL MH-20 | S21122600053 | New_Event | UG Cable Fault | Include | Include | Equipment | 448 | 2021-12-27 | 75712 | keep | 0 | Dec | 2021 | 0.051567 | 0.00011511 | Sustained | FALSE | FALSE | Not_TMED_Event | 169
BAYAMON | 2021-12-27 09:35 | 2021-12-27 17:03 | 233 | 007:28 | P | CABLE SOTERRADO AVERIADO | SE NORAMALIZO INTERRUPTOR NORMALIZO INTERRUPTOR 1116-04 PARA DAR SERVICIO A LAS CARGA TRANSFERIDAS AL 1116-05. SE REPORTO AVERIA TRAMO AVERIADO DEL MH-19 AL MH-20 | S21122600053 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 448 | 2021-12-27 | 104384 | keep | 0 | Dec | 2021 | 0.071095 | 0.0001587 | Sustained | FALSE | FALSE | Not_TMED_Event | 233
CANOVANAS | 2021-12-27 09:38 | 2021-12-27 12:02 | 55 | 002:24 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA Y SE REEMPLAZO AISLADOR | R21122700013 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 144 | 2021-12-27 | 7920 | keep | 0 | Dec | 2021 | 0.0053943 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
BAYAMON | 2021-12-27 09:43 | 2021-12-27 12:39 | 85 | 002:56 | P | PARARRAYOS DEFECTUOSO | 1 X 10 EN TRANSFORMADOR, 1 X 100 EN CORTE DE LINEA PRINCIPAL Y 1 X 80 EN RISER. SE REPORTA PARARRAYO AVERIADO | S21122700009 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 176 | 2021-12-27 | 14960 | keep | 0 | Dec | 2021 | 0.010189 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
VEGA BAJA | 2021-12-27 09:52 | 2021-12-27 16:55 | 1 | 007:03 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21122700013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 423 | 2021-12-27 | 423 | keep | 0 | Dec | 2021 | 0.0002881 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-27 10:04 | 2021-12-27 10:05 | 3511 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21122700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-27 | 3511 | keep | 0 | Dec | 2021 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
CANOVANAS | 2021-12-27 10:18 | 2021-12-27 11:13 | 239 | 000:55 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO CAUSA | R21122700018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 55 | 2021-12-27 | 13145 | keep | 0 | Dec | 2021 | 0.008953 | 0.00016278 | Sustained | FALSE | FALSE | Not_TMED_Event | 239
CAGUAS | 2021-12-27 10:26 | 2021-12-27 10:27 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21122700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-27 | 1702 | keep | 0 | Dec | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
MAYAGÃœEZ | 2021-12-27 10:28 | 2021-12-27 19:19 | 200 | 008:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 140 EN CORTE DE LINEA SE REEMPLAZO CAJAS QUEMADAS | M21122700017 | New_Event | Cutout Failure | Include | Include | Equipment | 531 | 2021-12-27 | 106200 | keep | 0 | Dec | 2021 | 0.072332 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2021-12-27 10:51 | 2021-12-27 12:00 | 1 | 001:09 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO CAUSA | C21122700025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 69 | 2021-12-27 | 69 | keep | 0 | Dec | 2021 | 4.6996e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-27 10:52 | 2021-12-27 12:32 | 5 | 001:40 | P | ESTRUCTURA AVERIADA | SE ABRIO XMR PARA SECCIONALIZAR POSTE PARTIDO SE DEJO UN CLIENTE SIN SERVICIO EN LO QUE SE INSTALA EL POSTE NUEVO | B21122600026 | New_Event | Defective Pole | Include | Include | Equipment | 100 | 2021-12-27 | 500 | keep | 0 | Dec | 2021 | 0.00034055 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2021-12-27 10:53 | 2021-12-27 10:54 | 4702 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 9004-10 Y SE CERRO POR SCADA LLEVA 9105-07 | B21122700020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-27 | 4702 | keep | 0 | Dec | 2021 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2021-12-27 10:53 | 2021-12-27 10:54 | 215 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 9004-10 Y SE CERRO POR SCADA LLEVA 9105-07 | B21122700020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-27 | 215 | keep | 0 | Dec | 2021 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
BAYAMON | 2021-12-27 10:55 | 2021-12-27 10:56 | 651 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21122700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-27 | 651 | keep | 0 | Dec | 2021 | 0.00044339 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
HUMACAO | 2021-12-27 11:01 | 2021-12-27 15:11 | 6 | 004:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE CON AVE | C21122700028 | New_Event |  |  | Include | Wildlife | 250 | 2021-12-27 | 1500 | keep | 0 | Dec | 2021 | 0.0010216 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-12-27 11:08 | 2021-12-27 13:17 | 80 | 002:09 | P | NO SE REPORTO CAUSA | 1 X 140 EN C/L | B21122700022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 129 | 2021-12-27 | 10320 | keep | 0 | Dec | 2021 | 0.0070289 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2021-12-27 11:20 | 2021-12-27 16:39 | 4 | 005:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE HACIA TRANSFORMADOR | C21122700034 | New_Event | Wire Down | Include | Include | Equipment | 319 | 2021-12-27 | 1276 | keep | 0 | Dec | 2021 | 0.00086908 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-12-27 11:25 | 2021-12-27 13:57 | 15 | 002:32 | P | OTRAS CAUSAS | 1 X 25 EN TRANSFORMADOR Y SE REPORTA PROA | S21122700019 | New_Event | Other Causes | Include | Include | Other | 152 | 2021-12-27 | 2280 | keep | 0 | Dec | 2021 | 0.0015529 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2021-12-27 11:40 | 2021-12-27 14:20 | 5 | 002:40 | P | SECUNDARIA/ESTRUCTURA AVERIADA | POSTE SECUNDARIO PARTIDO SE ABRIO TRANSFORMADOR Y SE RELOCALIZO LA LINEA SECUNDARIA EN POSTES EXISTENTES | A21122600029 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 160 | 2021-12-27 | 800 | keep | 0 | Dec | 2021 | 0.00054488 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-12-27 11:41 | 2021-12-27 17:08 | 6 | 005:27 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR LA MISMA CAPACIDAD | A21122700019 | New_Event | Service Transformer Failure | Include | Include | Equipment | 327 | 2021-12-27 | 1962 | keep | 0 | Dec | 2021 | 0.0013363 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-12-27 11:41 | 2021-12-27 16:14 | 1 | 004:33 | P | NO SE REPORTO CAUSA | 2 X 10 EN TRANSFORMADOR | B21122700020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 273 | 2021-12-27 | 273 | keep | 0 | Dec | 2021 | 0.00018594 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-12-27 12:08 | 2021-12-28 12:09 | 40 | 024:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO Y 1 X 100 EN CORTE DE LINEA | C2112700062 | New_Event | Wire Down | Include | Include | Equipment | 1441 | 2021-12-27 | 57640 | keep | 0 | Dec | 2021 | 0.039258 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2021-12-27 12:15 | 2021-12-27 14:51 | 75 | 002:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR FUERTES VIENTOS | M21122700027 | New_Event | Bad Weather | Include | Include | Weather | 156 | 2021-12-27 | 11700 | keep | 0 | Dec | 2021 | 0.0079688 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2021-12-27 12:19 | 2021-12-27 13:12 | 12 | 000:53 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA REALIZAR DESGANCHE SECUNDARIO Y REPARAR TRENZA | R21122700017 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 53 | 2021-12-27 | 636 | keep | 0 | Dec | 2021 | 0.00043318 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-12-27 12:46 | 2021-12-27 17:35 | 20 | 004:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | M21122700030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 289 | 2021-12-27 | 5780 | keep | 0 | Dec | 2021 | 0.0039367 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2021-12-27 13:11 | 2021-12-27 15:00 | 10 | 001:49 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE ENCONTRO NADA | P21122700022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2021-12-27 | 1090 | keep | 0 | Dec | 2021 | 0.00074239 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-12-27 13:13 | 2021-12-27 16:27 | 1 | 003:14 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA Y 1 X 20 EN TRANSFORMADOR | B21122700038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 194 | 2021-12-27 | 194 | keep | 0 | Dec | 2021 | 0.00013213 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-12-27 13:21 | 2021-12-27 20:17 | 80 | 006:56 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21122700041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 416 | 2021-12-27 | 33280 | keep | 0 | Dec | 2021 | 0.022667 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2021-12-27 13:34 | 2021-12-27 16:11 | 3 | 002:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO LINEA | C21122700043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 157 | 2021-12-27 | 471 | keep | 0 | Dec | 2021 | 0.0003208 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2021-12-27 13:40 | 2021-12-27 14:18 | 1 | 000:38 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER NO CAUSA | R21122700026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 38 | 2021-12-27 | 38 | keep | 0 | Dec | 2021 | 2.5882e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-12-27 13:46 | 2021-12-27 16:30 | 44 | 002:44 | P | DESGANCHE | 1 X 50 EN C/L Y 1 X 8 EN XMR | R21122700027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2021-12-27 | 7216 | keep | 0 | Dec | 2021 | 0.0049148 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
CANOVANAS | 2021-12-27 13:58 | 2021-12-27 15:32 | 20 | 001:34 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 15 EN RISER REMPLAZO PISTOLA AVERIADA EN PM Y CAJA AVERIADA EN RISER | R21122700030 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 94 | 2021-12-27 | 1880 | keep | 0 | Dec | 2021 | 0.0012805 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-12-27 14:01 | 2021-12-27 17:06 | 200 | 003:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A21122700024 | New_Event |  |  | Include | Wildlife | 185 | 2021-12-27 | 37000 | keep | 0 | Dec | 2021 | 0.025201 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2021-12-27 14:16 | 2021-12-27 15:00 | 1 | 000:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTE SECUNDARIO | M21122700038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 44 | 2021-12-27 | 44 | keep | 0 | Dec | 2021 | 2.9968e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-12-27 14:30 | 2021-12-27 14:40 | 7 | 000:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA RETEZAR LINEA SECUNDARIA | A21122700026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 10 | 2021-12-27 | 70 | keep | 0 | Dec | 2021 | 4.7677e-05 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2021-12-27 14:44 | 2021-12-27 15:07 | 293 | 000:23 | T | LINEA DE TRANSMISION 38KV | SE RETIRA CARGA PARA PODER CERRAR GOAB 7911-A | P21122700038 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-12-27 | 6739 | keep | 0 | Dec | 2021 | 0.0045899 | 0.00019956 | Sustained | FALSE | FALSE | Not_TMED_Event | 293
PONCE | 2021-12-27 14:44 | 2021-12-27 15:07 | 253 | 000:23 | T | LINEA DE TRANSMISION 38KV | SE RETIRA CARGA PARA PODER CERRAR GOAB 7911-A | P21122700040 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-12-27 | 5819 | keep | 0 | Dec | 2021 | 0.0039633 | 0.00017232 | Sustained | FALSE | FALSE | Not_TMED_Event | 253
PONCE | 2021-12-27 14:44 | 2021-12-27 15:07 | 900 | 000:23 | T | LINEA DE TRANSMISION 38KV | SE RETIRA CARGA PARA PODER CERRAR GOAB 7911-A | P21122700042 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-12-27 | 20700 | keep | 0 | Dec | 2021 | 0.014099 | 0.00061299 | Sustained | FALSE | FALSE | Not_TMED_Event | 900
PONCE | 2021-12-27 14:44 | 2021-12-27 15:07 | 1615 | 000:23 | T | LINEA DE TRANSMISION 38KV | SE RETIRA CARGA PARA PODER CERRAR GOAB 7911-A | P21122700043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-12-27 | 37145 | keep | 0 | Dec | 2021 | 0.025299 | 0.0011 | Sustained | FALSE | FALSE | Not_TMED_Event | 1615
PONCE | 2021-12-27 14:44 | 2021-12-27 15:07 | 3 | 000:23 | T | LINEA DE TRANSMISION 38KV | SE RETIRA CARGA PARA PODER CERRAR GOAB 7911-A | P21122700044 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-12-27 | 69 | keep | 0 | Dec | 2021 | 4.6996e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2021-12-27 14:47 | 2021-12-27 16:33 | 160 | 001:46 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO CAUSA | C21122700047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2021-12-27 | 16960 | keep | 0 | Dec | 2021 | 0.011551 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
MAYAGÃœEZ | 2021-12-27 14:47 | 2021-12-28 12:05 | 10 | 021:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO Y SE REMPLAZO CAJA EN MALAS CONDICIONES | M21122700047 | New_Event | Wire Down | Include | Include | Equipment | 1278 | 2021-12-27 | 12780 | keep | 0 | Dec | 2021 | 0.0087044 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-27 14:54 | 2021-12-27 17:55 | 513 | 003:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR 1118-10 QUE A SU VEZ LLEVA EL 20% DEL 1111-01. SE REALIZARON OPERACINES DE CAMPO Y SE RETIRO IGUANA SE REEMPLAZO CAJA AVERIADA Y SE CERRO AMARRE | S21122700039 | New_Event |  |  | Include | Wildlife | 181 | 2021-12-27 | 92853 | keep | 0 | Dec | 2021 | 0.063242 | 0.0003494 | Sustained | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2021-12-27 14:54 | 2021-12-27 15:46 | 2782 | 000:52 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR 1118-10 QUE A SU VEZ LLEVA EL 20% DEL 1111-01. SE REALIZARON OPERACINES DE CAMPO Y SE CERRO POR SCADA. ENTRA UN 50% DEL 1118-10. CONTINUA FUERA EN 20% DEL 1111-01 | S21122700039 | New_Event |  |  | Include | Wildlife | 52 | 2021-12-27 | 144664 | keep | 0 | Dec | 2021 | 0.09853 | 0.0018948 | Sustained | FALSE | FALSE | Not_TMED_Event | 2782
GUAYAMA | 2021-12-27 15:02 | 2021-12-27 17:22 | 292 | 002:20 | P | AISLADOR ROTO, PARTIDO O SAFADO | 3 X 100 EN CORTE DE LINEA SE REMPLAZARON DOS AISLADORES | P21122700048 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 140 | 2021-12-27 | 40880 | keep | 0 | Dec | 2021 | 0.027843 | 0.00019888 | Sustained | FALSE | FALSE | Not_TMED_Event | 292
CANOVANAS | 2021-12-27 15:10 | 2021-12-27 16:40 | 50 | 001:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE X AVE | R21122700033 | New_Event |  |  | Include | Wildlife | 90 | 2021-12-27 | 4500 | keep | 0 | Dec | 2021 | 0.0030649 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-27 15:14 | 2021-12-27 19:59 | 1 | 004:45 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | B21122700046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 285 | 2021-12-27 | 285 | keep | 0 | Dec | 2021 | 0.00019411 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-12-27 15:19 | 2021-12-27 17:29 | 10 | 002:10 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M21122700054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2021-12-27 | 1300 | keep | 0 | Dec | 2021 | 0.00088542 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-27 15:46 | 2021-12-27 16:44 | 1391 | 000:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE RETIRO GALLINA DE PALO Y SE REEMPLAZO MACHETE. ENTRA 100% 1118-10 Y EL 20% DEL 1111-01 | S21122700039 | Partial_restoration |  |  | Include | Wildlife | 58 | 2021-12-27 | 80678 | keep | 0 | Dec | 2021 | 0.054949 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-27 16:12 | 2021-12-27 16:13 | 1483 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 QUE A SU VEZ 1336-9 Y UN 30% DEL 1204-04 | S21122700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-27 | 1483 | keep | 0 | Dec | 2021 | 0.0010101 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2021-12-27 16:12 | 2021-12-27 16:13 | 5290 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 QUE A SU VEZ 1336-9 Y UN 30% DEL 1204-04 | S21122700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-27 | 5290 | keep | 0 | Dec | 2021 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2021-12-27 16:12 | 2021-12-27 16:13 | 207 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 QUE A SU VEZ 1336-9 Y UN 30% DEL 1204-04 | S21122700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-27 | 207 | keep | 0 | Dec | 2021 | 0.00014099 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2021-12-27 16:13 | 2021-12-27 16:14 | 1483 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 QUE A SU VEZ LLEVA LA CARGA PARCIAL DEL 1204-04 UN 30% Y UN 100% DEL 1336-09 | S21122700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-27 | 1483 | keep | 0 | Dec | 2021 | 0.0010101 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2021-12-27 16:13 | 2021-12-27 16:14 | 5290 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 QUE A SU VEZ LLEVA LA CARGA PARCIAL DEL 1204-04 UN 30% Y UN 100% DEL 1336-09 | S21122700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-27 | 5290 | keep | 0 | Dec | 2021 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2021-12-27 16:13 | 2021-12-27 16:14 | 207 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 QUE A SU VEZ LLEVA LA CARGA PARCIAL DEL 1204-04 UN 30% Y UN 100% DEL 1336-09 | S21122700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-27 | 207 | keep | 0 | Dec | 2021 | 0.00014099 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
YAUCO | 2021-12-27 16:32 | 2021-12-29 16:45 | 1 | 048:13 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | P21122700073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2893 | 2021-12-27 | 2893 | keep | 0 | Dec | 2021 | 0.0019704 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-12-27 16:36 | 2021-12-27 17:20 | 233 | 000:44 | P | DESGANCHE | 1 X 65 EN CORTE DELINEA POR DESGANCHE | P21122700075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 44 | 2021-12-27 | 10252 | keep | 0 | Dec | 2021 | 0.0069826 | 0.0001587 | Sustained | FALSE | FALSE | Not_TMED_Event | 233
VEGA BAJA | 2021-12-27 16:36 | 2021-12-27 18:36 | 40 | 002:00 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21122700051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2021-12-27 | 4800 | keep | 0 | Dec | 2021 | 0.0032693 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-12-27 16:39 | 2021-12-27 17:23 | 50 | 000:44 | P | DESGANCHE | 1 X 50 EN C/L | C21122700054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 44 | 2021-12-27 | 2200 | keep | 0 | Dec | 2021 | 0.0014984 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-12-27 16:44 | 2021-12-27 16:45 | 2782 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | EN OPERACIONES DE CAMPO DISPARO INTERRUPTOR 1118-10. SE SECCIONALIZO NUEVAMENTE Y SE CERRO POR SCADA. ENTRA UN 50% EN SERVICIO | S21122700039 | Additional_clients |  |  | Include | Wildlife | 1 | 2021-12-27 | 2782 | keep | 0 | Dec | 2021 | 0.0018948 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-27 16:45 | 2021-12-27 17:55 | 1391 | 001:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE RETIRO GALLINA DE PALO Y SE REEMPLAZO MACHETE. ENTRA 100% 1118-10 Y EL 20% DEL 1111-01 | S21122700039 | 1st_after_momentary |  |  | Include | Wildlife | 70 | 2021-12-27 | 97370 | keep | 0 | Dec | 2021 | 0.066318 | 0.0009474 | Sustained | FALSE | FALSE | Not_TMED_Event | 1391
ARECIBO | 2021-12-27 16:46 | 2021-12-27 17:10 | 5 | 000:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A21122700036 | New_Event |  |  | Include | Wildlife | 24 | 2021-12-27 | 120 | keep | 0 | Dec | 2021 | 8.1731e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-12-27 16:54 | 2021-12-27 17:34 | 15 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21122700023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2021-12-27 | 600 | keep | 0 | Dec | 2021 | 0.00040866 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2021-12-27 16:55 | 2021-12-28 16:28 | 25 | 023:33 | P | ESTRUCTURA AVERIADA | SE LEVANTO CONDUCTOR DEL SUELO Y SE REEMPLAZO POSTE DEL SUELO | C21122700027 | New_Event | Defective Pole | Include | Include | Equipment | 1413 | 2021-12-27 | 35325 | keep | 0 | Dec | 2021 | 0.02406 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-12-27 17:18 | 2021-12-27 20:06 | 20 | 002:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA | S21122700087 | New_Event | Cutout Failure | Include | Include | Equipment | 168 | 2021-12-27 | 3360 | keep | 0 | Dec | 2021 | 0.0022885 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-12-27 17:27 | 2021-12-27 17:28 | 271 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21122700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-27 | 271 | keep | 0 | Dec | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
BAYAMON | 2021-12-27 17:28 | 2021-12-27 17:29 | 948 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21122700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-27 | 948 | keep | 0 | Dec | 2021 | 0.00064568 | 0.00064568 | Momentary | FALSE | FALSE | Not_TMED_Event | 948
PONCE | 2021-12-27 17:48 | 2021-12-28 09:17 | 50 | 015:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21122700083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 929 | 2021-12-27 | 46450 | keep | 0 | Dec | 2021 | 0.031637 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-27 17:59 | 2021-12-27 18:00 | 271 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21122700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-27 | 271 | keep | 0 | Dec | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
ARECIBO | 2021-12-27 18:15 | 2021-12-28 11:07 | 1 | 016:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 10 EN TRANSFORMADOR SE REPARO BAJANTE DE TRANSFORMADOR | A21122700038 | New_Event | Wire Down | Include | Include | Equipment | 1012 | 2021-12-27 | 1012 | keep | 0 | Dec | 2021 | 0.00068927 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-27 18:51 | 2021-12-27 19:10 | 15 | 000:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR PEDESTAL SECUNDARIO | B21122700042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 19 | 2021-12-27 | 285 | keep | 0 | Dec | 2021 | 0.00019411 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-12-27 19:07 | 2021-12-27 19:33 | 30 | 000:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A21122700042 | New_Event |  |  | Include | Wildlife | 26 | 2021-12-27 | 780 | keep | 0 | Dec | 2021 | 0.00053125 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-27 19:43 | 2021-12-27 21:03 | 15 | 001:20 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR FUSIBLE CORROIDO | A21122700043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 80 | 2021-12-27 | 1200 | keep | 0 | Dec | 2021 | 0.00081731 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-12-27 19:58 | 2021-12-27 19:59 | 723 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA LA CARGA DEL 1711-05 | B21122700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-27 | 723 | keep | 0 | Dec | 2021 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2021-12-27 19:58 | 2021-12-27 19:59 | 1976 | 000:01 | T | NO SE REPORTO CAUSA | CARGA TRANSFERIDA AL 1711-02 | B21122700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-27 | 1976 | keep | 0 | Dec | 2021 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
MAYAGÃœEZ | 2021-12-27 20:27 | 2021-12-27 20:40 | 10 | 000:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 12 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M21122700076 | New_Event | Bad Weather | Include | Include | Weather | 13 | 2021-12-27 | 130 | keep | 0 | Dec | 2021 | 8.8542e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-27 21:19 | 2021-12-28 14:50 | 10 | 017:31 | P | PARARRAYOS DEFECTUOSO | 3 X 25 EN SU 2 SE ELIMINO PARARRAYOS AVERIADO EN SU | S21122700101 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1051 | 2021-12-27 | 10510 | keep | 0 | Dec | 2021 | 0.0071583 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-27 21:45 | 2021-12-27 22:21 | 10 | 000:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | A21122700039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 36 | 2021-12-27 | 360 | keep | 0 | Dec | 2021 | 0.00024519 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-27 22:12 | 2021-12-28 10:43 | 55 | 012:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA DEFECTUOSA | S21122700102 | New_Event | Cutout Failure | Include | Include | Equipment | 751 | 2021-12-27 | 41305 | keep | 0 | Dec | 2021 | 0.028133 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
SAN JUAN | 2021-12-27 23:36 | 2021-12-27 23:37 | 922 | 000:01 | T | NO SE REPORTO CAUSA | CARGA TRANSFERIDA AL 1401-08 | S21122700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-27 | 922 | keep | 0 | Dec | 2021 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-12-27 23:36 | 2021-12-27 23:37 | 135 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA LA CARGA DEL 1346-05 | S21122700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-27 | 135 | keep | 0 | Dec | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
UTUADO | 2021-12-28 00:56 | 2021-12-29 01:26 | 200 | 024:30 | P | ESTRUCTURA AVERIADA | SE SECCIONALIZO POSTE PARTIDO CON TRANSFORMADOR ABRIENDO PUENTES A AMBOS EXTREMOS DE POSTE PARTIDO Y SE CERRO N/O CON 8302-05 | A21122800083 | New_Event | Defective Pole | Include | Include | Equipment | 1470 | 2021-12-28 | 294000 | keep | 0 | Dec | 2021 | 0.20024 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2021-12-28 01:08 | 2021-12-28 13:27 | 20 | 012:19 | P | NO SE REPORTO CAUSA | SE REPUSO 1 X 40 EN CORTE DE LINEA | B21122800002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 739 | 2021-12-28 | 14780 | keep | 0 | Dec | 2021 | 0.010067 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-12-28 05:04 | 2021-12-28 09:12 | 25 | 004:08 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C21122800002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 248 | 2021-12-28 | 6200 | keep | 0 | Dec | 2021 | 0.0042228 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-12-28 05:14 | 2021-12-28 11:37 | 35 | 006:23 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21122800001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 383 | 2021-12-28 | 13405 | keep | 0 | Dec | 2021 | 0.0091301 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2021-12-28 06:38 | 2021-12-28 06:39 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21122800003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-28 | 2113 | keep | 0 | Dec | 2021 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
PONCE | 2021-12-28 06:39 | 2021-12-28 08:51 | 50 | 002:12 | P | NO SE REPORTO CAUSA | 1 X 50 EN SU-8/ NO CAUSA | P21122800005 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 132 | 2021-12-28 | 6600 | keep | 0 | Dec | 2021 | 0.0044952 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-12-28 07:51 | 2021-12-28 12:40 | 25 | 004:49 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21122800012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 289 | 2021-12-28 | 7225 | keep | 0 | Dec | 2021 | 0.0049209 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2021-12-28 08:13 | 2021-12-28 08:14 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21122800006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-28 | 1192 | keep | 0 | Dec | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
PONCE | 2021-12-28 08:14 | 2021-12-28 10:10 | 50 | 001:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 30 EN RISER | P21122800007 | New_Event |  |  | Include | Wildlife | 116 | 2021-12-28 | 5800 | keep | 0 | Dec | 2021 | 0.0039504 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-12-28 08:57 | 2021-12-28 20:45 | 12 | 011:48 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | A21122800006 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 708 | 2021-12-28 | 8496 | keep | 0 | Dec | 2021 | 0.0057866 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2021-12-28 09:03 | 2021-12-28 09:04 | 2484 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21122800009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-28 | 2484 | keep | 0 | Dec | 2021 | 0.0016918 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
MAYAGÃœEZ | 2021-12-28 09:12 | 2021-12-28 09:13 | 2560 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21122800010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-28 | 2560 | keep | 0 | Dec | 2021 | 0.0017436 | 0.0017436 | Momentary | FALSE | FALSE | Not_TMED_Event | 2560
CAGUAS | 2021-12-28 09:20 | 2021-12-28 10:22 | 12 | 001:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO TRANSFORMADOR PARA LEVANTAR SECUNDARIA Y REEMPLAZAR CAJA PRIMARIA | C21122800011 | New_Event | Cutout Failure | Include | Include | Equipment | 62 | 2021-12-28 | 744 | keep | 0 | Dec | 2021 | 0.00050674 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-12-28 09:21 | 2021-12-28 11:03 | 40 | 001:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN RISER SE REMPLAZO PORTAFUSIBLE | R21122800006 | New_Event | Cutout Failure | Include | Include | Equipment | 102 | 2021-12-28 | 4080 | keep | 0 | Dec | 2021 | 0.0027789 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-28 09:23 | 2021-12-28 19:05 | 6 | 009:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B21122800011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 582 | 2021-12-28 | 3492 | keep | 0 | Dec | 2021 | 0.0023784 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-12-28 09:25 | 2021-12-28 16:42 | 1 | 007:17 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | A21122800008 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 437 | 2021-12-28 | 437 | keep | 0 | Dec | 2021 | 0.00029764 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-28 09:29 | 2021-12-28 10:03 | 1 | 000:34 | P | NO SE REPORTO CAUSA | 1 X 15 EN RISER | R21122800009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 34 | 2021-12-28 | 34 | keep | 0 | Dec | 2021 | 2.3157e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-12-28 09:29 | 2021-12-28 14:37 | 30 | 005:08 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 80 EN CORTE DE LINEA | R21122800008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 308 | 2021-12-28 | 9240 | keep | 0 | Dec | 2021 | 0.0062933 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2021-12-28 09:33 | 2021-12-28 12:49 | 10 | 003:16 | P | NO SE REPORTO CAUSA | 2 X 10 EN TRANSFORMADOR | R21122800010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 196 | 2021-12-28 | 1960 | keep | 0 | Dec | 2021 | 0.0013349 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-12-28 09:52 | 2021-12-28 12:36 | 1 | 002:44 | P | NO SE REPORTO CAUSA | 1 X 20 XMR | S21122800019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 164 | 2021-12-28 | 164 | keep | 0 | Dec | 2021 | 0.0001117 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-12-28 09:54 | 2021-12-28 10:23 | 20 | 000:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR TRANSFORMADOR PARA REPARAR SECUNDARIA | C21122800017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 29 | 2021-12-28 | 580 | keep | 0 | Dec | 2021 | 0.00039504 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-12-28 09:55 | 2021-12-28 10:15 | 6 | 000:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A21122800003 | New_Event | Secondary Wire Down | Include | Include | Equipment | 20 | 2021-12-28 | 120 | keep | 0 | Dec | 2021 | 8.1731e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-12-28 10:04 | 2021-12-28 14:04 | 20 | 004:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN EL CORTE DE LINEA POR AVE EN EL 13KV | B21122800013 | New_Event |  |  | Include | Wildlife | 240 | 2021-12-28 | 4800 | keep | 0 | Dec | 2021 | 0.0032693 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-12-28 10:09 | 2021-12-28 15:15 | 2 | 005:06 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 37.5KVA X 37.5KVA | M21122800015 | New_Event | Service Transformer Failure | Include | Include | Equipment | 306 | 2021-12-28 | 612 | keep | 0 | Dec | 2021 | 0.00041683 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2021-12-28 10:10 | 2021-12-28 17:10 | 20 | 007:00 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | R21122800013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 420 | 2021-12-28 | 8400 | keep | 0 | Dec | 2021 | 0.0057212 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-12-28 10:11 | 2021-12-28 10:12 | 250 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DEL 1806-02 LLEVA PARTE DEL 1717-01 | B21122800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-28 | 250 | keep | 0 | Dec | 2021 | 0.00017027 | 0.00017027 | Momentary | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2021-12-28 10:11 | 2021-12-28 10:12 | 4622 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA PARTE DEL 1717-01 | B21122800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-28 | 4622 | keep | 0 | Dec | 2021 | 0.003148 | 0.003148 | Momentary | FALSE | FALSE | Not_TMED_Event | 4622
CAGUAS | 2021-12-28 10:14 | 2021-12-28 16:31 | 10 | 006:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LA LINEA | C21122800021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 377 | 2021-12-28 | 3770 | keep | 0 | Dec | 2021 | 0.0025677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-12-28 10:18 | 2021-12-28 11:47 | 15 | 001:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR TRANSFORMADOR PARA REEMPLAZAR BAJANTE SECUNDARIO | C2112700058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 89 | 2021-12-28 | 1335 | keep | 0 | Dec | 2021 | 0.00090926 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-12-28 10:18 | 2021-12-28 11:15 | 10 | 000:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B21122800017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 57 | 2021-12-28 | 570 | keep | 0 | Dec | 2021 | 0.00038822 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2021-12-28 10:24 | 2021-12-28 13:21 | 10 | 002:57 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REMPLAZO POSTE SECUNDARIO PARTIDO Y SE RELOCALIZO SECUNDARIA | P21122800014 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 177 | 2021-12-28 | 1770 | keep | 0 | Dec | 2021 | 0.0012055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-12-28 10:27 | 2021-12-28 12:15 | 100 | 001:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | R21122800017 | New_Event | Cutout Failure | Include | Include | Equipment | 108 | 2021-12-28 | 10800 | keep | 0 | Dec | 2021 | 0.0073558 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2021-12-28 10:28 | 2021-12-28 17:07 | 10 | 006:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LAS LINEAS | C21122800023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 399 | 2021-12-28 | 3990 | keep | 0 | Dec | 2021 | 0.0027176 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-12-28 10:32 | 2021-12-28 10:33 | 1494 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 9101-02 LLEVANDO LA CARGA DEL 9101-04 | B21122800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-28 | 1494 | keep | 0 | Dec | 2021 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
SAN JUAN | 2021-12-28 10:46 | 2021-12-28 10:47 | 726 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR SE CERRO POR SCADA LLEVA EL 1346-04 | S21122800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-28 | 726 | keep | 0 | Dec | 2021 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-12-28 10:46 | 2021-12-28 10:47 | 3932 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR SE CERRO POR SCADA CARGA POR EL 1303-03 | S21122800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-28 | 3932 | keep | 0 | Dec | 2021 | 0.0026781 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
HUMACAO | 2021-12-28 10:48 | 2021-12-28 13:25 | 3 | 002:37 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C21122800025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 157 | 2021-12-28 | 471 | keep | 0 | Dec | 2021 | 0.0003208 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2021-12-28 11:05 | 2021-12-28 14:15 | 120 | 003:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIAS | C21122800029 | New_Event | Bad Weather | Include | Include | Weather | 190 | 2021-12-28 | 22800 | keep | 0 | Dec | 2021 | 0.015529 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2021-12-28 11:17 | 2021-12-28 18:31 | 300 | 007:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR NEUTRAL PRIMARIO PARTIDO Y SE REALIZAR DESGANCHE | M21122800018 | New_Event | Wire Down | Include | Include | Equipment | 434 | 2021-12-28 | 130200 | keep | 0 | Dec | 2021 | 0.088679 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-12-28 11:32 | 2021-12-28 15:48 | 1 | 004:16 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO TRANSFORMADOR PARA ABRIR RISER SECUNDARIO AVERIADO | M21122800020 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 256 | 2021-12-28 | 256 | keep | 0 | Dec | 2021 | 0.00017436 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-28 11:38 | 2021-12-28 16:52 | 10 | 005:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR SECUNDARIA QUEMADA | S21122800025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 314 | 2021-12-28 | 3140 | keep | 0 | Dec | 2021 | 0.0021386 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-28 11:46 | 2021-12-28 15:01 | 10 | 003:15 | P | NO SE REPORTO CAUSA | 2 X 15 EN TRANSFORMADOR | S21122800038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 195 | 2021-12-28 | 1950 | keep | 0 | Dec | 2021 | 0.0013281 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-28 11:49 | 2021-12-28 16:32 | 12 | 004:43 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO | S21122800028 | New_Event | Defective Pole | Include | Include | Equipment | 283 | 2021-12-28 | 3396 | keep | 0 | Dec | 2021 | 0.002313 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-12-28 12:00 | 2021-12-28 15:41 | 1 | 003:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN RISER SE REMPLAZO PORTAFUSIBLE | R21122800026 | New_Event | Cutout Failure | Include | Include | Equipment | 221 | 2021-12-28 | 221 | keep | 0 | Dec | 2021 | 0.00015052 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-12-28 12:03 | 2021-12-28 16:32 | 12 | 004:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARARON VARIAS CONDICIONES EN LAS LINEAS Y BAJANTE HACIAS TRANSFORMADOR | C21122800038 | New_Event | Wire Down | Include | Include | Equipment | 269 | 2021-12-28 | 3228 | keep | 0 | Dec | 2021 | 0.0021986 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-12-28 12:19 | 2021-12-28 15:42 | 20 | 003:23 | P | ESTRUCTURA AVERIADA | 1 X 40 EN CORTE DE LINEA Y SE SECCIONALIZO TRAMO PARA CAMBIO DE POSTE | B21122800026 | New_Event | Defective Pole | Include | Include | Equipment | 203 | 2021-12-28 | 4060 | keep | 0 | Dec | 2021 | 0.0027652 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-12-28 12:33 | 2021-12-28 13:38 | 10 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES DE TRANSFORMADOR | A21122800017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2021-12-28 | 650 | keep | 0 | Dec | 2021 | 0.00044271 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-12-28 12:51 | 2021-12-28 14:30 | 10 | 001:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BARRAS SECUNDARIAS EN PEDESTAL | R21122800030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 99 | 2021-12-28 | 990 | keep | 0 | Dec | 2021 | 0.00067428 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-28 13:00 | 2021-12-28 17:00 | 30 | 004:00 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR POSTE SECUNDARIO PARTIDO Y LINEAS SECUNDARIAS | A21122800005 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 240 | 2021-12-28 | 7200 | keep | 0 | Dec | 2021 | 0.0049039 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-12-28 13:10 | 2021-12-28 15:19 | 15 | 002:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | C21122800025 | New_Event | Cutout Failure | Include | Include | Equipment | 129 | 2021-12-28 | 1935 | keep | 0 | Dec | 2021 | 0.0013179 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-12-28 13:15 | 2021-12-28 16:20 | 8 | 003:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA CLIENTE CORTANDO RAMAS CRUZO LA LINEA | A21122800027 | New_Event |  |  | Include | Wildlife | 185 | 2021-12-28 | 1480 | keep | 0 | Dec | 2021 | 0.001008 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-12-28 13:16 | 2021-12-28 16:33 | 40 | 003:17 | P | NO SE REPORTO CAUSA | SE REPUSO 1 X 50 EN CORTE DE LINEA Y 1 X 30 EN OTRO CORTE DE LINEA | B21122800031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 197 | 2021-12-28 | 7880 | keep | 0 | Dec | 2021 | 0.005367 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-28 13:17 | 2021-12-28 14:33 | 20 | 001:16 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S21122800045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 76 | 2021-12-28 | 1520 | keep | 0 | Dec | 2021 | 0.0010353 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-12-28 13:37 | 2021-12-28 14:25 | 4 | 000:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 8 EN TRANSFORMADOR SE REPARARON VIARIAS CONDICIONES EN LA LINEA | C21122800046 | New_Event | Secondary Wire Down | Include | Include | Equipment | 48 | 2021-12-28 | 192 | keep | 0 | Dec | 2021 | 0.00013077 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
FAJARDO | 2021-12-28 13:53 | 2021-12-28 16:25 | 10 | 002:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA | R21122800031 | New_Event | Cutout Failure | Include | Include | Equipment | 152 | 2021-12-28 | 1520 | keep | 0 | Dec | 2021 | 0.0010353 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-28 13:56 | 2021-12-28 15:39 | 270 | 001:43 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR INTERRUPTOR 1118-10 LLEVA 20% 1111-01, SE SECCIONALIZANDO ALIMENTADOR POR MACHETES AVERIADOS Y SE CERRO POR SCADA | S21122800048 | New_Event | Switch Failure | Include | Include | Equipment | 103 | 2021-12-28 | 27810 | keep | 0 | Dec | 2021 | 0.018941 | 0.0001839 | Sustained | FALSE | FALSE | Not_TMED_Event | 270
MAYAGÃœEZ | 2021-12-28 13:57 | 2021-12-28 15:41 | 40 | 001:44 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21122800032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2021-12-28 | 4160 | keep | 0 | Dec | 2021 | 0.0028334 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2021-12-28 13:58 | 2021-12-28 17:57 | 10 | 003:59 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | R21122800032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 239 | 2021-12-28 | 2390 | keep | 0 | Dec | 2021 | 0.0016278 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-12-28 14:26 | 2021-12-28 16:09 | 4 | 001:43 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA NO CERRARON LAS ORDENES | C21122800051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2021-12-28 | 412 | keep | 0 | Dec | 2021 | 0.00028061 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2021-12-28 14:35 | 2021-12-28 14:36 | 653 | 000:01 | T | DESGANCHE | RECIERRE DESAGNCGE | P211228000XX | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-28 | 653 | keep | 0 | Dec | 2021 | 0.00044476 | 0.00044476 | Momentary | FALSE | FALSE | Not_TMED_Event | 653
PONCE | 2021-12-28 14:36 | 2021-12-28 17:31 | 100 | 002:55 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHE | P21122800035 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 175 | 2021-12-28 | 17500 | keep | 0 | Dec | 2021 | 0.011919 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-12-28 14:45 | 2021-12-28 17:55 | 12 | 003:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES AVERIADO | A21122800031 | New_Event | Cutout Failure | Include | Include | Equipment | 190 | 2021-12-28 | 2280 | keep | 0 | Dec | 2021 | 0.0015529 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-12-28 15:12 | 2021-12-28 16:30 | 100 | 001:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PRIMARIO PARTIDO NO FUNDIO FUSIBLE | P21122800037 | New_Event | Wire Down | Include | Include | Equipment | 78 | 2021-12-28 | 7800 | keep | 0 | Dec | 2021 | 0.0053125 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2021-12-28 15:27 | 2021-12-28 16:11 | 25 | 000:44 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | B21122800035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 44 | 2021-12-28 | 1100 | keep | 0 | Dec | 2021 | 0.0007492 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-12-28 15:39 | 2021-12-28 15:48 | 1210 | 000:09 | P | DESCONECTIVO DEFECTUOSO | SE CERRO MACHETE EN CALLE BARTOLOME DE LAS CASAS ESQ AVE EDUARDO CONDE Y ABRIENDO EN LA CALLE MOREL CAMPOS POR MACHETES QUEMADOS | S21122800048 | Additional_clients | Switch Failure | Include | Include | Equipment | 9 | 2021-12-28 | 10890 | keep | 0 | Dec | 2021 | 0.0074171 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-12-28 15:40 | 2021-12-28 18:12 | 1 | 002:32 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21122800037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2021-12-28 | 152 | keep | 0 | Dec | 2021 | 0.00010353 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-28 15:42 | 2021-12-28 15:43 | 271 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21122800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-28 | 271 | keep | 0 | Dec | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
BAYAMON | 2021-12-28 15:42 | 2021-12-28 23:43 | 12 | 008:01 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE | B21122800026 | Partial_restoration | Defective Pole | Include | Include | Equipment | 481 | 2021-12-28 | 5772 | keep | 0 | Dec | 2021 | 0.0039313 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-28 15:48 | 2021-12-28 15:53 | 1251 | 000:05 | P | DESCONECTIVO DEFECTUOSO | SE CERRO MACHETE CALLE MOREL CAMPOS INT. EDUARDO CONDE DEJANDO ABIERTO HACIA BARTOLOME DE LAS CASAS POR MACHETES QUEMADOS | S21122800048 | Additional_clients | Switch Failure | Include | Include | Equipment | 5 | 2021-12-28 | 6255 | keep | 0 | Dec | 2021 | 0.0042603 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-28 15:53 | 2021-12-28 16:06 | 150 | 000:13 | P | DESCONECTIVO DEFECTUOSO | SE CERRO MACHETES HACIA BARTOLOME DE LAS CASAS | S21122800048 | Partial_restoration | Switch Failure | Include | Include | Equipment | 13 | 2021-12-28 | 1950 | keep | 0 | Dec | 2021 | 0.0013281 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-12-28 15:57 | 2021-12-28 15:58 | 1835 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21122800053 | New_Event |  |  | Include | Wildlife | 1 | 2021-12-28 | 1835 | keep | 0 | Dec | 2021 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
HUMACAO | 2021-12-28 15:58 | 2021-12-28 18:08 | 169 | 002:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 Y 1 X 50 EN CORTES DE LINEA CRUCE CON AVE | C21122800054 | 1st_after_momentary |  |  | Include | Wildlife | 130 | 2021-12-28 | 21970 | keep | 0 | Dec | 2021 | 0.014964 | 0.00011511 | Sustained | FALSE | FALSE | Not_TMED_Event | 169
BAYAMON | 2021-12-28 15:59 | 2021-12-28 19:16 | 6 | 003:17 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO XMR SE ENREDEZO POSTE Y SE REPARO SECUNDARIA | B21122800040 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 197 | 2021-12-28 | 1182 | keep | 0 | Dec | 2021 | 0.00080505 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-12-28 16:05 | 2021-12-28 20:17 | 50 | 004:12 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L SE REMPLAZO DISCO | B21122800041 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 252 | 2021-12-28 | 12600 | keep | 0 | Dec | 2021 | 0.0085818 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-12-28 16:06 | 2021-12-28 16:09 | 513 | 000:03 | P | DESCONECTIVO DEFECTUOSO | SE CERRO INTERRUPTOR 1118-10 LLEVA 20% 1111-01 SECCIONALIZANDO ALIMENTADOR HACIA CALLE BARTOLOME DE LAS CASAS POR MACHETES QUEMADOS | S21122800048 | New_Event | Switch Failure | Include | Include | Equipment | 3 | 2021-12-28 | 1539 | keep | 0 | Dec | 2021 | 0.0010482 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2021-12-28 16:06 | 2021-12-28 16:09 | 2642 | 000:03 | T | DESCONECTIVO DEFECTUOSO | SE CERRO INTERRUPTOR 1118-10 LLEVA 20% 1111-01 SECCIONALIZANDO ALIMENTADOR HACIA CALLE BARTOLOME DE LAS CASAS POR MACHETES QUEMADOS | S21122800048 | Additional_clients | Switch Failure | Include | Include | Equipment | 3 | 2021-12-28 | 7926 | keep | 0 | Dec | 2021 | 0.0053984 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-28 16:08 | 2021-12-28 20:23 | 40 | 004:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | S21122800101 | New_Event | Cutout Failure | Include | Include | Equipment | 255 | 2021-12-28 | 10200 | keep | 0 | Dec | 2021 | 0.0069472 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-12-28 16:08 | 2021-12-28 16:52 | 1 | 000:44 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21122800041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 44 | 2021-12-28 | 44 | keep | 0 | Dec | 2021 | 2.9968e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-28 16:09 | 2021-12-28 17:53 | 76 | 001:44 | P | DESCONECTIVO DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE REMPLAZARON 3 MACHETES | S21122800048 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 104 | 2021-12-28 | 7904 | keep | 0 | Dec | 2021 | 0.0053834 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
AGUADILLA | 2021-12-28 16:38 | 2021-12-28 19:36 | 15 | 002:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA AVERIADA | M21122800042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 178 | 2021-12-28 | 2670 | keep | 0 | Dec | 2021 | 0.0018185 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-12-28 16:52 | 2021-12-28 20:00 | 10 | 003:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21122800041 | New_Event | Bad Weather | Include | Include | Weather | 188 | 2021-12-28 | 1880 | keep | 0 | Dec | 2021 | 0.0012805 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-12-28 17:01 | 2021-12-28 21:06 | 10 | 004:05 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | R21122800037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 245 | 2021-12-28 | 2450 | keep | 0 | Dec | 2021 | 0.0016687 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-28 17:03 | 2021-12-28 20:00 | 500 | 002:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA CAMION IMPACTO POSTE Y CRUZO LAS LINEAS MOMENTÃNEAMENTE | A21122800053 | New_Event |  |  | Include | Wildlife | 177 | 2021-12-28 | 88500 | keep | 0 | Dec | 2021 | 0.060277 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CAGUAS | 2021-12-28 17:19 | 2021-12-29 09:16 | 100 | 015:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 Y 1 X 80 EN CORTES DE LINEA CRUCE X REPTIL | C21122800059 | New_Event |  |  | Include | Wildlife | 957 | 2021-12-28 | 95700 | keep | 0 | Dec | 2021 | 0.065181 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-12-28 17:37 | 2021-12-28 21:47 | 8 | 004:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA PARTIDA | M21122800051 | New_Event | Secondary Wire Down | Include | Include | Equipment | 250 | 2021-12-28 | 2000 | keep | 0 | Dec | 2021 | 0.0013622 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-12-28 17:53 | 2021-12-28 17:54 | 513 | 000:01 | P | DESCONECTIVO DEFECTUOSO | SE CERRO INTERRUPTOR 1118-10 LLEVA 20% 1111-01 SECCIONALIZANDO ALIMENTADOR HACIA CALLE BARTOLOME DE LAS CASAS POR MACHETES QUEMADOS | S21122800048 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-12-28 | 513 | keep | 0 | Dec | 2021 | 0.0003494 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2021-12-28 17:53 | 2021-12-28 17:54 | 2642 | 000:01 | T | DESCONECTIVO DEFECTUOSO | SE CERRO INTERRUPTOR 1118-10 LLEVA 20% 1111-01 SECCIONALIZANDO ALIMENTADOR POR MACHETES AVERIADOS | S21122800048 | Additional_clients | Switch Failure | Include | Include | Equipment | 1 | 2021-12-28 | 2642 | keep | 0 | Dec | 2021 | 0.0017995 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-28 17:54 | 2021-12-28 20:36 | 150 | 002:42 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZARON 3 MACHETES Y SE CERRO MACHETES HACIA CALLE BARTOLOME DE LAS CASAS | S21122800048 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 162 | 2021-12-28 | 24300 | keep | 0 | Dec | 2021 | 0.016551 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2021-12-28 18:06 | 2021-12-29 12:04 | 7 | 017:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR CONECTOR QUEMADO EN NEUTRAL SECUNDARIO | C21122800067 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1078 | 2021-12-28 | 7546 | keep | 0 | Dec | 2021 | 0.0051395 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-12-28 18:15 | 2021-12-28 21:02 | 10 | 002:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M21122800053 | New_Event | Secondary Wire Down | Include | Include | Equipment | 167 | 2021-12-28 | 1670 | keep | 0 | Dec | 2021 | 0.0011374 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-12-28 18:40 | 2021-12-28 20:14 | 650 | 001:34 | T | DESGANCHE | SE ABRIO MACHETES PARA SECCIONALIZAR Y CERRAR EL INTERRUPTOR PALMA SOBRE LINEAS | A21122800069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2021-12-28 | 61100 | keep | 0 | Dec | 2021 | 0.041615 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
CAGUAS | 2021-12-28 18:48 | 2021-12-29 13:19 | 4 | 018:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR BARRAS DE PEDESTAL | C21122800070 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1111 | 2021-12-28 | 4444 | keep | 0 | Dec | 2021 | 0.0030268 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2021-12-28 19:10 | 2021-12-28 22:08 | 4 | 002:58 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA INFORMA ARIS CORTES QUE REQUIERE DESGANCHE | M21122800055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2021-12-28 | 712 | keep | 0 | Dec | 2021 | 0.00048494 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2021-12-28 19:16 | 2021-12-29 00:56 | 150 | 005:40 | P | ESTRUCTURA AVERIADA | 2 X 140 EN CONVERTIDOR SE SECCIONALIZO POSTE PARTIDO CON TRANSFORMADOR ABRIENDO PUENTES A AMBOS EXTREMOS DE POSTE PARTIDO | A21122800083 | New_Event | Defective Pole | Include | Include | Equipment | 340 | 2021-12-28 | 51000 | keep | 0 | Dec | 2021 | 0.034736 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2021-12-28 20:08 | 2021-12-29 13:15 | 100 | 017:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO Y SE FIJO LINEA A PIN | P21122800056 | New_Event | Wire Down | Include | Include | Equipment | 1027 | 2021-12-28 | 102700 | keep | 0 | Dec | 2021 | 0.069949 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2021-12-28 20:14 | 2021-12-28 20:37 | 498 | 000:23 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA SECCIONALIZAR PALMA SOBRE LINEAS Y CERRAR LOS MACHETES | A21122800099 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 23 | 2021-12-28 | 11454 | keep | 0 | Dec | 2021 | 0.0078013 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-12-28 20:26 | 2021-12-28 22:15 | 200 | 001:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 200 EN CORTE DE LINEA AVE CRUZO LINEAS | M21122800058 | New_Event |  |  | Include | Wildlife | 109 | 2021-12-28 | 21800 | keep | 0 | Dec | 2021 | 0.014848 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-12-28 20:36 | 2021-12-28 21:18 | 76 | 000:42 | P | DESCONECTIVO DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE REMPLAZARON 3 MACHETES | S21122800048 | Partial_restoration | Switch Failure | Include | Include | Equipment | 42 | 2021-12-28 | 3192 | keep | 0 | Dec | 2021 | 0.0021741 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-12-28 20:52 | 2021-12-28 20:53 | 2608 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21122800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-28 | 2608 | keep | 0 | Dec | 2021 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
MAYAGÃœEZ | 2021-12-28 21:40 | 2021-12-29 09:15 | 15 | 011:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M21122800073 | New_Event | Bad Weather | Include | Include | Weather | 695 | 2021-12-28 | 10425 | keep | 0 | Dec | 2021 | 0.0071004 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2021-12-28 21:44 | 2021-12-29 11:44 | 20 | 014:00 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO PALMA | A21122800105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 840 | 2021-12-28 | 16800 | keep | 0 | Dec | 2021 | 0.011442 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-12-28 21:45 | 2021-12-28 22:13 | 7 | 000:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | B21122800044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 28 | 2021-12-28 | 196 | keep | 0 | Dec | 2021 | 0.00013349 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-12-28 22:37 | 2021-12-29 15:03 | 20 | 016:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LA LINEA | S21122800113 | New_Event | Secondary Wire Down | Include | Include | Equipment | 986 | 2021-12-28 | 19720 | keep | 0 | Dec | 2021 | 0.013431 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-12-28 22:53 | 2021-12-28 22:54 | 2450 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C21122800081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-28 | 2450 | keep | 0 | Dec | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
BARRANQUITAS | 2021-12-28 23:14 | 2021-12-28 23:15 | 2192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21122800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-28 | 2192 | keep | 0 | Dec | 2021 | 0.001493 | 0.001493 | Momentary | FALSE | FALSE | Not_TMED_Event | 2192
ARECIBO | 2021-12-28 23:30 | 2021-12-29 10:10 | 5 | 010:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | A21122800107 | New_Event | Bad Weather | Include | Include | Weather | 640 | 2021-12-28 | 3200 | keep | 0 | Dec | 2021 | 0.0021795 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-12-29 00:11 | 2021-12-29 12:31 | 45 | 012:20 | P | DESGANCHE | 1 X 65 EN C/L | C21122900001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 740 | 2021-12-29 | 33300 | keep | 0 | Dec | 2021 | 0.02268 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
VEGA BAJA | 2021-12-29 00:26 | 2021-12-29 00:27 | 1494 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 9101-2 | B21122900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-29 | 1494 | keep | 0 | Dec | 2021 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
SAN JUAN | 2021-12-29 00:34 | 2021-12-29 16:48 | 100 | 016:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE CRITICO | S21122900001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 974 | 2021-12-29 | 97400 | keep | 0 | Dec | 2021 | 0.066339 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2021-12-29 01:26 | 2021-12-29 17:50 | 6 | 016:24 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO SE ABRIO CORTE DE LINEA Y N/O CON 8302-05 PARA CERRAR PUENTES Y NORMALIZAR LA CARGA | A21122800076 | New_Event | Defective Pole | Include | Include | Equipment | 984 | 2021-12-29 | 5904 | keep | 0 | Dec | 2021 | 0.0040212 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-12-29 01:29 | 2021-12-29 01:30 | 2178 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C21122900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-29 | 2178 | keep | 0 | Dec | 2021 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
PONCE | 2021-12-29 02:01 | 2021-12-29 09:06 | 138 | 007:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA POR CONTACTO DE AVE | P21122900001 | New_Event |  |  | Include | Wildlife | 425 | 2021-12-29 | 58650 | keep | 0 | Dec | 2021 | 0.039946 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
CANOVANAS | 2021-12-29 03:14 | 2021-12-29 13:16 | 20 | 010:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA SE RETEZAR CONDUCTOR ARRIADO | R21122900004 | New_Event | Wire Down | Include | Include | Equipment | 602 | 2021-12-29 | 12040 | keep | 0 | Dec | 2021 | 0.0082004 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2021-12-29 03:15 | 2021-12-29 03:43 | 4 | 000:28 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJAS DE TRANSFORMADOR PARA SECCIONALIZAR POSTE SECUNDARIO PARTIDO | A21122900001 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 28 | 2021-12-29 | 112 | keep | 0 | Dec | 2021 | 7.6283e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-12-29 04:38 | 2021-12-29 09:17 | 5 | 004:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | A21122900004 | New_Event | Bad Weather | Include | Include | Weather | 279 | 2021-12-29 | 1395 | keep | 0 | Dec | 2021 | 0.00095013 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2021-12-29 04:59 | 2021-12-29 09:51 | 5 | 004:52 | P | NO SE REPORTO CAUSA | 1 X 8 EN XMR FUSIBLE VIEJO | C21122900003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 292 | 2021-12-29 | 1460 | keep | 0 | Dec | 2021 | 0.0009944 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-12-29 05:18 | 2021-12-29 17:33 | 30 | 012:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA SE RETIRO GLOBO METALICO | B21122900050 | New_Event |  |  | Include | Wildlife | 735 | 2021-12-29 | 22050 | keep | 0 | Dec | 2021 | 0.015018 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-29 05:29 | 2021-12-29 05:30 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21122900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-29 | 308 | keep | 0 | Dec | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
PONCE | 2021-12-29 07:03 | 2021-12-29 13:28 | 50 | 006:25 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21122900004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 385 | 2021-12-29 | 19250 | keep | 0 | Dec | 2021 | 0.013111 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-29 07:17 | 2021-12-29 07:18 | 4080 | 000:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DEL 1717-01 LLEVA 1717-05 Y PARTE DE SU CARGA NORMAL ESTA TRANSFERIDA AL 1806-02 | B21122900000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-12-29 | 4080 | keep | 0 | Dec | 2021 | 0.0027789 | 0.0027789 | Momentary | FALSE | FALSE | Not_TMED_Event | 4080
BAYAMON | 2021-12-29 07:17 | 2021-12-29 07:18 | 341 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DEL 1717-01 LLEVA 1717-05 | B21122900000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-12-29 | 341 | keep | 0 | Dec | 2021 | 0.00023225 | 0.00023225 | Momentary | FALSE | FALSE | Not_TMED_Event | 341
BAYAMON | 2021-12-29 07:18 | 2021-12-29 09:50 | 30 | 002:32 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA Y SE ENDEREZO AISLADOR QUE SE HABIA VIRADO SOBRE EL 13KV | B21122900002 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 152 | 2021-12-29 | 4560 | keep | 0 | Dec | 2021 | 0.0031058 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-29 07:19 | 2021-12-29 08:55 | 75 | 001:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO FASES | A21122900005 | New_Event |  |  | Include | Wildlife | 96 | 2021-12-29 | 7200 | keep | 0 | Dec | 2021 | 0.0049039 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2021-12-29 07:47 | 2021-12-29 19:08 | 20 | 011:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE REPARO SECUNDARIA | B21122900003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 681 | 2021-12-29 | 13620 | keep | 0 | Dec | 2021 | 0.0092765 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-12-29 08:20 | 2021-12-29 08:57 | 60 | 000:37 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | R21122900011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 37 | 2021-12-29 | 2220 | keep | 0 | Dec | 2021 | 0.001512 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-12-29 08:27 | 2021-12-29 08:28 | 1818 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21122900004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-29 | 1818 | keep | 0 | Dec | 2021 | 0.0012382 | 0.0012382 | Momentary | FALSE | FALSE | Not_TMED_Event | 1818
HUMACAO | 2021-12-29 08:53 | 2021-12-29 11:41 | 5 | 002:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 8 EN XMR REMPLAZO CONECTOR QUEMADO EN NEUTRAL SECUNDARIO | C21122900012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 168 | 2021-12-29 | 840 | keep | 0 | Dec | 2021 | 0.00057212 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2021-12-29 09:02 | 2021-12-29 09:40 | 7 | 000:38 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBU SOBRE LINEAS | A21122900015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 38 | 2021-12-29 | 266 | keep | 0 | Dec | 2021 | 0.00018117 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2021-12-29 09:09 | 2021-12-29 13:00 | 80 | 003:51 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | A21122900018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 231 | 2021-12-29 | 18480 | keep | 0 | Dec | 2021 | 0.012587 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-12-29 09:27 | 2021-12-29 15:55 | 3 | 006:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS Y CONEXIONES | M21122900009 | New_Event | Secondary Wire Down | Include | Include | Equipment | 388 | 2021-12-29 | 1164 | keep | 0 | Dec | 2021 | 0.0007928 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-12-29 09:33 | 2021-12-29 17:52 | 4 | 008:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO SECUNDARIA QUEMADA | S21122900007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 499 | 2021-12-29 | 1996 | keep | 0 | Dec | 2021 | 0.0013595 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-12-29 09:39 | 2021-12-29 10:46 | 30 | 001:07 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE | S21122900008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2021-12-29 | 2010 | keep | 0 | Dec | 2021 | 0.001369 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-12-29 09:50 | 2021-12-29 12:08 | 16 | 002:18 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 10 KVA POR UNO DE 37.5 KVA | M21122900007 | New_Event | Service Transformer Failure | Include | Include | Equipment | 138 | 2021-12-29 | 2208 | keep | 0 | Dec | 2021 | 0.0015039 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
HUMACAO | 2021-12-29 09:57 | 2021-12-29 11:17 | 4 | 001:20 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | C21122900019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 80 | 2021-12-29 | 320 | keep | 0 | Dec | 2021 | 0.00021795 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-12-29 10:11 | 2021-12-29 12:10 | 15 | 001:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE ZAFADO DE CAJA A TRANSFORMADOR | A21122900045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 119 | 2021-12-29 | 1785 | keep | 0 | Dec | 2021 | 0.0012158 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-12-29 10:17 | 2021-12-29 11:06 | 10 | 000:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZARON BAJANTES SECUNDARIOS EN TRANSFORMADOR | B21122900015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 49 | 2021-12-29 | 490 | keep | 0 | Dec | 2021 | 0.00033374 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-29 10:19 | 2021-12-29 10:20 | 2720 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR RAMA SOBRE LINEAS PRIMARIAS | A21122900049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-29 | 2720 | keep | 0 | Dec | 2021 | 0.0018526 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
ARECIBO | 2021-12-29 10:20 | 2021-12-29 13:33 | 80 | 003:13 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A21122900089 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 193 | 2021-12-29 | 15440 | keep | 0 | Dec | 2021 | 0.010516 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-12-29 10:25 | 2021-12-29 11:09 | 1000 | 000:44 | P | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR 1424-08 LLEVA EL 100% 1348-07 80% 1348-06 | S21122900011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 44 | 2021-12-29 | 44000 | keep | 0 | Dec | 2021 | 0.029968 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2021-12-29 10:25 | 2021-12-29 11:09 | 278 | 000:44 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR 1424-08 LLEVA EL 100% 1348-07 80% 1348-06 | S21122900011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 44 | 2021-12-29 | 12232 | keep | 0 | Dec | 2021 | 0.0083312 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2021-12-29 10:25 | 2021-12-29 11:09 | 9 | 000:44 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR 1424-08 LLEVA EL 100% 1348-07 80% 1348-06 | S21122900011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 44 | 2021-12-29 | 396 | keep | 0 | Dec | 2021 | 0.00026971 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2021-12-29 10:44 | 2021-12-29 14:22 | 1 | 003:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN RISER | A21122900081 | New_Event | Cutout Failure | Include | Include | Equipment | 218 | 2021-12-29 | 218 | keep | 0 | Dec | 2021 | 0.00014848 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-12-29 10:48 | 2021-12-29 15:53 | 10 | 005:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR ROEDOR CRUZO LINEAS | A21122900063 | New_Event |  |  | Include | Wildlife | 305 | 2021-12-29 | 3050 | keep | 0 | Dec | 2021 | 0.0020773 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2021-12-29 10:56 | 2021-12-29 11:42 | 10 | 000:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE CAJA DE TRANSFFORMADOR PARA REPARAR PEDESTAL SECUNDARIO | P21122900016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 46 | 2021-12-29 | 460 | keep | 0 | Dec | 2021 | 0.0003133 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-12-29 10:58 | 2021-12-29 13:19 | 80 | 002:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA POR CONTACTO DE IGUANA | P21122900017 | New_Event |  |  | Include | Wildlife | 141 | 2021-12-29 | 11280 | keep | 0 | Dec | 2021 | 0.0076828 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2021-12-29 11:03 | 2021-12-29 17:39 | 10 | 006:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A21122900017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 396 | 2021-12-29 | 3960 | keep | 0 | Dec | 2021 | 0.0026971 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-29 11:08 | 2021-12-29 15:13 | 30 | 004:05 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21122900071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2021-12-29 | 7350 | keep | 0 | Dec | 2021 | 0.0050061 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-12-29 11:09 | 2021-12-29 11:27 | 882 | 000:18 | P | DESCONECTIVO DEFECTUOSO | SE CERRO MH-3 HACIA CAJAS SECAS 10% EN SERVICIO | S21122900011 | New_Event | Switch Failure | Include | Include | Equipment | 18 | 2021-12-29 | 15876 | keep | 0 | Dec | 2021 | 0.010813 | 0.00060073 | Sustained | FALSE | FALSE | Not_TMED_Event | 882
SAN JUAN | 2021-12-29 11:09 | 2021-12-29 11:27 | 3 | 000:18 | P | DESCONECTIVO DEFECTUOSO | PERSONAL LOCALIZANDO AVERIA | S21122900011 | New_Event | Switch Failure | Include | Include | Equipment | 18 | 2021-12-29 | 54 | keep | 0 | Dec | 2021 | 3.6779e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2021-12-29 11:11 | 2021-12-29 16:05 | 10 | 004:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | P21122900018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 294 | 2021-12-29 | 2940 | keep | 0 | Dec | 2021 | 0.0020024 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-29 11:19 | 2021-12-29 16:26 | 7 | 005:07 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHO | C21122900031 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 307 | 2021-12-29 | 2149 | keep | 0 | Dec | 2021 | 0.0014637 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-12-29 11:27 | 2021-12-29 11:30 | 1000 | 000:03 | P | DESCONECTIVO DEFECTUOSO | DISPARO | S21122900011 | Additional_clients | Switch Failure | Include | Include | Equipment | 3 | 2021-12-29 | 3000 | keep | 0 | Dec | 2021 | 0.0020433 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-29 11:27 | 2021-12-29 11:30 | 9 | 000:03 | T | DESCONECTIVO DEFECTUOSO | DISPARO | S21122900011 | New_Event | Switch Failure | Include | Include | Equipment | 3 | 2021-12-29 | 27 | keep | 0 | Dec | 2021 | 1.839e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2021-12-29 11:27 | 2021-12-29 11:30 | 9 | 000:03 | T | DESCONECTIVO DEFECTUOSO | DISPARO | S21122900011 | Additional_clients | Switch Failure | Include | Include | Equipment | 3 | 2021-12-29 | 27 | keep | 0 | Dec | 2021 | 1.839e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-29 11:30 | 2021-12-29 11:46 | 3 | 000:16 | P | DESCONECTIVO DEFECTUOSO | PERSONAL LOCALIZANDO AVERIA | S21122900011 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 16 | 2021-12-29 | 48 | keep | 0 | Dec | 2021 | 3.2693e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
YAUCO | 2021-12-29 11:34 | 2021-12-29 11:53 | 10 | 000:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | P21122900019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 19 | 2021-12-29 | 190 | keep | 0 | Dec | 2021 | 0.00012941 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-29 11:38 | 2021-12-29 15:45 | 45 | 004:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21122900022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 247 | 2021-12-29 | 11115 | keep | 0 | Dec | 2021 | 0.0075704 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2021-12-29 11:46 | 2021-12-29 11:47 | 1000 | 000:01 | P | DESCONECTIVO DEFECTUOSO | DISPARO | S21122900011 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-12-29 | 1000 | keep | 0 | Dec | 2021 | 0.0006811 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2021-12-29 11:46 | 2021-12-29 11:47 | 278 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO | S21122900011 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2021-12-29 | 278 | keep | 0 | Dec | 2021 | 0.00018934 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2021-12-29 11:46 | 2021-12-29 11:47 | 9 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO | S21122900011 | Additional_clients | Switch Failure | Include | Include | Equipment | 1 | 2021-12-29 | 9 | keep | 0 | Dec | 2021 | 6.1299e-06 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-29 11:47 | 2021-12-29 12:52 | 4 | 001:05 | P | DESCONECTIVO DEFECTUOSO | PERSONAL LOCALIZANDO AVERIA | S21122900011 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 65 | 2021-12-29 | 260 | keep | 0 | Dec | 2021 | 0.00017708 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2021-12-29 12:00 | 2021-12-29 12:45 | 30 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PM PARA REMPLAZAR BARRA SECUNDARIA QUEMADA | M21122900020 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2021-12-29 | 1350 | keep | 0 | Dec | 2021 | 0.00091948 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-29 12:03 | 2021-12-29 13:30 | 1 | 001:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR AVE CRUZO FASES | A21122900081 | New_Event |  |  | Include | Wildlife | 87 | 2021-12-29 | 87 | keep | 0 | Dec | 2021 | 5.9255e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-29 12:04 | 2021-12-29 14:40 | 15 | 002:36 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE POSTE SECUNDARIO PARTIDO | M21122900027 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 156 | 2021-12-29 | 2340 | keep | 0 | Dec | 2021 | 0.0015938 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-12-29 12:11 | 2021-12-29 14:19 | 30 | 002:08 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | B21122900027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 128 | 2021-12-29 | 3840 | keep | 0 | Dec | 2021 | 0.0026154 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-12-29 12:16 | 2021-12-29 14:46 | 40 | 002:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21122900030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2021-12-29 | 6000 | keep | 0 | Dec | 2021 | 0.0040866 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2021-12-29 12:39 | 2021-12-29 14:38 | 15 | 001:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | P21122900029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 119 | 2021-12-29 | 1785 | keep | 0 | Dec | 2021 | 0.0012158 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2021-12-29 12:42 | 2021-12-29 14:14 | 20 | 001:32 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | P21122900030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2021-12-29 | 1840 | keep | 0 | Dec | 2021 | 0.0012532 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-12-29 12:44 | 2021-12-29 15:04 | 7 | 002:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR XMR PARA REPARAR BAJANTE SECUNDARIO | C21122900043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 140 | 2021-12-29 | 980 | keep | 0 | Dec | 2021 | 0.00066747 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-12-29 12:52 | 2021-12-29 13:10 | 1000 | 000:18 | P | DESCONECTIVO DEFECTUOSO | DISPARO | S21122900011 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 18 | 2021-12-29 | 18000 | keep | 0 | Dec | 2021 | 0.01226 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2021-12-29 12:52 | 2021-12-29 13:10 | 278 | 000:18 | T | DESCONECTIVO DEFECTUOSO | DISPARO | S21122900011 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 18 | 2021-12-29 | 5004 | keep | 0 | Dec | 2021 | 0.0034082 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2021-12-29 12:52 | 2021-12-29 13:10 | 9 | 000:18 | T | DESCONECTIVO DEFECTUOSO | DISPARO | S21122900011 | Additional_clients | Switch Failure | Include | Include | Equipment | 18 | 2021-12-29 | 162 | keep | 0 | Dec | 2021 | 0.00011034 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-29 13:07 | 2021-12-29 14:13 | 12 | 001:06 | P | CABLE SOTERRADO AVERIADO | SE REPARARON BARRAS EN PEDESTAL | B21122900034 | New_Event | UG Cable Fault | Include | Include | Equipment | 66 | 2021-12-29 | 792 | keep | 0 | Dec | 2021 | 0.00053943 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-12-29 13:10 | 2021-12-29 15:33 | 4 | 002:23 | P | DESCONECTIVO DEFECTUOSO | PERSONAL LOCALIZANDO AVERIA | S21122900011 | Partial_restoration | Switch Failure | Include | Include | Equipment | 143 | 2021-12-29 | 572 | keep | 0 | Dec | 2021 | 0.00038959 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-12-29 13:17 | 2021-12-29 14:54 | 100 | 001:37 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | P21122900033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2021-12-29 | 9700 | keep | 0 | Dec | 2021 | 0.0066066 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-12-29 13:54 | 2021-12-29 14:12 | 40 | 000:18 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21122900034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 18 | 2021-12-29 | 720 | keep | 0 | Dec | 2021 | 0.00049039 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-12-29 13:55 | 2021-12-29 19:00 | 50 | 005:05 | P | ESTRUCTURA AVERIADA | 1 X 50 EN CORTE DE LINEA SE SECCIONALIZO POSTE PARTIDO | A21122900103 | New_Event | Defective Pole | Include | Include | Equipment | 305 | 2021-12-29 | 15250 | keep | 0 | Dec | 2021 | 0.010387 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-12-29 14:15 | 2021-12-29 14:16 | 1105 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR BAMBUS HACIENDO CONTACTO CON LINEAS PRIMARIAS | A21122900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-12-29 | 1105 | keep | 0 | Dec | 2021 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
ARECIBO | 2021-12-29 14:16 | 2021-12-29 15:57 | 150 | 001:41 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA INFORMA JOURNEYMAN REQUIERE DESGANCHE | A21122900110 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 101 | 2021-12-29 | 15150 | keep | 0 | Dec | 2021 | 0.010319 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2021-12-29 14:56 | 2021-12-29 21:54 | 100 | 006:58 | P | DESGANCHE | 1 X 50 EN COPRTE DE LINEA Y 1 X 15 EN TRANSFORMADOR | S21122900052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 418 | 2021-12-29 | 41800 | keep | 0 | Dec | 2021 | 0.02847 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-12-29 14:57 | 2021-12-29 19:31 | 25 | 004:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21122900118 | New_Event | Bad Weather | Include | Include | Weather | 274 | 2021-12-29 | 6850 | keep | 0 | Dec | 2021 | 0.0046655 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-12-29 15:06 | 2021-12-29 16:35 | 30 | 001:29 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21122900044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 89 | 2021-12-29 | 2670 | keep | 0 | Dec | 2021 | 0.0018185 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-12-29 15:10 | 2021-12-29 17:21 | 100 | 002:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA ENERGIZADA EN EL PISO SE ABRIO INTERRUPTOR PARA SECCIONALIZAR | A21122900121 | New_Event | Wire Down | Include | Include | Equipment | 131 | 2021-12-29 | 13100 | keep | 0 | Dec | 2021 | 0.0089224 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2021-12-29 15:22 | 2021-12-29 20:02 | 600 | 004:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ABIERTO | M21122900045 | New_Event | Wire Down | Include | Include | Equipment | 280 | 2021-12-29 | 168000 | keep | 0 | Dec | 2021 | 0.11442 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2021-12-29 15:23 | 2021-12-29 16:28 | 100 | 001:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE CON LAGARTO | S21122900050 | New_Event |  |  | Include | Wildlife | 65 | 2021-12-29 | 6500 | keep | 0 | Dec | 2021 | 0.0044271 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-12-29 15:25 | 2021-12-29 19:15 | 150 | 003:50 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21122900047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 230 | 2021-12-29 | 34500 | keep | 0 | Dec | 2021 | 0.023498 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2021-12-29 15:33 | 2021-12-29 15:38 | 1000 | 000:05 | P | DESCONECTIVO DEFECTUOSO | DISPARO | S21122900011 | Partial_restoration | Switch Failure | Include | Include | Equipment | 5 | 2021-12-29 | 5000 | keep | 0 | Dec | 2021 | 0.0034055 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-29 15:33 | 2021-12-29 15:38 | 9 | 000:05 | T | DESCONECTIVO DEFECTUOSO | DISPARO | S21122900011 | New_Event | Switch Failure | Include | Include | Equipment | 5 | 2021-12-29 | 45 | keep | 0 | Dec | 2021 | 3.0649e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2021-12-29 15:33 | 2021-12-29 15:38 | 9 | 000:05 | T | DESCONECTIVO DEFECTUOSO | DISPARO SE VERIFICO PERSONAL FUERA | S21122900059 | Additional_clients | Switch Failure | Include | Include | Equipment | 5 | 2021-12-29 | 45 | keep | 0 | Dec | 2021 | 3.0649e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-29 15:38 | 2021-12-29 17:34 | 5 | 001:56 | P | DESCONECTIVO DEFECTUOSO | AVERIA EN CAJAS SECAS DEL MH 4A Y VACUUM SWITCH DEL MH 5 AVERIADO | S21122900011 | Partial_restoration | Switch Failure | Include | Include | Equipment | 116 | 2021-12-29 | 580 | keep | 0 | Dec | 2021 | 0.00039504 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-12-29 15:40 | 2021-12-29 16:54 | 4 | 001:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES ZULFATADOS | R21122900095 | New_Event | Secondary Wire Down | Include | Include | Equipment | 74 | 2021-12-29 | 296 | keep | 0 | Dec | 2021 | 0.0002016 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-12-29 15:48 | 2021-12-29 19:43 | 100 | 003:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA VIENTOS | S21122900063 | New_Event | Bad Weather | Include | Include | Weather | 235 | 2021-12-29 | 23500 | keep | 0 | Dec | 2021 | 0.016006 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2021-12-29 15:54 | 2021-12-29 19:04 | 200 | 003:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 Y OTRO DE 80 EN DIFERENTES CORTES DE LINEAS SE REPARO ALAMBRE PRIMARIO Y NEUTRAL PARTIDOS | P21122900044 | New_Event | Wire Down | Include | Include | Equipment | 190 | 2021-12-29 | 38000 | keep | 0 | Dec | 2021 | 0.025882 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2021-12-29 16:00 | 2021-12-29 16:01 | 2450 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21122900055 | New_Event |  |  | Include | Wildlife | 1 | 2021-12-29 | 2450 | keep | 0 | Dec | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2021-12-29 16:01 | 2021-12-29 17:47 | 50 | 001:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE X AVE | C21122900057 | 1st_after_momentary |  |  | Include | Wildlife | 106 | 2021-12-29 | 5300 | keep | 0 | Dec | 2021 | 0.0036098 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-29 16:02 | 2021-12-29 18:59 | 30 | 002:57 | P | NO SE REPORTO CAUSA | 1 X 50 EN SU 2 | B21122900049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 177 | 2021-12-29 | 5310 | keep | 0 | Dec | 2021 | 0.0036166 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2021-12-29 16:18 | 2021-12-30 12:08 | 30 | 019:50 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA X 37.5 KVA | M21123000001 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1190 | 2021-12-29 | 35700 | keep | 0 | Dec | 2021 | 0.024315 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-12-29 16:46 | 2021-12-29 18:08 | 1 | 001:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN RISER CRUCE X AVE | C21122900059 | New_Event |  |  | Include | Wildlife | 82 | 2021-12-29 | 82 | keep | 0 | Dec | 2021 | 5.585e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-12-29 16:53 | 2021-12-29 18:00 | 15 | 001:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21122900131 | New_Event | Bad Weather | Include | Include | Weather | 67 | 2021-12-29 | 1005 | keep | 0 | Dec | 2021 | 0.0006845 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-12-29 16:57 | 2021-12-29 17:01 | 1844 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | S21122900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-12-29 | 7376 | keep | 0 | Dec | 2021 | 0.0050238 | 0.0012559 | Momentary | FALSE | FALSE | Not_TMED_Event | 1844
MAYAGÃœEZ | 2021-12-29 17:10 | 2021-12-29 19:13 | 4387 | 002:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE RETIRO BAMBUS SOBRE LAS LINEAS SUBESTACION SIN RTU | M21122900072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2021-12-29 | 539601 | keep | 0 | Dec | 2021 | 0.36752 | 0.002988 | Sustained | FALSE | FALSE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2021-12-29 17:15 | 2021-12-29 18:34 | 100 | 001:19 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21122900077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2021-12-29 | 7900 | keep | 0 | Dec | 2021 | 0.0053807 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-12-29 17:20 | 2021-12-29 21:41 | 150 | 004:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A21122900133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 261 | 2021-12-29 | 39150 | keep | 0 | Dec | 2021 | 0.026665 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2021-12-29 17:21 | 2021-12-29 18:20 | 100 | 000:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | R21122900097 | New_Event |  |  | Include | Wildlife | 59 | 2021-12-29 | 5900 | keep | 0 | Dec | 2021 | 0.0040185 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-12-29 17:21 | 2021-12-29 17:22 | 3157 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO LINEA PRIMARIA PARTIDA SE CERRO INTERRUPTOR | A21122900134 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2021-12-29 | 3157 | keep | 0 | Dec | 2021 | 0.0021502 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-12-29 17:22 | 2021-12-29 18:26 | 300 | 001:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA SE CERRO CORTE DE LINEA | A21122900121 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 64 | 2021-12-29 | 19200 | keep | 0 | Dec | 2021 | 0.013077 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2021-12-29 17:34 | 2021-12-29 17:36 | 1000 | 000:02 | P | DESCONECTIVO DEFECTUOSO | DISPARO | S21122900011 | Partial_restoration | Switch Failure | Include | Include | Equipment | 2 | 2021-12-29 | 2000 | keep | 0 | Dec | 2021 | 0.0013622 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-29 17:34 | 2021-12-29 17:36 | 278 | 000:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO VACUUM SWITCH AVERIADO EN EL MH5 CARGA POR EL 1424-08 | S21122900073 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2021-12-29 | 556 | keep | 0 | Dec | 2021 | 0.00037869 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2021-12-29 17:34 | 2021-12-29 17:36 | 9 | 000:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO VACUUM SWITCH AVERIADO EN EL MH5 | S21122900073 | Additional_clients | Switch Failure | Include | Include | Equipment | 2 | 2021-12-29 | 18 | keep | 0 | Dec | 2021 | 1.226e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-12-29 17:39 | 2021-12-30 11:44 | 60 | 018:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE RETEZO LINEA | C21122900071 | New_Event | Wire Down | Include | Include | Equipment | 1085 | 2021-12-29 | 65100 | keep | 0 | Dec | 2021 | 0.044339 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2021-12-29 17:43 | 2021-12-29 18:58 | 10 | 001:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO Y TOMA | B21122800055 | New_Event | Secondary Wire Down | Include | Include | Equipment | 75 | 2021-12-29 | 750 | keep | 0 | Dec | 2021 | 0.00051082 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-12-29 17:50 | 2021-12-29 19:30 | 300 | 001:40 | P | ESTRUCTURA AVERIADA | SE CERRO PUENTES Y SE CERRO CORTE DE LINEA | A21122800076 | New_Event | Defective Pole | Include | Include | Equipment | 100 | 2021-12-29 | 30000 | keep | 0 | Dec | 2021 | 0.020433 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2021-12-29 18:16 | 2021-12-30 12:46 | 6 | 018:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C21122900078 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1110 | 2021-12-29 | 6660 | keep | 0 | Dec | 2021 | 0.0045361 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-12-29 18:19 | 2021-12-29 19:09 | 30 | 000:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | S21122900054 | New_Event | Cutout Failure | Include | Include | Equipment | 50 | 2021-12-29 | 1500 | keep | 0 | Dec | 2021 | 0.0010216 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2021-12-29 18:27 | 2021-12-30 16:11 | 40 | 021:44 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO CAUSA | C21122900080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1304 | 2021-12-29 | 52160 | keep | 0 | Dec | 2021 | 0.035526 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-29 18:37 | 2021-12-29 18:39 | 2234 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B21122900055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-29 | 4468 | keep | 0 | Dec | 2021 | 0.0030431 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2021-12-29 18:39 | 2021-12-29 20:51 | 30 | 002:12 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21122900061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 132 | 2021-12-29 | 3960 | keep | 0 | Dec | 2021 | 0.0026971 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2021-12-29 18:45 | 2021-12-29 19:04 | 50 | 000:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | P21122900068 | New_Event |  |  | Include | Wildlife | 19 | 2021-12-29 | 950 | keep | 0 | Dec | 2021 | 0.00064704 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2021-12-29 18:48 | 2021-12-29 20:09 | 7 | 001:21 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | R21122900098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2021-12-29 | 567 | keep | 0 | Dec | 2021 | 0.00038618 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2021-12-29 18:48 | 2021-12-30 10:56 | 8 | 016:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO BAJANTE DE SECUNDARIA | C21122900084 | New_Event | Secondary Wire Down | Include | Include | Equipment | 968 | 2021-12-29 | 7744 | keep | 0 | Dec | 2021 | 0.0052744 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2021-12-29 19:08 | 2021-12-29 20:34 | 5 | 001:26 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR INFORMA ARIS CORTES QUE NO ENCONTRO CAUSA | M21122900143 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 86 | 2021-12-29 | 430 | keep | 0 | Dec | 2021 | 0.00029287 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-12-29 19:42 | 2021-12-30 11:11 | 7 | 015:29 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHE | C21122900092 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 929 | 2021-12-29 | 6503 | keep | 0 | Dec | 2021 | 0.0044292 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2021-12-29 19:51 | 2021-12-29 19:58 | 3316 | 000:07 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA | A21122900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2021-12-29 | 23212 | keep | 0 | Dec | 2021 | 0.01581 | 0.0022585 | Sustained | FALSE | FALSE | Not_TMED_Event | 3316
AGUADILLA | 2021-12-29 20:02 | 2021-12-29 21:23 | 1943 | 001:21 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA PODER REPARAR PUENTE PRIMARIO ABIERTO EN TRONCAL DEL INTERRUPTOR | M21122900000 | Additional_clients | Wire Down | Include | Include | Equipment | 81 | 2021-12-29 | 157383 | keep | 0 | Dec | 2021 | 0.10719 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-29 20:12 | 2021-12-29 20:13 | 4080 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1806-02 LLEVA TRANSFERIDA PARTE DE LA CARGA DEL 1717-01 | B21122900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-29 | 4080 | keep | 0 | Dec | 2021 | 0.0027789 | 0.0027789 | Momentary | FALSE | FALSE | Not_TMED_Event | 4080
BAYAMON | 2021-12-29 20:12 | 2021-12-29 20:13 | 4622 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA TRANSFERIDA PARTE DE LA CARGA DEL 1717-01 | B21122900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-29 | 4622 | keep | 0 | Dec | 2021 | 0.003148 | 0.003148 | Momentary | FALSE | FALSE | Not_TMED_Event | 4622
BAYAMON | 2021-12-29 20:15 | 2021-12-29 20:16 | 4080 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1806-02 LLEVA TRANSFERIDA PARTE DE LA CARGA DEL 1717-01 | B21122900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-29 | 4080 | keep | 0 | Dec | 2021 | 0.0027789 | 0.0027789 | Momentary | FALSE | FALSE | Not_TMED_Event | 4080
BAYAMON | 2021-12-29 20:15 | 2021-12-29 20:16 | 4622 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA TRANSFERIDA PARTE DE LA CARGA DEL 1717-01 | B21122900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-29 | 4622 | keep | 0 | Dec | 2021 | 0.003148 | 0.003148 | Momentary | FALSE | FALSE | Not_TMED_Event | 4622
BAYAMON | 2021-12-29 20:17 | 2021-12-29 20:18 | 4080 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1806-02 LLEVA TRANSFERIDA PARTE DE LA CARGA DEL 1717-01 | B21122900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-29 | 4080 | keep | 0 | Dec | 2021 | 0.0027789 | 0.0027789 | Momentary | FALSE | FALSE | Not_TMED_Event | 4080
BAYAMON | 2021-12-29 20:17 | 2021-12-29 20:18 | 4622 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA TRANSFERIDA PARTE DE LA CARGA DEL 1717-01 | B21122900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-29 | 4622 | keep | 0 | Dec | 2021 | 0.003148 | 0.003148 | Momentary | FALSE | FALSE | Not_TMED_Event | 4622
BAYAMON | 2021-12-29 20:18 | 2021-12-30 01:21 | 600 | 005:03 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE DEL 1806-2 AVE. BOULEVARD ESQ. 167 Y SE CERRO SU CARGA POR 1806-2 | B21122900086 | New_Event | Switch Failure | Include | Include | Equipment | 303 | 2021-12-29 | 181800 | keep | 0 | Dec | 2021 | 0.12382 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
BAYAMON | 2021-12-29 20:18 | 2021-12-30 01:21 | 1500 | 005:03 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE AVE. BOULEVARD ESQ. 167 Y SE CERRO 100% EN SERVICIO | B21122900086 | New_Event | Switch Failure | Include | Include | Equipment | 303 | 2021-12-29 | 454500 | keep | 0 | Dec | 2021 | 0.30956 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
VEGA BAJA | 2021-12-29 20:29 | 2021-12-29 21:05 | 10 | 000:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BARRAS SECUNDARIAS EN PEDESTAL | B21122900082 | New_Event | Secondary Wire Down | Include | Include | Equipment | 36 | 2021-12-29 | 360 | keep | 0 | Dec | 2021 | 0.00024519 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-29 21:10 | 2021-12-29 22:24 | 2 | 001:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO SECUNDARIA QUEMADA | R21122900102 | New_Event | Secondary Wire Down | Include | Include | Equipment | 74 | 2021-12-29 | 148 | keep | 0 | Dec | 2021 | 0.0001008 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2021-12-29 22:15 | 2021-12-29 22:43 | 12 | 000:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | B21122900071 | New_Event | Secondary Wire Down | Include | Include | Equipment | 28 | 2021-12-29 | 336 | keep | 0 | Dec | 2021 | 0.00022885 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-12-29 22:32 | 2021-12-30 10:40 | 5 | 012:08 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B21122900187 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 728 | 2021-12-29 | 3640 | keep | 0 | Dec | 2021 | 0.0024792 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-12-29 23:05 | 2021-12-30 14:34 | 10 | 015:29 | P | ESTRUCTURA AVERIADA | 1 X 25 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO | A21122900152 | New_Event | Defective Pole | Include | Include | Equipment | 929 | 2021-12-29 | 9290 | keep | 0 | Dec | 2021 | 0.0063274 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-12-29 23:49 | 2021-12-30 10:03 | 40 | 010:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A21122900153 | New_Event | Cutout Failure | Include | Include | Equipment | 614 | 2021-12-29 | 24560 | keep | 0 | Dec | 2021 | 0.016728 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2021-12-30 00:01 | 2021-12-30 11:19 | 1 | 011:18 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE REPORTA CAUSA | P21123000001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 678 | 2021-12-30 | 678 | keep | 0 | Dec | 2021 | 0.00046178 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-12-30 00:19 | 2021-12-30 04:00 | 70 | 003:41 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL SOBRE LINEAS PRIMARIAS | M21122900185 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2021-12-30 | 15470 | keep | 0 | Dec | 2021 | 0.010537 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2021-12-30 01:27 | 2021-12-30 01:28 | 600 | 000:01 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE AVE. BOULEVARD ESQ. 167 PARTE POR 1806-2 | B21122900086 | Partial_restoration | Switch Failure | Include | Include | Equipment | 1 | 2021-12-30 | 600 | keep | 0 | Dec | 2021 | 0.00040866 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-30 02:06 | 2021-12-30 02:08 | 1983 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO CARGA TRANSFERIDA AL 1801-02 | B21123000006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-30 | 3966 | keep | 0 | Dec | 2021 | 0.0027012 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-12-30 02:06 | 2021-12-30 02:08 | 800 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO PARTE DE SU CARGA POR 1801-2 | B21123000006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-30 | 1600 | keep | 0 | Dec | 2021 | 0.0010898 | 0.00054488 | Momentary | FALSE | FALSE | Not_TMED_Event | 800
BAYAMON | 2021-12-30 02:06 | 2021-12-30 02:08 | 186 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1711-4 Y PARTE DEL 1717-1 | B21123000006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-30 | 372 | keep | 0 | Dec | 2021 | 0.00025337 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
UTUADO | 2021-12-30 05:17 | 2021-12-30 11:50 | 25 | 006:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A21123000001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 393 | 2021-12-30 | 9825 | keep | 0 | Dec | 2021 | 0.0066918 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2021-12-30 05:36 | 2021-12-30 10:00 | 250 | 004:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ROTO SE ABRIO MACHETES PARA REPARARLO | A21123000002 | New_Event | Wire Down | Include | Include | Equipment | 264 | 2021-12-30 | 66000 | keep | 0 | Dec | 2021 | 0.044952 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
ARECIBO | 2021-12-30 06:13 | 2021-12-30 11:02 | 60 | 004:49 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A21123000005 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 289 | 2021-12-30 | 17340 | keep | 0 | Dec | 2021 | 0.01181 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2021-12-30 06:49 | 2021-12-30 13:38 | 30 | 006:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUNTE NO FUNDIO | R21123000003 | New_Event | Wire Down | Include | Include | Equipment | 409 | 2021-12-30 | 12270 | keep | 0 | Dec | 2021 | 0.008357 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-12-30 08:06 | 2021-12-30 14:19 | 10 | 006:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR PEDESTAL | C21123000003 | New_Event | Secondary Wire Down | Include | Include | Equipment | 373 | 2021-12-30 | 3730 | keep | 0 | Dec | 2021 | 0.0025405 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-30 08:16 | 2021-12-30 09:38 | 1617 | 001:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21123000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 82 | 2021-12-30 | 132594 | keep | 0 | Dec | 2021 | 0.090309 | 0.0011013 | Sustained | FALSE | FALSE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-12-30 08:16 | 2021-12-30 09:38 | 1017 | 001:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21123000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 82 | 2021-12-30 | 83394 | keep | 0 | Dec | 2021 | 0.056799 | 0.00069267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-12-30 08:16 | 2021-12-30 09:38 | 828 | 001:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21123000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 82 | 2021-12-30 | 67896 | keep | 0 | Dec | 2021 | 0.046244 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
MAYAGÃœEZ | 2021-12-30 08:16 | 2021-12-30 11:52 | 863 | 003:36 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21123000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 216 | 2021-12-30 | 186408 | keep | 0 | Dec | 2021 | 0.12696 | 0.00058779 | Sustained | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2021-12-30 08:16 | 2021-12-30 11:52 | 309 | 003:36 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21123000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 216 | 2021-12-30 | 66744 | keep | 0 | Dec | 2021 | 0.045459 | 0.00021046 | Sustained | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2021-12-30 08:16 | 2021-12-30 11:52 | 176 | 003:36 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21123000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 216 | 2021-12-30 | 38016 | keep | 0 | Dec | 2021 | 0.025893 | 0.00011987 | Sustained | FALSE | FALSE | Not_TMED_Event | 176
HUMACAO | 2021-12-30 08:18 | 2021-12-30 14:04 | 15 | 005:46 | P | NO SE REPORTO CAUSA | 1 X 25 Y 1 X 30 EN SU-02B8B NO CAUSA | C21123000002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 346 | 2021-12-30 | 5190 | keep | 0 | Dec | 2021 | 0.0035349 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-12-30 08:33 | 2021-12-30 10:58 | 40 | 002:25 | P | DESGANCHE | 1 X 80 EN RISER CARGA POR EL 1909-08 | S21123000002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 145 | 2021-12-30 | 5800 | keep | 0 | Dec | 2021 | 0.0039504 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2021-12-30 08:35 | 2021-12-30 08:36 | 1830 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | R21123000006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-30 | 1830 | keep | 0 | Dec | 2021 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
BAYAMON | 2021-12-30 08:45 | 2021-12-30 11:19 | 8 | 002:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE DE PALOMA | B21123000010 | New_Event |  |  | Include | Wildlife | 154 | 2021-12-30 | 1232 | keep | 0 | Dec | 2021 | 0.00083911 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-12-30 08:48 | 2021-12-30 10:00 | 40 | 001:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A21123000017 | New_Event | Cutout Failure | Include | Include | Equipment | 72 | 2021-12-30 | 2880 | keep | 0 | Dec | 2021 | 0.0019616 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-30 08:59 | 2021-12-30 10:32 | 35 | 001:33 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B21123000011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2021-12-30 | 3255 | keep | 0 | Dec | 2021 | 0.002217 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2021-12-30 09:10 | 2021-12-30 15:21 | 18 | 006:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR CONECTORES | M21123000037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 371 | 2021-12-30 | 6678 | keep | 0 | Dec | 2021 | 0.0045484 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CAGUAS | 2021-12-30 09:20 | 2021-12-30 09:27 | 2906 | 000:07 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR PERSONAL PRIVADO DESGANCHANDO | C21123000000 | New_Event |  |  | Include | Wildlife | 7 | 2021-12-30 | 20342 | keep | 0 | Dec | 2021 | 0.013855 | 0.0019793 | Sustained | FALSE | FALSE | Not_TMED_Event | 2906
SAN JUAN | 2021-12-30 09:25 | 2021-12-30 09:54 | 15 | 000:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA CONECTAR CLIENTE A PETICION DE PERSONAL LOW VOLTAGE | R21123000009 | New_Event | Secondary Wire Down | Include | Include | Equipment | 29 | 2021-12-30 | 435 | keep | 0 | Dec | 2021 | 0.00029628 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-12-30 09:26 | 2021-12-30 09:50 | 10 | 000:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21123000009 | New_Event | Secondary Wire Down | Include | Include | Equipment | 24 | 2021-12-30 | 240 | keep | 0 | Dec | 2021 | 0.00016346 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-30 09:27 | 2021-12-30 11:33 | 200 | 002:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 Y 1 X 100 EN CORTES DE LINEA PERSONAL PRIVADO DESGANCHANDO | C21123000014 | Partial_restoration |  |  | Include | Wildlife | 126 | 2021-12-30 | 25200 | keep | 0 | Dec | 2021 | 0.017164 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-12-30 09:30 | 2021-12-30 13:16 | 25 | 003:46 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR POSTE PARTIDO | P21123000013 | New_Event | Defective Pole | Include | Include | Equipment | 226 | 2021-12-30 | 5650 | keep | 0 | Dec | 2021 | 0.0038482 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2021-12-30 10:00 | 2021-12-30 10:54 | 500 | 000:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ROTO SE CERRO MACHETES | A21123000002 | New_Event | Wire Down | Include | Include | Equipment | 54 | 2021-12-30 | 27000 | keep | 0 | Dec | 2021 | 0.01839 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2021-12-30 10:07 | 2021-12-30 10:08 | 418 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | S21123000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-30 | 418 | keep | 0 | Dec | 2021 | 0.0002847 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
VEGA BAJA | 2021-12-30 10:13 | 2021-12-30 20:29 | 15 | 010:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | B21123000018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 616 | 2021-12-30 | 9240 | keep | 0 | Dec | 2021 | 0.0062933 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-12-30 10:15 | 2021-12-30 10:18 | 3902 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE VERIFICO PERSONAL FUERA | C21123000042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-12-30 | 11706 | keep | 0 | Dec | 2021 | 0.0079729 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
CAGUAS | 2021-12-30 10:29 | 2021-12-30 10:30 | 1342 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21123000043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-30 | 1342 | keep | 0 | Dec | 2021 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
MAYAGÃœEZ | 2021-12-30 10:39 | 2021-12-30 13:35 | 12 | 002:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | M21123000062 | New_Event | Secondary Wire Down | Include | Include | Equipment | 176 | 2021-12-30 | 2112 | keep | 0 | Dec | 2021 | 0.0014385 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-12-30 10:41 | 2021-12-30 11:37 | 8 | 000:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A21123000022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 56 | 2021-12-30 | 448 | keep | 0 | Dec | 2021 | 0.00030513 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-12-30 10:42 | 2021-12-30 13:10 | 25 | 002:28 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21123000022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 148 | 2021-12-30 | 3700 | keep | 0 | Dec | 2021 | 0.0025201 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-12-30 10:43 | 2021-12-30 16:20 | 60 | 005:37 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21123000065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 337 | 2021-12-30 | 20220 | keep | 0 | Dec | 2021 | 0.013772 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-12-30 10:51 | 2021-12-30 10:54 | 858 | 000:03 | P | DESGANCHE | DISPARO DE INTERRUPTOR 1303-02 LLEVA 20% DEL 1204_02 | S21123000009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-12-30 | 2574 | keep | 0 | Dec | 2021 | 0.0017531 | 0.00058438 | Momentary | FALSE | FALSE | Not_TMED_Event | 858
SAN JUAN | 2021-12-30 10:51 | 2021-12-30 10:54 | 2435 | 000:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA 20% DEL 1204-02 | S21123000009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-12-30 | 7305 | keep | 0 | Dec | 2021 | 0.0049754 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2021-12-30 10:56 | 2021-12-30 11:34 | 858 | 000:38 | P | DESGANCHE | DISPARO DE INTERRUPTOR 1303-02 LLEVA 20% DEL 1204_02 | S21123000009 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 38 | 2021-12-30 | 32604 | keep | 0 | Dec | 2021 | 0.022206 | 0.00058438 | Sustained | FALSE | FALSE | Not_TMED_Event | 858
SAN JUAN | 2021-12-30 10:56 | 2021-12-30 11:34 | 2435 | 000:38 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA 20% DEL 1204-02 SE ABRIO MACHETE N/0 CONTRA EL 1204-02 Y SE CERRO INTERRUPTOR | S21123000009 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 38 | 2021-12-30 | 92530 | keep | 0 | Dec | 2021 | 0.063022 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
AGUADILLA | 2021-12-30 11:06 | 2021-12-30 11:07 | 558 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA ALGUNA | M21123000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-30 | 558 | keep | 0 | Dec | 2021 | 0.00038005 | 0.00038005 | Momentary | FALSE | FALSE | Not_TMED_Event | 558
BARRANQUITAS | 2021-12-30 11:16 | 2021-12-30 16:23 | 25 | 005:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | C21123000054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 307 | 2021-12-30 | 7675 | keep | 0 | Dec | 2021 | 0.0052274 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2021-12-30 11:21 | 2021-12-30 14:24 | 80 | 003:03 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | P21123000029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2021-12-30 | 14640 | keep | 0 | Dec | 2021 | 0.0099712 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2021-12-30 11:24 | 2021-12-30 12:02 | 12 | 000:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BARRAS DE PEDESTAL | R21123000013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 38 | 2021-12-30 | 456 | keep | 0 | Dec | 2021 | 0.00031058 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-12-30 11:34 | 2021-12-30 12:46 | 50 | 001:12 | P | DESGANCHE | 1 X 100 EN C/L Y SE REALIZO DESGANCHE 20% POR EL 1303-02 EN SERVICIO | S21123000064 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 72 | 2021-12-30 | 3600 | keep | 0 | Dec | 2021 | 0.0024519 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-12-30 11:41 | 2021-12-30 12:22 | 80 | 000:41 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21123000015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 41 | 2021-12-30 | 3280 | keep | 0 | Dec | 2021 | 0.002234 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-12-30 11:45 | 2021-12-30 13:30 | 3 | 001:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | M21123000002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 105 | 2021-12-30 | 315 | keep | 0 | Dec | 2021 | 0.00021455 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-12-30 11:52 | 2021-12-30 15:00 | 5 | 003:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | M21123000063 | New_Event | Secondary Wire Down | Include | Include | Equipment | 188 | 2021-12-30 | 940 | keep | 0 | Dec | 2021 | 0.00064023 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2021-12-30 12:12 | 2021-12-30 12:54 | 17 | 000:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA QUEMADA EN TRANSFORMADOR | P21123000037 | New_Event | Cutout Failure | Include | Include | Equipment | 42 | 2021-12-30 | 714 | keep | 0 | Dec | 2021 | 0.0004863 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
HUMACAO | 2021-12-30 12:13 | 2021-12-30 12:14 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21123000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-30 | 1827 | keep | 0 | Dec | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
BAYAMON | 2021-12-30 12:14 | 2021-12-30 14:13 | 95 | 001:59 | P | DESGANCHE | 1 X 50, 1 X 65 Y 1 X 80 DESGANCHE | S21123000054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2021-12-30 | 11305 | keep | 0 | Dec | 2021 | 0.0076998 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
ARECIBO | 2021-12-30 12:24 | 2021-12-30 12:25 | 1105 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21123000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-30 | 1105 | keep | 0 | Dec | 2021 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
CAGUAS | 2021-12-30 12:25 | 2021-12-30 14:18 | 20 | 001:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 40 EN CORTE DE LINEA CRUCE X AVE | C21123000063 | New_Event |  |  | Include | Wildlife | 113 | 2021-12-30 | 2260 | keep | 0 | Dec | 2021 | 0.0015393 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-12-30 12:35 | 2021-12-31 10:24 | 300 | 021:49 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA Y SE RETEZO LINEAS | C21123000065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1309 | 2021-12-30 | 392700 | keep | 0 | Dec | 2021 | 0.26747 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
ARECIBO | 2021-12-30 12:42 | 2021-12-30 13:11 | 6 | 000:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A21123000059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 29 | 2021-12-30 | 174 | keep | 0 | Dec | 2021 | 0.00011851 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2021-12-30 12:47 | 2021-12-30 17:31 | 100 | 004:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE REPARO PUENTES PRIMARIOS | A21123000062 | New_Event | Wire Down | Include | Include | Equipment | 284 | 2021-12-30 | 28400 | keep | 0 | Dec | 2021 | 0.019343 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2021-12-30 12:52 | 2021-12-30 14:54 | 15 | 002:02 | P | NO SE REPORTO CAUSA | 1 X 30 EN TRANSFORMADOR NO CAUSA | P21123000042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2021-12-30 | 1830 | keep | 0 | Dec | 2021 | 0.0012464 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-12-30 12:53 | 2021-12-30 15:19 | 2 | 002:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21123000027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 146 | 2021-12-30 | 292 | keep | 0 | Dec | 2021 | 0.00019888 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2021-12-30 12:56 | 2021-12-30 12:57 | 2999 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M21123000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-30 | 2999 | keep | 0 | Dec | 2021 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
GUAYAMA | 2021-12-30 13:11 | 2021-12-30 14:57 | 200 | 001:46 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA DESGANCHE | P21123000043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2021-12-30 | 21200 | keep | 0 | Dec | 2021 | 0.014439 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2021-12-30 13:18 | 2021-12-30 13:45 | 1 | 000:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN TRANSFORMADOR SE REPARO BAJANTE PRIMARIO | P21123000044 | New_Event | Wire Down | Include | Include | Equipment | 27 | 2021-12-30 | 27 | keep | 0 | Dec | 2021 | 1.839e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-12-30 13:19 | 2021-12-30 13:34 | 11 | 000:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | ABRIO XMR PARA DESPEGAR TENSOR DE BAJANTE PRIMARIO | C21123000071 | New_Event |  |  | Include | Wildlife | 15 | 2021-12-30 | 165 | keep | 0 | Dec | 2021 | 0.00011238 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2021-12-30 13:27 | 2021-12-30 16:11 | 25 | 002:44 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B21123000029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 164 | 2021-12-30 | 4100 | keep | 0 | Dec | 2021 | 0.0027925 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2021-12-30 13:35 | 2021-12-30 18:28 | 50 | 004:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE X REPTIL FIJO BAJANTE DE CAJA A LINEA | C21123000070 | New_Event |  |  | Include | Wildlife | 293 | 2021-12-30 | 14650 | keep | 0 | Dec | 2021 | 0.009978 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-12-30 13:48 | 2021-12-30 13:50 | 2694 | 000:02 | S | NO SE REPORTO CAUSA | DISPARO DEL 0050 EN LA SUBESTACION | A21123000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-30 | 5388 | keep | 0 | Dec | 2021 | 0.0036697 | 0.0018349 | Momentary | FALSE | FALSE | Not_TMED_Event | 2694
ARECIBO | 2021-12-30 13:48 | 2021-12-30 13:50 | 2228 | 000:02 | S | NO SE REPORTO CAUSA | DISPARO DEL 0050 EN LA SUBESTACION | A21123000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-30 | 4456 | keep | 0 | Dec | 2021 | 0.003035 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2021-12-30 13:48 | 2021-12-30 13:50 | 438 | 000:02 | S | NO SE REPORTO CAUSA | DISPARO DEL 0050 EN LA SUBESTACION | A21123000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-30 | 876 | keep | 0 | Dec | 2021 | 0.00059664 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
MAYAGÃœEZ | 2021-12-30 13:59 | 2021-12-30 15:20 | 2 | 001:21 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR REQUIERE DESGANCHE | M21123000089 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 81 | 2021-12-30 | 162 | keep | 0 | Dec | 2021 | 0.00011034 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2021-12-30 14:00 | 2021-12-30 16:20 | 2635 | 002:20 | T | BREAKER DEFECTUOSO O NO OPERA | DISPARO SE TRANSFIRIO LA CARGA AL 9902-03 BKR NO CERRO POR CONTROL NI ELECTRICAMENTE | C21123000074 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 140 | 2021-12-30 | 368900 | keep | 0 | Dec | 2021 | 0.25126 | 0.0017947 | Sustained | FALSE | FALSE | Not_TMED_Event | 2635
AGUADILLA | 2021-12-30 14:21 | 2021-12-30 19:15 | 150 | 004:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | M21123000090 | New_Event | Wire Down | Include | Include | Equipment | 294 | 2021-12-30 | 44100 | keep | 0 | Dec | 2021 | 0.030036 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2021-12-30 14:34 | 2021-12-30 16:17 | 30 | 001:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE X AVE | C21123000088 | New_Event |  |  | Include | Wildlife | 103 | 2021-12-30 | 3090 | keep | 0 | Dec | 2021 | 0.0021046 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2021-12-30 14:47 | 2021-12-30 16:05 | 10 | 001:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR NEUTRAL SECUNDARIO | M21122800054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 78 | 2021-12-30 | 780 | keep | 0 | Dec | 2021 | 0.00053125 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-30 14:51 | 2021-12-30 18:18 | 1597 | 003:27 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REPARO LINEA ZAFADA DE AISLADOR | M21123000094 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 207 | 2021-12-30 | 330579 | keep | 0 | Dec | 2021 | 0.22516 | 0.0010877 | Sustained | FALSE | FALSE | Not_TMED_Event | 1597
BAYAMON | 2021-12-30 14:52 | 2021-12-30 16:51 | 50 | 001:59 | P | ESTRUCTURA AVERIADA | 2 X 65 EN C/L SE RETIRO POSTE VACANTE PARTIDO | B21123000059 | New_Event | Defective Pole | Include | Include | Equipment | 119 | 2021-12-30 | 5950 | keep | 0 | Dec | 2021 | 0.0040525 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-12-30 15:01 | 2021-12-30 15:40 | 40 | 000:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A21123000074 | New_Event | Wire Down | Include | Include | Equipment | 39 | 2021-12-30 | 1560 | keep | 0 | Dec | 2021 | 0.0010625 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-12-30 15:25 | 2021-12-30 16:49 | 30 | 001:24 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO CAUSA | S21123000108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2021-12-30 | 2520 | keep | 0 | Dec | 2021 | 0.0017164 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2021-12-30 15:28 | 2021-12-30 16:45 | 99 | 001:17 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | R21123000113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2021-12-30 | 7623 | keep | 0 | Dec | 2021 | 0.005192 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
HUMACAO | 2021-12-30 15:35 | 2021-12-30 16:45 | 15 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO Y LINEA SECUNDARIA | C21123000103 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2021-12-30 | 1050 | keep | 0 | Dec | 2021 | 0.00071515 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-12-30 15:50 | 2021-12-31 03:07 | 4 | 011:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES ZULFATADOS | R21123000116 | New_Event | Secondary Wire Down | Include | Include | Equipment | 677 | 2021-12-30 | 2708 | keep | 0 | Dec | 2021 | 0.0018444 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-12-30 15:52 | 2021-12-30 19:19 | 6 | 003:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S21123000113 | New_Event | Secondary Wire Down | Include | Include | Equipment | 207 | 2021-12-30 | 1242 | keep | 0 | Dec | 2021 | 0.00084592 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-12-30 16:00 | 2021-12-30 16:01 | 767 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE LLEVA 50% DE SU CARGA Y CARGA DEL 1709-05 | B21123000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-30 | 767 | keep | 0 | Dec | 2021 | 0.0005224 | 0.0005224 | Momentary | FALSE | FALSE | Not_TMED_Event | 767
BAYAMON | 2021-12-30 16:00 | 2021-12-30 16:01 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 1709-05 LLEVA 50% DE SU CARGA Y CARGA DEL 1709-05 | B21123000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-30 | 2364 | keep | 0 | Dec | 2021 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
BAYAMON | 2021-12-30 16:01 | 2021-12-30 18:06 | 50 | 002:05 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S21123000116 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 125 | 2021-12-30 | 6250 | keep | 0 | Dec | 2021 | 0.0042568 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2021-12-30 16:05 | 2021-12-30 19:26 | 40 | 003:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L REMPLAZO CAJA AVERIADA | C21123000108 | New_Event | Cutout Failure | Include | Include | Equipment | 201 | 2021-12-30 | 8040 | keep | 0 | Dec | 2021 | 0.005476 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2021-12-30 16:14 | 2021-12-30 18:28 | 40 | 002:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA AVERIADA NO FUNDIO | C21123000116 | New_Event | Cutout Failure | Include | Include | Equipment | 134 | 2021-12-30 | 5360 | keep | 0 | Dec | 2021 | 0.0036507 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-12-30 16:24 | 2021-12-30 18:41 | 6 | 002:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR BAJANTE SECUNDARIO | C21123000121 | New_Event | Secondary Wire Down | Include | Include | Equipment | 137 | 2021-12-30 | 822 | keep | 0 | Dec | 2021 | 0.00055986 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2021-12-30 16:32 | 2021-12-30 17:00 | 6 | 000:28 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B21122900054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 28 | 2021-12-30 | 168 | keep | 0 | Dec | 2021 | 0.00011442 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-12-30 16:33 | 2021-12-30 17:49 | 60 | 001:16 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B21123000064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 76 | 2021-12-30 | 4560 | keep | 0 | Dec | 2021 | 0.0031058 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2021-12-30 16:41 | 2021-12-31 13:22 | 4 | 020:41 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | C21123000126 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1241 | 2021-12-30 | 4964 | keep | 0 | Dec | 2021 | 0.003381 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-12-30 17:01 | 2021-12-31 10:50 | 1 | 017:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR FUERTE VIENTO | M21123000124 | New_Event | Bad Weather | Include | Include | Weather | 1069 | 2021-12-30 | 1069 | keep | 0 | Dec | 2021 | 0.00072809 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-12-30 17:25 | 2021-12-30 19:23 | 30 | 001:58 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B21123000071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 118 | 2021-12-30 | 3540 | keep | 0 | Dec | 2021 | 0.0024111 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-12-30 17:30 | 2021-12-30 18:18 | 56 | 000:48 | P | DESGANCHE | 1 X 140 EN C/L SE REALIZO DESGANCHE | B21123000072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 48 | 2021-12-30 | 2688 | keep | 0 | Dec | 2021 | 0.0018308 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
GUAYAMA | 2021-12-30 18:36 | 2021-12-30 20:40 | 50 | 002:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | P21123000072 | New_Event |  |  | Include | Wildlife | 124 | 2021-12-30 | 6200 | keep | 0 | Dec | 2021 | 0.0042228 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-30 18:40 | 2021-12-30 21:35 | 36 | 002:55 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S21123000126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 175 | 2021-12-30 | 6300 | keep | 0 | Dec | 2021 | 0.0042909 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
VEGA BAJA | 2021-12-30 18:40 | 2021-12-30 20:20 | 6 | 001:40 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B21123000126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 100 | 2021-12-30 | 600 | keep | 0 | Dec | 2021 | 0.00040866 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-12-30 19:00 | 2021-12-30 20:00 | 15 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR CONECTORES SECUNDARIOS | M21123000138 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2021-12-30 | 900 | keep | 0 | Dec | 2021 | 0.00061299 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-12-30 19:32 | 2021-12-31 08:42 | 30 | 013:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | B21123000082 | New_Event | Wire Down | Include | Include | Equipment | 790 | 2021-12-30 | 23700 | keep | 0 | Dec | 2021 | 0.016142 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2021-12-30 19:54 | 2021-12-30 20:58 | 150 | 001:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA CERRAR PUENTE PRIMARIO NO ESTA RELACIONADO CON EL OTRO EVENTO | M21123000150 | Partial_restoration | Wire Down | Include | Include | Equipment | 64 | 2021-12-30 | 9600 | keep | 0 | Dec | 2021 | 0.0065385 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-12-30 20:42 | 2021-12-31 08:23 | 8 | 011:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P21123000083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 701 | 2021-12-30 | 5608 | keep | 0 | Dec | 2021 | 0.0038196 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2021-12-30 20:58 | 2021-12-31 11:59 | 20 | 015:01 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR LA MISMA CAPACIDAD | M21123000155 | New_Event | Service Transformer Failure | Include | Include | Equipment | 901 | 2021-12-30 | 18020 | keep | 0 | Dec | 2021 | 0.012273 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-12-30 20:58 | 2021-12-30 22:26 | 8 | 001:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO MONTURA DE TRANSFROMADOR Y SE REPARO BAJANTE SECUNDARIO | A21123000092 | New_Event | Secondary Wire Down | Include | Include | Equipment | 88 | 2021-12-30 | 704 | keep | 0 | Dec | 2021 | 0.00047949 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2021-12-30 21:34 | 2021-12-30 21:35 | 1902 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21123000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-30 | 1902 | keep | 0 | Dec | 2021 | 0.0012954 | 0.0012954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1902
BARRANQUITAS | 2021-12-30 21:46 | 2021-12-31 12:50 | 50 | 015:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN C/L RETEZO LINEA | C21123000149 | New_Event | Wire Down | Include | Include | Equipment | 904 | 2021-12-30 | 45200 | keep | 0 | Dec | 2021 | 0.030786 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-12-30 23:25 | 2021-12-30 23:26 | 449 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P211230000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-30 | 449 | keep | 0 | Dec | 2021 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
CAGUAS | 2021-12-31 03:28 | 2021-12-31 03:29 | 4369 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21123100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-31 | 4369 | keep | 0 | Dec | 2021 | 0.0029757 | 0.0029757 | Momentary | FALSE | FALSE | Not_TMED_Event | 4369
CAGUAS | 2021-12-31 03:29 | 2021-12-31 11:51 | 85 | 008:22 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER 1 SMU 20 DE 40 AMP EN SU - 20 NO CAUSA | C21123100002 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 502 | 2021-12-31 | 42670 | keep | 0 | Dec | 2021 | 0.029062 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
PONCE | 2021-12-31 06:16 | 2021-12-31 09:58 | 50 | 003:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN RISER POR RATON CRUZAR FASE | P21123100002 | New_Event |  |  | Include | Wildlife | 222 | 2021-12-31 | 11100 | keep | 0 | Dec | 2021 | 0.0075602 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-12-31 06:33 | 2021-12-31 10:43 | 40 | 004:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L REMPLAZO CAJA QUEMADA | C21123100009 | New_Event | Cutout Failure | Include | Include | Equipment | 250 | 2021-12-31 | 10000 | keep | 0 | Dec | 2021 | 0.006811 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-12-31 06:51 | 2021-12-31 11:12 | 12 | 004:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | A21123100001 | New_Event | Bad Weather | Include | Include | Weather | 261 | 2021-12-31 | 3132 | keep | 0 | Dec | 2021 | 0.0021332 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2021-12-31 07:09 | 2021-12-31 11:18 | 50 | 004:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21123100004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 249 | 2021-12-31 | 12450 | keep | 0 | Dec | 2021 | 0.0084796 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-12-31 07:10 | 2021-12-31 10:27 | 80 | 003:17 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | C21123100012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2021-12-31 | 15760 | keep | 0 | Dec | 2021 | 0.010734 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2021-12-31 07:24 | 2021-12-31 09:10 | 2 | 001:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | A21123100002 | New_Event | Bad Weather | Include | Include | Weather | 106 | 2021-12-31 | 212 | keep | 0 | Dec | 2021 | 0.00014439 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2021-12-31 07:29 | 2021-12-31 07:30 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21123100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-31 | 3941 | keep | 0 | Dec | 2021 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
HUMACAO | 2021-12-31 07:37 | 2021-12-31 12:00 | 50 | 004:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 C/L CRUCE X AVE | C21123100016 | New_Event |  |  | Include | Wildlife | 263 | 2021-12-31 | 13150 | keep | 0 | Dec | 2021 | 0.0089564 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-12-31 07:44 | 2021-12-31 11:32 | 50 | 003:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A21123100003 | New_Event | Bad Weather | Include | Include | Weather | 228 | 2021-12-31 | 11400 | keep | 0 | Dec | 2021 | 0.0077645 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-12-31 07:55 | 2021-12-31 14:12 | 80 | 006:17 | P | DESGANCHE | 1 X 50 Y 1 X 65 EN CORTES DE LINEA | C21123100021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 377 | 2021-12-31 | 30160 | keep | 0 | Dec | 2021 | 0.020542 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2021-12-31 08:17 | 2021-12-31 09:24 | 1 | 001:07 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTA CAUSA | P21123100009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 67 | 2021-12-31 | 67 | keep | 0 | Dec | 2021 | 4.5633e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-12-31 08:19 | 2021-12-31 10:54 | 10 | 002:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO CONECTOR EN BAJANTE SECUNDARIO EN EL 1204-03 CARGA TRANSFERIDA AL 1206-04 | S21123100001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 155 | 2021-12-31 | 1550 | keep | 0 | Dec | 2021 | 0.0010557 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-31 08:19 | 2021-12-31 10:54 | 10 | 002:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO CONECTOR EN BAJANTE SECUNDARIO EN EL 1204-03 CARGA TRANSFERIDA AL 1206-04 | S21123100001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 155 | 2021-12-31 | 1550 | keep | 0 | Dec | 2021 | 0.0010557 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-12-31 08:20 | 2021-12-31 09:17 | 40 | 000:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C21123100022 | New_Event |  |  | Include | Wildlife | 57 | 2021-12-31 | 2280 | keep | 0 | Dec | 2021 | 0.0015529 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-12-31 08:27 | 2021-12-31 09:46 | 20 | 001:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CRUCE POR AVE | B21123100004 | New_Event |  |  | Include | Wildlife | 79 | 2021-12-31 | 1580 | keep | 0 | Dec | 2021 | 0.0010761 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2021-12-31 08:27 | 2021-12-31 13:25 | 12 | 004:58 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO DOS TRANSFORMADORES AVERIADOS UNO DE 50KVA Y OTRO DE 75KVA POR LA MISMA CAPACIDAD | M21123100003 | New_Event | Service Transformer Failure | Include | Include | Equipment | 298 | 2021-12-31 | 3576 | keep | 0 | Dec | 2021 | 0.0024356 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-12-31 08:32 | 2021-12-31 09:31 | 2450 | 000:59 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO | C21123100029 | New_Event |  |  | Include | Wildlife | 59 | 2021-12-31 | 144550 | keep | 0 | Dec | 2021 | 0.098452 | 0.0016687 | Sustained | FALSE | FALSE | Not_TMED_Event | 2450
BAYAMON | 2021-12-31 08:58 | 2021-12-31 11:18 | 40 | 002:20 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | B21123100006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2021-12-31 | 5600 | keep | 0 | Dec | 2021 | 0.0038141 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-12-31 08:59 | 2021-12-31 09:19 | 300 | 000:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA CRUCE POR AVE | C21123100004 | New_Event |  |  | Include | Wildlife | 20 | 2021-12-31 | 6000 | keep | 0 | Dec | 2021 | 0.0040866 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-12-31 09:09 | 2021-12-31 17:40 | 60 | 008:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS | M21123100005 | New_Event | Wire Down | Include | Include | Equipment | 511 | 2021-12-31 | 30660 | keep | 0 | Dec | 2021 | 0.020882 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2021-12-31 09:14 | 2021-12-31 09:15 | 732 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21123100010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-31 | 732 | keep | 0 | Dec | 2021 | 0.00049856 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
BAYAMON | 2021-12-31 09:16 | 2021-12-31 11:09 | 1 | 001:53 | P | DESCONECTIVO DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE QUEMADO | B21123100010 | New_Event | Switch Failure | Include | Include | Equipment | 113 | 2021-12-31 | 113 | keep | 0 | Dec | 2021 | 7.6964e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-12-31 09:23 | 2021-12-31 09:57 | 12 | 000:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO AMR PARA REPARAR SECUNDARIA | R21123100003 | New_Event | Secondary Wire Down | Include | Include | Equipment | 34 | 2021-12-31 | 408 | keep | 0 | Dec | 2021 | 0.00027789 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-12-31 09:31 | 2021-12-31 10:53 | 80 | 001:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L CRUCE X AVE | C21123100059 | Partial_restoration |  |  | Include | Wildlife | 82 | 2021-12-31 | 6560 | keep | 0 | Dec | 2021 | 0.004468 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-12-31 09:37 | 2021-12-31 09:39 | 2126 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR SCADA | C21123100066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-12-31 | 4252 | keep | 0 | Dec | 2021 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
BAYAMON | 2021-12-31 09:39 | 2021-12-31 09:42 | 546 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO DE BREAKER 1529-15 SE CERRO POR CONTROL LLEVA 30% DEL 1346-02 | S21123100009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-12-31 | 1638 | keep | 0 | Dec | 2021 | 0.0011156 | 0.00037188 | Momentary | FALSE | FALSE | Not_TMED_Event | 546
BAYAMON | 2021-12-31 09:51 | 2021-12-31 09:52 | 1802 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE BREAKER SE CERRO POR CONTROL LLEVA 30% DEL 1346-02 | S21123100009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-31 | 1802 | keep | 0 | Dec | 2021 | 0.0012273 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
MAYAGÃœEZ | 2021-12-31 10:06 | 2021-12-31 11:58 | 4 | 001:52 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR LA MISMA CAPACIDAD | M21123100014 | New_Event | Service Transformer Failure | Include | Include | Equipment | 112 | 2021-12-31 | 448 | keep | 0 | Dec | 2021 | 0.00030513 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2021-12-31 10:12 | 2021-12-31 15:12 | 50 | 005:00 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21123100008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 300 | 2021-12-31 | 15000 | keep | 0 | Dec | 2021 | 0.010216 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-12-31 10:25 | 2021-12-31 11:37 | 75 | 001:12 | P | DESGANCHE | 1 X 65 Y 1 X 80 EN CORTE DE LINEA DESGANCHE | S21123100014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2021-12-31 | 5400 | keep | 0 | Dec | 2021 | 0.0036779 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2021-12-31 10:28 | 2021-12-31 14:09 | 10 | 003:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A21123100011 | New_Event | Bad Weather | Include | Include | Weather | 221 | 2021-12-31 | 2210 | keep | 0 | Dec | 2021 | 0.0015052 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-31 10:37 | 2021-12-31 15:14 | 35 | 004:37 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21123100016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 277 | 2021-12-31 | 9695 | keep | 0 | Dec | 2021 | 0.0066032 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2021-12-31 10:37 | 2021-12-31 16:15 | 15 | 005:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A21123100013 | New_Event | Bad Weather | Include | Include | Weather | 338 | 2021-12-31 | 5070 | keep | 0 | Dec | 2021 | 0.0034532 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2021-12-31 10:40 | 2021-12-31 11:08 | 15 | 000:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REEMPLAZAR BARRA EN PEDESTAL | R21123100005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 28 | 2021-12-31 | 420 | keep | 0 | Dec | 2021 | 0.00028606 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-12-31 10:59 | 2021-12-31 11:59 | 10 | 001:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CAJA DE TRANSFORMADOR PARA REMPLAZAR BAJANTES Y REGULAR VOLTAJE | P21123100015 | New_Event | Wire Down | Include | Include | Equipment | 60 | 2021-12-31 | 600 | keep | 0 | Dec | 2021 | 0.00040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-31 11:01 | 2021-12-31 12:24 | 8 | 001:23 | P | DESGANCHE | DESGANCHE DE BAMBUA SE REMPLAZO CAJA PRIMARIA NO FUNDIO | S21123100006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2021-12-31 | 664 | keep | 0 | Dec | 2021 | 0.00045225 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-12-31 12:00 | 2021-12-31 13:47 | 4 | 001:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA ROTA | M21123100006 | New_Event | Secondary Wire Down | Include | Include | Equipment | 107 | 2021-12-31 | 428 | keep | 0 | Dec | 2021 | 0.00029151 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
GUAYAMA | 2021-12-31 12:22 | 2021-12-31 15:00 | 20 | 002:38 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE HIZO DESGANCHE | P21123100017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2021-12-31 | 3160 | keep | 0 | Dec | 2021 | 0.0021523 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-12-31 12:28 | 2021-12-31 13:24 | 10 | 000:56 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C21123100078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 56 | 2021-12-31 | 560 | keep | 0 | Dec | 2021 | 0.00038141 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-12-31 12:36 | 2021-12-31 16:07 | 40 | 003:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | M21123100022 | New_Event | Wire Down | Include | Include | Equipment | 211 | 2021-12-31 | 8440 | keep | 0 | Dec | 2021 | 0.0057484 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2021-12-31 12:47 | 2021-12-31 12:48 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21123100022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-31 | 1827 | keep | 0 | Dec | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
CAGUAS | 2021-12-31 13:11 | 2021-12-31 14:30 | 125 | 001:19 | P | DESGANCHE | 2 X 50 Y 2 X 50 EN CORTE DE LINEA | C21123100083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2021-12-31 | 9875 | keep | 0 | Dec | 2021 | 0.0067258 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2021-12-31 13:13 | 2021-12-31 16:12 | 10 | 002:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE DIERON CONECTORES Y SE LE REPARO LA SECUNDARIA TRASPATIO | S21123100026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 179 | 2021-12-31 | 1790 | keep | 0 | Dec | 2021 | 0.0012192 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-12-31 13:20 | 2021-12-31 14:57 | 20 | 001:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | ABRIR XMR PARA ELIMINMAR POSTE SECUNDARIO PEGADO AL BUSHING SECUNDARIO | C21123100085 | New_Event |  |  | Include | Wildlife | 97 | 2021-12-31 | 1940 | keep | 0 | Dec | 2021 | 0.0013213 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-12-31 13:35 | 2021-12-31 14:29 | 35 | 000:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE POR AVE | B21123100022 | New_Event |  |  | Include | Wildlife | 54 | 2021-12-31 | 1890 | keep | 0 | Dec | 2021 | 0.0012873 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2021-12-31 14:15 | 2021-12-31 15:34 | 100 | 001:19 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO CAUSA | R21123100010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 79 | 2021-12-31 | 7900 | keep | 0 | Dec | 2021 | 0.0053807 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-12-31 14:17 | 2021-12-31 14:53 | 8 | 000:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO BARRA DE PEDESTAL SECUNDARIO | R21123100011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 36 | 2021-12-31 | 288 | keep | 0 | Dec | 2021 | 0.00019616 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2021-12-31 14:17 | 2021-12-31 16:30 | 174 | 002:13 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE HIZO DESGANCHE | P21123100019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2021-12-31 | 23142 | keep | 0 | Dec | 2021 | 0.015762 | 0.00011851 | Sustained | FALSE | FALSE | Not_TMED_Event | 174
BAYAMON | 2021-12-31 14:20 | 2021-12-31 14:51 | 8 | 000:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21123100016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 31 | 2021-12-31 | 248 | keep | 0 | Dec | 2021 | 0.00016891 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-12-31 14:29 | 2021-12-31 15:53 | 25 | 001:24 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21123100033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2021-12-31 | 2100 | keep | 0 | Dec | 2021 | 0.0014303 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-12-31 14:37 | 2021-12-31 14:42 | 36 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04 LLEVA 1620-01 COMPLETO Y 95% DEL 1336-10 | S21123100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-12-31 | 180 | keep | 0 | Dec | 2021 | 0.0001226 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-12-31 14:37 | 2021-12-31 14:42 | 172 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVA 1620-01 Y 95% DEL 1336-10 | S21123100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-12-31 | 860 | keep | 0 | Dec | 2021 | 0.00058574 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
CAGUAS | 2021-12-31 14:40 | 2021-12-31 15:46 | 11 | 001:06 | P | DESGANCHE | 1 X 65 EN C/L | C21123100080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2021-12-31 | 726 | keep | 0 | Dec | 2021 | 0.00049448 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BARRANQUITAS | 2021-12-31 14:45 | 2021-12-31 19:09 | 75 | 004:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 30 EN C/L CRUCE X GLOBOS | C21123100091 | New_Event |  |  | Include | Wildlife | 264 | 2021-12-31 | 19800 | keep | 0 | Dec | 2021 | 0.013486 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2021-12-31 14:46 | 2021-12-31 14:47 | 382 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-01 LLEVA 1620-01 COMPLETO Y 95% DEL 1336-10 | S21123100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-31 | 382 | keep | 0 | Dec | 2021 | 0.00026018 | 0.00026018 | Momentary | FALSE | FALSE | Not_TMED_Event | 382
SAN JUAN | 2021-12-31 14:47 | 2021-12-31 15:57 | 86 | 001:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | R21123100013 | New_Event |  |  | Include | Wildlife | 70 | 2021-12-31 | 6020 | keep | 0 | Dec | 2021 | 0.0041002 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
CAGUAS | 2021-12-31 14:50 | 2022-01-01 10:05 | 4 | 019:15 | P | NO SE REPORTO CAUSA | 1 X 8 EN XMR NO CAUSA | C22010100003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1155 | 2021-12-31 | 4620 | keep | 0 | Dec | 2021 | 0.0031467 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2021-12-31 14:50 | 2021-12-31 15:31 | 8 | 000:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR TRANSFORMADOR PARA REPARAR SECUNDARIA | B21123100000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 41 | 2021-12-31 | 328 | keep | 0 | Dec | 2021 | 0.0002234 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-12-31 14:54 | 2021-12-31 14:55 | 1859 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA EL 9207-9 | B21123100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-31 | 1859 | keep | 0 | Dec | 2021 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2021-12-31 14:54 | 2021-12-31 14:55 | 7 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 9207-8 | B21123100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-31 | 7 | keep | 0 | Dec | 2021 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-12-31 14:55 | 2021-12-31 15:25 | 40 | 000:30 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B21123100025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 30 | 2021-12-31 | 1200 | keep | 0 | Dec | 2021 | 0.00081731 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-12-31 14:56 | 2021-12-31 15:44 | 10 | 000:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C21123100093 | New_Event | Secondary Wire Down | Include | Include | Equipment | 48 | 2021-12-31 | 480 | keep | 0 | Dec | 2021 | 0.00032693 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-12-31 15:09 | 2021-12-31 15:10 | 4537 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE LLEVA 30% DE SU CARGA TRANSFERIDA AL 1619-02 | S21123100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-31 | 4537 | keep | 0 | Dec | 2021 | 0.0030901 | 0.0030901 | Momentary | FALSE | FALSE | Not_TMED_Event | 4537
SAN JUAN | 2021-12-31 15:15 | 2021-12-31 16:17 | 300 | 001:02 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA NO CAUSA | R21123100017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 62 | 2021-12-31 | 18600 | keep | 0 | Dec | 2021 | 0.012668 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
PONCE | 2021-12-31 15:21 | 2021-12-31 15:22 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21123100022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-31 | 969 | keep | 0 | Dec | 2021 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
VEGA BAJA | 2021-12-31 15:23 | 2021-12-31 18:02 | 20 | 002:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO DE LINEA A CAJA EN CORTE DE LINEA | B21123100032 | New_Event | Wire Down | Include | Include | Equipment | 159 | 2021-12-31 | 3180 | keep | 0 | Dec | 2021 | 0.0021659 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-12-31 15:30 | 2021-12-31 17:54 | 12 | 002:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21123100031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 144 | 2021-12-31 | 1728 | keep | 0 | Dec | 2021 | 0.0011769 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-12-31 16:06 | 2021-12-31 20:20 | 5 | 004:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR CONECTORES SECUNDARIOS | A21123100038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 254 | 2021-12-31 | 1270 | keep | 0 | Dec | 2021 | 0.00086499 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-12-31 16:18 | 2022-01-01 09:48 | 300 | 017:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A MACHETE | S21123100037 | New_Event | Wire Down | Include | Include | Equipment | 1050 | 2021-12-31 | 315000 | keep | 0 | Dec | 2021 | 0.21455 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2021-12-31 16:27 | 2022-01-01 13:51 | 60 | 021:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 1 X 65 1 X 20 EN CORTE DE LINEA DIFERENTES SE REMPLAZO CAJA PRIMARIA | S21123100038 | New_Event | Cutout Failure | Include | Include | Equipment | 1284 | 2021-12-31 | 77040 | keep | 0 | Dec | 2021 | 0.052472 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2021-12-31 16:32 | 2021-12-31 17:13 | 80 | 000:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE X AVE | C21123100100 | New_Event |  |  | Include | Wildlife | 41 | 2021-12-31 | 3280 | keep | 0 | Dec | 2021 | 0.002234 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-12-31 16:39 | 2021-12-31 16:40 | 767 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1709-03 CON 50% DE SU CARGA POR 1909-07 Y LLEVANDO 1709-05 | B21123100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-31 | 767 | keep | 0 | Dec | 2021 | 0.0005224 | 0.0005224 | Momentary | FALSE | FALSE | Not_TMED_Event | 767
BAYAMON | 2021-12-31 16:39 | 2021-12-31 16:40 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1709-03 CON 50% DE SU CARGA POR 1909-07 Y LLEVANDO 1709-05 | B21123100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-31 | 2364 | keep | 0 | Dec | 2021 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
YAUCO | 2021-12-31 16:52 | 2021-12-31 21:34 | 83 | 004:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REMPLAZO POSTE PARTIDO POR AUTO 2 X 40 EN CORTE DE LINEA | P21123100034 | New_Event |  |  | Include | Wildlife | 282 | 2021-12-31 | 23406 | keep | 0 | Dec | 2021 | 0.015942 | 5.6531e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 83
YAUCO | 2021-12-31 17:12 | 2022-01-01 08:15 | 92 | 015:03 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P21123100035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 903 | 2021-12-31 | 83076 | keep | 0 | Dec | 2021 | 0.056583 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
ARECIBO | 2021-12-31 17:30 | 2021-12-31 18:12 | 6 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR CONECTORES SECUNDARIOS | A21123100039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2021-12-31 | 252 | keep | 0 | Dec | 2021 | 0.00017164 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-12-31 17:40 | 2021-12-31 19:54 | 1 | 002:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | A21123100040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 134 | 2021-12-31 | 134 | keep | 0 | Dec | 2021 | 9.1267e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-12-31 18:24 | 2021-12-31 20:33 | 514 | 002:09 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO L-7500 | S21123100091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 129 | 2021-12-31 | 66306 | keep | 0 | Dec | 2021 | 0.045161 | 0.00035008 | Sustained | FALSE | FALSE | Not_TMED_Event | 514
BAYAMON | 2021-12-31 18:24 | 2021-12-31 20:33 | 681 | 002:09 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO L-7500 | S21123100091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 129 | 2021-12-31 | 87849 | keep | 0 | Dec | 2021 | 0.059834 | 0.00046383 | Sustained | FALSE | FALSE | Not_TMED_Event | 681
BAYAMON | 2021-12-31 18:24 | 2021-12-31 20:33 | 752 | 002:09 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO L-7500 | S21123100091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 129 | 2021-12-31 | 97008 | keep | 0 | Dec | 2021 | 0.066072 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
BAYAMON | 2021-12-31 18:24 | 2021-12-31 20:33 | 68 | 002:09 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO L-7500 | S21123100091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 129 | 2021-12-31 | 8772 | keep | 0 | Dec | 2021 | 0.0059746 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
ARECIBO | 2021-12-31 18:35 | 2021-12-31 19:29 | 100 | 000:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21123100042 | New_Event | Bad Weather | Include | Include | Weather | 54 | 2021-12-31 | 5400 | keep | 0 | Dec | 2021 | 0.0036779 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-12-31 18:42 | 2021-12-31 23:13 | 710 | 004:31 | P | NO SE REPORTO CAUSA | 1 X 200 EN CONVERTIDOR | B21123100060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 271 | 2021-12-31 | 192410 | keep | 0 | Dec | 2021 | 0.13105 | 0.00048358 | Sustained | FALSE | FALSE | Not_TMED_Event | 710
HUMACAO | 2021-12-31 19:09 | 2021-12-31 21:06 | 80 | 001:57 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO CAUSA | C21123100110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 117 | 2021-12-31 | 9360 | keep | 0 | Dec | 2021 | 0.0063751 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2021-12-31 19:48 | 2021-12-31 19:49 | 922 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1 VEZ SE PROBO QUEDO EN SERVICIO CARGA POR 1401-8 | S21123100091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-31 | 922 | keep | 0 | Dec | 2021 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-12-31 19:48 | 2021-12-31 19:49 | 135 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1 VEZ SE PROBO QUEDO EN SERVICIO LLEVA 1346-5 | S21123100091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-12-31 | 135 | keep | 0 | Dec | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
AGUADILLA | 2021-12-31 20:29 | 2022-01-01 09:53 | 8 | 013:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE ROTO | M21123100041 | New_Event | Cutout Failure | Include | Include | Equipment | 804 | 2021-12-31 | 6432 | keep | 0 | Dec | 2021 | 0.0043808 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-12-31 20:54 | 2021-12-31 22:43 | 514 | 001:49 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7500 PUENTE ABIERTO | S21123100091 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 109 | 2021-12-31 | 56026 | keep | 0 | Dec | 2021 | 0.038159 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-31 20:54 | 2021-12-31 22:43 | 681 | 001:49 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7500 PUENTE ABIERTO | S21123100091 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 109 | 2021-12-31 | 74229 | keep | 0 | Dec | 2021 | 0.050557 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-31 20:54 | 2021-12-31 22:43 | 752 | 001:49 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7500 PUENTE ABIERTO | S21123100091 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 109 | 2021-12-31 | 81968 | keep | 0 | Dec | 2021 | 0.055828 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-12-31 20:54 | 2021-12-31 22:43 | 68 | 001:49 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7500 PUENTE ABIERTO | S21123100091 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 109 | 2021-12-31 | 7412 | keep | 0 | Dec | 2021 | 0.0050483 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-12-31 22:55 | 2022-01-01 16:56 | 1 | 018:01 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS | A21123100053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1081 | 2021-12-31 | 1081 | keep | 0 | Dec | 2021 | 0.00073626 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-12-31 22:55 | 2022-01-01 11:30 | 8 | 012:35 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | A21123100053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 755 | 2021-12-31 | 6040 | keep | 0 | Dec | 2021 | 0.0041138 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-01-01 00:14 | 2022-01-01 17:25 | 66 | 017:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO DE CAJA PRIMARIA 1 X 65 EN CORTE DE LINEA | P22010100001 | New_Event | Cutout Failure | Include | Include | Equipment | 1031 | 2022-01-01 | 68046 | keep | 0 | Jan | 2022 | 0.046346 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
MAYAGÃœEZ | 2022-01-01 00:22 | 2022-01-01 17:17 | 100 | 016:55 | P | DESGANCHE | 1X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M22010100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1015 | 2022-01-01 | 101500 | keep | 0 | Jan | 2022 | 0.069131 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-01-01 00:29 | 2022-01-01 11:09 | 30 | 010:40 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 30 EN CORTE DE LINEA SE REMPLAZO PISTOLA EN TRANSFORMADOR | S22010100001 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 640 | 2022-01-01 | 19200 | keep | 0 | Jan | 2022 | 0.013077 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-01-01 00:50 | 2022-01-01 08:45 | 80 | 007:55 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B22010100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 475 | 2022-01-01 | 38000 | keep | 0 | Jan | 2022 | 0.025882 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2022-01-01 01:07 | 2022-01-01 10:18 | 196 | 009:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO DE CAJA PRIMARIA QUEMADA | P22010100004 | New_Event | Cutout Failure | Include | Include | Equipment | 551 | 2022-01-01 | 107996 | keep | 0 | Jan | 2022 | 0.073556 | 0.00013349 | Sustained | FALSE | FALSE | Not_TMED_Event | 196
ARECIBO | 2022-01-01 01:25 | 2022-01-01 10:35 | 40 | 009:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22010100001 | New_Event | Bad Weather | Include | Include | Weather | 550 | 2022-01-01 | 22000 | keep | 0 | Jan | 2022 | 0.014984 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-01-01 01:45 | 2022-01-01 10:25 | 100 | 008:40 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22010100006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 520 | 2022-01-01 | 52000 | keep | 0 | Jan | 2022 | 0.035417 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-01-01 01:53 | 2022-01-01 10:24 | 75 | 008:31 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22010100004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 511 | 2022-01-01 | 38325 | keep | 0 | Jan | 2022 | 0.026103 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2022-01-01 03:29 | 2022-01-01 12:41 | 10 | 009:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | REMPLAZO XMR IMPACTADO POR VEHICULO 50 KVA X 50 KVA | C22010100002 | New_Event |  |  | Include | Wildlife | 552 | 2022-01-01 | 5520 | keep | 0 | Jan | 2022 | 0.0037596 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-01 04:47 | 2022-01-01 04:48 | 1859 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22010100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-01 | 1859 | keep | 0 | Jan | 2022 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
AGUADILLA | 2022-01-01 05:29 | 2022-01-01 16:21 | 39 | 010:52 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE AVERIADO | M22010100012 | New_Event | Switch Failure | Include | Include | Equipment | 652 | 2022-01-01 | 25428 | keep | 0 | Jan | 2022 | 0.017319 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
CAGUAS | 2022-01-01 05:48 | 2022-01-01 05:50 | 1017 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C22010100003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-01 | 2034 | keep | 0 | Jan | 2022 | 0.0013853 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
SAN JUAN | 2022-01-01 06:55 | 2022-01-01 09:03 | 100 | 002:08 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 40 EN CORTES DE LINEA NO CAUSA | R22010100002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 128 | 2022-01-01 | 12800 | keep | 0 | Jan | 2022 | 0.008718 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-01-01 06:57 | 2022-01-01 10:22 | 50 | 003:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE X AVE | C22010100004 | New_Event |  |  | Include | Wildlife | 205 | 2022-01-01 | 10250 | keep | 0 | Jan | 2022 | 0.0069812 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2022-01-01 07:28 | 2022-01-01 07:29 | 2484 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22010100012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-01 | 2484 | keep | 0 | Jan | 2022 | 0.0016918 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
CAGUAS | 2022-01-01 07:50 | 2022-01-01 10:52 | 40 | 003:02 | P | DESGANCHE | 1 X 40 EN C/L | C22010100006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2022-01-01 | 7280 | keep | 0 | Jan | 2022 | 0.0049584 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2022-01-01 08:02 | 2022-01-01 08:03 | 661 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22010100013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-01 | 661 | keep | 0 | Jan | 2022 | 0.0004502 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
ARECIBO | 2022-01-01 08:05 | 2022-01-01 09:30 | 20 | 001:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA AVE CRUZO FASES | A22010100002 | New_Event |  |  | Include | Wildlife | 85 | 2022-01-01 | 1700 | keep | 0 | Jan | 2022 | 0.0011579 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-01-01 08:47 | 2022-01-01 12:40 | 10 | 003:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA AVE CRUZO FASES | A22010100004 | New_Event |  |  | Include | Wildlife | 233 | 2022-01-01 | 2330 | keep | 0 | Jan | 2022 | 0.001587 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-01-01 08:48 | 2022-01-01 12:54 | 12 | 004:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO Y SE RETIRO ARBOL SOBRE LINEA | A22010100005 | New_Event | Wire Down | Include | Include | Equipment | 246 | 2022-01-01 | 2952 | keep | 0 | Jan | 2022 | 0.0020106 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-01-01 08:52 | 2022-01-01 13:32 | 150 | 004:40 | P | PARARRAYOS DEFECTUOSO | 1 X 100 Y 1 X 80 EN C/L Y 1 X 40 EN SU SE REMPLAZARON PARARRYOS | S22010100012 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 280 | 2022-01-01 | 42000 | keep | 0 | Jan | 2022 | 0.028606 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2022-01-01 08:56 | 2022-01-01 10:56 | 10 | 002:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE DE LINEA A CAJA | C22010100009 | New_Event | Wire Down | Include | Include | Equipment | 120 | 2022-01-01 | 1200 | keep | 0 | Jan | 2022 | 0.00081731 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-01-01 08:57 | 2022-01-01 11:34 | 80 | 002:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE X AVE | C22010100010 | New_Event |  |  | Include | Wildlife | 157 | 2022-01-01 | 12560 | keep | 0 | Jan | 2022 | 0.0085546 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-01-01 09:07 | 2022-01-01 10:07 | 40 | 001:00 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO CAUSA | C22010100016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 60 | 2022-01-01 | 2400 | keep | 0 | Jan | 2022 | 0.0016346 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2022-01-01 09:29 | 2022-01-01 10:36 | 40 | 001:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CRUCE X AVE | R22010100009 | New_Event |  |  | Include | Wildlife | 67 | 2022-01-01 | 2680 | keep | 0 | Jan | 2022 | 0.0018253 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2022-01-01 09:40 | 2022-01-01 11:33 | 45 | 001:53 | P | CABLE SOTERRADO AVERIADO | 1 X 65 EN C/L | R22010100010 | New_Event | UG Cable Fault | Include | Include | Equipment | 113 | 2022-01-01 | 5085 | keep | 0 | Jan | 2022 | 0.0034634 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BARRANQUITAS | 2022-01-01 10:00 | 2022-01-01 10:01 | 2635 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22010100024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-01 | 2635 | keep | 0 | Jan | 2022 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2022-01-01 10:01 | 2022-01-01 14:53 | 60 | 004:52 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | C22010100027 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 292 | 2022-01-01 | 17520 | keep | 0 | Jan | 2022 | 0.011933 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-01-01 10:13 | 2022-01-01 13:35 | 20 | 003:22 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S22010100020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 202 | 2022-01-01 | 4040 | keep | 0 | Jan | 2022 | 0.0027516 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-01-01 10:21 | 2022-01-01 16:58 | 80 | 006:37 | P | DESGANCHE | 1 X 80 EN C/L | C22010100035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 397 | 2022-01-01 | 31760 | keep | 0 | Jan | 2022 | 0.021632 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-01-01 10:38 | 2022-01-01 14:03 | 50 | 003:25 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 50 Y 1 X 40 EN CORTES DE LINEAS REPARO PISTOLA EN PM | R22010100015 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 205 | 2022-01-01 | 10250 | keep | 0 | Jan | 2022 | 0.0069812 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-01-01 11:02 | 2022-01-01 14:00 | 45 | 002:58 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22010100008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2022-01-01 | 8010 | keep | 0 | Jan | 2022 | 0.0054556 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BARRANQUITAS | 2022-01-01 11:04 | 2022-01-01 15:35 | 85 | 004:31 | P | DESGANCHE | 2 X 50 EN C/L | C22010100041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 271 | 2022-01-01 | 23035 | keep | 0 | Jan | 2022 | 0.015689 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
MAYAGÃœEZ | 2022-01-01 11:06 | 2022-01-01 13:35 | 200 | 002:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M22010100044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2022-01-01 | 29800 | keep | 0 | Jan | 2022 | 0.020297 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2022-01-01 11:33 | 2022-01-01 17:09 | 30 | 005:36 | P | CABLE SOTERRADO AVERIADO | AVERIA SU-3 @ T-19. CONSTRUYO PROVISIONAL AEREO DE AEREO EXISTENTE @ T-19 | R22010100010 | New_Event | UG Cable Fault | Include | Include | Equipment | 336 | 2022-01-01 | 10080 | keep | 0 | Jan | 2022 | 0.0068654 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-01-01 11:38 | 2022-01-01 15:28 | 6 | 003:50 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 25 KVA X 37.5 KVA | C22010100053 | New_Event | Service Transformer Failure | Include | Include | Equipment | 230 | 2022-01-01 | 1380 | keep | 0 | Jan | 2022 | 0.00093991 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-01-01 11:50 | 2022-01-01 12:55 | 12 | 001:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA DE TRANSFORMADOR Y SE REPARO SECUNDARIA PARTIDA | A22010100007 | New_Event | Cutout Failure | Include | Include | Equipment | 65 | 2022-01-01 | 780 | keep | 0 | Jan | 2022 | 0.00053125 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-01-01 11:52 | 2022-01-01 14:52 | 3 | 003:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22010100010 | New_Event | Bad Weather | Include | Include | Weather | 180 | 2022-01-01 | 540 | keep | 0 | Jan | 2022 | 0.00036779 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2022-01-01 12:11 | 2022-01-01 15:00 | 356 | 002:49 | P | DESGANCHE | 2 X 200 EN CORTE DE LINEA | P22010100022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2022-01-01 | 60164 | keep | 0 | Jan | 2022 | 0.040977 | 0.00024247 | Sustained | FALSE | FALSE | Not_TMED_Event | 356
BAYAMON | 2022-01-01 12:27 | 2022-01-01 17:07 | 100 | 004:40 | P | PARARRAYOS DEFECTUOSO | 1 X 80, 1 X 65, 1 X 20 EN CORTES DE LINEA DIFERENTES SE REMPLAZO PARARAYO | B22010100015 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 280 | 2022-01-01 | 28000 | keep | 0 | Jan | 2022 | 0.019071 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-01-01 12:55 | 2022-01-02 00:21 | 20 | 011:26 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR UNO IGUAL | A22010100013 | New_Event | Service Transformer Failure | Include | Include | Equipment | 686 | 2022-01-01 | 13720 | keep | 0 | Jan | 2022 | 0.0093446 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-01-01 12:57 | 2022-01-01 18:16 | 75 | 005:19 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22010100020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 319 | 2022-01-01 | 23925 | keep | 0 | Jan | 2022 | 0.016295 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2022-01-01 13:03 | 2022-01-01 15:00 | 5 | 001:57 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 15 KVA POR LA MISMA CAPACIDAD | M22010100064 | New_Event | Service Transformer Failure | Include | Include | Equipment | 117 | 2022-01-01 | 585 | keep | 0 | Jan | 2022 | 0.00039844 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-01-01 13:06 | 2022-01-01 13:07 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22010100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-01 | 3458 | keep | 0 | Jan | 2022 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
CAGUAS | 2022-01-01 13:15 | 2022-01-01 15:08 | 25 | 001:53 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | C22010100066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 113 | 2022-01-01 | 2825 | keep | 0 | Jan | 2022 | 0.0019241 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-01-01 13:20 | 2022-01-01 17:00 | 50 | 003:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR FUERTES VIENTOS | M22010100069 | New_Event | Bad Weather | Include | Include | Weather | 220 | 2022-01-01 | 11000 | keep | 0 | Jan | 2022 | 0.007492 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-01 14:03 | 2022-01-01 14:06 | 1474 | 000:03 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO RR/OFF PERMANENTE | R22010100019 | Additional_clients | UG - Broken Splice / Terminal | Include | Include | Equipment | 3 | 2022-01-01 | 4422 | keep | 0 | Jan | 2022 | 0.0030118 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-01 14:06 | 2022-01-01 15:35 | 50 | 001:29 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 50 Y 1 X 40 EN CORTES DE LINEAS REPARO PISTOLA EN PM | R22010100015 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 89 | 2022-01-01 | 4450 | keep | 0 | Jan | 2022 | 0.0030309 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-01 14:40 | 2022-01-01 18:00 | 50 | 003:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 Y 1 X 65 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | S22010100033 | New_Event | Wire Down | Include | Include | Equipment | 200 | 2022-01-01 | 10000 | keep | 0 | Jan | 2022 | 0.006811 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-01-01 15:20 | 2022-01-02 10:19 | 50 | 018:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | M22010100074 | New_Event |  |  | Include | Wildlife | 1139 | 2022-01-01 | 56950 | keep | 0 | Jan | 2022 | 0.038788 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-01 15:22 | 2022-01-01 19:16 | 10 | 003:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22010100041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 234 | 2022-01-01 | 2340 | keep | 0 | Jan | 2022 | 0.0015938 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-01-01 15:29 | 2022-01-01 19:08 | 53 | 003:39 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22010100037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2022-01-01 | 11607 | keep | 0 | Jan | 2022 | 0.0079055 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
CANOVANAS | 2022-01-01 15:40 | 2022-01-01 18:02 | 90 | 002:22 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R22010100022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-01-01 | 12780 | keep | 0 | Jan | 2022 | 0.0087044 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CAGUAS | 2022-01-01 15:44 | 2022-01-01 17:05 | 20 | 001:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE CAJA A LINEA NO FUNDIO | C22010100076 | New_Event | Wire Down | Include | Include | Equipment | 81 | 2022-01-01 | 1620 | keep | 0 | Jan | 2022 | 0.0011034 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-01-01 15:59 | 2022-01-01 18:28 | 250 | 002:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO DE CAJA PRIMARIA QUEMADA | P22010100038 | New_Event | Cutout Failure | Include | Include | Equipment | 149 | 2022-01-01 | 37250 | keep | 0 | Jan | 2022 | 0.025371 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2022-01-01 16:11 | 2022-01-01 16:47 | 15 | 000:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22010100030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 36 | 2022-01-01 | 540 | keep | 0 | Jan | 2022 | 0.00036779 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-01-01 16:29 | 2022-01-01 22:18 | 9 | 005:49 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22010100027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 349 | 2022-01-01 | 3141 | keep | 0 | Jan | 2022 | 0.0021393 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2022-01-01 17:07 | 2022-01-01 17:08 | 1863 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 500 | P22010100046 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-01 | 1863 | keep | 0 | Jan | 2022 | 0.0012689 | 0.0012689 | Momentary | FALSE | FALSE | Not_TMED_Event | 1863
PONCE | 2022-01-01 17:07 | 2022-01-01 17:08 | 708 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 500 | P22010100046 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-01 | 708 | keep | 0 | Jan | 2022 | 0.00048222 | 0.00048222 | Momentary | FALSE | FALSE | Not_TMED_Event | 708
YAUCO | 2022-01-01 17:07 | 2022-01-01 17:08 | 502 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 500 | P22010100043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-01 | 502 | keep | 0 | Jan | 2022 | 0.00034191 | 0.00034191 | Momentary | FALSE | FALSE | Not_TMED_Event | 502
YAUCO | 2022-01-01 17:07 | 2022-01-01 17:08 | 2747 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 500 | P22010100043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-01 | 2747 | keep | 0 | Jan | 2022 | 0.001871 | 0.001871 | Momentary | FALSE | FALSE | Not_TMED_Event | 2747
YAUCO | 2022-01-01 17:07 | 2022-01-01 17:08 | 1587 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 500 | P22010100043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-01 | 1587 | keep | 0 | Jan | 2022 | 0.0010809 | 0.0010809 | Momentary | FALSE | FALSE | Not_TMED_Event | 1587
YAUCO | 2022-01-01 17:07 | 2022-01-01 17:08 | 2671 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 500 | P22010100043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-01 | 2671 | keep | 0 | Jan | 2022 | 0.0018192 | 0.0018192 | Momentary | FALSE | FALSE | Not_TMED_Event | 2671
YAUCO | 2022-01-01 17:07 | 2022-01-01 17:08 | 508 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 500 | P22010100045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-01 | 508 | keep | 0 | Jan | 2022 | 0.000346 | 0.000346 | Momentary | FALSE | FALSE | Not_TMED_Event | 508
YAUCO | 2022-01-01 17:07 | 2022-01-01 17:08 | 64 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 500 | P22010100045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-01 | 64 | keep | 0 | Jan | 2022 | 4.359e-05 | 4.359e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 64
YAUCO | 2022-01-01 17:18 | 2022-01-02 09:30 | 25 | 016:12 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P22010100040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 972 | 2022-01-01 | 24300 | keep | 0 | Jan | 2022 | 0.016551 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-01-01 18:06 | 2022-01-02 12:11 | 100 | 018:05 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN CORTES DE LINEA | C22010100078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1085 | 2022-01-01 | 108500 | keep | 0 | Jan | 2022 | 0.073899 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-01-01 18:43 | 2022-01-02 09:22 | 1 | 014:39 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A22010100021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 879 | 2022-01-01 | 879 | keep | 0 | Jan | 2022 | 0.00059868 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-01-01 18:45 | 2022-01-02 08:46 | 15 | 014:01 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B22010100030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 841 | 2022-01-01 | 12615 | keep | 0 | Jan | 2022 | 0.008592 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-01-01 18:52 | 2022-01-02 09:50 | 3 | 014:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M22010100085 | New_Event | Wire Down | Include | Include | Equipment | 898 | 2022-01-01 | 2694 | keep | 0 | Jan | 2022 | 0.0018349 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2022-01-01 19:23 | 2022-01-02 12:12 | 200 | 016:49 | P | DESGANCHE | 2 X 50 Y 2 X 65 EN CORTES DE LINEA | C22010100081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1009 | 2022-01-01 | 201800 | keep | 0 | Jan | 2022 | 0.13745 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-01-01 19:55 | 2022-01-02 13:58 | 13 | 018:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REEMPLAZAR BAJANTE SECUNDARIO | C22010100083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1083 | 2022-01-01 | 14079 | keep | 0 | Jan | 2022 | 0.0095891 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2022-01-01 21:30 | 2022-01-02 17:26 | 150 | 019:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | M22010100088 | New_Event | Wire Down | Include | Include | Equipment | 1196 | 2022-01-01 | 179400 | keep | 0 | Jan | 2022 | 0.12219 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2022-01-01 22:41 | 2022-01-02 12:09 | 7 | 013:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REEMPLAZAR BAJANTE SECUNDARIO QUEMADO | C22010100089 | New_Event | Secondary Wire Down | Include | Include | Equipment | 808 | 2022-01-01 | 5656 | keep | 0 | Jan | 2022 | 0.0038523 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2022-01-01 22:52 | 2022-01-01 22:56 | 1830 | 000:04 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO INTERRUPTOR PARA RETIRAR TENSOR CRUZADO CON LINEA DE FIBRA OPTICA EN FUEGO | R22010100030 | New_Event |  |  | Include | Wildlife | 4 | 2022-01-01 | 7320 | keep | 0 | Jan | 2022 | 0.0049856 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
BAYAMON | 2022-01-01 23:07 | 2022-01-02 15:59 | 6 | 016:52 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 25KVA POR UNO DE IGUAL CAPACIDAD | B220100033 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1012 | 2022-01-01 | 6072 | keep | 0 | Jan | 2022 | 0.0041356 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-01-01 23:59 | 2022-01-02 08:01 | 40 | 008:02 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22010100035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 482 | 2022-01-01 | 19280 | keep | 0 | Jan | 2022 | 0.013132 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-01-02 00:02 | 2022-01-02 12:17 | 200 | 012:15 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA INFORMA JOURNEYMAN QUE REQUIERE DESGANCHE | M22010200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 735 | 2022-01-02 | 147000 | keep | 0 | Jan | 2022 | 0.10012 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-01-02 00:10 | 2022-01-02 12:34 | 8 | 012:24 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR NO CAUSA | C22010200001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 744 | 2022-01-02 | 5952 | keep | 0 | Jan | 2022 | 0.0040539 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-01-02 03:50 | 2022-01-02 11:44 | 40 | 007:54 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA INDICO JOURNEYMAN NO IDENTIFICO CAUSA | M22010200004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 474 | 2022-01-02 | 18960 | keep | 0 | Jan | 2022 | 0.012914 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-01-02 05:17 | 2022-01-02 05:18 | 24 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | A22010300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-02 | 24 | keep | 0 | Jan | 2022 | 1.6346e-05 | 1.6346e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 24
MAYAGÃœEZ | 2022-01-02 06:32 | 2022-01-02 13:39 | 200 | 007:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | M22010200005 | New_Event | Cutout Failure | Include | Include | Equipment | 427 | 2022-01-02 | 85400 | keep | 0 | Jan | 2022 | 0.058166 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-01-02 06:33 | 2022-01-02 10:29 | 4 | 003:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B22010200002 | New_Event | Cutout Failure | Include | Include | Equipment | 236 | 2022-01-02 | 944 | keep | 0 | Jan | 2022 | 0.00064295 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-01-02 07:47 | 2022-01-02 13:44 | 1 | 005:57 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B22010200005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 357 | 2022-01-02 | 357 | keep | 0 | Jan | 2022 | 0.00024315 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-01-02 08:04 | 2022-01-02 08:05 | 513 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1118-10 Y SE CERRO POR SCADA LLEVA 20% DEL 1111-01 | S22010200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-02 | 513 | keep | 0 | Jan | 2022 | 0.0003494 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2022-01-02 08:04 | 2022-01-02 08:05 | 2782 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1118-10 Y SE CERRO POR SCADA LLEVA 20% DEL 1111-01 | S22010200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-02 | 2782 | keep | 0 | Jan | 2022 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
CANOVANAS | 2022-01-02 08:22 | 2022-01-02 09:55 | 3766 | 001:33 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE LA ALTA DE LA SUBESTACION PORTATIL #20, SE TRANSFIRIO LA CARGA AL 2305-04 | R22010200020 | New_Event |  |  | Include | Wildlife | 93 | 2022-01-02 | 350238 | keep | 0 | Jan | 2022 | 0.23855 | 0.002565 | Sustained | FALSE | FALSE | Not_TMED_Event | 3766
CANOVANAS | 2022-01-02 08:22 | 2022-01-02 09:55 | 1608 | 001:33 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE LA ALTA DE LA SUBESTACION PORTATIL #20, SE TRANSFIRIO LA CARGA AL 2305-04 | R22010200020 | New_Event |  |  | Include | Wildlife | 93 | 2022-01-02 | 149544 | keep | 0 | Jan | 2022 | 0.10185 | 0.0010952 | Sustained | FALSE | FALSE | Not_TMED_Event | 1608
PONCE | 2022-01-02 08:30 | 2022-01-02 10:17 | 150 | 001:47 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA DE PALMA DE LINEA PRIMARIA | P22010200002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 107 | 2022-01-02 | 16050 | keep | 0 | Jan | 2022 | 0.010932 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-01-02 08:34 | 2022-01-02 11:14 | 89 | 002:40 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P22010200003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2022-01-02 | 14240 | keep | 0 | Jan | 2022 | 0.0096988 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
GUAYAMA | 2022-01-02 08:45 | 2022-01-02 15:30 | 107 | 006:45 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA POR DESGANCHE | P22010200004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 405 | 2022-01-02 | 43335 | keep | 0 | Jan | 2022 | 0.029515 | 7.2877e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 107
GUAYAMA | 2022-01-02 09:02 | 2022-01-02 12:34 | 16 | 003:32 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE HIZO DESGANCHE | P22010200009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2022-01-02 | 3392 | keep | 0 | Jan | 2022 | 0.0023103 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2022-01-02 09:03 | 2022-01-02 09:36 | 15 | 000:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22010200001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 33 | 2022-01-02 | 495 | keep | 0 | Jan | 2022 | 0.00033714 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2022-01-02 09:22 | 2022-01-02 10:50 | 100 | 001:28 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22010200013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2022-01-02 | 8800 | keep | 0 | Jan | 2022 | 0.0059936 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2022-01-02 09:25 | 2022-01-02 09:54 | 9 | 000:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR CONECCIONES EN LINEA SECUNDARIA | P22010200011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 29 | 2022-01-02 | 261 | keep | 0 | Jan | 2022 | 0.00017777 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
YAUCO | 2022-01-02 09:36 | 2022-01-02 15:58 | 18 | 006:22 | P | TRANSFORMADOR AVERIADO | 1 X 10 Y 1 X 8 EN DISTINTOS TRANSFORMADORES. TRANSFORMADOR DE 25KVA A 4.16KV AVERIADO | P22010200018 | New_Event | Service Transformer Failure | Include | Include | Equipment | 382 | 2022-01-02 | 6876 | keep | 0 | Jan | 2022 | 0.0046832 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
UTUADO | 2022-01-02 10:00 | 2022-01-02 16:18 | 6 | 006:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN TRANSFORMADOR SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A22010200003 | New_Event | Wire Down | Include | Include | Equipment | 378 | 2022-01-02 | 2268 | keep | 0 | Jan | 2022 | 0.0015447 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-01-02 10:22 | 2022-01-02 10:23 | 1798 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 13700 | A22010200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-02 | 1798 | keep | 0 | Jan | 2022 | 0.0012246 | 0.0012246 | Momentary | FALSE | FALSE | Not_TMED_Event | 1798
ARECIBO | 2022-01-02 10:22 | 2022-01-02 10:23 | 3309 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 13700 | A22010200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-02 | 3309 | keep | 0 | Jan | 2022 | 0.0022537 | 0.0022537 | Momentary | FALSE | FALSE | Not_TMED_Event | 3309
ARECIBO | 2022-01-02 10:22 | 2022-01-02 10:23 | 713 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 13700 | A22010200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-02 | 713 | keep | 0 | Jan | 2022 | 0.00048562 | 0.00048562 | Momentary | FALSE | FALSE | Not_TMED_Event | 713
ARECIBO | 2022-01-02 10:22 | 2022-01-02 10:23 | 1628 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 13700 | A22010200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-02 | 1628 | keep | 0 | Jan | 2022 | 0.0011088 | 0.0011088 | Momentary | FALSE | FALSE | Not_TMED_Event | 1628
ARECIBO | 2022-01-02 10:22 | 2022-01-02 10:23 | 1483 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 13700 | A22010200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-02 | 1483 | keep | 0 | Jan | 2022 | 0.0010101 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
ARECIBO | 2022-01-02 10:22 | 2022-01-02 10:23 | 89 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 13700 | A22010200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-02 | 89 | keep | 0 | Jan | 2022 | 6.0617e-05 | 6.0617e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 89
MAYAGÃœEZ | 2022-01-02 10:22 | 2022-01-02 17:19 | 60 | 006:57 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22010200045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 417 | 2022-01-02 | 25020 | keep | 0 | Jan | 2022 | 0.017041 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-01-02 10:37 | 2022-01-02 14:32 | 33 | 003:55 | P | DESGANCHE | 1 X 50 EN C/L | C22010200014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 235 | 2022-01-02 | 7755 | keep | 0 | Jan | 2022 | 0.0052819 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
MAYAGÃœEZ | 2022-01-02 10:40 | 2022-01-02 12:59 | 300 | 002:19 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22010200047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2022-01-02 | 41700 | keep | 0 | Jan | 2022 | 0.028402 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-01-02 10:43 | 2022-01-02 11:04 | 20 | 000:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22010200006 | New_Event | Secondary Wire Down | Include | Include | Equipment | 21 | 2022-01-02 | 420 | keep | 0 | Jan | 2022 | 0.00028606 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-01-02 11:15 | 2022-01-02 13:51 | 3 | 002:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22010200005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 156 | 2022-01-02 | 468 | keep | 0 | Jan | 2022 | 0.00031875 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2022-01-02 11:17 | 2022-01-02 13:42 | 6 | 002:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REEMPLAZAR TOMA | C22010200020 | New_Event | Secondary Wire Down | Include | Include | Equipment | 145 | 2022-01-02 | 870 | keep | 0 | Jan | 2022 | 0.00059255 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-01-02 11:27 | 2022-01-02 12:10 | 15 | 000:43 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B22010200009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 43 | 2022-01-02 | 645 | keep | 0 | Jan | 2022 | 0.00043931 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-01-02 12:09 | 2022-01-02 15:33 | 200 | 003:24 | P | DESGANCHE | 2 X 100 EN C/L SE REALIZO DESGANCHE | B22010200011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2022-01-02 | 40800 | keep | 0 | Jan | 2022 | 0.027789 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-01-02 12:19 | 2022-01-02 20:42 | 80 | 008:23 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22010200065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 503 | 2022-01-02 | 40240 | keep | 0 | Jan | 2022 | 0.027407 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-01-02 12:22 | 2022-01-02 14:02 | 1 | 001:40 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER NO CAUSA | R22010200082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 100 | 2022-01-02 | 100 | keep | 0 | Jan | 2022 | 6.811e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-01-02 12:23 | 2022-01-02 12:24 | 452 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DEL ALIMENTADOR 9206-09 LLEVA TRANSFERIDA EL 75% DE LA CARGA DEL ALIMENTADOR 9206-08 | B22010700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-02 | 452 | keep | 0 | Jan | 2022 | 0.00030786 | 0.00030786 | Momentary | FALSE | FALSE | Not_TMED_Event | 452
VEGA BAJA | 2022-01-02 12:23 | 2022-01-02 12:24 | 6 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECERRO LLEVA 75% DE LA CARGA DEL 9206-08 | B22010200000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-01-02 | 6 | keep | 0 | Jan | 2022 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-01-02 12:24 | 2022-01-03 11:46 | 60 | 023:22 | P | NO SE REPORTO CAUSA | 1 X 125 EN SU-2 | B22010300057 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1402 | 2022-01-02 | 84120 | keep | 0 | Jan | 2022 | 0.057294 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-01-02 12:24 | 2022-01-02 22:09 | 5 | 009:45 | P | NO SE REPORTO CAUSA | SE CERRO MACHETES DE AMARRE DEL 9206-09 CONTRA EL ALIMENTADOR 9206-08 | B22010200016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 585 | 2022-01-02 | 2925 | keep | 0 | Jan | 2022 | 0.0019922 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-01-02 12:41 | 2022-01-02 16:51 | 14 | 004:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO ABIERTO EN XMR | R22010200083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 250 | 2022-01-02 | 3500 | keep | 0 | Jan | 2022 | 0.0023838 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
YAUCO | 2022-01-02 12:49 | 2022-01-02 16:38 | 16 | 003:49 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR POR DESGANCHE SECUNDARIO | P22010200036 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 229 | 2022-01-02 | 3664 | keep | 0 | Jan | 2022 | 0.0024955 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2022-01-02 13:16 | 2022-01-02 15:38 | 40 | 002:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN C/L RETEZO LINEA | C22010200026 | New_Event | Wire Down | Include | Include | Equipment | 142 | 2022-01-02 | 5680 | keep | 0 | Jan | 2022 | 0.0038686 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-01-02 13:38 | 2022-01-02 16:54 | 20 | 003:16 | P | PARARRAYOS DEFECTUOSO | 1 X 20 EN C/L REEMPLAZO PARARRAYO | C22010200027 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 196 | 2022-01-02 | 3920 | keep | 0 | Jan | 2022 | 0.0026699 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-01-02 14:42 | 2022-01-02 14:43 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22010200039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-02 | 969 | keep | 0 | Jan | 2022 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
CANOVANAS | 2022-01-02 15:28 | 2022-01-03 10:42 | 69 | 019:14 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R22010300013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1154 | 2022-01-02 | 79626 | keep | 0 | Jan | 2022 | 0.054233 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
BAYAMON | 2022-01-02 15:34 | 2022-01-02 17:13 | 130 | 001:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 80 Y 1 X 100 EN DISTINSTOS CORTE DE LINEAS. SE REPORTA PODA POR PARTE DE ABONADO | S22010200012 | New_Event |  |  | Include | Wildlife | 99 | 2022-01-02 | 12870 | keep | 0 | Jan | 2022 | 0.0087657 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
SAN JUAN | 2022-01-02 15:40 | 2022-01-02 18:04 | 9 | 002:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REEMPLAZAR BARRA EN PEDESTAL | R22010200085 | New_Event | Secondary Wire Down | Include | Include | Equipment | 144 | 2022-01-02 | 1296 | keep | 0 | Jan | 2022 | 0.0008827 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2022-01-02 15:42 | 2022-01-02 15:43 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22010200042 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-02 | 969 | keep | 0 | Jan | 2022 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
FAJARDO | 2022-01-02 16:11 | 2022-01-02 18:39 | 90 | 002:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA REEMPLAZO PORTAFUSIBLE | R22010200086 | New_Event | Cutout Failure | Include | Include | Equipment | 148 | 2022-01-02 | 13320 | keep | 0 | Jan | 2022 | 0.0090722 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
HUMACAO | 2022-01-02 16:46 | 2022-01-03 12:22 | 10 | 019:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LA LINEA SECUNDARIA | C22010200031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1176 | 2022-01-02 | 11760 | keep | 0 | Jan | 2022 | 0.0080097 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-01-02 17:40 | 2022-01-02 18:32 | 10 | 000:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | M22010200084 | New_Event |  |  | Include | Wildlife | 52 | 2022-01-02 | 520 | keep | 0 | Jan | 2022 | 0.00035417 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-02 17:45 | 2022-01-02 19:16 | 8 | 001:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJAS PRIMARIAS DEL TRANSFORMADOR Y BAJANTES SECUNDARIOS | A22010200012 | New_Event | Cutout Failure | Include | Include | Equipment | 91 | 2022-01-02 | 728 | keep | 0 | Jan | 2022 | 0.00049584 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-01-02 18:27 | 2022-01-02 18:28 | 3699 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO | R22010200091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-02 | 3699 | keep | 0 | Jan | 2022 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
ARECIBO | 2022-01-02 18:34 | 2022-01-02 20:07 | 40 | 001:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ABIERTO SE ABRIO CORTE DE LINEA PARA REPARARLO | A22010200014 | New_Event | Wire Down | Include | Include | Equipment | 93 | 2022-01-02 | 3720 | keep | 0 | Jan | 2022 | 0.0025337 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-01-02 18:54 | 2022-01-02 18:55 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22010200087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-02 | 1097 | keep | 0 | Jan | 2022 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
MAYAGÃœEZ | 2022-01-02 18:59 | 2022-01-02 21:11 | 15 | 002:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA IGUANA CRUZO LINEAS | M22010200088 | New_Event |  |  | Include | Wildlife | 132 | 2022-01-02 | 1980 | keep | 0 | Jan | 2022 | 0.0013486 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-01-02 19:06 | 2022-01-02 22:30 | 30 | 003:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 30 EN CORTE DE LINEA POSTE IMPACTADO POR CAMION | A22010200017 | New_Event |  |  | Include | Wildlife | 204 | 2022-01-02 | 6120 | keep | 0 | Jan | 2022 | 0.0041683 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-01-02 19:37 | 2022-01-03 12:37 | 300 | 017:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22010200021 | New_Event | Cutout Failure | Include | Include | Equipment | 1020 | 2022-01-02 | 306000 | keep | 0 | Jan | 2022 | 0.20842 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2022-01-02 19:50 | 2022-01-03 14:00 | 25 | 018:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA DE TRANSFORMADOR | R22010200092 | New_Event | Cutout Failure | Include | Include | Equipment | 1090 | 2022-01-02 | 27250 | keep | 0 | Jan | 2022 | 0.01856 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-01-02 20:07 | 2022-01-02 20:27 | 576 | 000:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO SE CERRO CORTE DE LINEA | A22010200014 | Additional_clients | Wire Down | Include | Include | Equipment | 20 | 2022-01-02 | 11520 | keep | 0 | Jan | 2022 | 0.0078462 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-02 20:53 | 2022-01-03 11:30 | 120 | 014:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO | C22010200040 | New_Event | Cutout Failure | Include | Include | Equipment | 877 | 2022-01-02 | 105240 | keep | 0 | Jan | 2022 | 0.071678 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CANOVANAS | 2022-01-02 20:57 | 2022-01-03 01:40 | 90 | 004:43 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN AEREO PROVISIONAL Y 1 X 50 EN SU-12 AVERIA NUEVA DEL T-14 AL T-13 | R22010200097 | New_Event | UG Cable Fault | Include | Include | Equipment | 283 | 2022-01-02 | 25470 | keep | 0 | Jan | 2022 | 0.017348 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2022-01-02 23:02 | 2022-01-02 23:03 | 922 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 QUE A SU VEZ LLEVA LA CARGA DEL 1346-05 | S22010200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-02 | 922 | keep | 0 | Jan | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-01-02 23:02 | 2022-01-02 23:03 | 135 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-08 QUE A SU VEZ LLEVA LA CARGA DEL 1346-05 | S22010200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-02 | 135 | keep | 0 | Jan | 2022 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
CANOVANAS | 2022-01-02 23:48 | 2022-01-02 23:49 | 539 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22010200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-02 | 539 | keep | 0 | Jan | 2022 | 0.00036711 | 0.00036711 | Momentary | FALSE | FALSE | Not_TMED_Event | 539
CANOVANAS | 2022-01-03 01:42 | 2022-01-03 13:11 | 36 | 011:29 | P | CABLE SOTERRADO AVERIADO | AVERIA DEL T14 AL T13 SE CONSTRUYO AEREO PROVISIONAL DE EXISTENTE AL T12 | R22010300002 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 689 | 2022-01-03 | 24804 | keep | 0 | Jan | 2022 | 0.016894 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-03 01:49 | 2022-01-03 12:27 | 6 | 010:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTE DE LINEA CRUCE CON AVE | C22010300005 | New_Event |  |  | Include | Wildlife | 638 | 2022-01-03 | 3828 | keep | 0 | Jan | 2022 | 0.0026072 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-01-03 01:52 | 2022-01-03 09:14 | 100 | 007:22 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R22010300003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 442 | 2022-01-03 | 44200 | keep | 0 | Jan | 2022 | 0.030104 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-01-03 02:37 | 2022-01-03 02:38 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | NO SE REPORTO CAUSA | P220103000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-03 | 3744 | keep | 0 | Jan | 2022 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
SAN JUAN | 2022-01-03 03:07 | 2022-01-03 11:10 | 109 | 008:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 Y 1 X 10 EN CORTE DE LINEA Y TRANSFORMADOR LLUVIAS | R22010300006 | New_Event | Bad Weather | Include | Include | Weather | 483 | 2022-01-03 | 52647 | keep | 0 | Jan | 2022 | 0.035858 | 7.4239e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 109
CANOVANAS | 2022-01-03 03:31 | 2022-01-03 14:20 | 87 | 010:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | R22010300008 | New_Event |  |  | Include | Wildlife | 649 | 2022-01-03 | 56463 | keep | 0 | Jan | 2022 | 0.038457 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
VEGA BAJA | 2022-01-03 03:48 | 2022-01-03 03:49 | 1494 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE DE INTERRUPTOR | B22010300000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-01-03 | 1494 | keep | 0 | Jan | 2022 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
SAN JUAN | 2022-01-03 04:24 | 2022-01-03 04:25 | 726 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-03 QUE LLEVA A SU VEZ LA CARGA DEL 1346-04 | S22010300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-03 | 726 | keep | 0 | Jan | 2022 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2022-01-03 04:24 | 2022-01-03 04:25 | 3932 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1303-03 QUE LLEVA A SU VEZ LA CARGA DEL 1346-04 | S22010300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-03 | 3932 | keep | 0 | Jan | 2022 | 0.0026781 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
SAN JUAN | 2022-01-03 04:25 | 2022-01-03 11:00 | 100 | 006:35 | P | DESGANCHE | 2 X 100 EN C/L SE REALIZO DESGANCHE | S22010300003 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 395 | 2022-01-03 | 39500 | keep | 0 | Jan | 2022 | 0.026903 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-01-03 04:33 | 2022-01-03 04:34 | 2610 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | B22010300000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-01-03 | 2610 | keep | 0 | Jan | 2022 | 0.0017777 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
VEGA BAJA | 2022-01-03 04:34 | 2022-01-03 04:51 | 862 | 0:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE IDENTIFICO PUENTE ABIERTO EN TRONCAL | B22010300000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 17 | 2022-01-03 | 14654 | keep | 0 | Jan | 2022 | 0.0099808 | 0.0005871 | Sustained | FALSE | FALSE | Not_TMED_Event | 862
VEGA BAJA | 2022-01-03 04:41 | 2022-01-03 04:42 | 1494 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE DE INTERRUPTOR | B22010300000 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-01-03 | 1494 | keep | 0 | Jan | 2022 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
VEGA BAJA | 2022-01-03 04:48 | 2022-01-03 04:49 | 1494 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE DE INTERRUPTOR | B22010300000 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-01-03 | 1494 | keep | 0 | Jan | 2022 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
BAYAMON | 2022-01-03 04:51 | 2022-01-03 04:52 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22010300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-03 | 1746 | keep | 0 | Jan | 2022 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
VEGA BAJA | 2022-01-03 04:51 | 2022-01-03 04:52 | 2610 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | B22010300000 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2022-01-03 | 2610 | keep | 0 | Jan | 2022 | 0.0017777 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-01-03 04:51 | 2022-01-03 04:52 | 1494 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE DE INTERRUPTOR | B22010300000 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-01-03 | 1494 | keep | 0 | Jan | 2022 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
BAYAMON | 2022-01-03 04:52 | 2022-01-03 16:08 | 80 | 011:16 | P | NO SE REPORTO CAUSA | 2 X 100 EN SU-1 | B22010300008 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 676 | 2022-01-03 | 54080 | keep | 0 | Jan | 2022 | 0.036834 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-01-03 04:52 | 2022-01-03 20:40 | 300 | 015:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE IDENTIFICO PUENTE ABIERTO EN TRONCAL | B22010300001 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 948 | 2022-01-03 | 284400 | keep | 0 | Jan | 2022 | 0.1937 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
HUMACAO | 2022-01-03 05:16 | 2022-01-03 12:38 | 90 | 007:22 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22010300002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 442 | 2022-01-03 | 39780 | keep | 0 | Jan | 2022 | 0.027094 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
HUMACAO | 2022-01-03 05:26 | 2022-01-03 05:27 | 1467 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | C22010300003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-03 | 1467 | keep | 0 | Jan | 2022 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
HUMACAO | 2022-01-03 05:27 | 2022-01-03 12:12 | 70 | 006:45 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C22010300007 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 405 | 2022-01-03 | 28350 | keep | 0 | Jan | 2022 | 0.019309 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
GUAYAMA | 2022-01-03 05:28 | 2022-01-03 08:40 | 50 | 003:12 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE DESCONECTO PARARAYO DEFECTUOSO | P22010300005 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 192 | 2022-01-03 | 9600 | keep | 0 | Jan | 2022 | 0.0065385 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-03 05:36 | 2022-01-03 05:37 | 514 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR 1520-05 QUE LLEVA LA CARGA DEL 1520-01 Y 1520-04 | S22010300000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-01-03 | 514 | keep | 0 | Jan | 2022 | 0.00035008 | 0.00035008 | Momentary | FALSE | FALSE | Not_TMED_Event | 514
BAYAMON | 2022-01-03 05:36 | 2022-01-03 05:37 | 752 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR 1520-05 QUE LLEVA LA CARGA DEL 1520-01 Y 1520-04 | S22010300000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-01-03 | 752 | keep | 0 | Jan | 2022 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
BAYAMON | 2022-01-03 05:36 | 2022-01-03 05:37 | 68 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR 1520-05 QUE LLEVA LA CARGA DEL 1520-01 Y 1520-04 | S22010300000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-01-03 | 68 | keep | 0 | Jan | 2022 | 4.6314e-05 | 4.6314e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 68
BAYAMON | 2022-01-03 05:37 | 2022-01-03 11:11 | 6 | 005:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR SE REMPLAZO CAJA PRIMARIA | S22010300007 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 334 | 2022-01-03 | 2004 | keep | 0 | Jan | 2022 | 0.0013649 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-01-03 05:50 | 2022-01-03 05:51 | 2858 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22020300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-03 | 2858 | keep | 0 | Jan | 2022 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
ARECIBO | 2022-01-03 06:07 | 2022-01-03 09:30 | 40 | 003:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22010300004 | New_Event | Bad Weather | Include | Include | Weather | 203 | 2022-01-03 | 8120 | keep | 0 | Jan | 2022 | 0.0055305 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-01-03 06:10 | 2022-01-03 08:05 | 30 | 001:55 | P | NO SE REPORTO CAUSA | 1 X 50 EN PROVISIONAL | S22010300008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2022-01-03 | 3450 | keep | 0 | Jan | 2022 | 0.0023498 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-01-03 06:29 | 2022-01-03 11:16 | 75 | 004:47 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO TERMINACION SOTERRADA HACIA PROVISIONAL AEREO | B22010300013 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 287 | 2022-01-03 | 21525 | keep | 0 | Jan | 2022 | 0.014661 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2022-01-03 06:37 | 2022-01-03 06:38 | 2694 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22010300006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-03 | 2694 | keep | 0 | Jan | 2022 | 0.0018349 | 0.0018349 | Momentary | FALSE | FALSE | Not_TMED_Event | 2694
SAN JUAN | 2022-01-03 06:47 | 2022-01-03 09:50 | 125 | 003:03 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L | S22010300013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 183 | 2022-01-03 | 22875 | keep | 0 | Jan | 2022 | 0.01558 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2022-01-03 06:49 | 2022-01-03 08:55 | 15 | 002:06 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B22010300016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2022-01-03 | 1890 | keep | 0 | Jan | 2022 | 0.0012873 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-01-03 06:52 | 2022-01-03 09:16 | 60 | 002:24 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22010300015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 144 | 2022-01-03 | 8640 | keep | 0 | Jan | 2022 | 0.0058847 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-01-03 07:00 | 2022-01-03 10:18 | 1494 | 003:18 | T | PARARRAYOS DEFECTUOSO | SE ELIMINO PARARAYO Y SE CERRO INTERRUPTOR POR CONTROL | B22010300000 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 198 | 2022-01-03 | 295812 | keep | 0 | Jan | 2022 | 0.20148 | 0.0010176 | Sustained | FALSE | FALSE | Not_TMED_Event | 1494
ARECIBO | 2022-01-03 07:06 | 2022-01-03 09:46 | 30 | 002:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22010300008 | New_Event | Bad Weather | Include | Include | Weather | 160 | 2022-01-03 | 4800 | keep | 0 | Jan | 2022 | 0.0032693 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-01-03 07:08 | 2022-01-03 08:45 | 2 | 001:37 | P | NO SE REPORTO CAUSA | 1 X 15 EN BANCO DE TRANSFORMADOR | S22010300017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 97 | 2022-01-03 | 194 | keep | 0 | Jan | 2022 | 0.00013213 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-01-03 07:12 | 2022-01-03 10:37 | 15 | 003:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE TRANSFORMADOR | B22010300025 | New_Event | Wire Down | Include | Include | Equipment | 205 | 2022-01-03 | 3075 | keep | 0 | Jan | 2022 | 0.0020944 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-01-03 08:06 | 2022-01-03 10:02 | 50 | 001:56 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTA CAUSA | P22010300006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2022-01-03 | 5800 | keep | 0 | Jan | 2022 | 0.0039504 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-03 08:07 | 2022-01-03 13:04 | 60 | 004:57 | P | DESGANCHE | 1 X 65 Y 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22010300052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 297 | 2022-01-03 | 17820 | keep | 0 | Jan | 2022 | 0.012137 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-01-03 08:08 | 2022-01-03 17:23 | 15 | 009:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | B22010300053 | New_Event | Cutout Failure | Include | Include | Equipment | 555 | 2022-01-03 | 8325 | keep | 0 | Jan | 2022 | 0.0056701 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-01-03 08:10 | 2022-01-03 08:12 | 36 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1620-04 Y SE CERRO POR SCADA LLEVA 1336-10 | S22010300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-03 | 72 | keep | 0 | Jan | 2022 | 4.9039e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-01-03 08:10 | 2022-01-03 08:12 | 36 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1620-04 Y SE CERRO POR SCADA LLEVA 1620-01 | S22010300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-03 | 72 | keep | 0 | Jan | 2022 | 4.9039e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-01-03 08:10 | 2022-01-03 08:12 | 172 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1620-04 Y SE CERRO POR SCADA LLEVA 1620-01 Y 1336-10 | S22010300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-03 | 344 | keep | 0 | Jan | 2022 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
VEGA BAJA | 2022-01-03 08:25 | 2022-01-03 16:36 | 100 | 008:11 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B22010300058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 491 | 2022-01-03 | 49100 | keep | 0 | Jan | 2022 | 0.033442 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-01-03 08:37 | 2022-01-03 18:29 | 25 | 009:52 | P | CABLE SOTERRADO AVERIADO | SE REPARO LINEA PRIMARIA SOTERRADA | S22010300026 | New_Event | UG Cable Fault | Include | Include | Equipment | 592 | 2022-01-03 | 14800 | keep | 0 | Jan | 2022 | 0.01008 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-01-03 08:46 | 2022-01-03 11:08 | 26 | 002:22 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22010300029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 142 | 2022-01-03 | 3692 | keep | 0 | Jan | 2022 | 0.0025146 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
SAN JUAN | 2022-01-03 08:54 | 2022-01-03 08:56 | 922 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1401-08 Y SE CERRO POR SCADA LLEVA 1346-05 | S22010300031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-03 | 1844 | keep | 0 | Jan | 2022 | 0.0012559 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-01-03 08:54 | 2022-01-03 08:56 | 135 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1401-08 Y SE CERRO POR SCADA LLEVA 1346-05 | S22010300031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-03 | 270 | keep | 0 | Jan | 2022 | 0.0001839 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
CANOVANAS | 2022-01-03 08:56 | 2022-01-03 14:30 | 2 | 005:34 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO CAUSA | R22010300027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 334 | 2022-01-03 | 668 | keep | 0 | Jan | 2022 | 0.00045497 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-01-03 08:59 | 2022-01-03 09:00 | 2179 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22010300029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-03 | 2179 | keep | 0 | Jan | 2022 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
ARECIBO | 2022-01-03 08:59 | 2022-01-04 09:22 | 20 | 024:23 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA EL JOURNEYMAN INFORMO QUE NO ENCONTRO CAUSA PARA QUE FUNDIERA LOS FUSIBLES | A22010300019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1463 | 2022-01-03 | 29260 | keep | 0 | Jan | 2022 | 0.019929 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-01-03 09:15 | 2022-01-03 13:07 | 2 | 003:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO NEUTRAL | C22010300013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 232 | 2022-01-03 | 464 | keep | 0 | Jan | 2022 | 0.00031603 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
UTUADO | 2022-01-03 09:15 | 2022-01-03 14:13 | 6 | 004:58 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR POR BUSHING AVERIADO DE 25 KVA X 37.5 KVA | A22010300017 | New_Event | Service Transformer Failure | Include | Include | Equipment | 298 | 2022-01-03 | 1788 | keep | 0 | Jan | 2022 | 0.0012178 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-01-03 09:17 | 2022-01-03 13:52 | 6 | 004:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22010300004 | New_Event | Bad Weather | Include | Include | Weather | 275 | 2022-01-03 | 1650 | keep | 0 | Jan | 2022 | 0.0011238 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-01-03 09:20 | 2022-01-03 14:30 | 10 | 005:10 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22010300005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 310 | 2022-01-03 | 3100 | keep | 0 | Jan | 2022 | 0.0021114 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-03 09:37 | 2022-01-03 09:38 | 271 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S22010300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-03 | 271 | keep | 0 | Jan | 2022 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
SAN JUAN | 2022-01-03 09:40 | 2022-01-03 13:25 | 100 | 003:45 | P | DESGANCHE | 2 X 50 EN C/L SE REALIZO DESGANCHE | S22010300041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2022-01-03 | 22500 | keep | 0 | Jan | 2022 | 0.015325 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-01-03 09:57 | 2022-01-03 13:24 | 3 | 003:27 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 Y 2 X 15 EN CORTES DE LINEAS MAL TIEMPO | C22010300018 | New_Event | Bad Weather | Include | Include | Weather | 207 | 2022-01-03 | 621 | keep | 0 | Jan | 2022 | 0.00042296 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2022-01-03 09:57 | 2022-01-03 13:29 | 3 | 003:32 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 Y 2 X 15 EN CORTE DE LINEA Y TRANSFORMADOR LLUVIAS | C22010300018 | New_Event | Bad Weather | Include | Include | Weather | 212 | 2022-01-03 | 636 | keep | 0 | Jan | 2022 | 0.00043318 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2022-01-03 10:01 | 2022-01-03 12:39 | 6 | 002:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REEMPLAZAR LINEA SECUNDARIA ZULFATADA | C22010300019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 158 | 2022-01-03 | 948 | keep | 0 | Jan | 2022 | 0.00064568 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-01-03 10:12 | 2022-01-03 11:35 | 10 | 001:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA IGUANA CRUZO FASE A TIERRA | M22010300007 | New_Event |  |  | Include | Wildlife | 83 | 2022-01-03 | 830 | keep | 0 | Jan | 2022 | 0.00056531 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-01-03 10:19 | 2022-01-03 10:20 | 2704 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22010300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-03 | 2704 | keep | 0 | Jan | 2022 | 0.0018417 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
VEGA BAJA | 2022-01-03 10:20 | 2022-01-03 18:23 | 15 | 008:03 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | B22010300082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 483 | 2022-01-03 | 7245 | keep | 0 | Jan | 2022 | 0.0049345 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-01-03 10:37 | 2022-01-03 10:38 | 3511 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22010300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-03 | 3511 | keep | 0 | Jan | 2022 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
BAYAMON | 2022-01-03 10:42 | 2022-01-03 13:19 | 15 | 002:37 | P | PARARRAYOS DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REMPLAZO PARARAYO | B22010300020 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 157 | 2022-01-03 | 2355 | keep | 0 | Jan | 2022 | 0.001604 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-01-03 10:49 | 2022-01-03 16:30 | 16 | 005:41 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRE CAJA DE TRANSFORMADOR PARA CAMBIAR 2 POSTES SECUNDRIOS Y SE CERRO CAJA DE TRANSFORMADOR | P22010300022 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 341 | 2022-01-03 | 5456 | keep | 0 | Jan | 2022 | 0.0037161 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2022-01-03 11:02 | 2022-01-03 11:26 | 6 | 000:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C22010300023 | New_Event | Bad Weather | Include | Include | Weather | 24 | 2022-01-03 | 144 | keep | 0 | Jan | 2022 | 9.8078e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2022-01-03 11:05 | 2022-01-03 11:06 | 4279 | 000:01 | T | NO SE REPORTO CAUSA | REIERRE | P22010300024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-03 | 4279 | keep | 0 | Jan | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
BARRANQUITAS | 2022-01-03 11:21 | 2022-01-03 16:58 | 40 | 005:37 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C22010300025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 337 | 2022-01-03 | 13480 | keep | 0 | Jan | 2022 | 0.0091812 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-01-03 11:30 | 2022-01-03 11:31 | 4390 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 9300 | C22010300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-03 | 4390 | keep | 0 | Jan | 2022 | 0.00299 | 0.00299 | Momentary | FALSE | FALSE | Not_TMED_Event | 4390
CAGUAS | 2022-01-03 11:30 | 2022-01-03 11:31 | 2092 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 9300 | C22010300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-03 | 2092 | keep | 0 | Jan | 2022 | 0.0014249 | 0.0014249 | Momentary | FALSE | FALSE | Not_TMED_Event | 2092
CAGUAS | 2022-01-03 11:30 | 2022-01-03 11:31 | 540 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 9300 | C22010300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-03 | 540 | keep | 0 | Jan | 2022 | 0.00036779 | 0.00036779 | Momentary | FALSE | FALSE | Not_TMED_Event | 540
CAGUAS | 2022-01-03 11:30 | 2022-01-03 11:31 | 131 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 9300 | C22010300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-03 | 131 | keep | 0 | Jan | 2022 | 8.9224e-05 | 8.9224e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 131
CAGUAS | 2022-01-03 11:30 | 2022-01-03 11:31 | 2281 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 9300 | C22010300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-03 | 2281 | keep | 0 | Jan | 2022 | 0.0015536 | 0.0015536 | Momentary | FALSE | FALSE | Not_TMED_Event | 2281
CAGUAS | 2022-01-03 11:30 | 2022-01-03 11:31 | 1569 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 9300 | C22010300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-03 | 1569 | keep | 0 | Jan | 2022 | 0.0010686 | 0.0010686 | Momentary | FALSE | FALSE | Not_TMED_Event | 1569
CAGUAS | 2022-01-03 11:30 | 2022-01-03 11:31 | 2417 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 9300 | C22010300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-03 | 2417 | keep | 0 | Jan | 2022 | 0.0016462 | 0.0016462 | Momentary | FALSE | FALSE | Not_TMED_Event | 2417
BARRANQUITAS | 2022-01-03 11:30 | 2022-01-03 16:06 | 110 | 004:36 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHO Y REEMPLAZARON 6 DISCOS AVERIADOS | C22010300027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 276 | 2022-01-03 | 30360 | keep | 0 | Jan | 2022 | 0.020678 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
GUAYAMA | 2022-01-03 11:43 | 2022-01-03 16:24 | 50 | 004:41 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P22010300028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 281 | 2022-01-03 | 14050 | keep | 0 | Jan | 2022 | 0.0095694 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-01-03 11:59 | 2022-01-03 14:43 | 100 | 002:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 EN CORTE DE LINEA SE CERRO PUENTE PRIMARIO ABIERTO | A22010300036 | New_Event | Wire Down | Include | Include | Equipment | 164 | 2022-01-03 | 16400 | keep | 0 | Jan | 2022 | 0.01117 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-01-03 12:06 | 2022-01-03 14:30 | 5 | 002:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR SE REPARO BAJANTES SECUNDARIOS QUEMADOS | A22010300037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 144 | 2022-01-03 | 720 | keep | 0 | Jan | 2022 | 0.00049039 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2022-01-03 12:12 | 2022-01-03 18:15 | 100 | 006:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN RISER Y 1 X 65 EN CORTE DE LINEA POR CONTACTO DE AVE | P22010300030 | New_Event |  |  | Include | Wildlife | 363 | 2022-01-03 | 36300 | keep | 0 | Jan | 2022 | 0.024724 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-01-03 12:17 | 2022-01-03 16:18 | 200 | 004:01 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22010300015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2022-01-03 | 48200 | keep | 0 | Jan | 2022 | 0.032829 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-01-03 12:45 | 2022-01-03 16:13 | 3 | 003:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REEMPLAZAR 200' PIES DE SECUNDARIA AVERIADA | C22010300033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 208 | 2022-01-03 | 624 | keep | 0 | Jan | 2022 | 0.000425 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2022-01-03 13:32 | 2022-01-03 13:33 | 1284 | 000:01 | T | DESGANCHE | RECERRO | B22010300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-03 | 1284 | keep | 0 | Jan | 2022 | 0.00087453 | 0.00087453 | Momentary | FALSE | FALSE | Not_TMED_Event | 1284
BAYAMON | 2022-01-03 13:39 | 2022-01-03 18:41 | 60 | 005:02 | P | CABLE SOTERRADO AVERIADO | 1 X 100 EN CORTE DE LINEA 1 X 50 EN RISER SE SECCIONALIZO TRAMO SOTERRADO AVERIADO | S22010300052 | New_Event | UG Cable Fault | Include | Include | Equipment | 302 | 2022-01-03 | 18120 | keep | 0 | Jan | 2022 | 0.012341 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-01-03 13:43 | 2022-01-03 14:55 | 1284 | 001:12 | T | DESGANCHE | SE SECCIONALIZO ALIMENTADOR | B22010300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 72 | 2022-01-03 | 92448 | keep | 0 | Jan | 2022 | 0.062966 | 0.00087453 | Sustained | FALSE | FALSE | Not_TMED_Event | 1284
BAYAMON | 2022-01-03 13:45 | 2022-01-03 15:01 | 60 | 001:16 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22010300140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2022-01-03 | 4560 | keep | 0 | Jan | 2022 | 0.0031058 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-01-03 14:22 | 2022-01-03 16:24 | 100 | 002:02 | P | DESGANCHE | 1 X 80 Y 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | A22010300046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2022-01-03 | 12200 | keep | 0 | Jan | 2022 | 0.0083094 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-01-03 14:31 | 2022-01-03 16:19 | 1464 | 1:48 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO | P22010300037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2022-01-03 | 158112 | keep | 0 | Jan | 2022 | 0.10769 | 0.00099712 | Sustained | FALSE | FALSE | Not_TMED_Event | 1464
PONCE | 2022-01-03 14:38 | 2022-01-03 14:39 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22010300038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-03 | 3718 | keep | 0 | Jan | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
CANOVANAS | 2022-01-03 14:54 | 2022-01-03 17:15 | 14 | 002:21 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR 2 BARRAS EN PEDESTAL Y SE REPARO 5 TOMAS | R22010300035 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 141 | 2022-01-03 | 1974 | keep | 0 | Jan | 2022 | 0.0013445 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CAGUAS | 2022-01-03 14:55 | 2022-01-03 18:26 | 95 | 003:31 | P | ESTRUCTURA AVERIADA | 2 X 80 EN CORTE DE LINEA SE ABRIO PUENTE HACIA AVERIA DE POSTE ROTO | C22010300052 | New_Event | Defective Pole | Include | Include | Equipment | 211 | 2022-01-03 | 20045 | keep | 0 | Jan | 2022 | 0.013653 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
VEGA BAJA | 2022-01-03 14:55 | 2022-01-03 15:18 | 950 | 000:23 | P | DESGANCHE | SE RETIRO BAMBUA SOBRE LA LINEA Y SE CERRO DESCONECTIVO | B22010300000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 23 | 2022-01-03 | 21850 | keep | 0 | Jan | 2022 | 0.014882 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-01-03 15:02 | 2022-01-03 16:16 | 30 | 001:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR FUERTES VIENTOS | A22010300052 | New_Event | Bad Weather | Include | Include | Weather | 74 | 2022-01-03 | 2220 | keep | 0 | Jan | 2022 | 0.001512 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-01-03 15:14 | 2022-01-03 15:42 | 15 | 000:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO DE XMR | C22010300056 | New_Event | Secondary Wire Down | Include | Include | Equipment | 28 | 2022-01-03 | 420 | keep | 0 | Jan | 2022 | 0.00028606 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-01-03 15:33 | 2022-01-03 18:55 | 15 | 003:22 | P | NO SE REPORTO CAUSA | 1 X 25 EN BOVEDA | S22010300056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 202 | 2022-01-03 | 3030 | keep | 0 | Jan | 2022 | 0.0020637 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-01-03 15:33 | 2022-01-03 17:13 | 12 | 001:40 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA X 37.5 KVA | R22010300039 | New_Event | Service Transformer Failure | Include | Include | Equipment | 100 | 2022-01-03 | 1200 | keep | 0 | Jan | 2022 | 0.00081731 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-01-03 15:34 | 2022-01-03 18:18 | 19 | 002:44 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22010300043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2022-01-03 | 3116 | keep | 0 | Jan | 2022 | 0.0021223 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
HUMACAO | 2022-01-03 15:34 | 2022-01-03 18:23 | 10 | 002:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO EN XMR | C22010300061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 169 | 2022-01-03 | 1690 | keep | 0 | Jan | 2022 | 0.0011511 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-01-03 15:46 | 2022-01-03 17:27 | 1 | 001:41 | P | OTRAS CAUSAS | TRANSFORMADOR PRIVADO QUEMADO | P22010300055 | New_Event | Other Causes | Include | Include | Other | 101 | 2022-01-03 | 101 | keep | 0 | Jan | 2022 | 6.8791e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-01-03 15:52 | 2022-01-03 19:42 | 20 | 003:50 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 25KVA CON PROBLEMAS DE VOLTAJE | B22010300185 | New_Event | Service Transformer Failure | Include | Include | Equipment | 230 | 2022-01-03 | 4600 | keep | 0 | Jan | 2022 | 0.003133 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-01-03 16:07 | 2022-01-03 16:08 | 1155 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22010300040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-03 | 1155 | keep | 0 | Jan | 2022 | 0.00078667 | 0.00078667 | Momentary | FALSE | FALSE | Not_TMED_Event | 1155
GUAYAMA | 2022-01-03 16:19 | 2022-01-03 19:03 | 75 | 002:44 | P | DESGANCHE | ARBOL TUMBO LINEAS | P22010300047 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 164 | 2022-01-03 | 12300 | keep | 0 | Jan | 2022 | 0.0083775 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-01-03 16:43 | 2022-01-03 22:09 | 50 | 005:26 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESAGANCHE | P22010300052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 326 | 2022-01-03 | 16300 | keep | 0 | Jan | 2022 | 0.011102 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2022-01-03 17:18 | 2022-01-03 18:15 | 2 | 000:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P22010300054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 57 | 2022-01-03 | 114 | keep | 0 | Jan | 2022 | 7.7645e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-01-03 17:35 | 2022-01-03 18:08 | 1 | 000:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | R22010300051 | New_Event |  |  | Include | Wildlife | 33 | 2022-01-03 | 33 | keep | 0 | Jan | 2022 | 2.2476e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-01-03 17:47 | 2022-01-03 23:24 | 35 | 005:37 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22010300200 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 337 | 2022-01-03 | 11795 | keep | 0 | Jan | 2022 | 0.0080335 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
HUMACAO | 2022-01-03 18:04 | 2022-01-04 10:16 | 25 | 016:12 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C22010300079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 972 | 2022-01-03 | 24300 | keep | 0 | Jan | 2022 | 0.016551 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-01-03 18:10 | 2022-01-04 19:57 | 110 | 025:47 | P | ESTRUCTURA AVERIADA | 3 X 80 EN CORTE DE LINEAS REEMPLAZARON DOS POSTES ROTOS | C22010300081 | New_Event | Defective Pole | Include | Include | Equipment | 1547 | 2022-01-03 | 170170 | keep | 0 | Jan | 2022 | 0.1159 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
MAYAGÃœEZ | 2022-01-03 18:19 | 2022-01-03 19:20 | 100 | 001:01 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22010300042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2022-01-03 | 6100 | keep | 0 | Jan | 2022 | 0.0041547 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-01-03 18:40 | 2022-01-03 20:32 | 15 | 001:52 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | S22010300071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2022-01-03 | 1680 | keep | 0 | Jan | 2022 | 0.0011442 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-01-03 18:41 | 2022-01-04 19:47 | 14 | 025:06 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVISIONAL DE T-10 @ T-13 POR AVERIA NUEVA DE T-14 @ T-13 Y VIEJA DE T-12 @ T-13 | S22010300242 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1506 | 2022-01-03 | 21084 | keep | 0 | Jan | 2022 | 0.01436 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-01-03 18:42 | 2022-01-03 20:38 | 60 | 001:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REFIERE SECTOR PARA REALIZAR PODA MASIVA | B22010300214 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2022-01-03 | 6960 | keep | 0 | Jan | 2022 | 0.0047404 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-01-03 18:56 | 2022-01-03 20:05 | 142 | 001:09 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22010300075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 69 | 2022-01-03 | 9798 | keep | 0 | Jan | 2022 | 0.0066734 | 9.6716e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 142
BAYAMON | 2022-01-03 19:02 | 2022-01-03 19:28 | 15 | 000:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22010300083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 26 | 2022-01-03 | 390 | keep | 0 | Jan | 2022 | 0.00026563 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2022-01-03 19:03 | 2022-01-03 19:05 | 1464 | 000:02 | T | DESGANCHE | SE ABRE INTERRUPTOR PARA CERRAR PUENTES PRIMARIOS Y SE CERRO INTERRUPTOR | P22010300059 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-01-03 | 2928 | keep | 0 | Jan | 2022 | 0.0019942 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-03 19:30 | 2022-01-03 21:38 | 2124 | 002:08 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO INTERRUPTOR CARGA POR EL 1657-04 SE DEJO SECCIONALIZADO LAS CAJAS SECAS DE LAS BOMBAS DE LA PIEDAD CERRADO POR CONTROL | R22010300056 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 128 | 2022-01-03 | 271872 | keep | 0 | Jan | 2022 | 0.18517 | 0.0014466 | Sustained | FALSE | FALSE | Not_TMED_Event | 2124
SAN JUAN | 2022-01-03 19:30 | 2022-01-03 21:38 | 14 | 002:08 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO INTERRUPTOR LLEVANDO LA CARGA DEL 1118-07 SE DEJO SECCIONALIZADO LAS CAJAS SECAS DE LAS BOMBAS DE LA PIEDAD CERRADO POR CONTROL | R22010300056 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 128 | 2022-01-03 | 1792 | keep | 0 | Jan | 2022 | 0.0012205 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2022-01-03 20:33 | 2022-01-04 00:40 | 50 | 004:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RETIRO CARGA Y SE CERRO PUENTE ABIERTO DE RISER A LINEA | S22010300079 | New_Event | Wire Down | Include | Include | Equipment | 247 | 2022-01-03 | 12350 | keep | 0 | Jan | 2022 | 0.0084115 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-01-03 20:40 | 2022-01-03 22:42 | 650 | 002:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIERON MACHETES Y SE CERRO PUENTE ABIERTO MEDIANTE GOI BY-220103-02 | B22010300001 | New_Event | Wire Down | Include | Include | Equipment | 122 | 2022-01-03 | 79300 | keep | 0 | Jan | 2022 | 0.054011 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
SAN JUAN | 2022-01-03 21:24 | 2022-01-03 22:50 | 50 | 001:26 | P | DESGANCHE | 1 X 65 EN C/L. SE RETIRO ENREDADERA | S22010300077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2022-01-03 | 4300 | keep | 0 | Jan | 2022 | 0.0029287 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-03 21:38 | 2022-01-04 19:33 | 1 | 021:55 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REMPLAZO PISTOLA EN V/S MH 1510 | C22010300149 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 1315 | 2022-01-03 | 1315 | keep | 0 | Jan | 2022 | 0.00089564 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-01-04 00:14 | 2022-01-04 00:15 | 5809 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22010400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-04 | 5809 | keep | 0 | Jan | 2022 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
YAUCO | 2022-01-04 00:23 | 2022-01-04 09:22 | 8 | 008:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE FIJO BAJANTE SECUNDARIO EN SALIDA DE TRANSFORMADOR | P22010400001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 539 | 2022-01-04 | 4312 | keep | 0 | Jan | 2022 | 0.0029369 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-01-04 03:11 | 2022-01-04 03:12 | 2450 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CARGA POR EL 2605-02 CERRADO POR CONTROL | C22010300001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-04 | 2450 | keep | 0 | Jan | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-01-04 03:11 | 2022-01-04 03:12 | 640 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVANDO LA CARGA DEL 2605-01 CERRADO POR CONTROL | C22010300001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-04 | 640 | keep | 0 | Jan | 2022 | 0.0004359 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
ARECIBO | 2022-01-04 06:50 | 2022-01-04 14:58 | 2201 | 008:08 | T | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO | A22010400005 | New_Event | Defective Pole | Include | Include | Equipment | 488 | 2022-01-04 | 1074088 | keep | 0 | Jan | 2022 | 0.73156 | 0.0014991 | Sustained | FALSE | FALSE | Not_TMED_Event | 2201
MAYAGÃœEZ | 2022-01-04 07:34 | 2022-01-04 07:35 | 1444 | 000:01 | T | NO SE REPORTO CAUSA | CARGA POR 6014-02 | M22010400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-04 | 1444 | keep | 0 | Jan | 2022 | 0.0009835 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-01-04 07:34 | 2022-01-04 07:35 | 3630 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO CERRADO POR SCADA | M22010400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-04 | 3630 | keep | 0 | Jan | 2022 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2022-01-04 07:53 | 2022-01-04 11:33 | 50 | 003:40 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22010400008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2022-01-04 | 11000 | keep | 0 | Jan | 2022 | 0.007492 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-01-04 08:02 | 2022-01-04 10:49 | 150 | 002:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN CORTE DE LINEA POR CONTACTO CON AVE | P22010400008 | New_Event |  |  | Include | Wildlife | 167 | 2022-01-04 | 25050 | keep | 0 | Jan | 2022 | 0.017061 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-01-04 08:15 | 2022-01-04 08:16 | 888 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M22010400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-04 | 888 | keep | 0 | Jan | 2022 | 0.00060481 | 0.00060481 | Momentary | FALSE | FALSE | Not_TMED_Event | 888
MAYAGÃœEZ | 2022-01-04 08:15 | 2022-01-04 08:16 | 393 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M22010400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-04 | 393 | keep | 0 | Jan | 2022 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2022-01-04 08:15 | 2022-01-04 08:16 | 4 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M22010400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-04 | 4 | keep | 0 | Jan | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-01-04 08:15 | 2022-01-04 08:16 | 372 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M22010400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-04 | 372 | keep | 0 | Jan | 2022 | 0.00025337 | 0.00025337 | Momentary | FALSE | FALSE | Not_TMED_Event | 372
MAYAGÃœEZ | 2022-01-04 08:15 | 2022-01-04 08:16 | 2530 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M22010400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-04 | 2530 | keep | 0 | Jan | 2022 | 0.0017232 | 0.0017232 | Momentary | FALSE | FALSE | Not_TMED_Event | 2530
MAYAGÃœEZ | 2022-01-04 08:15 | 2022-01-04 08:16 | 199 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M22010400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-04 | 199 | keep | 0 | Jan | 2022 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
MAYAGÃœEZ | 2022-01-04 08:15 | 2022-01-04 08:16 | 312 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M22010400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-04 | 312 | keep | 0 | Jan | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
MAYAGÃœEZ | 2022-01-04 08:15 | 2022-01-04 08:16 | 4641 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M22010400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-04 | 4641 | keep | 0 | Jan | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
ARECIBO | 2022-01-04 08:27 | 2022-01-04 08:28 | 2107 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22010400010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-04 | 2107 | keep | 0 | Jan | 2022 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
VEGA BAJA | 2022-01-04 08:58 | 2022-01-04 19:00 | 100 | 010:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE REALIZO DESGANCHE | B22010400012 | New_Event | Wire Down | Include | Include | Equipment | 602 | 2022-01-04 | 60200 | keep | 0 | Jan | 2022 | 0.041002 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-01-04 09:05 | 2022-01-04 10:27 | 80 | 001:22 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A22010400014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 82 | 2022-01-04 | 6560 | keep | 0 | Jan | 2022 | 0.004468 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-01-04 09:13 | 2022-01-04 11:56 | 100 | 002:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE RETEZO LINEA | M22010400025 | New_Event | Wire Down | Include | Include | Equipment | 163 | 2022-01-04 | 16300 | keep | 0 | Jan | 2022 | 0.011102 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-01-04 09:20 | 2022-01-04 12:14 | 35 | 002:54 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22010400013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2022-01-04 | 6090 | keep | 0 | Jan | 2022 | 0.0041479 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2022-01-04 09:41 | 2022-01-04 10:14 | 15 | 000:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | P22010400011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 33 | 2022-01-04 | 495 | keep | 0 | Jan | 2022 | 0.00033714 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-01-04 09:44 | 2022-01-04 10:39 | 12 | 000:55 | P | DESGANCHE | SE RETEZO SECUNDARIA Y DESGANCHE | S22010400011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2022-01-04 | 660 | keep | 0 | Jan | 2022 | 0.00044952 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-01-04 09:53 | 2022-01-04 11:00 | 4 | 001:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | M22010400031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 67 | 2022-01-04 | 268 | keep | 0 | Jan | 2022 | 0.00018253 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-01-04 10:24 | 2022-01-04 16:59 | 8 | 006:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR NEUTRAL SECUNDARIO | C22040100016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 395 | 2022-01-04 | 3160 | keep | 0 | Jan | 2022 | 0.0021523 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-01-04 10:26 | 2022-01-04 12:37 | 10 | 002:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR BAJANTE | S22010300018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 131 | 2022-01-04 | 1310 | keep | 0 | Jan | 2022 | 0.00089224 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-01-04 10:34 | 2022-01-04 12:33 | 8 | 001:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZARON BARRAS SECUNDARIAS EN PEDESTAL | C22010400018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 119 | 2022-01-04 | 952 | keep | 0 | Jan | 2022 | 0.0006484 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-01-04 10:35 | 2022-01-04 11:28 | 20 | 000:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONECTORES SECUNDARIOS | M22010400001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 53 | 2022-01-04 | 1060 | keep | 0 | Jan | 2022 | 0.00072196 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-01-04 10:41 | 2022-01-04 15:24 | 8 | 004:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO ZAFADO A CAJA EN TRANSFORMADOR | C22010400021 | New_Event | Wire Down | Include | Include | Equipment | 283 | 2022-01-04 | 2264 | keep | 0 | Jan | 2022 | 0.001542 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-01-04 10:46 | 2022-01-04 18:57 | 6 | 008:11 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO XMR Y SE REMPLAZO POSTE Y SECUNDARIA | B22010400026 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 491 | 2022-01-04 | 2946 | keep | 0 | Jan | 2022 | 0.0020065 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-01-04 10:49 | 2022-01-04 11:16 | 1 | 000:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN RISER MAL TIEMPO | C22010400024 | New_Event | Bad Weather | Include | Include | Weather | 27 | 2022-01-04 | 27 | keep | 0 | Jan | 2022 | 1.839e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-01-04 10:49 | 2022-01-04 11:14 | 10 | 000:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES EN BARRA DE PEDESTAL SECUNDARIO | P22010400017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 25 | 2022-01-04 | 250 | keep | 0 | Jan | 2022 | 0.00017027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-01-04 10:58 | 2022-01-04 13:31 | 10 | 002:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | C22010400029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 153 | 2022-01-04 | 1530 | keep | 0 | Jan | 2022 | 0.0010421 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-01-04 11:14 | 2022-01-04 19:00 | 12 | 007:46 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 40 DE SU-2 @ T-5 SE REPARO PISTOLA AVERIADA | B22010400028 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 466 | 2022-01-04 | 5592 | keep | 0 | Jan | 2022 | 0.0038087 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-01-04 11:17 | 2022-01-04 13:16 | 40 | 001:59 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22010400029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 119 | 2022-01-04 | 4760 | keep | 0 | Jan | 2022 | 0.003242 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-01-04 11:20 | 2022-01-04 12:37 | 13 | 001:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | S22010300076 | New_Event | Secondary Wire Down | Include | Include | Equipment | 77 | 2022-01-04 | 1001 | keep | 0 | Jan | 2022 | 0.00068178 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2022-01-04 11:25 | 2022-01-04 15:11 | 14 | 003:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 1 X 10 EN XMR | S22010400027 | New_Event | Cutout Failure | Include | Include | Equipment | 226 | 2022-01-04 | 3164 | keep | 0 | Jan | 2022 | 0.002155 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2022-01-04 11:35 | 2022-01-04 11:54 | 10 | 000:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | A22010400027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 19 | 2022-01-04 | 190 | keep | 0 | Jan | 2022 | 0.00012941 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-01-04 12:05 | 2022-01-04 14:50 | 15 | 002:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M22010400040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 165 | 2022-01-04 | 2475 | keep | 0 | Jan | 2022 | 0.0016857 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-01-04 12:06 | 2022-01-04 12:07 | 641 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE LLEVA LA CARGA DEL 1206-02 | S22010400000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-01-04 | 641 | keep | 0 | Jan | 2022 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2022-01-04 12:06 | 2022-01-04 12:07 | 733 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE 1206-02 LLEVANDO LA CARGA DEL 1206-01 | S22010400000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-01-04 | 733 | keep | 0 | Jan | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2022-01-04 12:07 | 2022-01-04 13:59 | 100 | 001:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO MACHETE PARA SUBIR LINEA PRIMARIA | S22010400032 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 112 | 2022-01-04 | 11200 | keep | 0 | Jan | 2022 | 0.0076283 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-01-04 12:44 | 2022-01-04 16:57 | 40 | 004:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22010400042 | New_Event | Cutout Failure | Include | Include | Equipment | 253 | 2022-01-04 | 10120 | keep | 0 | Jan | 2022 | 0.0068927 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-01-04 13:06 | 2022-01-04 15:23 | 12 | 002:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA Y SE REPARO SECUNDARIA | S22010400034 | New_Event | Cutout Failure | Include | Include | Equipment | 137 | 2022-01-04 | 1644 | keep | 0 | Jan | 2022 | 0.0011197 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-01-04 13:12 | 2022-01-04 14:36 | 4390 | 001:24 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9300 | C22010400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2022-01-04 | 368760 | keep | 0 | Jan | 2022 | 0.25116 | 0.00299 | Sustained | FALSE | FALSE | Not_TMED_Event | 4390
CAGUAS | 2022-01-04 13:12 | 2022-01-04 14:36 | 2092 | 001:24 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9300 | C22010400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2022-01-04 | 175728 | keep | 0 | Jan | 2022 | 0.11969 | 0.0014249 | Sustained | FALSE | FALSE | Not_TMED_Event | 2092
CAGUAS | 2022-01-04 13:12 | 2022-01-04 14:36 | 540 | 001:24 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9300 | C22010400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2022-01-04 | 45360 | keep | 0 | Jan | 2022 | 0.030894 | 0.00036779 | Sustained | FALSE | FALSE | Not_TMED_Event | 540
CAGUAS | 2022-01-04 13:12 | 2022-01-04 14:36 | 131 | 001:24 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9300 | C22010400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2022-01-04 | 11004 | keep | 0 | Jan | 2022 | 0.0074948 | 8.9224e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 131
CAGUAS | 2022-01-04 13:12 | 2022-01-04 14:36 | 2281 | 001:24 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9300 | C22010400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2022-01-04 | 191604 | keep | 0 | Jan | 2022 | 0.1305 | 0.0015536 | Sustained | FALSE | FALSE | Not_TMED_Event | 2281
CAGUAS | 2022-01-04 13:12 | 2022-01-04 14:36 | 1569 | 001:24 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9300 | C22010400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2022-01-04 | 131796 | keep | 0 | Jan | 2022 | 0.089766 | 0.0010686 | Sustained | FALSE | FALSE | Not_TMED_Event | 1569
CAGUAS | 2022-01-04 13:12 | 2022-01-04 14:36 | 2417 | 001:24 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9300 | C22010400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2022-01-04 | 203028 | keep | 0 | Jan | 2022 | 0.13828 | 0.0016462 | Sustained | FALSE | FALSE | Not_TMED_Event | 2417
AGUADILLA | 2022-01-04 13:20 | 2022-01-04 14:15 | 20 | 000:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | M22010400026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 55 | 2022-01-04 | 1100 | keep | 0 | Jan | 2022 | 0.0007492 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-01-04 13:21 | 2022-01-04 13:48 | 10 | 000:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO LINEAS SECUNDARIAS CRUZADAS | A22010400047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 27 | 2022-01-04 | 270 | keep | 0 | Jan | 2022 | 0.0001839 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-01-04 13:26 | 2022-01-04 20:55 | 100 | 007:29 | P | ESTRUCTURA AVERIADA | 2 X 65 EN CORTE DE LINEA POR POSTE PRIMARIO PARTIDO SE ABRIO PUENTES PRIMARIOS PARA SECCIONALIZAR AVERIA | P22010400035 | New_Event | Defective Pole | Include | Include | Equipment | 449 | 2022-01-04 | 44900 | keep | 0 | Jan | 2022 | 0.030581 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-01-04 13:43 | 2022-01-05 09:45 | 20 | 020:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE DE IGUANA | C22010400084 | New_Event |  |  | Include | Wildlife | 1202 | 2022-01-04 | 24040 | keep | 0 | Jan | 2022 | 0.016374 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-01-04 14:50 | 2022-01-04 16:43 | 20 | 001:53 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | M22010400074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2022-01-04 | 2260 | keep | 0 | Jan | 2022 | 0.0015393 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-01-04 15:11 | 2022-01-04 15:54 | 50 | 000:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L CRUCE X AVE | R22010400020 | New_Event |  |  | Include | Wildlife | 43 | 2022-01-04 | 2150 | keep | 0 | Jan | 2022 | 0.0014644 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-01-04 15:30 | 2022-01-04 17:05 | 6 | 001:35 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 50 KVA X 50 KVA CON ESCAPE DE ACEITE | M22010400079 | New_Event | Service Transformer Failure | Include | Include | Equipment | 95 | 2022-01-04 | 570 | keep | 0 | Jan | 2022 | 0.00038822 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-01-04 15:51 | 2022-01-04 17:11 | 100 | 001:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN C/L CRUCE X GLOBO | R22010400027 | New_Event |  |  | Include | Wildlife | 80 | 2022-01-04 | 8000 | keep | 0 | Jan | 2022 | 0.0054488 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-01-04 16:27 | 2022-01-04 18:30 | 15 | 002:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN TRANSFORMADOR IGUANA CRUZO FASES | M22010400087 | New_Event |  |  | Include | Wildlife | 123 | 2022-01-04 | 1845 | keep | 0 | Jan | 2022 | 0.0012566 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-01-04 16:44 | 2022-01-04 17:32 | 6 | 000:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22010300002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 48 | 2022-01-04 | 288 | keep | 0 | Jan | 2022 | 0.00019616 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-01-04 17:10 | 2022-01-04 20:18 | 90 | 003:08 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | C22040100167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2022-01-04 | 16920 | keep | 0 | Jan | 2022 | 0.011524 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2022-01-04 17:24 | 2022-01-04 17:32 | 635 | 000:08 | T | OTRAS CAUSAS | SE ABRIO EL BKR PARA TRANSFERIR CARGA AL 2306-03 NO FASEAN | R22010400000 | New_Event | Other Causes | Include | Include | Other | 8 | 2022-01-04 | 5080 | keep | 0 | Jan | 2022 | 0.00346 | 0.0004325 | Sustained | FALSE | FALSE | Not_TMED_Event | 635
ARECIBO | 2022-01-04 17:30 | 2022-01-04 17:54 | 10 | 000:24 | P | TRANSFORMADOR AVERIADO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BUSHING SECUNDARIO | A22010400056 | New_Event | Service Transformer Failure | Include | Include | Equipment | 24 | 2022-01-04 | 240 | keep | 0 | Jan | 2022 | 0.00016346 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-01-04 17:31 | 2022-01-04 18:39 | 9 | 001:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR NEUTRAL SECUNDARIO Y RETEZAR LINEA SECUNDARIA | C22040100170 | New_Event | Secondary Wire Down | Include | Include | Equipment | 68 | 2022-01-04 | 612 | keep | 0 | Jan | 2022 | 0.00041683 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
GUAYAMA | 2022-01-04 17:35 | 2022-01-04 18:25 | 10 | 000:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO ZAFADO A CAJA EN TRANSFORMADOR | P22010400049 | New_Event | Wire Down | Include | Include | Equipment | 50 | 2022-01-04 | 500 | keep | 0 | Jan | 2022 | 0.00034055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-01-04 18:25 | 2022-01-04 20:16 | 30 | 001:51 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | R22010400037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 111 | 2022-01-04 | 3330 | keep | 0 | Jan | 2022 | 0.002268 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-01-04 18:30 | 2022-01-05 12:36 | 10 | 018:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR TRANSFORMADOR PARA REPARAR SECUNDARIA | C22010400178 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1086 | 2022-01-04 | 10860 | keep | 0 | Jan | 2022 | 0.0073967 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-01-04 18:37 | 2022-01-05 09:44 | 125 | 015:07 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R22010400059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 907 | 2022-01-04 | 113375 | keep | 0 | Jan | 2022 | 0.077219 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
HUMACAO | 2022-01-04 19:06 | 2022-01-05 09:20 | 10 | 014:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE CERRO PUENTE SECUNDARIO | C22010400182 | New_Event | Secondary Wire Down | Include | Include | Equipment | 854 | 2022-01-04 | 8540 | keep | 0 | Jan | 2022 | 0.0058166 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-04 19:30 | 2022-01-04 20:51 | 10 | 001:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A22010400060 | New_Event | Cutout Failure | Include | Include | Equipment | 81 | 2022-01-04 | 810 | keep | 0 | Jan | 2022 | 0.00055169 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-04 19:52 | 2022-01-04 19:53 | 1264 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1904-07 Y SE CERRO POR SCADA LLEVA 1901-04 | S22010400062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-04 | 1264 | keep | 0 | Jan | 2022 | 0.0008609 | 0.0008609 | Momentary | FALSE | FALSE | Not_TMED_Event | 1264
MAYAGÃœEZ | 2022-01-04 19:59 | 2022-01-04 21:45 | 30 | 001:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22010400093 | New_Event | Bad Weather | Include | Include | Weather | 106 | 2022-01-04 | 3180 | keep | 0 | Jan | 2022 | 0.0021659 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-01-04 20:06 | 2022-01-04 21:15 | 100 | 001:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AUTO IMPACTO POSTE Y CRUZO LINEAS | M22010400098 | New_Event |  |  | Include | Wildlife | 69 | 2022-01-04 | 6900 | keep | 0 | Jan | 2022 | 0.0046996 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-01-04 20:24 | 2022-01-04 22:35 | 15 | 002:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CERRO PUENTE DE CAJA A LINEA DE XMR Y SE REEMPLAZO CAJA AVERIADA (NO FUNDIO) | B22010400078 | New_Event | Cutout Failure | Include | Include | Equipment | 131 | 2022-01-04 | 1965 | keep | 0 | Jan | 2022 | 0.0013384 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-01-04 20:35 | 2022-01-04 20:36 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S22010400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-04 | 2203 | keep | 0 | Jan | 2022 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
ARECIBO | 2022-01-04 21:33 | 2022-01-05 09:20 | 10 | 011:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22010400065 | New_Event | Bad Weather | Include | Include | Weather | 707 | 2022-01-04 | 7070 | keep | 0 | Jan | 2022 | 0.0048153 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-01-04 21:49 | 2022-01-04 23:39 | 80 | 001:50 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22010400086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 110 | 2022-01-04 | 8800 | keep | 0 | Jan | 2022 | 0.0059936 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-01-04 22:40 | 2022-01-05 08:45 | 500 | 010:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE Y CONECTOR DE LINEA A CAJA EN MACHETE | B22010400092 | New_Event | Wire Down | Include | Include | Equipment | 605 | 2022-01-04 | 302500 | keep | 0 | Jan | 2022 | 0.20603 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2022-01-04 23:38 | 2022-01-04 23:40 | 1026 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C22010400062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-04 | 2052 | keep | 0 | Jan | 2022 | 0.0013976 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
FAJARDO | 2022-01-05 00:05 | 2022-01-05 05:40 | 41 | 005:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN C/L MAL TIEMPO | R22010500001 | New_Event | Bad Weather | Include | Include | Weather | 335 | 2022-01-05 | 13735 | keep | 0 | Jan | 2022 | 0.0093548 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
BAYAMON | 2022-01-05 00:20 | 2022-01-05 00:21 | 492 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22010500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-05 | 492 | keep | 0 | Jan | 2022 | 0.0003351 | 0.0003351 | Momentary | FALSE | FALSE | Not_TMED_Event | 492
BAYAMON | 2022-01-05 00:21 | 2022-01-05 13:06 | 1 | 012:45 | P | NO SE REPORTO CAUSA | 3 X 100 EN SU 212 | B22010500027 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 765 | 2022-01-05 | 765 | keep | 0 | Jan | 2022 | 0.00052104 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-01-05 01:04 | 2022-01-05 12:30 | 40 | 011:26 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B22010500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 686 | 2022-01-05 | 27440 | keep | 0 | Jan | 2022 | 0.018689 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-01-05 01:17 | 2022-01-05 16:13 | 30 | 014:56 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 15 EN C/L PROVISIONAL SE REPARO TERMINACION EN PROVISIONAL AEREO | R22010500004 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 896 | 2022-01-05 | 26880 | keep | 0 | Jan | 2022 | 0.018308 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-01-05 05:07 | 2022-01-05 05:08 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22010500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-05 | 990 | keep | 0 | Jan | 2022 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
SAN JUAN | 2022-01-05 05:18 | 2022-01-05 05:21 | 553 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO 1529-15 LLEVANDO 30% DEL 1346-02 | S22010500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-01-05 | 1659 | keep | 0 | Jan | 2022 | 0.0011299 | 0.00037665 | Momentary | FALSE | FALSE | Not_TMED_Event | 553
BAYAMON | 2022-01-05 05:18 | 2022-01-05 05:21 | 1802 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO 1529-15 LLEVANDO 30% DEL 1346-02 | S22010500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-01-05 | 5406 | keep | 0 | Jan | 2022 | 0.003682 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
ARECIBO | 2022-01-05 05:35 | 2022-01-05 15:30 | 100 | 009:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22010500002 | New_Event | Bad Weather | Include | Include | Weather | 595 | 2022-01-05 | 59500 | keep | 0 | Jan | 2022 | 0.040525 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-01-05 05:37 | 2022-01-05 10:42 | 3 | 005:05 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHO | R22010500008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 305 | 2022-01-05 | 915 | keep | 0 | Jan | 2022 | 0.0006232 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2022-01-05 06:05 | 2022-01-05 09:36 | 40 | 003:31 | P | OTRAS CAUSAS | 1 X 100 EN CORTE DE LINEA SE RETIRO CARGA DE DEPENDENCIA MUNICIPAL POR APARENTE PROBLEMA INTERNO | B22010500011 | New_Event | Other Causes | Include | Include | Other | 211 | 2022-01-05 | 8440 | keep | 0 | Jan | 2022 | 0.0057484 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-01-05 06:16 | 2022-01-05 06:17 | 3432 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO LLEVANDO 80% DEL 1204-02 POR PORTATIL Y 20% DEL 1303-02 | S22010500000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-01-05 | 3432 | keep | 0 | Jan | 2022 | 0.0023375 | 0.0023375 | Momentary | FALSE | FALSE | Not_TMED_Event | 3432
SAN JUAN | 2022-01-05 06:16 | 2022-01-05 06:17 | 487 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO LLEVANDO 80% DEL 1204-02 POR PORTATIL Y 20% DEL 1303-02 | S22010500000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-01-05 | 487 | keep | 0 | Jan | 2022 | 0.00033169 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
SAN JUAN | 2022-01-05 06:17 | 2022-01-05 14:38 | 65 | 008:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA | S22010500086 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 501 | 2022-01-05 | 32565 | keep | 0 | Jan | 2022 | 0.02218 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2022-01-05 06:25 | 2022-01-05 06:26 | 10211 | 000:01 | T | DESGANCHE | RECERRO SU CARGA POR 1206-3 | S22010500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-05 | 10211 | keep | 0 | Jan | 2022 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2022-01-05 06:25 | 2022-01-05 06:26 | 4133 | 000:01 | T | DESGANCHE | RECERRO LLEVA 1204-5 | S22010500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-05 | 4133 | keep | 0 | Jan | 2022 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2022-01-05 06:28 | 2022-01-05 07:37 | 10211 | 001:09 | T | DESGANCHE | SE ABRE MACHETE DEL 1204-5 URB. VILLA DEL SOL CALLE 5 Y SE CERRO INTERRUPTOR 1206-3 100% EN SERVICIO Y 95% EN SERVICIO 1204-5 | S22010500004 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 69 | 2022-01-05 | 704559 | keep | 0 | Jan | 2022 | 0.47987 | 0.0069547 | Sustained | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2022-01-05 06:28 | 2022-01-05 07:37 | 4133 | 001:09 | T | DESGANCHE | DISPARO 1206-03 LLEVANDO EL 1204-05. SE ABRE MACHETE DEL 1204-5 URB. VILLA DEL SOL CALLE 5 Y SE CERRO INTERRUPTOR 1206-3 100% EN SERVICIO Y 95% EN SERVICIO 1204-5 | S22010500004 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 69 | 2022-01-05 | 285177 | keep | 0 | Jan | 2022 | 0.19423 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2022-01-05 06:55 | 2022-01-05 11:29 | 36 | 004:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN SU LLUVIAS | R22010500010 | New_Event | Bad Weather | Include | Include | Weather | 274 | 2022-01-05 | 9864 | keep | 0 | Jan | 2022 | 0.0067183 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-01-05 06:55 | 2022-01-05 11:29 | 10 | 004:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN SU LLUVIAS | R22010500010 | New_Event | Bad Weather | Include | Include | Weather | 274 | 2022-01-05 | 2740 | keep | 0 | Jan | 2022 | 0.0018662 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-01-05 07:00 | 2022-01-05 07:01 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22010500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-05 | 1827 | keep | 0 | Jan | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
GUAYAMA | 2022-01-05 07:04 | 2022-01-05 07:05 | 1945 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P22010500002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-05 | 1945 | keep | 0 | Jan | 2022 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
SAN JUAN | 2022-01-05 07:10 | 2022-01-05 13:36 | 922 | 006:26 | T | CABLE SOTERRADO AVERIADO | SE REEMPLAZO AISLADOR AVERIADO PERO PROBO MALO. SE PROCEDIO A PATRULLAR ALIMENTADOR 1401-08 QUE LLEVA EL 1346-05 | S22010500036 | New_Event | UG Cable Fault | Include | Include | Equipment | 386 | 2022-01-05 | 355892 | keep | 0 | Jan | 2022 | 0.2424 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-01-05 07:10 | 2022-01-05 11:40 | 837 | 004:30 | S | CABLE SOTERRADO AVERIADO | RECERRO 1401-8 Y DISPARO 0050 SE FUE A LOCKOUT DISPARO POR DIFERENCIAL SE ENCONTRO TRANSFORMADOR NO TENIA TIERRAS INSTALADAS | S22010500036 | New_Event | UG Cable Fault | Include | Include | Equipment | 270 | 2022-01-05 | 225990 | keep | 0 | Jan | 2022 | 0.15392 | 0.00057008 | Sustained | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2022-01-05 07:10 | 2022-01-05 11:39 | 908 | 004:29 | S | CABLE SOTERRADO AVERIADO | RECERRO 1401-8 Y DISPARO 0050 SE FUE A LOCKOUT DISPARO POR DIFERENCIAL SE ENCONTRO TRANSFORMADOR NO TENIA TIERRAS INSTALADAS | S22010500036 | New_Event | UG Cable Fault | Include | Include | Equipment | 269 | 2022-01-05 | 244252 | keep | 0 | Jan | 2022 | 0.16636 | 0.00061843 | Sustained | FALSE | FALSE | Not_TMED_Event | 908
SAN JUAN | 2022-01-05 07:10 | 2022-01-05 15:12 | 135 | 008:02 | S | CABLE SOTERRADO AVERIADO | RECERRO 1401-8 Y DISPARO 0050 SE FUE A LOCKOUT DISPARO POR DIFERENCIAL SE ENCONTRO TRANSFORMADOR NO TENIA TIERRAS INSTALADAS. ADEMAS, SE REEMPLAZO AISLADOR AVERIADO EN EL ALIMENTADOR 1401-08 QUE LLEVA EL 1346-05 | S22010500036 | New_Event | UG Cable Fault | Include | Include | Equipment | 482 | 2022-01-05 | 65070 | keep | 0 | Jan | 2022 | 0.044319 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2022-01-05 07:10 | 2022-01-05 11:40 | 1 | 004:30 | S | CABLE SOTERRADO AVERIADO | RECERRO 1401-8 Y DISPARO 0050 SE FUE A LOCKOUT DISPARO POR DIFERENCIAL SE ENCONTRO TRANSFORMADOR NO TENIA TIERRAS INSTALADAS | S22010500036 | New_Event | UG Cable Fault | Include | Include | Equipment | 270 | 2022-01-05 | 270 | keep | 0 | Jan | 2022 | 0.0001839 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-01-05 07:10 | 2022-01-05 11:40 | 1295 | 004:30 | S | CABLE SOTERRADO AVERIADO | RECERRO 1401-8 Y DISPARO 0050 SE FUE A LOCKOUT DISPARO POR DIFERENCIAL SE ENCONTRO TRANSFORMADOR NO TENIA TIERRAS INSTALADAS | S22010500036 | New_Event | UG Cable Fault | Include | Include | Equipment | 270 | 2022-01-05 | 349650 | keep | 0 | Jan | 2022 | 0.23815 | 0.00088202 | Sustained | FALSE | FALSE | Not_TMED_Event | 1295
MAYAGÃœEZ | 2022-01-05 07:15 | 2022-01-05 18:25 | 50 | 011:10 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M22010500002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 670 | 2022-01-05 | 33500 | keep | 0 | Jan | 2022 | 0.022817 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-05 07:23 | 2022-01-05 11:15 | 6 | 003:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22010500050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 232 | 2022-01-05 | 1392 | keep | 0 | Jan | 2022 | 0.00094808 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-01-05 07:33 | 2022-01-05 10:09 | 80 | 002:36 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M22010500004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-01-05 | 12480 | keep | 0 | Jan | 2022 | 0.0085001 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-01-05 07:33 | 2022-01-05 07:34 | 1494 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9101-02 SPARE LLEVANDO 9101-04 | B22010500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-05 | 1494 | keep | 0 | Jan | 2022 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
BAYAMON | 2022-01-05 07:34 | 2022-01-05 16:39 | 50 | 009:05 | P | DESGANCHE | 1 X 80 EN C/L | B22010500020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 545 | 2022-01-05 | 27250 | keep | 0 | Jan | 2022 | 0.01856 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-05 07:37 | 2022-01-05 17:21 | 102 | 009:44 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE INSTALO MACHETES QUE HABIAN SIDO ELIMINADOS | S2201050005 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 584 | 2022-01-05 | 59568 | keep | 0 | Jan | 2022 | 0.040571 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-01-05 07:42 | 2022-01-05 07:44 | 1494 | 000:02 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9101-02 SPARE LLEVANDO 9101-04 | B22010500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-05 | 2988 | keep | 0 | Jan | 2022 | 0.0020351 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
BAYAMON | 2022-01-05 07:50 | 2022-01-05 07:51 | 1264 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR 1904-07 LLEVANDO LA CARGA 1901-04 | S22010500000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-01-05 | 1264 | keep | 0 | Jan | 2022 | 0.0008609 | 0.0008609 | Momentary | FALSE | FALSE | Not_TMED_Event | 1264
PONCE | 2022-01-05 07:50 | 2022-01-05 09:39 | 50 | 001:49 | P | OTRAS CAUSAS | SE REALIZO TRANSPOSICION DE FASE EN 2 TRANSFORMADORES | P22010500006 | New_Event | Other Causes | Include | Include | Other | 109 | 2022-01-05 | 5450 | keep | 0 | Jan | 2022 | 0.003712 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-01-05 07:50 | 2022-01-05 12:50 | 60 | 005:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA SE CERRO CORTE DE LINEA | A22010500008 | New_Event | Wire Down | Include | Include | Equipment | 300 | 2022-01-05 | 18000 | keep | 0 | Jan | 2022 | 0.01226 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-01-05 07:51 | 2022-01-05 13:42 | 150 | 005:51 | P | DESCONECTIVO DEFECTUOSO | SE IDENTIFICO JUEGO DE MACHETES AVERIADOS | S22010500079 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 351 | 2022-01-05 | 52650 | keep | 0 | Jan | 2022 | 0.03586 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
GUAYAMA | 2022-01-05 07:58 | 2022-01-06 09:55 | 60 | 025:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE EVENTO DEL DIA 5 VERIFICADO EN OMS | P22040500084 | New_Event |  |  | Include | Wildlife | 1557 | 2022-01-05 | 93420 | keep | 0 | Jan | 2022 | 0.063628 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-01-05 08:00 | 2022-01-05 22:15 | 75 | 014:15 | P | ESTRUCTURA AVERIADA | 1 X 50 EN C/L. SE REEMPLAZARON DOS POSTES AVERIADOS | B22010500024 | New_Event | Defective Pole | Include | Include | Equipment | 855 | 2022-01-05 | 64125 | keep | 0 | Jan | 2022 | 0.043675 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-01-05 08:13 | 2022-01-05 10:24 | 10 | 002:11 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22010500026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-01-05 | 1310 | keep | 0 | Jan | 2022 | 0.00089224 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-05 08:25 | 2022-01-05 10:42 | 1 | 002:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22010500013 | New_Event | Bad Weather | Include | Include | Weather | 137 | 2022-01-05 | 137 | keep | 0 | Jan | 2022 | 9.331e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-01-05 08:25 | 2022-01-05 14:55 | 40 | 006:30 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C22010500044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 390 | 2022-01-05 | 15600 | keep | 0 | Jan | 2022 | 0.010625 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-01-05 08:37 | 2022-01-05 10:45 | 60 | 002:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | R22010500016 | New_Event |  |  | Include | Wildlife | 128 | 2022-01-05 | 7680 | keep | 0 | Jan | 2022 | 0.0052308 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-01-05 08:45 | 2022-01-05 08:47 | 723 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1711-02 LLEVANDO 1711-05. PUENTE ABIERTO LINEA A MACHETE EN RISER | B22010500000 | Additional_clients | Wire Down | Include | Include | Equipment | 2 | 2022-01-05 | 1446 | keep | 0 | Jan | 2022 | 0.00098486 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-01-05 08:45 | 2022-01-05 08:47 | 1976 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1711-02 LLEVANDO 1711-05. PUENTE ABIERTO LINEA A MACHETE EN RISER | B22010500000 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-01-05 | 3952 | keep | 0 | Jan | 2022 | 0.0026917 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2022-01-05 08:47 | 2022-01-05 12:31 | 300 | 003:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REMPLAZO PUENTE EN MACHETE DEL 13KV EN BTC | B22010500000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 224 | 2022-01-05 | 67200 | keep | 0 | Jan | 2022 | 0.04577 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-01-05 08:47 | 2022-01-05 08:48 | 1597 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22010500017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-05 | 1597 | keep | 0 | Jan | 2022 | 0.0010877 | 0.0010877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1597
CAGUAS | 2022-01-05 08:51 | 2022-01-05 12:15 | 100 | 003:24 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 65 EN CORTE DE LINEA NO CAUSA | C22010500057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 204 | 2022-01-05 | 20400 | keep | 0 | Jan | 2022 | 0.013894 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-01-05 08:54 | 2022-01-05 08:55 | 2107 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22010500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-05 | 2107 | keep | 0 | Jan | 2022 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
SAN JUAN | 2022-01-05 09:03 | 2022-01-05 09:04 | 1447 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1419-9 Y 12 | S22010500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-05 | 1447 | keep | 0 | Jan | 2022 | 0.00098555 | 0.00098555 | Momentary | FALSE | FALSE | Not_TMED_Event | 1447
SAN JUAN | 2022-01-05 09:03 | 2022-01-05 09:05 | 266 | 000:02 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1112-4 | S22010500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-05 | 532 | keep | 0 | Jan | 2022 | 0.00036234 | 0.00018117 | Momentary | FALSE | FALSE | Not_TMED_Event | 266
SAN JUAN | 2022-01-05 09:03 | 2022-01-05 09:05 | 73 | 000:02 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1112-4 | S22010500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-05 | 146 | keep | 0 | Jan | 2022 | 9.944e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
UTUADO | 2022-01-05 09:05 | 2022-01-05 16:08 | 6 | 007:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A22010500066 | New_Event | Cutout Failure | Include | Include | Equipment | 423 | 2022-01-05 | 2538 | keep | 0 | Jan | 2022 | 0.0017286 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-01-05 09:23 | 2022-01-05 09:24 | 1986 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22010500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-05 | 1986 | keep | 0 | Jan | 2022 | 0.0013527 | 0.0013527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1986
ARECIBO | 2022-01-05 09:23 | 2022-01-05 09:24 | 2231 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 14700 | A22010500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-05 | 2231 | keep | 0 | Jan | 2022 | 0.0015195 | 0.0015195 | Momentary | FALSE | FALSE | Not_TMED_Event | 2231
ARECIBO | 2022-01-05 09:23 | 2022-01-05 09:24 | 1923 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 14700 | A22010500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-05 | 1923 | keep | 0 | Jan | 2022 | 0.0013097 | 0.0013097 | Momentary | FALSE | FALSE | Not_TMED_Event | 1923
ARECIBO | 2022-01-05 09:23 | 2022-01-05 09:24 | 1066 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 14700 | A22010500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-05 | 1066 | keep | 0 | Jan | 2022 | 0.00072605 | 0.00072605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1066
ARECIBO | 2022-01-05 09:23 | 2022-01-05 09:24 | 141 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 14700 | A22010500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-05 | 141 | keep | 0 | Jan | 2022 | 9.6034e-05 | 9.6034e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 141
ARECIBO | 2022-01-05 09:23 | 2022-01-05 09:24 | 2107 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 14700 | A22010500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-05 | 2107 | keep | 0 | Jan | 2022 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
ARECIBO | 2022-01-05 09:23 | 2022-01-05 09:24 | 308 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 14700 | A22010500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-05 | 308 | keep | 0 | Jan | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
ARECIBO | 2022-01-05 09:23 | 2022-01-05 09:24 | 2697 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 14700 | A22010500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-05 | 2697 | keep | 0 | Jan | 2022 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
ARECIBO | 2022-01-05 09:23 | 2022-01-05 09:24 | 67 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 14700 | A22010500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-05 | 67 | keep | 0 | Jan | 2022 | 4.5633e-05 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
ARECIBO | 2022-01-05 09:24 | 2022-01-05 10:27 | 10 | 001:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN RISER MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22010500033 | New_Event | Bad Weather | Include | Include | Weather | 63 | 2022-01-05 | 630 | keep | 0 | Jan | 2022 | 0.00042909 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-05 09:34 | 2022-01-05 16:29 | 7 | 006:55 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE REALIZO DESGANCHE Y SE REPARO SECUNDARIA | B22010500035 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 415 | 2022-01-05 | 2905 | keep | 0 | Jan | 2022 | 0.0019786 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-01-05 09:36 | 2022-01-05 09:37 | 478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1705-01 QUE LLEVA 90% DEL 1705-03 | B22010500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-05 | 478 | keep | 0 | Jan | 2022 | 0.00032556 | 0.00032556 | Momentary | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2022-01-05 09:36 | 2022-01-05 09:37 | 854 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1705-01 QUE LLEVA 90% DEL 1705-03 | B22010500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-05 | 854 | keep | 0 | Jan | 2022 | 0.00058166 | 0.00058166 | Momentary | FALSE | FALSE | Not_TMED_Event | 854
YAUCO | 2022-01-05 09:36 | 2022-01-05 13:59 | 10 | 004:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BARRAS DE PEDESTAL SECUNDARIO | P22010500019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 263 | 2022-01-05 | 2630 | keep | 0 | Jan | 2022 | 0.0017913 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-01-05 09:37 | 2022-01-05 12:53 | 25 | 003:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C22010500080 | New_Event |  |  | Include | Wildlife | 196 | 2022-01-05 | 4900 | keep | 0 | Jan | 2022 | 0.0033374 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-01-05 09:40 | 2022-01-05 17:00 | 50 | 007:20 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR POSTE PARTIDO | M22010500015 | New_Event | Defective Pole | Include | Include | Equipment | 440 | 2022-01-05 | 22000 | keep | 0 | Jan | 2022 | 0.014984 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-05 09:41 | 2022-01-05 09:42 | 478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1705-01 QUE LLEVA 90% DEL 1705-03 | B22010500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-05 | 478 | keep | 0 | Jan | 2022 | 0.00032556 | 0.00032556 | Momentary | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2022-01-05 09:41 | 2022-01-05 09:42 | 854 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1705-01 QUE LLEVA 90% DEL 1705-03 | B22010500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-05 | 854 | keep | 0 | Jan | 2022 | 0.00058166 | 0.00058166 | Momentary | FALSE | FALSE | Not_TMED_Event | 854
FAJARDO | 2022-01-05 09:42 | 2022-01-05 14:20 | 10 | 004:38 | P | SECUNDARIA/ESTRUCTURA AVERIADA | 1 X 10 EN XMR REEMPLAZARON DOS POSTES SECUNDARIOS ROTOS | R22010500023 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 278 | 2022-01-05 | 2780 | keep | 0 | Jan | 2022 | 0.0018934 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-01-05 09:52 | 2022-01-05 14:47 | 15 | 004:55 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50KVA X 25KVA | C22010500088 | New_Event | Service Transformer Failure | Include | Include | Equipment | 295 | 2022-01-05 | 4425 | keep | 0 | Jan | 2022 | 0.0030138 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-01-05 10:03 | 2022-01-05 10:05 | 513 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO 1118-10 LLEVANDO 20% DEL 1111-01 | S22010500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-05 | 1026 | keep | 0 | Jan | 2022 | 0.0006988 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2022-01-05 10:03 | 2022-01-05 10:05 | 2782 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO LLEVA 20% DEL 1111-1 SE PROBO QUEDO EN SERVICIO | S22010500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-05 | 5564 | keep | 0 | Jan | 2022 | 0.0037896 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
PONCE | 2022-01-05 10:14 | 2022-01-05 15:06 | 14 | 004:52 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRE CAJA DE TRANSFORMADOR PARA CAMBIAR 2 POSTES SECUNDARIOS | P22010500033 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 292 | 2022-01-05 | 4088 | keep | 0 | Jan | 2022 | 0.0027843 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-01-05 10:19 | 2022-01-05 14:48 | 70 | 004:29 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | S22010500188 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 269 | 2022-01-05 | 18830 | keep | 0 | Jan | 2022 | 0.012825 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2022-01-05 10:27 | 2022-01-05 10:28 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P22010500025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-05 | 3114 | keep | 0 | Jan | 2022 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
ARECIBO | 2022-01-05 10:32 | 2022-01-05 14:08 | 200 | 003:36 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A22010500038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 216 | 2022-01-05 | 43200 | keep | 0 | Jan | 2022 | 0.029423 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-01-05 10:33 | 2022-01-05 10:35 | 1514 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR SCADA | B22010500048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-05 | 3028 | keep | 0 | Jan | 2022 | 0.0020624 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
AGUADILLA | 2022-01-05 10:35 | 2022-01-05 12:30 | 15 | 001:55 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON PROBLEMAS DE VOLTAJE DE 37.5 KVA X 37.5 KVA | M22010500018 | New_Event | Service Transformer Failure | Include | Include | Equipment | 115 | 2022-01-05 | 1725 | keep | 0 | Jan | 2022 | 0.0011749 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-01-05 10:37 | 2022-01-05 18:05 | 7 | 007:28 | P | ESTRUCTURA AVERIADA | ABRIO XMR PARA REMPLAZAR POSTE | C22010500103 | New_Event | Defective Pole | Include | Include | Equipment | 448 | 2022-01-05 | 3136 | keep | 0 | Jan | 2022 | 0.0021359 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-01-05 10:56 | 2022-01-05 13:08 | 50 | 002:12 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R22010500027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2022-01-05 | 6600 | keep | 0 | Jan | 2022 | 0.0044952 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-01-05 11:05 | 2022-01-05 17:20 | 15 | 006:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | M22010400109 | New_Event | Secondary Wire Down | Include | Include | Equipment | 375 | 2022-01-05 | 5625 | keep | 0 | Jan | 2022 | 0.0038312 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-01-05 11:09 | 2022-01-05 13:47 | 15 | 002:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22010500044 | New_Event | Bad Weather | Include | Include | Weather | 158 | 2022-01-05 | 2370 | keep | 0 | Jan | 2022 | 0.0016142 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-01-05 11:17 | 2022-01-05 14:50 | 5 | 003:33 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M22010500020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2022-01-05 | 1065 | keep | 0 | Jan | 2022 | 0.00072537 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-01-05 11:23 | 2022-01-05 20:31 | 25 | 009:08 | P | DESGANCHE | 1 X 40 EN C/L | C22010500106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 548 | 2022-01-05 | 13700 | keep | 0 | Jan | 2022 | 0.009331 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-01-05 11:28 | 2022-01-05 13:15 | 12 | 001:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22010500047 | New_Event | Bad Weather | Include | Include | Weather | 107 | 2022-01-05 | 1284 | keep | 0 | Jan | 2022 | 0.00087453 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-01-05 11:44 | 2022-01-05 14:31 | 1 | 002:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN C/L MAL TIEMPO | C22010500111 | New_Event | Bad Weather | Include | Include | Weather | 167 | 2022-01-05 | 167 | keep | 0 | Jan | 2022 | 0.00011374 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-01-05 11:45 | 2022-01-05 13:17 | 15 | 001:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR NEUTRAL PRIMARIO PARTIDO | M22010500021 | New_Event | Wire Down | Include | Include | Equipment | 92 | 2022-01-05 | 1380 | keep | 0 | Jan | 2022 | 0.00093991 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-01-05 11:48 | 2022-01-05 11:50 | 215 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22010500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-05 | 430 | keep | 0 | Jan | 2022 | 0.00029287 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2022-01-05 11:50 | 2022-01-05 16:04 | 60 | 004:14 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22010500068 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 254 | 2022-01-05 | 15240 | keep | 0 | Jan | 2022 | 0.01038 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-01-05 11:54 | 2022-01-05 13:57 | 100 | 002:03 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA POR DESGANCHE | P22010500022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2022-01-05 | 12300 | keep | 0 | Jan | 2022 | 0.0083775 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-01-05 12:04 | 2022-01-05 14:38 | 9 | 002:34 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN XMR DESGANCHO | R22010500030 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 154 | 2022-01-05 | 1386 | keep | 0 | Jan | 2022 | 0.000944 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-01-05 12:12 | 2022-01-05 12:13 | 51 | 000:01 | T | NO SE REPORTO CAUSA | CARGA POR 7902-03 | M22010500024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-05 | 51 | keep | 0 | Jan | 2022 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2022-01-05 12:12 | 2022-01-05 12:13 | 721 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 7902-02 | M22010500024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-05 | 721 | keep | 0 | Jan | 2022 | 0.00049107 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
MAYAGÃœEZ | 2022-01-05 12:25 | 2022-01-05 13:05 | 4 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | M22010500013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2022-01-05 | 160 | keep | 0 | Jan | 2022 | 0.00010898 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-01-05 12:42 | 2022-01-05 17:40 | 20 | 004:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ZAFADA | A22010500057 | New_Event | Wire Down | Include | Include | Equipment | 298 | 2022-01-05 | 5960 | keep | 0 | Jan | 2022 | 0.0040593 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-01-05 12:43 | 2022-01-05 13:41 | 10 | 000:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BARRAS SECUNDARIAS | A22010400066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 58 | 2022-01-05 | 580 | keep | 0 | Jan | 2022 | 0.00039504 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-01-05 13:02 | 2022-01-05 17:10 | 6 | 004:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | M22010500026 | New_Event | Bad Weather | Include | Include | Weather | 248 | 2022-01-05 | 1488 | keep | 0 | Jan | 2022 | 0.0010135 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-01-05 13:19 | 2022-01-12 13:42 | 40 | 168:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO/RETEZO LINEA PRIMARIA | S22010500154 | New_Event | Wire Down | Include | Include | Equipment | 10103 | 2022-01-05 | 404120 | keep | 0 | Jan | 2022 | 0.27524 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-01-05 13:25 | 2022-01-05 14:35 | 12 | 001:10 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5 KVA X 37.5 KVA CON ESCAPE DE ACEITE | M22010500027 | New_Event | Service Transformer Failure | Include | Include | Equipment | 70 | 2022-01-05 | 840 | keep | 0 | Jan | 2022 | 0.00057212 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-01-05 13:36 | 2022-01-05 20:05 | 150 | 006:29 | P | CABLE SOTERRADO AVERIADO | SE PASO 90% DE LA CARGA AL 1303-02 ABIERTO MACHETE CARR.176 ESQ. 845 Y SE CERRO N/O CONTRA 1303-2 CALLE VICTOR LABIOSA ESQ. 8176. SE DEJO SECCIONALIZADO TRAMO SOTERRADO DE VS-4 Y VS-5 QUE AFECTA ALUMBRADO Y EDIFICIO ANA G. MENDEZ MEDIANTE GOI SJ-220105-02 | S22010500036 | New_Event | UG Cable Fault | Include | Include | Equipment | 389 | 2022-01-05 | 58350 | keep | 0 | Jan | 2022 | 0.039742 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-01-05 13:38 | 2022-01-05 18:34 | 80 | 004:56 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22010500326 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 296 | 2022-01-05 | 23680 | keep | 0 | Jan | 2022 | 0.016128 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-01-05 13:41 | 2022-01-05 17:10 | 100 | 003:29 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | M22010500029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2022-01-05 | 20900 | keep | 0 | Jan | 2022 | 0.014235 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-01-05 13:42 | 2022-01-05 17:40 | 1264 | 003:58 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR 1904-07 QUE LLEVA LA CARGA DEL 1901-04 PARA REMPLAZAR JUEGO DE MACHETES AVERIADOS | S22010500079 | New_Event | Switch Failure | Include | Include | Equipment | 238 | 2022-01-05 | 300832 | keep | 0 | Jan | 2022 | 0.2049 | 0.0008609 | Sustained | FALSE | FALSE | Not_TMED_Event | 1264
SAN JUAN | 2022-01-05 13:49 | 2022-01-05 17:28 | 25 | 003:39 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER HACIA T-7 | S22010500334 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 219 | 2022-01-05 | 5475 | keep | 0 | Jan | 2022 | 0.003729 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-01-05 13:52 | 2022-01-05 14:52 | 1 | 001:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 15 EN CORTE DE LINEA @ SUB. BURGER KING Y 2 X 10 EN BANCO DE XMR CRUCE POR AVE | R22010500033 | New_Event |  |  | Include | Wildlife | 60 | 2022-01-05 | 60 | keep | 0 | Jan | 2022 | 4.0866e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-01-05 14:03 | 2022-01-05 17:15 | 50 | 003:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA POR CONTACTO DE AVE | P22010500056 | New_Event |  |  | Include | Wildlife | 192 | 2022-01-05 | 9600 | keep | 0 | Jan | 2022 | 0.0065385 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-05 14:13 | 2022-01-05 17:13 | 6 | 003:00 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22010500076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 180 | 2022-01-05 | 1080 | keep | 0 | Jan | 2022 | 0.00073558 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-01-05 14:24 | 2022-01-05 14:25 | 1712 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P22010500059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-05 | 1712 | keep | 0 | Jan | 2022 | 0.001166 | 0.001166 | Momentary | FALSE | FALSE | Not_TMED_Event | 1712
PONCE | 2022-01-05 14:24 | 2022-01-05 14:25 | 7 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 5005-03 CON CARGA 5010-04 | P22010500059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-05 | 7 | keep | 0 | Jan | 2022 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2022-01-05 14:49 | 2022-01-05 17:02 | 10 | 002:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO T-16 PARA REPARAR NEUTRAL Y BARRA SECUNDARIA | R22010500035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 133 | 2022-01-05 | 1330 | keep | 0 | Jan | 2022 | 0.00090586 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-05 15:45 | 2022-01-05 15:46 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22010500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-05 | 308 | keep | 0 | Jan | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
SAN JUAN | 2022-01-05 15:47 | 2022-01-05 19:37 | 25 | 003:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y SE REALIZO PODA | S22010500376 | New_Event | Vegetation Contact | Include | Include | Vegetation | 230 | 2022-01-05 | 5750 | keep | 0 | Jan | 2022 | 0.0039163 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-01-05 15:59 | 2022-01-05 16:36 | 317 | 000:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | AVE CRUZO LINEAS Y OCASIONO DISPARO DE ALTA DE XMR 1711-00. 80% DE SU CARGA POR EL 1716-03 | B22010500000 | New_Event |  |  | Include | Wildlife | 37 | 2022-01-05 | 11729 | keep | 0 | Jan | 2022 | 0.0079886 | 0.00021591 | Sustained | FALSE | FALSE | Not_TMED_Event | 317
BAYAMON | 2022-01-05 15:59 | 2022-01-05 16:31 | 1270 | 000:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO 1716-03 JUNTO A OPERACION DE LA 1711-00. AVE CRUZO LINEAS Y OCASIONO DISPARO DE ALTA DE XMR 1711-00. 80% DE SU CARGA POR EL 1716-03 | B22010500000 | New_Event |  |  | Include | Wildlife | 32 | 2022-01-05 | 40640 | keep | 0 | Jan | 2022 | 0.02768 | 0.00086499 | Sustained | FALSE | FALSE | Not_TMED_Event | 1270
BAYAMON | 2022-01-05 15:59 | 2022-01-05 16:36 | 723 | 000:37 | S | ANIMAL U OBJETO EXTRAÃ‘O | AVE CRUZO LINEAS Y OCASIONO DISPARO DE ALTA DE XMR 1711-00 | B22010500000 | New_Event |  |  | Include | Wildlife | 37 | 2022-01-05 | 26751 | keep | 0 | Jan | 2022 | 0.01822 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-01-05 15:59 | 2022-01-05 16:31 | 13 | 000:32 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO 1716-03 JUNTO A OPERACION DE LA 1711-00. AVE CRUZO LINEAS Y OCASIONO DISPARO DE ALTA DE XMR 1711-00 CARGA DEL 1711-03 POR 1716-03 | B22010500000 | New_Event |  |  | Include | Wildlife | 32 | 2022-01-05 | 416 | keep | 0 | Jan | 2022 | 0.00028334 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2022-01-05 15:59 | 2022-01-05 16:36 | 1976 | 000:37 | S | ANIMAL U OBJETO EXTRAÃ‘O | AVE CRUZO LINEAS Y OCASIONO DISPARO DE ALTA DE XMR 1711-00 CARGA 1711-05 POR 1711-02 | B22010500000 | New_Event |  |  | Include | Wildlife | 37 | 2022-01-05 | 73112 | keep | 0 | Jan | 2022 | 0.049796 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2022-01-05 15:59 | 2022-01-05 16:31 | 1812 | 000:32 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO 1716-03 JUNTO A OPERACION DE LA 1711-00. AVE CRUZO LINEAS Y OCASIONO DISPARO DE ALTA DE XMR 1711-00. LLEVA LA CARGA DEL 1711-03 Y 80% DEL 1711-01 | B22010500000 | New_Event |  |  | Include | Wildlife | 32 | 2022-01-05 | 57984 | keep | 0 | Jan | 2022 | 0.039493 | 0.0012341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1812
ARECIBO | 2022-01-05 16:21 | 2022-01-05 17:24 | 10 | 001:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A22010500075 | New_Event | Secondary Wire Down | Include | Include | Equipment | 63 | 2022-01-05 | 630 | keep | 0 | Jan | 2022 | 0.00042909 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-05 16:36 | 2022-01-05 18:21 | 50 | 001:45 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETES EN JARDINES DE CAPARRA | B22010500046 | New_Event | Switch Failure | Include | Include | Equipment | 105 | 2022-01-05 | 5250 | keep | 0 | Jan | 2022 | 0.0035758 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-01-05 16:42 | 2022-01-05 18:03 | 65 | 001:21 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L NO CAUSA | C22010500155 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2022-01-05 | 5265 | keep | 0 | Jan | 2022 | 0.003586 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
GUAYAMA | 2022-01-05 17:11 | 2022-01-05 19:52 | 50 | 002:41 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR ARBOL PARTIO POSTE PRIMARIO SE ABRIO PUENTES PRIMARIOS PARA SECCIONALIZAR AVERIA | P22010500070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-01-05 | 8050 | keep | 0 | Jan | 2022 | 0.0054828 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-01-05 17:14 | 2022-01-05 20:00 | 100 | 002:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22010500080 | New_Event | Bad Weather | Include | Include | Weather | 166 | 2022-01-05 | 16600 | keep | 0 | Jan | 2022 | 0.011306 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-01-05 17:15 | 2022-01-06 08:57 | 10 | 015:42 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA INDICA JOURNEYMAN NO IDENTIFICO CAUSA | M22010500062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 942 | 2022-01-05 | 9420 | keep | 0 | Jan | 2022 | 0.0064159 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-01-05 18:16 | 2022-01-05 19:55 | 50 | 001:39 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R22010500041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2022-01-05 | 4950 | keep | 0 | Jan | 2022 | 0.0033714 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-05 18:21 | 2022-01-05 19:46 | 50 | 001:25 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22010500138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 85 | 2022-01-05 | 4250 | keep | 0 | Jan | 2022 | 0.0028947 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-01-05 18:25 | 2022-01-05 21:39 | 100 | 003:14 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P22010500081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2022-01-05 | 19400 | keep | 0 | Jan | 2022 | 0.013213 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-01-05 18:39 | 2022-01-05 23:15 | 50 | 004:36 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REQUIERE DESGANCHE | A22010500087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 276 | 2022-01-05 | 13800 | keep | 0 | Jan | 2022 | 0.0093991 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-01-05 18:43 | 2022-01-06 09:13 | 100 | 014:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 Y 1 X 25 EN CORTES DE LINEA SE REEMPLAZO | C22010500016 | New_Event | Cutout Failure | Include | Include | Equipment | 870 | 2022-01-05 | 87000 | keep | 0 | Jan | 2022 | 0.059255 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-01-05 18:45 | 2022-01-05 18:46 | 3511 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22010500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-05 | 3511 | keep | 0 | Jan | 2022 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
CANOVANAS | 2022-01-05 19:03 | 2022-01-06 00:46 | 6 | 005:43 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR DE 37.5 KVA X 37.5 KVA | R22010500044 | New_Event | Service Transformer Failure | Include | Include | Equipment | 343 | 2022-01-05 | 2058 | keep | 0 | Jan | 2022 | 0.0014017 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-01-05 19:11 | 2022-01-06 11:38 | 4 | 016:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIAS | R22010500045 | New_Event | Bad Weather | Include | Include | Weather | 987 | 2022-01-05 | 3948 | keep | 0 | Jan | 2022 | 0.002689 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2022-01-05 19:50 | 2022-01-06 00:53 | 75 | 005:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L. SE REEMPLAZO CAJA AVERIADA | B22010500140 | New_Event | Cutout Failure | Include | Include | Equipment | 303 | 2022-01-05 | 22725 | keep | 0 | Jan | 2022 | 0.015478 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2022-01-05 19:51 | 2022-01-05 22:09 | 20 | 002:18 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22010500095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2022-01-05 | 2760 | keep | 0 | Jan | 2022 | 0.0018798 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2022-01-05 19:52 | 2022-01-06 13:30 | 1 | 017:38 | P | DESGANCHE | SE CAMBIO POSTE Y SE CERRARON PUENTES | P22010500005 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1058 | 2022-01-05 | 1058 | keep | 0 | Jan | 2022 | 0.0007206 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-01-05 20:00 | 2022-01-05 20:01 | 2107 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22010500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-05 | 2107 | keep | 0 | Jan | 2022 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
ARECIBO | 2022-01-05 20:03 | 2022-01-05 21:01 | 20 | 000:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | A22010500097 | New_Event |  |  | Include | Wildlife | 58 | 2022-01-05 | 1160 | keep | 0 | Jan | 2022 | 0.00079007 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-01-05 20:04 | 2022-01-05 20:52 | 30 | 000:48 | P | NO SE REPORTO CAUSA | SE SUBIO FUSIBLE ABIERTO NO FUNDIO | R22010500047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 48 | 2022-01-05 | 1440 | keep | 0 | Jan | 2022 | 0.00098078 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-01-05 20:13 | 2022-01-05 20:14 | 5809 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22010500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-05 | 5809 | keep | 0 | Jan | 2022 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
BAYAMON | 2022-01-05 20:14 | 2022-01-05 22:03 | 60 | 001:49 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L | B22010500161 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 109 | 2022-01-05 | 6540 | keep | 0 | Jan | 2022 | 0.0044544 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-01-05 20:17 | 2022-01-05 20:18 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22010500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-05 | 1746 | keep | 0 | Jan | 2022 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
SAN JUAN | 2022-01-05 20:37 | 2022-01-05 20:38 | 234 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | R22010500000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-01-05 | 234 | keep | 0 | Jan | 2022 | 0.00015938 | 0.00015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 234
SAN JUAN | 2022-01-05 20:37 | 2022-01-05 20:38 | 2179 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22010500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-05 | 2179 | keep | 0 | Jan | 2022 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
SAN JUAN | 2022-01-05 20:37 | 2022-01-05 21:40 | 3046 | 001:03 | T | DESCONECTIVO DEFECTUOSO | MACHETE QUEMADO DEL 1618-03 | R22010500116 | New_Event | Switch Failure | Include | Include | Equipment | 63 | 2022-01-05 | 191898 | keep | 0 | Jan | 2022 | 0.1307 | 0.0020746 | Sustained | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2022-01-05 20:38 | 2022-01-06 01:50 | 117 | 005:12 | P | DESCONECTIVO DEFECTUOSO | REMPLAZO MACHETE QUEMADO | R22010500141 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 312 | 2022-01-05 | 36504 | keep | 0 | Jan | 2022 | 0.024863 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
ARECIBO | 2022-01-05 21:33 | 2022-01-05 22:36 | 150 | 001:03 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22010500098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2022-01-05 | 9450 | keep | 0 | Jan | 2022 | 0.0064364 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2022-01-05 22:35 | 2022-01-05 22:58 | 10 | 000:23 | P | TRANSFORMADOR AVERIADO | 1 X 25 EN TRANSFORMADOR BUSHING SECUNDARIO DEL TRANSFORMADOR AVERIADO SE AJUSTO PERO HAY QUE REEMPLAZAR TRANSFORMADOR | M22010500072 | New_Event | Service Transformer Failure | Include | Include | Equipment | 23 | 2022-01-05 | 230 | keep | 0 | Jan | 2022 | 0.00015665 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-01-05 23:15 | 2022-01-05 23:17 | 2053 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | R22010500146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-05 | 4106 | keep | 0 | Jan | 2022 | 0.0027966 | 0.0013983 | Momentary | FALSE | FALSE | Not_TMED_Event | 2053
SAN JUAN | 2022-01-06 00:11 | 2022-01-06 00:12 | 382 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1620-04 LLEVANDO LA CARGA DEL 1620-01 Y 95% DEL 1336-10 | S22010600001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-06 | 382 | keep | 0 | Jan | 2022 | 0.00026018 | 0.00026018 | Momentary | FALSE | FALSE | Not_TMED_Event | 382
SAN JUAN | 2022-01-06 00:11 | 2022-01-06 00:12 | 36 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1620-04 LLEVANDO LA CARGA DEL 1620-01 Y 95% DEL 1336-10 | S22010600001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-06 | 36 | keep | 0 | Jan | 2022 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-01-06 00:11 | 2022-01-06 00:12 | 172 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO, LLEVANDO LA CARGA DEL 1620-01 Y 95% DEL 1336-10 | S22010600001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-06 | 172 | keep | 0 | Jan | 2022 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
MAYAGÃœEZ | 2022-01-06 00:35 | 2022-01-06 00:36 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22010600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-06 | 1097 | keep | 0 | Jan | 2022 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
HUMACAO | 2022-01-06 00:55 | 2022-01-06 00:56 | 2354 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE | C22010600000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-01-06 | 2354 | keep | 0 | Jan | 2022 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
HUMACAO | 2022-01-06 00:56 | 2022-01-06 13:32 | 40 | 012:36 | P | CABLE SOTERRADO AVERIADO | 1 X 80 EN SU2 AVERIA DEL SU6 AL T4 SE CERRO N/O EN T1 | C22010600025 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 756 | 2022-01-06 | 30240 | keep | 0 | Jan | 2022 | 0.020596 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-01-06 01:11 | 2022-01-06 11:52 | 20 | 010:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REMPLAZO SECUNDARIA Y DESGANCHE | S22010600002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 641 | 2022-01-06 | 12820 | keep | 0 | Jan | 2022 | 0.0087316 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-01-06 04:30 | 2022-01-06 10:08 | 100 | 005:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN RISER ROEDOR CRUZO LINEAS | M22010600007 | New_Event |  |  | Include | Wildlife | 338 | 2022-01-06 | 33800 | keep | 0 | Jan | 2022 | 0.023021 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-01-06 04:53 | 2022-01-06 04:54 | 4641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22010600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-06 | 4641 | keep | 0 | Jan | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
GUAYAMA | 2022-01-06 05:13 | 2022-01-06 05:14 | 1457 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22010600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-06 | 1457 | keep | 0 | Jan | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
PONCE | 2022-01-06 05:29 | 2022-01-06 08:29 | 155 | 003:00 | P | DESGANCHE | 3 X 100 EN CORTE DE LINEA POR DESGANCHE | P22010600003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2022-01-06 | 27900 | keep | 0 | Jan | 2022 | 0.019003 | 0.00010557 | Sustained | FALSE | FALSE | Not_TMED_Event | 155
SAN JUAN | 2022-01-06 06:27 | 2022-01-06 06:28 | 1447 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1419-9 Y 12 | S22010600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-06 | 1447 | keep | 0 | Jan | 2022 | 0.00098555 | 0.00098555 | Momentary | FALSE | FALSE | Not_TMED_Event | 1447
SAN JUAN | 2022-01-06 06:27 | 2022-01-06 06:28 | 266 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1112-04 | S22010600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-06 | 266 | keep | 0 | Jan | 2022 | 0.00018117 | 0.00018117 | Momentary | FALSE | FALSE | Not_TMED_Event | 266
SAN JUAN | 2022-01-06 06:27 | 2022-01-06 06:28 | 73 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1112-04 | S22010600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-06 | 73 | keep | 0 | Jan | 2022 | 4.972e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
MAYAGÃœEZ | 2022-01-06 06:55 | 2022-01-06 10:06 | 80 | 003:11 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA INDICA JOURNEYMAN REQUIERE DESGANCHE | M22010600009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2022-01-06 | 15280 | keep | 0 | Jan | 2022 | 0.010407 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-01-06 07:23 | 2022-01-06 11:01 | 70 | 003:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 200 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | S22010600003 | New_Event | Cutout Failure | Include | Include | Equipment | 218 | 2022-01-06 | 15260 | keep | 0 | Jan | 2022 | 0.010394 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-01-06 07:51 | 2022-01-06 13:13 | 30 | 005:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | M22010600011 | New_Event | Wire Down | Include | Include | Equipment | 322 | 2022-01-06 | 9660 | keep | 0 | Jan | 2022 | 0.0065794 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-01-06 08:01 | 2022-01-06 14:13 | 85 | 006:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 40 EN C/L VEHICULO IMPACTO POSTE | C22010600033 | New_Event |  |  | Include | Wildlife | 372 | 2022-01-06 | 31620 | keep | 0 | Jan | 2022 | 0.021536 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
BAYAMON | 2022-01-06 08:23 | 2022-01-06 09:58 | 20 | 001:35 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22010600011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 95 | 2022-01-06 | 1900 | keep | 0 | Jan | 2022 | 0.0012941 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-01-06 08:30 | 2022-01-06 10:11 | 70 | 001:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINE CRUCE CON AVE | R22010600005 | New_Event |  |  | Include | Wildlife | 101 | 2022-01-06 | 7070 | keep | 0 | Jan | 2022 | 0.0048153 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2022-01-06 08:35 | 2022-01-06 11:05 | 100 | 002:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIAS | C22010600003 | New_Event | Bad Weather | Include | Include | Weather | 150 | 2022-01-06 | 15000 | keep | 0 | Jan | 2022 | 0.010216 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-01-06 08:35 | 2022-01-06 10:08 | 90 | 001:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIAS | C22010600002 | New_Event | Bad Weather | Include | Include | Weather | 93 | 2022-01-06 | 8370 | keep | 0 | Jan | 2022 | 0.0057008 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CAGUAS | 2022-01-06 08:51 | 2022-01-06 11:15 | 39 | 002:24 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | C22010600005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2022-01-06 | 5616 | keep | 0 | Jan | 2022 | 0.003825 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
BAYAMON | 2022-01-06 09:03 | 2022-01-06 09:45 | 12 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | S22010500139 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2022-01-06 | 504 | keep | 0 | Jan | 2022 | 0.00034327 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-01-06 09:05 | 2022-01-06 09:30 | 15 | 000:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | M22010500034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 25 | 2022-01-06 | 375 | keep | 0 | Jan | 2022 | 0.00025541 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-01-06 09:10 | 2022-01-06 10:25 | 203 | 001:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 Y 1 X 40 EN CORTES DE LINEA CRUCE CON AVE | R22010600006 | New_Event |  |  | Include | Wildlife | 75 | 2022-01-06 | 15225 | keep | 0 | Jan | 2022 | 0.01037 | 0.00013826 | Sustained | FALSE | FALSE | Not_TMED_Event | 203
ARECIBO | 2022-01-06 09:12 | 2022-01-06 09:35 | 8 | 000:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BARRAS SECUNDARIAS | A22010600001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 23 | 2022-01-06 | 184 | keep | 0 | Jan | 2022 | 0.00012532 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-01-06 09:18 | 2022-01-06 09:19 | 3005 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C22010600006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-06 | 3005 | keep | 0 | Jan | 2022 | 0.0020467 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
CAGUAS | 2022-01-06 09:19 | 2022-01-06 10:16 | 1701 | 000:57 | P | NO SE REPORTO CAUSA | SE CERRO PBD LOCALMENTE | C22010600006 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 57 | 2022-01-06 | 96957 | keep | 0 | Jan | 2022 | 0.066037 | 0.0011585 | Sustained | FALSE | FALSE | Not_TMED_Event | 1701
AGUADILLA | 2022-01-06 09:21 | 2022-01-06 12:00 | 15 | 002:39 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON BUSHING PRIMARIO PARTIDO 37.5 KVA X 37.5 KVA | M22010600015 | New_Event | Service Transformer Failure | Include | Include | Equipment | 159 | 2022-01-06 | 2385 | keep | 0 | Jan | 2022 | 0.0016244 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-01-06 09:23 | 2022-01-06 16:06 | 7 | 006:43 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN XMR SE REALIZO DESGANCHE | B22010500139 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 403 | 2022-01-06 | 2821 | keep | 0 | Jan | 2022 | 0.0019214 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-01-06 09:34 | 2022-01-06 09:35 | 2107 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22010600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-06 | 2107 | keep | 0 | Jan | 2022 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
VEGA BAJA | 2022-01-06 09:36 | 2022-01-06 10:12 | 10 | 000:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTE SECUNDARIO | B22010500137 | New_Event | Secondary Wire Down | Include | Include | Equipment | 36 | 2022-01-06 | 360 | keep | 0 | Jan | 2022 | 0.00024519 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-01-06 09:52 | 2022-01-06 12:21 | 120 | 002:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA | R22010600009 | New_Event | Cutout Failure | Include | Include | Equipment | 149 | 2022-01-06 | 17880 | keep | 0 | Jan | 2022 | 0.012178 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2022-01-06 09:52 | 2022-01-06 11:42 | 100 | 001:50 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA INDICA JOURNEYMAN QUE REQUIERE DESGANCHE | M22010600016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2022-01-06 | 11000 | keep | 0 | Jan | 2022 | 0.007492 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-01-06 10:14 | 2022-01-06 11:05 | 33 | 000:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA LLUVIAS | R22010600011 | New_Event | Bad Weather | Include | Include | Weather | 51 | 2022-01-06 | 1683 | keep | 0 | Jan | 2022 | 0.0011463 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
BAYAMON | 2022-01-06 10:29 | 2022-01-06 12:19 | 6 | 001:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 12 EN TRANSFORMADOR PERSONA TRABAJANDO EN BASE CONTADOR CRUZO LINEAS | B22010600020 | New_Event |  |  | Include | Wildlife | 110 | 2022-01-06 | 660 | keep | 0 | Jan | 2022 | 0.00044952 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-01-06 10:50 | 2022-01-06 15:40 | 10 | 004:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE LINEA A CAJA DE TRANSFORMADOR | M22010600018 | New_Event | Wire Down | Include | Include | Equipment | 290 | 2022-01-06 | 2900 | keep | 0 | Jan | 2022 | 0.0019752 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-01-06 11:20 | 2022-01-06 14:59 | 12 | 003:39 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 15 KVA POR UNO DE 37.5 KVA | A22010600004 | New_Event | Service Transformer Failure | Include | Include | Equipment | 219 | 2022-01-06 | 2628 | keep | 0 | Jan | 2022 | 0.0017899 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-01-06 12:26 | 2022-01-06 14:55 | 28 | 002:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | R22010600019 | New_Event |  |  | Include | Wildlife | 149 | 2022-01-06 | 4172 | keep | 0 | Jan | 2022 | 0.0028415 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
SAN JUAN | 2022-01-06 12:39 | 2022-01-06 12:57 | 200 | 000:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA | R22010600021 | New_Event | Cutout Failure | Include | Include | Equipment | 18 | 2022-01-06 | 3600 | keep | 0 | Jan | 2022 | 0.0024519 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-01-06 12:40 | 2022-01-06 14:48 | 25 | 002:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE CERRO C/L | B22010600030 | New_Event | Wire Down | Include | Include | Equipment | 128 | 2022-01-06 | 3200 | keep | 0 | Jan | 2022 | 0.0021795 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-01-06 12:41 | 2022-01-06 13:40 | 12 | 000:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22010600007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 59 | 2022-01-06 | 708 | keep | 0 | Jan | 2022 | 0.00048222 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-01-06 12:46 | 2022-01-06 12:48 | 3957 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO | S22010600021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-06 | 7914 | keep | 0 | Jan | 2022 | 0.0053902 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
GUAYAMA | 2022-01-06 12:58 | 2022-01-06 12:59 | 464 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22010500020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-06 | 464 | keep | 0 | Jan | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
BAYAMON | 2022-01-06 13:01 | 2022-01-06 15:35 | 35 | 002:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L 1 X 10 EN XMR SE RETIRO GLOBO | B22010600032 | New_Event |  |  | Include | Wildlife | 154 | 2022-01-06 | 5390 | keep | 0 | Jan | 2022 | 0.0036711 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2022-01-06 13:55 | 2022-01-06 17:45 | 100 | 003:50 | P | CABLE SOTERRADO AVERIADO | 2 X 65 EN RISER CABLE SOTERRADO AVERIADO SE ENERGIZO POR CIRCUITO ALTERNO | A22010600010 | New_Event | UG Cable Fault | Include | Include | Equipment | 230 | 2022-01-06 | 23000 | keep | 0 | Jan | 2022 | 0.015665 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-01-06 14:17 | 2022-01-06 15:30 | 20 | 001:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN RISER AVE CRUZO FASES | M22010600027 | New_Event |  |  | Include | Wildlife | 73 | 2022-01-06 | 1460 | keep | 0 | Jan | 2022 | 0.0009944 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-01-06 14:30 | 2022-01-07 10:56 | 10 | 020:26 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22010600035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1226 | 2022-01-06 | 12260 | keep | 0 | Jan | 2022 | 0.0083502 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-01-06 14:32 | 2022-01-06 16:13 | 20 | 001:41 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S22010600026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 101 | 2022-01-06 | 2020 | keep | 0 | Jan | 2022 | 0.0013758 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-01-06 14:42 | 2022-01-06 17:01 | 12 | 002:19 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFOMADOR PARA REPARAR SECUNDARIA. CAUSA DESGANCHE | S22010600028 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 139 | 2022-01-06 | 1668 | keep | 0 | Jan | 2022 | 0.0011361 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-01-06 15:06 | 2022-01-06 17:02 | 40 | 001:56 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S22010600035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2022-01-06 | 4640 | keep | 0 | Jan | 2022 | 0.0031603 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-01-06 15:15 | 2022-01-06 15:16 | 1339 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22010600030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-06 | 1339 | keep | 0 | Jan | 2022 | 0.00091199 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
SAN JUAN | 2022-01-06 15:47 | 2022-01-06 15:48 | 533 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-15 QUE LLEVA EL 30% DEL 1346-02 | S22010600040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-06 | 533 | keep | 0 | Jan | 2022 | 0.00036302 | 0.00036302 | Momentary | FALSE | FALSE | Not_TMED_Event | 533
BAYAMON | 2022-01-06 15:47 | 2022-01-06 15:48 | 1802 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-15 QUE LLEVA EL 30% DEL 1346-02 | S22010600040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-06 | 1802 | keep | 0 | Jan | 2022 | 0.0012273 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
SAN JUAN | 2022-01-06 16:08 | 2022-01-06 18:06 | 1 | 001:58 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 50 EN CORTE DE LINEA Y SE REPARO TERMINACION EN RISER | S22010600042 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 118 | 2022-01-06 | 118 | keep | 0 | Jan | 2022 | 8.0369e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-01-06 16:26 | 2022-01-06 16:27 | 281 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22010600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-06 | 281 | keep | 0 | Jan | 2022 | 0.00019139 | 0.00019139 | Momentary | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2022-01-06 16:26 | 2022-01-06 16:27 | 1252 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22010600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-06 | 1252 | keep | 0 | Jan | 2022 | 0.00085273 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2022-01-06 16:26 | 2022-01-06 16:27 | 595 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22010600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-06 | 595 | keep | 0 | Jan | 2022 | 0.00040525 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
MAYAGÃœEZ | 2022-01-06 16:26 | 2022-01-06 16:27 | 51 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22010600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-06 | 51 | keep | 0 | Jan | 2022 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2022-01-06 16:26 | 2022-01-06 16:27 | 721 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22010600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-06 | 721 | keep | 0 | Jan | 2022 | 0.00049107 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2022-01-06 16:26 | 2022-01-06 16:27 | 1382 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | A22010600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-06 | 1382 | keep | 0 | Jan | 2022 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2022-01-06 16:26 | 2022-01-06 16:27 | 654 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | A22010600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-06 | 654 | keep | 0 | Jan | 2022 | 0.00044544 | 0.00044544 | Momentary | FALSE | FALSE | Not_TMED_Event | 654
CAGUAS | 2022-01-06 17:15 | 2022-01-06 17:16 | 4390 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9300 | C22010600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-06 | 4390 | keep | 0 | Jan | 2022 | 0.00299 | 0.00299 | Momentary | FALSE | FALSE | Not_TMED_Event | 4390
CAGUAS | 2022-01-06 17:15 | 2022-01-06 17:16 | 2092 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9300 | C22010600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-06 | 2092 | keep | 0 | Jan | 2022 | 0.0014249 | 0.0014249 | Momentary | FALSE | FALSE | Not_TMED_Event | 2092
CAGUAS | 2022-01-06 17:15 | 2022-01-06 17:16 | 540 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9300 | C22010600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-06 | 540 | keep | 0 | Jan | 2022 | 0.00036779 | 0.00036779 | Momentary | FALSE | FALSE | Not_TMED_Event | 540
CAGUAS | 2022-01-06 17:15 | 2022-01-06 17:16 | 131 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9300 | C22010600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-06 | 131 | keep | 0 | Jan | 2022 | 8.9224e-05 | 8.9224e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 131
CAGUAS | 2022-01-06 17:15 | 2022-01-06 17:16 | 2281 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9300 | C22010600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-06 | 2281 | keep | 0 | Jan | 2022 | 0.0015536 | 0.0015536 | Momentary | FALSE | FALSE | Not_TMED_Event | 2281
CAGUAS | 2022-01-06 17:15 | 2022-01-06 17:16 | 1569 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9300 | C22010600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-06 | 1569 | keep | 0 | Jan | 2022 | 0.0010686 | 0.0010686 | Momentary | FALSE | FALSE | Not_TMED_Event | 1569
CAGUAS | 2022-01-06 17:15 | 2022-01-06 17:16 | 2417 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9300 | C22010600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-06 | 2417 | keep | 0 | Jan | 2022 | 0.0016462 | 0.0016462 | Momentary | FALSE | FALSE | Not_TMED_Event | 2417
UTUADO | 2022-01-06 18:01 | 2022-01-06 19:52 | 50 | 001:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22010600018 | New_Event | Bad Weather | Include | Include | Weather | 111 | 2022-01-06 | 5550 | keep | 0 | Jan | 2022 | 0.0037801 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-06 18:45 | 2022-01-06 19:05 | 12 | 000:20 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA CRUZADA POR DESGANCHE | S22010600044 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 20 | 2022-01-06 | 240 | keep | 0 | Jan | 2022 | 0.00016346 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-01-06 19:50 | 2022-01-07 11:23 | 4 | 015:33 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA Y SE REPARO NEUTRAL | C22010600049 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 933 | 2022-01-06 | 3732 | keep | 0 | Jan | 2022 | 0.0025418 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-01-06 19:52 | 2022-01-07 10:22 | 200 | 014:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | M22010600039 | New_Event | Cutout Failure | Include | Include | Equipment | 870 | 2022-01-06 | 174000 | keep | 0 | Jan | 2022 | 0.11851 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-01-06 20:29 | 2022-01-06 22:22 | 40 | 001:53 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22010600043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 113 | 2022-01-06 | 4520 | keep | 0 | Jan | 2022 | 0.0030786 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-01-06 20:40 | 2022-01-07 00:58 | 120 | 004:18 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE | S22010600060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 258 | 2022-01-06 | 30960 | keep | 0 | Jan | 2022 | 0.021087 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2022-01-06 21:16 | 2022-01-06 21:17 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22010600047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-06 | 1097 | keep | 0 | Jan | 2022 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
SAN JUAN | 2022-01-06 21:19 | 2022-01-07 05:01 | 80 | 007:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN C/L REPARO CONDUCTOR AVERIADO | R22010600026 | New_Event | Wire Down | Include | Include | Equipment | 462 | 2022-01-06 | 36960 | keep | 0 | Jan | 2022 | 0.025173 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-01-06 21:19 | 2022-01-06 22:12 | 12 | 000:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR POR PORTAFUSIBLE QUEMADO | A22010600024 | New_Event | Cutout Failure | Include | Include | Equipment | 53 | 2022-01-06 | 636 | keep | 0 | Jan | 2022 | 0.00043318 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-01-06 21:38 | 2022-01-06 21:43 | 425 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10700 | B22010600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-01-06 | 2125 | keep | 0 | Jan | 2022 | 0.0014473 | 0.00028947 | Momentary | FALSE | FALSE | Not_TMED_Event | 425
MAYAGÃœEZ | 2022-01-06 22:17 | 2022-01-07 02:35 | 300 | 004:18 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22010600067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 258 | 2022-01-06 | 77400 | keep | 0 | Jan | 2022 | 0.052717 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-01-06 23:46 | 2022-01-07 02:58 | 2000 | 003:12 | P | NO SE REPORTO CAUSA | DISPARO CARGA POR 1619-02 SE CERRO INTERRUPTOR PERO NO ASUMIO CARGA. SE PATRULLO NO SE ENCONTRO NADA. SE ABRIO Y SE CERRO INTERRUPTOR APARENTA QUE EL INTERRUPTOR NO CERRO CORRECTAMENTE EN LA OPERACION DEL 6-ENE-22 A LAS 23:46 @ 23:47 | R22010600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 192 | 2022-01-06 | 384000 | keep | 0 | Jan | 2022 | 0.26154 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
SAN JUAN | 2022-01-07 01:16 | 2022-01-07 01:17 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1206-03 LLEVANDO LA CARGA DEL 1204-05 | S22010700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-07 | 10211 | keep | 0 | Jan | 2022 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2022-01-07 01:16 | 2022-01-07 01:17 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1206-03 LLEVANDO LA CARGA DEL 1204-05 | S22010700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-07 | 4133 | keep | 0 | Jan | 2022 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
CAGUAS | 2022-01-07 02:10 | 2022-01-07 08:33 | 316 | 006:23 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO | C22010700001 | New_Event | Bad Weather | Include | Include | Weather | 383 | 2022-01-07 | 121028 | keep | 0 | Jan | 2022 | 0.082432 | 0.00021523 | Sustained | FALSE | FALSE | Not_TMED_Event | 316
CAGUAS | 2022-01-07 02:19 | 2022-01-07 10:04 | 512 | 007:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C22010700004 | New_Event | Bad Weather | Include | Include | Weather | 465 | 2022-01-07 | 238080 | keep | 0 | Jan | 2022 | 0.16216 | 0.00034872 | Sustained | FALSE | FALSE | Not_TMED_Event | 512
GUAYAMA | 2022-01-07 02:28 | 2022-01-07 09:14 | 20 | 006:46 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO AISLADOR AVERIADO | P22010700003 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 406 | 2022-01-07 | 8120 | keep | 0 | Jan | 2022 | 0.0055305 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-01-07 03:20 | 2022-01-07 10:42 | 132 | 007:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA AVERIADA | C22010700008 | New_Event | Cutout Failure | Include | Include | Equipment | 442 | 2022-01-07 | 58344 | keep | 0 | Jan | 2022 | 0.039738 | 8.9905e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 132
AGUADILLA | 2022-01-07 03:25 | 2022-01-07 14:16 | 30 | 010:51 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22010700002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 651 | 2022-01-07 | 19530 | keep | 0 | Jan | 2022 | 0.013302 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-01-07 03:25 | 2022-01-07 03:26 | 1494 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | B22010700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-07 | 1494 | keep | 0 | Jan | 2022 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
VEGA BAJA | 2022-01-07 03:28 | 2022-01-07 03:29 | 1494 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | B22010700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-07 | 1494 | keep | 0 | Jan | 2022 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
CAGUAS | 2022-01-07 04:06 | 2022-01-07 19:30 | 100 | 015:24 | P | DESGANCHE | 2 X 80 EN C/L | C22010700010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 924 | 2022-01-07 | 92400 | keep | 0 | Jan | 2022 | 0.062933 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-01-07 04:27 | 2022-01-07 09:12 | 167 | 004:45 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C22010700013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 285 | 2022-01-07 | 47595 | keep | 0 | Jan | 2022 | 0.032417 | 0.00011374 | Sustained | FALSE | FALSE | Not_TMED_Event | 167
VEGA BAJA | 2022-01-07 04:33 | 2022-01-07 04:34 | 1494 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | B22010700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-07 | 1494 | keep | 0 | Jan | 2022 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
AGUADILLA | 2022-01-07 05:07 | 2022-01-07 05:08 | 558 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22010700003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-07 | 558 | keep | 0 | Jan | 2022 | 0.00038005 | 0.00038005 | Momentary | FALSE | FALSE | Not_TMED_Event | 558
VEGA BAJA | 2022-01-07 05:12 | 2022-01-07 05:13 | 1494 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | B22010700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-07 | 1494 | keep | 0 | Jan | 2022 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
CANOVANAS | 2022-01-07 05:24 | 2022-01-07 09:30 | 10 | 004:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO TRONCAL SECUNDARIO PARTIDO | R22010700057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 246 | 2022-01-07 | 2460 | keep | 0 | Jan | 2022 | 0.0016755 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-01-07 05:30 | 2022-01-07 09:27 | 30 | 003:57 | P | NO SE REPORTO CAUSA | 1 X 50 EN AEREO PROVICIONAL | S22010700010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 237 | 2022-01-07 | 7110 | keep | 0 | Jan | 2022 | 0.0048426 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-01-07 05:37 | 2022-01-07 05:39 | 3630 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR | M22010700000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2022-01-07 | 7260 | keep | 0 | Jan | 2022 | 0.0049448 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2022-01-07 05:39 | 2022-01-07 11:42 | 150 | 006:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR FUERTES VIENTOS | M22010700015 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 363 | 2022-01-07 | 54450 | keep | 0 | Jan | 2022 | 0.037086 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-01-07 05:40 | 2022-01-07 11:05 | 40 | 005:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1SMU20 X 40 EN SU-2 Y SE TRANSPOSICIONO FASE EN EL SU-2 | R22010600058 | New_Event | Cutout Failure | Include | Include | Equipment | 325 | 2022-01-07 | 13000 | keep | 0 | Jan | 2022 | 0.0088542 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-01-07 05:41 | 2022-01-07 05:42 | 558 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22010700005 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-07 | 558 | keep | 0 | Jan | 2022 | 0.00038005 | 0.00038005 | Momentary | FALSE | FALSE | Not_TMED_Event | 558
PONCE | 2022-01-07 06:28 | 2022-01-07 08:45 | 12 | 002:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | P22010700007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 137 | 2022-01-07 | 1644 | keep | 0 | Jan | 2022 | 0.0011197 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-01-07 06:46 | 2022-01-07 08:49 | 30 | 002:03 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P22010700008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 123 | 2022-01-07 | 3690 | keep | 0 | Jan | 2022 | 0.0025132 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-01-07 06:57 | 2022-01-07 20:41 | 67 | 013:44 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN C/L Y 1 X 65 EN SU 15 SE CONSTRUYO PROVICIONAL AEREO DEL SU - 15 AL T - 9A | C22010700020 | New_Event | UG Cable Fault | Include | Include | Equipment | 824 | 2022-01-07 | 55208 | keep | 0 | Jan | 2022 | 0.037602 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
CAGUAS | 2022-01-07 07:01 | 2022-01-07 09:50 | 15 | 002:49 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ARBOL | C22010700022 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 169 | 2022-01-07 | 2535 | keep | 0 | Jan | 2022 | 0.0017266 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-01-07 07:10 | 2022-01-07 15:17 | 45 | 008:07 | P | NO SE REPORTO CAUSA | 1 X 40 Y 1 X 50 EN CORTE DE LINEA | S22010700019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 487 | 2022-01-07 | 21915 | keep | 0 | Jan | 2022 | 0.014926 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-01-07 07:30 | 2022-01-07 10:42 | 8 | 003:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | S22010500418 | New_Event | Secondary Wire Down | Include | Include | Equipment | 192 | 2022-01-07 | 1536 | keep | 0 | Jan | 2022 | 0.0010462 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-01-07 07:39 | 2022-01-07 11:13 | 1 | 003:34 | P | HERRAJE ROTO O PODRIDO | 3 X 25 EN RISER SE REMPLAZO CRUCETA Y CAJAS PRIMARIAS | M22010700010 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 214 | 2022-01-07 | 214 | keep | 0 | Jan | 2022 | 0.00014575 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-01-07 07:54 | 2022-01-07 13:52 | 40 | 005:58 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22010700001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 358 | 2022-01-07 | 14320 | keep | 0 | Jan | 2022 | 0.0097533 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-01-07 07:57 | 2022-01-07 09:10 | 8 | 001:13 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22010700022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2022-01-07 | 584 | keep | 0 | Jan | 2022 | 0.00039776 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-01-07 08:10 | 2022-01-07 09:48 | 50 | 001:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE CERRO PUENTE PRIMARIO | P22010700019 | New_Event | Wire Down | Include | Include | Equipment | 98 | 2022-01-07 | 4900 | keep | 0 | Jan | 2022 | 0.0033374 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-07 08:19 | 2022-01-07 10:20 | 25 | 002:01 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22010700024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 121 | 2022-01-07 | 3025 | keep | 0 | Jan | 2022 | 0.0020603 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-01-07 08:21 | 2022-01-07 11:23 | 35 | 003:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | B22010700025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2022-01-07 | 6370 | keep | 0 | Jan | 2022 | 0.0043386 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2022-01-07 08:25 | 2022-01-07 08:26 | 732 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22010700024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-07 | 732 | keep | 0 | Jan | 2022 | 0.00049856 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
PONCE | 2022-01-07 08:28 | 2022-01-07 10:39 | 20 | 002:11 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA CRUCE DE FASES PRIMARIAS POR RAMA | P22010700026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-01-07 | 2620 | keep | 0 | Jan | 2022 | 0.0017845 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-01-07 08:29 | 2022-01-07 10:04 | 86 | 001:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C22010700046 | New_Event | Bad Weather | Include | Include | Weather | 95 | 2022-01-07 | 8170 | keep | 0 | Jan | 2022 | 0.0055645 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
HUMACAO | 2022-01-07 08:34 | 2022-01-07 11:30 | 1 | 002:56 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO | C22010700047 | New_Event | Bad Weather | Include | Include | Weather | 176 | 2022-01-07 | 176 | keep | 0 | Jan | 2022 | 0.00011987 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-01-07 08:37 | 2022-01-07 10:11 | 2 | 001:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR FUERTES VIENTOS | M22010700018 | New_Event | Bad Weather | Include | Include | Weather | 94 | 2022-01-07 | 188 | keep | 0 | Jan | 2022 | 0.00012805 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-01-07 08:46 | 2022-01-07 11:22 | 32 | 002:36 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R22010700063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-01-07 | 4992 | keep | 0 | Jan | 2022 | 0.0034 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
FAJARDO | 2022-01-07 08:50 | 2022-01-07 14:48 | 60 | 005:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON 6 JUEGOS DE DISCOS PRIMARIOS, SE REMPLAZO CAJA PRIMARIA, SE REPARO NEUTRAL DEL SISTEMA Y SE REPARO NEUTRAL SECUNDARIO | R22010700064 | New_Event | Cutout Failure | Include | Include | Equipment | 358 | 2022-01-07 | 21480 | keep | 0 | Jan | 2022 | 0.01463 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-01-07 09:06 | 2022-01-07 15:50 | 30 | 006:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON 2 CAJAS PRIMARIAS AVERIADAS | A22010700005 | New_Event | Cutout Failure | Include | Include | Equipment | 404 | 2022-01-07 | 12120 | keep | 0 | Jan | 2022 | 0.0082549 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-01-07 09:07 | 2022-01-07 14:15 | 4 | 005:08 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO Y SE CERRO PUENTE PRIMARIO | M22010700022 | New_Event | Defective Pole | Include | Include | Equipment | 308 | 2022-01-07 | 1232 | keep | 0 | Jan | 2022 | 0.00083911 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-01-07 09:13 | 2022-01-07 12:35 | 51 | 003:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE RETEZO LINEA MONOFASICA | C22010700057 | New_Event | Wire Down | Include | Include | Equipment | 202 | 2022-01-07 | 10302 | keep | 0 | Jan | 2022 | 0.0070166 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
HUMACAO | 2022-01-07 09:23 | 2022-01-07 10:30 | 18 | 001:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR Y REEMPLAZAR CONECTOR EN BAJANTE PRIMARIO | C22010600044 | New_Event | Wire Down | Include | Include | Equipment | 67 | 2022-01-07 | 1206 | keep | 0 | Jan | 2022 | 0.0008214 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
GUAYAMA | 2022-01-07 09:34 | 2022-01-07 10:25 | 15 | 000:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | P22010700036 | New_Event | Cutout Failure | Include | Include | Equipment | 51 | 2022-01-07 | 765 | keep | 0 | Jan | 2022 | 0.00052104 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-01-07 09:35 | 2022-01-07 09:36 | 2379 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22010700040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-07 | 2379 | keep | 0 | Jan | 2022 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
SAN JUAN | 2022-01-07 09:46 | 2022-01-07 14:26 | 15 | 004:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | S22010600007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 280 | 2022-01-07 | 4200 | keep | 0 | Jan | 2022 | 0.0028606 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-01-07 09:51 | 2022-01-07 09:52 | 767 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE 50% POR EL 1909-07 Y LLEVA 100% DEL 1709-05 | B22010700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-07 | 767 | keep | 0 | Jan | 2022 | 0.0005224 | 0.0005224 | Momentary | FALSE | FALSE | Not_TMED_Event | 767
BAYAMON | 2022-01-07 09:51 | 2022-01-07 09:52 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1709-03 | B22010700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-07 | 2364 | keep | 0 | Jan | 2022 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
CANOVANAS | 2022-01-07 09:54 | 2022-01-07 10:53 | 10 | 000:59 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR NO CAUSA | R22010700067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 59 | 2022-01-07 | 590 | keep | 0 | Jan | 2022 | 0.00040185 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-01-07 10:00 | 2022-01-07 13:36 | 486 | 003:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETE PARA REPARAR FASE ABIERTA | S22010700003 | New_Event | Wire Down | Include | Include | Equipment | 216 | 2022-01-07 | 104976 | keep | 0 | Jan | 2022 | 0.071499 | 0.00033101 | Sustained | FALSE | FALSE | Not_TMED_Event | 486
PONCE | 2022-01-07 10:04 | 2022-01-07 11:15 | 20 | 001:11 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22010700042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2022-01-07 | 1420 | keep | 0 | Jan | 2022 | 0.00096716 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-01-07 10:05 | 2022-01-07 12:00 | 6 | 001:55 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 25 KVA A 4.16 KV DEBIDO A FASE INTERNA ABIERTA | P22010700029 | New_Event | Service Transformer Failure | Include | Include | Equipment | 115 | 2022-01-07 | 690 | keep | 0 | Jan | 2022 | 0.00046996 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-01-07 10:14 | 2022-01-07 10:15 | 1702 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR CRUCE POR AVE EN SERVICIO | C22010700000 | New_Event |  |  | Include | Wildlife | 1 | 2022-01-07 | 1702 | keep | 0 | Jan | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
PONCE | 2022-01-07 10:14 | 2022-01-07 10:16 | 4035 | 000:02 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA ABRIR MACHETES ATORRADOS Y COMPLETAR PASO 8 GOI D2021-00796A | P22010700018 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2022-01-07 | 8070 | keep | 0 | Jan | 2022 | 0.0054964 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
CAGUAS | 2022-01-07 10:15 | 2022-01-07 12:10 | 77 | 001:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | C22010700075 | 1st_after_momentary |  |  | Include | Wildlife | 115 | 2022-01-07 | 8855 | keep | 0 | Jan | 2022 | 0.0060311 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
BAYAMON | 2022-01-07 10:17 | 2022-01-07 12:30 | 45 | 002:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | B22010700032 | New_Event | Wire Down | Include | Include | Equipment | 133 | 2022-01-07 | 5985 | keep | 0 | Jan | 2022 | 0.0040764 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2022-01-07 10:20 | 2022-01-07 15:06 | 150 | 004:46 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA QUE PERSONAL REALIZARA DESGANCHE | M22010700033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 286 | 2022-01-07 | 42900 | keep | 0 | Jan | 2022 | 0.029219 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2022-01-07 10:24 | 2022-01-07 13:12 | 11 | 002:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR BAJANTE SECUNDARIO Y 200 PIES DE SECUNDARIA | C22010600050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 168 | 2022-01-07 | 1848 | keep | 0 | Jan | 2022 | 0.0012587 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2022-01-07 10:25 | 2022-01-07 13:55 | 15 | 003:30 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5KVA X 37.5KVA POR DERRAME DE ACEITE | M22010700029 | New_Event | Service Transformer Failure | Include | Include | Equipment | 210 | 2022-01-07 | 3150 | keep | 0 | Jan | 2022 | 0.0021455 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-01-07 10:29 | 2022-01-07 12:23 | 168 | 001:54 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C22010700071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2022-01-07 | 19152 | keep | 0 | Jan | 2022 | 0.013044 | 0.00011442 | Sustained | FALSE | FALSE | Not_TMED_Event | 168
UTUADO | 2022-01-07 10:35 | 2022-01-07 18:35 | 50 | 008:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA Y SE REALIZO DESGANCHE | A22010700013 | New_Event | Wire Down | Include | Include | Equipment | 480 | 2022-01-07 | 24000 | keep | 0 | Jan | 2022 | 0.016346 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-07 10:36 | 2022-01-07 14:35 | 1977 | 003:59 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO EN EL 1336-08. 30% DE LA CARGA POR EL 1336-08 | S22010700052 | New_Event | Switch Failure | Include | Include | Equipment | 239 | 2022-01-07 | 472503 | keep | 0 | Jan | 2022 | 0.32182 | 0.0013465 | Sustained | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2022-01-07 10:36 | 2022-01-07 12:28 | 5290 | 001:52 | T | DESCONECTIVO DEFECTUOSO | DISPARO SE SECCIONALIZO Y SE CERRO POR SCADA PARA REEMPLAZAR MACHETE QUEMADO 90% EN SERVICIO | S22010700052 | New_Event | Switch Failure | Include | Include | Equipment | 112 | 2022-01-07 | 592480 | keep | 0 | Jan | 2022 | 0.40354 | 0.003603 | Sustained | FALSE | FALSE | Not_TMED_Event | 5290
BAYAMON | 2022-01-07 10:37 | 2022-01-07 15:19 | 50 | 004:42 | P | NO SE REPORTO CAUSA | 2 X 80 EN RISER Y 2 X 100 SU A RISER | S22010700041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 282 | 2022-01-07 | 14100 | keep | 0 | Jan | 2022 | 0.0096034 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-01-07 10:52 | 2022-01-07 11:31 | 19 | 000:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZO DE 2 BARRAS EN PEDESTAL | C22010700076 | New_Event | Secondary Wire Down | Include | Include | Equipment | 39 | 2022-01-07 | 741 | keep | 0 | Jan | 2022 | 0.00050469 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
PONCE | 2022-01-07 11:09 | 2022-01-07 15:51 | 15 | 004:42 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA 7620 VOLT POR UNO DE LA MISMA CAPACIDAD | P22010700050 | New_Event | Service Transformer Failure | Include | Include | Equipment | 282 | 2022-01-07 | 4230 | keep | 0 | Jan | 2022 | 0.002881 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-01-07 11:09 | 2022-01-07 12:43 | 50 | 001:34 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22010700050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2022-01-07 | 4700 | keep | 0 | Jan | 2022 | 0.0032011 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-01-07 11:11 | 2022-01-07 12:33 | 5 | 001:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA AVERIADA | M22010700048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 82 | 2022-01-07 | 410 | keep | 0 | Jan | 2022 | 0.00027925 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-01-07 11:13 | 2022-01-07 11:40 | 1339 | 000:27 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA REPARAR MACHETE QUEMADO NO HAY PARCIAL DE CLIENTES SIN SERVICIO NO AFECTO CLIENTES ANTES | M22010700044 | New_Event | Switch Failure | Include | Include | Equipment | 27 | 2022-01-07 | 36153 | keep | 0 | Jan | 2022 | 0.024624 | 0.00091199 | Sustained | FALSE | FALSE | Not_TMED_Event | 1339
UTUADO | 2022-01-07 11:15 | 2022-01-08 10:09 | 10 | 022:54 | P | TRANSFORMADOR AVERIADO | SE REPARO BUSHING SECUNDARIO AVERIADO | A22010700023 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1374 | 2022-01-07 | 13740 | keep | 0 | Jan | 2022 | 0.0093583 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-01-07 11:19 | 2022-01-08 13:05 | 100 | 025:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | M22010700051 | New_Event | Cutout Failure | Include | Include | Equipment | 1546 | 2022-01-07 | 154600 | keep | 0 | Jan | 2022 | 0.1053 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-01-07 11:28 | 2022-01-07 11:37 | 1264 | 000:09 | T | ERROR HUMANO | SE DISPARO BKR A CAUSA PERSONAL DE CONSERVACION TRABAJANDO | S22010700128 | New_Event | Human Error | Include | Include | Other | 9 | 2022-01-07 | 11376 | keep | 0 | Jan | 2022 | 0.0077481 | 0.0008609 | Sustained | FALSE | FALSE | Not_TMED_Event | 1264
AGUADILLA | 2022-01-07 11:37 | 2022-01-07 11:38 | 1192 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | M22010700000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-01-07 | 1192 | keep | 0 | Jan | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2022-01-07 11:38 | 2022-01-07 14:55 | 20 | 003:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON CAJAS PRIMARIAS AVERIADAS EN RISER | M22010700072 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 197 | 2022-01-07 | 3940 | keep | 0 | Jan | 2022 | 0.0026835 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-01-07 11:40 | 2022-01-07 15:16 | 1 | 003:36 | P | HERRAJE ROTO O PODRIDO | 3 X 25 EN RISER SE REMPLAZO CRUCETA Y CAJAS PRIMARIAS | M22010700010 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 216 | 2022-01-07 | 216 | keep | 0 | Jan | 2022 | 0.00014712 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-01-07 11:42 | 2022-01-07 12:43 | 8 | 001:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO AVERIADO | M22010700062 | New_Event | Wire Down | Include | Include | Equipment | 61 | 2022-01-07 | 488 | keep | 0 | Jan | 2022 | 0.00033237 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-01-07 11:59 | 2022-01-07 16:43 | 80 | 004:44 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | P22010700055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 284 | 2022-01-07 | 22720 | keep | 0 | Jan | 2022 | 0.015474 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-01-07 12:00 | 2022-01-07 13:04 | 108 | 001:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C22010700091 | New_Event |  |  | Include | Wildlife | 64 | 2022-01-07 | 6912 | keep | 0 | Jan | 2022 | 0.0047077 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
UTUADO | 2022-01-07 12:03 | 2022-01-07 14:33 | 50 | 002:30 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22010700028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2022-01-07 | 7500 | keep | 0 | Jan | 2022 | 0.0051082 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-01-07 12:09 | 2022-01-07 18:16 | 30 | 006:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M22010700073 | New_Event | Wire Down | Include | Include | Equipment | 367 | 2022-01-07 | 11010 | keep | 0 | Jan | 2022 | 0.0074989 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-01-07 12:17 | 2022-01-07 12:23 | 1494 | 000:06 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR SE CERRO POR SCADA | B22010700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-01-07 | 8964 | keep | 0 | Jan | 2022 | 0.0061053 | 0.0010176 | Sustained | FALSE | FALSE | Not_TMED_Event | 1494
PONCE | 2022-01-07 12:26 | 2022-01-07 14:15 | 50 | 001:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA GLOBO DE HELIO CRUZO LINEAS PRIMARIAS | P22010700058 | New_Event |  |  | Include | Wildlife | 109 | 2022-01-07 | 5450 | keep | 0 | Jan | 2022 | 0.003712 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-07 12:28 | 2022-01-07 14:32 | 529 | 002:04 | P | DESCONECTIVO DEFECTUOSO | ALIMENTADOR SECCIONALIZADO | S22010700052 | Partial_restoration | Switch Failure | Include | Include | Equipment | 124 | 2022-01-07 | 65596 | keep | 0 | Jan | 2022 | 0.044677 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-01-07 12:30 | 2022-01-07 14:00 | 40 | 001:30 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZO DE POSTE PRIMARIO | M22010700043 | New_Event | Defective Pole | Include | Include | Equipment | 90 | 2022-01-07 | 3600 | keep | 0 | Jan | 2022 | 0.0024519 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-01-07 12:39 | 2022-01-07 16:10 | 100 | 003:31 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | P22010700059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2022-01-07 | 21100 | keep | 0 | Jan | 2022 | 0.014371 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-01-07 12:50 | 2022-01-07 16:36 | 15 | 003:46 | P | NO SE REPORTO CAUSA | 1 X 30 EN PROVISIONAL AEREO | B22010700059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 226 | 2022-01-07 | 3390 | keep | 0 | Jan | 2022 | 0.0023089 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-01-07 12:52 | 2022-01-07 12:53 | 4035 | 000:01 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA CERRAR MACHETES ATORRADOS Y COMPLETAR PASO 8 GOI D2021-00796A | P22010700018 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2022-01-07 | 4035 | keep | 0 | Jan | 2022 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
CAGUAS | 2022-01-07 13:05 | 2022-01-07 15:38 | 22 | 002:33 | P | DESGANCHE | 1 X 40 EN C/L | C22010700103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2022-01-07 | 3366 | keep | 0 | Jan | 2022 | 0.0022926 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
SAN JUAN | 2022-01-07 13:06 | 2022-01-07 13:33 | 10 | 000:27 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO CAUSA | R22010700076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 27 | 2022-01-07 | 270 | keep | 0 | Jan | 2022 | 0.0001839 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-07 13:07 | 2022-01-07 17:38 | 100 | 004:31 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A22010700033 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 271 | 2022-01-07 | 27100 | keep | 0 | Jan | 2022 | 0.018458 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-01-07 13:08 | 2022-01-07 14:30 | 15 | 001:22 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | B22010700061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2022-01-07 | 1230 | keep | 0 | Jan | 2022 | 0.00083775 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2022-01-07 13:16 | 2022-01-07 14:10 | 40 | 000:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | P22010700062 | New_Event |  |  | Include | Wildlife | 54 | 2022-01-07 | 2160 | keep | 0 | Jan | 2022 | 0.0014712 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-01-07 13:39 | 2022-01-07 14:25 | 7 | 000:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C22010700104 | New_Event | Secondary Wire Down | Include | Include | Equipment | 46 | 2022-01-07 | 322 | keep | 0 | Jan | 2022 | 0.00021931 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-01-07 13:42 | 2022-01-07 14:15 | 1494 | 000:33 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 9101-02 SE SECCIONALIZO ABRIENDO MACHETES EN CARR 647 KM 12 CASCO URBANO 50% EN SERVICIO | B22010700010 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 33 | 2022-01-07 | 49302 | keep | 0 | Jan | 2022 | 0.033579 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-01-07 13:49 | 2022-01-07 16:38 | 15 | 002:49 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 75KVA X 75KVA | A22010700038 | New_Event | Service Transformer Failure | Include | Include | Equipment | 169 | 2022-01-07 | 2535 | keep | 0 | Jan | 2022 | 0.0017266 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-01-07 13:54 | 2022-01-08 12:30 | 40 | 022:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO | M22010700090 | New_Event | Wire Down | Include | Include | Equipment | 1356 | 2022-01-07 | 54240 | keep | 0 | Jan | 2022 | 0.036943 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-01-07 14:03 | 2022-01-07 14:04 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA TRANSFERIDA AL 1206-03 | S22010700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-07 | 10211 | keep | 0 | Jan | 2022 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2022-01-07 14:03 | 2022-01-07 14:04 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 1204-05 | S22010700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-07 | 4133 | keep | 0 | Jan | 2022 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2022-01-07 14:04 | 2022-01-07 20:07 | 5 | 006:03 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22010700345 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 363 | 2022-01-07 | 1815 | keep | 0 | Jan | 2022 | 0.0012362 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2022-01-07 14:06 | 2022-01-07 15:51 | 9 | 001:45 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO SECUNDARIO 40 PIES | A22010700039 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 105 | 2022-01-07 | 945 | keep | 0 | Jan | 2022 | 0.00064364 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-01-07 14:13 | 2022-01-07 15:04 | 40 | 000:51 | P | NO SE REPORTO CAUSA | 2 X 40 SMU20 EN SU | B22010700085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 51 | 2022-01-07 | 2040 | keep | 0 | Jan | 2022 | 0.0013894 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-01-07 14:15 | 2022-01-07 14:39 | 896 | 000:24 | P | NO SE REPORTO CAUSA | SE SECCIONALIZO ABRIENDO MACHETES EN CARR 677 KM 0.1 Y FUSIBLES HACIA CANDELARIA Y SE CERRO MACHETES EN CARR 647 KM 12 CASCO URBANO. 60% EN SERVICIO | B22010700010 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 24 | 2022-01-07 | 21504 | keep | 0 | Jan | 2022 | 0.014646 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-07 14:16 | 2022-01-07 17:31 | 5 | 003:15 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIO XMR PARA REMPLAZAR POSTE SECUNDARIO | C22010700112 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 195 | 2022-01-07 | 975 | keep | 0 | Jan | 2022 | 0.00066407 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-01-07 14:22 | 2022-01-07 17:23 | 5 | 003:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BARRA DEL NEUTRAL SECUNDARIO | A22010700043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 181 | 2022-01-07 | 905 | keep | 0 | Jan | 2022 | 0.00061639 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-01-07 14:26 | 2022-01-07 18:11 | 100 | 003:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L REMPLAZO CAJA AVERIADA | C22010700113 | New_Event | Cutout Failure | Include | Include | Equipment | 225 | 2022-01-07 | 22500 | keep | 0 | Jan | 2022 | 0.015325 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-01-07 14:32 | 2022-01-07 14:35 | 5290 | 000:03 | T | DESCONECTIVO DEFECTUOSO | CUANDO SE ESTABA CERRANDO MACHETES HUBO DISPARO DEL ALIMENTADOR, SE CERRO MACHETES Y SE CERRO INTERRUPTOR. SE REMPLAZO MACHETE QUEMADO LLEVA LA CARGA DEL 1336-09 Y 30% 1204-04 | S22010700052 | Additional_clients | Switch Failure | Include | Include | Equipment | 3 | 2022-01-07 | 15870 | keep | 0 | Jan | 2022 | 0.010809 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-07 14:32 | 2022-01-07 14:33 | 2859 | 000:01 | T | DESGANCHE | RECIERRE | C22010700115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-07 | 2859 | keep | 0 | Jan | 2022 | 0.0019473 | 0.0019473 | Momentary | FALSE | FALSE | Not_TMED_Event | 2859
CAGUAS | 2022-01-07 14:33 | 2022-01-07 18:45 | 80 | 004:12 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHO Y REMPLAZO PARARRAYO | C22010700121 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 252 | 2022-01-07 | 20160 | keep | 0 | Jan | 2022 | 0.013731 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-01-07 14:33 | 2022-01-07 16:16 | 10 | 001:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REQUIERE DESGANCHE | A22010700048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2022-01-07 | 1030 | keep | 0 | Jan | 2022 | 0.00070153 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-01-07 14:34 | 2022-01-07 16:04 | 7 | 001:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR BAJANTE SECUNDARIO | C22010700116 | New_Event | Secondary Wire Down | Include | Include | Equipment | 90 | 2022-01-07 | 630 | keep | 0 | Jan | 2022 | 0.00042909 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-01-07 14:35 | 2022-01-07 15:36 | 10 | 001:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22010700324 | New_Event | Secondary Wire Down | Include | Include | Equipment | 61 | 2022-01-07 | 610 | keep | 0 | Jan | 2022 | 0.00041547 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-01-07 14:39 | 2022-01-07 15:06 | 747 | 000:27 | P | NO SE REPORTO CAUSA | SE SECCIONALIZO ABRIENDO FUSIBLES Y SE CERRO MACHETES EN CARR 677 KM 0.1. 70% EN SERVICIO | B22010700010 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 27 | 2022-01-07 | 20169 | keep | 0 | Jan | 2022 | 0.013737 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-01-07 15:05 | 2022-01-07 18:26 | 50 | 003:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA FIJAR BAJANTE SAFADO EN CORTE DE LINEA NO FUNDIO FUSIBLE | P22010700078 | New_Event | Wire Down | Include | Include | Equipment | 201 | 2022-01-07 | 10050 | keep | 0 | Jan | 2022 | 0.006845 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-01-07 15:06 | 2022-01-07 15:32 | 448 | 000:26 | P | NO SE REPORTO CAUSA | SE SECCIONALIZO SE CERRO FUSIBLES HACIA CANDELARIA 80% EN SERVICIO | B22010700010 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 26 | 2022-01-07 | 11648 | keep | 0 | Jan | 2022 | 0.0079334 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-01-07 15:11 | 2022-01-07 16:19 | 30 | 001:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | CAMION DEL MUNICIPIO LIMPIANDO AREAS VERDES CRUZO LINEAS CON RAMAS | A22010700055 | New_Event |  |  | Include | Wildlife | 68 | 2022-01-07 | 2040 | keep | 0 | Jan | 2022 | 0.0013894 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-01-07 15:25 | 2022-01-07 15:54 | 45 | 000:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 EN CORTE DE LINEA LINEAS CRUZADAS | M22010700102 | New_Event | Wire Down | Include | Include | Equipment | 29 | 2022-01-07 | 1305 | keep | 0 | Jan | 2022 | 0.00088883 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
VEGA BAJA | 2022-01-07 15:32 | 2022-01-07 15:36 | 300 | 000:04 | P | NO SE REPORTO CAUSA | SE CERRARON FUSIBLES ALIMENTADOR 100% EN SERVICIO | B22010700010 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-01-07 | 1200 | keep | 0 | Jan | 2022 | 0.00081731 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-01-07 15:35 | 2022-01-07 19:40 | 40 | 004:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REQUIERE DESGANCHE | A22010700059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2022-01-07 | 9800 | keep | 0 | Jan | 2022 | 0.0066747 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-01-07 15:43 | 2022-01-07 16:00 | 1 | 000:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | M22010700106 | New_Event | Bad Weather | Include | Include | Weather | 17 | 2022-01-07 | 17 | keep | 0 | Jan | 2022 | 1.1579e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-01-07 15:49 | 2022-01-07 20:13 | 10 | 004:24 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REMPLAZO TERMINACION TIPO PISTOLA EN TRANSFORMADOR | B22010700108 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 264 | 2022-01-07 | 2640 | keep | 0 | Jan | 2022 | 0.0017981 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-01-07 15:49 | 2022-01-07 15:53 | 1950 | 000:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR LINEA PRIMARIA PARTIDA QUEMANDOSE SE ABRIO PUENTES PARA SECCIONALIZAR LA AVERIA EN TRONCAL DEL INTERRUPTOR | A22010700000 | New_Event | Wire Down | Include | Include | Equipment | 4 | 2022-01-07 | 7800 | keep | 0 | Jan | 2022 | 0.0053125 | 0.0013281 | Momentary | FALSE | FALSE | Not_TMED_Event | 1950
FAJARDO | 2022-01-07 15:56 | 2022-01-07 16:59 | 15 | 001:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BARRAS EN PEDESTAL | R22010700082 | New_Event | Secondary Wire Down | Include | Include | Equipment | 63 | 2022-01-07 | 945 | keep | 0 | Jan | 2022 | 0.00064364 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-01-07 15:57 | 2022-01-07 16:34 | 4 | 000:37 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS | A22010700062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 37 | 2022-01-07 | 148 | keep | 0 | Jan | 2022 | 0.0001008 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2022-01-07 16:09 | 2022-01-07 20:00 | 20 | 003:51 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO PARARRAYO | B22010700109 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 231 | 2022-01-07 | 4620 | keep | 0 | Jan | 2022 | 0.0031467 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-01-07 16:37 | 2022-01-07 21:31 | 10 | 004:54 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B22010700111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 294 | 2022-01-07 | 2940 | keep | 0 | Jan | 2022 | 0.0020024 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-01-07 16:43 | 2022-01-07 16:44 | 108 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1500 | M22010700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-07 | 108 | keep | 0 | Jan | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
BAYAMON | 2022-01-07 16:48 | 2022-01-07 16:57 | 1 | 000:09 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22010700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2022-01-07 | 9 | keep | 0 | Jan | 2022 | 6.1299e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-01-07 16:50 | 2022-01-07 18:43 | 60 | 001:53 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | R22010700083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 113 | 2022-01-07 | 6780 | keep | 0 | Jan | 2022 | 0.0046178 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-01-07 17:00 | 2022-01-07 18:58 | 30 | 001:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA 1 X 15 EN TRANSFORMADOR CULEBRA CRUZO LINEAS | A22010700072 | New_Event |  |  | Include | Wildlife | 118 | 2022-01-07 | 3540 | keep | 0 | Jan | 2022 | 0.0024111 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-01-07 17:28 | 2022-01-08 09:02 | 65 | 015:34 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER @ SU-11 | C22010700132 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 934 | 2022-01-07 | 60710 | keep | 0 | Jan | 2022 | 0.041349 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
FAJARDO | 2022-01-07 17:34 | 2022-01-07 19:20 | 30 | 001:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA | R22010700087 | New_Event | Wire Down | Include | Include | Equipment | 106 | 2022-01-07 | 3180 | keep | 0 | Jan | 2022 | 0.0021659 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-01-07 17:44 | 2022-01-07 17:45 | 325 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22010700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-07 | 325 | keep | 0 | Jan | 2022 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
AGUADILLA | 2022-01-07 17:53 | 2022-01-07 22:24 | 40 | 004:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22010700119 | New_Event | Bad Weather | Include | Include | Weather | 271 | 2022-01-07 | 10840 | keep | 0 | Jan | 2022 | 0.0073831 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-01-07 18:01 | 2022-01-07 19:36 | 5 | 001:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | S22010700346 | New_Event | Secondary Wire Down | Include | Include | Equipment | 95 | 2022-01-07 | 475 | keep | 0 | Jan | 2022 | 0.00032352 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-01-07 18:24 | 2022-01-07 18:25 | 3012 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | R22010700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-07 | 3012 | keep | 0 | Jan | 2022 | 0.0020515 | 0.0020515 | Momentary | FALSE | FALSE | Not_TMED_Event | 3012
GUAYAMA | 2022-01-07 18:24 | 2022-01-07 18:25 | 1173 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P22010700089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-07 | 1173 | keep | 0 | Jan | 2022 | 0.00079892 | 0.00079892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1173
AGUADILLA | 2022-01-07 18:41 | 2022-01-08 00:40 | 60 | 005:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22010700123 | New_Event | Bad Weather | Include | Include | Weather | 359 | 2022-01-07 | 21540 | keep | 0 | Jan | 2022 | 0.014671 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-01-07 19:40 | 2022-01-07 20:31 | 10 | 000:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO CAJAS DE TRANSFORMADOR PARA RETIRAR TENSOR CERCA DE LA PRIMARIA | M22010700127 | New_Event |  |  | Include | Wildlife | 51 | 2022-01-07 | 510 | keep | 0 | Jan | 2022 | 0.00034736 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-01-07 20:22 | 2022-01-07 20:23 | 2039 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO | R22010700000 | New_Event |  |  | Include | Wildlife | 1 | 2022-01-07 | 2039 | keep | 0 | Jan | 2022 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
CANOVANAS | 2022-01-07 20:23 | 2022-01-08 11:54 | 1 | 015:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 Y 1 X 100 EN CORTES DE LINEA CRUCE POR AVE | R22010700090 | 1st_after_momentary |  |  | Include | Wildlife | 931 | 2022-01-07 | 931 | keep | 0 | Jan | 2022 | 0.0006341 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-01-07 20:26 | 2022-01-07 20:27 | 1709 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22010700157 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-07 | 1709 | keep | 0 | Jan | 2022 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
CAGUAS | 2022-01-07 20:27 | 2022-01-08 10:53 | 95 | 014:26 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU-19 @ T-43A | C22010700159 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 866 | 2022-01-07 | 82270 | keep | 0 | Jan | 2022 | 0.056034 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
AGUADILLA | 2022-01-07 21:06 | 2022-01-07 21:43 | 12 | 000:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | M22010700135 | New_Event | Secondary Wire Down | Include | Include | Equipment | 37 | 2022-01-07 | 444 | keep | 0 | Jan | 2022 | 0.00030241 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-01-07 21:14 | 2022-01-08 08:35 | 10 | 011:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR NEUTRAL SECUNDARIO | B22010700122 | New_Event | Secondary Wire Down | Include | Include | Equipment | 681 | 2022-01-07 | 6810 | keep | 0 | Jan | 2022 | 0.0046383 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-01-07 21:49 | 2022-01-07 21:50 | 1891 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | C22010700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-07 | 1891 | keep | 0 | Jan | 2022 | 0.001288 | 0.001288 | Momentary | FALSE | FALSE | Not_TMED_Event | 1891
HUMACAO | 2022-01-07 21:49 | 2022-01-07 21:50 | 1250 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | C22010700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-07 | 1250 | keep | 0 | Jan | 2022 | 0.00085137 | 0.00085137 | Momentary | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2022-01-07 21:49 | 2022-01-07 21:50 | 2141 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | C22010700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-07 | 2141 | keep | 0 | Jan | 2022 | 0.0014582 | 0.0014582 | Momentary | FALSE | FALSE | Not_TMED_Event | 2141
HUMACAO | 2022-01-07 21:49 | 2022-01-07 21:50 | 1827 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | C22010700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-07 | 1827 | keep | 0 | Jan | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
GUAYAMA | 2022-01-07 21:49 | 2022-01-07 21:50 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010700096 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-07 | 2100 | keep | 0 | Jan | 2022 | 0.0014303 | 0.0014303 | Momentary | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-01-07 21:49 | 2022-01-07 21:50 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010700096 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-07 | 922 | keep | 0 | Jan | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-01-07 21:49 | 2022-01-07 21:50 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010700096 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-07 | 1676 | keep | 0 | Jan | 2022 | 0.0011415 | 0.0011415 | Momentary | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-01-07 21:49 | 2022-01-07 21:50 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010700096 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-07 | 2844 | keep | 0 | Jan | 2022 | 0.001937 | 0.001937 | Momentary | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-01-07 21:49 | 2022-01-07 21:50 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010700096 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-07 | 2775 | keep | 0 | Jan | 2022 | 0.00189 | 0.00189 | Momentary | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-01-07 21:49 | 2022-01-07 21:50 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010700096 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-07 | 1457 | keep | 0 | Jan | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-01-07 21:49 | 2022-01-07 21:50 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010700096 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-07 | 1086 | keep | 0 | Jan | 2022 | 0.00073967 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-01-07 21:49 | 2022-01-07 21:50 | 2134 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010700096 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-07 | 2134 | keep | 0 | Jan | 2022 | 0.0014535 | 0.0014535 | Momentary | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-01-07 21:49 | 2022-01-07 21:50 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010700096 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-07 | 1464 | keep | 0 | Jan | 2022 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-01-07 21:49 | 2022-01-07 21:50 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010700096 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-07 | 1833 | keep | 0 | Jan | 2022 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-01-07 21:49 | 2022-01-07 21:50 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010700096 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-07 | 1565 | keep | 0 | Jan | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-01-07 21:49 | 2022-01-07 21:50 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010700096 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-07 | 977 | keep | 0 | Jan | 2022 | 0.00066543 | 0.00066543 | Momentary | FALSE | FALSE | Not_TMED_Event | 977
MAYAGÃœEZ | 2022-01-07 22:13 | 2022-01-08 09:31 | 30 | 011:18 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22010700136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 678 | 2022-01-07 | 20340 | keep | 0 | Jan | 2022 | 0.013853 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-01-07 23:15 | 2022-01-08 09:24 | 50 | 010:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA RETIRO GLOBO CRUZANDO LINEA | C22010700162 | New_Event |  |  | Include | Wildlife | 609 | 2022-01-07 | 30450 | keep | 0 | Jan | 2022 | 0.020739 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-07 23:27 | 2022-01-08 09:28 | 150 | 010:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 Y 1 X 40 EN CORTES DE LINEA CRUCE POR AVE | R22010700092 | New_Event |  |  | Include | Wildlife | 601 | 2022-01-07 | 90150 | keep | 0 | Jan | 2022 | 0.061401 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-01-07 23:34 | 2022-01-08 09:47 | 500 | 010:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M22010700143 | New_Event | Cutout Failure | Include | Include | Equipment | 613 | 2022-01-07 | 306500 | keep | 0 | Jan | 2022 | 0.20876 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2022-01-07 23:52 | 2022-01-08 02:05 | 1382 | 002:13 | T | NO SE REPORTO CAUSA | DISPARO LLEVA LA CARGA DEL 1706-03 SE PATRULLO Y NO SE REPORTO CAUSA PARA EL DISPARO | B22010700123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 133 | 2022-01-07 | 183806 | keep | 0 | Jan | 2022 | 0.12519 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2022-01-07 23:52 | 2022-01-08 03:36 | 663 | 003:44 | T | NO SE REPORTO CAUSA | CARGA TRASFERIDA AL 1706-02 SE ABRIO N/O SE PATRULLO Y NO SE REPORTO CAUSA PARA DISPARO | B22010700123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 224 | 2022-01-07 | 148512 | keep | 0 | Jan | 2022 | 0.10115 | 0.00045157 | Sustained | FALSE | FALSE | Not_TMED_Event | 663
SAN JUAN | 2022-01-08 00:53 | 2022-01-08 11:38 | 15 | 010:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA | S22010800001 | New_Event | Cutout Failure | Include | Include | Equipment | 645 | 2022-01-08 | 9675 | keep | 0 | Jan | 2022 | 0.0065896 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-01-08 00:55 | 2022-01-08 11:00 | 100 | 010:05 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA EL JOURNEYMAN INFORMO QUE NO ENCONTRO CAUSA PARA EL FUSIBLE FUNDIDO | M22010800008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 605 | 2022-01-08 | 60500 | keep | 0 | Jan | 2022 | 0.041206 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-01-08 02:35 | 2022-01-08 09:02 | 15 | 006:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE FIJO NEUTRAL | R22010800001 | New_Event | Wire Down | Include | Include | Equipment | 387 | 2022-01-08 | 5805 | keep | 0 | Jan | 2022 | 0.0039538 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-01-08 03:09 | 2022-01-08 03:10 | 6197 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C22010800000 | New_Event |  |  | Include | Wildlife | 1 | 2022-01-08 | 6197 | keep | 0 | Jan | 2022 | 0.0042207 | 0.0042207 | Momentary | FALSE | FALSE | Not_TMED_Event | 6197
CAGUAS | 2022-01-08 03:10 | 2022-01-08 12:39 | 60 | 009:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C22010800002 | 1st_after_momentary |  |  | Include | Wildlife | 569 | 2022-01-08 | 34140 | keep | 0 | Jan | 2022 | 0.023253 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-01-08 03:21 | 2022-01-08 10:55 | 6 | 007:34 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR PM T-1 DE 75 KVA X 100 KVA | R22010800003 | New_Event | Service Transformer Failure | Include | Include | Equipment | 454 | 2022-01-08 | 2724 | keep | 0 | Jan | 2022 | 0.0018553 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-01-08 05:27 | 2022-01-08 09:36 | 30 | 004:09 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22010800028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 249 | 2022-01-08 | 7470 | keep | 0 | Jan | 2022 | 0.0050878 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-01-08 06:38 | 2022-01-08 09:44 | 200 | 003:06 | P | NO SE REPORTO CAUSA | 1 X 100 EN PROVISIONAL | S22010800006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 186 | 2022-01-08 | 37200 | keep | 0 | Jan | 2022 | 0.025337 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2022-01-08 07:13 | 2022-01-08 07:14 | 1891 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | C22010800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 1891 | keep | 0 | Jan | 2022 | 0.001288 | 0.001288 | Momentary | FALSE | FALSE | Not_TMED_Event | 1891
HUMACAO | 2022-01-08 07:13 | 2022-01-08 07:14 | 1250 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | C22010800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 1250 | keep | 0 | Jan | 2022 | 0.00085137 | 0.00085137 | Momentary | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2022-01-08 07:13 | 2022-01-08 07:14 | 2141 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | C22010800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 2141 | keep | 0 | Jan | 2022 | 0.0014582 | 0.0014582 | Momentary | FALSE | FALSE | Not_TMED_Event | 2141
HUMACAO | 2022-01-08 07:13 | 2022-01-08 07:14 | 1827 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | C22010800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 1827 | keep | 0 | Jan | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
GUAYAMA | 2022-01-08 07:14 | 2022-01-08 07:15 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010800003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 2100 | keep | 0 | Jan | 2022 | 0.0014303 | 0.0014303 | Momentary | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-01-08 07:14 | 2022-01-08 07:15 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010800003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 922 | keep | 0 | Jan | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-01-08 07:14 | 2022-01-08 07:15 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010800003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 1676 | keep | 0 | Jan | 2022 | 0.0011415 | 0.0011415 | Momentary | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-01-08 07:14 | 2022-01-08 07:15 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010800003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 2844 | keep | 0 | Jan | 2022 | 0.001937 | 0.001937 | Momentary | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-01-08 07:14 | 2022-01-08 07:15 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010800003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 2775 | keep | 0 | Jan | 2022 | 0.00189 | 0.00189 | Momentary | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-01-08 07:14 | 2022-01-08 07:15 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010800003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 1457 | keep | 0 | Jan | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-01-08 07:14 | 2022-01-08 07:15 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010800003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 1086 | keep | 0 | Jan | 2022 | 0.00073967 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-01-08 07:14 | 2022-01-08 07:15 | 2134 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010800003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 2134 | keep | 0 | Jan | 2022 | 0.0014535 | 0.0014535 | Momentary | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-01-08 07:14 | 2022-01-08 07:15 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010800003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 1464 | keep | 0 | Jan | 2022 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-01-08 07:14 | 2022-01-08 07:15 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010800003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 1833 | keep | 0 | Jan | 2022 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-01-08 07:14 | 2022-01-08 07:15 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010800003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 1565 | keep | 0 | Jan | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-01-08 07:14 | 2022-01-08 07:15 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010800003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 977 | keep | 0 | Jan | 2022 | 0.00066543 | 0.00066543 | Momentary | FALSE | FALSE | Not_TMED_Event | 977
FAJARDO | 2022-01-08 08:13 | 2022-01-08 10:14 | 9 | 002:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA SE FIJO NEUTRAL | R22010800006 | New_Event | Wire Down | Include | Include | Equipment | 121 | 2022-01-08 | 1089 | keep | 0 | Jan | 2022 | 0.00074171 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2022-01-08 08:49 | 2022-01-08 08:50 | 1494 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR 9101-02 LLEVANDO CARGA 9101-04 | B22010800000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-01-08 | 1494 | keep | 0 | Jan | 2022 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
VEGA BAJA | 2022-01-08 08:50 | 2022-01-08 08:51 | 1494 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR 9101-02 LLEVANDO CARGA 9101-04 | B22010800000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-01-08 | 1494 | keep | 0 | Jan | 2022 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
VEGA BAJA | 2022-01-08 08:51 | 2022-01-08 08:53 | 1494 | 000:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 9101-02 LLEVANDO CARGA 9101-04 SE CERRO POR SCADA | B22010800000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2022-01-08 | 2988 | keep | 0 | Jan | 2022 | 0.0020351 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
VEGA BAJA | 2022-01-08 08:54 | 2022-01-08 11:48 | 1494 | 002:54 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 9101-02 LLEVANDO CARGA 9101-04 SE CERRO POR SCADA SE REMPLAZO AISLADOR PARTIDO | B22010800000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 174 | 2022-01-08 | 259956 | keep | 0 | Jan | 2022 | 0.17705 | 0.0010176 | Sustained | FALSE | FALSE | Not_TMED_Event | 1494
ARECIBO | 2022-01-08 09:12 | 2022-01-08 13:27 | 5 | 004:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA SECUNDARIA PARTIDA | A22010800001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 255 | 2022-01-08 | 1275 | keep | 0 | Jan | 2022 | 0.0008684 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2022-01-08 09:15 | 2022-01-08 13:10 | 1 | 003:55 | P | DESGANCHE | 2 X 15 EN MONTURA TRANSFORMADORES SE REALIZO DESGANCHE | B22010800057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 235 | 2022-01-08 | 235 | keep | 0 | Jan | 2022 | 0.00016006 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-01-08 09:18 | 2022-01-08 11:40 | 60 | 002:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C22010800015 | New_Event |  |  | Include | Wildlife | 142 | 2022-01-08 | 8520 | keep | 0 | Jan | 2022 | 0.0058029 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-01-08 09:31 | 2022-01-08 13:14 | 15 | 003:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22010800037 | New_Event | Bad Weather | Include | Include | Weather | 223 | 2022-01-08 | 3345 | keep | 0 | Jan | 2022 | 0.0022783 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-01-08 09:34 | 2022-01-08 10:47 | 30 | 001:13 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22010800064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2022-01-08 | 2190 | keep | 0 | Jan | 2022 | 0.0014916 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-01-08 09:35 | 2022-01-08 09:37 | 1 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22010800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-08 | 2 | keep | 0 | Jan | 2022 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-01-08 09:38 | 2022-01-08 17:17 | 15 | 007:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22010800066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 459 | 2022-01-08 | 6885 | keep | 0 | Jan | 2022 | 0.0046893 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-01-08 10:04 | 2022-01-08 14:01 | 30 | 003:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA | B22010800080 | New_Event | Cutout Failure | Include | Include | Equipment | 237 | 2022-01-08 | 7110 | keep | 0 | Jan | 2022 | 0.0048426 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-01-08 10:19 | 2022-01-08 10:20 | 1606 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22010800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-08 | 1606 | keep | 0 | Jan | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
VEGA BAJA | 2022-01-08 10:21 | 2022-01-08 15:13 | 100 | 004:52 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | B22010800018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 292 | 2022-01-08 | 29200 | keep | 0 | Jan | 2022 | 0.019888 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-01-08 10:33 | 2022-01-08 16:21 | 50 | 005:48 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22010800057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 348 | 2022-01-08 | 17400 | keep | 0 | Jan | 2022 | 0.011851 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-01-08 10:47 | 2022-01-08 15:12 | 200 | 004:25 | P | DESGANCHE | 1 X 100, 1 X 65 Y 1 X 40 EN CORTES DE LINEA SECCIONALIZO CONDUCTOR EN EL SUELO, HAY QUE DESGANCHAR PARA PODERLO LEVANTAR | C22010800022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 265 | 2022-01-08 | 53000 | keep | 0 | Jan | 2022 | 0.036098 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2022-01-08 10:54 | 2022-01-08 12:21 | 40 | 001:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA QUEMADA | C22010800023 | New_Event | Cutout Failure | Include | Include | Equipment | 87 | 2022-01-08 | 3480 | keep | 0 | Jan | 2022 | 0.0023702 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-01-08 11:02 | 2022-01-08 18:15 | 12 | 007:13 | P | HERRAJE ROTO O PODRIDO | 2 X 15 EN TRANSFORMADOR SE FIJO TRANSFORMADOR EN CRUCETA Y SE REMPLAZARON DOS CAJAS PRIMARIAS | P21010800008 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 433 | 2022-01-08 | 5196 | keep | 0 | Jan | 2022 | 0.003539 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-01-08 11:04 | 2022-01-08 17:17 | 5 | 006:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C22010800025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 373 | 2022-01-08 | 1865 | keep | 0 | Jan | 2022 | 0.0012702 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2022-01-08 11:33 | 2022-01-08 11:34 | 3973 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | P22010800011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-08 | 3973 | keep | 0 | Jan | 2022 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
CAGUAS | 2022-01-08 11:39 | 2022-01-08 11:40 | 125 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA | C22010800028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-08 | 125 | keep | 0 | Jan | 2022 | 8.5137e-05 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
YAUCO | 2022-01-08 11:39 | 2022-01-08 11:40 | 3973 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | P22010800012 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-08 | 3973 | keep | 0 | Jan | 2022 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2022-01-08 11:41 | 2022-01-08 11:42 | 3973 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | P22010800013 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-08 | 3973 | keep | 0 | Jan | 2022 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
CAGUAS | 2022-01-08 11:46 | 2022-01-08 14:22 | 55 | 002:36 | P | DESGANCHE | 1 X 65 EN C/L | C22010800031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-01-08 | 8580 | keep | 0 | Jan | 2022 | 0.0058438 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
YAUCO | 2022-01-08 11:52 | 2022-01-08 12:30 | 3973 | 000:38 | T | DESGANCHE | DISPARO INTERRUPTOR RAMA CAE SOBRE LINEAS PRIMARIAS EN TRONCAL | P22010800018 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 38 | 2022-01-08 | 150974 | keep | 0 | Jan | 2022 | 0.10283 | 0.002706 | Sustained | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2022-01-08 11:54 | 2022-01-08 13:32 | 100 | 001:38 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P22010800020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 98 | 2022-01-08 | 9800 | keep | 0 | Jan | 2022 | 0.0066747 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-01-08 11:58 | 2022-01-08 16:12 | 40 | 004:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 XC 80 EN C/L CRUCE X REPTIL | C22010800035 | New_Event |  |  | Include | Wildlife | 254 | 2022-01-08 | 10160 | keep | 0 | Jan | 2022 | 0.0069199 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-01-08 12:09 | 2022-01-08 16:20 | 80 | 004:11 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 50 EN RISER SE REPARO TERMINACION | S22010800051 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 251 | 2022-01-08 | 20080 | keep | 0 | Jan | 2022 | 0.013676 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-01-08 12:09 | 2022-01-08 13:57 | 150 | 001:48 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | S22010800049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2022-01-08 | 16200 | keep | 0 | Jan | 2022 | 0.011034 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-01-08 12:25 | 2022-01-08 15:09 | 9 | 002:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22010800063 | New_Event | Secondary Wire Down | Include | Include | Equipment | 164 | 2022-01-08 | 1476 | keep | 0 | Jan | 2022 | 0.0010053 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-01-08 12:32 | 2022-01-08 12:34 | 375 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF 95% DEL 1336-10 POR 1620-01 SE PROBO QUEDO EN SERVICIO | S22010800060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-08 | 750 | keep | 0 | Jan | 2022 | 0.00051082 | 0.00025541 | Momentary | FALSE | FALSE | Not_TMED_Event | 375
SAN JUAN | 2022-01-08 12:32 | 2022-01-08 12:34 | 36 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SU CARGA POR 1620-4 Y 95% 1336-10 SE PROBO QUEDO EN SERVICIO | S22010800060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-08 | 72 | keep | 0 | Jan | 2022 | 4.9039e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-01-08 12:32 | 2022-01-08 12:34 | 172 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA 1620-1 Y 95% 1336-10 SE PROBO QUEDO EN SERVICIO | S22010800060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-08 | 344 | keep | 0 | Jan | 2022 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2022-01-08 12:41 | 2022-01-08 14:36 | 300 | 001:55 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S22010800063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2022-01-08 | 34500 | keep | 0 | Jan | 2022 | 0.023498 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-01-08 12:48 | 2022-01-08 14:52 | 60 | 002:04 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22010800116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 124 | 2022-01-08 | 7440 | keep | 0 | Jan | 2022 | 0.0050674 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-01-08 12:49 | 2022-01-08 15:49 | 10 | 003:00 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22010800086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2022-01-08 | 1800 | keep | 0 | Jan | 2022 | 0.001226 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-01-08 12:51 | 2022-01-08 14:55 | 60 | 002:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22010800009 | New_Event | Bad Weather | Include | Include | Weather | 124 | 2022-01-08 | 7440 | keep | 0 | Jan | 2022 | 0.0050674 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-01-08 12:52 | 2022-01-08 14:49 | 80 | 001:57 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | S22010800070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2022-01-08 | 9360 | keep | 0 | Jan | 2022 | 0.0063751 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-01-08 13:12 | 2022-01-08 13:13 | 1180 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22010800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-08 | 1180 | keep | 0 | Jan | 2022 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2022-01-08 13:12 | 2022-01-08 13:13 | 2147 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22010800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-08 | 2147 | keep | 0 | Jan | 2022 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
SAN JUAN | 2022-01-08 13:22 | 2022-01-08 13:23 | 2179 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22010800011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-08 | 2179 | keep | 0 | Jan | 2022 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
ARECIBO | 2022-01-08 13:30 | 2022-01-08 14:02 | 80 | 000:32 | P | AISLADOR ROTO, PARTIDO O SAFADO | AISLADOR PARTIDO | A22010800013 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 32 | 2022-01-08 | 2560 | keep | 0 | Jan | 2022 | 0.0017436 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-01-08 13:32 | 2022-01-08 21:16 | 60 | 007:44 | P | DESGANCHE | 1 X 80 1 X 40 Y 1 X 10 EN DISTINTOS CORTES DE LINEA REQUIEREN DESGANCHE | M22010800091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 464 | 2022-01-08 | 27840 | keep | 0 | Jan | 2022 | 0.018962 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-01-08 13:41 | 2022-01-08 19:23 | 50 | 005:42 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO PALMA | S22010800080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 342 | 2022-01-08 | 17100 | keep | 0 | Jan | 2022 | 0.011647 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-01-08 14:02 | 2022-01-08 14:03 | 3431 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR | A22010800014 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-01-08 | 3431 | keep | 0 | Jan | 2022 | 0.0023368 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-01-08 14:03 | 2022-01-08 15:04 | 80 | 001:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | AISLADOR PARTIDO | A22010800013 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 61 | 2022-01-08 | 4880 | keep | 0 | Jan | 2022 | 0.0033237 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-01-08 14:09 | 2022-01-08 16:37 | 1185 | 002:28 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | ALAMBRE PARTIDO EN TRONCAL DE ALIMENTADOR | A22010800017 | New_Event | Wire Down | Include | Include | Equipment | 148 | 2022-01-08 | 175380 | keep | 0 | Jan | 2022 | 0.11945 | 0.0008071 | Sustained | FALSE | FALSE | Not_TMED_Event | 1185
ARECIBO | 2022-01-08 14:09 | 2022-01-08 16:37 | 63 | 002:28 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | CARGA POR 8002-03 | A22010800017 | New_Event | Wire Down | Include | Include | Equipment | 148 | 2022-01-08 | 9324 | keep | 0 | Jan | 2022 | 0.0063505 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
ARECIBO | 2022-01-08 14:24 | 2022-01-08 22:57 | 79 | 008:33 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTE DE LINEA 2 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22010800019 | New_Event | Bad Weather | Include | Include | Weather | 513 | 2022-01-08 | 40527 | keep | 0 | Jan | 2022 | 0.027603 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
CAGUAS | 2022-01-08 14:33 | 2022-01-08 17:15 | 185 | 002:42 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN C/L MAL TIEMPO | C22010800057 | New_Event | Bad Weather | Include | Include | Weather | 162 | 2022-01-08 | 29970 | keep | 0 | Jan | 2022 | 0.020412 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
MAYAGÃœEZ | 2022-01-08 14:34 | 2022-01-08 14:35 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22010800103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-08 | 176 | keep | 0 | Jan | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
UTUADO | 2022-01-08 14:36 | 2022-01-08 16:50 | 100 | 002:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22010800027 | New_Event | Bad Weather | Include | Include | Weather | 134 | 2022-01-08 | 13400 | keep | 0 | Jan | 2022 | 0.0091267 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-01-08 14:37 | 2022-01-08 17:50 | 10 | 003:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON DOS CAJAS PRIMARIAS EN TRANSFORMADOR | P22010800038 | New_Event | Cutout Failure | Include | Include | Equipment | 193 | 2022-01-08 | 1930 | keep | 0 | Jan | 2022 | 0.0013145 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-01-08 14:39 | 2022-01-08 16:31 | 30 | 001:52 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22010800105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2022-01-08 | 3360 | keep | 0 | Jan | 2022 | 0.0022885 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-01-08 14:45 | 2022-01-08 19:42 | 50 | 004:57 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22010800135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 297 | 2022-01-08 | 14850 | keep | 0 | Jan | 2022 | 0.010114 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-01-08 14:47 | 2022-01-08 17:52 | 40 | 003:05 | P | DESGANCHE | 1 X 40 EN C/L | C22010800061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2022-01-08 | 7400 | keep | 0 | Jan | 2022 | 0.0050401 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-01-08 14:48 | 2022-01-08 19:50 | 3332 | 005:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADORES EN TRONCAL CON GOI BY-220108-02 | B22010800136 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 302 | 2022-01-08 | 1006264 | keep | 0 | Jan | 2022 | 0.68536 | 0.0022694 | Sustained | FALSE | FALSE | Not_TMED_Event | 3332
PONCE | 2022-01-08 14:49 | 2022-01-08 20:00 | 45 | 005:11 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN EN CORTE DE LINEA SE ELIMINO PARARRAYO AVERIADO | P22010800041 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 311 | 2022-01-08 | 13995 | keep | 0 | Jan | 2022 | 0.0095319 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-01-08 14:56 | 2022-01-08 15:43 | 75 | 000:47 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22010800063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 47 | 2022-01-08 | 3525 | keep | 0 | Jan | 2022 | 0.0024009 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2022-01-08 15:00 | 2022-01-08 15:01 | 4641 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR NEUTRAL PRIMARIO ROTO | M22010800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-01-08 | 4641 | keep | 0 | Jan | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2022-01-08 15:01 | 2022-01-08 17:23 | 100 | 002:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE REPARO NEUTRAL PRIMARIO ROTO | M22010800116 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 142 | 2022-01-08 | 14200 | keep | 0 | Jan | 2022 | 0.0096716 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-01-08 15:03 | 2022-01-09 11:17 | 25 | 020:14 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22010800034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1214 | 2022-01-08 | 30350 | keep | 0 | Jan | 2022 | 0.020671 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-01-08 15:04 | 2022-01-08 15:05 | 3431 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR AL CERRAR CORTE DE LINEA | A22010800000 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-01-08 | 3431 | keep | 0 | Jan | 2022 | 0.0023368 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-08 15:05 | 2022-01-08 16:15 | 100 | 001:10 | P | DESGANCHE | DISPARO SE ABRIO MACHETE FTE. COND. SAN IGNASIO Y SE CERRO MACHETE FTE. HOSP. METROPOLITANO 10% EN SERVICIO POR 1529-15 | S22010800093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2022-01-08 | 7000 | keep | 0 | Jan | 2022 | 0.0047677 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-01-08 15:05 | 2022-01-08 16:15 | 80 | 001:10 | P | DESGANCHE | DISPARO SE ABRIO MACHETE FTE. COND. SAN IGNASIO Y SE CERRO FTE. HOSPITAL METROPOLITANO SU CARGA POR 1529-15 | S22010800093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2022-01-08 | 5600 | keep | 0 | Jan | 2022 | 0.0038141 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-01-08 15:05 | 2022-01-08 15:28 | 1802 | 000:23 | T | DESGANCHE | DISPARO SE ABRIO CARR.21 FTE. HOSPITAL METROPOLITANO Y SE CERRO INTERRUPTOR 30% EN SERVICIO QUEDO FUERA 30% DEL 1346-2 Y PARTE DEL 1401-8 | S22010800093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 23 | 2022-01-08 | 41446 | keep | 0 | Jan | 2022 | 0.028229 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
ARECIBO | 2022-01-08 15:05 | 2022-01-08 15:55 | 80 | 000:50 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | A22010800013 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 50 | 2022-01-08 | 4000 | keep | 0 | Jan | 2022 | 0.0027244 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-01-08 15:25 | 2022-01-08 15:26 | 637 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22010800113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-08 | 637 | keep | 0 | Jan | 2022 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
BAYAMON | 2022-01-08 15:28 | 2022-01-08 16:15 | 1300 | 000:47 | P | DESGANCHE | SE ABRIO MACHETE 1346-2 FTE. COND. SAN IGNASIO Y SE CERRO MACHETE FTE. HOSP. METROPOLITANO 100% EN SERVICIO Y PARTE DEL 1401-8 Y SE DIO SERVICIO 10% DEL 1346-2 CONTINUAN PATRULLANDO | S22010800093 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 47 | 2022-01-08 | 61100 | keep | 0 | Jan | 2022 | 0.041615 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-01-08 15:33 | 2022-01-08 15:34 | 2696 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P22010800047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-08 | 2696 | keep | 0 | Jan | 2022 | 0.0018362 | 0.0018362 | Momentary | FALSE | FALSE | Not_TMED_Event | 2696
UTUADO | 2022-01-08 15:35 | 2022-01-08 17:05 | 60 | 001:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22010800044 | New_Event | Bad Weather | Include | Include | Weather | 90 | 2022-01-08 | 5400 | keep | 0 | Jan | 2022 | 0.0036779 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-01-08 15:38 | 2022-01-08 15:39 | 167 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | P22010800083 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 167 | keep | 0 | Jan | 2022 | 0.00011374 | 0.00011374 | Momentary | FALSE | FALSE | Not_TMED_Event | 167
PONCE | 2022-01-08 15:38 | 2022-01-08 15:39 | 202 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | P22010800083 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 202 | keep | 0 | Jan | 2022 | 0.00013758 | 0.00013758 | Momentary | FALSE | FALSE | Not_TMED_Event | 202
YAUCO | 2022-01-08 15:38 | 2022-01-08 15:57 | 1924 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P22010800070 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-01-08 | 36556 | keep | 0 | Jan | 2022 | 0.024898 | 0.0013104 | Sustained | FALSE | FALSE | Not_TMED_Event | 1924
YAUCO | 2022-01-08 15:38 | 2022-01-08 15:57 | 968 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P22010800070 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-01-08 | 18392 | keep | 0 | Jan | 2022 | 0.012527 | 0.0006593 | Sustained | FALSE | FALSE | Not_TMED_Event | 968
YAUCO | 2022-01-08 15:38 | 2022-01-08 15:57 | 680 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P22010800070 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-01-08 | 12920 | keep | 0 | Jan | 2022 | 0.0087998 | 0.00046314 | Sustained | FALSE | FALSE | Not_TMED_Event | 680
YAUCO | 2022-01-08 15:38 | 2022-01-08 15:57 | 2246 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P22010800070 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-01-08 | 42674 | keep | 0 | Jan | 2022 | 0.029065 | 0.0015297 | Sustained | FALSE | FALSE | Not_TMED_Event | 2246
YAUCO | 2022-01-08 15:38 | 2022-01-08 15:39 | 2011 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1200 | P22010800082 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 2011 | keep | 0 | Jan | 2022 | 0.0013697 | 0.0013697 | Momentary | FALSE | FALSE | Not_TMED_Event | 2011
YAUCO | 2022-01-08 15:38 | 2022-01-08 15:39 | 339 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1200 | P22010800082 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 339 | keep | 0 | Jan | 2022 | 0.00023089 | 0.00023089 | Momentary | FALSE | FALSE | Not_TMED_Event | 339
YAUCO | 2022-01-08 15:38 | 2022-01-08 15:39 | 2470 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8300 | P22010800072 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 2470 | keep | 0 | Jan | 2022 | 0.0016823 | 0.0016823 | Momentary | FALSE | FALSE | Not_TMED_Event | 2470
YAUCO | 2022-01-08 15:38 | 2022-01-08 15:39 | 1182 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8300 | P22010800072 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 1182 | keep | 0 | Jan | 2022 | 0.00080505 | 0.00080505 | Momentary | FALSE | FALSE | Not_TMED_Event | 1182
YAUCO | 2022-01-08 15:38 | 2022-01-08 15:39 | 2340 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8300 | P22010800072 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 2340 | keep | 0 | Jan | 2022 | 0.0015938 | 0.0015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 2340
YAUCO | 2022-01-08 15:38 | 2022-01-08 15:39 | 1637 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8300 | P22010800072 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 1637 | keep | 0 | Jan | 2022 | 0.001115 | 0.001115 | Momentary | FALSE | FALSE | Not_TMED_Event | 1637
YAUCO | 2022-01-08 15:38 | 2022-01-08 15:39 | 1475 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8300 | P22010800074 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 1475 | keep | 0 | Jan | 2022 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
YAUCO | 2022-01-08 15:38 | 2022-01-08 15:39 | 661 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8300 | P22010800074 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 661 | keep | 0 | Jan | 2022 | 0.0004502 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
YAUCO | 2022-01-08 15:38 | 2022-01-08 15:57 | 1569 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P22010800069 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-01-08 | 29811 | keep | 0 | Jan | 2022 | 0.020304 | 0.0010686 | Sustained | FALSE | FALSE | Not_TMED_Event | 1569
YAUCO | 2022-01-08 15:38 | 2022-01-08 15:57 | 2309 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P22010800069 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-01-08 | 43871 | keep | 0 | Jan | 2022 | 0.02988 | 0.0015726 | Sustained | FALSE | FALSE | Not_TMED_Event | 2309
YAUCO | 2022-01-08 15:38 | 2022-01-08 15:57 | 2179 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P22010800069 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-01-08 | 41401 | keep | 0 | Jan | 2022 | 0.028198 | 0.0014841 | Sustained | FALSE | FALSE | Not_TMED_Event | 2179
YAUCO | 2022-01-08 15:38 | 2022-01-08 15:57 | 2440 | 000:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P22010800069 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-01-08 | 46360 | keep | 0 | Jan | 2022 | 0.031576 | 0.0016619 | Sustained | FALSE | FALSE | Not_TMED_Event | 2440
YAUCO | 2022-01-08 15:38 | 2022-01-08 15:39 | 1352 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8300 | P22010800076 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 1352 | keep | 0 | Jan | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
YAUCO | 2022-01-08 15:38 | 2022-01-08 15:39 | 3973 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8300 | P22010800076 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 3973 | keep | 0 | Jan | 2022 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2022-01-08 15:38 | 2022-01-08 15:39 | 2484 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8300 | P22010800076 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 2484 | keep | 0 | Jan | 2022 | 0.0016918 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
MAYAGÃœEZ | 2022-01-08 15:38 | 2022-01-08 15:40 | 281 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | M22010800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-01-08 | 562 | keep | 0 | Jan | 2022 | 0.00038278 | 0.00019139 | Momentary | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2022-01-08 15:38 | 2022-01-08 15:40 | 1252 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | M22010800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-01-08 | 2504 | keep | 0 | Jan | 2022 | 0.0017055 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2022-01-08 15:38 | 2022-01-08 15:40 | 1268 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1200 | M22010800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-01-08 | 2536 | keep | 0 | Jan | 2022 | 0.0017273 | 0.00086363 | Momentary | FALSE | FALSE | Not_TMED_Event | 1268
MAYAGÃœEZ | 2022-01-08 15:38 | 2022-01-08 15:40 | 2064 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1200 | M22010800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-01-08 | 4128 | keep | 0 | Jan | 2022 | 0.0028116 | 0.0014058 | Momentary | FALSE | FALSE | Not_TMED_Event | 2064
MAYAGÃœEZ | 2022-01-08 15:38 | 2022-01-08 15:40 | 3036 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1200 | M22010800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-01-08 | 6072 | keep | 0 | Jan | 2022 | 0.0041356 | 0.0020678 | Momentary | FALSE | FALSE | Not_TMED_Event | 3036
MAYAGÃœEZ | 2022-01-08 15:38 | 2022-01-08 15:40 | 2952 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1200 | M22010800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-01-08 | 5904 | keep | 0 | Jan | 2022 | 0.0040212 | 0.0020106 | Momentary | FALSE | FALSE | Not_TMED_Event | 2952
MAYAGÃœEZ | 2022-01-08 15:38 | 2022-01-08 15:40 | 595 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | M22010800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-01-08 | 1190 | keep | 0 | Jan | 2022 | 0.0008105 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
MAYAGÃœEZ | 2022-01-08 15:38 | 2022-01-08 15:40 | 51 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | M22010800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-01-08 | 102 | keep | 0 | Jan | 2022 | 6.9472e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2022-01-08 15:38 | 2022-01-08 15:40 | 721 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | M22010800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-01-08 | 1442 | keep | 0 | Jan | 2022 | 0.00098214 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2022-01-08 15:38 | 2022-01-08 15:39 | 3316 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1200 | A22010800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 3316 | keep | 0 | Jan | 2022 | 0.0022585 | 0.0022585 | Momentary | FALSE | FALSE | Not_TMED_Event | 3316
UTUADO | 2022-01-08 15:38 | 2022-01-08 15:39 | 1241 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1200 | A22010800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 1241 | keep | 0 | Jan | 2022 | 0.00084524 | 0.00084524 | Momentary | FALSE | FALSE | Not_TMED_Event | 1241
UTUADO | 2022-01-08 15:38 | 2022-01-08 15:39 | 650 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1200 | A22010800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 650 | keep | 0 | Jan | 2022 | 0.00044271 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
UTUADO | 2022-01-08 15:38 | 2022-01-08 15:39 | 1382 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1200 | A22010800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 1382 | keep | 0 | Jan | 2022 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2022-01-08 15:38 | 2022-01-08 15:39 | 654 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1200 | A22010800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 654 | keep | 0 | Jan | 2022 | 0.00044544 | 0.00044544 | Momentary | FALSE | FALSE | Not_TMED_Event | 654
MAYAGÃœEZ | 2022-01-08 15:44 | 2022-01-08 17:14 | 70 | 001:30 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M22010800121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2022-01-08 | 6300 | keep | 0 | Jan | 2022 | 0.0042909 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-01-08 15:50 | 2022-01-08 15:52 | 225 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO SU CARGA POR 1303-5 | S22010800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-08 | 450 | keep | 0 | Jan | 2022 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-01-08 15:50 | 2022-01-08 15:52 | 870 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1303-4 | S22010800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-08 | 1740 | keep | 0 | Jan | 2022 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-01-08 15:54 | 2022-01-08 18:28 | 12 | 002:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 25 EN TRANSFORMADOR SE REPARO TOMA Y SECUNDARIA | S22010800090 | New_Event | Secondary Wire Down | Include | Include | Equipment | 154 | 2022-01-08 | 1848 | keep | 0 | Jan | 2022 | 0.0012587 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-01-08 15:55 | 2022-01-08 16:35 | 20 | 000:40 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL SOBRE LINEA | A22010800018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 40 | 2022-01-08 | 800 | keep | 0 | Jan | 2022 | 0.00054488 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-01-08 15:55 | 2022-01-08 18:43 | 44 | 002:48 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHO Y ENDEREZO POSTE | C22010800075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2022-01-08 | 7392 | keep | 0 | Jan | 2022 | 0.0050347 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
PONCE | 2022-01-08 15:57 | 2022-01-08 19:34 | 238 | 003:37 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA CRUCE DE FASES PRIMARIAS POR RAMA | P22010800067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2022-01-08 | 51646 | keep | 0 | Jan | 2022 | 0.035176 | 0.0001621 | Sustained | FALSE | FALSE | Not_TMED_Event | 238
AGUADILLA | 2022-01-08 16:12 | 2022-01-08 19:15 | 75 | 003:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO | M22010800128 | New_Event | Wire Down | Include | Include | Equipment | 183 | 2022-01-08 | 13725 | keep | 0 | Jan | 2022 | 0.009348 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2022-01-08 16:15 | 2022-01-08 16:45 | 435 | 000:30 | P | DESGANCHE | RAMA SOBRE LINEA CALLE SAN GUILLERMO Y SE CERRO MACHETE 20% EN SERVICIO FTE. CON. SAN IGNASIO | S22010800093 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 30 | 2022-01-08 | 13050 | keep | 0 | Jan | 2022 | 0.0088883 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-08 16:18 | 2022-01-08 19:25 | 272 | 003:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO EN LINEA PRIMARIA | P22010800081 | New_Event | Wire Down | Include | Include | Equipment | 187 | 2022-01-08 | 50864 | keep | 0 | Jan | 2022 | 0.034643 | 0.00018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 272
ARECIBO | 2022-01-08 16:24 | 2022-01-08 19:05 | 25 | 002:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A22010800057 | New_Event | Wire Down | Include | Include | Equipment | 161 | 2022-01-08 | 4025 | keep | 0 | Jan | 2022 | 0.0027414 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-01-08 16:31 | 2022-01-08 16:33 | 225 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1303-5 | S22010800000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-08 | 450 | keep | 0 | Jan | 2022 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-01-08 16:31 | 2022-01-08 16:33 | 870 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO LLEVA 1303-4 | S22010800000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-08 | 1740 | keep | 0 | Jan | 2022 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
ARECIBO | 2022-01-08 16:37 | 2022-01-08 17:10 | 458 | 000:33 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RETIRO CARGA A SUBESTACION PARA REPARAR ALAMBRE PARTIDO DE INTERRUPTOR 8002-03 SOBRE BARRA DE SUBESTACION | A22010800064 | New_Event | Wire Down | Include | Include | Equipment | 33 | 2022-01-08 | 15114 | keep | 0 | Jan | 2022 | 0.010294 | 0.00031194 | Sustained | FALSE | FALSE | Not_TMED_Event | 458
ARECIBO | 2022-01-08 16:37 | 2022-01-08 17:10 | 437 | 000:33 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RETIRO CARGA A SUBESTACION PARA REPARAR ALAMBRE PARTIDO DE INTERRUPTOR 8002-03 SOBRE BARRA DE SUBESTACION | A22010800064 | New_Event | Wire Down | Include | Include | Equipment | 33 | 2022-01-08 | 14421 | keep | 0 | Jan | 2022 | 0.0098221 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
ARECIBO | 2022-01-08 16:37 | 2022-01-08 17:10 | 1185 | 000:33 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RETIRO CARGA A SUBESTACION PARA REPARAR ALAMBRE PARTIDO DE INTERRUPTOR 8002-03 SOBRE BARRA DE SUBESTACION | A22010800064 | Partial_restoration | Wire Down | Include | Include | Equipment | 33 | 2022-01-08 | 39105 | keep | 0 | Jan | 2022 | 0.026634 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-01-08 16:37 | 2022-01-08 17:10 | 63 | 000:33 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RETIRO CARGA A SUBESTACION PARA REPARAR ALAMBRE PARTIDO DE INTERRUPTOR 8002-03 SOBRE BARRA DE SUBESTACION | A22010800064 | Partial_restoration | Wire Down | Include | Include | Equipment | 33 | 2022-01-08 | 2079 | keep | 0 | Jan | 2022 | 0.001416 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-01-08 16:37 | 2022-01-08 17:10 | 232 | 000:33 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RETIRO CARGA A SUBESTACION PARA REPARAR ALAMBRE PARTIDO DE INTERRUPTOR 8002-03 SOBRE BARRA DE SUBESTACION | A22010800064 | New_Event | Wire Down | Include | Include | Equipment | 33 | 2022-01-08 | 7656 | keep | 0 | Jan | 2022 | 0.0052145 | 0.00015801 | Sustained | FALSE | FALSE | Not_TMED_Event | 232
CANOVANAS | 2022-01-08 16:54 | 2022-01-08 20:25 | 8 | 003:31 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE, REPARO BAJANTE PRIMARIO Y SECUNDARIO | R22010800018 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 211 | 2022-01-08 | 1688 | keep | 0 | Jan | 2022 | 0.0011497 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-01-08 17:00 | 2022-01-08 18:07 | 45 | 001:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN C/L CRUCE X AVE | C22010800087 | New_Event |  |  | Include | Wildlife | 67 | 2022-01-08 | 3015 | keep | 0 | Jan | 2022 | 0.0020535 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2022-01-08 17:29 | 2022-01-08 17:58 | 4 | 000:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO NEUTRAL SECUNDARIO Y RESETEO XMR | C22010800091 | New_Event | Secondary Wire Down | Include | Include | Equipment | 29 | 2022-01-08 | 116 | keep | 0 | Jan | 2022 | 7.9007e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2022-01-08 17:42 | 2022-01-08 18:13 | 55 | 000:31 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P22010800090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 31 | 2022-01-08 | 1705 | keep | 0 | Jan | 2022 | 0.0011613 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
PONCE | 2022-01-08 17:55 | 2022-01-08 19:00 | 179 | 001:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA ALAMBRE PRIMARIO EN EL PISO | P22010800091 | New_Event | Wire Down | Include | Include | Equipment | 65 | 2022-01-08 | 11635 | keep | 0 | Jan | 2022 | 0.0079245 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
YAUCO | 2022-01-08 18:12 | 2022-01-09 08:30 | 102 | 014:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA FUERTE LLUVIA | P22010800095 | New_Event | Bad Weather | Include | Include | Weather | 858 | 2022-01-08 | 87516 | keep | 0 | Jan | 2022 | 0.059607 | 6.9472e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 102
ARECIBO | 2022-01-08 18:14 | 2022-01-08 19:35 | 150 | 001:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22010800071 | New_Event | Bad Weather | Include | Include | Weather | 81 | 2022-01-08 | 12150 | keep | 0 | Jan | 2022 | 0.0082753 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-01-08 18:46 | 2022-01-08 23:17 | 10 | 004:31 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 75 KVA X 75 KVA | R22010800021 | New_Event | Service Transformer Failure | Include | Include | Equipment | 271 | 2022-01-08 | 2710 | keep | 0 | Jan | 2022 | 0.0018458 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-08 18:47 | 2022-01-08 18:48 | 1834 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22010800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-08 | 1834 | keep | 0 | Jan | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
CAGUAS | 2022-01-08 19:22 | 2022-01-09 10:20 | 60 | 014:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 SMU 20 DE 25 AMP. SE RETIRO REPTIL DEL T-24 | C22010800107 | New_Event |  |  | Include | Wildlife | 898 | 2022-01-08 | 53880 | keep | 0 | Jan | 2022 | 0.036697 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-01-08 19:36 | 2022-01-09 09:32 | 116 | 013:56 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C22010800108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 836 | 2022-01-08 | 96976 | keep | 0 | Jan | 2022 | 0.06605 | 7.9007e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 116
YAUCO | 2022-01-08 19:36 | 2022-01-09 10:45 | 31 | 015:09 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE ELIMINO PARARRAYO AVERIADO | P22010800100 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 909 | 2022-01-08 | 28179 | keep | 0 | Jan | 2022 | 0.019193 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
ARECIBO | 2022-01-08 19:55 | 2022-01-08 21:35 | 10 | 001:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA CRUZADA | A22010800089 | New_Event | Secondary Wire Down | Include | Include | Equipment | 100 | 2022-01-08 | 1000 | keep | 0 | Jan | 2022 | 0.0006811 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-08 20:21 | 2022-01-08 20:22 | 2694 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22010800092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-08 | 2694 | keep | 0 | Jan | 2022 | 0.0018349 | 0.0018349 | Momentary | FALSE | FALSE | Not_TMED_Event | 2694
ARECIBO | 2022-01-08 20:59 | 2022-01-09 12:34 | 65 | 015:35 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22010800084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 935 | 2022-01-08 | 60775 | keep | 0 | Jan | 2022 | 0.041394 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
ARECIBO | 2022-01-08 21:16 | 2022-01-09 00:06 | 50 | 002:50 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22010800095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2022-01-08 | 8500 | keep | 0 | Jan | 2022 | 0.0057893 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-01-08 21:34 | 2022-01-08 23:04 | 25 | 001:30 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REQUIERE DESGANCHE | M22010800148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2022-01-08 | 2250 | keep | 0 | Jan | 2022 | 0.0015325 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-01-08 22:00 | 2022-01-09 08:36 | 9 | 010:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN XMR REEMPLAZO PORTAFUSIBLE | R22010800025 | New_Event | Cutout Failure | Include | Include | Equipment | 636 | 2022-01-08 | 5724 | keep | 0 | Jan | 2022 | 0.0038986 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
FAJARDO | 2022-01-08 22:13 | 2022-01-09 16:16 | 21 | 018:03 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN C/L SE CONSTRUYO PROVICIONAL AEREO DEL T - 1A AL T - 4A | R22010800029 | New_Event | UG Cable Fault | Include | Include | Equipment | 1083 | 2022-01-08 | 22743 | keep | 0 | Jan | 2022 | 0.01549 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
MAYAGÃœEZ | 2022-01-08 22:15 | 2022-01-09 11:14 | 300 | 012:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CONVERTIDOR SE SECCIONALIZO LINEA PRIMARIA PARTIDA | M22010800158 | New_Event | Wire Down | Include | Include | Equipment | 779 | 2022-01-08 | 233700 | keep | 0 | Jan | 2022 | 0.15917 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
GUAYAMA | 2022-01-08 23:54 | 2022-01-08 23:55 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010800113 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 2100 | keep | 0 | Jan | 2022 | 0.0014303 | 0.0014303 | Momentary | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-01-08 23:54 | 2022-01-08 23:55 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010800113 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 922 | keep | 0 | Jan | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-01-08 23:54 | 2022-01-08 23:55 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010800113 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 1676 | keep | 0 | Jan | 2022 | 0.0011415 | 0.0011415 | Momentary | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-01-08 23:54 | 2022-01-08 23:55 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010800113 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 2844 | keep | 0 | Jan | 2022 | 0.001937 | 0.001937 | Momentary | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-01-08 23:54 | 2022-01-08 23:55 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010800113 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 2775 | keep | 0 | Jan | 2022 | 0.00189 | 0.00189 | Momentary | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-01-08 23:54 | 2022-01-08 23:55 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010800113 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 1457 | keep | 0 | Jan | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-01-08 23:54 | 2022-01-08 23:55 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010800113 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 1086 | keep | 0 | Jan | 2022 | 0.00073967 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-01-08 23:54 | 2022-01-08 23:55 | 2134 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010800113 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 2134 | keep | 0 | Jan | 2022 | 0.0014535 | 0.0014535 | Momentary | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-01-08 23:54 | 2022-01-08 23:55 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010800113 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 1464 | keep | 0 | Jan | 2022 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-01-08 23:54 | 2022-01-08 23:55 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010800113 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 1833 | keep | 0 | Jan | 2022 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-01-08 23:54 | 2022-01-08 23:55 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010800113 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 1565 | keep | 0 | Jan | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-01-08 23:54 | 2022-01-08 23:55 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010800113 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-08 | 977 | keep | 0 | Jan | 2022 | 0.00066543 | 0.00066543 | Momentary | FALSE | FALSE | Not_TMED_Event | 977
BARRANQUITAS | 2022-01-09 00:41 | 2022-01-09 14:02 | 251 | 013:21 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO DISCO Y DESGANCHARON | C22010900001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 801 | 2022-01-09 | 201051 | keep | 0 | Jan | 2022 | 0.13693 | 0.00017095 | Sustained | FALSE | FALSE | Not_TMED_Event | 251
ARECIBO | 2022-01-09 02:34 | 2022-01-09 09:35 | 100 | 007:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22010900002 | New_Event | Bad Weather | Include | Include | Weather | 421 | 2022-01-09 | 42100 | keep | 0 | Jan | 2022 | 0.028674 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-01-09 02:39 | 2022-01-09 02:40 | 2073 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22010900003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-09 | 2073 | keep | 0 | Jan | 2022 | 0.0014119 | 0.0014119 | Momentary | FALSE | FALSE | Not_TMED_Event | 2073
HUMACAO | 2022-01-09 04:13 | 2022-01-09 04:30 | 1891 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | C22010900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-01-09 | 32147 | keep | 0 | Jan | 2022 | 0.021895 | 0.001288 | Sustained | FALSE | FALSE | Not_TMED_Event | 1891
HUMACAO | 2022-01-09 04:13 | 2022-01-09 04:30 | 1250 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | C22010900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-01-09 | 21250 | keep | 0 | Jan | 2022 | 0.014473 | 0.00085137 | Sustained | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2022-01-09 04:13 | 2022-01-09 04:30 | 2141 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | C22010900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-01-09 | 36397 | keep | 0 | Jan | 2022 | 0.02479 | 0.0014582 | Sustained | FALSE | FALSE | Not_TMED_Event | 2141
HUMACAO | 2022-01-09 04:13 | 2022-01-09 04:30 | 1827 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | C22010900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-01-09 | 31059 | keep | 0 | Jan | 2022 | 0.021154 | 0.0012444 | Sustained | FALSE | FALSE | Not_TMED_Event | 1827
GUAYAMA | 2022-01-09 04:13 | 2022-01-09 04:30 | 2100 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P22010900002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-01-09 | 35700 | keep | 0 | Jan | 2022 | 0.024315 | 0.0014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-01-09 04:13 | 2022-01-09 04:30 | 922 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P22010900002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-01-09 | 15674 | keep | 0 | Jan | 2022 | 0.010675 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-01-09 04:13 | 2022-01-09 04:30 | 1676 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P22010900002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-01-09 | 28492 | keep | 0 | Jan | 2022 | 0.019406 | 0.0011415 | Sustained | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-01-09 04:13 | 2022-01-09 04:30 | 2844 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P22010900002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-01-09 | 48348 | keep | 0 | Jan | 2022 | 0.03293 | 0.001937 | Sustained | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-01-09 04:13 | 2022-01-09 04:30 | 2775 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P22010900002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-01-09 | 47175 | keep | 0 | Jan | 2022 | 0.032131 | 0.00189 | Sustained | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-01-09 04:13 | 2022-01-09 04:30 | 1457 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P22010900002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-01-09 | 24769 | keep | 0 | Jan | 2022 | 0.01687 | 0.00099236 | Sustained | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-01-09 04:13 | 2022-01-09 04:30 | 1086 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P22010900002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-01-09 | 18462 | keep | 0 | Jan | 2022 | 0.012574 | 0.00073967 | Sustained | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-01-09 04:13 | 2022-01-09 04:30 | 2134 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P22010900002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-01-09 | 36278 | keep | 0 | Jan | 2022 | 0.024709 | 0.0014535 | Sustained | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-01-09 04:13 | 2022-01-09 04:30 | 1464 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P22010900002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-01-09 | 24888 | keep | 0 | Jan | 2022 | 0.016951 | 0.00099712 | Sustained | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-01-09 04:13 | 2022-01-09 04:30 | 1833 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P22010900002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-01-09 | 31161 | keep | 0 | Jan | 2022 | 0.021224 | 0.0012484 | Sustained | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-01-09 04:13 | 2022-01-09 04:30 | 1565 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P22010900002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-01-09 | 26605 | keep | 0 | Jan | 2022 | 0.018121 | 0.0010659 | Sustained | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-01-09 04:13 | 2022-01-09 04:30 | 977 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P22010900002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-01-09 | 16609 | keep | 0 | Jan | 2022 | 0.011312 | 0.00066543 | Sustained | FALSE | FALSE | Not_TMED_Event | 977
GUAYAMA | 2022-01-09 04:29 | 2022-01-09 04:30 | 464 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22010900019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-09 | 464 | keep | 0 | Jan | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
AGUADILLA | 2022-01-09 04:57 | 2022-01-09 04:58 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22010900007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-09 | 1192 | keep | 0 | Jan | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
ARECIBO | 2022-01-09 05:15 | 2022-01-09 06:44 | 1100 | 001:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA AVERIADA | A22010900004 | New_Event | Wire Down | Include | Include | Equipment | 89 | 2022-01-09 | 97900 | keep | 0 | Jan | 2022 | 0.066679 | 0.0007492 | Sustained | FALSE | FALSE | Not_TMED_Event | 1100
BAYAMON | 2022-01-09 05:21 | 2022-01-09 05:22 | 750 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO SOLO LLEVA EL 50% DE SU CARGA Y LLEVA LA CARGA DEL 1709-05 | S22010900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-09 | 750 | keep | 0 | Jan | 2022 | 0.00051082 | 0.00051082 | Momentary | FALSE | FALSE | Not_TMED_Event | 750
BAYAMON | 2022-01-09 05:21 | 2022-01-09 05:22 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA TRANSFERIDA AL 1709-03 | S22010900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-09 | 2364 | keep | 0 | Jan | 2022 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
FAJARDO | 2022-01-09 06:32 | 2022-01-09 11:07 | 90 | 004:35 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R22010900003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2022-01-09 | 24750 | keep | 0 | Jan | 2022 | 0.016857 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2022-01-09 06:43 | 2022-01-09 06:44 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22010900008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-09 | 108 | keep | 0 | Jan | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
ARECIBO | 2022-01-09 06:44 | 2022-01-09 07:09 | 2132 | 000:25 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR MANUAL (NO RTU) PARA RETIRAR PELIGRO SE ABRIO MACHETES | A22010900000 | Additional_clients | Wire Down | Include | Include | Equipment | 25 | 2022-01-09 | 53300 | keep | 0 | Jan | 2022 | 0.036302 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-01-09 07:09 | 2022-01-09 23:03 | 1132 | 015:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA Y SE REMPLAZO CRUCETA PARTIDA SE CERRO MACHETES | A22010900010 | Partial_restoration | Wire Down | Include | Include | Equipment | 954 | 2022-01-09 | 1079928 | keep | 0 | Jan | 2022 | 0.73553 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-01-09 07:18 | 2022-01-09 07:19 | 2635 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO INTERRUPTOR MAL TIEMPO EN SERVICIO | C22010900023 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-01-09 | 2635 | keep | 0 | Jan | 2022 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2022-01-09 07:19 | 2022-01-09 09:09 | 491 | 001:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO | C22010900027 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 110 | 2022-01-09 | 54010 | keep | 0 | Jan | 2022 | 0.036786 | 0.00033442 | Sustained | FALSE | FALSE | Not_TMED_Event | 491
HUMACAO | 2022-01-09 07:24 | 2022-01-09 07:25 | 1891 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3700 DE JOBOS A YABUCOA | C22010900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1891 | keep | 0 | Jan | 2022 | 0.001288 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-01-09 07:24 | 2022-01-09 07:25 | 1250 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3700 DE JOBOS A YABUCOA | C22010900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1250 | keep | 0 | Jan | 2022 | 0.00085137 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-01-09 07:24 | 2022-01-09 07:25 | 2141 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3700 DE JOBOS A YABUCOA | C22010900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 2141 | keep | 0 | Jan | 2022 | 0.0014582 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-01-09 07:24 | 2022-01-09 07:25 | 1827 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3700 DE JOBOS A YABUCOA | C22010900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1827 | keep | 0 | Jan | 2022 | 0.0012444 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-09 07:24 | 2022-01-09 07:25 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22010900024 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 2100 | keep | 0 | Jan | 2022 | 0.0014303 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-09 07:24 | 2022-01-09 07:25 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22010900024 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 922 | keep | 0 | Jan | 2022 | 0.00062797 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-09 07:24 | 2022-01-09 07:25 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22010900024 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1676 | keep | 0 | Jan | 2022 | 0.0011415 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-09 07:24 | 2022-01-09 07:25 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22010900024 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 2844 | keep | 0 | Jan | 2022 | 0.001937 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-09 07:24 | 2022-01-09 07:25 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22010900026 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 2775 | keep | 0 | Jan | 2022 | 0.00189 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-09 07:24 | 2022-01-09 07:25 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22010900026 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1457 | keep | 0 | Jan | 2022 | 0.00099236 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-09 07:24 | 2022-01-09 07:25 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22010900026 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1086 | keep | 0 | Jan | 2022 | 0.00073967 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-09 07:24 | 2022-01-09 07:25 | 2134 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22010900026 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 2134 | keep | 0 | Jan | 2022 | 0.0014535 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-09 07:24 | 2022-01-09 07:25 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22010900027 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1464 | keep | 0 | Jan | 2022 | 0.00099712 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-09 07:24 | 2022-01-09 07:25 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22010900027 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1833 | keep | 0 | Jan | 2022 | 0.0012484 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-09 07:24 | 2022-01-09 07:25 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22010900027 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1565 | keep | 0 | Jan | 2022 | 0.0010659 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-09 07:24 | 2022-01-09 07:25 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22010900027 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 977 | keep | 0 | Jan | 2022 | 0.00066543 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-09 07:36 | 2022-01-09 12:00 | 153 | 004:24 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA ARBOL CAYO SOBRE LINEA MONOFASICA Y LA TUMBO, SE DEJO SECCIONALIZADA | C22010900026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 264 | 2022-01-09 | 40392 | keep | 0 | Jan | 2022 | 0.027511 | 0.00010421 | Sustained | FALSE | FALSE | Not_TMED_Event | 153
HUMACAO | 2022-01-09 07:37 | 2022-01-09 07:38 | 1891 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3700 DE JOBOS A YABUCOA | C22010900000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1891 | keep | 0 | Jan | 2022 | 0.001288 | 0.001288 | Momentary | FALSE | FALSE | Not_TMED_Event | 1891
HUMACAO | 2022-01-09 07:37 | 2022-01-09 07:38 | 1250 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3700 DE JOBOS A YABUCOA | C22010900000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1250 | keep | 0 | Jan | 2022 | 0.00085137 | 0.00085137 | Momentary | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2022-01-09 07:37 | 2022-01-09 07:38 | 2141 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3700 DE JOBOS A YABUCOA | C22010900000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 2141 | keep | 0 | Jan | 2022 | 0.0014582 | 0.0014582 | Momentary | FALSE | FALSE | Not_TMED_Event | 2141
HUMACAO | 2022-01-09 07:37 | 2022-01-09 07:38 | 1827 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3700 DE JOBOS A YABUCOA | C22010900000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1827 | keep | 0 | Jan | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
GUAYAMA | 2022-01-09 07:37 | 2022-01-09 07:38 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22010900035 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 2100 | keep | 0 | Jan | 2022 | 0.0014303 | 0.0014303 | Momentary | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-01-09 07:37 | 2022-01-09 07:38 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22010900035 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 922 | keep | 0 | Jan | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-01-09 07:37 | 2022-01-09 07:38 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22010900035 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1676 | keep | 0 | Jan | 2022 | 0.0011415 | 0.0011415 | Momentary | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-01-09 07:37 | 2022-01-09 07:38 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22010900035 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 2844 | keep | 0 | Jan | 2022 | 0.001937 | 0.001937 | Momentary | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-01-09 07:37 | 2022-01-09 07:38 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22010900033 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 2775 | keep | 0 | Jan | 2022 | 0.00189 | 0.00189 | Momentary | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-01-09 07:37 | 2022-01-09 07:38 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22010900033 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1457 | keep | 0 | Jan | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-01-09 07:37 | 2022-01-09 07:38 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22010900033 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1086 | keep | 0 | Jan | 2022 | 0.00073967 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-01-09 07:37 | 2022-01-09 07:38 | 2134 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22010900033 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 2134 | keep | 0 | Jan | 2022 | 0.0014535 | 0.0014535 | Momentary | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-01-09 07:37 | 2022-01-09 07:38 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22010900032 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1464 | keep | 0 | Jan | 2022 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-01-09 07:37 | 2022-01-09 07:38 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22010900032 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1833 | keep | 0 | Jan | 2022 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-01-09 07:37 | 2022-01-09 07:38 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22010900032 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1565 | keep | 0 | Jan | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-01-09 07:37 | 2022-01-09 07:38 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3700 | P22010900032 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 977 | keep | 0 | Jan | 2022 | 0.00066543 | 0.00066543 | Momentary | FALSE | FALSE | Not_TMED_Event | 977
MAYAGÃœEZ | 2022-01-09 07:38 | 2022-01-09 07:39 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22010900009 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-09 | 108 | keep | 0 | Jan | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
BARRANQUITAS | 2022-01-09 07:47 | 2022-01-09 14:29 | 307 | 006:42 | P | DESGANCHE | 1 X 100 Y 1 X 80 EN CORTE DE LINEA | C22010900034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 402 | 2022-01-09 | 123414 | keep | 0 | Jan | 2022 | 0.084057 | 0.0002091 | Sustained | FALSE | FALSE | Not_TMED_Event | 307
CAGUAS | 2022-01-09 07:51 | 2022-01-09 15:42 | 270 | 007:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO SE ABRIO CORTE DE LINEA TOTAL PARA TRABAJAR | C22010900036 | New_Event | Wire Down | Include | Include | Equipment | 471 | 2022-01-09 | 127170 | keep | 0 | Jan | 2022 | 0.086615 | 0.0001839 | Sustained | FALSE | FALSE | Not_TMED_Event | 270
BAYAMON | 2022-01-09 07:53 | 2022-01-09 09:32 | 40 | 001:39 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B22010900004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2022-01-09 | 3960 | keep | 0 | Jan | 2022 | 0.0026971 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2022-01-09 08:03 | 2022-01-09 16:15 | 35 | 008:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO DE CAJA PRIMARIA EN CORTE DE LINEA 1 X 80 EN CORTE DE LINEA | P22010900043 | New_Event | Cutout Failure | Include | Include | Equipment | 492 | 2022-01-09 | 17220 | keep | 0 | Jan | 2022 | 0.011728 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
GUAYAMA | 2022-01-09 08:17 | 2022-01-09 09:04 | 2100 | 000:47 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22010900055 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 47 | 2022-01-09 | 98700 | keep | 0 | Jan | 2022 | 0.067224 | 0.0014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-01-09 08:17 | 2022-01-09 09:04 | 922 | 000:47 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22010900055 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 47 | 2022-01-09 | 43334 | keep | 0 | Jan | 2022 | 0.029515 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-01-09 08:17 | 2022-01-09 09:04 | 1676 | 000:47 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22010900055 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 47 | 2022-01-09 | 78772 | keep | 0 | Jan | 2022 | 0.053651 | 0.0011415 | Sustained | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-01-09 08:17 | 2022-01-09 09:04 | 2775 | 000:47 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22010900058 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 47 | 2022-01-09 | 130425 | keep | 0 | Jan | 2022 | 0.088832 | 0.00189 | Sustained | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-01-09 08:17 | 2022-01-09 09:04 | 1457 | 000:47 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22010900058 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 47 | 2022-01-09 | 68479 | keep | 0 | Jan | 2022 | 0.046641 | 0.00099236 | Sustained | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-01-09 08:17 | 2022-01-09 09:04 | 1086 | 000:47 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22010900058 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 47 | 2022-01-09 | 51042 | keep | 0 | Jan | 2022 | 0.034764 | 0.00073967 | Sustained | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-01-09 08:17 | 2022-01-09 09:04 | 2134 | 000:47 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22010900058 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 47 | 2022-01-09 | 100298 | keep | 0 | Jan | 2022 | 0.068313 | 0.0014535 | Sustained | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-01-09 08:17 | 2022-01-09 09:04 | 1464 | 000:47 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22010900059 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 47 | 2022-01-09 | 68808 | keep | 0 | Jan | 2022 | 0.046865 | 0.00099712 | Sustained | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-01-09 08:17 | 2022-01-09 09:04 | 1833 | 000:47 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22010900059 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 47 | 2022-01-09 | 86151 | keep | 0 | Jan | 2022 | 0.058677 | 0.0012484 | Sustained | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-01-09 08:17 | 2022-01-09 09:04 | 1565 | 000:47 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22010900059 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 47 | 2022-01-09 | 73555 | keep | 0 | Jan | 2022 | 0.050098 | 0.0010659 | Sustained | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-01-09 08:17 | 2022-01-09 09:04 | 977 | 000:47 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22010900059 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 47 | 2022-01-09 | 45919 | keep | 0 | Jan | 2022 | 0.031275 | 0.00066543 | Sustained | FALSE | FALSE | Not_TMED_Event | 977
HUMACAO | 2022-01-09 08:18 | 2022-01-09 09:04 | 1891 | 000:46 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3700 DE JOBOS A YABUCOA | C22010900000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 46 | 2022-01-09 | 86986 | keep | 0 | Jan | 2022 | 0.059246 | 0.001288 | Sustained | FALSE | FALSE | Not_TMED_Event | 1891
HUMACAO | 2022-01-09 08:18 | 2022-01-09 09:04 | 1250 | 000:46 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3700 DE JOBOS A YABUCOA | C22010900000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 46 | 2022-01-09 | 57500 | keep | 0 | Jan | 2022 | 0.039163 | 0.00085137 | Sustained | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2022-01-09 08:18 | 2022-01-09 09:04 | 2141 | 000:46 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3700 DE JOBOS A YABUCOA | C22010900000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 46 | 2022-01-09 | 98486 | keep | 0 | Jan | 2022 | 0.067078 | 0.0014582 | Sustained | FALSE | FALSE | Not_TMED_Event | 2141
HUMACAO | 2022-01-09 08:18 | 2022-01-09 09:04 | 1827 | 000:46 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3700 DE JOBOS A YABUCOA | C22010900000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 46 | 2022-01-09 | 84042 | keep | 0 | Jan | 2022 | 0.057241 | 0.0012444 | Sustained | FALSE | FALSE | Not_TMED_Event | 1827
MAYAGÃœEZ | 2022-01-09 08:42 | 2022-01-09 13:22 | 20 | 004:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22010900015 | New_Event | Bad Weather | Include | Include | Weather | 280 | 2022-01-09 | 5600 | keep | 0 | Jan | 2022 | 0.0038141 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-01-09 08:49 | 2022-01-09 11:11 | 60 | 002:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22010900019 | New_Event | Bad Weather | Include | Include | Weather | 142 | 2022-01-09 | 8520 | keep | 0 | Jan | 2022 | 0.0058029 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-01-09 09:05 | 2022-01-09 11:40 | 75 | 002:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN RISER 1 X 50 EN RISER 1 X 40 EN SU #11 SE RETIRO SERVICIO A GARAJE DE GASOLINA PUMA EL CUAL TIENE DEFECTO INTERNO | P22010900079 | New_Event | Cutout Failure | Include | Include | Equipment | 155 | 2022-01-09 | 11625 | keep | 0 | Jan | 2022 | 0.0079177 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BARRANQUITAS | 2022-01-09 09:09 | 2022-01-09 09:10 | 2635 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 6500 DE BARRANQUITAS A TORO NEGRO | C22010900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 2635 | keep | 0 | Jan | 2022 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2022-01-09 09:09 | 2022-01-09 09:10 | 2280 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 6500 DE BARRANQUITAS A TORO NEGRO | C22010900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 2280 | keep | 0 | Jan | 2022 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2022-01-09 09:09 | 2022-01-09 09:10 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 6500 DE BARRANQUITAS A TORO NEGRO | C22010900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1617 | keep | 0 | Jan | 2022 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
BARRANQUITAS | 2022-01-09 09:10 | 2022-01-09 15:34 | 491 | 006:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO | C22010900027 | Partial_restoration | Bad Weather | Include | Include | Weather | 384 | 2022-01-09 | 188544 | keep | 0 | Jan | 2022 | 0.12842 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-01-09 09:16 | 2022-01-09 09:17 | 863 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR MAL TIEMPO VIENTOS FUERTES | M22010900028 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-01-09 | 863 | keep | 0 | Jan | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
PONCE | 2022-01-09 09:21 | 2022-01-09 16:22 | 8 | 007:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA FUERTE BRISA | A22010900023 | New_Event | Bad Weather | Include | Include | Weather | 421 | 2022-01-09 | 3368 | keep | 0 | Jan | 2022 | 0.0022939 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-01-09 09:27 | 2022-01-09 09:32 | 1891 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3700 DE JOBOS A YABUCOA | C22010900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-01-09 | 9455 | keep | 0 | Jan | 2022 | 0.0064398 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-01-09 09:27 | 2022-01-09 09:32 | 1250 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3700 DE JOBOS A YABUCOA | C22010900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-01-09 | 6250 | keep | 0 | Jan | 2022 | 0.0042568 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-01-09 09:27 | 2022-01-09 09:32 | 2141 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3700 DE JOBOS A YABUCOA | C22010900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-01-09 | 10705 | keep | 0 | Jan | 2022 | 0.0072911 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-01-09 09:27 | 2022-01-09 09:32 | 1827 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 3700 DE JOBOS A YABUCOA | C22010900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-01-09 | 9135 | keep | 0 | Jan | 2022 | 0.0062218 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-09 09:27 | 2022-01-09 09:32 | 2100 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22010900096 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-01-09 | 10500 | keep | 0 | Jan | 2022 | 0.0071515 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-09 09:27 | 2022-01-09 09:32 | 922 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22010900096 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-01-09 | 4610 | keep | 0 | Jan | 2022 | 0.0031399 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-09 09:27 | 2022-01-09 09:32 | 1676 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22010900096 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-01-09 | 8380 | keep | 0 | Jan | 2022 | 0.0057076 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-09 09:27 | 2022-01-09 09:32 | 2844 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22010900096 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-01-09 | 14220 | keep | 0 | Jan | 2022 | 0.0096852 | 0.001937 | Momentary | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-01-09 09:27 | 2022-01-09 09:32 | 2775 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22010900097 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-01-09 | 13875 | keep | 0 | Jan | 2022 | 0.0094502 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-09 09:27 | 2022-01-09 09:32 | 1457 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22010900097 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-01-09 | 7285 | keep | 0 | Jan | 2022 | 0.0049618 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-09 09:27 | 2022-01-09 09:32 | 1086 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22010900097 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-01-09 | 5430 | keep | 0 | Jan | 2022 | 0.0036983 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-09 09:27 | 2022-01-09 09:32 | 2134 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22010900097 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-01-09 | 10670 | keep | 0 | Jan | 2022 | 0.0072673 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-09 09:27 | 2022-01-09 09:32 | 1464 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22010900098 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-01-09 | 7320 | keep | 0 | Jan | 2022 | 0.0049856 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-09 09:27 | 2022-01-09 09:32 | 1833 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22010900098 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-01-09 | 9165 | keep | 0 | Jan | 2022 | 0.0062422 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-09 09:27 | 2022-01-09 09:32 | 1565 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22010900098 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-01-09 | 7825 | keep | 0 | Jan | 2022 | 0.0053296 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-09 09:27 | 2022-01-09 09:32 | 977 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22010900098 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-01-09 | 4885 | keep | 0 | Jan | 2022 | 0.0033272 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-09 09:30 | 2022-01-09 10:48 | 7 | 001:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR CONECTOR SECUNDARIO 120V POR FASE | S22010800144 | New_Event | Secondary Wire Down | Include | Include | Equipment | 78 | 2022-01-09 | 546 | keep | 0 | Jan | 2022 | 0.00037188 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2022-01-09 09:33 | 2022-01-09 10:53 | 5 | 001:20 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE HIZO DESGANCHE | P22010900099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2022-01-09 | 400 | keep | 0 | Jan | 2022 | 0.00027244 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-01-09 09:38 | 2022-01-09 11:59 | 10 | 002:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO LINEA A CAJA EN TRANSFORMADOR | S22010900006 | New_Event | Wire Down | Include | Include | Equipment | 141 | 2022-01-09 | 1410 | keep | 0 | Jan | 2022 | 0.00096034 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-01-09 09:51 | 2022-01-09 14:36 | 200 | 004:45 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE DESGANCHO ARBOL | A22010900029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 285 | 2022-01-09 | 57000 | keep | 0 | Jan | 2022 | 0.038822 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-01-09 10:06 | 2022-01-09 18:20 | 13 | 008:14 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA | C22010900115 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 494 | 2022-01-09 | 6422 | keep | 0 | Jan | 2022 | 0.004374 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
ARECIBO | 2022-01-09 10:12 | 2022-01-09 12:08 | 200 | 001:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22010900034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2022-01-09 | 23200 | keep | 0 | Jan | 2022 | 0.015801 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-01-09 10:13 | 2022-01-09 12:40 | 53 | 002:27 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22010900120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2022-01-09 | 7791 | keep | 0 | Jan | 2022 | 0.0053064 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
CAGUAS | 2022-01-09 10:16 | 2022-01-09 12:11 | 249 | 001:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C22010900123 | New_Event | Bad Weather | Include | Include | Weather | 115 | 2022-01-09 | 28635 | keep | 0 | Jan | 2022 | 0.019503 | 0.00016959 | Sustained | FALSE | FALSE | Not_TMED_Event | 249
CAGUAS | 2022-01-09 10:20 | 2022-01-09 10:21 | 1606 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR CRUCE POR REPTIL | C22010800107 | Additional_clients |  |  | Include | Wildlife | 1 | 2022-01-09 | 1606 | keep | 0 | Jan | 2022 | 0.0010938 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-09 10:21 | 2022-01-09 12:23 | 60 | 002:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 SMU 20 DE 25 AMP. SE RETIRO REPTIL DEL T-24 | C22010800107 | 1st_after_momentary |  |  | Include | Wildlife | 122 | 2022-01-09 | 7320 | keep | 0 | Jan | 2022 | 0.0049856 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-01-09 10:22 | 2022-01-09 12:18 | 16 | 001:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO Y LA SECUNDARIA | C22010700168 | New_Event | Secondary Wire Down | Include | Include | Equipment | 116 | 2022-01-09 | 1856 | keep | 0 | Jan | 2022 | 0.0012641 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2022-01-09 10:28 | 2022-01-09 15:42 | 1 | 005:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y VIENTO | M22010900039 | New_Event | Bad Weather | Include | Include | Weather | 314 | 2022-01-09 | 314 | keep | 0 | Jan | 2022 | 0.00021386 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-01-09 10:36 | 2022-01-09 19:03 | 50 | 008:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CONVERTIDOR POR FUERTES VIENTOS | A22010900037 | New_Event | Bad Weather | Include | Include | Weather | 507 | 2022-01-09 | 25350 | keep | 0 | Jan | 2022 | 0.017266 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-01-09 10:37 | 2022-01-09 10:47 | 15 | 000:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A22010900086 | New_Event | Secondary Wire Down | Include | Include | Equipment | 10 | 2022-01-09 | 150 | keep | 0 | Jan | 2022 | 0.00010216 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-01-09 10:39 | 2022-01-09 10:40 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22010900041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-09 | 176 | keep | 0 | Jan | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
SAN JUAN | 2022-01-09 10:43 | 2022-01-09 10:44 | 36 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SU CARGA POR 1620-4 SE PROBO QUEDO EN SERVICIO | S22010900010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-09 | 36 | keep | 0 | Jan | 2022 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-01-09 10:43 | 2022-01-09 10:44 | 172 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA 1620-1 SE PROBO QUEDO EN SERVICIO | S22010900010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-09 | 172 | keep | 0 | Jan | 2022 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
MAYAGÃœEZ | 2022-01-09 11:14 | 2022-01-09 20:55 | 1 | 009:41 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M22010900046 | New_Event | Bad Weather | Include | Include | Weather | 581 | 2022-01-09 | 581 | keep | 0 | Jan | 2022 | 0.00039572 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-01-09 11:14 | 2022-01-09 13:46 | 60 | 002:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA SE CERRO PUENTES PRIMARIOS | M22010800158 | Partial_restoration | Wire Down | Include | Include | Equipment | 152 | 2022-01-09 | 9120 | keep | 0 | Jan | 2022 | 0.0062116 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-01-09 11:18 | 2022-01-09 17:35 | 16 | 006:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | P22010900135 | New_Event | Wire Down | Include | Include | Equipment | 377 | 2022-01-09 | 6032 | keep | 0 | Jan | 2022 | 0.0041084 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
UTUADO | 2022-01-09 11:20 | 2022-01-09 17:33 | 35 | 006:13 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE DESGANCHO PALMAS | A22010900042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 373 | 2022-01-09 | 13055 | keep | 0 | Jan | 2022 | 0.0088917 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-01-09 11:23 | 2022-01-09 11:24 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22010900047 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-09 | 176 | keep | 0 | Jan | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
HUMACAO | 2022-01-09 11:32 | 2022-01-09 17:33 | 200 | 006:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO DE FASE A FASE SE ABRIO EN CONVERTIDOR PARA CERRAR PUENTE | C22010900163 | New_Event | Wire Down | Include | Include | Equipment | 361 | 2022-01-09 | 72200 | keep | 0 | Jan | 2022 | 0.049175 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2022-01-09 11:33 | 2022-01-09 18:30 | 70 | 006:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA FUERTE BRISA | P22010900137 | New_Event | Bad Weather | Include | Include | Weather | 417 | 2022-01-09 | 29190 | keep | 0 | Jan | 2022 | 0.019881 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BARRANQUITAS | 2022-01-09 11:37 | 2022-01-09 18:30 | 135 | 006:53 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22010900166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 413 | 2022-01-09 | 55755 | keep | 0 | Jan | 2022 | 0.037974 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
MAYAGÃœEZ | 2022-01-09 11:37 | 2022-01-09 11:38 | 863 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR MAL TIEMPO VIENTOS FUERTES | M22010900048 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-01-09 | 863 | keep | 0 | Jan | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
HUMACAO | 2022-01-09 11:38 | 2022-01-09 13:43 | 1891 | 002:05 | S | LINEA DE TRANSMISION 38KV | SE RETIRO LA CARGA A LA SUBESTACION AUTORIZADO POR EL ING. LUIS MAESO PARA CONSTRUIR PUENTE EN MOD 3715 Y PODER DEJAR LA SUBESTACION POR HUMACAO | C22010900170 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 125 | 2022-01-09 | 236375 | keep | 0 | Jan | 2022 | 0.16099 | 0.001288 | Sustained | FALSE | FALSE | Not_TMED_Event | 1891
HUMACAO | 2022-01-09 11:38 | 2022-01-09 13:43 | 1250 | 002:05 | S | LINEA DE TRANSMISION 38KV | SE RETIRO LA CARGA A LA SUBESTACION AUTORIZADO POR EL ING. LUIS MAESO PARA CONSTRUIR PUENTE EN MOD 3715 Y PODER DEJAR LA SUBESTACION POR HUMACAO | C22010900170 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 125 | 2022-01-09 | 156250 | keep | 0 | Jan | 2022 | 0.10642 | 0.00085137 | Sustained | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2022-01-09 11:38 | 2022-01-09 13:43 | 2141 | 002:05 | S | LINEA DE TRANSMISION 38KV | SE RETIRO LA CARGA A LA SUBESTACION AUTORIZADO POR EL ING. LUIS MAESO PARA CONSTRUIR PUENTE EN MOD 3715 Y PODER DEJAR LA SUBESTACION POR HUMACAO | C22010900170 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 125 | 2022-01-09 | 267625 | keep | 0 | Jan | 2022 | 0.18228 | 0.0014582 | Sustained | FALSE | FALSE | Not_TMED_Event | 2141
HUMACAO | 2022-01-09 11:38 | 2022-01-09 13:43 | 1827 | 002:05 | S | LINEA DE TRANSMISION 38KV | SE RETIRO LA CARGA A LA SUBESTACION AUTORIZADO POR EL ING. LUIS MAESO PARA CONSTRUIR PUENTE EN MOD 3715 Y PODER DEJAR LA SUBESTACION POR HUMACAO | C22010900170 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 125 | 2022-01-09 | 228375 | keep | 0 | Jan | 2022 | 0.15555 | 0.0012444 | Sustained | FALSE | FALSE | Not_TMED_Event | 1827
MAYAGÃœEZ | 2022-01-09 11:38 | 2022-01-09 13:11 | 50 | 001:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22010900045 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 93 | 2022-01-09 | 4650 | keep | 0 | Jan | 2022 | 0.0031671 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-01-09 11:40 | 2022-01-09 19:02 | 41 | 007:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C22010900173 | New_Event | Bad Weather | Include | Include | Weather | 442 | 2022-01-09 | 18122 | keep | 0 | Jan | 2022 | 0.012343 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
ARECIBO | 2022-01-09 11:41 | 2022-01-09 16:06 | 6 | 004:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA DE TRANSFORMADOR Y SE REPARO BAJANTE SECUNDARIO | A22010900047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 265 | 2022-01-09 | 1590 | keep | 0 | Jan | 2022 | 0.0010829 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-01-09 11:44 | 2022-01-09 11:46 | 36 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1620-4 | S22010900017 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-09 | 72 | keep | 0 | Jan | 2022 | 4.9039e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-01-09 11:44 | 2022-01-09 11:46 | 172 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1620-01 | S22010900017 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-09 | 344 | keep | 0 | Jan | 2022 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
ARECIBO | 2022-01-09 11:45 | 2022-01-09 11:46 | 1227 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22010900049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-09 | 1227 | keep | 0 | Jan | 2022 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
SAN JUAN | 2022-01-09 11:51 | 2022-01-09 15:01 | 60 | 003:10 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22010900018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 190 | 2022-01-09 | 11400 | keep | 0 | Jan | 2022 | 0.0077645 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-01-09 12:00 | 2022-01-10 20:25 | 2 | 032:25 | P | DESGANCHE | SE REPARO PRIMARIA SE REMPLAZO POSTE Y SE REALIZO DESGANCHE | C22010900203 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1945 | 2022-01-09 | 3890 | keep | 0 | Jan | 2022 | 0.0026495 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-01-09 12:10 | 2022-01-09 13:36 | 2 | 001:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22010900050 | New_Event | Bad Weather | Include | Include | Weather | 86 | 2022-01-09 | 172 | keep | 0 | Jan | 2022 | 0.00011715 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-01-09 12:14 | 2022-01-09 15:10 | 200 | 002:56 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22010900026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2022-01-09 | 35200 | keep | 0 | Jan | 2022 | 0.023975 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2022-01-09 12:28 | 2022-01-09 16:09 | 60 | 003:41 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M22010900053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2022-01-09 | 13260 | keep | 0 | Jan | 2022 | 0.0090313 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-01-09 12:30 | 2022-01-09 13:04 | 20 | 000:34 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO CORTE DE LINEA PARA FIJAR LINEA ZAFADA DE AISLADOR | A22010900040 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 34 | 2022-01-09 | 680 | keep | 0 | Jan | 2022 | 0.00046314 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-01-09 12:39 | 2022-01-09 12:48 | 1565 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 DE COMSAT A SABANERA | C22010900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-01-09 | 14085 | keep | 0 | Jan | 2022 | 0.0095932 | 0.0010659 | Sustained | FALSE | FALSE | Not_TMED_Event | 1565
CAGUAS | 2022-01-09 12:39 | 2022-01-09 12:48 | 976 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 DE COMSAT A SABANERA | C22010900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-01-09 | 8784 | keep | 0 | Jan | 2022 | 0.0059827 | 0.00066475 | Sustained | FALSE | FALSE | Not_TMED_Event | 976
CAGUAS | 2022-01-09 12:39 | 2022-01-09 12:48 | 548 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 DE COMSAT A SABANERA | C22010900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-01-09 | 4932 | keep | 0 | Jan | 2022 | 0.0033592 | 0.00037324 | Sustained | FALSE | FALSE | Not_TMED_Event | 548
CAGUAS | 2022-01-09 12:39 | 2022-01-09 12:48 | 315 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 DE COMSAT A SABANERA | C22010900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-01-09 | 2835 | keep | 0 | Jan | 2022 | 0.0019309 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
CAGUAS | 2022-01-09 12:39 | 2022-01-09 12:48 | 870 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 DE COMSAT A SABANERA | C22010900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-01-09 | 7830 | keep | 0 | Jan | 2022 | 0.005333 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
CAGUAS | 2022-01-09 12:39 | 2022-01-09 12:48 | 2906 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 DE COMSAT A SABANERA | C22010900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-01-09 | 26154 | keep | 0 | Jan | 2022 | 0.017813 | 0.0019793 | Sustained | FALSE | FALSE | Not_TMED_Event | 2906
CAGUAS | 2022-01-09 12:39 | 2022-01-09 12:48 | 2343 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 DE COMSAT A SABANERA | C22010900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-01-09 | 21087 | keep | 0 | Jan | 2022 | 0.014362 | 0.0015958 | Sustained | FALSE | FALSE | Not_TMED_Event | 2343
BAYAMON | 2022-01-09 12:56 | 2022-01-09 15:21 | 40 | 002:25 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22010900017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2022-01-09 | 5800 | keep | 0 | Jan | 2022 | 0.0039504 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-01-09 12:57 | 2022-01-09 14:12 | 1565 | 001:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 DE COMSAT A SABANERA | C22010900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 75 | 2022-01-09 | 117375 | keep | 0 | Jan | 2022 | 0.079944 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-09 12:57 | 2022-01-09 14:12 | 976 | 001:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 DE COMSAT A SABANERA | C22010900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 75 | 2022-01-09 | 73200 | keep | 0 | Jan | 2022 | 0.049856 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-09 12:57 | 2022-01-09 14:12 | 548 | 001:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 DE COMSAT A SABANERA | C22010900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 75 | 2022-01-09 | 41100 | keep | 0 | Jan | 2022 | 0.027993 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-09 12:57 | 2022-01-09 14:12 | 315 | 001:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 DE COMSAT A SABANERA | C22010900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 75 | 2022-01-09 | 23625 | keep | 0 | Jan | 2022 | 0.016091 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-09 12:57 | 2022-01-09 14:12 | 870 | 001:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 DE COMSAT A SABANERA | C22010900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 75 | 2022-01-09 | 65250 | keep | 0 | Jan | 2022 | 0.044441 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-09 12:57 | 2022-01-09 14:12 | 2906 | 001:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 DE COMSAT A SABANERA | C22010900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 75 | 2022-01-09 | 217950 | keep | 0 | Jan | 2022 | 0.14844 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-09 12:57 | 2022-01-09 14:12 | 2343 | 001:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 DE COMSAT A SABANERA | C22010900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 75 | 2022-01-09 | 175725 | keep | 0 | Jan | 2022 | 0.11969 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-01-09 13:09 | 2022-01-09 19:21 | 150 | 006:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22010900060 | New_Event | Wire Down | Include | Include | Equipment | 372 | 2022-01-09 | 55800 | keep | 0 | Jan | 2022 | 0.038005 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-01-09 13:16 | 2022-01-10 10:41 | 2 | 021:25 | P | NO SE REPORTO CAUSA | 1 X 30 EN SU-1 Y 1 X 25 EN SU-3 | B22010900009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1285 | 2022-01-09 | 2570 | keep | 0 | Jan | 2022 | 0.0017504 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-01-09 13:23 | 2022-01-09 16:57 | 10 | 003:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE TRANSFORMADOR | S22010900037 | New_Event | Wire Down | Include | Include | Equipment | 214 | 2022-01-09 | 2140 | keep | 0 | Jan | 2022 | 0.0014575 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-01-09 13:32 | 2022-01-09 13:33 | 1830 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22010900015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-09 | 1830 | keep | 0 | Jan | 2022 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
AGUADILLA | 2022-01-09 13:35 | 2022-01-09 13:36 | 1245 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22010900062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-09 | 1245 | keep | 0 | Jan | 2022 | 0.00084796 | 0.00084796 | Momentary | FALSE | FALSE | Not_TMED_Event | 1245
HUMACAO | 2022-01-09 13:38 | 2022-01-09 14:56 | 12 | 001:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C22010900305 | New_Event | Bad Weather | Include | Include | Weather | 78 | 2022-01-09 | 936 | keep | 0 | Jan | 2022 | 0.00063751 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-01-09 14:14 | 2022-01-09 15:25 | 10 | 001:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTE SECUNDARIO | B22010700120 | New_Event | Secondary Wire Down | Include | Include | Equipment | 71 | 2022-01-09 | 710 | keep | 0 | Jan | 2022 | 0.00048358 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-01-09 14:17 | 2022-01-09 16:38 | 1565 | 002:21 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 SE RETIRO BAMBUA DE LA LINEA | C22010900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 141 | 2022-01-09 | 220665 | keep | 0 | Jan | 2022 | 0.15029 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-09 14:17 | 2022-01-09 16:38 | 976 | 002:21 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 SE RETIRO BAMBUA DE LA LINEA | C22010900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 141 | 2022-01-09 | 137616 | keep | 0 | Jan | 2022 | 0.09373 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-09 14:17 | 2022-01-09 16:38 | 548 | 002:21 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 SE RETIRO BAMBUA DE LA LINEA | C22010900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 141 | 2022-01-09 | 77268 | keep | 0 | Jan | 2022 | 0.052627 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-09 14:17 | 2022-01-09 16:38 | 315 | 002:21 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 SE RETIRO BAMBUA DE LA LINEA | C22010900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 141 | 2022-01-09 | 44415 | keep | 0 | Jan | 2022 | 0.030251 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-09 14:17 | 2022-01-09 16:38 | 870 | 002:21 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 SE RETIRO BAMBUA DE LA LINEA | C22010900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 141 | 2022-01-09 | 122670 | keep | 0 | Jan | 2022 | 0.08355 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-09 14:17 | 2022-01-09 16:38 | 2906 | 002:21 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 SE RETIRO BAMBUA DE LA LINEA | C22010900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 141 | 2022-01-09 | 409746 | keep | 0 | Jan | 2022 | 0.27908 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-09 14:17 | 2022-01-09 16:38 | 2343 | 002:21 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 SE RETIRO BAMBUA DE LA LINEA | C22010900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 141 | 2022-01-09 | 330363 | keep | 0 | Jan | 2022 | 0.22501 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-01-09 14:18 | 2022-01-09 20:42 | 60 | 006:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR FUERTES VIENTOS Y LLUVIA | A22010900069 | New_Event | Bad Weather | Include | Include | Weather | 384 | 2022-01-09 | 23040 | keep | 0 | Jan | 2022 | 0.015692 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-01-09 14:26 | 2022-01-09 15:53 | 80 | 001:27 | P | DESGANCHE | 1 X 65 EN C/L | R22010900016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2022-01-09 | 6960 | keep | 0 | Jan | 2022 | 0.0047404 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-01-09 14:41 | 2022-01-09 17:00 | 80 | 002:19 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22010900068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2022-01-09 | 11120 | keep | 0 | Jan | 2022 | 0.0075738 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-01-09 14:43 | 2022-01-10 17:20 | 5 | 026:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M22010900069 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1597 | 2022-01-09 | 7985 | keep | 0 | Jan | 2022 | 0.0054385 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2022-01-09 14:52 | 2022-01-09 16:35 | 2565 | 001:43 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | CONDUCTOR PRIMARIO EN EL SUELO SE TRANSFIRIO PARTE DE LA CARGA AL 9601-02 | C22010900173 | New_Event | Wire Down | Include | Include | Equipment | 103 | 2022-01-09 | 264195 | keep | 0 | Jan | 2022 | 0.17994 | 0.001747 | Sustained | FALSE | FALSE | Not_TMED_Event | 2565
GUAYAMA | 2022-01-09 15:21 | 2022-01-09 17:10 | 45 | 001:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA FUERTE BRISA | C22010900268 | New_Event | Bad Weather | Include | Include | Weather | 109 | 2022-01-09 | 4905 | keep | 0 | Jan | 2022 | 0.0033408 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
PONCE | 2022-01-09 15:27 | 2022-01-09 15:28 | 1093 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22010900170 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-09 | 1093 | keep | 0 | Jan | 2022 | 0.00074444 | 0.00074444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1093
VEGA BAJA | 2022-01-09 15:31 | 2022-01-09 17:13 | 30 | 001:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE LEVANTO NEUTRAL PRIMARIO | B22010900025 | New_Event | Wire Down | Include | Include | Equipment | 102 | 2022-01-09 | 3060 | keep | 0 | Jan | 2022 | 0.0020842 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-01-09 15:42 | 2022-01-09 15:59 | 440 | 000:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA TOTAL PARA CERRAR PUENTE | C22010900036 | New_Event | Wire Down | Include | Include | Equipment | 17 | 2022-01-09 | 7480 | keep | 0 | Jan | 2022 | 0.0050946 | 0.00029968 | Sustained | FALSE | FALSE | Not_TMED_Event | 440
UTUADO | 2022-01-09 15:42 | 2022-01-09 17:45 | 50 | 002:03 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA | A22010900077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2022-01-09 | 6150 | keep | 0 | Jan | 2022 | 0.0041887 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-01-09 15:46 | 2022-01-09 15:47 | 1256 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR 7002-4 QUE ESTA LLEVANDO LA CARGA DEL 7002-03 POR PUENTE PRIMARIO ABIERTO EN EL 7002-03 | M22010900074 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-01-09 | 1256 | keep | 0 | Jan | 2022 | 0.00085546 | 0.00085546 | Momentary | FALSE | FALSE | Not_TMED_Event | 1256
AGUADILLA | 2022-01-09 15:46 | 2022-01-09 15:47 | 558 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR POR PUENTE PRIMARIO ABIERTO EN EL ALIMENTADOR 7002-03 QUE SU CARGA ESTA POR EL 7002-04 | M22010900074 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-01-09 | 558 | keep | 0 | Jan | 2022 | 0.00038005 | 0.00038005 | Momentary | FALSE | FALSE | Not_TMED_Event | 558
AGUADILLA | 2022-01-09 15:46 | 2022-01-09 15:47 | 390 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR POR PUENTE PRIMARIO ABIERTO EN EL ALIMENTADOR 7002-03 QUE PASA CERCA DE ESTE ALIMENTADOR | M22010900073 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-01-09 | 390 | keep | 0 | Jan | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
AGUADILLA | 2022-01-09 15:47 | 2022-01-09 18:25 | 180 | 002:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO | M22010900078 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 158 | 2022-01-09 | 28440 | keep | 0 | Jan | 2022 | 0.01937 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
SAN JUAN | 2022-01-09 15:57 | 2022-01-09 17:48 | 75 | 001:51 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADOR | S22010900053 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 111 | 2022-01-09 | 8325 | keep | 0 | Jan | 2022 | 0.0056701 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
PONCE | 2022-01-09 16:08 | 2022-01-09 18:00 | 174 | 001:52 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22010900176 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2022-01-09 | 19488 | keep | 0 | Jan | 2022 | 0.013273 | 0.00011851 | Sustained | FALSE | FALSE | Not_TMED_Event | 174
SAN JUAN | 2022-01-09 16:12 | 2022-01-09 16:13 | 500 | 000:01 | P | NO SE REPORTO CAUSA | 20% DE LA CARGA TRANSFERIDA AL 1118-10 INTERRUPTOR DISPARO Y SE CERRO POR CONTROL | S22010900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-09 | 500 | keep | 0 | Jan | 2022 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2022-01-09 16:12 | 2022-01-09 16:13 | 2782 | 000:01 | T | NO SE REPORTO CAUSA | INTERRUPTOR DISPARO Y SE CERRO POR CONTROL LLEVA 20% 1111-01 | S22010900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-09 | 2782 | keep | 0 | Jan | 2022 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
MAYAGÃœEZ | 2022-01-09 16:20 | 2022-01-09 20:09 | 50 | 003:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22010900082 | New_Event | Bad Weather | Include | Include | Weather | 229 | 2022-01-09 | 11450 | keep | 0 | Jan | 2022 | 0.0077985 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-01-09 16:30 | 2022-01-09 18:35 | 100 | 002:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE DE ARBOL | A22010900079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2022-01-09 | 12500 | keep | 0 | Jan | 2022 | 0.0085137 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-01-09 16:32 | 2022-01-09 17:23 | 20 | 000:51 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22010900028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 51 | 2022-01-09 | 1020 | keep | 0 | Jan | 2022 | 0.00069472 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2022-01-09 16:33 | 2022-01-09 18:58 | 20 | 002:25 | P | DESGANCHE | 1 X 30 EN C/L | R22010900021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 145 | 2022-01-09 | 2900 | keep | 0 | Jan | 2022 | 0.0019752 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-01-09 16:35 | 2022-01-09 17:07 | 418 | 000:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR PRIMARIO EN EL SUELO Y SE CERRO INTERRUPTOR | C22010900173 | Partial_restoration | Wire Down | Include | Include | Equipment | 32 | 2022-01-09 | 13376 | keep | 0 | Jan | 2022 | 0.0091103 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-09 16:50 | 2022-01-10 15:27 | 57 | 022:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA EN MACHETE | S22010900055 | New_Event | Wire Down | Include | Include | Equipment | 1357 | 2022-01-09 | 77349 | keep | 0 | Jan | 2022 | 0.052682 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
BARRANQUITAS | 2022-01-09 17:07 | 2022-01-09 17:49 | 1249 | 000:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO | C22010900173 | Additional_clients | Wire Down | Include | Include | Equipment | 42 | 2022-01-09 | 52458 | keep | 0 | Jan | 2022 | 0.035729 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-01-09 17:10 | 2022-01-10 15:27 | 50 | 022:17 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C22010900583 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1337 | 2022-01-09 | 66850 | keep | 0 | Jan | 2022 | 0.045531 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-01-09 17:11 | 2022-01-09 19:32 | 7 | 002:21 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | C22010900585 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 141 | 2022-01-09 | 987 | keep | 0 | Jan | 2022 | 0.00067224 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2022-01-09 17:11 | 2022-01-10 11:51 | 90 | 018:40 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C22010900584 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1120 | 2022-01-09 | 100800 | keep | 0 | Jan | 2022 | 0.068654 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CAGUAS | 2022-01-09 17:13 | 2022-01-09 17:57 | 119 | 000:44 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C22010900586 | New_Event | Vegetation Contact | Include | Include | Vegetation | 44 | 2022-01-09 | 5236 | keep | 0 | Jan | 2022 | 0.0035662 | 8.105e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 119
VEGA BAJA | 2022-01-09 17:16 | 2022-01-09 17:55 | 10 | 000:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | B22010900033 | New_Event | Cutout Failure | Include | Include | Equipment | 39 | 2022-01-09 | 390 | keep | 0 | Jan | 2022 | 0.00026563 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-09 17:19 | 2022-01-09 19:06 | 40 | 001:47 | P | FUEGO | SE ABRIO CORTE DE LINEA PARA QUE BOMBEROS APAGUE FUEGO | S22010900056 | New_Event | Fire | Include | Include | Public | 107 | 2022-01-09 | 4280 | keep | 0 | Jan | 2022 | 0.0029151 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-01-09 17:31 | 2022-01-09 19:20 | 65 | 001:49 | P | DESGANCHE | 1 X 100 EN C/L | R22010900024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2022-01-09 | 7085 | keep | 0 | Jan | 2022 | 0.0048256 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
PONCE | 2022-01-09 17:31 | 2022-01-09 19:17 | 1 | 001:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CABLE SAFADO EN RISER POR DESGANCHE | P22010900182 | New_Event | Wire Down | Include | Include | Equipment | 106 | 2022-01-09 | 106 | keep | 0 | Jan | 2022 | 7.2196e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-01-09 17:33 | 2022-01-09 18:14 | 728 | 000:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO TOTAL EN EL CONVERTIDOR PARA CERRAR PUENTE EN ANCLADA | C22010900163 | Additional_clients | Wire Down | Include | Include | Equipment | 41 | 2022-01-09 | 29848 | keep | 0 | Jan | 2022 | 0.020329 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-01-09 17:41 | 2022-01-09 17:42 | 141 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | A22010900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-09 | 141 | keep | 0 | Jan | 2022 | 9.6034e-05 | 9.6034e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 141
BARRANQUITAS | 2022-01-09 17:49 | 2022-01-10 19:13 | 13 | 025:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO PRIMARIA Y SE ENERGIZO LOS CLIENTES FUERA | C22010900173 | Partial_restoration | Wire Down | Include | Include | Equipment | 1524 | 2022-01-09 | 19812 | keep | 0 | Jan | 2022 | 0.013494 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-01-09 17:50 | 2022-01-09 18:20 | 18 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | P22010900157 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2022-01-09 | 540 | keep | 0 | Jan | 2022 | 0.00036779 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
FAJARDO | 2022-01-09 18:08 | 2022-01-09 18:33 | 6 | 000:25 | P | NO SE REPORTO CAUSA | 1 X 20 EN C/L Y 1 X 15 EN XMR NO CAUSA | R22010900030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 25 | 2022-01-09 | 150 | keep | 0 | Jan | 2022 | 0.00010216 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-01-09 18:17 | 2022-01-10 18:19 | 30 | 024:02 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVISIONAL HACIA T-17 | C22010900608 | New_Event | UG Cable Fault | Include | Include | Equipment | 1442 | 2022-01-09 | 43260 | keep | 0 | Jan | 2022 | 0.029464 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-01-09 18:29 | 2022-01-10 09:11 | 30 | 014:42 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22010900062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 882 | 2022-01-09 | 26460 | keep | 0 | Jan | 2022 | 0.018022 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-01-09 18:55 | 2022-01-10 20:26 | 300 | 025:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22011000070 | New_Event | Wire Down | Include | Include | Equipment | 1531 | 2022-01-09 | 459300 | keep | 0 | Jan | 2022 | 0.31283 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2022-01-09 18:58 | 2022-01-10 12:32 | 30 | 017:34 | P | CABLE SOTERRADO AVERIADO | 1 X 20 EN CORTE DE LINEA DE PROVISIONAL AEREO. SE CONSTRUYO PROVISIONAL DE PROVISIONAL AEREO @ T-22 | C22010800103 | New_Event | UG Cable Fault | Include | Include | Equipment | 1054 | 2022-01-09 | 31620 | keep | 0 | Jan | 2022 | 0.021536 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-01-09 18:59 | 2022-01-10 14:54 | 10 | 019:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO BAJANTE SECUNDARIO Y CONECTOR SECUNDARIO EN TRANSFORMADOR | C22010900621 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1195 | 2022-01-09 | 11950 | keep | 0 | Jan | 2022 | 0.0081391 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-01-09 19:20 | 2022-01-10 10:28 | 20 | 015:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | C22010900627 | New_Event | Bad Weather | Include | Include | Weather | 908 | 2022-01-09 | 18160 | keep | 0 | Jan | 2022 | 0.012369 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2022-01-09 19:36 | 2022-01-09 19:37 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010900185 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 2100 | keep | 0 | Jan | 2022 | 0.0014303 | 0.0014303 | Momentary | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-01-09 19:36 | 2022-01-09 19:37 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010900185 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 922 | keep | 0 | Jan | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-01-09 19:36 | 2022-01-09 19:37 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010900185 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1676 | keep | 0 | Jan | 2022 | 0.0011415 | 0.0011415 | Momentary | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-01-09 19:36 | 2022-01-09 19:37 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010900185 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 2844 | keep | 0 | Jan | 2022 | 0.001937 | 0.001937 | Momentary | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-01-09 19:36 | 2022-01-09 19:37 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010900186 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 2775 | keep | 0 | Jan | 2022 | 0.00189 | 0.00189 | Momentary | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-01-09 19:36 | 2022-01-09 19:37 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010900186 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1457 | keep | 0 | Jan | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-01-09 19:36 | 2022-01-09 19:37 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010900186 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1086 | keep | 0 | Jan | 2022 | 0.00073967 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-01-09 19:36 | 2022-01-09 19:37 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010900187 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1464 | keep | 0 | Jan | 2022 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-01-09 19:36 | 2022-01-09 19:37 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010900187 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1833 | keep | 0 | Jan | 2022 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-01-09 19:36 | 2022-01-09 19:37 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010900187 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 1565 | keep | 0 | Jan | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-01-09 19:36 | 2022-01-09 19:37 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P22010900187 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-09 | 977 | keep | 0 | Jan | 2022 | 0.00066543 | 0.00066543 | Momentary | FALSE | FALSE | Not_TMED_Event | 977
MAYAGÃœEZ | 2022-01-09 19:45 | 2022-01-10 09:39 | 6 | 013:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR POR LLUVIA | M22010900091 | New_Event | Bad Weather | Include | Include | Weather | 834 | 2022-01-09 | 5004 | keep | 0 | Jan | 2022 | 0.0034082 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-01-09 19:47 | 2022-01-09 22:10 | 35 | 002:23 | P | DESGANCHE | 1 X 50 EN C/L | R22010900037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2022-01-09 | 5005 | keep | 0 | Jan | 2022 | 0.0034089 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2022-01-09 20:45 | 2022-01-10 09:33 | 90 | 012:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22010900094 | New_Event | Bad Weather | Include | Include | Weather | 768 | 2022-01-09 | 69120 | keep | 0 | Jan | 2022 | 0.047077 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BARRANQUITAS | 2022-01-09 20:45 | 2022-01-10 11:52 | 10 | 015:07 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | C22010900638 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 907 | 2022-01-09 | 9070 | keep | 0 | Jan | 2022 | 0.0061775 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-01-09 21:06 | 2022-01-10 12:44 | 5 | 015:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE DE XMR ABIERTO | C22010900640 | New_Event | Secondary Wire Down | Include | Include | Equipment | 938 | 2022-01-09 | 4690 | keep | 0 | Jan | 2022 | 0.0031943 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-01-09 21:19 | 2022-01-10 09:22 | 22 | 012:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65, 1 X 40 Y 1 X 25 EN CORTES DE LINEA SE SECCIONALIZO MONOFASICA VACANTE | R22010900040 | New_Event | Wire Down | Include | Include | Equipment | 723 | 2022-01-09 | 15906 | keep | 0 | Jan | 2022 | 0.010834 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
MAYAGÃœEZ | 2022-01-09 21:28 | 2022-01-10 00:24 | 50 | 002:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22010900102 | New_Event | Wire Down | Include | Include | Equipment | 176 | 2022-01-09 | 8800 | keep | 0 | Jan | 2022 | 0.0059936 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-01-09 22:31 | 2022-01-10 11:06 | 50 | 012:35 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22010900650 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 755 | 2022-01-09 | 37750 | keep | 0 | Jan | 2022 | 0.025711 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-09 22:37 | 2022-01-10 11:16 | 10 | 012:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BAJANTE SECUNDARIO | S22010900066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 759 | 2022-01-09 | 7590 | keep | 0 | Jan | 2022 | 0.0051695 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-01-09 23:00 | 2022-01-10 19:07 | 30 | 020:07 | P | ERROR HUMANO | 2 X 65 EN C/L PERSONAL DE PRIVADA DESGANCHO | C22010900654 | New_Event | Human Error | Include | Include | Other | 1207 | 2022-01-09 | 36210 | keep | 0 | Jan | 2022 | 0.024662 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-01-10 00:17 | 2022-01-10 01:09 | 519 | 000:52 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV HUMACAO TC | C22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 52 | 2022-01-10 | 26988 | keep | 0 | Jan | 2022 | 0.018381 | 0.00035349 | Sustained | FALSE | FALSE | Not_TMED_Event | 519
HUMACAO | 2022-01-10 00:17 | 2022-01-10 01:09 | 1117 | 000:52 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV HUMACAO TC | C22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 52 | 2022-01-10 | 58084 | keep | 0 | Jan | 2022 | 0.039561 | 0.00076078 | Sustained | FALSE | FALSE | Not_TMED_Event | 1117
HUMACAO | 2022-01-10 00:17 | 2022-01-10 01:09 | 4161 | 000:52 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV HUMACAO TC | C22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 52 | 2022-01-10 | 216372 | keep | 0 | Jan | 2022 | 0.14737 | 0.002834 | Sustained | FALSE | FALSE | Not_TMED_Event | 4161
HUMACAO | 2022-01-10 00:17 | 2022-01-10 01:09 | 2450 | 000:52 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA HUMACAO TC 38KV | C22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 52 | 2022-01-10 | 127400 | keep | 0 | Jan | 2022 | 0.086772 | 0.0016687 | Sustained | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-01-10 00:17 | 2022-01-10 01:09 | 640 | 000:52 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA HUMACAO TC 38KV | C22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 52 | 2022-01-10 | 33280 | keep | 0 | Jan | 2022 | 0.022667 | 0.0004359 | Sustained | FALSE | FALSE | Not_TMED_Event | 640
HUMACAO | 2022-01-10 00:17 | 2022-01-10 01:09 | 1891 | 000:52 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA HUMACAO TC 38KV | C22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 52 | 2022-01-10 | 98332 | keep | 0 | Jan | 2022 | 0.066973 | 0.001288 | Sustained | FALSE | FALSE | Not_TMED_Event | 1891
HUMACAO | 2022-01-10 00:17 | 2022-01-10 01:09 | 1250 | 000:52 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA HUMACAO TC 38KV | C22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 52 | 2022-01-10 | 65000 | keep | 0 | Jan | 2022 | 0.044271 | 0.00085137 | Sustained | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2022-01-10 00:17 | 2022-01-10 01:09 | 2141 | 000:52 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA HUMACAO TC 38KV | C22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 52 | 2022-01-10 | 111332 | keep | 0 | Jan | 2022 | 0.075828 | 0.0014582 | Sustained | FALSE | FALSE | Not_TMED_Event | 2141
HUMACAO | 2022-01-10 00:17 | 2022-01-10 01:09 | 1827 | 000:52 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA HUMACAO TC 38KV | C22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 52 | 2022-01-10 | 95004 | keep | 0 | Jan | 2022 | 0.064707 | 0.0012444 | Sustained | FALSE | FALSE | Not_TMED_Event | 1827
CANOVANAS | 2022-01-10 00:31 | 2022-01-10 10:14 | 16 | 009:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN AEREO PROVISIONAL CRUCE POR RATA | R22011000001 | New_Event |  |  | Include | Wildlife | 583 | 2022-01-10 | 9328 | keep | 0 | Jan | 2022 | 0.0063533 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2022-01-10 01:43 | 2022-01-10 01:44 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22011000001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-10 | 1097 | keep | 0 | Jan | 2022 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
GUAYAMA | 2022-01-10 01:51 | 2022-01-10 10:30 | 1 | 008:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 30 EN TRANSFORMADOR SE REPARO BAJANTE SECUNDARIO | P22011000003 | New_Event | Secondary Wire Down | Include | Include | Equipment | 519 | 2022-01-10 | 519 | keep | 0 | Jan | 2022 | 0.00035349 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-01-10 02:44 | 2022-01-10 02:45 | 325 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22011100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-10 | 325 | keep | 0 | Jan | 2022 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
HUMACAO | 2022-01-10 03:21 | 2022-01-10 10:58 | 120 | 007:37 | P | DESGANCHE | 3 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | C22011000049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 457 | 2022-01-10 | 54840 | keep | 0 | Jan | 2022 | 0.037351 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
HUMACAO | 2022-01-10 03:54 | 2022-01-10 15:00 | 15 | 011:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA Y SE REMPLAZO JUEGO DE DISCOS | C22011000052 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 666 | 2022-01-10 | 9990 | keep | 0 | Jan | 2022 | 0.0068041 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-01-10 05:31 | 2022-01-10 09:22 | 30 | 003:51 | P | DESGANCHE | 1 X 25 EN XMR Y 1 X 40 EN CORTE DE LINEA DESGANCHE | S22011000001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 231 | 2022-01-10 | 6930 | keep | 0 | Jan | 2022 | 0.00472 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-01-10 05:55 | 2022-01-10 10:40 | 120 | 004:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 A LA ENTRADA DE CONVERTIDOR Y 1X100 A LA SALIDA DE CONVERTIDOR Y SE RETIRO IGUANA DEL TENDIDO ELECTRICO PRIMARIO | C22011000053 | New_Event |  |  | Include | Wildlife | 285 | 2022-01-10 | 34200 | keep | 0 | Jan | 2022 | 0.023293 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
ARECIBO | 2022-01-10 06:24 | 2022-01-10 17:45 | 15 | 011:21 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR LA MISMA CAPACIDAD | A22011000002 | New_Event | Service Transformer Failure | Include | Include | Equipment | 681 | 2022-01-10 | 10215 | keep | 0 | Jan | 2022 | 0.0069574 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-01-10 06:41 | 2022-01-10 10:03 | 7 | 003:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REEMPLAZO PM T-8 DE 100 KVA X 100 KVA IMPACTADO | R22011000002 | New_Event |  |  | Include | Wildlife | 202 | 2022-01-10 | 1414 | keep | 0 | Jan | 2022 | 0.00096307 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-01-10 06:57 | 2022-01-10 10:30 | 20 | 003:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE CAJA A LINEA | S22011000005 | New_Event | Wire Down | Include | Include | Equipment | 213 | 2022-01-10 | 4260 | keep | 0 | Jan | 2022 | 0.0029015 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-01-10 07:03 | 2022-01-10 11:12 | 50 | 004:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22011000003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 249 | 2022-01-10 | 12450 | keep | 0 | Jan | 2022 | 0.0084796 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-10 07:33 | 2022-01-10 10:16 | 30 | 002:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REEMPLAZO CAJA PRIMARIA | S22011000008 | New_Event | Cutout Failure | Include | Include | Equipment | 163 | 2022-01-10 | 4890 | keep | 0 | Jan | 2022 | 0.0033306 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-01-10 07:45 | 2022-01-10 10:42 | 50 | 002:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO | A22011000004 | New_Event | Wire Down | Include | Include | Equipment | 177 | 2022-01-10 | 8850 | keep | 0 | Jan | 2022 | 0.0060277 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-01-10 07:48 | 2022-01-10 15:23 | 10 | 007:35 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | A22011000005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 455 | 2022-01-10 | 4550 | keep | 0 | Jan | 2022 | 0.003099 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-01-10 08:06 | 2022-01-10 17:10 | 1 | 009:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | M22011000008 | New_Event | Cutout Failure | Include | Include | Equipment | 544 | 2022-01-10 | 544 | keep | 0 | Jan | 2022 | 0.00037052 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-01-10 08:12 | 2022-01-10 15:37 | 25 | 007:25 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y SE DESGANCHO BAMBUA | C22011000063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 445 | 2022-01-10 | 11125 | keep | 0 | Jan | 2022 | 0.0075772 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-01-10 08:19 | 2022-01-10 16:27 | 30 | 008:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO PUENTE DE LINEA A CAJA | S22011000010 | New_Event | Wire Down | Include | Include | Equipment | 488 | 2022-01-10 | 14640 | keep | 0 | Jan | 2022 | 0.0099712 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-01-10 08:23 | 2022-01-10 14:42 | 10 | 006:19 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22011000002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 379 | 2022-01-10 | 3790 | keep | 0 | Jan | 2022 | 0.0025814 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-01-10 08:29 | 2022-01-10 09:09 | 100 | 000:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA POR CONTACTO DE AVE | P22011000006 | New_Event |  |  | Include | Wildlife | 40 | 2022-01-10 | 4000 | keep | 0 | Jan | 2022 | 0.0027244 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-01-10 08:33 | 2022-01-10 16:22 | 8 | 007:49 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C22011000068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 469 | 2022-01-10 | 3752 | keep | 0 | Jan | 2022 | 0.0025555 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-01-10 08:51 | 2022-01-10 10:40 | 1 | 001:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA POR IGUANA CRUZO LINEA | M22011000016 | New_Event |  |  | Include | Wildlife | 109 | 2022-01-10 | 109 | keep | 0 | Jan | 2022 | 7.4239e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-01-10 08:56 | 2022-01-10 12:15 | 50 | 003:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN RISER CRUCE POR RATA | R22011000008 | New_Event |  |  | Include | Wildlife | 199 | 2022-01-10 | 9950 | keep | 0 | Jan | 2022 | 0.0067769 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-10 09:01 | 2022-01-10 10:23 | 10 | 001:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22011000014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 82 | 2022-01-10 | 820 | keep | 0 | Jan | 2022 | 0.0005585 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-01-10 09:02 | 2022-01-10 14:18 | 50 | 005:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | P22011000013 | New_Event | Bad Weather | Include | Include | Weather | 316 | 2022-01-10 | 15800 | keep | 0 | Jan | 2022 | 0.010761 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-10 09:05 | 2022-01-11 09:56 | 1 | 024:51 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR Y 1 X 50 EN C/L | S22011000016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1491 | 2022-01-10 | 1491 | keep | 0 | Jan | 2022 | 0.0010155 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-01-10 09:23 | 2022-01-10 12:02 | 9 | 002:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA, DESGANCHARON Y LEVANTARON NEUTRAL PRIMARIO | R22011000012 | New_Event | Cutout Failure | Include | Include | Equipment | 159 | 2022-01-10 | 1431 | keep | 0 | Jan | 2022 | 0.00097465 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2022-01-10 09:27 | 2022-01-10 11:53 | 10 | 002:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE CAJA DE TRANSFORMADOR PARA REPARAR CONEXIONES EN PEDESTAL SECUNDARIO | P22011000016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 146 | 2022-01-10 | 1460 | keep | 0 | Jan | 2022 | 0.0009944 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-10 09:30 | 2022-01-10 11:10 | 4 | 001:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA RELOCALIZAR SECUNDARIA | A22011000008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 100 | 2022-01-10 | 400 | keep | 0 | Jan | 2022 | 0.00027244 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-01-10 09:38 | 2022-01-10 12:19 | 13 | 002:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | S22011000020 | New_Event | Secondary Wire Down | Include | Include | Equipment | 161 | 2022-01-10 | 2093 | keep | 0 | Jan | 2022 | 0.0014255 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
ARECIBO | 2022-01-10 09:39 | 2022-01-10 12:20 | 1 | 002:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22011000011 | New_Event | Bad Weather | Include | Include | Weather | 161 | 2022-01-10 | 161 | keep | 0 | Jan | 2022 | 0.00010966 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-01-10 09:47 | 2022-01-10 18:30 | 30 | 008:43 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR | B22011000058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 523 | 2022-01-10 | 15690 | keep | 0 | Jan | 2022 | 0.010686 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-01-10 10:18 | 2022-01-10 11:42 | 12 | 001:24 | P | NO SE REPORTO CAUSA | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22011000005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2022-01-10 | 1008 | keep | 0 | Jan | 2022 | 0.00068654 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2022-01-10 10:20 | 2022-01-10 11:09 | 10 | 000:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE CAJA DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | P22011000023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 49 | 2022-01-10 | 490 | keep | 0 | Jan | 2022 | 0.00033374 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-01-10 10:21 | 2022-01-10 10:32 | 10 | 000:11 | P | NO SE REPORTO CAUSA | SE REEMPLAZO 1 X 15 EN XMR | B22011000004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 11 | 2022-01-10 | 110 | keep | 0 | Jan | 2022 | 7.492e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-10 10:22 | 2022-01-11 09:37 | 1 | 023:15 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU-2B | B22011000012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1395 | 2022-01-10 | 1395 | keep | 0 | Jan | 2022 | 0.00095013 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-01-10 11:10 | 2022-01-10 19:31 | 13 | 008:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | C22011000115 | New_Event | Secondary Wire Down | Include | Include | Equipment | 501 | 2022-01-10 | 6513 | keep | 0 | Jan | 2022 | 0.004436 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2022-01-10 11:10 | 2022-01-10 13:24 | 15 | 002:14 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO XMR PARA REPARAR POSTE SECUNDARIO PARTIDO | B22011000014 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 134 | 2022-01-10 | 2010 | keep | 0 | Jan | 2022 | 0.001369 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-01-10 11:13 | 2022-01-10 14:03 | 8 | 002:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR PEDESTAL | S22011000032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 170 | 2022-01-10 | 1360 | keep | 0 | Jan | 2022 | 0.00092629 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-01-10 11:14 | 2022-01-10 13:15 | 50 | 002:01 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22011000019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2022-01-10 | 6050 | keep | 0 | Jan | 2022 | 0.0041206 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-10 11:31 | 2022-01-10 11:32 | 3597 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | B22011000000 | New_Event |  |  | Include | Wildlife | 1 | 2022-01-10 | 3597 | keep | 0 | Jan | 2022 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2022-01-10 11:32 | 2022-01-10 13:25 | 80 | 001:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 Y 1 X 65 EN CORTES DE LINEA DIFERENTE SE RETIRO AVE | B22011000018 | 1st_after_momentary |  |  | Include | Wildlife | 113 | 2022-01-10 | 9040 | keep | 0 | Jan | 2022 | 0.0061571 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-01-10 11:36 | 2022-01-10 11:53 | 1 | 000:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 25 EN RISER CRUCE POR LAGARTO | R22011000023 | New_Event |  |  | Include | Wildlife | 17 | 2022-01-10 | 17 | keep | 0 | Jan | 2022 | 1.1579e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-01-10 11:36 | 2022-01-10 13:25 | 10 | 001:49 | P | TRANSFORMADOR AVERIADO | SE CAMBIA TRANSFORMADOR AVERIADO DE 50KVA A 7620 VOLTIOS POR UNO DE LA MISMA CAPACIDAD | P22011000034 | New_Event | Service Transformer Failure | Include | Include | Equipment | 109 | 2022-01-10 | 1090 | keep | 0 | Jan | 2022 | 0.00074239 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-01-10 11:43 | 2022-01-10 13:10 | 9 | 001:27 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA DESGANCHAR Y REPARAR SECUNDARIA | R22011000025 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 87 | 2022-01-10 | 783 | keep | 0 | Jan | 2022 | 0.0005333 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-01-10 11:50 | 2022-01-10 11:51 | 2147 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22011000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-10 | 2147 | keep | 0 | Jan | 2022 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
CAGUAS | 2022-01-10 11:58 | 2022-01-10 13:09 | 5 | 001:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO ABIERTO EN TRANSFORMADOR | C22011000057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 71 | 2022-01-10 | 355 | keep | 0 | Jan | 2022 | 0.00024179 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-01-10 12:00 | 2022-01-10 15:03 | 15 | 003:03 | P | NO SE REPORTO CAUSA | 1 X 15 EN CORTE DE LINEA | B22011000027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 183 | 2022-01-10 | 2745 | keep | 0 | Jan | 2022 | 0.0018696 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-01-10 12:04 | 2022-01-10 14:52 | 100 | 002:48 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | P22011000036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2022-01-10 | 16800 | keep | 0 | Jan | 2022 | 0.011442 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-01-10 12:16 | 2022-01-11 11:25 | 10 | 023:09 | P | TRANSFORMADOR AVERIADO | SE IDENTIFICO T-36 AVERIADO | B22011000034 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1389 | 2022-01-10 | 13890 | keep | 0 | Jan | 2022 | 0.0094604 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-01-10 12:20 | 2022-01-10 16:50 | 100 | 004:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | P22011000039 | New_Event | Wire Down | Include | Include | Equipment | 270 | 2022-01-10 | 27000 | keep | 0 | Jan | 2022 | 0.01839 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-01-10 12:21 | 2022-01-10 12:22 | 1827 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22011000043 | New_Event |  |  | Include | Wildlife | 1 | 2022-01-10 | 1827 | keep | 0 | Jan | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2022-01-10 12:22 | 2022-01-10 14:25 | 40 | 002:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE CRUZO LINEAS | M22011000045 | 1st_after_momentary |  |  | Include | Wildlife | 123 | 2022-01-10 | 4920 | keep | 0 | Jan | 2022 | 0.003351 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-01-10 12:32 | 2022-01-10 14:36 | 15 | 002:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA CLIENTE HACIENDO DESGANCHE DEJO CAER RAMAS SOBRE LINEAS | A22011000024 | New_Event |  |  | Include | Wildlife | 124 | 2022-01-10 | 1860 | keep | 0 | Jan | 2022 | 0.0012668 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-01-10 12:44 | 2022-01-10 13:15 | 50 | 000:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO ABIERTO | A22011000025 | New_Event | Wire Down | Include | Include | Equipment | 31 | 2022-01-10 | 1550 | keep | 0 | Jan | 2022 | 0.0010557 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-01-10 12:45 | 2022-01-10 14:28 | 5 | 001:43 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZO DE POSTE SECUNDARIO PARTIDO | M22011000046 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 103 | 2022-01-10 | 515 | keep | 0 | Jan | 2022 | 0.00035076 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2022-01-10 12:51 | 2022-01-10 12:52 | 75 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE | P22011000043 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-01-10 | 75 | keep | 0 | Jan | 2022 | 5.1082e-05 | 5.1082e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 75
PONCE | 2022-01-10 12:52 | 2022-01-10 16:57 | 50 | 004:05 | P | CABLE SOTERRADO AVERIADO | AVERIA SOTERRADA SE CERRO NORMALLY OPEN | P22011000053 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 245 | 2022-01-10 | 12250 | keep | 0 | Jan | 2022 | 0.0083434 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-01-10 13:01 | 2022-01-10 13:05 | 3087 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE TRANSMISION DE SAN SEBASTIAN | M22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-01-10 | 12348 | keep | 0 | Jan | 2022 | 0.0084102 | 0.0021025 | Momentary | FALSE | FALSE | Not_TMED_Event | 3087
MAYAGÃœEZ | 2022-01-10 13:01 | 2022-01-10 13:05 | 770 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE TRANSMISION DE SAN SEBASTIAN | M22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-01-10 | 3080 | keep | 0 | Jan | 2022 | 0.0020978 | 0.00052444 | Momentary | FALSE | FALSE | Not_TMED_Event | 770
MAYAGÃœEZ | 2022-01-10 13:01 | 2022-01-10 13:05 | 1192 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE TRANSMISION DE SAN SEBASTIAN | M22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-01-10 | 4768 | keep | 0 | Jan | 2022 | 0.0032475 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
MAYAGÃœEZ | 2022-01-10 13:01 | 2022-01-10 13:05 | 1772 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE TRANSMISION DE SAN SEBASTIAN | M22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-01-10 | 7088 | keep | 0 | Jan | 2022 | 0.0048276 | 0.0012069 | Momentary | FALSE | FALSE | Not_TMED_Event | 1772
MAYAGÃœEZ | 2022-01-10 13:01 | 2022-01-10 13:05 | 2174 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE TRANSMISION DE SAN SEBASTIAN | M22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-01-10 | 8696 | keep | 0 | Jan | 2022 | 0.0059228 | 0.0014807 | Momentary | FALSE | FALSE | Not_TMED_Event | 2174
MAYAGÃœEZ | 2022-01-10 13:01 | 2022-01-10 13:05 | 64 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE TRANSMISION DE SAN SEBASTIAN | M22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-01-10 | 256 | keep | 0 | Jan | 2022 | 0.00017436 | 4.359e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 64
MAYAGÃœEZ | 2022-01-10 13:01 | 2022-01-10 13:05 | 2658 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE TRANSMISION DE SAN SEBASTIAN | M22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-01-10 | 10632 | keep | 0 | Jan | 2022 | 0.0072414 | 0.0018104 | Momentary | FALSE | FALSE | Not_TMED_Event | 2658
MAYAGÃœEZ | 2022-01-10 13:01 | 2022-01-10 13:05 | 6285 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE TRANSMISION DE SAN SEBASTIAN | M22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-01-10 | 25140 | keep | 0 | Jan | 2022 | 0.017123 | 0.0042807 | Momentary | FALSE | FALSE | Not_TMED_Event | 6285
MAYAGÃœEZ | 2022-01-10 13:01 | 2022-01-10 13:05 | 2225 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE TRANSMISION DE SAN SEBASTIAN | M22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-01-10 | 8900 | keep | 0 | Jan | 2022 | 0.0060617 | 0.0015154 | Momentary | FALSE | FALSE | Not_TMED_Event | 2225
MAYAGÃœEZ | 2022-01-10 13:01 | 2022-01-10 13:05 | 3522 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE TRANSMISION DE SAN SEBASTIAN | M22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-01-10 | 14088 | keep | 0 | Jan | 2022 | 0.0095953 | 0.0023988 | Momentary | FALSE | FALSE | Not_TMED_Event | 3522
MAYAGÃœEZ | 2022-01-10 13:01 | 2022-01-10 13:05 | 1337 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE TRANSMISION DE SAN SEBASTIAN | M22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-01-10 | 5348 | keep | 0 | Jan | 2022 | 0.0036425 | 0.00091062 | Momentary | FALSE | FALSE | Not_TMED_Event | 1337
MAYAGÃœEZ | 2022-01-10 13:01 | 2022-01-10 13:05 | 2825 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE TRANSMISION DE SAN SEBASTIAN | M22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-01-10 | 11300 | keep | 0 | Jan | 2022 | 0.0076964 | 0.0019241 | Momentary | FALSE | FALSE | Not_TMED_Event | 2825
MAYAGÃœEZ | 2022-01-10 13:01 | 2022-01-10 13:05 | 1287 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE TRANSMISION DE SAN SEBASTIAN | M22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-01-10 | 5148 | keep | 0 | Jan | 2022 | 0.0035063 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
MAYAGÃœEZ | 2022-01-10 13:01 | 2022-01-10 13:05 | 1417 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE TRANSMISION DE SAN SEBASTIAN | M22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-01-10 | 5668 | keep | 0 | Jan | 2022 | 0.0038604 | 0.00096511 | Momentary | FALSE | FALSE | Not_TMED_Event | 1417
MAYAGÃœEZ | 2022-01-10 13:01 | 2022-01-10 13:05 | 80 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE TRANSMISION DE SAN SEBASTIAN | M22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2022-01-10 | 320 | keep | 0 | Jan | 2022 | 0.00021795 | 5.4488e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-01-10 13:05 | 2022-01-10 16:00 | 100 | 002:55 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA INDICA JOURNEYMAN QUE REQUIERE DESGANCHE | M22011000039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2022-01-10 | 17500 | keep | 0 | Jan | 2022 | 0.011919 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-01-10 13:07 | 2022-01-10 13:08 | 4381 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22011000060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-10 | 4381 | keep | 0 | Jan | 2022 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
VEGA BAJA | 2022-01-10 13:08 | 2022-01-10 13:43 | 15 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | B22011000045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2022-01-10 | 525 | keep | 0 | Jan | 2022 | 0.00035758 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-01-10 13:13 | 2022-01-10 18:34 | 30 | 005:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO C.L PARA CERRAR BAJANTE A CAJA | C22011000136 | New_Event | Wire Down | Include | Include | Equipment | 321 | 2022-01-10 | 9630 | keep | 0 | Jan | 2022 | 0.0065589 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-01-10 13:15 | 2022-01-10 13:31 | 1105 | 000:16 | T | ERROR HUMANO | DISPARO INTERRUPTOR PERSONAL PRIVADO DE LUMA REALIZANDO DESGANCHE | A22011000026 | New_Event | Human Error | Include | Include | Other | 16 | 2022-01-10 | 17680 | keep | 0 | Jan | 2022 | 0.012042 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
UTUADO | 2022-01-10 13:30 | 2022-01-10 14:09 | 1 | 000:39 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR EL JOURNEYMAN INFORMO QUE NO ENCONTRO CAUSA PARA EL FUSIBLE FUNDIDO | A22011000029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 39 | 2022-01-10 | 39 | keep | 0 | Jan | 2022 | 2.6563e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-01-10 13:31 | 2022-01-10 14:19 | 50 | 000:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO ABIERTO | A22011000025 | Partial_restoration | Wire Down | Include | Include | Equipment | 48 | 2022-01-10 | 2400 | keep | 0 | Jan | 2022 | 0.0016346 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-01-10 13:31 | 2022-01-10 13:33 | 50 | 000:02 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22011000019 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-01-10 | 100 | keep | 0 | Jan | 2022 | 6.811e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-01-10 13:42 | 2022-01-10 16:21 | 100 | 002:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | M22011000066 | New_Event |  |  | Include | Wildlife | 159 | 2022-01-10 | 15900 | keep | 0 | Jan | 2022 | 0.010829 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-01-10 13:53 | 2022-01-10 16:45 | 162 | 002:52 | P | TRANSFORMADOR AVERIADO | 2 X 50 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE REEMPLAZO 2 CAJAS PRIMARIAS Y UN TRANSFORMADOR DE 50 KVA X 50 KVA | R22011000030 | New_Event | Service Transformer Failure | Include | Include | Equipment | 172 | 2022-01-10 | 27864 | keep | 0 | Jan | 2022 | 0.018978 | 0.00011034 | Sustained | FALSE | FALSE | Not_TMED_Event | 162
MAYAGÃœEZ | 2022-01-10 14:12 | 2022-01-10 19:12 | 60 | 005:00 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA PALMA CRUZO LINEAS | M22011000071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 300 | 2022-01-10 | 18000 | keep | 0 | Jan | 2022 | 0.01226 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-01-10 14:20 | 2022-01-10 16:02 | 10 | 001:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22011000041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 102 | 2022-01-10 | 1020 | keep | 0 | Jan | 2022 | 0.00069472 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-01-10 14:25 | 2022-01-10 16:06 | 1 | 001:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | R22011000032 | New_Event | Cutout Failure | Include | Include | Equipment | 101 | 2022-01-10 | 101 | keep | 0 | Jan | 2022 | 6.8791e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-01-10 14:25 | 2022-01-10 14:26 | 888 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1600 | M22011000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-10 | 888 | keep | 0 | Jan | 2022 | 0.00060481 | 0.00060481 | Momentary | FALSE | FALSE | Not_TMED_Event | 888
MAYAGÃœEZ | 2022-01-10 14:25 | 2022-01-10 14:26 | 393 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1600 | M22011000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-10 | 393 | keep | 0 | Jan | 2022 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2022-01-10 14:25 | 2022-01-10 14:26 | 4 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1600 | M22011000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-10 | 4 | keep | 0 | Jan | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-01-10 14:25 | 2022-01-10 14:26 | 372 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1600 | M22011000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-10 | 372 | keep | 0 | Jan | 2022 | 0.00025337 | 0.00025337 | Momentary | FALSE | FALSE | Not_TMED_Event | 372
MAYAGÃœEZ | 2022-01-10 14:25 | 2022-01-10 14:26 | 2530 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1600 | M22011000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-10 | 2530 | keep | 0 | Jan | 2022 | 0.0017232 | 0.0017232 | Momentary | FALSE | FALSE | Not_TMED_Event | 2530
MAYAGÃœEZ | 2022-01-10 14:25 | 2022-01-10 14:26 | 199 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1600 | M22011000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-10 | 199 | keep | 0 | Jan | 2022 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
MAYAGÃœEZ | 2022-01-10 14:25 | 2022-01-10 14:26 | 312 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1600 | M22011000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-10 | 312 | keep | 0 | Jan | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
MAYAGÃœEZ | 2022-01-10 14:25 | 2022-01-10 14:26 | 4641 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1600 | M22011000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-10 | 4641 | keep | 0 | Jan | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2022-01-10 14:28 | 2022-01-10 14:29 | 1097 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22011000077 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2022-01-10 | 1097 | keep | 0 | Jan | 2022 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
MAYAGÃœEZ | 2022-01-10 14:29 | 2022-01-10 16:47 | 300 | 002:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22011000082 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 138 | 2022-01-10 | 41400 | keep | 0 | Jan | 2022 | 0.028197 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-01-10 14:29 | 2022-01-10 16:09 | 5 | 001:40 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZO DE POSTE SECUNDARIO PARTIDO | M22011000046 | Partial_restoration | Secondary Defective Pole | Include | Include | Equipment | 100 | 2022-01-10 | 500 | keep | 0 | Jan | 2022 | 0.00034055 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-10 14:35 | 2022-01-10 16:17 | 1 | 001:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y SE REPARO PUENTE DE LINEA A CAJA | S22011000046 | New_Event | Cutout Failure | Include | Include | Equipment | 102 | 2022-01-10 | 102 | keep | 0 | Jan | 2022 | 6.9472e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-01-10 14:52 | 2022-01-10 15:36 | 24 | 000:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BARRA EN PEDESTAL | R22011000027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 44 | 2022-01-10 | 1056 | keep | 0 | Jan | 2022 | 0.00071924 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
MAYAGÃœEZ | 2022-01-10 14:56 | 2022-01-10 22:15 | 40 | 007:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y SE RETIRO RAMAS SOBRE LAS LINEAS | M22011000091 | New_Event | Wire Down | Include | Include | Equipment | 439 | 2022-01-10 | 17560 | keep | 0 | Jan | 2022 | 0.01196 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-01-10 14:58 | 2022-01-10 15:00 | 1588 | 000:02 | T | OTRAS CAUSAS | SE ABRIO INTERRUPTOR PARA QUE PERSONAL DEL CAMPO CERTIFICARA CORRIDA DE ALIMENTADOR | B22011000000 | New_Event | Other Causes | Include | Include | Other | 2 | 2022-01-10 | 3176 | keep | 0 | Jan | 2022 | 0.0021632 | 0.0010816 | Momentary | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2022-01-10 15:00 | 2022-01-10 15:02 | 723 | 000:02 | T | OTRAS CAUSAS | SE ABRIO INTERRUPTOR PARA QUE PERSONAL DEL CAMPO CERTIFICARA CORRIDA DE ALIMENTADOR LLEVA LA CARGA DEL 1711-05 | B22011000000 | New_Event | Other Causes | Include | Include | Other | 2 | 2022-01-10 | 1446 | keep | 0 | Jan | 2022 | 0.00098486 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-01-10 15:08 | 2022-01-10 15:09 | 1976 | 000:01 | T | OTRAS CAUSAS | SE ABRIO INTERRUPTOR PARA QUE PERSONAL DEL CAMPO CERTIFICARA CORRIDA DE ALIMENTADOR CARGA POR EL 1711-02 | B22011000000 | New_Event | Other Causes | Include | Include | Other | 1 | 2022-01-10 | 1976 | keep | 0 | Jan | 2022 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
VEGA BAJA | 2022-01-10 15:27 | 2022-01-10 21:18 | 1 | 005:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE CAJA A TRANSFORMADOR | B22011000054 | New_Event | Wire Down | Include | Include | Equipment | 351 | 2022-01-10 | 351 | keep | 0 | Jan | 2022 | 0.00023906 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-01-10 15:35 | 2022-01-10 18:23 | 60 | 002:48 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE DESGANCHO | B22011000055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2022-01-10 | 10080 | keep | 0 | Jan | 2022 | 0.0068654 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-01-10 15:36 | 2022-01-10 18:18 | 80 | 002:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X SMU-20 DE 25 AMP. EN SU-A AL T-42 Y 1 X 65 EN RISER CRUCE POR LAGARTO | R22011000038 | New_Event |  |  | Include | Wildlife | 162 | 2022-01-10 | 12960 | keep | 0 | Jan | 2022 | 0.008827 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-01-10 15:43 | 2022-01-11 10:31 | 35 | 018:48 | P | DESGANCHE | 1X50 EN CORTE DE LINEA Y 1X25 EN CORTE DE LINEA SE DESGANCHARON BAMBUAS | C22011000158 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1128 | 2022-01-10 | 39480 | keep | 0 | Jan | 2022 | 0.02689 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
HUMACAO | 2022-01-10 15:54 | 2022-01-10 18:14 | 6 | 002:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTE | C22011000159 | New_Event | Secondary Wire Down | Include | Include | Equipment | 140 | 2022-01-10 | 840 | keep | 0 | Jan | 2022 | 0.00057212 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-01-10 15:57 | 2022-01-10 16:56 | 12 | 000:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22011000016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 59 | 2022-01-10 | 708 | keep | 0 | Jan | 2022 | 0.00048222 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-01-10 16:07 | 2022-01-10 18:35 | 40 | 002:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 40 EN CORTE DE LINEA SE REPARO AISLADOR ZAFADO | M22011000109 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 148 | 2022-01-10 | 5920 | keep | 0 | Jan | 2022 | 0.0040321 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2022-01-10 16:18 | 2022-01-10 16:52 | 40 | 000:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA PERSONAL DEL MUNICIPIO IMPACTO TENSOR CON VEHICULO PESADO Y CAUSO CRUCE DE LINEAS | A22011000049 | New_Event |  |  | Include | Wildlife | 34 | 2022-01-10 | 1360 | keep | 0 | Jan | 2022 | 0.00092629 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-01-10 16:25 | 2022-01-10 16:26 | 2064 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22011000115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-10 | 2064 | keep | 0 | Jan | 2022 | 0.0014058 | 0.0014058 | Momentary | FALSE | FALSE | Not_TMED_Event | 2064
CAGUAS | 2022-01-10 16:27 | 2022-01-10 16:28 | 25 | 000:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA Y SE RETIRO AVE DEL TENDIDO ELECTRICO PRIMARIO | C22011000148 | New_Event |  |  | Include | Wildlife | 1 | 2022-01-10 | 25 | keep | 0 | Jan | 2022 | 1.7027e-05 | 1.7027e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-01-10 16:59 | 2022-01-10 17:59 | 6 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | R22011000041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2022-01-10 | 360 | keep | 0 | Jan | 2022 | 0.00024519 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-01-10 17:09 | 2022-01-10 17:44 | 10 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B22011000060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2022-01-10 | 350 | keep | 0 | Jan | 2022 | 0.00023838 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2022-01-10 17:20 | 2022-01-10 17:21 | 2011 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P220110000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-10 | 2011 | keep | 0 | Jan | 2022 | 0.0013697 | 0.0013697 | Momentary | FALSE | FALSE | Not_TMED_Event | 2011
YAUCO | 2022-01-10 17:20 | 2022-01-10 17:21 | 339 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P220110000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-10 | 339 | keep | 0 | Jan | 2022 | 0.00023089 | 0.00023089 | Momentary | FALSE | FALSE | Not_TMED_Event | 339
YAUCO | 2022-01-10 17:20 | 2022-01-10 17:21 | 2470 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P220110000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-10 | 2470 | keep | 0 | Jan | 2022 | 0.0016823 | 0.0016823 | Momentary | FALSE | FALSE | Not_TMED_Event | 2470
YAUCO | 2022-01-10 17:20 | 2022-01-10 17:21 | 1182 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P220110000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-10 | 1182 | keep | 0 | Jan | 2022 | 0.00080505 | 0.00080505 | Momentary | FALSE | FALSE | Not_TMED_Event | 1182
YAUCO | 2022-01-10 17:20 | 2022-01-10 17:21 | 2340 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P220110000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-10 | 2340 | keep | 0 | Jan | 2022 | 0.0015938 | 0.0015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 2340
YAUCO | 2022-01-10 17:20 | 2022-01-10 17:21 | 1637 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P220110000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-10 | 1637 | keep | 0 | Jan | 2022 | 0.001115 | 0.001115 | Momentary | FALSE | FALSE | Not_TMED_Event | 1637
YAUCO | 2022-01-10 17:20 | 2022-01-10 17:21 | 1475 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P220110000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-10 | 1475 | keep | 0 | Jan | 2022 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
YAUCO | 2022-01-10 17:20 | 2022-01-10 17:21 | 661 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P220110000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-10 | 661 | keep | 0 | Jan | 2022 | 0.0004502 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
YAUCO | 2022-01-10 17:20 | 2022-01-10 17:30 | 1569 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P220110000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2022-01-10 | 15690 | keep | 0 | Jan | 2022 | 0.010686 | 0.0010686 | Sustained | FALSE | FALSE | Not_TMED_Event | 1569
YAUCO | 2022-01-10 17:20 | 2022-01-10 17:30 | 2309 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P220110000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2022-01-10 | 23090 | keep | 0 | Jan | 2022 | 0.015726 | 0.0015726 | Sustained | FALSE | FALSE | Not_TMED_Event | 2309
YAUCO | 2022-01-10 17:20 | 2022-01-10 17:30 | 2179 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P220110000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2022-01-10 | 21790 | keep | 0 | Jan | 2022 | 0.014841 | 0.0014841 | Sustained | FALSE | FALSE | Not_TMED_Event | 2179
YAUCO | 2022-01-10 17:20 | 2022-01-10 17:30 | 2440 | 000:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P220110000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2022-01-10 | 24400 | keep | 0 | Jan | 2022 | 0.016619 | 0.0016619 | Sustained | FALSE | FALSE | Not_TMED_Event | 2440
YAUCO | 2022-01-10 17:20 | 2022-01-10 17:21 | 1352 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P220110000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-10 | 1352 | keep | 0 | Jan | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
YAUCO | 2022-01-10 17:20 | 2022-01-10 17:21 | 3973 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P220110000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-10 | 3973 | keep | 0 | Jan | 2022 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2022-01-10 17:20 | 2022-01-10 17:21 | 2484 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P220110000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-10 | 2484 | keep | 0 | Jan | 2022 | 0.0016918 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
MAYAGÃœEZ | 2022-01-10 17:20 | 2022-01-10 17:21 | 281 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV YAUCO 2 | M22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-01-10 | 281 | keep | 0 | Jan | 2022 | 0.00019139 | 0.00019139 | Momentary | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2022-01-10 17:20 | 2022-01-10 17:21 | 1252 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV YAUCO 2 | M22011000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-01-10 | 1252 | keep | 0 | Jan | 2022 | 0.00085273 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2022-01-10 17:21 | 2022-01-10 20:21 | 5 | 003:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M22010900069 | New_Event | Secondary Wire Down | Include | Include | Equipment | 180 | 2022-01-10 | 900 | keep | 0 | Jan | 2022 | 0.00061299 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-01-10 17:28 | 2022-01-11 08:00 | 100 | 014:32 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22011000127 | New_Event | Bad Weather | Include | Include | Weather | 872 | 2022-01-10 | 87200 | keep | 0 | Jan | 2022 | 0.059392 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-01-10 17:49 | 2022-01-10 18:28 | 100 | 000:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN CORTE DE LINEA POR CONTACTO DE GLOBO DE HELIO | P22011000082 | New_Event |  |  | Include | Wildlife | 39 | 2022-01-10 | 3900 | keep | 0 | Jan | 2022 | 0.0026563 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-01-10 18:02 | 2022-01-11 09:51 | 32 | 015:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA Y SE RETIRO AVE DEL TENDIDO ELECTRICO PRIMARIO | C22011000171 | New_Event |  |  | Include | Wildlife | 949 | 2022-01-10 | 30368 | keep | 0 | Jan | 2022 | 0.020684 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
MAYAGÃœEZ | 2022-01-10 18:16 | 2022-01-10 21:05 | 4 | 002:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 5 EN TRANSFORMADOR MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22011000138 | New_Event | Bad Weather | Include | Include | Weather | 169 | 2022-01-10 | 676 | keep | 0 | Jan | 2022 | 0.00046042 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-01-10 18:30 | 2022-01-10 19:40 | 10 | 001:10 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO TRANSFORMADOR PARA REMPLAZAR AISLADOR | A22011000053 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 70 | 2022-01-10 | 700 | keep | 0 | Jan | 2022 | 0.00047677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-01-10 19:17 | 2022-01-11 10:39 | 8 | 015:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA EN PEDESTAL | C22011000177 | New_Event | Secondary Wire Down | Include | Include | Equipment | 922 | 2022-01-10 | 7376 | keep | 0 | Jan | 2022 | 0.0050238 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-01-10 19:32 | 2022-01-11 00:12 | 8 | 004:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR PEDESTAL SOTERRADO | A22011000054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 280 | 2022-01-10 | 2240 | keep | 0 | Jan | 2022 | 0.0015257 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-01-10 20:14 | 2022-01-10 22:44 | 25 | 002:30 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACION EN EN PROVISIONAL | S22011000058 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 150 | 2022-01-10 | 3750 | keep | 0 | Jan | 2022 | 0.0025541 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2022-01-10 20:18 | 2022-01-10 22:32 | 100 | 002:14 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA POR DESGANCHE | P22011000087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2022-01-10 | 13400 | keep | 0 | Jan | 2022 | 0.0091267 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-01-10 20:27 | 2022-01-10 20:28 | 1444 | 000:01 | T | NO SE REPORTO CAUSA | CARGA POR 6014-02 | M22011000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-10 | 1444 | keep | 0 | Jan | 2022 | 0.0009835 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-01-10 20:27 | 2022-01-10 20:28 | 3630 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR RECIERRE EN ON NO RECERRO SE CERRO POR CONTROL SCADA LLEVA LA CARGA DEL 6014-01 | M22011000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-10 | 3630 | keep | 0 | Jan | 2022 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
YAUCO | 2022-01-10 20:35 | 2022-01-11 10:34 | 24 | 013:59 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P22011000090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 839 | 2022-01-10 | 20136 | keep | 0 | Jan | 2022 | 0.013715 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
CAGUAS | 2022-01-10 21:05 | 2022-01-11 10:55 | 87 | 013:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA Y SE DESPEGO PUENTE PRIMARIO | C22011000183 | New_Event | Wire Down | Include | Include | Equipment | 830 | 2022-01-10 | 72210 | keep | 0 | Jan | 2022 | 0.049182 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
YAUCO | 2022-01-10 21:21 | 2022-01-10 21:22 | 1924 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P220110000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-10 | 1924 | keep | 0 | Jan | 2022 | 0.0013104 | 0.0013104 | Momentary | FALSE | FALSE | Not_TMED_Event | 1924
YAUCO | 2022-01-10 21:21 | 2022-01-10 21:22 | 968 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P220110000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-10 | 968 | keep | 0 | Jan | 2022 | 0.0006593 | 0.0006593 | Momentary | FALSE | FALSE | Not_TMED_Event | 968
YAUCO | 2022-01-10 21:21 | 2022-01-10 21:22 | 680 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P220110000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-10 | 680 | keep | 0 | Jan | 2022 | 0.00046314 | 0.00046314 | Momentary | FALSE | FALSE | Not_TMED_Event | 680
YAUCO | 2022-01-10 21:21 | 2022-01-10 21:22 | 2246 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P220110000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-10 | 2246 | keep | 0 | Jan | 2022 | 0.0015297 | 0.0015297 | Momentary | FALSE | FALSE | Not_TMED_Event | 2246
SAN JUAN | 2022-01-10 22:00 | 2022-01-11 10:23 | 50 | 012:23 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22011000061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 743 | 2022-01-10 | 37150 | keep | 0 | Jan | 2022 | 0.025303 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-01-10 22:09 | 2022-01-11 11:53 | 20 | 013:44 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22011000099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 824 | 2022-01-10 | 16480 | keep | 0 | Jan | 2022 | 0.011224 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-01-10 22:14 | 2022-01-11 14:26 | 3 | 016:12 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR LA MISMA CAPACIDAD | M22011000102 | New_Event | Service Transformer Failure | Include | Include | Equipment | 972 | 2022-01-10 | 2916 | keep | 0 | Jan | 2022 | 0.0019861 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-01-10 23:26 | 2022-01-11 10:10 | 6 | 010:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22011000163 | New_Event | Bad Weather | Include | Include | Weather | 644 | 2022-01-10 | 3864 | keep | 0 | Jan | 2022 | 0.0026318 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-01-10 23:46 | 2022-01-11 09:51 | 45 | 010:05 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR | R22011000046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 605 | 2022-01-10 | 27225 | keep | 0 | Jan | 2022 | 0.018543 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2022-01-11 01:17 | 2022-01-11 10:39 | 10 | 009:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22011100127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 562 | 2022-01-11 | 5620 | keep | 0 | Jan | 2022 | 0.0038278 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-01-11 05:42 | 2022-01-11 13:29 | 10 | 007:47 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR Y SE LIMPIO ENRREDADERA | C22011100002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 467 | 2022-01-11 | 4670 | keep | 0 | Jan | 2022 | 0.0031807 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-01-11 05:47 | 2022-01-11 14:12 | 35 | 008:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA LEVANTAR CONDUCTOR PRIMARIO | C22011100003 | New_Event | Wire Down | Include | Include | Equipment | 505 | 2022-01-11 | 17675 | keep | 0 | Jan | 2022 | 0.012038 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2022-01-11 06:20 | 2022-01-11 09:54 | 60 | 003:34 | P | DESGANCHE | DESGANCHE Y 1 X 80 EN CONVERTIDOR | B22011100003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 214 | 2022-01-11 | 12840 | keep | 0 | Jan | 2022 | 0.0087453 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-01-11 07:07 | 2022-01-11 15:10 | 31 | 008:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1X30 EN CORTE DE LINEA Y SE REPARO/LEVANTO CONDUCTOR PRIMARIO DEL SUELO | C22011100076 | New_Event | Wire Down | Include | Include | Equipment | 483 | 2022-01-11 | 14973 | keep | 0 | Jan | 2022 | 0.010198 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
BARRANQUITAS | 2022-01-11 07:07 | 2022-01-11 15:00 | 68 | 007:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA SE REEMPLAZO AISLADOR Y DISCO, DESGANCHARON CERRARON PUENTE Y REPARARON SECUNDARIA | C22011100006 | New_Event | Wire Down | Include | Include | Equipment | 473 | 2022-01-11 | 32164 | keep | 0 | Jan | 2022 | 0.021907 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
SAN JUAN | 2022-01-11 08:08 | 2022-01-11 09:06 | 70 | 000:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN CORTE DE LINEA CRUCE POR PALOMA | S22011100009 | New_Event |  |  | Include | Wildlife | 58 | 2022-01-11 | 4060 | keep | 0 | Jan | 2022 | 0.0027652 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-01-11 08:08 | 2022-01-11 08:09 | 2234 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22011100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-11 | 2234 | keep | 0 | Jan | 2022 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
HUMACAO | 2022-01-11 08:49 | 2022-01-11 14:30 | 10 | 005:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO NEUTRAL EN BAJANTE SECUNDARIO DE TRANSFORMADOR | C22011100076 | New_Event | Secondary Wire Down | Include | Include | Equipment | 341 | 2022-01-11 | 3410 | keep | 0 | Jan | 2022 | 0.0023225 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-11 09:20 | 2022-01-11 10:31 | 10 | 001:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | B22011000066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 71 | 2022-01-11 | 710 | keep | 0 | Jan | 2022 | 0.00048358 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-11 09:26 | 2022-01-11 11:42 | 1 | 002:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22011100021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 136 | 2022-01-11 | 136 | keep | 0 | Jan | 2022 | 9.2629e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-01-11 09:30 | 2022-01-11 11:04 | 75 | 001:34 | P | DESGANCHE | 1 X 30 Y 1 X 20 EN CORTES DE LINEAS | R22011100009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2022-01-11 | 7050 | keep | 0 | Jan | 2022 | 0.0048017 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2022-01-11 09:43 | 2022-01-12 16:50 | 8 | 031:07 | P | CABLE SOTERRADO AVERIADO | AVERIA DE RISER A PM-1 SE ENERGIZO A TRAVES DE LINEA PROVISIONAL AEREA DE PM-2 A PM-1 | M22011100022 | New_Event | UG Cable Fault | Include | Include | Equipment | 1867 | 2022-01-11 | 14936 | keep | 0 | Jan | 2022 | 0.010173 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2022-01-11 09:53 | 2022-01-11 12:28 | 9 | 002:35 | P | NO SE REPORTO CAUSA | 1 X 10 EN CORTE DE LINEA PROVISIONAL AEREO | R22011100012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 155 | 2022-01-11 | 1395 | keep | 0 | Jan | 2022 | 0.00095013 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-01-11 09:58 | 2022-01-11 11:19 | 30 | 001:21 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22011100029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2022-01-11 | 2430 | keep | 0 | Jan | 2022 | 0.0016551 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-01-11 10:05 | 2022-01-11 11:43 | 12 | 001:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA | S22011000054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 98 | 2022-01-11 | 1176 | keep | 0 | Jan | 2022 | 0.00080097 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-01-11 10:15 | 2022-01-11 11:20 | 8 | 001:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | P21011100011 | New_Event |  |  | Include | Wildlife | 65 | 2022-01-11 | 520 | keep | 0 | Jan | 2022 | 0.00035417 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-01-11 10:21 | 2022-01-11 12:48 | 3 | 002:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA Y SE REMPLAZO BAJANTE PRIMARIO | A22011100010 | New_Event | Wire Down | Include | Include | Equipment | 147 | 2022-01-11 | 441 | keep | 0 | Jan | 2022 | 0.00030036 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2022-01-11 10:28 | 2022-01-11 11:11 | 60 | 000:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA PAJARO CRUZO FASE | P22011100015 | New_Event |  |  | Include | Wildlife | 43 | 2022-01-11 | 2580 | keep | 0 | Jan | 2022 | 0.0017572 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-01-11 10:29 | 2022-01-11 13:05 | 35 | 002:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO PORTAFUSIBLE QUEMADO 1 X 65 EN CORTE DE LINEA | S22011100029 | New_Event | Cutout Failure | Include | Include | Equipment | 156 | 2022-01-11 | 5460 | keep | 0 | Jan | 2022 | 0.0037188 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-01-11 10:47 | 2022-01-11 14:21 | 1 | 003:34 | P | NO SE REPORTO CAUSA | 1 X 25 EN SU-6 | B22011100034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 214 | 2022-01-11 | 214 | keep | 0 | Jan | 2022 | 0.00014575 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-01-11 10:51 | 2022-01-11 11:33 | 11 | 000:42 | P | DESGANCHE | 1 X 15 EN XMR | R22011100014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 42 | 2022-01-11 | 462 | keep | 0 | Jan | 2022 | 0.00031467 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2022-01-11 10:55 | 2022-01-11 14:59 | 25 | 004:04 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B22011100038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 244 | 2022-01-11 | 6100 | keep | 0 | Jan | 2022 | 0.0041547 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2022-01-11 11:00 | 2022-01-11 13:45 | 18 | 002:45 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE TRANSFORMADOR DE 37.5 KVA A 4160 VOLTS POR OTRO IGUAL CAPACIDAD Y VOLTAJE | P22011100018 | New_Event | Service Transformer Failure | Include | Include | Equipment | 165 | 2022-01-11 | 2970 | keep | 0 | Jan | 2022 | 0.0020229 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2022-01-11 11:15 | 2022-01-11 12:21 | 80 | 001:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA REEMPLAZO PIN POLE TOP | R22011100015 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 66 | 2022-01-11 | 5280 | keep | 0 | Jan | 2022 | 0.0035962 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-01-11 11:21 | 2022-01-11 12:05 | 13 | 000:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 1 X 15 EN XMR | S22011100002 | New_Event | Cutout Failure | Include | Include | Equipment | 44 | 2022-01-11 | 572 | keep | 0 | Jan | 2022 | 0.00038959 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2022-01-11 11:25 | 2022-01-11 14:28 | 30 | 003:03 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO T-36 MEDIANTE GOI BY-220111-01 | B22011000034 | Additional_clients | Service Transformer Failure | Include | Include | Equipment | 183 | 2022-01-11 | 5490 | keep | 0 | Jan | 2022 | 0.0037392 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-01-11 11:28 | 2022-01-11 13:30 | 6 | 002:02 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | P22011100022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2022-01-11 | 732 | keep | 0 | Jan | 2022 | 0.00049856 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-01-11 11:58 | 2022-01-11 13:31 | 190 | 001:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA POR VIENTOS | A22011100022 | New_Event | Bad Weather | Include | Include | Weather | 93 | 2022-01-11 | 17670 | keep | 0 | Jan | 2022 | 0.012035 | 0.00012941 | Sustained | FALSE | FALSE | Not_TMED_Event | 190
BAYAMON | 2022-01-11 12:08 | 2022-01-11 15:14 | 2 | 003:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO BANCO DE XMR Y SE REPARO CONEXIONES PROBO MALO Y SE REFIRIO A CONSTRUCCION | S22011100042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 186 | 2022-01-11 | 372 | keep | 0 | Jan | 2022 | 0.00025337 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-01-11 12:16 | 2022-01-11 13:47 | 5 | 001:31 | P | ESTRUCTURA AVERIADA | SE ABRIO PUENTE PARA ENDEREZAR POSTE | A22011100025 | New_Event | Defective Pole | Include | Include | Equipment | 91 | 2022-01-11 | 455 | keep | 0 | Jan | 2022 | 0.0003099 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-01-11 12:46 | 2022-01-11 14:44 | 1 | 001:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN RISER POR DESCARGAS ELECTRICAS | M22011100117 | New_Event | Bad Weather | Include | Include | Weather | 118 | 2022-01-11 | 118 | keep | 0 | Jan | 2022 | 8.0369e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-01-11 12:53 | 2022-01-11 16:23 | 1 | 003:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA DEL TRANSFORMADOR | R22011100021 | New_Event | Cutout Failure | Include | Include | Equipment | 210 | 2022-01-11 | 210 | keep | 0 | Jan | 2022 | 0.00014303 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-01-11 12:55 | 2022-01-11 17:40 | 1 | 004:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA MONOFASICO PARA LEVANTAR NEUTRAL PRIMARIO | C22011100119 | New_Event | Wire Down | Include | Include | Equipment | 285 | 2022-01-11 | 285 | keep | 0 | Jan | 2022 | 0.00019411 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-01-11 13:29 | 2022-01-11 14:44 | 1 | 001:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22011100030 | New_Event | Bad Weather | Include | Include | Weather | 75 | 2022-01-11 | 75 | keep | 0 | Jan | 2022 | 5.1082e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-01-11 13:30 | 2022-01-11 13:38 | 1725 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 JUNCOS @ JUNCOS PROVISIONAL | C22011100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-01-11 | 13800 | keep | 0 | Jan | 2022 | 0.0093991 | 0.0011749 | Sustained | FALSE | FALSE | Not_TMED_Event | 1725
BAYAMON | 2022-01-11 13:39 | 2022-01-11 17:14 | 40 | 003:35 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | B22011100052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 215 | 2022-01-11 | 8600 | keep | 0 | Jan | 2022 | 0.0058574 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-01-11 13:40 | 2022-01-11 15:15 | 80 | 001:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA INDICA JOURNEYMAN REQUIERE DESGANCHE | A22011100033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2022-01-11 | 7600 | keep | 0 | Jan | 2022 | 0.0051763 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-01-11 14:10 | 2022-01-11 18:45 | 6 | 004:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22011100146 | New_Event | Secondary Wire Down | Include | Include | Equipment | 275 | 2022-01-11 | 1650 | keep | 0 | Jan | 2022 | 0.0011238 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-01-11 14:17 | 2022-01-11 14:18 | 25 | 000:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22011100018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-11 | 25 | keep | 0 | Jan | 2022 | 1.7027e-05 | 1.7027e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-01-11 14:21 | 2022-01-11 16:47 | 1 | 002:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X10 EN TRANSFORMADOR Y SE RETIRO AVE DEL TENDIDO ELECTRICO CARGA ESTA TRANSFERIDA AL 2605-02 | C22011100088 | New_Event |  |  | Include | Wildlife | 146 | 2022-01-11 | 146 | keep | 0 | Jan | 2022 | 9.944e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-01-11 14:23 | 2022-01-11 20:10 | 45 | 005:47 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 75 KVA X 75 KVA | A22011100038 | New_Event | Service Transformer Failure | Include | Include | Equipment | 347 | 2022-01-11 | 15615 | keep | 0 | Jan | 2022 | 0.010635 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
UTUADO | 2022-01-11 14:27 | 2022-01-11 15:54 | 150 | 001:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22011100040 | New_Event | Bad Weather | Include | Include | Weather | 87 | 2022-01-11 | 13050 | keep | 0 | Jan | 2022 | 0.0088883 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2022-01-11 14:35 | 2022-01-11 15:03 | 8 | 000:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22011100028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 28 | 2022-01-11 | 224 | keep | 0 | Jan | 2022 | 0.00015257 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-01-11 14:35 | 2022-01-11 16:37 | 3 | 002:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A22011100042 | New_Event | Wire Down | Include | Include | Equipment | 122 | 2022-01-11 | 366 | keep | 0 | Jan | 2022 | 0.00024928 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2022-01-11 14:40 | 2022-01-11 14:55 | 27 | 000:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA EN VARIOS PUNTOS Y 4 TOMAS | B22011100058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 15 | 2022-01-11 | 405 | keep | 0 | Jan | 2022 | 0.00027584 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2022-01-11 14:44 | 2022-01-11 17:28 | 36 | 002:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REMPLAZO CAJA PRIMARIA | S22011100060 | New_Event | Cutout Failure | Include | Include | Equipment | 164 | 2022-01-11 | 5904 | keep | 0 | Jan | 2022 | 0.0040212 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CAGUAS | 2022-01-11 14:54 | 2022-01-11 17:28 | 48 | 002:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C22011100092 | New_Event |  |  | Include | Wildlife | 154 | 2022-01-11 | 7392 | keep | 0 | Jan | 2022 | 0.0050347 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
CAGUAS | 2022-01-11 15:05 | 2022-01-11 15:06 | 1307 | 000:01 | T | DESGANCHE | RECIERRE | C22011100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-11 | 1307 | keep | 0 | Jan | 2022 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
CAGUAS | 2022-01-11 15:06 | 2022-01-11 16:34 | 40 | 001:28 | P | DESGANCHE | 2X65 EN CORTE DE LINEA | C22011100098 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 88 | 2022-01-11 | 3520 | keep | 0 | Jan | 2022 | 0.0023975 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-01-11 15:10 | 2022-01-11 16:54 | 10 | 001:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | A22011000059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 104 | 2022-01-11 | 1040 | keep | 0 | Jan | 2022 | 0.00070834 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-11 15:14 | 2022-01-12 13:02 | 2 | 021:48 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZAZO BANCO DE XMR DE 75KVA | S22011100042 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1308 | 2022-01-11 | 2616 | keep | 0 | Jan | 2022 | 0.0017817 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-01-11 15:16 | 2022-01-11 15:44 | 16 | 000:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | C22011100100 | New_Event | Secondary Wire Down | Include | Include | Equipment | 28 | 2022-01-11 | 448 | keep | 0 | Jan | 2022 | 0.00030513 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2022-01-11 15:24 | 2022-01-11 17:55 | 4381 | 002:31 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE ABRIO MACHETES Y SE CERRO EL INTERRUPTOR SE CONTINUA PATRULLANDO | M22011100174 | New_Event | Wire Down | Include | Include | Equipment | 151 | 2022-01-11 | 661531 | keep | 0 | Jan | 2022 | 0.45057 | 0.0029839 | Sustained | FALSE | FALSE | Not_TMED_Event | 4381
MAYAGÃœEZ | 2022-01-11 15:30 | 2022-01-11 21:33 | 274 | 006:03 | P | BREAKER DEFECTUOSO O NO OPERA | INTERRUPTOR TIENE LA FASE A ABIERTA INTERNAMENTE | M22011100175 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 363 | 2022-01-11 | 99462 | keep | 0 | Jan | 2022 | 0.067743 | 0.00018662 | Sustained | FALSE | FALSE | Not_TMED_Event | 274
HUMACAO | 2022-01-11 15:32 | 2022-01-11 16:20 | 8 | 000:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X15 EN TRANSFORMADOR Y SE REMPLAZO EL PORTAFUSIBLE | C22011100105 | New_Event | Cutout Failure | Include | Include | Equipment | 48 | 2022-01-11 | 384 | keep | 0 | Jan | 2022 | 0.00026154 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2022-01-11 15:51 | 2022-01-11 17:29 | 20 | 001:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE CAJA A LINEA | C22011100106 | New_Event | Wire Down | Include | Include | Equipment | 98 | 2022-01-11 | 1960 | keep | 0 | Jan | 2022 | 0.0013349 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-01-11 15:51 | 2022-01-11 21:03 | 1 | 005:12 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25 KVA X 25 KVA | C22011100106 | New_Event | Service Transformer Failure | Include | Include | Equipment | 312 | 2022-01-11 | 312 | keep | 0 | Jan | 2022 | 0.0002125 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-01-11 15:56 | 2022-01-11 16:40 | 80 | 000:44 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22011100186 | New_Event | Vegetation Contact | Include | Include | Vegetation | 44 | 2022-01-11 | 3520 | keep | 0 | Jan | 2022 | 0.0023975 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-01-11 16:11 | 2022-01-11 16:48 | 10 | 000:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO NEUTRAL EN BAJANTE SECUNDARIO DEL TRANSFORMADOR | C22011100109 | New_Event | Secondary Wire Down | Include | Include | Equipment | 37 | 2022-01-11 | 370 | keep | 0 | Jan | 2022 | 0.00025201 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-01-11 16:20 | 2022-01-11 17:10 | 10 | 000:50 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE TRANSFORMADOR 50 KVA A 2400VOLT AVERIADO POR OTRO IGUAL CAPACIDAD Y VOLTAJE | P22011100051 | New_Event | Service Transformer Failure | Include | Include | Equipment | 50 | 2022-01-11 | 500 | keep | 0 | Jan | 2022 | 0.00034055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-01-11 16:40 | 2022-01-11 17:24 | 25 | 000:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22011100168 | New_Event | Secondary Wire Down | Include | Include | Equipment | 44 | 2022-01-11 | 1100 | keep | 0 | Jan | 2022 | 0.0007492 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-01-11 16:43 | 2022-01-12 10:37 | 12 | 017:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | M22011100205 | New_Event | Wire Down | Include | Include | Equipment | 1074 | 2022-01-11 | 12888 | keep | 0 | Jan | 2022 | 0.008778 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-01-11 16:45 | 2022-01-11 18:28 | 10 | 001:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR 3 BARRAS EN PEDESTAL | C22011100089 | New_Event | Secondary Wire Down | Include | Include | Equipment | 103 | 2022-01-11 | 1030 | keep | 0 | Jan | 2022 | 0.00070153 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-01-11 17:02 | 2022-01-11 18:46 | 8 | 001:44 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR PEDESTAL QUEMADO | R22011100028 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 104 | 2022-01-11 | 832 | keep | 0 | Jan | 2022 | 0.00056667 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-01-11 17:10 | 2022-01-11 17:53 | 5 | 000:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22011100045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 43 | 2022-01-11 | 215 | keep | 0 | Jan | 2022 | 0.00014644 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2022-01-11 17:14 | 2022-01-11 17:54 | 11 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO Y SECUNDARIA | C22011100110 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2022-01-11 | 440 | keep | 0 | Jan | 2022 | 0.00029968 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2022-01-11 17:38 | 2022-01-11 19:55 | 6 | 002:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR 100 PIES DE SECUNDARIA Y TIRAR GROUND AL TRANSFORMADOR | C22011100119 | New_Event | Secondary Wire Down | Include | Include | Equipment | 137 | 2022-01-11 | 822 | keep | 0 | Jan | 2022 | 0.00055986 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-01-11 17:41 | 2022-01-11 19:52 | 100 | 002:11 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22011100073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 131 | 2022-01-11 | 13100 | keep | 0 | Jan | 2022 | 0.0089224 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-01-11 17:55 | 2022-01-11 20:02 | 3286 | 002:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE PATRULLO Y NO SE ENCONTRO CAUSA PARA EL DISPARO DEL INTERRUPTOR SOLO LLUVIA Y VIENTO EN EL AREA SE CERRARON LOS MACHETES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR Y CERRAR EL INTERRUPTOR | M22011100233 | Partial_restoration | Wire Down | Include | Include | Equipment | 127 | 2022-01-11 | 417322 | keep | 0 | Jan | 2022 | 0.28424 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-01-11 17:55 | 2022-01-11 19:18 | 150 | 001:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PORTA FUSIBLE AVERIADO | A22011100054 | New_Event | Cutout Failure | Include | Include | Equipment | 83 | 2022-01-11 | 12450 | keep | 0 | Jan | 2022 | 0.0084796 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-01-11 18:14 | 2022-01-11 18:15 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1206-03 LLEVA 1204-05 | S22011100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-11 | 10211 | keep | 0 | Jan | 2022 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2022-01-11 18:14 | 2022-01-11 18:15 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1206-03 LLEVA 1204-05 | S22011100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-11 | 4133 | keep | 0 | Jan | 2022 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
UTUADO | 2022-01-11 18:29 | 2022-01-11 19:15 | 7 | 000:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA ABIERTA | A22011100052 | New_Event | Secondary Wire Down | Include | Include | Equipment | 46 | 2022-01-11 | 322 | keep | 0 | Jan | 2022 | 0.00021931 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-01-11 18:45 | 2022-01-11 21:17 | 9 | 002:32 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR INDICO UL2 TRAINED NO IDENTIFICO CAUSA | A22011100061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 152 | 2022-01-11 | 1368 | keep | 0 | Jan | 2022 | 0.00093174 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
FAJARDO | 2022-01-11 18:56 | 2022-01-11 20:29 | 7 | 001:33 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | R22011100039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2022-01-11 | 651 | keep | 0 | Jan | 2022 | 0.00044339 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-01-11 18:58 | 2022-01-11 20:27 | 150 | 001:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA Y VIENTO | M22011100246 | New_Event | Bad Weather | Include | Include | Weather | 89 | 2022-01-11 | 13350 | keep | 0 | Jan | 2022 | 0.0090926 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
FAJARDO | 2022-01-11 19:13 | 2022-01-11 19:56 | 102 | 000:43 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R22011100044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 43 | 2022-01-11 | 4386 | keep | 0 | Jan | 2022 | 0.0029873 | 6.9472e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 102
VEGA BAJA | 2022-01-11 19:40 | 2022-01-11 19:41 | 1859 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22011100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-11 | 1859 | keep | 0 | Jan | 2022 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
ARECIBO | 2022-01-11 19:51 | 2022-01-11 21:10 | 3 | 001:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A22011100062 | New_Event | Cutout Failure | Include | Include | Equipment | 79 | 2022-01-11 | 237 | keep | 0 | Jan | 2022 | 0.00016142 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2022-01-11 19:52 | 2022-01-11 21:13 | 334 | 001:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE QUEMADO | R22011100048 | New_Event | Cutout Failure | Include | Include | Equipment | 81 | 2022-01-11 | 27054 | keep | 0 | Jan | 2022 | 0.018426 | 0.00022749 | Sustained | FALSE | FALSE | Not_TMED_Event | 334
YAUCO | 2022-01-11 20:00 | 2022-01-12 09:14 | 30 | 013:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA POR CONTACTO DE AVE | P22011100057 | New_Event |  |  | Include | Wildlife | 794 | 2022-01-11 | 23820 | keep | 0 | Jan | 2022 | 0.016224 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-01-11 20:00 | 2022-01-11 20:47 | 1 | 000:47 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA RETIRAR ENREDADERA SOBRE MONTURA DE TRANSFORMADORES | A22011100053 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 47 | 2022-01-11 | 47 | keep | 0 | Jan | 2022 | 3.2011e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-01-11 20:02 | 2022-01-12 13:34 | 100 | 017:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO LINEA PRIMARIA PARTIDA SE CERRO N/O EN EL MISMO ALIMENTADOR | M22011100262 | Partial_restoration | Wire Down | Include | Include | Equipment | 1052 | 2022-01-11 | 105200 | keep | 0 | Jan | 2022 | 0.071651 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-11 20:25 | 2022-01-11 21:04 | 8 | 000:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA POR AUTO | P22011100048 | New_Event |  |  | Include | Wildlife | 39 | 2022-01-11 | 312 | keep | 0 | Jan | 2022 | 0.0002125 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-01-11 21:01 | 2022-01-11 23:30 | 150 | 002:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTES PRIMARIOS | A22011100066 | New_Event | Wire Down | Include | Include | Equipment | 149 | 2022-01-11 | 22350 | keep | 0 | Jan | 2022 | 0.015222 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-01-11 21:01 | 2022-01-12 09:10 | 10 | 012:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO DE CAJA A TRANSFORMADOR | B22011100076 | New_Event | Wire Down | Include | Include | Equipment | 729 | 2022-01-11 | 7290 | keep | 0 | Jan | 2022 | 0.0049652 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-11 21:25 | 2022-01-12 10:01 | 8 | 012:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A22011100068 | New_Event | Secondary Wire Down | Include | Include | Equipment | 756 | 2022-01-11 | 6048 | keep | 0 | Jan | 2022 | 0.0041193 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-01-11 21:33 | 2022-01-11 21:41 | 824 | 000:08 | T | BREAKER DEFECTUOSO O NO OPERA | SE ABRIO INTERRUPTOR PARA CERRAR EL AMARRE ENTRE EL 6003-01 Y EL 6003-03 Y TRANSFERIR LA CARGA YA QUE EL 6003-1 TIENE LA FASE A ABIERTA INTERNAMENTE | M22011100000 | Additional_clients | Feeder Breaker Failure | Include | Include | Equipment | 8 | 2022-01-11 | 6592 | keep | 0 | Jan | 2022 | 0.0044898 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-01-11 21:34 | 2022-01-11 21:41 | 667 | 000:07 | T | BREAKER DEFECTUOSO O NO OPERA | SE ABRIO INTERRUPTOR PARA CERRAR EL AMARRE ENTRE EL 6003-01 Y EL 6003-03 Y TRANSFERIR LA CARGA YA QUE EL 6003-1 TIENE LA FASE A ABIERTA INTERNAMENTE | M22011100000 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 7 | 2022-01-11 | 4669 | keep | 0 | Jan | 2022 | 0.00318 | 0.00045429 | Sustained | FALSE | FALSE | Not_TMED_Event | 667
SAN JUAN | 2022-01-11 22:04 | 2022-01-11 22:56 | 15 | 000:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22011100075 | New_Event | Secondary Wire Down | Include | Include | Equipment | 52 | 2022-01-11 | 780 | keep | 0 | Jan | 2022 | 0.00053125 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-01-11 23:43 | 2022-01-11 23:44 | 225 | 000:01 | T | NO SE REPORTO CAUSA | CARGA TRANSFERIDA AL 1303-05 DISPARO INTERRUPTOR Y SE CERRO POR CONTROL | S22011100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-11 | 225 | keep | 0 | Jan | 2022 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-01-11 23:43 | 2022-01-11 23:44 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA LA CARGA DEL 1303-04 | S22011100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-11 | 870 | keep | 0 | Jan | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-01-12 03:56 | 2022-01-12 11:04 | 85 | 007:08 | P | DESGANCHE | 2 X 50 EN C/L | R22011200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 428 | 2022-01-12 | 36380 | keep | 0 | Jan | 2022 | 0.024778 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
YAUCO | 2022-01-12 05:19 | 2022-01-12 05:20 | 2470 | 000:01 | T | NO SE REPORTO CAUSA | BREAKER ABRIO NO RECERRO SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P22011200001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-12 | 2470 | keep | 0 | Jan | 2022 | 0.0016823 | 0.0016823 | Momentary | FALSE | FALSE | Not_TMED_Event | 2470
CAGUAS | 2022-01-12 05:28 | 2022-01-12 12:45 | 400 | 007:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 CAJAS PRIMARIAS Y 3 X 140 EN CORTES DE LINEA | C22011200001 | New_Event | Cutout Failure | Include | Include | Equipment | 437 | 2022-01-12 | 174800 | keep | 0 | Jan | 2022 | 0.11906 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2022-01-12 05:44 | 2022-01-12 10:31 | 40 | 004:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA Y SE REMPLAZO CAJA PRIMARIA | S22011200002 | New_Event | Cutout Failure | Include | Include | Equipment | 287 | 2022-01-12 | 11480 | keep | 0 | Jan | 2022 | 0.007819 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-01-12 07:15 | 2022-01-12 11:16 | 25 | 004:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X50 EN CORTE DE LINEA Y SE REMPLAZO CAJA PRIMARIA | B22011200006 | New_Event | Cutout Failure | Include | Include | Equipment | 241 | 2022-01-12 | 6025 | keep | 0 | Jan | 2022 | 0.0041036 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-01-12 07:21 | 2022-01-12 07:22 | 7621 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22011200002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-12 | 7621 | keep | 0 | Jan | 2022 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
CAGUAS | 2022-01-12 07:57 | 2022-01-12 11:11 | 50 | 003:14 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C22011200009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 194 | 2022-01-12 | 9700 | keep | 0 | Jan | 2022 | 0.0066066 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-01-12 07:59 | 2022-01-12 09:52 | 25 | 001:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L SE RETIRO AVE | C22011200010 | New_Event |  |  | Include | Wildlife | 113 | 2022-01-12 | 2825 | keep | 0 | Jan | 2022 | 0.0019241 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-01-12 08:16 | 2022-01-12 13:12 | 3 | 004:56 | P | DESGANCHE | 1 X 8 EN TRANSFORMADOR POR DESGANCHE | A22011200008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 296 | 2022-01-12 | 888 | keep | 0 | Jan | 2022 | 0.00060481 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2022-01-12 08:22 | 2022-01-12 08:23 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22011200005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-12 | 2113 | keep | 0 | Jan | 2022 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
ARECIBO | 2022-01-12 08:27 | 2022-01-12 10:33 | 50 | 002:06 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22011200010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2022-01-12 | 6300 | keep | 0 | Jan | 2022 | 0.0042909 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-12 08:30 | 2022-01-12 11:29 | 10 | 002:59 | P | NO SE REPORTO CAUSA | 1X15 EN TRANSFORMADOR | B21011200011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 179 | 2022-01-12 | 1790 | keep | 0 | Jan | 2022 | 0.0012192 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-01-12 08:36 | 2022-01-12 14:00 | 10 | 005:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR REMPLAZO CAJA AVERIADA | R22011200009 | New_Event | Cutout Failure | Include | Include | Equipment | 324 | 2022-01-12 | 3240 | keep | 0 | Jan | 2022 | 0.0022067 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-12 08:44 | 2022-01-12 14:15 | 25 | 005:31 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22011200013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 331 | 2022-01-12 | 8275 | keep | 0 | Jan | 2022 | 0.0056361 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-01-12 08:58 | 2022-01-12 17:32 | 501 | 008:34 | P | DESGANCHE | D2021-00773 VIA LIBRE PARA REALIZAR DESGANCHE | C22011200014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 514 | 2022-01-12 | 257514 | keep | 0 | Jan | 2022 | 0.17539 | 0.00034123 | Sustained | FALSE | FALSE | Not_TMED_Event | 501
SAN JUAN | 2022-01-12 08:59 | 2022-01-12 10:57 | 120 | 001:58 | P | PARARRAYOS DEFECTUOSO | 3 X 80 EN CORTE DE LINEA Y SE REEMPLAZARON 3 PARRARAYOS | S22011200011 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 118 | 2022-01-12 | 14160 | keep | 0 | Jan | 2022 | 0.0096443 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
ARECIBO | 2022-01-12 08:59 | 2022-01-12 14:28 | 1 | 005:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE QUEMADO | A22011200015 | New_Event | Cutout Failure | Include | Include | Equipment | 329 | 2022-01-12 | 329 | keep | 0 | Jan | 2022 | 0.00022408 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-01-12 09:23 | 2022-01-12 09:24 | 1307 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22011200026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-12 | 1307 | keep | 0 | Jan | 2022 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
ARECIBO | 2022-01-12 09:25 | 2022-01-12 11:14 | 1105 | 001:49 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR LINEA PRIMARIA PARTIDA SE SECCIONALIZO | A22011200018 | New_Event | Wire Down | Include | Include | Equipment | 109 | 2022-01-12 | 120445 | keep | 0 | Jan | 2022 | 0.082035 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
SAN JUAN | 2022-01-12 09:27 | 2022-01-12 09:28 | 9 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3600 | R22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-12 | 9 | keep | 0 | Jan | 2022 | 6.1299e-06 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-01-12 09:27 | 2022-01-12 09:28 | 6 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3600 | R22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-12 | 6 | keep | 0 | Jan | 2022 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-01-12 09:27 | 2022-01-12 09:28 | 1 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3600 | R22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-12 | 1 | keep | 0 | Jan | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-01-12 09:27 | 2022-01-12 09:28 | 1 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3600 | R22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-12 | 1 | keep | 0 | Jan | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-01-12 09:27 | 2022-01-12 09:28 | 12 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3600 | R22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-12 | 12 | keep | 0 | Jan | 2022 | 8.1731e-06 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-01-12 09:27 | 2022-01-12 09:28 | 331 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3600 | R22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-12 | 331 | keep | 0 | Jan | 2022 | 0.00022544 | 0.00022544 | Momentary | FALSE | FALSE | Not_TMED_Event | 331
SAN JUAN | 2022-01-12 09:27 | 2022-01-12 09:28 | 1132 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3600 | R22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-12 | 1132 | keep | 0 | Jan | 2022 | 0.000771 | 0.000771 | Momentary | FALSE | FALSE | Not_TMED_Event | 1132
SAN JUAN | 2022-01-12 09:27 | 2022-01-12 09:28 | 234 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3600 | R22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-12 | 234 | keep | 0 | Jan | 2022 | 0.00015938 | 0.00015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 234
SAN JUAN | 2022-01-12 09:27 | 2022-01-12 09:28 | 2179 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3600 | R22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-12 | 2179 | keep | 0 | Jan | 2022 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
SAN JUAN | 2022-01-12 09:27 | 2022-01-12 09:28 | 5062 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3600 | R22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-12 | 5062 | keep | 0 | Jan | 2022 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
MAYAGÃœEZ | 2022-01-12 09:31 | 2022-01-12 09:53 | 1617 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2022-01-12 | 35574 | keep | 0 | Jan | 2022 | 0.024229 | 0.0011013 | Sustained | FALSE | FALSE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2022-01-12 09:31 | 2022-01-12 09:53 | 1017 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2022-01-12 | 22374 | keep | 0 | Jan | 2022 | 0.015239 | 0.00069267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2022-01-12 09:31 | 2022-01-12 09:53 | 828 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2022-01-12 | 18216 | keep | 0 | Jan | 2022 | 0.012407 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
AGUADILLA | 2022-01-12 09:35 | 2022-01-12 12:55 | 15 | 003:20 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE 25 KVA X 25 KVA | M22011200013 | New_Event | Service Transformer Failure | Include | Include | Equipment | 200 | 2022-01-12 | 3000 | keep | 0 | Jan | 2022 | 0.0020433 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-01-12 09:40 | 2022-01-12 12:55 | 20 | 003:15 | P | NO SE REPORTO CAUSA | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO Y SECUNDARIA | C22011200017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 195 | 2022-01-12 | 3900 | keep | 0 | Jan | 2022 | 0.0026563 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-01-12 09:49 | 2022-01-12 16:49 | 100 | 007:00 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22011200026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 420 | 2022-01-12 | 42000 | keep | 0 | Jan | 2022 | 0.028606 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-01-12 10:15 | 2022-01-12 13:35 | 9 | 003:20 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50KVA X 37.5KVA | A22011200027 | New_Event | Service Transformer Failure | Include | Include | Equipment | 200 | 2022-01-12 | 1800 | keep | 0 | Jan | 2022 | 0.001226 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-01-12 10:57 | 2022-01-12 11:01 | 1484 | 000:04 | P | PARARRAYOS DEFECTUOSO | DISPARO DE ALIMENTADOR 1336-08 SE CERRO POR SCADA LLEVA EL 1336-09 Y 30% DEL 1204-04 | S22011200000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 4 | 2022-01-12 | 5936 | keep | 0 | Jan | 2022 | 0.004043 | 0.0010107 | Momentary | FALSE | FALSE | Not_TMED_Event | 1484
SAN JUAN | 2022-01-12 10:57 | 2022-01-12 11:01 | 5290 | 000:04 | T | PARARRAYOS DEFECTUOSO | DISPARO DE ALIMENTADOR 1336-08 SE CERRO POR SCADA LLEVA EL 1336-09 Y 30% DEL 1204-04 | S22011200000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 4 | 2022-01-12 | 21160 | keep | 0 | Jan | 2022 | 0.014412 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-01-12 10:57 | 2022-01-12 11:01 | 207 | 000:04 | T | PARARRAYOS DEFECTUOSO | DISPARO DE ALIMENTADOR 1336-08 SE CERRO POR SCADA LLEVA EL 1336-09 Y 30% DEL 1204-04 | S22011200000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 4 | 2022-01-12 | 828 | keep | 0 | Jan | 2022 | 0.00056395 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2022-01-12 11:01 | 2022-01-12 11:21 | 120 | 000:20 | P | PARARRAYOS DEFECTUOSO | 3 X 80 EN CORTE DE LINEA Y SE REEMPLAZARON 3 PARRARAYOS | S22011200011 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 20 | 2022-01-12 | 2400 | keep | 0 | Jan | 2022 | 0.0016346 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
YAUCO | 2022-01-12 11:09 | 2022-01-12 12:12 | 12 | 001:03 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR NO SE REPORTA CAUSA | P22011200016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2022-01-12 | 756 | keep | 0 | Jan | 2022 | 0.00051491 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-01-12 11:14 | 2022-01-12 15:37 | 300 | 004:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO LINEA PRIMARIA PARTIDA | A22011200018 | New_Event | Wire Down | Include | Include | Equipment | 263 | 2022-01-12 | 78900 | keep | 0 | Jan | 2022 | 0.053738 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-01-12 11:19 | 2022-01-12 12:52 | 10 | 001:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA Y SE RETIRO GLOBO | B22011200030 | New_Event |  |  | Include | Wildlife | 93 | 2022-01-12 | 930 | keep | 0 | Jan | 2022 | 0.00063342 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-01-12 11:22 | 2022-01-12 17:19 | 30 | 005:57 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN C/L REMPLAZO AISLADOR PARTIDO | R22011200018 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 357 | 2022-01-12 | 10710 | keep | 0 | Jan | 2022 | 0.0072945 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-01-12 11:25 | 2022-01-12 15:19 | 10 | 003:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZARON BARRAS EN PEDESTAL | B22011200025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 234 | 2022-01-12 | 2340 | keep | 0 | Jan | 2022 | 0.0015938 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-12 11:30 | 2022-01-12 11:32 | 946 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1525-05 SE CERRO POR SCADA LLEVA EL 1525-02 | S22011200024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-12 | 1892 | keep | 0 | Jan | 2022 | 0.0012886 | 0.00064432 | Momentary | FALSE | FALSE | Not_TMED_Event | 946
BAYAMON | 2022-01-12 11:30 | 2022-01-12 11:32 | 937 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA EL 1525-02 | S22011200024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-12 | 1874 | keep | 0 | Jan | 2022 | 0.0012764 | 0.00063819 | Momentary | FALSE | FALSE | Not_TMED_Event | 937
BAYAMON | 2022-01-12 11:31 | 2022-01-12 11:32 | 15 | 000:01 | P | NO SE REPORTO CAUSA | 1X30 EN TRANSFORMADOR | B22011200008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-12 | 15 | keep | 0 | Jan | 2022 | 1.0216e-05 | 1.0216e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-01-12 11:43 | 2022-01-12 15:20 | 25 | 003:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA INDICA JOURNEYMAN REQUIERE DESGANCHE | M22011200026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2022-01-12 | 5425 | keep | 0 | Jan | 2022 | 0.0036949 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-01-12 11:49 | 2022-01-12 13:21 | 10 | 001:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO Y LINEA SECUNDARIA EN VARIOS PUNTOS | B22011200031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 92 | 2022-01-12 | 920 | keep | 0 | Jan | 2022 | 0.00062661 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-01-12 12:01 | 2022-01-12 17:08 | 50 | 005:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 40 EN CORTE DE LINEA CAMION CRUZO LINEAS | M22011200048 | New_Event |  |  | Include | Wildlife | 307 | 2022-01-12 | 15350 | keep | 0 | Jan | 2022 | 0.010455 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-01-12 12:07 | 2022-01-12 12:41 | 12 | 000:34 | P | NO SE REPORTO CAUSA | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C22011200030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 34 | 2022-01-12 | 408 | keep | 0 | Jan | 2022 | 0.00027789 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-01-12 12:07 | 2022-01-12 15:49 | 6 | 003:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | C22011200047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 222 | 2022-01-12 | 1332 | keep | 0 | Jan | 2022 | 0.00090722 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-01-12 13:04 | 2022-01-12 13:05 | 4154 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | R22011200050 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-01-12 | 4154 | keep | 0 | Jan | 2022 | 0.0028293 | 0.0028293 | Momentary | FALSE | FALSE | Not_TMED_Event | 4154
CANOVANAS | 2022-01-12 13:05 | 2022-01-12 14:01 | 200 | 000:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 140 EN C/L LEVANTO CONDUCTORES | R22011200051 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 56 | 2022-01-12 | 11200 | keep | 0 | Jan | 2022 | 0.0076283 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-01-12 13:11 | 2022-01-12 14:54 | 25 | 001:43 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S22011200037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 103 | 2022-01-12 | 2575 | keep | 0 | Jan | 2022 | 0.0017538 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2022-01-12 13:20 | 2022-01-12 16:30 | 100 | 003:10 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO QUEMADO | A22011200051 | New_Event | Defective Pole | Include | Include | Equipment | 190 | 2022-01-12 | 19000 | keep | 0 | Jan | 2022 | 0.012941 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-01-12 13:33 | 2022-01-12 16:10 | 3 | 002:37 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22011200052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 157 | 2022-01-12 | 471 | keep | 0 | Jan | 2022 | 0.0003208 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-01-12 13:45 | 2022-01-12 13:46 | 2560 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22011200066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-12 | 2560 | keep | 0 | Jan | 2022 | 0.0017436 | 0.0017436 | Momentary | FALSE | FALSE | Not_TMED_Event | 2560
CAGUAS | 2022-01-12 13:46 | 2022-01-12 15:56 | 20 | 002:10 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | C22011200056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2022-01-12 | 2600 | keep | 0 | Jan | 2022 | 0.0017708 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-01-12 13:55 | 2022-01-12 14:24 | 12 | 000:29 | P | NO SE REPORTO CAUSA | SE ABRIO XMR PARA REPARAR NEUTRAL | C22011100122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 29 | 2022-01-12 | 348 | keep | 0 | Jan | 2022 | 0.00023702 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-01-12 14:00 | 2022-01-12 14:01 | 3025 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22011200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-12 | 3025 | keep | 0 | Jan | 2022 | 0.0020603 | 0.0020603 | Momentary | FALSE | FALSE | Not_TMED_Event | 3025
CANOVANAS | 2022-01-12 14:01 | 2022-01-12 14:06 | 4154 | 000:05 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO BKR PARA SECCIONALIZAR CONDUCTOR EN EL SUELO | R22011200050 | Additional_clients | Wire Down | Include | Include | Equipment | 5 | 2022-01-12 | 20770 | keep | 0 | Jan | 2022 | 0.014146 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-01-12 14:03 | 2022-01-12 15:22 | 80 | 001:19 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA INDICA JOURNEYMAN QUE REQUIERE DESGANCHE | M22011200070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2022-01-12 | 6320 | keep | 0 | Jan | 2022 | 0.0043045 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-01-12 14:05 | 2022-01-12 15:22 | 20 | 001:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | M22011200045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 77 | 2022-01-12 | 1540 | keep | 0 | Jan | 2022 | 0.0010489 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-01-12 14:06 | 2022-01-12 18:13 | 200 | 004:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 140 EN C/L LEVANTO CONDUCTORES | R22011200051 | Partial_restoration | Wire Down | Include | Include | Equipment | 247 | 2022-01-12 | 49400 | keep | 0 | Jan | 2022 | 0.033646 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-12 14:06 | 2022-01-12 15:30 | 6 | 001:24 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 25KVA POR UNO DE 25KVA | C22011200061 | New_Event | Service Transformer Failure | Include | Include | Equipment | 84 | 2022-01-12 | 504 | keep | 0 | Jan | 2022 | 0.00034327 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-01-12 14:35 | 2022-01-12 15:41 | 10 | 001:06 | P | NO SE REPORTO CAUSA | 1X15 EN TRANSFORMADOR | B22011200042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 66 | 2022-01-12 | 660 | keep | 0 | Jan | 2022 | 0.00044952 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-01-12 14:44 | 2022-01-12 16:55 | 1 | 002:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO SE ABRIO CORTE DE LINEA PARA CERRARLO | M22011200085 | New_Event | Wire Down | Include | Include | Equipment | 131 | 2022-01-12 | 131 | keep | 0 | Jan | 2022 | 8.9224e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-01-12 15:06 | 2022-01-12 15:35 | 15 | 000:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA Y CONEXIONES | A22011200066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 29 | 2022-01-12 | 435 | keep | 0 | Jan | 2022 | 0.00029628 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-01-12 15:08 | 2022-01-12 18:30 | 50 | 003:22 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M22011200092 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 202 | 2022-01-12 | 10100 | keep | 0 | Jan | 2022 | 0.0068791 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-12 15:18 | 2022-01-13 15:19 | 10 | 024:01 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR | S22011200054 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1441 | 2022-01-12 | 14410 | keep | 0 | Jan | 2022 | 0.0098146 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-12 15:20 | 2022-01-12 15:21 | 1834 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-12 | 1834 | keep | 0 | Jan | 2022 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BAYAMON | 2022-01-12 15:20 | 2022-01-12 15:21 | 2324 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-12 | 2324 | keep | 0 | Jan | 2022 | 0.0015829 | 0.0015829 | Momentary | FALSE | FALSE | Not_TMED_Event | 2324
VEGA BAJA | 2022-01-12 15:20 | 2022-01-12 15:21 | 1570 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-12 | 1570 | keep | 0 | Jan | 2022 | 0.0010693 | 0.0010693 | Momentary | FALSE | FALSE | Not_TMED_Event | 1570
VEGA BAJA | 2022-01-12 15:30 | 2022-01-12 15:31 | 652 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-12 | 652 | keep | 0 | Jan | 2022 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2022-01-12 15:30 | 2022-01-12 15:31 | 2704 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-12 | 2704 | keep | 0 | Jan | 2022 | 0.0018417 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
BAYAMON | 2022-01-12 15:30 | 2022-01-12 15:31 | 2861 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-12 | 2861 | keep | 0 | Jan | 2022 | 0.0019486 | 0.0019486 | Momentary | FALSE | FALSE | Not_TMED_Event | 2861
BAYAMON | 2022-01-12 15:30 | 2022-01-12 15:31 | 2096 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-12 | 2096 | keep | 0 | Jan | 2022 | 0.0014276 | 0.0014276 | Momentary | FALSE | FALSE | Not_TMED_Event | 2096
BAYAMON | 2022-01-12 15:30 | 2022-01-12 15:31 | 493 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-12 | 493 | keep | 0 | Jan | 2022 | 0.00033578 | 0.00033578 | Momentary | FALSE | FALSE | Not_TMED_Event | 493
VEGA BAJA | 2022-01-12 15:31 | 2022-01-12 15:32 | 1526 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-12 | 1526 | keep | 0 | Jan | 2022 | 0.0010394 | 0.0010394 | Momentary | FALSE | FALSE | Not_TMED_Event | 1526
VEGA BAJA | 2022-01-12 15:31 | 2022-01-12 15:32 | 308 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-12 | 308 | keep | 0 | Jan | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2022-01-12 15:31 | 2022-01-12 15:32 | 1397 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-12 | 1397 | keep | 0 | Jan | 2022 | 0.00095149 | 0.00095149 | Momentary | FALSE | FALSE | Not_TMED_Event | 1397
VEGA BAJA | 2022-01-12 15:31 | 2022-01-12 15:32 | 2926 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22011200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-12 | 2926 | keep | 0 | Jan | 2022 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
PONCE | 2022-01-12 15:43 | 2022-01-12 16:22 | 100 | 000:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 65 EN CORTE DE LINEA CARPA CRUZO LINEAS | P22011200050 | New_Event |  |  | Include | Wildlife | 39 | 2022-01-12 | 3900 | keep | 0 | Jan | 2022 | 0.0026563 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-01-12 15:58 | 2022-01-12 18:46 | 1 | 002:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA NO FUNDIO | R22011200079 | New_Event | Wire Down | Include | Include | Equipment | 168 | 2022-01-12 | 168 | keep | 0 | Jan | 2022 | 0.00011442 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-01-12 16:09 | 2022-01-12 16:55 | 10 | 000:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | B22011200029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 46 | 2022-01-12 | 460 | keep | 0 | Jan | 2022 | 0.0003133 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-01-12 16:26 | 2022-01-13 08:22 | 1 | 015:56 | P | NO SE REPORTO CAUSA | 1 X 10 EN RISER NO CAUSA | C22011200072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 956 | 2022-01-12 | 956 | keep | 0 | Jan | 2022 | 0.00065113 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-01-12 16:29 | 2022-01-12 21:09 | 65 | 004:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22011200117 | New_Event | Bad Weather | Include | Include | Weather | 280 | 2022-01-12 | 18200 | keep | 0 | Jan | 2022 | 0.012396 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2022-01-12 16:32 | 2022-01-12 17:31 | 10 | 000:59 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 25KVA POR UNO DE 37.5KVA | C22011200075 | New_Event | Service Transformer Failure | Include | Include | Equipment | 59 | 2022-01-12 | 590 | keep | 0 | Jan | 2022 | 0.00040185 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-12 16:32 | 2022-01-12 16:33 | 1986 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22011200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-12 | 1986 | keep | 0 | Jan | 2022 | 0.0013527 | 0.0013527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1986
HUMACAO | 2022-01-12 16:34 | 2022-01-12 17:04 | 6 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | C22011200077 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2022-01-12 | 180 | keep | 0 | Jan | 2022 | 0.0001226 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2022-01-12 16:36 | 2022-01-12 18:44 | 15 | 002:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTES SECUNDARIOS | P22011200058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 128 | 2022-01-12 | 1920 | keep | 0 | Jan | 2022 | 0.0013077 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-01-12 16:38 | 2022-01-12 19:24 | 60 | 002:46 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22011200076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2022-01-12 | 9960 | keep | 0 | Jan | 2022 | 0.0067837 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-01-12 16:46 | 2022-01-12 16:49 | 3420 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | C22011200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-01-12 | 10260 | keep | 0 | Jan | 2022 | 0.006988 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
PONCE | 2022-01-12 16:52 | 2022-01-12 18:15 | 50 | 001:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA ESA ES LA CANTIDAD DE CLIENTES QUE SE INFORMO TRANSFORMADOR DE 75 KVA | P22011200059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 83 | 2022-01-12 | 4150 | keep | 0 | Jan | 2022 | 0.0028265 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-12 16:55 | 2022-01-12 18:05 | 14 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA Y BAJANTE | S22011210056 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2022-01-12 | 980 | keep | 0 | Jan | 2022 | 0.00066747 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2022-01-12 16:55 | 2022-01-12 18:45 | 80 | 001:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO SE CERRO CORTE DE LINEA | M22011200085 | Additional_clients | Wire Down | Include | Include | Equipment | 110 | 2022-01-12 | 8800 | keep | 0 | Jan | 2022 | 0.0059936 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-01-12 16:58 | 2022-01-12 18:46 | 100 | 001:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22011200077 | New_Event | Cutout Failure | Include | Include | Equipment | 108 | 2022-01-12 | 10800 | keep | 0 | Jan | 2022 | 0.0073558 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-01-12 17:00 | 2022-01-12 19:00 | 80 | 002:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L AVE | C22011200082 | New_Event |  |  | Include | Wildlife | 120 | 2022-01-12 | 9600 | keep | 0 | Jan | 2022 | 0.0065385 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-01-12 17:00 | 2022-01-12 17:40 | 50 | 000:40 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | P22011200062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 40 | 2022-01-12 | 2000 | keep | 0 | Jan | 2022 | 0.0013622 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-01-12 17:00 | 2022-01-12 18:40 | 20 | 001:40 | P | DESGANCHE | 1 X 30 EN CONVERTIDOR SE RETIRO RAMAS SOBRE LAS LINEAS | A22011200078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2022-01-12 | 2000 | keep | 0 | Jan | 2022 | 0.0013622 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-01-12 17:10 | 2022-01-12 19:20 | 1 | 002:10 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | M22011200123 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 130 | 2022-01-12 | 130 | keep | 0 | Jan | 2022 | 8.8542e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-01-12 17:22 | 2022-01-12 17:23 | 1022 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DEL INTERRUPTOR | A22011200000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-01-12 | 1022 | keep | 0 | Jan | 2022 | 0.00069608 | 0.00069608 | Momentary | FALSE | FALSE | Not_TMED_Event | 1022
ARECIBO | 2022-01-12 17:23 | 2022-01-12 20:33 | 800 | 003:10 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR PARTIDO | A22011200083 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 190 | 2022-01-12 | 152000 | keep | 0 | Jan | 2022 | 0.10353 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
CANOVANAS | 2022-01-12 17:45 | 2022-01-12 19:37 | 100 | 001:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN C/L, 1 X 50 Y 1 X 40 EN RISERS REMPLAZO AISLADOR ROTO | R22011200100 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 112 | 2022-01-12 | 11200 | keep | 0 | Jan | 2022 | 0.0076283 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-01-12 17:51 | 2022-01-12 18:43 | 1 | 000:52 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | R22011200101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 52 | 2022-01-12 | 52 | keep | 0 | Jan | 2022 | 3.5417e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-01-12 17:52 | 2022-01-12 18:46 | 3 | 000:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO NEUTRAL | C22011200070 | New_Event | Secondary Wire Down | Include | Include | Equipment | 54 | 2022-01-12 | 162 | keep | 0 | Jan | 2022 | 0.00011034 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-01-12 17:55 | 2022-01-12 18:02 | 8 | 000:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M22011200129 | New_Event | Secondary Wire Down | Include | Include | Equipment | 7 | 2022-01-12 | 56 | keep | 0 | Jan | 2022 | 3.8141e-05 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2022-01-12 18:07 | 2022-01-12 22:11 | 100 | 004:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE CAMBIO CAJA PRIMARIA QUEMADA | P22011200063 | New_Event | Cutout Failure | Include | Include | Equipment | 244 | 2022-01-12 | 24400 | keep | 0 | Jan | 2022 | 0.016619 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-01-12 18:12 | 2022-01-12 18:13 | 718 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22011200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-12 | 718 | keep | 0 | Jan | 2022 | 0.00048903 | 0.00048903 | Momentary | FALSE | FALSE | Not_TMED_Event | 718
GUAYAMA | 2022-01-12 18:30 | 2022-01-12 18:43 | 50 | 000:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | P22011200067 | New_Event |  |  | Include | Wildlife | 13 | 2022-01-12 | 650 | keep | 0 | Jan | 2022 | 0.00044271 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-01-12 18:37 | 2022-01-13 11:58 | 7 | 017:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR SECUNDARIA | C22011200087 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1041 | 2022-01-12 | 7287 | keep | 0 | Jan | 2022 | 0.0049631 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-01-12 18:49 | 2022-01-12 19:30 | 80 | 000:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA VEHICULO CRUZO LINEAS | M22011200136 | New_Event |  |  | Include | Wildlife | 41 | 2022-01-12 | 3280 | keep | 0 | Jan | 2022 | 0.002234 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-01-12 19:10 | 2022-01-12 20:10 | 12 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR BAJANTE SECUNDARIO | S22011200061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2022-01-12 | 720 | keep | 0 | Jan | 2022 | 0.00049039 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-01-12 19:58 | 2022-01-12 22:40 | 5 | 002:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22011200141 | New_Event | Bad Weather | Include | Include | Weather | 162 | 2022-01-12 | 810 | keep | 0 | Jan | 2022 | 0.00055169 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-01-12 20:27 | 2022-01-12 22:23 | 40 | 001:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M22011200143 | New_Event | Cutout Failure | Include | Include | Equipment | 116 | 2022-01-12 | 4640 | keep | 0 | Jan | 2022 | 0.0031603 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-01-12 20:39 | 2022-01-13 09:18 | 9 | 012:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | R22011200107 | New_Event | Secondary Wire Down | Include | Include | Equipment | 759 | 2022-01-12 | 6831 | keep | 0 | Jan | 2022 | 0.0046526 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2022-01-12 20:39 | 2022-01-12 20:40 | 2302 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22011200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-12 | 2302 | keep | 0 | Jan | 2022 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
MAYAGÃœEZ | 2022-01-12 20:45 | 2022-01-12 21:55 | 1 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M22011200145 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2022-01-12 | 70 | keep | 0 | Jan | 2022 | 4.7677e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-01-12 20:58 | 2022-01-13 11:27 | 7 | 014:29 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | C22011200092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 869 | 2022-01-12 | 6083 | keep | 0 | Jan | 2022 | 0.0041431 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-01-12 21:07 | 2022-01-12 23:42 | 100 | 002:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN C/L SE REMPLAZO CAJA PRIMARIA | B22011200060 | New_Event | Cutout Failure | Include | Include | Equipment | 155 | 2022-01-12 | 15500 | keep | 0 | Jan | 2022 | 0.010557 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-01-12 22:10 | 2022-01-13 09:45 | 75 | 011:35 | P | DESGANCHE | SE RETIRO ARBOL SOBRE LINEAS PRIMARIAS Y SE CERRO CORTE DE LINEA | A22011200120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 695 | 2022-01-12 | 52125 | keep | 0 | Jan | 2022 | 0.035502 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
UTUADO | 2022-01-12 22:22 | 2022-01-13 13:47 | 30 | 015:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA Y SE REALIZO DESGANCHE | A22011200123 | New_Event | Wire Down | Include | Include | Equipment | 925 | 2022-01-12 | 27750 | keep | 0 | Jan | 2022 | 0.0189 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-01-12 22:24 | 2022-01-13 10:10 | 45 | 011:46 | P | DESGANCHE | 1 X 65 EN C/L | C22011200097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 706 | 2022-01-12 | 31770 | keep | 0 | Jan | 2022 | 0.021638 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2022-01-12 23:45 | 2022-01-12 23:46 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22011200149 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-12 | 1192 | keep | 0 | Jan | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
MAYAGÃœEZ | 2022-01-13 01:00 | 2022-01-13 06:33 | 6 | 005:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | M22011300001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 333 | 2022-01-13 | 1998 | keep | 0 | Jan | 2022 | 0.0013608 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-01-13 01:13 | 2022-01-13 14:06 | 30 | 012:53 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22011300001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 773 | 2022-01-13 | 23190 | keep | 0 | Jan | 2022 | 0.015795 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2022-01-13 02:25 | 2022-01-13 10:22 | 75 | 007:57 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22011300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 477 | 2022-01-13 | 35775 | keep | 0 | Jan | 2022 | 0.024366 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2022-01-13 03:43 | 2022-01-13 08:12 | 169 | 004:29 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA, 1 X 65 EN PROVISIONAL, 1 X 50 EN PROVISIONAL, 1 X 40 EN RISER Y NO SE REPORTA CAUSA | S22011300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 269 | 2022-01-13 | 45461 | keep | 0 | Jan | 2022 | 0.030963 | 0.00011511 | Sustained | FALSE | FALSE | Not_TMED_Event | 169
BAYAMON | 2022-01-13 06:43 | 2022-01-13 06:44 | 3798 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22011300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-13 | 3798 | keep | 0 | Jan | 2022 | 0.0025868 | 0.0025868 | Momentary | FALSE | FALSE | Not_TMED_Event | 3798
HUMACAO | 2022-01-13 06:55 | 2022-01-13 11:21 | 30 | 004:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN C/L CRUCE X REPTIL | C22011300001 | New_Event |  |  | Include | Wildlife | 266 | 2022-01-13 | 7980 | keep | 0 | Jan | 2022 | 0.0054351 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-01-13 07:03 | 2022-01-13 10:23 | 50 | 003:20 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22011300003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2022-01-13 | 10000 | keep | 0 | Jan | 2022 | 0.006811 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-01-13 07:38 | 2022-01-13 10:40 | 80 | 003:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA IGUANA CRUZO LINEAS | M22011300004 | New_Event |  |  | Include | Wildlife | 182 | 2022-01-13 | 14560 | keep | 0 | Jan | 2022 | 0.0099167 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-01-13 07:51 | 2022-01-13 07:52 | 4634 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22011300005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-13 | 4634 | keep | 0 | Jan | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
BAYAMON | 2022-01-13 08:03 | 2022-01-13 15:28 | 2 | 007:25 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACION AVERIADA | B22011300001 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 445 | 2022-01-13 | 890 | keep | 0 | Jan | 2022 | 0.00060617 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-01-13 08:08 | 2022-01-13 16:10 | 100 | 008:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA INDICA JOURNEYMAN REQUIERE DESGANCHE | M22011300005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 482 | 2022-01-13 | 48200 | keep | 0 | Jan | 2022 | 0.032829 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-01-13 08:12 | 2022-01-13 14:20 | 80 | 006:08 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA INDICA FOREMAN REQUIERE DESGANCHE | M22011300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 368 | 2022-01-13 | 29440 | keep | 0 | Jan | 2022 | 0.020051 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-01-13 08:33 | 2022-01-14 11:37 | 40 | 027:04 | P | PARARRAYOS DEFECTUOSO | 3 PARARAYO 1 X 50 EN CORTE DE LINEA | C22011300342 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1624 | 2022-01-13 | 64960 | keep | 0 | Jan | 2022 | 0.044244 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-01-13 09:09 | 2022-01-13 11:11 | 100 | 002:02 | P | DESGANCHE | 1 X 80 EN C/L. SE REALIZO DESGANCHE | B22011300010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2022-01-13 | 12200 | keep | 0 | Jan | 2022 | 0.0083094 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-01-13 09:11 | 2022-01-13 15:50 | 10 | 006:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | S22011300011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 399 | 2022-01-13 | 3990 | keep | 0 | Jan | 2022 | 0.0027176 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-01-13 09:16 | 2022-01-13 14:55 | 1 | 005:39 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P22011300009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 339 | 2022-01-13 | 339 | keep | 0 | Jan | 2022 | 0.00023089 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-01-13 09:16 | 2022-01-13 12:55 | 2 | 003:39 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS | A22011300011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2022-01-13 | 438 | keep | 0 | Jan | 2022 | 0.00029832 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
FAJARDO | 2022-01-13 09:21 | 2022-01-13 12:14 | 9 | 002:53 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZO DE POSTE SECUNDARIO | R22011200003 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 173 | 2022-01-13 | 1557 | keep | 0 | Jan | 2022 | 0.0010605 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-01-13 09:22 | 2022-01-13 09:23 | 888 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 1600 | M22011300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-13 | 888 | keep | 0 | Jan | 2022 | 0.00060481 | 0.00060481 | Momentary | FALSE | FALSE | Not_TMED_Event | 888
MAYAGÃœEZ | 2022-01-13 09:22 | 2022-01-13 09:23 | 393 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 1600 | M22011300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-13 | 393 | keep | 0 | Jan | 2022 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2022-01-13 09:22 | 2022-01-13 09:23 | 4 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 1600 | M22011300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-13 | 4 | keep | 0 | Jan | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-01-13 09:22 | 2022-01-13 09:23 | 372 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 1600 | M22011300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-13 | 372 | keep | 0 | Jan | 2022 | 0.00025337 | 0.00025337 | Momentary | FALSE | FALSE | Not_TMED_Event | 372
MAYAGÃœEZ | 2022-01-13 09:22 | 2022-01-13 09:23 | 2530 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 1600 | M22011300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-13 | 2530 | keep | 0 | Jan | 2022 | 0.0017232 | 0.0017232 | Momentary | FALSE | FALSE | Not_TMED_Event | 2530
MAYAGÃœEZ | 2022-01-13 09:22 | 2022-01-13 09:23 | 199 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 1600 | M22011300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-13 | 199 | keep | 0 | Jan | 2022 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
MAYAGÃœEZ | 2022-01-13 09:22 | 2022-01-13 09:23 | 312 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 1600 | M22011300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-13 | 312 | keep | 0 | Jan | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
MAYAGÃœEZ | 2022-01-13 09:22 | 2022-01-13 09:23 | 4641 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 1600 | M22011300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-13 | 4641 | keep | 0 | Jan | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
ARECIBO | 2022-01-13 09:29 | 2022-01-13 11:09 | 75 | 001:40 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22011300014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2022-01-13 | 7500 | keep | 0 | Jan | 2022 | 0.0051082 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2022-01-13 09:32 | 2022-01-13 09:36 | 725 | 000:04 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO PERSONAL CONTRATISTA DESGANCHANDO | C22011300007 | New_Event |  |  | Include | Wildlife | 4 | 2022-01-13 | 2900 | keep | 0 | Jan | 2022 | 0.0019752 | 0.00049379 | Momentary | FALSE | FALSE | Not_TMED_Event | 725
CAGUAS | 2022-01-13 09:34 | 2022-01-13 13:47 | 43 | 004:13 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | REMPLAZO TERMINACION EN EL SU - 1 | C22011300008 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 253 | 2022-01-13 | 10879 | keep | 0 | Jan | 2022 | 0.0074096 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
GUAYAMA | 2022-01-13 09:41 | 2022-01-13 10:40 | 20 | 000:59 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5 KVA A 7.2 / 13.2 KV POR ESCAPE DE ACEITE | P22011300016 | New_Event | Service Transformer Failure | Include | Include | Equipment | 59 | 2022-01-13 | 1180 | keep | 0 | Jan | 2022 | 0.00080369 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-01-13 09:55 | 2022-01-13 09:56 | 317 | 000:01 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR 1711-01 A PETICION DE RANGEL VAZQUEZ Y ELVIN MORALES POR SEGURIDAD EN TRABAJOS GOI BY-211220-02 YA QUE EL DESCONECTIVO DEL SU-13B ESTA ROTO Y TUVIERON QUE HACERLO CON VARETA. 80% DE SU CARGA POR EL 1716-03 | B22011300015 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-01-13 | 317 | keep | 0 | Jan | 2022 | 0.00021591 | 0.00021591 | Momentary | FALSE | FALSE | Not_TMED_Event | 317
CAGUAS | 2022-01-13 10:16 | 2022-01-13 12:44 | 6 | 002:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR TOMA | C22011200012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 148 | 2022-01-13 | 888 | keep | 0 | Jan | 2022 | 0.00060481 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-01-13 10:20 | 2022-01-13 13:20 | 5 | 003:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | M22011300027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 180 | 2022-01-13 | 900 | keep | 0 | Jan | 2022 | 0.00061299 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-01-13 10:28 | 2022-01-13 10:58 | 50 | 000:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22011300020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 30 | 2022-01-13 | 1500 | keep | 0 | Jan | 2022 | 0.0010216 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-01-13 10:31 | 2022-01-13 12:19 | 20 | 001:48 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22011300022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2022-01-13 | 2160 | keep | 0 | Jan | 2022 | 0.0014712 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2022-01-13 10:37 | 2022-01-14 13:36 | 10 | 026:59 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR QUEMADO DE 75 KVA X 75 KVA | R22011300012 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1619 | 2022-01-13 | 16190 | keep | 0 | Jan | 2022 | 0.011027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-13 10:39 | 2022-01-13 16:38 | 1 | 005:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | A22011300069 | New_Event | Wire Down | Include | Include | Equipment | 359 | 2022-01-13 | 359 | keep | 0 | Jan | 2022 | 0.00024451 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-01-13 10:41 | 2022-01-13 10:42 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22011300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-13 | 1310 | keep | 0 | Jan | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2022-01-13 10:50 | 2022-01-13 10:51 | 3 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO BKR PROVISIONAL #6 QUE LLEVA LAS CARGAS DEL 1707-02, 1707-03 Y 1707-05 | B22011300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-13 | 3 | keep | 0 | Jan | 2022 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-01-13 10:50 | 2022-01-13 10:51 | 61 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO BKR PROVISIONAL #6 QUE LLEVA LAS CARGAS DEL 1707-02, 1707-03 Y 1707-05 | B22011300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-13 | 61 | keep | 0 | Jan | 2022 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2022-01-13 10:50 | 2022-01-13 10:51 | 546 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO BKR PROVISIONAL #6 QUE LLEVA LAS CARGAS DEL 1707-02, 1707-03 Y 1707-05 | B22011300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-13 | 546 | keep | 0 | Jan | 2022 | 0.00037188 | 0.00037188 | Momentary | FALSE | FALSE | Not_TMED_Event | 546
GUAYAMA | 2022-01-13 10:50 | 2022-01-13 12:39 | 23 | 001:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22011300028 | New_Event |  |  | Include | Wildlife | 109 | 2022-01-13 | 2507 | keep | 0 | Jan | 2022 | 0.0017075 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
CANOVANAS | 2022-01-13 10:55 | 2022-01-13 14:35 | 85 | 003:40 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN CORTES DE LINEA | R22011300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2022-01-13 | 18700 | keep | 0 | Jan | 2022 | 0.012736 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
SAN JUAN | 2022-01-13 11:12 | 2022-01-13 14:55 | 50 | 003:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S22011300018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 223 | 2022-01-13 | 11150 | keep | 0 | Jan | 2022 | 0.0075942 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-13 11:25 | 2022-01-13 14:38 | 10 | 003:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA | B22011300022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 193 | 2022-01-13 | 1930 | keep | 0 | Jan | 2022 | 0.0013145 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-01-13 11:36 | 2022-01-13 12:17 | 7 | 000:41 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5 KVA A 2.4KV AVERIADO POR OTRO IGUAL CAPACIDAD Y VOLTAJE | P22011300024 | New_Event | Service Transformer Failure | Include | Include | Equipment | 41 | 2022-01-13 | 287 | keep | 0 | Jan | 2022 | 0.00019547 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2022-01-13 11:49 | 2022-01-13 14:42 | 20 | 002:53 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R22011300011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2022-01-13 | 3460 | keep | 0 | Jan | 2022 | 0.0023566 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-01-13 12:08 | 2022-01-13 13:23 | 35 | 001:15 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22011300031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2022-01-13 | 2625 | keep | 0 | Jan | 2022 | 0.0017879 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-01-13 12:48 | 2022-01-13 16:58 | 15 | 004:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22011300045 | New_Event | Bad Weather | Include | Include | Weather | 250 | 2022-01-13 | 3750 | keep | 0 | Jan | 2022 | 0.0025541 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2022-01-13 13:18 | 2022-01-13 16:35 | 12 | 003:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR CONEXIONES EN LINEA SECUNDARIA | P22011300030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 197 | 2022-01-13 | 2364 | keep | 0 | Jan | 2022 | 0.0016101 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-01-13 13:27 | 2022-01-13 15:32 | 1017 | 002:05 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO LINEAS PRIMARIAS ROTAS SE CERRO EL INTERRUPTOR | M22011300047 | New_Event | Wire Down | Include | Include | Equipment | 125 | 2022-01-13 | 127125 | keep | 0 | Jan | 2022 | 0.086584 | 0.00069267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1017
AGUADILLA | 2022-01-13 13:38 | 2022-01-13 15:31 | 175 | 001:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22011300115 | New_Event | Bad Weather | Include | Include | Weather | 113 | 2022-01-13 | 19775 | keep | 0 | Jan | 2022 | 0.013469 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
BAYAMON | 2022-01-13 13:43 | 2022-01-13 14:11 | 10 | 000:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | B22011300034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 28 | 2022-01-13 | 280 | keep | 0 | Jan | 2022 | 0.00019071 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-01-13 13:43 | 2022-01-13 16:29 | 40 | 002:46 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C22011300097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 166 | 2022-01-13 | 6640 | keep | 0 | Jan | 2022 | 0.0045225 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-01-13 13:47 | 2022-01-13 19:55 | 40 | 006:08 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R22011300016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 368 | 2022-01-13 | 14720 | keep | 0 | Jan | 2022 | 0.010026 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-01-13 13:51 | 2022-01-13 13:56 | 2735 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO 9501-03 LLEVANDO LA CARGA DEL 9501-02. SE VERIFICO PERSONAL FUERA EN ORDEN 514 | B22011300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-01-13 | 13675 | keep | 0 | Jan | 2022 | 0.009314 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2022-01-13 13:51 | 2022-01-13 13:56 | 1070 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO 9501-03 LLEVANDO LA CARGA DEL 9501-02 | B22011300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-01-13 | 5350 | keep | 0 | Jan | 2022 | 0.0036439 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
CANOVANAS | 2022-01-13 14:01 | 2022-01-13 15:11 | 18 | 001:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X30 EN CORTE DE LINEA Y SE RETIRO AVE DE LA LINEA | R22011300020 | New_Event |  |  | Include | Wildlife | 70 | 2022-01-13 | 1260 | keep | 0 | Jan | 2022 | 0.00085818 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
VEGA BAJA | 2022-01-13 14:09 | 2022-01-13 16:53 | 35 | 002:44 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22011300039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 164 | 2022-01-13 | 5740 | keep | 0 | Jan | 2022 | 0.0039095 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2022-01-13 14:23 | 2022-01-13 15:20 | 6 | 000:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A22011300021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 57 | 2022-01-13 | 342 | keep | 0 | Jan | 2022 | 0.00023293 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-01-13 14:24 | 2022-01-13 17:17 | 50 | 002:53 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22011300023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2022-01-13 | 8650 | keep | 0 | Jan | 2022 | 0.0058915 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-01-13 14:25 | 2022-01-13 17:38 | 125 | 003:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22011300063 | New_Event | Bad Weather | Include | Include | Weather | 193 | 2022-01-13 | 24125 | keep | 0 | Jan | 2022 | 0.016431 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
CANOVANAS | 2022-01-13 14:26 | 2022-01-13 15:33 | 15 | 001:07 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R22011300024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 67 | 2022-01-13 | 1005 | keep | 0 | Jan | 2022 | 0.0006845 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2022-01-13 14:31 | 2022-01-13 15:00 | 1 | 000:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO DE TRES CAJAS PRIMARIAS EN RAISER | P22011300033 | New_Event | Cutout Failure | Include | Include | Equipment | 29 | 2022-01-13 | 29 | keep | 0 | Jan | 2022 | 1.9752e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-01-13 15:00 | 2022-01-13 19:34 | 30 | 004:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE LEVANTO NEUTRAL PRIMARIO Y SE REALIZO DESGANCHE | B22011300043 | New_Event | Wire Down | Include | Include | Equipment | 274 | 2022-01-13 | 8220 | keep | 0 | Jan | 2022 | 0.0055986 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-01-13 15:21 | 2022-01-13 15:31 | 10 | 000:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | B22011300026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 10 | 2022-01-13 | 100 | keep | 0 | Jan | 2022 | 6.811e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-13 15:23 | 2022-01-13 16:17 | 10 | 000:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA Y BAJANTE SECUNDARIO | B22011300031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 54 | 2022-01-13 | 540 | keep | 0 | Jan | 2022 | 0.00036779 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-01-13 15:28 | 2022-01-13 18:01 | 40 | 002:33 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22011300077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2022-01-13 | 6120 | keep | 0 | Jan | 2022 | 0.0041683 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-01-13 15:32 | 2022-01-13 20:00 | 450 | 004:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y SE RETIRO RAMAS SOBRE LAS LINEAS | M22011300125 | Partial_restoration | Wire Down | Include | Include | Equipment | 268 | 2022-01-13 | 120600 | keep | 0 | Jan | 2022 | 0.08214 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-13 15:40 | 2022-01-13 15:41 | 464 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DEBIDO A PAJARO QUE CRUZO FASE | P220113000XX | New_Event |  |  | Include | Wildlife | 1 | 2022-01-13 | 464 | keep | 0 | Jan | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
MAYAGÃœEZ | 2022-01-13 15:40 | 2022-01-13 19:56 | 50 | 004:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA INDICA JOURNEYMAN REQUIERE DESGANCHE | M22011300087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 256 | 2022-01-13 | 12800 | keep | 0 | Jan | 2022 | 0.008718 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-01-13 15:41 | 2022-01-13 17:24 | 45 | 001:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA PAJARO CRUZO FASE | P22011300061 | 1st_after_momentary |  |  | Include | Wildlife | 103 | 2022-01-13 | 4635 | keep | 0 | Jan | 2022 | 0.0031569 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-01-13 15:46 | 2022-01-13 15:56 | 3 | 000:10 | T | NO SE REPORTO CAUSA | DISPARO BKR PROVISIONAL #6 LLEVANDO CARGA 1707-03 1707-04 1707-05 | B22011300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2022-01-13 | 30 | keep | 0 | Jan | 2022 | 2.0433e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-01-13 15:46 | 2022-01-13 15:56 | 61 | 000:10 | T | NO SE REPORTO CAUSA | DISPARO BKR PROVISIONAL #6 LLEVANDO CARGA 1707-03 1707-04 1707-05 | B22011300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2022-01-13 | 610 | keep | 0 | Jan | 2022 | 0.00041547 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2022-01-13 15:46 | 2022-01-13 15:56 | 1501 | 000:10 | T | NO SE REPORTO CAUSA | DISPARO BKR PROVISIONAL #6 LLEVANDO CARGA 1707-03 1707-04 1707-05 | B22011300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2022-01-13 | 15010 | keep | 0 | Jan | 2022 | 0.010223 | 0.0010223 | Sustained | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2022-01-13 15:46 | 2022-01-13 15:56 | 546 | 000:10 | T | NO SE REPORTO CAUSA | DISPARO BKR PROVISIONAL #6 LLEVANDO CARGA 1707-03 1707-04 1707-05 | B22011300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2022-01-13 | 5460 | keep | 0 | Jan | 2022 | 0.0037188 | 0.00037188 | Sustained | FALSE | FALSE | Not_TMED_Event | 546
CANOVANAS | 2022-01-13 15:46 | 2022-01-13 16:09 | 15 | 000:23 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | R22011300063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 23 | 2022-01-13 | 345 | keep | 0 | Jan | 2022 | 0.00023498 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-01-13 15:48 | 2022-01-13 16:04 | 1 | 000:16 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22011300092 | New_Event | Bad Weather | Include | Include | Weather | 16 | 2022-01-13 | 16 | keep | 0 | Jan | 2022 | 1.0898e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-01-13 15:53 | 2022-01-13 17:54 | 10 | 002:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | B22011300026 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 121 | 2022-01-13 | 1210 | keep | 0 | Jan | 2022 | 0.00082413 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-01-13 15:56 | 2022-01-13 17:35 | 20 | 001:39 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B22011300065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2022-01-13 | 1980 | keep | 0 | Jan | 2022 | 0.0013486 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-01-13 16:10 | 2022-01-13 17:43 | 100 | 001:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN RISER SE REMPLAZO CAJA | S22011300093 | New_Event | Cutout Failure | Include | Include | Equipment | 93 | 2022-01-13 | 9300 | keep | 0 | Jan | 2022 | 0.0063342 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-01-13 16:15 | 2022-01-13 19:30 | 2039 | 003:15 | T | DESCONECTIVO DEFECTUOSO | MACHETE DE BARRA DEL ALIMENTADOR 2402-03 QUEMADO SE TRANSFIRIO CARAGA AL 2402-03 POR B.I. | R22011300000 | New_Event | Switch Failure | Include | Include | Equipment | 195 | 2022-01-13 | 397605 | keep | 0 | Jan | 2022 | 0.27081 | 0.0013888 | Sustained | FALSE | FALSE | Not_TMED_Event | 2039
CANOVANAS | 2022-01-13 16:15 | 2022-01-13 18:43 | 4188 | 002:28 | T | DESCONECTIVO DEFECTUOSO | MACHETE DE BARRA DEL ALIMENTADOR 2402-03 QUEMADO 25% EN SERVICIO A TRAVES DEL 2302-01 | R22011300000 | New_Event | Switch Failure | Include | Include | Equipment | 148 | 2022-01-13 | 619824 | keep | 0 | Jan | 2022 | 0.42216 | 0.0028524 | Sustained | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2022-01-13 16:15 | 2022-01-13 18:00 | 4085 | 001:45 | T | DESCONECTIVO DEFECTUOSO | MACHETE DE BARRA DEL ALIMENTADOR 2402-03 QUEMADO SE TRANSFIRIO 50% DE LA CARGA AL 1646-02 | R22011300000 | New_Event | Switch Failure | Include | Include | Equipment | 105 | 2022-01-13 | 428925 | keep | 0 | Jan | 2022 | 0.29214 | 0.0027823 | Sustained | FALSE | FALSE | Not_TMED_Event | 4085
GUAYAMA | 2022-01-13 16:25 | 2022-01-13 21:20 | 15 | 004:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA AJUSTAR CONEXIONES EN PEDESTAL | P22011300018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 295 | 2022-01-13 | 4425 | keep | 0 | Jan | 2022 | 0.0030138 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-01-13 16:40 | 2022-01-13 16:42 | 959 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22011300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-13 | 1918 | keep | 0 | Jan | 2022 | 0.0013063 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
ARECIBO | 2022-01-13 16:40 | 2022-01-13 18:55 | 2 | 002:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 20 EN TRANSFORMADOR SE REMPLAZO AISLADOR ROTO Y SE REMPLAZO PORTAFUSIBLES | A22011300077 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 135 | 2022-01-13 | 270 | keep | 0 | Jan | 2022 | 0.0001839 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-01-13 16:40 | 2022-01-13 19:14 | 100 | 002:34 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22011300078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2022-01-13 | 15400 | keep | 0 | Jan | 2022 | 0.010489 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-01-13 16:59 | 2022-01-13 17:00 | 3438 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | B22011300000 | New_Event |  |  | Include | Wildlife | 1 | 2022-01-13 | 3438 | keep | 0 | Jan | 2022 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
BAYAMON | 2022-01-13 17:00 | 2022-01-13 18:55 | 20 | 001:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA SE RETIRO AVE CRUZANDO LINEAS | B22011300138 | 1st_after_momentary |  |  | Include | Wildlife | 115 | 2022-01-13 | 2300 | keep | 0 | Jan | 2022 | 0.0015665 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-01-13 17:01 | 2022-01-13 20:30 | 500 | 003:29 | P | NO SE REPORTO CAUSA | SE CERRO AMARRE ENTRE 1708-02 Y 1708-03 CALLE DAKKAR SECCIONALIZANDO ALIMENTADOR 1708-02 | B22011300100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 209 | 2022-01-13 | 104500 | keep | 0 | Jan | 2022 | 0.071174 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2022-01-13 17:01 | 2022-01-13 18:03 | 1498 | 001:02 | T | NO SE REPORTO CAUSA | SE CERRO INTERRUPTOR 1708-03 ABRIENDO AMARRE CON 1708-02 | B22011300100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 62 | 2022-01-13 | 92876 | keep | 0 | Jan | 2022 | 0.063257 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
HUMACAO | 2022-01-13 17:01 | 2022-01-13 18:08 | 89 | 001:07 | P | DESGANCHE | 1 X 100 EN C/L | C22011300297 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2022-01-13 | 5963 | keep | 0 | Jan | 2022 | 0.0040614 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
SAN JUAN | 2022-01-13 17:03 | 2022-01-13 18:41 | 10 | 001:38 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S22011300128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 98 | 2022-01-13 | 980 | keep | 0 | Jan | 2022 | 0.00066747 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-01-13 17:05 | 2022-01-13 19:55 | 9 | 002:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BARRAS SOTERRADAS AVERIADAS | M22011300116 | New_Event | Secondary Wire Down | Include | Include | Equipment | 170 | 2022-01-13 | 1530 | keep | 0 | Jan | 2022 | 0.0010421 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2022-01-13 17:07 | 2022-01-13 20:30 | 40 | 003:23 | P | DESGANCHE | 1 X 40 EN C/L | C22011300304 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2022-01-13 | 8120 | keep | 0 | Jan | 2022 | 0.0055305 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-01-13 17:31 | 2022-01-13 18:39 | 30 | 001:08 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22011300125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 68 | 2022-01-13 | 2040 | keep | 0 | Jan | 2022 | 0.0013894 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-01-13 17:36 | 2022-01-14 16:47 | 200 | 023:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO Y SE REALIZO DESGANCHE | M22011300125 | New_Event | Wire Down | Include | Include | Equipment | 1391 | 2022-01-13 | 278200 | keep | 0 | Jan | 2022 | 0.18948 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-01-13 17:43 | 2022-01-13 17:44 | 350 | 000:01 | P | DESGANCHE | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO 60% POR 1346-02 | S22011300135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-13 | 350 | keep | 0 | Jan | 2022 | 0.00023838 | 0.00023838 | Momentary | FALSE | FALSE | Not_TMED_Event | 350
FAJARDO | 2022-01-13 17:44 | 2022-01-13 20:00 | 60 | 002:16 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22011300167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2022-01-13 | 8160 | keep | 0 | Jan | 2022 | 0.0055577 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-01-13 17:47 | 2022-01-13 17:48 | 350 | 000:01 | P | DESGANCHE | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO 60% POR 1346-02 | S22011300135 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-13 | 350 | keep | 0 | Jan | 2022 | 0.00023838 | 0.00023838 | Momentary | FALSE | FALSE | Not_TMED_Event | 350
SAN JUAN | 2022-01-13 17:50 | 2022-01-13 18:44 | 350 | 000:54 | P | DESGANCHE | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO SE RETIRO RAMA SOBRE LINEA 60% POR 1346-02 | S22011300135 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 54 | 2022-01-13 | 18900 | keep | 0 | Jan | 2022 | 0.012873 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
CAGUAS | 2022-01-13 17:59 | 2022-01-13 18:29 | 89 | 000:30 | P | AISLADOR ROTO, PARTIDO O SAFADO | ABRIO C/L PARA REMPLAZAR AISLADOR PARTIDO | C22011300326 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 30 | 2022-01-13 | 2670 | keep | 0 | Jan | 2022 | 0.0018185 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
CANOVANAS | 2022-01-13 18:00 | 2022-01-13 18:09 | 2040 | 000:09 | P | DESCONECTIVO DEFECTUOSO | MACHETE DE BARRA DEL ALIMENTADOR 2402-03 QUEMADO SE TRANSFIRIO 50% DE LA CARGA AL 2404-07 | R22011300000 | Partial_restoration | Switch Failure | Include | Include | Equipment | 9 | 2022-01-13 | 18360 | keep | 0 | Jan | 2022 | 0.012505 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-01-13 18:08 | 2022-01-14 16:15 | 75 | 022:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA SE CERRO CORTE DE LINEA | A22011300089 | New_Event | Wire Down | Include | Include | Equipment | 1327 | 2022-01-13 | 99525 | keep | 0 | Jan | 2022 | 0.067786 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-01-13 18:14 | 2022-01-13 23:26 | 6 | 005:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22011300157 | New_Event | Secondary Wire Down | Include | Include | Equipment | 312 | 2022-01-13 | 1872 | keep | 0 | Jan | 2022 | 0.001275 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-01-13 18:24 | 2022-01-13 22:19 | 30 | 003:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REMPLAZO CAJA PRIMARIA | B22011300162 | New_Event | Cutout Failure | Include | Include | Equipment | 235 | 2022-01-13 | 7050 | keep | 0 | Jan | 2022 | 0.0048017 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-01-13 18:30 | 2022-01-13 19:26 | 12 | 000:56 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE TRANSFORMADOR DE 75 KVA A 2400VOLTS POR OTRO IGUAL CAPACIDAD Y VOLTAJE | P22011300133 | New_Event | Service Transformer Failure | Include | Include | Equipment | 56 | 2022-01-13 | 672 | keep | 0 | Jan | 2022 | 0.0004577 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-01-13 18:43 | 2022-01-13 19:10 | 1050 | 000:27 | P | DESCONECTIVO DEFECTUOSO | MACHETE DE BARRA DEL ALIMENTADOR 2402-03 QUEMADO 25% ADICIONAL EN SERVICIO A TRAVES DEL 2404-05 | R22011300000 | Partial_restoration | Switch Failure | Include | Include | Equipment | 27 | 2022-01-13 | 28350 | keep | 0 | Jan | 2022 | 0.019309 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-01-13 18:43 | 2022-01-13 19:00 | 2100 | 000:17 | P | DESCONECTIVO DEFECTUOSO | MACHETE DE BARRA DEL ALIMENTADOR 2402-03 QUEMADO 50% ADICIONAL EN SERVICIO A TRAVES DEL 2404-05 | R22011300000 | New_Event | Switch Failure | Include | Include | Equipment | 17 | 2022-01-13 | 35700 | keep | 0 | Jan | 2022 | 0.024315 | 0.0014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-01-13 18:44 | 2022-01-13 20:30 | 195 | 001:46 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P22011300124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2022-01-13 | 20670 | keep | 0 | Jan | 2022 | 0.014078 | 0.00013281 | Sustained | FALSE | FALSE | Not_TMED_Event | 195
BAYAMON | 2022-01-13 18:51 | 2022-01-14 15:58 | 70 | 021:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 50 EN C/L Y 2 X 15 EN XMR. SE REPARO BAJANTE SECUNDARIO | S22011300174 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1267 | 2022-01-13 | 88690 | keep | 0 | Jan | 2022 | 0.060406 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-01-13 19:02 | 2022-01-13 19:03 | 350 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO QUEDO EN SERVICIO 60% POR 1346-02 | S22011300135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-13 | 350 | keep | 0 | Jan | 2022 | 0.00023838 | 0.00023838 | Momentary | FALSE | FALSE | Not_TMED_Event | 350
ARECIBO | 2022-01-13 19:06 | 2022-01-13 20:50 | 15 | 001:44 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA FOREMAN INDICA SECTOR REQUIERE DESGANCHE | A22011300097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2022-01-13 | 1560 | keep | 0 | Jan | 2022 | 0.0010625 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-01-13 19:29 | 2022-01-14 00:51 | 36 | 005:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y SE REMPLAZO CAJA PRIMARIA | S22011300099 | New_Event | Wire Down | Include | Include | Equipment | 322 | 2022-01-13 | 11592 | keep | 0 | Jan | 2022 | 0.0078953 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-01-13 19:35 | 2022-01-13 20:44 | 60 | 001:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | HACIENDO PRUEBA EN C/L DISPARO INTERRUPTOR EVENTUALMENTE SE SECCIONALIZO | S22011300147 | New_Event | Wire Down | Include | Include | Equipment | 69 | 2022-01-13 | 4140 | keep | 0 | Jan | 2022 | 0.0028197 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-01-13 19:59 | 2022-01-13 20:00 | 476 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C2201130014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-13 | 476 | keep | 0 | Jan | 2022 | 0.0003242 | 0.0003242 | Momentary | FALSE | FALSE | Not_TMED_Event | 476
CAGUAS | 2022-01-13 19:59 | 2022-01-13 20:00 | 1655 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C2201130014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-13 | 1655 | keep | 0 | Jan | 2022 | 0.0011272 | 0.0011272 | Momentary | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2022-01-13 19:59 | 2022-01-13 20:00 | 361 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C2201130014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-13 | 361 | keep | 0 | Jan | 2022 | 0.00024588 | 0.00024588 | Momentary | FALSE | FALSE | Not_TMED_Event | 361
CAGUAS | 2022-01-13 19:59 | 2022-01-13 20:00 | 2842 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C2201130014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-13 | 2842 | keep | 0 | Jan | 2022 | 0.0019357 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
CAGUAS | 2022-01-13 19:59 | 2022-01-13 20:00 | 1702 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C2201130014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-13 | 1702 | keep | 0 | Jan | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2022-01-13 19:59 | 2022-01-13 20:00 | 918 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C2201130014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-13 | 918 | keep | 0 | Jan | 2022 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2022-01-13 20:13 | 2022-01-13 20:15 | 476 | 000:02 | S | DESGANCHE | DISPARO LINEA 3000 | C22011300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-01-13 | 952 | keep | 0 | Jan | 2022 | 0.0006484 | 0.0003242 | Momentary | FALSE | FALSE | Not_TMED_Event | 476
CAGUAS | 2022-01-13 20:13 | 2022-01-13 20:15 | 1655 | 000:02 | S | DESGANCHE | DISPARO LINEA 3000 | C22011300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-01-13 | 3310 | keep | 0 | Jan | 2022 | 0.0022544 | 0.0011272 | Momentary | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2022-01-13 20:13 | 2022-01-13 20:15 | 361 | 000:02 | S | DESGANCHE | DISPARO LINEA 3000 | C22011300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-01-13 | 722 | keep | 0 | Jan | 2022 | 0.00049175 | 0.00024588 | Momentary | FALSE | FALSE | Not_TMED_Event | 361
CAGUAS | 2022-01-13 20:13 | 2022-01-13 20:15 | 2842 | 000:02 | S | DESGANCHE | DISPARO LINEA 3000 | C22011300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-01-13 | 5684 | keep | 0 | Jan | 2022 | 0.0038713 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
CAGUAS | 2022-01-13 20:13 | 2022-01-13 20:15 | 1702 | 000:02 | S | DESGANCHE | DISPARO LINEA 3000 | C22011300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-01-13 | 3404 | keep | 0 | Jan | 2022 | 0.0023184 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2022-01-13 20:13 | 2022-01-13 20:15 | 918 | 000:02 | S | DESGANCHE | DISPARO LINEA 3000 | C22011300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-01-13 | 1836 | keep | 0 | Jan | 2022 | 0.0012505 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
BAYAMON | 2022-01-13 20:30 | 2022-01-13 21:17 | 500 | 000:47 | P | NO SE REPORTO CAUSA | SE CERRO MACHETES EN CALLE 26 ABRIENDO MACHETES EN OTRO PUNTO | B22011300100 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 47 | 2022-01-13 | 23500 | keep | 0 | Jan | 2022 | 0.016006 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-13 20:44 | 2022-01-13 21:22 | 1844 | 000:38 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO AL REPONER FUSIBLE EN RISER CARGA DEL 60% 1346-3 SE ENCONTRO LINEA PRIMARIA EN EL PISO SE ABRIO MACHETE PARA SECCIONALIZAR 100% 1346-2 Y 30% EN SERVICIO 1346-3 | S22011300156 | New_Event | Wire Down | Include | Include | Equipment | 38 | 2022-01-13 | 70072 | keep | 0 | Jan | 2022 | 0.047726 | 0.0012559 | Sustained | FALSE | FALSE | Not_TMED_Event | 1844
SAN JUAN | 2022-01-13 20:44 | 2022-01-13 21:22 | 1452 | 000:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO AL REPONER FUSIBLE EN RISER CARGA DEL 60% 1346-3 SE ENCONTRO LINEA PRIMARIA EN EL PISO SE ABRIO MACHETE PARA SECCIONALIZAR 100% 1346-2 Y 30% EN SERVICIO 1346-3 | S22011300156 | Additional_clients | Wire Down | Include | Include | Equipment | 38 | 2022-01-13 | 55176 | keep | 0 | Jan | 2022 | 0.03758 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-01-13 20:47 | 2022-01-13 21:37 | 5 | 000:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | M22011300149 | New_Event | Secondary Wire Down | Include | Include | Equipment | 50 | 2022-01-13 | 250 | keep | 0 | Jan | 2022 | 0.00017027 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2022-01-13 21:05 | 2022-01-13 23:01 | 20 | 001:56 | P | DESGANCHE | 1 X 30 EN C/L SE RETIRO RAMA | B22011300182 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2022-01-13 | 2320 | keep | 0 | Jan | 2022 | 0.0015801 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-01-13 21:17 | 2022-01-13 21:21 | 500 | 000:04 | P | NO SE REPORTO CAUSA | SE CERRO MACHETES HASTA N/O NO SE ENCONTRO CAUSA | B22011300100 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-01-13 | 2000 | keep | 0 | Jan | 2022 | 0.0013622 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-13 21:22 | 2022-01-13 22:19 | 726 | 000:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y SE NORMALIZO LAS CARGAS ENTRO EL 30% RESTANTE | S22011300147 | Partial_restoration | Wire Down | Include | Include | Equipment | 57 | 2022-01-13 | 41382 | keep | 0 | Jan | 2022 | 0.028185 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-01-13 21:22 | 2022-01-14 09:32 | 13 | 012:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR CHANGO | C22011300337 | New_Event |  |  | Include | Wildlife | 730 | 2022-01-13 | 9490 | keep | 0 | Jan | 2022 | 0.0064636 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2022-01-13 22:04 | 2022-01-14 13:56 | 80 | 015:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22011300154 | New_Event | Cutout Failure | Include | Include | Equipment | 952 | 2022-01-13 | 76160 | keep | 0 | Jan | 2022 | 0.051872 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-01-13 22:41 | 2022-01-14 09:42 | 25 | 011:01 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN C/L Y SE REEMPLAZO PARRARAYO | B22011300217 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 661 | 2022-01-13 | 16525 | keep | 0 | Jan | 2022 | 0.011255 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-01-13 23:41 | 2022-01-14 21:59 | 30 | 022:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 Y 1 X 40 EN CORTE DE LINEAS SE RETIRO AVE | C22011400364 | New_Event |  |  | Include | Wildlife | 1338 | 2022-01-13 | 40140 | keep | 0 | Jan | 2022 | 0.027339 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-01-14 00:06 | 2022-01-14 02:29 | 1 | 002:23 | P | NO SE REPORTO CAUSA | 1 X 25 EN SU NO IDENTIFICADO | R22011400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 143 | 2022-01-14 | 143 | keep | 0 | Jan | 2022 | 9.7397e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-01-14 00:27 | 2022-01-14 00:28 | 1089 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22011400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-14 | 1089 | keep | 0 | Jan | 2022 | 0.00074171 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
SAN JUAN | 2022-01-14 02:29 | 2022-01-14 02:30 | 163 | 000:01 | P | OTRAS CAUSAS | DISPARO 1620-04 Y SE CERRO POR SCADA LLEVA 1620-01 Y 95% DEL 1336-10 | S22011400000 | New_Event | Other Causes | Include | Include | Other | 1 | 2022-01-14 | 163 | keep | 0 | Jan | 2022 | 0.00011102 | 0.00011102 | Momentary | FALSE | FALSE | Not_TMED_Event | 163
SAN JUAN | 2022-01-14 02:29 | 2022-01-14 02:30 | 36 | 000:01 | T | OTRAS CAUSAS | DISPARO 1620-04 Y SE CERRO POR SCADA LLEVA 1620-01 | S22011400000 | New_Event | Other Causes | Include | Include | Other | 1 | 2022-01-14 | 36 | keep | 0 | Jan | 2022 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-01-14 02:29 | 2022-01-14 02:30 | 172 | 000:01 | T | OTRAS CAUSAS | DISPARO 1620-04 Y SE CERRO POR SCADA LLEVA 1620-01 Y 95% DEL 1336-10 | S22011400000 | New_Event | Other Causes | Include | Include | Other | 1 | 2022-01-14 | 172 | keep | 0 | Jan | 2022 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2022-01-14 02:30 | 2022-01-14 09:38 | 1 | 007:08 | P | NO SE REPORTO CAUSA | 1 X 25 EN SU NO IDENTIFICADO | R22011400001 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 428 | 2022-01-14 | 428 | keep | 0 | Jan | 2022 | 0.00029151 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-14 02:30 | 2022-01-14 09:38 | 1 | 007:08 | P | OTRAS CAUSAS | 2X65 EN RISER POR PROBLEMA DEL CLIENTE (PROA) | S22011400001 | 1st_after_momentary | Other Causes | Include | Include | Other | 428 | 2022-01-14 | 428 | keep | 0 | Jan | 2022 | 0.00029151 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-01-14 02:53 | 2022-01-14 09:29 | 80 | 006:36 | P | DESGANCHE | 1 X65 EN CORTE DE LINEA DESGANCHE | B22011400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 396 | 2022-01-14 | 31680 | keep | 0 | Jan | 2022 | 0.021577 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-01-14 02:56 | 2022-01-14 02:57 | 922 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1401-08 SE CERRO POR SCADA LLEVA 1346-05 | S22011400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-14 | 922 | keep | 0 | Jan | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-01-14 02:56 | 2022-01-14 02:57 | 135 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1401-08 SE CERRO POR SCADA LLEVA 1346-05 | S22011400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-14 | 135 | keep | 0 | Jan | 2022 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
UTUADO | 2022-01-14 03:59 | 2022-01-14 13:23 | 150 | 009:24 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO ARBOL DE SOBRE LAS LINEAS | A22011400001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 564 | 2022-01-14 | 84600 | keep | 0 | Jan | 2022 | 0.057621 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-01-14 04:16 | 2022-01-14 12:05 | 60 | 007:49 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22011400014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 469 | 2022-01-14 | 28140 | keep | 0 | Jan | 2022 | 0.019166 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-01-14 05:15 | 2022-01-14 11:07 | 88 | 005:52 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22011400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 352 | 2022-01-14 | 30976 | keep | 0 | Jan | 2022 | 0.021098 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
BAYAMON | 2022-01-14 06:38 | 2022-01-14 10:16 | 25 | 003:38 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN RISER AVERIA NUEVA DE T-13 A T-12. SE QUEDO EL T-12 FUERA DE SERVICIO | B22011400002 | New_Event | UG Cable Fault | Include | Include | Equipment | 218 | 2022-01-14 | 5450 | keep | 0 | Jan | 2022 | 0.003712 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-01-14 06:54 | 2022-01-14 10:00 | 22 | 003:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE X AVE | R22011400002 | New_Event |  |  | Include | Wildlife | 186 | 2022-01-14 | 4092 | keep | 0 | Jan | 2022 | 0.002787 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
CAGUAS | 2022-01-14 07:01 | 2022-01-14 07:02 | 2608 | 000:01 | T | LINEA DE TRANSMISION 115KV | RECERRO INTERRUPTOR EN SERVICIO | C22011400000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-01-14 | 2608 | keep | 0 | Jan | 2022 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
CAGUAS | 2022-01-14 07:02 | 2022-01-14 18:57 | 70 | 011:55 | P | LINEA DE TRANSMISION 115KV | CONDUCTOR DE LINEA TRANSMISION 39000 CAYO SOBRE LINEA PRIMARIA | C22011400028 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 715 | 2022-01-14 | 50050 | keep | 0 | Jan | 2022 | 0.034089 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
UTUADO | 2022-01-14 07:12 | 2022-01-14 10:53 | 25 | 003:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A22011400008 | New_Event | Wire Down | Include | Include | Equipment | 221 | 2022-01-14 | 5525 | keep | 0 | Jan | 2022 | 0.0037631 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-01-14 07:17 | 2022-01-14 07:18 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-03 LLEVA TRANSFERIDA LA CARGA DEL 1204-05 | S22011400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-14 | 10211 | keep | 0 | Jan | 2022 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2022-01-14 07:17 | 2022-01-14 07:18 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 1204-05 | S22010140000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-14 | 4133 | keep | 0 | Jan | 2022 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
BAYAMON | 2022-01-14 07:26 | 2022-01-14 11:10 | 6 | 003:44 | P | NO SE REPORTO CAUSA | 1 X 12 EN PROVISIONAL AEREO | B22011400010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 224 | 2022-01-14 | 1344 | keep | 0 | Jan | 2022 | 0.00091539 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-01-14 07:40 | 2022-01-14 08:52 | 92 | 001:12 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REEMPLAZO DE POSTE PRIMARIO PODRIDO Y SE VOLVIO A CERRAR PARA PASAR A TRABAJAR CON EL EVENTO C22011400024 | C22011400004 | New_Event | Defective Pole | Include | Include | Equipment | 72 | 2022-01-14 | 6624 | keep | 0 | Jan | 2022 | 0.0045116 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
GUAYAMA | 2022-01-14 07:42 | 2022-01-14 09:57 | 30 | 002:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22011400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2022-01-14 | 4050 | keep | 0 | Jan | 2022 | 0.0027584 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-01-14 07:43 | 2022-01-14 15:15 | 300 | 007:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22011400020 | New_Event | Wire Down | Include | Include | Equipment | 452 | 2022-01-14 | 135600 | keep | 0 | Jan | 2022 | 0.092357 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-01-14 07:44 | 2022-01-14 17:50 | 50 | 010:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22011400021 | New_Event | Bad Weather | Include | Include | Weather | 606 | 2022-01-14 | 30300 | keep | 0 | Jan | 2022 | 0.020637 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-01-14 07:51 | 2022-01-14 10:33 | 32 | 002:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1X65 EN CORTE DE LINEA (POR AVE EN LA LINEA) | S22011400007 | New_Event |  |  | Include | Wildlife | 162 | 2022-01-14 | 5184 | keep | 0 | Jan | 2022 | 0.0035308 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
UTUADO | 2022-01-14 08:01 | 2022-01-14 12:24 | 45 | 004:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22011400011 | New_Event | Bad Weather | Include | Include | Weather | 263 | 2022-01-14 | 11835 | keep | 0 | Jan | 2022 | 0.0080608 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2022-01-14 08:02 | 2022-01-14 08:16 | 1105 | 000:14 | T | ERROR HUMANO | PERSONAL DESGANCHANDO DISPARO INTERRUPTOR | A22011400012 | New_Event | Human Error | Include | Include | Other | 14 | 2022-01-14 | 15470 | keep | 0 | Jan | 2022 | 0.010537 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
SAN JUAN | 2022-01-14 08:04 | 2022-01-14 10:44 | 50 | 002:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X100 EN CORTE DE LINEA Y SE REMPLAZO CAJA PRIMARIA | S22011400010 | New_Event | Cutout Failure | Include | Include | Equipment | 160 | 2022-01-14 | 8000 | keep | 0 | Jan | 2022 | 0.0054488 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-01-14 08:16 | 2022-01-14 13:04 | 150 | 004:48 | P | ERROR HUMANO | 1 X 80 EN CORTE DE LINEA PERSONAL DESGANCHANDO | A22011400038 | Partial_restoration | Human Error | Include | Include | Other | 288 | 2022-01-14 | 43200 | keep | 0 | Jan | 2022 | 0.029423 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-01-14 08:23 | 2022-01-14 12:34 | 60 | 004:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | A22011400015 | New_Event | Wire Down | Include | Include | Equipment | 251 | 2022-01-14 | 15060 | keep | 0 | Jan | 2022 | 0.010257 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-01-14 08:29 | 2022-01-14 12:16 | 35 | 003:47 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22011400023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 227 | 2022-01-14 | 7945 | keep | 0 | Jan | 2022 | 0.0054113 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-01-14 08:52 | 2022-01-14 09:18 | 4390 | 000:26 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO INTERRUPTOR CAMION IMPACTO LINEAS Y PARTIO POSTE PRIMARIO DEL TRONCAL SE SECCIONALIZO | C22011400020 | New_Event |  |  | Include | Wildlife | 26 | 2022-01-14 | 114140 | keep | 0 | Jan | 2022 | 0.07774 | 0.00299 | Sustained | FALSE | FALSE | Not_TMED_Event | 4390
SAN JUAN | 2022-01-14 08:53 | 2022-01-14 10:37 | 40 | 001:44 | P | DESGANCHE | 1X80 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22011400016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2022-01-14 | 4160 | keep | 0 | Jan | 2022 | 0.0028334 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-01-14 09:02 | 2022-01-14 17:04 | 15 | 008:02 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR 37 . 5 KVA A 4160 VOLTS POR OTRO DE LA MISMA CAPACIDAD | P22011400004 | New_Event | Service Transformer Failure | Include | Include | Equipment | 482 | 2022-01-14 | 7230 | keep | 0 | Jan | 2022 | 0.0049243 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-01-14 09:02 | 2022-01-14 12:47 | 5 | 003:45 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUE NO REGULABA DE 25KVA A 4KV POR OTRO IGUAL CAPACIDAD | P22011400005 | New_Event | Service Transformer Failure | Include | Include | Equipment | 225 | 2022-01-14 | 1125 | keep | 0 | Jan | 2022 | 0.00076623 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-01-14 09:03 | 2022-01-14 09:04 | 767 | 000:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE 50% POR EL 1909-07 Y LLEVA EL 1709-05 | S22011400000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-01-14 | 767 | keep | 0 | Jan | 2022 | 0.0005224 | 0.0005224 | Momentary | FALSE | FALSE | Not_TMED_Event | 767
BAYAMON | 2022-01-14 09:03 | 2022-01-14 09:04 | 2364 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE 1709-03 Y LLEVA LA CARGA DEL 1709-05 | S22011400000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-01-14 | 2364 | keep | 0 | Jan | 2022 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
BAYAMON | 2022-01-14 09:04 | 2022-01-14 11:48 | 40 | 002:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN RISER SE REEMPLAZO CAJA PRIMARIA Y SE CERRO PUENTE PRIMARIO | B22011400017 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 164 | 2022-01-14 | 6560 | keep | 0 | Jan | 2022 | 0.004468 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-01-14 09:12 | 2022-01-14 15:25 | 120 | 006:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22011400039 | New_Event | Wire Down | Include | Include | Equipment | 373 | 2022-01-14 | 44760 | keep | 0 | Jan | 2022 | 0.030486 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CAGUAS | 2022-01-14 09:18 | 2022-01-14 17:08 | 2150 | 007:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REEMPLAZO POSTE PRIMARIO PARTIDO POR VEHICULO | C22011400020 | Partial_restoration |  |  | Include | Wildlife | 470 | 2022-01-14 | 1010500 | keep | 0 | Jan | 2022 | 0.68825 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-14 09:38 | 2022-01-14 09:41 | 383 | 000:03 | P | OTRAS CAUSAS | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA 1620-01 Y 95% DEL 1336-10 | S22011400000 | New_Event | Other Causes | Include | Include | Other | 3 | 2022-01-14 | 1149 | keep | 0 | Jan | 2022 | 0.00078258 | 0.00026086 | Momentary | FALSE | FALSE | Not_TMED_Event | 383
SAN JUAN | 2022-01-14 09:38 | 2022-01-14 09:41 | 36 | 000:03 | T | OTRAS CAUSAS | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA 1620-01 Y 95% DEL 1336-10 | S22011400000 | Additional_clients | Other Causes | Include | Include | Other | 3 | 2022-01-14 | 108 | keep | 0 | Jan | 2022 | 7.3558e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-14 09:38 | 2022-01-14 09:41 | 172 | 000:03 | T | OTRAS CAUSAS | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA 1620-01 Y 95% DEL 1336-10 | S22011400000 | New_Event | Other Causes | Include | Include | Other | 3 | 2022-01-14 | 516 | keep | 0 | Jan | 2022 | 0.00035145 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
GUAYAMA | 2022-01-14 09:38 | 2022-01-14 11:28 | 7 | 001:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE CAJA DE TRANSFORMADOR PARA REPARAR BARRAS EN PEDESTAL SECUNDARIO | P22011400008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 110 | 2022-01-14 | 770 | keep | 0 | Jan | 2022 | 0.00052444 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2022-01-14 09:38 | 2022-01-14 11:04 | 207 | 001:26 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO ARBOL DE LA LINEA Y SE DIO LIGADURA | C22011400003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2022-01-14 | 17802 | keep | 0 | Jan | 2022 | 0.012125 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2022-01-14 09:41 | 2022-01-14 14:19 | 1 | 004:38 | P | NO SE REPORTO CAUSA | 1 X 25 EN SU NO IDENTIFICADO | R22011400001 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 278 | 2022-01-14 | 278 | keep | 0 | Jan | 2022 | 0.00018934 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-14 09:41 | 2022-01-14 12:09 | 1 | 002:28 | P | OTRAS CAUSAS | 2X65 EN RISER POR PROBLEMA DEL CLIENTE (PROA) | S22011400001 | 1st_after_momentary | Other Causes | Include | Include | Other | 148 | 2022-01-14 | 148 | keep | 0 | Jan | 2022 | 0.0001008 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-01-14 09:52 | 2022-01-14 15:17 | 60 | 005:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR NEUTRAL PRIMARIO PARTIDO | A22011400021 | New_Event | Wire Down | Include | Include | Equipment | 325 | 2022-01-14 | 19500 | keep | 0 | Jan | 2022 | 0.013281 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-01-14 10:01 | 2022-01-14 12:03 | 1 | 002:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22011400023 | New_Event | Bad Weather | Include | Include | Weather | 122 | 2022-01-14 | 122 | keep | 0 | Jan | 2022 | 8.3094e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-01-14 10:13 | 2022-01-14 15:10 | 10 | 004:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P22011400012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 297 | 2022-01-14 | 2970 | keep | 0 | Jan | 2022 | 0.0020229 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-01-14 10:15 | 2022-01-14 11:07 | 3 | 000:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA CAMBIAR BAJANTE SECUNDARIO | P22011400011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 52 | 2022-01-14 | 156 | keep | 0 | Jan | 2022 | 0.00010625 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-01-14 10:16 | 2022-01-14 18:44 | 10 | 008:28 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL HACIA T-12 MEDIANTE GOI BY-220114-01 | B22011400002 | New_Event | UG Cable Fault | Include | Include | Equipment | 508 | 2022-01-14 | 5080 | keep | 0 | Jan | 2022 | 0.00346 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-01-14 10:27 | 2022-01-14 11:36 | 5 | 001:09 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 37.5 POR 37.5KVA | C22011400033 | New_Event | Service Transformer Failure | Include | Include | Equipment | 69 | 2022-01-14 | 345 | keep | 0 | Jan | 2022 | 0.00023498 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2022-01-14 10:42 | 2022-01-14 12:03 | 18 | 001:21 | P | DESGANCHE | 1 X 30 EN C/L | R22011400013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2022-01-14 | 1458 | keep | 0 | Jan | 2022 | 0.00099304 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
AGUADILLA | 2022-01-14 10:52 | 2022-01-14 13:54 | 50 | 003:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22011400068 | New_Event | Wire Down | Include | Include | Equipment | 182 | 2022-01-14 | 9100 | keep | 0 | Jan | 2022 | 0.006198 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-14 10:53 | 2022-01-14 10:55 | 959 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERO POR SCADA | B22011400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-14 | 1918 | keep | 0 | Jan | 2022 | 0.0013063 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
CAGUAS | 2022-01-14 10:53 | 2022-01-14 14:03 | 15 | 003:10 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU | C22011400035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 190 | 2022-01-14 | 2850 | keep | 0 | Jan | 2022 | 0.0019411 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-01-14 11:09 | 2022-01-14 14:42 | 80 | 003:33 | P | DESGANCHE | 1 X 65 EN C/L. SE REALIZO DESGANCHE PERO REQUIERE DESGANCHE MASIVO | B22011400047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2022-01-14 | 17040 | keep | 0 | Jan | 2022 | 0.011606 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-01-14 11:15 | 2022-01-14 12:19 | 35 | 001:04 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22011400049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 64 | 2022-01-14 | 2240 | keep | 0 | Jan | 2022 | 0.0015257 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-01-14 11:20 | 2022-01-14 14:57 | 100 | 003:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22011400081 | New_Event | Bad Weather | Include | Include | Weather | 217 | 2022-01-14 | 21700 | keep | 0 | Jan | 2022 | 0.01478 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-01-14 11:21 | 2022-01-14 12:20 | 12 | 000:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M22011400082 | New_Event | Secondary Wire Down | Include | Include | Equipment | 59 | 2022-01-14 | 708 | keep | 0 | Jan | 2022 | 0.00048222 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2022-01-14 11:29 | 2022-01-14 12:48 | 5 | 001:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR EXCAVADORA AVERIO LINEA SECUNDARIA | P22011400016 | New_Event |  |  | Include | Wildlife | 79 | 2022-01-14 | 395 | keep | 0 | Jan | 2022 | 0.00026903 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-01-14 11:34 | 2022-01-14 11:37 | 2422 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S22011400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-01-14 | 7266 | keep | 0 | Jan | 2022 | 0.0049488 | 0.0016496 | Momentary | FALSE | FALSE | Not_TMED_Event | 2422
MAYAGÃœEZ | 2022-01-14 11:45 | 2022-01-17 15:30 | 60 | 075:45 | P | DESGANCHE | SE REALIZO DESGANCHE MASIVO Y SE REPARO LINEA PRIMARIA AVERIADA | M22011400090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 4545 | 2022-01-14 | 272700 | keep | 0 | Jan | 2022 | 0.18573 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-01-14 11:50 | 2022-01-14 11:52 | 2422 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S22011400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-14 | 4844 | keep | 0 | Jan | 2022 | 0.0032992 | 0.0016496 | Momentary | FALSE | FALSE | Not_TMED_Event | 2422
CANOVANAS | 2022-01-14 11:52 | 2022-01-14 12:38 | 6 | 000:46 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | R22011400015 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 46 | 2022-01-14 | 276 | keep | 0 | Jan | 2022 | 0.00018798 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-01-14 11:55 | 2022-01-14 13:52 | 969 | 001:57 | P | DESGANCHE | DISPARO DE INTERRUPTOR LLEVA 40% DE SU CARGA SE REALIZO DESGANCHE | S22011400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2022-01-14 | 113373 | keep | 0 | Jan | 2022 | 0.077218 | 0.00065998 | Sustained | FALSE | FALSE | Not_TMED_Event | 969
MAYAGÃœEZ | 2022-01-14 11:56 | 2022-01-14 17:40 | 5 | 005:44 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR QUEMADO DE 10 KVA POR 15 KVA VERIFICADO EN BITACORA VERIFICADO EN OMS EVENTO DEL DIA 14 | M22011400185 | New_Event | Service Transformer Failure | Include | Include | Equipment | 344 | 2022-01-14 | 1720 | keep | 0 | Jan | 2022 | 0.0011715 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-01-14 11:59 | 2022-01-14 12:05 | 5191 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22011400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-01-14 | 31146 | keep | 0 | Jan | 2022 | 0.021213 | 0.0035356 | Sustained | FALSE | FALSE | Not_TMED_Event | 5191
MAYAGÃœEZ | 2022-01-14 11:59 | 2022-01-14 15:56 | 100 | 003:57 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22011400096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 237 | 2022-01-14 | 23700 | keep | 0 | Jan | 2022 | 0.016142 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-01-14 12:05 | 2022-01-14 13:59 | 40 | 001:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE X AVE | R22011400017 | New_Event |  |  | Include | Wildlife | 114 | 2022-01-14 | 4560 | keep | 0 | Jan | 2022 | 0.0031058 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-01-14 12:08 | 2022-01-14 13:53 | 15 | 001:45 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | C22011400050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2022-01-14 | 1575 | keep | 0 | Jan | 2022 | 0.0010727 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-01-14 12:19 | 2022-01-14 14:50 | 250 | 002:31 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 140 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22011400033 | New_Event | Bad Weather | Include | Include | Weather | 151 | 2022-01-14 | 37750 | keep | 0 | Jan | 2022 | 0.025711 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2022-01-14 12:22 | 2022-01-14 13:38 | 1 | 001:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2X50 EN CORTE DE LINEA DE ELLOS Y SE REPARO CONDUCTOR SECUNDARIO AVERIADO | S22011400060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 76 | 2022-01-14 | 76 | keep | 0 | Jan | 2022 | 5.1763e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-01-14 12:32 | 2022-01-14 14:06 | 1 | 001:34 | P | DESGANCHE | 1 X 80 EN C/L | R22011400019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2022-01-14 | 94 | keep | 0 | Jan | 2022 | 6.4023e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-01-14 12:38 | 2022-01-14 15:31 | 20 | 002:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22011400036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2022-01-14 | 3460 | keep | 0 | Jan | 2022 | 0.0023566 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-01-14 12:38 | 2022-01-14 12:39 | 3295 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR SE CERRO POR SCADA | B22011400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-14 | 3295 | keep | 0 | Jan | 2022 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2022-01-14 12:43 | 2022-01-14 17:28 | 60 | 004:45 | P | DESGANCHE | 1 X 65 EN C/L. SE RETIRO RAMA | B22011400068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 285 | 2022-01-14 | 17100 | keep | 0 | Jan | 2022 | 0.011647 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-01-14 12:48 | 2022-01-14 17:30 | 25 | 004:42 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 50 KVA POR 50 KVA | M22011400116 | New_Event | Service Transformer Failure | Include | Include | Equipment | 282 | 2022-01-14 | 7050 | keep | 0 | Jan | 2022 | 0.0048017 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-01-14 12:49 | 2022-01-14 16:50 | 60 | 004:01 | P | DESGANCHE | 1 X 65 EN C/L. SE REALIZO DESGANCHE | B22011400070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2022-01-14 | 14460 | keep | 0 | Jan | 2022 | 0.0098486 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-01-14 12:50 | 2022-01-14 15:50 | 40 | 003:00 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | C22011400056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2022-01-14 | 7200 | keep | 0 | Jan | 2022 | 0.0049039 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-01-14 13:02 | 2022-01-14 17:32 | 50 | 004:30 | P | DESGANCHE | 1 X 65 EN C/L. SE REALIZO DESGANCHE | B22011400072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 270 | 2022-01-14 | 13500 | keep | 0 | Jan | 2022 | 0.0091948 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-01-14 13:05 | 2022-01-14 14:42 | 12 | 001:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22011400009 | New_Event | Secondary Wire Down | Include | Include | Equipment | 97 | 2022-01-14 | 1164 | keep | 0 | Jan | 2022 | 0.0007928 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-01-14 13:08 | 2022-01-14 17:14 | 125 | 004:06 | P | DESGANCHE | 3 X 140 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22011400124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2022-01-14 | 30750 | keep | 0 | Jan | 2022 | 0.020944 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
HUMACAO | 2022-01-14 13:21 | 2022-01-14 14:34 | 30 | 001:13 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | C22011400064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2022-01-14 | 2190 | keep | 0 | Jan | 2022 | 0.0014916 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-01-14 13:24 | 2022-01-14 15:30 | 30 | 002:06 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL ENCIMA DE LA LINEA NO FUNDIO | C22011400065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2022-01-14 | 3780 | keep | 0 | Jan | 2022 | 0.0025745 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-01-14 13:28 | 2022-01-14 13:32 | 135 | 000:04 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 CARGA POR EL 1346-05 | S21011400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-01-14 | 540 | keep | 0 | Jan | 2022 | 0.00036779 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2022-01-14 13:28 | 2022-01-14 13:32 | 837 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S21011400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-01-14 | 3348 | keep | 0 | Jan | 2022 | 0.0022803 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2022-01-14 13:28 | 2022-01-14 13:32 | 908 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S21011400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-01-14 | 3632 | keep | 0 | Jan | 2022 | 0.0024737 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
SAN JUAN | 2022-01-14 13:28 | 2022-01-14 13:32 | 135 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 LLEVA 1346-05 | S21011400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-01-14 | 540 | keep | 0 | Jan | 2022 | 0.00036779 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2022-01-14 13:28 | 2022-01-14 13:32 | 1 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S21011400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-01-14 | 4 | keep | 0 | Jan | 2022 | 2.7244e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-01-14 13:28 | 2022-01-14 13:32 | 1295 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S21011400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-01-14 | 5180 | keep | 0 | Jan | 2022 | 0.0035281 | 0.00088202 | Momentary | FALSE | FALSE | Not_TMED_Event | 1295
BAYAMON | 2022-01-14 13:28 | 2022-01-14 18:25 | 164 | 004:57 | T | LINEA DE TRANSMISION 38KV | DISPARO L-8900 PUENTE ABIERTO Y MOD 8927 NO QUERIA CERRAR SE PASO SUBEST. A LINEA 10100. EL 1531-02 LLEVA 1421-2 | S22011400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 297 | 2022-01-14 | 48708 | keep | 0 | Jan | 2022 | 0.033175 | 0.0001117 | Sustained | FALSE | FALSE | Not_TMED_Event | 164
BAYAMON | 2022-01-14 13:28 | 2022-01-14 18:22 | 427 | 004:54 | S | LINEA DE TRANSMISION 38KV | DIPARO L-8900 PUENTE ABIERTO Y MOD 8927 NO QUERIA CERRAR SE PASO SUBEST. A LINEA 10100 | S22011400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 294 | 2022-01-14 | 125538 | keep | 0 | Jan | 2022 | 0.085503 | 0.00029083 | Sustained | FALSE | FALSE | Not_TMED_Event | 427
BAYAMON | 2022-01-14 13:28 | 2022-01-14 18:25 | 716 | 004:57 | S | LINEA DE TRANSMISION 38KV | DIPARO L-8900 PUENTE ABIERTO Y MOD 8927 NO QUERIA CERRAR SE PASO SUBEST. A LINEA 10100 LLEVA 1421-2 | S22011400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 297 | 2022-01-14 | 212652 | keep | 0 | Jan | 2022 | 0.14484 | 0.00048766 | Sustained | FALSE | FALSE | Not_TMED_Event | 716
BAYAMON | 2022-01-14 13:28 | 2022-01-14 18:35 | 867 | 005:07 | S | LINEA DE TRANSMISION 38KV | DIPARO L-8900 PUENTE ABIERTO Y MOD 8927 NO QUERIA CERRAR SE PASO SUBEST. A LINEA 10100 | S22011400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 307 | 2022-01-14 | 266169 | keep | 0 | Jan | 2022 | 0.18129 | 0.00059051 | Sustained | FALSE | FALSE | Not_TMED_Event | 867
BAYAMON | 2022-01-14 13:28 | 2022-01-14 18:32 | 353 | 005:04 | S | LINEA DE TRANSMISION 38KV | DIPARO L-8900 PUENTE ABIERTO Y MOD 8927 NO QUERIA CERRAR SE PASO SUBEST. A LINEA 10100 | S22011400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 304 | 2022-01-14 | 107312 | keep | 0 | Jan | 2022 | 0.07309 | 0.00024043 | Sustained | FALSE | FALSE | Not_TMED_Event | 353
MAYAGÃœEZ | 2022-01-14 13:29 | 2022-01-14 13:30 | 721 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22011400135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-14 | 721 | keep | 0 | Jan | 2022 | 0.00049107 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
BAYAMON | 2022-01-14 13:45 | 2022-01-14 13:46 | 20 | 000:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22011300152 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1 | 2022-01-14 | 20 | keep | 0 | Jan | 2022 | 1.3622e-05 | 1.3622e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-01-14 13:50 | 2022-01-14 18:10 | 4 | 004:20 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR QUEMADO 15 KVA EN BANCO DE TRANSFORMADORES SE TRANSFIRIO LA CARGA A OTRO DEL BANCO HASTA QUE SE REALICE EL REMPLAZO | M22011400142 | New_Event | Service Transformer Failure | Include | Include | Equipment | 260 | 2022-01-14 | 1040 | keep | 0 | Jan | 2022 | 0.00070834 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-01-14 13:52 | 2022-01-14 18:08 | 40 | 004:16 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | S22011400117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 256 | 2022-01-14 | 10240 | keep | 0 | Jan | 2022 | 0.0069744 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-01-14 14:09 | 2022-01-14 16:27 | 10 | 002:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22011400082 | New_Event | Secondary Wire Down | Include | Include | Equipment | 138 | 2022-01-14 | 1380 | keep | 0 | Jan | 2022 | 0.00093991 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-01-14 14:15 | 2022-01-14 15:46 | 5 | 001:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P22011400038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 91 | 2022-01-14 | 455 | keep | 0 | Jan | 2022 | 0.0003099 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2022-01-14 14:18 | 2022-01-14 15:18 | 10 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BARRA EN PEDESTAL SECUNDARIO | P22011400040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2022-01-14 | 600 | keep | 0 | Jan | 2022 | 0.00040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-14 14:30 | 2022-01-14 16:20 | 40 | 001:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA RETEZAR LINEA PRIMARIA ARRIADA | A22011400045 | New_Event | Wire Down | Include | Include | Equipment | 110 | 2022-01-14 | 4400 | keep | 0 | Jan | 2022 | 0.0029968 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-01-14 14:43 | 2022-01-14 14:45 | 1483 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 30% DE LA CARGA DEL 1204-04 Y LA CARGA TOTAL DEL 1336-09 | S22011400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-14 | 2966 | keep | 0 | Jan | 2022 | 0.0020201 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-01-14 14:43 | 2022-01-14 14:45 | 5290 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 30% DE LA CARGA DEL 1204-04 Y LA CARGA TOTAL DEL 1336-09 | S22011400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-14 | 10580 | keep | 0 | Jan | 2022 | 0.007206 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-01-14 14:43 | 2022-01-14 14:45 | 207 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 30% DE LA CARGA DEL 1204-04 Y LA CARGA TOTAL DEL 1336-09 | S22011400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-14 | 414 | keep | 0 | Jan | 2022 | 0.00028197 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
ARECIBO | 2022-01-14 14:44 | 2022-01-14 15:01 | 100 | 000:17 | P | ERROR HUMANO | 1 X 80 EN CORTE DE LINEA PERSONAL DESGANCHANDO FUNDIO FUSIBLE | A22011400053 | New_Event | Human Error | Include | Include | Other | 17 | 2022-01-14 | 1700 | keep | 0 | Jan | 2022 | 0.0011579 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-01-14 14:45 | 2022-01-14 14:46 | 2770 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | C22011400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-14 | 2770 | keep | 0 | Jan | 2022 | 0.0018866 | 0.0018866 | Momentary | FALSE | FALSE | Not_TMED_Event | 2770
CAGUAS | 2022-01-14 14:46 | 2022-01-14 20:10 | 40 | 005:24 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | C22011400089 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 324 | 2022-01-14 | 12960 | keep | 0 | Jan | 2022 | 0.008827 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-01-14 14:49 | 2022-01-14 17:18 | 50 | 002:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22011400156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2022-01-14 | 7450 | keep | 0 | Jan | 2022 | 0.0050742 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-01-14 14:54 | 2022-01-14 14:55 | 1467 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22011400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-14 | 1467 | keep | 0 | Jan | 2022 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
PONCE | 2022-01-14 14:54 | 2022-01-14 18:42 | 100 | 003:48 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA DESGANCHE | P22011400043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2022-01-14 | 22800 | keep | 0 | Jan | 2022 | 0.015529 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-01-14 14:57 | 2022-01-14 17:59 | 10 | 003:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA E INSTALAR TENSOR | C22011400051 | New_Event | Secondary Wire Down | Include | Include | Equipment | 182 | 2022-01-14 | 1820 | keep | 0 | Jan | 2022 | 0.0012396 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-01-14 15:08 | 2022-01-14 16:41 | 50 | 001:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | P22011400045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2022-01-14 | 4650 | keep | 0 | Jan | 2022 | 0.0031671 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-01-14 15:15 | 2022-01-14 19:12 | 6 | 003:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN XMR REPARO BAJANTE DE LINEA A CAJA | R22011400026 | New_Event | Wire Down | Include | Include | Equipment | 237 | 2022-01-14 | 1422 | keep | 0 | Jan | 2022 | 0.00096852 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-01-14 15:18 | 2022-01-14 17:40 | 100 | 002:22 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22011400163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-01-14 | 14200 | keep | 0 | Jan | 2022 | 0.0096716 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-01-14 15:28 | 2022-01-14 15:30 | 1527 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR CON RECIERRE EN ON NO RECERRO NO SE REPORTO CAUSA SE CERRO POR CONTROL SCADA | A22011400062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-14 | 3054 | keep | 0 | Jan | 2022 | 0.0020801 | 0.00104 | Momentary | FALSE | FALSE | Not_TMED_Event | 1527
YAUCO | 2022-01-14 15:30 | 2022-01-14 16:27 | 50 | 000:57 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA DESGANCHE | P22011400051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2022-01-14 | 2850 | keep | 0 | Jan | 2022 | 0.0019411 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-01-14 15:37 | 2022-01-14 17:36 | 1467 | 001:59 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE TRANSFIRIO PARTE DE LA CARGA DE ALIMENTADOR 2701-03 AL 2701-02 SECCIONALIZANDO CONDUCTOR PRIMARIO DE TRONCAL EN EL SUELO | C22011400084 | New_Event | Wire Down | Include | Include | Equipment | 119 | 2022-01-14 | 174573 | keep | 0 | Jan | 2022 | 0.1189 | 0.00099917 | Sustained | FALSE | FALSE | Not_TMED_Event | 1467
SAN JUAN | 2022-01-14 15:50 | 2022-01-14 17:11 | 50 | 001:21 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22011400161 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2022-01-14 | 4050 | keep | 0 | Jan | 2022 | 0.0027584 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-01-14 15:56 | 2022-01-14 20:30 | 15 | 004:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | M22011400172 | New_Event | Wire Down | Include | Include | Equipment | 274 | 2022-01-14 | 4110 | keep | 0 | Jan | 2022 | 0.0027993 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-01-14 16:09 | 2022-01-14 17:26 | 20 | 001:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE RETIRO IGUANA CRUZANDO LINEA | C22011400101 | New_Event |  |  | Include | Wildlife | 77 | 2022-01-14 | 1540 | keep | 0 | Jan | 2022 | 0.0010489 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-01-14 16:14 | 2022-01-14 22:48 | 300 | 006:34 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | C22011400106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 394 | 2022-01-14 | 118200 | keep | 0 | Jan | 2022 | 0.080505 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-01-14 16:17 | 2022-01-14 18:09 | 40 | 001:52 | P | DESGANCHE | 1 X 50 EN C/L. SE REALIZO DESGANCHE | B22011400099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2022-01-14 | 4480 | keep | 0 | Jan | 2022 | 0.0030513 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-01-14 16:23 | 2022-01-15 08:52 | 108 | 016:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | S22011400178 | New_Event |  |  | Include | Wildlife | 989 | 2022-01-14 | 106812 | keep | 0 | Jan | 2022 | 0.072749 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
BAYAMON | 2022-01-14 16:26 | 2022-01-14 17:23 | 80 | 000:57 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B22011400104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 57 | 2022-01-14 | 4560 | keep | 0 | Jan | 2022 | 0.0031058 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2022-01-14 16:28 | 2022-01-14 17:32 | 20 | 001:04 | P | DESGANCHE | 1 X 30 EN C/L | R22011400030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2022-01-14 | 1280 | keep | 0 | Jan | 2022 | 0.0008718 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-01-14 16:28 | 2022-01-14 18:56 | 10 | 002:28 | P | NO SE REPORTO CAUSA | 2 X 10 EN TRANSFORMADOR | C22011400115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 148 | 2022-01-14 | 1480 | keep | 0 | Jan | 2022 | 0.001008 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-14 16:30 | 2022-01-14 17:21 | 8 | 000:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22011400069 | New_Event | Secondary Wire Down | Include | Include | Equipment | 51 | 2022-01-14 | 408 | keep | 0 | Jan | 2022 | 0.00027789 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-01-14 16:34 | 2022-01-14 18:06 | 60 | 001:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO | M22011400177 | New_Event | Wire Down | Include | Include | Equipment | 92 | 2022-01-14 | 5520 | keep | 0 | Jan | 2022 | 0.0037596 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-01-14 16:41 | 2022-01-14 20:56 | 7 | 004:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR AVE CRUZO FASE | S22011400183 | New_Event |  |  | Include | Wildlife | 255 | 2022-01-14 | 1785 | keep | 0 | Jan | 2022 | 0.0012158 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-01-14 16:44 | 2022-01-14 19:30 | 40 | 002:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN C/L. SE LEVANTO CONDUCTOR EN AEREO PROVISIONAL | S22011400185 | New_Event | Wire Down | Include | Include | Equipment | 166 | 2022-01-14 | 6640 | keep | 0 | Jan | 2022 | 0.0045225 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-01-14 16:59 | 2022-01-14 17:00 | 425 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR CON RECIERRE EN ON NO RECERRO NO SE REPORTO CAUSA SE CERRO POR CONTROL SCADA | A22011400077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-14 | 425 | keep | 0 | Jan | 2022 | 0.00028947 | 0.00028947 | Momentary | FALSE | FALSE | Not_TMED_Event | 425
CAGUAS | 2022-01-14 17:12 | 2022-01-15 09:17 | 95 | 016:05 | P | DESGANCHE | 2 X 50 EN C/L | C22011400140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 965 | 2022-01-14 | 91675 | keep | 0 | Jan | 2022 | 0.062439 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
ARECIBO | 2022-01-14 17:17 | 2022-01-14 19:53 | 10 | 002:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CAMION CRUZO LINEAS | A22011400078 | New_Event |  |  | Include | Wildlife | 156 | 2022-01-14 | 1560 | keep | 0 | Jan | 2022 | 0.0010625 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-01-14 17:32 | 2022-01-15 11:02 | 45 | 017:30 | P | DESGANCHE | 1 X 65 EN C/L | C22011400149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1050 | 2022-01-14 | 47250 | keep | 0 | Jan | 2022 | 0.032182 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
HUMACAO | 2022-01-14 17:36 | 2022-01-14 19:14 | 367 | 001:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO INTERRUPTOR Y SE LEVANTO CONDUCTOR PRIMARIO PARTIDO | C22011400084 | Partial_restoration | Wire Down | Include | Include | Equipment | 98 | 2022-01-14 | 35966 | keep | 0 | Jan | 2022 | 0.024496 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-01-14 17:38 | 2022-01-15 01:48 | 522 | 008:10 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PARTIDO MEDIANTE GOI BY-220114-02 | B22011400106 | New_Event | Defective Pole | Include | Include | Equipment | 490 | 2022-01-14 | 255780 | keep | 0 | Jan | 2022 | 0.17421 | 0.00035553 | Sustained | FALSE | FALSE | Not_TMED_Event | 522
MAYAGÃœEZ | 2022-01-14 17:40 | 2022-01-14 18:30 | 30 | 000:50 | P | TRANSFORMADOR AVERIADO | SE ABRIO CORTE DE LINEA PARA REMPLAZO TRANSFORMADOR QUEMADO DE 10KVA POR 15 KVA | M22011400185 | Additional_clients | Service Transformer Failure | Include | Include | Equipment | 50 | 2022-01-14 | 1500 | keep | 0 | Jan | 2022 | 0.0010216 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-01-14 18:21 | 2022-01-15 10:26 | 1 | 016:05 | P | NO SE REPORTO CAUSA | 1 X 20 EN BANCO DE XMRS | C22011400157 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 965 | 2022-01-14 | 965 | keep | 0 | Jan | 2022 | 0.00065726 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-01-14 18:52 | 2022-01-14 20:09 | 30 | 001:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN C/L CRUCE X AVE | R22011400033 | New_Event |  |  | Include | Wildlife | 77 | 2022-01-14 | 2310 | keep | 0 | Jan | 2022 | 0.0015733 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-01-14 18:52 | 2022-01-14 19:14 | 30 | 000:22 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA INDICA FOREMAN REQUIERE DESGANCHE | A22011400083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 22 | 2022-01-14 | 660 | keep | 0 | Jan | 2022 | 0.00044952 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-01-14 19:01 | 2022-01-14 19:02 | 2675 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22011400034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-14 | 2675 | keep | 0 | Jan | 2022 | 0.0018219 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
ARECIBO | 2022-01-14 19:01 | 2022-01-14 21:15 | 100 | 002:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A22011400085 | New_Event | Cutout Failure | Include | Include | Equipment | 134 | 2022-01-14 | 13400 | keep | 0 | Jan | 2022 | 0.0091267 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-01-14 19:03 | 2022-01-15 11:27 | 10 | 016:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | S22011400237 | New_Event | Secondary Wire Down | Include | Include | Equipment | 984 | 2022-01-14 | 9840 | keep | 0 | Jan | 2022 | 0.006702 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-01-14 19:53 | 2022-01-15 13:13 | 10 | 017:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22011400200 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1040 | 2022-01-14 | 10400 | keep | 0 | Jan | 2022 | 0.0070834 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-01-14 20:16 | 2022-01-14 20:17 | 30 | 000:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA SE RETIRO AVE CRUZANDO LINEAS | C22011400097 | New_Event |  |  | Include | Wildlife | 1 | 2022-01-14 | 30 | keep | 0 | Jan | 2022 | 2.0433e-05 | 2.0433e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-01-14 20:38 | 2022-01-14 22:31 | 270 | 001:53 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | R22011400038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 113 | 2022-01-14 | 30510 | keep | 0 | Jan | 2022 | 0.02078 | 0.0001839 | Sustained | FALSE | FALSE | Not_TMED_Event | 270
BAYAMON | 2022-01-14 22:08 | 2022-01-15 12:59 | 64 | 014:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO PUENTE DE LINEA A CAJA | S22011400249 | New_Event | Wire Down | Include | Include | Equipment | 891 | 2022-01-14 | 57024 | keep | 0 | Jan | 2022 | 0.038839 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
MAYAGÃœEZ | 2022-01-14 22:35 | 2022-01-14 22:49 | 6 | 000:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 5 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA | M22011400205 | New_Event | Secondary Wire Down | Include | Include | Equipment | 14 | 2022-01-14 | 84 | keep | 0 | Jan | 2022 | 5.7212e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-01-14 22:53 | 2022-01-15 15:41 | 20 | 016:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA | M22011400206 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1008 | 2022-01-14 | 20160 | keep | 0 | Jan | 2022 | 0.013731 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-01-14 23:00 | 2022-01-15 01:37 | 75 | 002:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO CONDUCTOR PRIMARIO | B22011400133 | New_Event | Wire Down | Include | Include | Equipment | 157 | 2022-01-14 | 11775 | keep | 0 | Jan | 2022 | 0.0080199 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CANOVANAS | 2022-01-15 00:05 | 2022-01-15 00:06 | 3766 | 000:01 | T | DESGANCHE | RECIERRE | R22011500001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-15 | 3766 | keep | 0 | Jan | 2022 | 0.002565 | 0.002565 | Momentary | FALSE | FALSE | Not_TMED_Event | 3766
CANOVANAS | 2022-01-15 00:06 | 2022-01-15 11:15 | 88 | 011:09 | P | DESGANCHE | 1 X 100 EN C/L | R22011500002 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 669 | 2022-01-15 | 58872 | keep | 0 | Jan | 2022 | 0.040097 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
BAYAMON | 2022-01-15 00:48 | 2022-01-15 00:49 | 4622 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 10% 1717-01 | B22011500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-15 | 4622 | keep | 0 | Jan | 2022 | 0.003148 | 0.003148 | Momentary | FALSE | FALSE | Not_TMED_Event | 4622
CAGUAS | 2022-01-15 02:24 | 2022-01-15 13:15 | 15 | 010:51 | P | ESTRUCTURA AVERIADA | 1 X 30 EN C/L REMPLAZO POSTE PARTIDO | C22011500004 | New_Event | Defective Pole | Include | Include | Equipment | 651 | 2022-01-15 | 9765 | keep | 0 | Jan | 2022 | 0.0066509 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-01-15 03:18 | 2022-01-15 03:19 | 2126 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C22011500005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-15 | 2126 | keep | 0 | Jan | 2022 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
BAYAMON | 2022-01-15 03:37 | 2022-01-15 03:38 | 453 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1806-02 LLEVA 10% DEL 1717-01 | B22011500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-15 | 453 | keep | 0 | Jan | 2022 | 0.00030854 | 0.00030854 | Momentary | FALSE | FALSE | Not_TMED_Event | 453
ARECIBO | 2022-01-15 04:17 | 2022-01-15 04:18 | 2107 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22011500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-15 | 2107 | keep | 0 | Jan | 2022 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
BAYAMON | 2022-01-15 05:27 | 2022-01-15 05:29 | 3 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR PROVISIONAL #6 LLEVA LA CARGA DE LOS BREAKERS: 1707-02, 1707-03, 1707-04, 1707-05 | B22011500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-15 | 6 | keep | 0 | Jan | 2022 | 4.0866e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-01-15 05:27 | 2022-01-15 05:29 | 61 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR PROVISIONAL #6 LLEVA LA CARGA DE LOS BREAKERS: 1707-02, 1707-03, 1707-04, 1707-05 | B22011500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-15 | 122 | keep | 0 | Jan | 2022 | 8.3094e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2022-01-15 05:27 | 2022-01-15 05:29 | 1501 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR PROVISIONAL #6 LLEVA LA CARGA DE LOS BREAKERS: 1707-02, 1707-03, 1707-04, 1707-05 | B22011500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-15 | 3002 | keep | 0 | Jan | 2022 | 0.0020446 | 0.0010223 | Momentary | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2022-01-15 05:27 | 2022-01-15 05:29 | 546 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR PROVISIONAL #6 LLEVA LA CARGA DE LOS BREAKERS: 1707-02, 1707-03, 1707-04, 1707-05 | B22011500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-15 | 1092 | keep | 0 | Jan | 2022 | 0.00074376 | 0.00037188 | Momentary | FALSE | FALSE | Not_TMED_Event | 546
BAYAMON | 2022-01-15 06:07 | 2022-01-15 06:10 | 2617 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22011500008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-01-15 | 7851 | keep | 0 | Jan | 2022 | 0.0053473 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
MAYAGÃœEZ | 2022-01-15 07:25 | 2022-01-15 14:22 | 150 | 006:57 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22011500004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 417 | 2022-01-15 | 62550 | keep | 0 | Jan | 2022 | 0.042603 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2022-01-15 07:27 | 2022-01-15 09:39 | 2635 | 002:12 | T | PARARRAYOS DEFECTUOSO | SE SECCIONALIZO EL ALIMENTADOR | C22011500012 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 132 | 2022-01-15 | 347820 | keep | 0 | Jan | 2022 | 0.2369 | 0.0017947 | Sustained | FALSE | FALSE | Not_TMED_Event | 2635
CAGUAS | 2022-01-15 07:40 | 2022-01-15 14:59 | 92 | 007:19 | P | ESTRUCTURA AVERIADA | ABRIO C/L PARA REMPLAZAR POSTE PARTIDO | C22011500014 | New_Event | Defective Pole | Include | Include | Equipment | 439 | 2022-01-15 | 40388 | keep | 0 | Jan | 2022 | 0.027508 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
CANOVANAS | 2022-01-15 07:45 | 2022-01-15 15:47 | 25 | 008:02 | P | DESGANCHE | 1 X 25 EN C/L | R22011500007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 482 | 2022-01-15 | 12050 | keep | 0 | Jan | 2022 | 0.0082072 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2022-01-15 07:47 | 2022-01-15 15:21 | 80 | 007:34 | P | CABLE SOTERRADO AVERIADO | 1 X 200 EN SU Y 1 X 40 EN RISER | B22011500010 | New_Event | UG Cable Fault | Include | Include | Equipment | 454 | 2022-01-15 | 36320 | keep | 0 | Jan | 2022 | 0.024737 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-01-15 07:50 | 2022-01-15 08:59 | 1648 | 001:09 | T | AISLADOR ROTO, PARTIDO O SAFADO | SECCIONALIZO AISLADORES PARTIDOS | R22011500010 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 69 | 2022-01-15 | 113712 | keep | 0 | Jan | 2022 | 0.077449 | 0.0011224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1648
HUMACAO | 2022-01-15 08:10 | 2022-01-15 12:02 | 95 | 003:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN C/L CRUCE X AVE | C22011500024 | New_Event |  |  | Include | Wildlife | 232 | 2022-01-15 | 22040 | keep | 0 | Jan | 2022 | 0.015011 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
PONCE | 2022-01-15 08:19 | 2022-01-15 11:15 | 50 | 002:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA CERRAR PUENTE PRIMARIO EN POSTE DE MADERA NO TRABAJA VEHICULO | P22011500001 | New_Event | Wire Down | Include | Include | Equipment | 176 | 2022-01-15 | 8800 | keep | 0 | Jan | 2022 | 0.0059936 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-01-15 08:47 | 2022-01-15 17:54 | 40 | 009:07 | P | DESGANCHE | 1 X 40 EN C/L | C22011500035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 547 | 2022-01-15 | 21880 | keep | 0 | Jan | 2022 | 0.014902 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-01-15 08:59 | 2022-01-15 09:44 | 720 | 000:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | REMPLAZO AISLADORES PARTIDOS | R22011500010 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 45 | 2022-01-15 | 32400 | keep | 0 | Jan | 2022 | 0.022067 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-01-15 09:00 | 2022-01-15 09:02 | 2617 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22011500016 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-15 | 5234 | keep | 0 | Jan | 2022 | 0.0035649 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
FAJARDO | 2022-01-15 09:07 | 2022-01-15 14:16 | 7 | 005:09 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 25 KVA X 50 KVA | R22011500047 | New_Event | Service Transformer Failure | Include | Include | Equipment | 309 | 2022-01-15 | 2163 | keep | 0 | Jan | 2022 | 0.0014732 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2022-01-15 09:10 | 2022-01-15 10:24 | 4 | 001:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR BARRAS DE PEDESTAL | C22011500038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 74 | 2022-01-15 | 296 | keep | 0 | Jan | 2022 | 0.0002016 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
FAJARDO | 2022-01-15 09:13 | 2022-01-15 10:04 | 55 | 000:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN C/L FIJO BAJANTE DE CAJA A LINEA | R22011500048 | New_Event | Wire Down | Include | Include | Equipment | 51 | 2022-01-15 | 2805 | keep | 0 | Jan | 2022 | 0.0019105 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
ARECIBO | 2022-01-15 09:24 | 2022-01-15 11:09 | 9 | 001:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22011500002 | New_Event | Bad Weather | Include | Include | Weather | 105 | 2022-01-15 | 945 | keep | 0 | Jan | 2022 | 0.00064364 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-01-15 09:38 | 2022-01-15 09:39 | 863 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22011500012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-15 | 863 | keep | 0 | Jan | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
BARRANQUITAS | 2022-01-15 09:39 | 2022-01-15 10:30 | 659 | 000:51 | P | PARARRAYOS DEFECTUOSO | SE SECCIONALIZO PARARRAYO CRUZADO | C22011500012 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 51 | 2022-01-15 | 33609 | keep | 0 | Jan | 2022 | 0.022891 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-01-15 10:09 | 2022-01-15 15:12 | 5 | 005:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA Y VIENTO | M22011500014 | New_Event | Bad Weather | Include | Include | Weather | 303 | 2022-01-15 | 1515 | keep | 0 | Jan | 2022 | 0.0010319 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2022-01-15 10:10 | 2022-01-15 12:05 | 4 | 001:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR BAJANTES SECUNDARIOS | P22011500007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 115 | 2022-01-15 | 460 | keep | 0 | Jan | 2022 | 0.0003133 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-01-15 10:29 | 2022-01-15 17:30 | 150 | 007:01 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22011500019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 421 | 2022-01-15 | 63150 | keep | 0 | Jan | 2022 | 0.043011 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2022-01-15 10:30 | 2022-01-15 11:50 | 1975 | 001:20 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRAYO | C22011500012 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 80 | 2022-01-15 | 158000 | keep | 0 | Jan | 2022 | 0.10761 | 0.0013452 | Sustained | FALSE | FALSE | Not_TMED_Event | 1975
SAN JUAN | 2022-01-15 11:12 | 2022-01-15 15:41 | 40 | 004:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CRUCE X AVE | R22011500080 | New_Event |  |  | Include | Wildlife | 269 | 2022-01-15 | 10760 | keep | 0 | Jan | 2022 | 0.0073286 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-01-15 11:15 | 2022-01-15 14:03 | 150 | 002:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO Y SE PROCEDIO A CERRAR CAJAS EN CORTE DE LINEA | P22011500001 | New_Event | Wire Down | Include | Include | Equipment | 168 | 2022-01-15 | 25200 | keep | 0 | Jan | 2022 | 0.017164 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-01-15 11:17 | 2022-01-15 15:13 | 100 | 003:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN C/L CRUCE X AVE | R22011500081 | New_Event |  |  | Include | Wildlife | 236 | 2022-01-15 | 23600 | keep | 0 | Jan | 2022 | 0.016074 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-01-15 11:20 | 2022-01-16 14:48 | 2 | 027:28 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA POR LA MISMA CAPACIDAD | M22011500030 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1648 | 2022-01-15 | 3296 | keep | 0 | Jan | 2022 | 0.0022449 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-01-15 11:23 | 2022-01-15 12:57 | 30 | 001:34 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B22011500046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 94 | 2022-01-15 | 2820 | keep | 0 | Jan | 2022 | 0.0019207 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-01-15 11:27 | 2022-01-15 16:57 | 5 | 005:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR LA MISMA CAPACIDAD | M22011500031 | New_Event | Service Transformer Failure | Include | Include | Equipment | 330 | 2022-01-15 | 1650 | keep | 0 | Jan | 2022 | 0.0011238 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-01-15 11:40 | 2022-01-15 13:51 | 20 | 002:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO PARA REPARAR BAJANTES SECUNDARIOS DE TRANSFORMADORES | M22011500033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 131 | 2022-01-15 | 2620 | keep | 0 | Jan | 2022 | 0.0017845 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-01-15 12:28 | 2022-01-15 18:04 | 1 | 005:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M22011500038 | New_Event |  |  | Include | Wildlife | 336 | 2022-01-15 | 336 | keep | 0 | Jan | 2022 | 0.00022885 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-01-15 12:31 | 2022-01-15 14:33 | 1337 | 002:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO CERRO POR SCADA SE PATRULLO Y NO SE ENCONTRO CAUSA PARA EL DISPARO DEL INTERRUPTOR SE CERRO EN LA SUBESTACION POR MIGUEL RAMOS DE SUBESTACIONES INFORMO QUE LO TENIAN PENDIENTE PARA VERIFICAR | M22011500040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2022-01-15 | 163114 | keep | 0 | Jan | 2022 | 0.1111 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
BAYAMON | 2022-01-15 12:32 | 2022-01-15 13:47 | 10 | 001:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA Y REALIZAR DESGANCHE | B22011500056 | New_Event | Secondary Wire Down | Include | Include | Equipment | 75 | 2022-01-15 | 750 | keep | 0 | Jan | 2022 | 0.00051082 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-01-15 12:33 | 2022-01-15 14:01 | 25 | 001:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR BAJANTES SECUNDARIOS | P22011500021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 88 | 2022-01-15 | 2200 | keep | 0 | Jan | 2022 | 0.0014984 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-01-15 12:39 | 2022-01-15 12:40 | 1225 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVA LA CARGA DEL 1203-03 | S22011500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-15 | 1225 | keep | 0 | Jan | 2022 | 0.00083434 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2022-01-15 12:39 | 2022-01-15 12:40 | 616 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR CARGA POR EL 1203-01 | S22011500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-15 | 616 | keep | 0 | Jan | 2022 | 0.00041955 | 0.00041955 | Momentary | FALSE | FALSE | Not_TMED_Event | 616
ARECIBO | 2022-01-15 12:42 | 2022-01-15 14:35 | 80 | 001:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A22011500008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2022-01-15 | 9040 | keep | 0 | Jan | 2022 | 0.0061571 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-01-15 13:02 | 2022-01-15 16:22 | 10 | 003:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | B22011300197 | New_Event | Secondary Wire Down | Include | Include | Equipment | 200 | 2022-01-15 | 2000 | keep | 0 | Jan | 2022 | 0.0013622 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-15 13:05 | 2022-01-15 14:27 | 15 | 001:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22011500010 | New_Event | Bad Weather | Include | Include | Weather | 82 | 2022-01-15 | 1230 | keep | 0 | Jan | 2022 | 0.00083775 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-01-15 13:28 | 2022-01-15 14:50 | 75 | 001:22 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22011500036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 82 | 2022-01-15 | 6150 | keep | 0 | Jan | 2022 | 0.0041887 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CANOVANAS | 2022-01-15 13:48 | 2022-01-15 16:01 | 20 | 002:13 | P | DESGANCHE | 1 X 20 EN C/L | R22011500024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2022-01-15 | 2660 | keep | 0 | Jan | 2022 | 0.0018117 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-01-15 14:05 | 2022-01-15 15:59 | 50 | 001:54 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22011500037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2022-01-15 | 5700 | keep | 0 | Jan | 2022 | 0.0038822 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-01-15 14:05 | 2022-01-15 16:43 | 40 | 002:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L REMPLAZO CAJA AVERIADA | R22011500105 | New_Event | Cutout Failure | Include | Include | Equipment | 158 | 2022-01-15 | 6320 | keep | 0 | Jan | 2022 | 0.0043045 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-01-15 14:13 | 2022-01-15 14:33 | 18 | 000:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C22011500091 | New_Event | Secondary Wire Down | Include | Include | Equipment | 20 | 2022-01-15 | 360 | keep | 0 | Jan | 2022 | 0.00024519 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
GUAYAMA | 2022-01-15 14:17 | 2022-01-15 15:23 | 16 | 001:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P22011500026 | New_Event |  |  | Include | Wildlife | 66 | 2022-01-15 | 1056 | keep | 0 | Jan | 2022 | 0.00071924 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2022-01-15 14:20 | 2022-01-15 16:32 | 12 | 002:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22011500028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 132 | 2022-01-15 | 1584 | keep | 0 | Jan | 2022 | 0.0010789 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-01-15 14:33 | 2022-01-15 14:34 | 527 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22011500029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-15 | 527 | keep | 0 | Jan | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
BAYAMON | 2022-01-15 14:34 | 2022-01-15 14:36 | 767 | 000:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1709-03 LLEVANDO CARGA 1709-05 50% DE 1709-03 POR 1909-07 | B22011500066 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-01-15 | 1534 | keep | 0 | Jan | 2022 | 0.0010448 | 0.0005224 | Momentary | FALSE | FALSE | Not_TMED_Event | 767
BAYAMON | 2022-01-15 14:34 | 2022-01-15 14:36 | 2364 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1709-03 LLEVANDO CARGA 1709-05 50% DE 1709-03 POR 1909-07 | B22011500066 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2022-01-15 | 4728 | keep | 0 | Jan | 2022 | 0.0032202 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
BAYAMON | 2022-01-15 14:36 | 2022-01-15 15:18 | 100 | 000:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO Y SE LEVANTO CONDUCTOR PRIMARIO PARTIDO | B22011500042 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 42 | 2022-01-15 | 4200 | keep | 0 | Jan | 2022 | 0.0028606 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-01-15 14:42 | 2022-01-15 14:43 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22011500057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-15 | 1097 | keep | 0 | Jan | 2022 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
YAUCO | 2022-01-15 14:43 | 2022-01-15 15:39 | 12 | 000:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22011500030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2022-01-15 | 672 | keep | 0 | Jan | 2022 | 0.0004577 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-01-15 15:00 | 2022-01-15 16:36 | 12 | 001:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22011500035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 96 | 2022-01-15 | 1152 | keep | 0 | Jan | 2022 | 0.00078462 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-01-15 15:06 | 2022-01-15 15:07 | 390 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22011500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-15 | 390 | keep | 0 | Jan | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
CAGUAS | 2022-01-15 15:08 | 2022-01-15 16:09 | 40 | 001:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA AVERIADA NO FUNDIO | C22011500095 | New_Event | Cutout Failure | Include | Include | Equipment | 61 | 2022-01-15 | 2440 | keep | 0 | Jan | 2022 | 0.0016619 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-01-15 15:08 | 2022-01-15 16:42 | 120 | 001:34 | P | DESGANCHE | 2 X 80 EN C/L | C22011500094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2022-01-15 | 11280 | keep | 0 | Jan | 2022 | 0.0076828 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
AGUADILLA | 2022-01-15 15:11 | 2022-01-15 18:27 | 6 | 003:16 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER EL JOURNEYMAN INFORMO QUE NO DETECTO CAUSA PARA EL FUSIBLE FUNDIDO | M22011500061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 196 | 2022-01-15 | 1176 | keep | 0 | Jan | 2022 | 0.00080097 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-01-15 15:12 | 2022-01-15 16:21 | 8 | 001:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN XMR REPARO SECUNDARIA | C22011500096 | New_Event | Secondary Wire Down | Include | Include | Equipment | 69 | 2022-01-15 | 552 | keep | 0 | Jan | 2022 | 0.00037596 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-01-15 15:18 | 2022-01-15 15:27 | 767 | 000:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1709-03 LLEVANDO CARGA 1709-05 50% DE 1709-03 POR 1909-07 CONDUCTOR PRIMARIO EN EL SUELO | B22011500073 | Additional_clients | Wire Down | Include | Include | Equipment | 9 | 2022-01-15 | 6903 | keep | 0 | Jan | 2022 | 0.0047016 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-01-15 15:18 | 2022-01-15 15:27 | 2364 | 000:09 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1709-03 LLEVANDO CARGA 1709-05 50% DE 1709-03 POR 1909-07 CONDUCTOR PRIMARIO EN EL SUELO | B22011500073 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 9 | 2022-01-15 | 21276 | keep | 0 | Jan | 2022 | 0.014491 | 0.0016101 | Sustained | FALSE | FALSE | Not_TMED_Event | 2364
VEGA BAJA | 2022-01-15 15:21 | 2022-01-15 20:06 | 80 | 004:45 | P | CABLE SOTERRADO AVERIADO | 1 X 200 EN SU Y 1 X 40 EN RISER AVERIA SOTERRADA SE QUEDARON 3 TRANSFORMADORES FUERA | B22011500010 | New_Event | UG Cable Fault | Include | Include | Equipment | 285 | 2022-01-15 | 22800 | keep | 0 | Jan | 2022 | 0.015529 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-01-15 15:26 | 2022-01-15 17:18 | 18 | 001:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN C/L MAL TIEMPO | R22011500108 | New_Event | Bad Weather | Include | Include | Weather | 112 | 2022-01-15 | 2016 | keep | 0 | Jan | 2022 | 0.0013731 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2022-01-15 15:27 | 2022-01-15 18:02 | 100 | 002:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO Y SE LEVANTO CONDUCTOR PRIMARIO PARTIDO | B22011500042 | Partial_restoration | Wire Down | Include | Include | Equipment | 155 | 2022-01-15 | 15500 | keep | 0 | Jan | 2022 | 0.010557 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-01-15 15:30 | 2022-01-15 19:09 | 44 | 003:39 | P | DESGANCHE | 1 X 50 EN C/L | C22011500104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2022-01-15 | 9636 | keep | 0 | Jan | 2022 | 0.006563 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
PONCE | 2022-01-15 15:34 | 2022-01-15 16:09 | 40 | 000:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P22011500035 | New_Event |  |  | Include | Wildlife | 35 | 2022-01-15 | 1400 | keep | 0 | Jan | 2022 | 0.00095353 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-01-15 15:51 | 2022-01-15 15:54 | 350 | 000:03 | P | NO SE REPORTO CAUSA | LLEVA 95% 1336-10 Y 1620-01 INTERRUPTOR 1620-04 DISPARO Y SE CERRO POR CONTROL | S22011500048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-01-15 | 1050 | keep | 0 | Jan | 2022 | 0.00071515 | 0.00023838 | Momentary | FALSE | FALSE | Not_TMED_Event | 350
SAN JUAN | 2022-01-15 15:51 | 2022-01-15 15:54 | 36 | 000:03 | T | NO SE REPORTO CAUSA | LLEVA 95% 1336-10 Y 1620-01 INTERRUPTOR 1620-04 DISPARO Y SE CERRO POR CONTROL | S22011500048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-01-15 | 108 | keep | 0 | Jan | 2022 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-01-15 15:51 | 2022-01-15 15:54 | 172 | 000:03 | T | NO SE REPORTO CAUSA | LLEVA 95% 1336-10 Y 1620-01 INTERRUPTOR DISPARO Y SE CERRO POR CONTROL | S22011500048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-01-15 | 516 | keep | 0 | Jan | 2022 | 0.00035145 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
BAYAMON | 2022-01-15 15:52 | 2022-01-15 16:53 | 10 | 001:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | B22011500070 | New_Event | Secondary Wire Down | Include | Include | Equipment | 61 | 2022-01-15 | 610 | keep | 0 | Jan | 2022 | 0.00041547 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-01-15 16:06 | 2022-01-15 17:45 | 4536 | 001:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | ESTE ALIMENTADOR TIENE EL 30% DE SU CARGA TRANSFERIDA SE RETIRO IGUANA DE LOS MACHETES DE SALIDA | S22011500050 | New_Event |  |  | Include | Wildlife | 99 | 2022-01-15 | 449064 | keep | 0 | Jan | 2022 | 0.30586 | 0.0030894 | Sustained | FALSE | FALSE | Not_TMED_Event | 4536
SAN JUAN | 2022-01-15 16:06 | 2022-01-15 16:07 | 20 | 000:01 | P | NO SE REPORTO CAUSA | PROTECCION OPERO AL VER LA AVERIA DEL FEEDER 1336-06 95% TRANSFERIDO AL 1620-01 | S22011500050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-15 | 20 | keep | 0 | Jan | 2022 | 1.3622e-05 | 1.3622e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-01-15 16:08 | 2022-01-15 18:31 | 80 | 002:23 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22011500051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2022-01-15 | 11440 | keep | 0 | Jan | 2022 | 0.0077917 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-01-15 16:15 | 2022-01-15 17:45 | 14 | 001:30 | P | NO SE REPORTO CAUSA | 1 X 30 EN MONTURA DE TRANSFORMADORES JOURNEYMAN INDICO NO ENCONTRO CAUSA | A22011500064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 90 | 2022-01-15 | 1260 | keep | 0 | Jan | 2022 | 0.00085818 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2022-01-15 16:18 | 2022-01-15 17:39 | 75 | 001:21 | P | NO SE REPORTO CAUSA | 1 X 50 EN PROVISIONAL AEREO | S22011500057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2022-01-15 | 6075 | keep | 0 | Jan | 2022 | 0.0041377 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-01-15 16:42 | 2022-01-15 18:01 | 35 | 001:19 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22011500080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 79 | 2022-01-15 | 2765 | keep | 0 | Jan | 2022 | 0.0018832 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2022-01-15 16:46 | 2022-01-15 18:09 | 1712 | 001:23 | T | DESGANCHE | DISPARO INTERRUPTOR NO RECERRO TIENE LA CARGA 5010-04 | P22011500038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2022-01-15 | 142096 | keep | 0 | Jan | 2022 | 0.096781 | 0.001166 | Sustained | FALSE | FALSE | Not_TMED_Event | 1712
PONCE | 2022-01-15 16:46 | 2022-01-15 18:09 | 7 | 001:23 | T | DESGANCHE | DISPARO INTERRUPTOR 5005-03 CON CARGA 5010-04 | P22011500038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2022-01-15 | 581 | keep | 0 | Jan | 2022 | 0.00039572 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-01-15 16:48 | 2022-01-15 19:18 | 60 | 002:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22011500066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2022-01-15 | 9000 | keep | 0 | Jan | 2022 | 0.0061299 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-01-15 16:50 | 2022-01-15 17:28 | 7 | 000:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22011500011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 38 | 2022-01-15 | 266 | keep | 0 | Jan | 2022 | 0.00018117 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-01-15 16:56 | 2022-01-15 18:39 | 240 | 001:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA Y SE REMPLAZARON CAJAS PRIMARIAS | A22011500017 | New_Event | Wire Down | Include | Include | Equipment | 103 | 2022-01-15 | 24720 | keep | 0 | Jan | 2022 | 0.016837 | 0.00016346 | Sustained | FALSE | FALSE | Not_TMED_Event | 240
BAYAMON | 2022-01-15 17:00 | 2022-01-15 19:31 | 40 | 002:31 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22011500068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2022-01-15 | 6040 | keep | 0 | Jan | 2022 | 0.0041138 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-01-15 17:03 | 2022-01-15 17:05 | 1844 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | INTERRUPTOR DISPARO Y SE CERRO POR CONTROL LLEVA 60% 1346-03 & 30% 1529-15 | S22011500000 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2022-01-15 | 3688 | keep | 0 | Jan | 2022 | 0.0025119 | 0.0012559 | Momentary | FALSE | FALSE | Not_TMED_Event | 1844
SAN JUAN | 2022-01-15 17:03 | 2022-01-15 17:05 | 969 | 000:02 | P | DESCONECTIVO DEFECTUOSO | 60% DE LA CARGA TRANSFERIDA AL 1346-02 INTERRUPTOR DISPARO Y SE CERRO POR CONTROL | S22011500000 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2022-01-15 | 1938 | keep | 0 | Jan | 2022 | 0.00132 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
BAYAMON | 2022-01-15 17:03 | 2022-01-15 17:05 | 300 | 000:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 30% DE LA CARGA TRANSFERIDA AL 1346-02 INTERRUPTOR DISPARO Y SE CERRO POR CONTROL | S22011500000 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2022-01-15 | 600 | keep | 0 | Jan | 2022 | 0.00040866 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-01-15 17:05 | 2022-01-15 20:16 | 300 | 003:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 140 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | S22011500070 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 191 | 2022-01-15 | 57300 | keep | 0 | Jan | 2022 | 0.039027 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2022-01-15 17:27 | 2022-01-16 08:33 | 4 | 015:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR BARRA DE PEDESTAL | R22011500183 | New_Event | Secondary Wire Down | Include | Include | Equipment | 906 | 2022-01-15 | 3624 | keep | 0 | Jan | 2022 | 0.0024683 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2022-01-15 17:45 | 2022-01-15 23:43 | 60 | 005:58 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS Y SE CERRO PUENTE ABIERTO | M22011500074 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 358 | 2022-01-15 | 21480 | keep | 0 | Jan | 2022 | 0.01463 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-01-15 17:45 | 2022-01-16 22:13 | 5 | 028:28 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22011500024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1708 | 2022-01-15 | 8540 | keep | 0 | Jan | 2022 | 0.0058166 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2022-01-15 17:49 | 2022-01-15 17:50 | 2280 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 9902-03 | C22011500113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-15 | 2280 | keep | 0 | Jan | 2022 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2022-01-15 17:49 | 2022-01-15 17:50 | 1617 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 9902-02 | C22011500113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-15 | 1617 | keep | 0 | Jan | 2022 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
BAYAMON | 2022-01-15 17:54 | 2022-01-15 23:12 | 100 | 005:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 Y 2 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | S22011500095 | New_Event | Wire Down | Include | Include | Equipment | 318 | 2022-01-15 | 31800 | keep | 0 | Jan | 2022 | 0.021659 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-01-15 17:55 | 2022-01-15 17:58 | 1943 | 000:03 | T | OTRAS CAUSAS | DISPARO DE INTERRUPTOR AL PERSONAL DE SUBESTACIONES CERRAR PUERTA DEL MISMO SE VERIFICO PERSONAL FUERA DEL AREA Y SE CERRO EL INTERRUPTOR | M22011500000 | New_Event | Other Causes | Include | Include | Other | 3 | 2022-01-15 | 5829 | keep | 0 | Jan | 2022 | 0.0039701 | 0.0013234 | Momentary | FALSE | FALSE | Not_TMED_Event | 1943
BAYAMON | 2022-01-15 18:00 | 2022-01-15 18:01 | 1647 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22011500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-15 | 1647 | keep | 0 | Jan | 2022 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
SAN JUAN | 2022-01-15 18:05 | 2022-01-16 10:07 | 45 | 016:02 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22011500102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 962 | 2022-01-15 | 43290 | keep | 0 | Jan | 2022 | 0.029485 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
PONCE | 2022-01-15 18:09 | 2022-01-15 18:27 | 475 | 000:18 | P | DESGANCHE | SE RETIRO RAMA DE PALMAS Y SE CERRO MACHETES | P22011500057 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 18 | 2022-01-15 | 8550 | keep | 0 | Jan | 2022 | 0.0058234 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-01-15 18:23 | 2022-01-16 00:31 | 15 | 006:08 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA | B22011500094 | New_Event | Service Transformer Failure | Include | Include | Equipment | 368 | 2022-01-15 | 5520 | keep | 0 | Jan | 2022 | 0.0037596 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2022-01-15 18:46 | 2022-01-15 20:31 | 75 | 001:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR GLOBO | P22011500059 | New_Event |  |  | Include | Wildlife | 105 | 2022-01-15 | 7875 | keep | 0 | Jan | 2022 | 0.0053636 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
FAJARDO | 2022-01-15 19:05 | 2022-01-15 20:18 | 12 | 001:13 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L NO CAUSA | R22011500202 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2022-01-15 | 876 | keep | 0 | Jan | 2022 | 0.00059664 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-01-15 19:46 | 2022-01-16 10:30 | 55 | 014:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 40 EN C/L RETIRO LINEA VACANTE | C22011500117 | New_Event | Wire Down | Include | Include | Equipment | 884 | 2022-01-15 | 48620 | keep | 0 | Jan | 2022 | 0.033115 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CAGUAS | 2022-01-15 19:52 | 2022-01-16 09:07 | 67 | 013:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE X AVE | C22011500118 | New_Event |  |  | Include | Wildlife | 795 | 2022-01-15 | 53265 | keep | 0 | Jan | 2022 | 0.036279 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
VEGA BAJA | 2022-01-15 20:06 | 2022-01-16 17:00 | 30 | 020:54 | P | CABLE SOTERRADO AVERIADO | MEDIANTE GOI BY-220116-01 SE REPARO TRAMO SOTERRADO AVERIADO | B22011500124 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1254 | 2022-01-15 | 37620 | keep | 0 | Jan | 2022 | 0.025623 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-01-15 20:36 | 2022-01-16 00:26 | 2858 | 003:50 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN RISER | B22011500109 | New_Event | Cutout Failure | Include | Include | Equipment | 230 | 2022-01-15 | 657340 | keep | 0 | Jan | 2022 | 0.44771 | 0.0019466 | Sustained | FALSE | FALSE | Not_TMED_Event | 2858
FAJARDO | 2022-01-15 21:03 | 2022-01-15 21:04 | 2286 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22011500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-15 | 2286 | keep | 0 | Jan | 2022 | 0.001557 | 0.001557 | Momentary | FALSE | FALSE | Not_TMED_Event | 2286
CANOVANAS | 2022-01-15 21:05 | 2022-01-15 22:46 | 10 | 001:41 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR AVERIADO DE 25 X 25KVA | R22011500206 | New_Event | Service Transformer Failure | Include | Include | Equipment | 101 | 2022-01-15 | 1010 | keep | 0 | Jan | 2022 | 0.00068791 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-01-15 21:10 | 2022-01-16 00:54 | 50 | 003:44 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R22011500209 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2022-01-15 | 11200 | keep | 0 | Jan | 2022 | 0.0076283 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-01-15 23:29 | 2022-01-16 09:41 | 35 | 010:12 | P | DESGANCHE | 1 X 50 EN C/L | C22011500133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 612 | 2022-01-15 | 21420 | keep | 0 | Jan | 2022 | 0.014589 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-01-16 00:45 | 2022-01-16 00:47 | 946 | 000:02 | T | DESGANCHE | CARGA TRANSFERIDA AL 1525-05 INTERRUPTOR DISPARO Y SE CERRO POR CONTROL | S22011600001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-01-16 | 1892 | keep | 0 | Jan | 2022 | 0.0012886 | 0.00064432 | Momentary | FALSE | FALSE | Not_TMED_Event | 946
BAYAMON | 2022-01-16 00:45 | 2022-01-16 00:47 | 937 | 000:02 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL LLEVA LA CARGA 1525-02 | S22011600001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-01-16 | 1874 | keep | 0 | Jan | 2022 | 0.0012764 | 0.00063819 | Momentary | FALSE | FALSE | Not_TMED_Event | 937
BAYAMON | 2022-01-16 01:02 | 2022-01-16 09:27 | 50 | 008:25 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22011600005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 505 | 2022-01-16 | 25250 | keep | 0 | Jan | 2022 | 0.017198 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-01-16 03:10 | 2022-01-16 10:52 | 50 | 007:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR IGUANA | P22011600002 | New_Event |  |  | Include | Wildlife | 462 | 2022-01-16 | 23100 | keep | 0 | Jan | 2022 | 0.015733 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-01-16 03:34 | 2022-01-16 11:16 | 35 | 007:42 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO CAUSA | C22011600003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 462 | 2022-01-16 | 16170 | keep | 0 | Jan | 2022 | 0.011013 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BARRANQUITAS | 2022-01-16 03:34 | 2022-01-16 09:30 | 8 | 005:56 | P | PARARRAYOS DEFECTUOSO | 1 X 8 EN XMR REMPLAZO PARARRAYO E INSTALO HOT CLAMP | C22011500114 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 356 | 2022-01-16 | 2848 | keep | 0 | Jan | 2022 | 0.0019398 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-01-16 04:18 | 2022-01-16 04:19 | 31 | 000:01 | T | NO SE REPORTO CAUSA | INTERRUPTOR DISPARO Y SE CERRO POR CONTROL | B22011600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-16 | 31 | keep | 0 | Jan | 2022 | 2.1114e-05 | 2.1114e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 31
MAYAGÃœEZ | 2022-01-16 04:38 | 2022-01-16 04:39 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22011600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-16 | 1097 | keep | 0 | Jan | 2022 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
VEGA BAJA | 2022-01-16 05:18 | 2022-01-16 05:19 | 2704 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22011600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-16 | 2704 | keep | 0 | Jan | 2022 | 0.0018417 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
CANOVANAS | 2022-01-16 05:19 | 2022-01-16 08:44 | 40 | 003:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE X AVE | R22011600002 | New_Event |  |  | Include | Wildlife | 205 | 2022-01-16 | 8200 | keep | 0 | Jan | 2022 | 0.005585 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-01-16 05:32 | 2022-01-16 10:56 | 100 | 005:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L REMPLAZO CAJA AVERIADA | C22011600007 | New_Event | Cutout Failure | Include | Include | Equipment | 324 | 2022-01-16 | 32400 | keep | 0 | Jan | 2022 | 0.022067 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-01-16 06:43 | 2022-01-16 11:17 | 75 | 004:34 | P | DESGANCHE | 2 X 40 EN C/L | C22011600008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 274 | 2022-01-16 | 20550 | keep | 0 | Jan | 2022 | 0.013997 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2022-01-16 07:15 | 2022-01-16 11:50 | 48 | 004:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L REMPLAZO CAJA AVERIADA | C22011600011 | New_Event | Cutout Failure | Include | Include | Equipment | 275 | 2022-01-16 | 13200 | keep | 0 | Jan | 2022 | 0.0089905 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
MAYAGÃœEZ | 2022-01-16 07:33 | 2022-01-16 15:32 | 40 | 007:59 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22011600006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 479 | 2022-01-16 | 19160 | keep | 0 | Jan | 2022 | 0.01305 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-01-16 07:40 | 2022-01-16 08:57 | 100 | 001:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN C/L CRUCE X AVE | R22011600003 | New_Event |  |  | Include | Wildlife | 77 | 2022-01-16 | 7700 | keep | 0 | Jan | 2022 | 0.0052444 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-01-16 07:46 | 2022-01-16 10:07 | 80 | 002:21 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA PERSONAL INDICO NO ENCONTRO CAUSA | M22011600008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 141 | 2022-01-16 | 11280 | keep | 0 | Jan | 2022 | 0.0076828 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-01-16 08:16 | 2022-01-16 08:17 | 325 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | B22011600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-16 | 325 | keep | 0 | Jan | 2022 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
CANOVANAS | 2022-01-16 08:33 | 2022-01-16 08:34 | 2708 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | R22011600004 | New_Event |  |  | Include | Wildlife | 1 | 2022-01-16 | 2708 | keep | 0 | Jan | 2022 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
SAN JUAN | 2022-01-16 08:34 | 2022-01-16 08:38 | 3718 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA | S22011600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-01-16 | 14872 | keep | 0 | Jan | 2022 | 0.010129 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
CANOVANAS | 2022-01-16 08:34 | 2022-01-16 17:07 | 32 | 008:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN C/L CRUCE X AVE | R22011600023 | 1st_after_momentary |  |  | Include | Wildlife | 513 | 2022-01-16 | 16416 | keep | 0 | Jan | 2022 | 0.011181 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
CANOVANAS | 2022-01-16 08:34 | 2022-01-16 10:03 | 4 | 001:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REMPLAZAR BARRA DE PEDESTAL | R22011500183 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 89 | 2022-01-16 | 356 | keep | 0 | Jan | 2022 | 0.00024247 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-01-16 08:36 | 2022-01-16 12:29 | 115 | 003:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE LEVANTO NEUTRAL PRIMARIO | B22011600006 | New_Event | Wire Down | Include | Include | Equipment | 233 | 2022-01-16 | 26795 | keep | 0 | Jan | 2022 | 0.01825 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
SAN JUAN | 2022-01-16 08:55 | 2022-01-16 12:28 | 40 | 003:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN RISER Y 1 SMU 20 DE 25AMP EN EL SU - A REMPLAZO BASE DEL SMU | R22011600007 | New_Event | Cutout Failure | Include | Include | Equipment | 213 | 2022-01-16 | 8520 | keep | 0 | Jan | 2022 | 0.0058029 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-01-16 09:04 | 2022-01-16 12:44 | 40 | 003:40 | P | DESGANCHE | 1 X 40 EN C/L | C22011600032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2022-01-16 | 8800 | keep | 0 | Jan | 2022 | 0.0059936 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-01-16 09:08 | 2022-01-16 12:28 | 200 | 003:20 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P22011600027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 200 | 2022-01-16 | 40000 | keep | 0 | Jan | 2022 | 0.027244 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-01-16 09:10 | 2022-01-16 16:43 | 80 | 007:33 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22011600017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 453 | 2022-01-16 | 36240 | keep | 0 | Jan | 2022 | 0.024683 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-01-16 09:55 | 2022-01-16 09:56 | 651 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | B22011600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-16 | 651 | keep | 0 | Jan | 2022 | 0.00044339 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
VEGA BAJA | 2022-01-16 10:00 | 2022-01-16 11:30 | 893 | 001:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A LINEA | B22011600015 | New_Event | Wire Down | Include | Include | Equipment | 90 | 2022-01-16 | 80370 | keep | 0 | Jan | 2022 | 0.05474 | 0.00060822 | Sustained | FALSE | FALSE | Not_TMED_Event | 893
SAN JUAN | 2022-01-16 10:01 | 2022-01-16 11:59 | 10 | 001:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN RISER SE REMPLAZO CAJA PRIMARIA Y SE REPARO BAJANTE PRIMARIO DE LINEA A CAJA | S22011600027 | New_Event | Cutout Failure | Include | Include | Equipment | 118 | 2022-01-16 | 1180 | keep | 0 | Jan | 2022 | 0.00080369 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-01-16 10:07 | 2022-01-16 10:17 | 1192 | 000:10 | T | TRANSFORMADOR AVERIADO | SE ABRIO INTERRUPTOR A PETICION DE WILFREDO HERNANDEZ PARA SECCIONALIZAR CONVERTIDOR PRENDIDO EN FUEGO | M22011600024 | New_Event | Service Transformer Failure | Include | Include | Equipment | 10 | 2022-01-16 | 11920 | keep | 0 | Jan | 2022 | 0.0081187 | 0.00081187 | Sustained | FALSE | FALSE | Not_TMED_Event | 1192
BARRANQUITAS | 2022-01-16 10:07 | 2022-01-16 13:35 | 25 | 003:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | C22011600037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2022-01-16 | 5200 | keep | 0 | Jan | 2022 | 0.0035417 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2022-01-16 10:17 | 2022-01-16 10:41 | 80 | 000:24 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA PERSONAL INDICO NO ENCONTRO CAUSA | M22011600008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 24 | 2022-01-16 | 1920 | keep | 0 | Jan | 2022 | 0.0013077 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-01-16 10:17 | 2022-01-17 21:32 | 500 | 035:15 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO CONVERTIDOR AVERIADO | M22011600008 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 2115 | 2022-01-16 | 1057500 | keep | 0 | Jan | 2022 | 0.72026 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-01-16 10:21 | 2022-01-16 10:57 | 10 | 000:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22011500123 | New_Event | Secondary Wire Down | Include | Include | Equipment | 36 | 2022-01-16 | 360 | keep | 0 | Jan | 2022 | 0.00024519 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-01-16 10:43 | 2022-01-16 11:00 | 9 | 000:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA DESPEGAR GUY DE BUSHING SECUNDARIO | B22011400118 | New_Event |  |  | Include | Wildlife | 17 | 2022-01-16 | 153 | keep | 0 | Jan | 2022 | 0.00010421 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-01-16 10:55 | 2022-01-16 12:37 | 80 | 001:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22011600040 | New_Event | Bad Weather | Include | Include | Weather | 102 | 2022-01-16 | 8160 | keep | 0 | Jan | 2022 | 0.0055577 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-01-16 10:57 | 2022-01-16 12:14 | 30 | 001:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | B22011600020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2022-01-16 | 2310 | keep | 0 | Jan | 2022 | 0.0015733 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-01-16 10:58 | 2022-01-16 10:59 | 3 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22011600012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-16 | 3 | keep | 0 | Jan | 2022 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-01-16 10:58 | 2022-01-16 10:59 | 1 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22011600013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-16 | 1 | keep | 0 | Jan | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-01-16 10:58 | 2022-01-16 10:59 | 4 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22011600013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-16 | 4 | keep | 0 | Jan | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2022-01-16 11:16 | 2022-01-16 11:17 | 5630 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22011600044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-16 | 5630 | keep | 0 | Jan | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
BAYAMON | 2022-01-16 11:17 | 2022-01-16 13:13 | 10 | 001:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA Y REALIZAR DESGANCHE | S22011500119 | New_Event | Secondary Wire Down | Include | Include | Equipment | 116 | 2022-01-16 | 1160 | keep | 0 | Jan | 2022 | 0.00079007 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-16 11:17 | 2022-01-16 13:12 | 110 | 001:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | B22011600021 | New_Event |  |  | Include | Wildlife | 115 | 2022-01-16 | 12650 | keep | 0 | Jan | 2022 | 0.0086159 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
HUMACAO | 2022-01-16 11:29 | 2022-01-16 13:35 | 65 | 002:06 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | C22011600045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2022-01-16 | 8190 | keep | 0 | Jan | 2022 | 0.0055782 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CANOVANAS | 2022-01-16 11:31 | 2022-01-16 14:32 | 60 | 003:01 | P | PARARRAYOS DEFECTUOSO | 3 SMU 20 DE 100 AMP REMPLAZO 3 PARARRAYOS EN EL SU - 7B | R22011600015 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 181 | 2022-01-16 | 10860 | keep | 0 | Jan | 2022 | 0.0073967 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-01-16 11:35 | 2022-01-16 15:01 | 7 | 003:26 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | R22011600016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 206 | 2022-01-16 | 1442 | keep | 0 | Jan | 2022 | 0.00098214 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-01-16 12:00 | 2022-01-16 12:43 | 1 | 000:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | B22011600025 | New_Event |  |  | Include | Wildlife | 43 | 2022-01-16 | 43 | keep | 0 | Jan | 2022 | 2.9287e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-01-16 12:01 | 2022-01-16 20:36 | 1 | 008:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA DE 100 AMPERES | A22011600005 | New_Event | Cutout Failure | Include | Include | Equipment | 515 | 2022-01-16 | 515 | keep | 0 | Jan | 2022 | 0.00035076 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-01-16 12:13 | 2022-01-16 15:44 | 60 | 003:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO NEUTRAL PRIMARIO PARTIDO | A22011600008 | New_Event | Wire Down | Include | Include | Equipment | 211 | 2022-01-16 | 12660 | keep | 0 | Jan | 2022 | 0.0086227 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-01-16 12:40 | 2022-01-16 13:19 | 1 | 000:39 | P | NO SE REPORTO CAUSA | 1 X 8 EN BANCO DE TRANSFORMADORES | S22011600059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 39 | 2022-01-16 | 39 | keep | 0 | Jan | 2022 | 2.6563e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-01-16 12:40 | 2022-01-16 12:41 | 2106 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO | R22011600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-16 | 2106 | keep | 0 | Jan | 2022 | 0.0014344 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
ARECIBO | 2022-01-16 12:41 | 2022-01-16 15:31 | 50 | 002:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA INFORMA PERSONAL QUE SE NECESITA REALIZAR DESGANCHE MASIVO | A22011600010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2022-01-16 | 8500 | keep | 0 | Jan | 2022 | 0.0057893 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-01-16 12:48 | 2022-01-16 15:57 | 40 | 003:09 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22011600029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 189 | 2022-01-16 | 7560 | keep | 0 | Jan | 2022 | 0.0051491 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-01-16 12:53 | 2022-01-16 15:23 | 105 | 002:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C22011600055 | New_Event |  |  | Include | Wildlife | 150 | 2022-01-16 | 15750 | keep | 0 | Jan | 2022 | 0.010727 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
SAN JUAN | 2022-01-16 13:13 | 2022-01-16 19:24 | 10 | 006:11 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR SE REALIZO DESGANCHE | S22011600071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 371 | 2022-01-16 | 3710 | keep | 0 | Jan | 2022 | 0.0025269 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-01-16 13:19 | 2022-01-16 13:20 | 10211 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR 1206-03 LLEVANDO CARGA 1204-05 | S22011600000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-01-16 | 10211 | keep | 0 | Jan | 2022 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2022-01-16 13:19 | 2022-01-16 13:20 | 4133 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR 1206-03 LLEVANDO CARGA 1204-05 | S22011600000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2022-01-16 | 4133 | keep | 0 | Jan | 2022 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2022-01-16 13:20 | 2022-01-16 16:20 | 200 | 003:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO EN TRONCAL | S22011600123 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 180 | 2022-01-16 | 36000 | keep | 0 | Jan | 2022 | 0.024519 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-01-16 13:20 | 2022-01-16 18:25 | 1 | 005:05 | P | NO SE REPORTO CAUSA | 1 X 8 EN BANCO DE TRANSFORMADORES | S22011600059 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 305 | 2022-01-16 | 305 | keep | 0 | Jan | 2022 | 0.00020773 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-01-16 13:23 | 2022-01-16 15:07 | 40 | 001:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR GLOBO | P22011600035 | New_Event |  |  | Include | Wildlife | 104 | 2022-01-16 | 4160 | keep | 0 | Jan | 2022 | 0.0028334 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-01-16 13:44 | 2022-01-16 14:27 | 60 | 000:43 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | B22011600033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 43 | 2022-01-16 | 2580 | keep | 0 | Jan | 2022 | 0.0017572 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-01-16 13:45 | 2022-01-16 13:47 | 1180 | 000:02 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 2 VECES Y QUEDO FUERA SE LE REALIZO PRUEBA POR CONTROL | B22011600035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-16 | 2360 | keep | 0 | Jan | 2022 | 0.0016074 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
SAN JUAN | 2022-01-16 14:00 | 2022-01-16 14:02 | 1447 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1112-04 LLEVANDO CARGA 1409-09 Y 1409-12 | S22011600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-16 | 2894 | keep | 0 | Jan | 2022 | 0.0019711 | 0.00098555 | Momentary | FALSE | FALSE | Not_TMED_Event | 1447
SAN JUAN | 2022-01-16 14:00 | 2022-01-16 14:02 | 266 | 000:02 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1112-04 LLEVANDO CARGA 1419-09 Y 1419-12 | S22011600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-16 | 532 | keep | 0 | Jan | 2022 | 0.00036234 | 0.00018117 | Momentary | FALSE | FALSE | Not_TMED_Event | 266
SAN JUAN | 2022-01-16 14:00 | 2022-01-16 14:02 | 73 | 000:02 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1112-04 LLEVANDO CARGA 1419-09 Y 1419-12 | S22011600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-01-16 | 146 | keep | 0 | Jan | 2022 | 9.944e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
MAYAGÃœEZ | 2022-01-16 14:12 | 2022-01-16 17:50 | 25 | 003:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEAS CRUZADAS | M22011600059 | New_Event | Wire Down | Include | Include | Equipment | 218 | 2022-01-16 | 5450 | keep | 0 | Jan | 2022 | 0.003712 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-01-16 14:18 | 2022-01-17 10:17 | 100 | 019:59 | P | DESGANCHE | 2X100 EN CORTE DE LINEA | S22011600125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1199 | 2022-01-16 | 119900 | keep | 0 | Jan | 2022 | 0.081663 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-01-16 14:21 | 2022-01-16 16:40 | 6 | 002:19 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR RAMA | P22011600037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2022-01-16 | 834 | keep | 0 | Jan | 2022 | 0.00056803 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-01-16 14:29 | 2022-01-16 20:33 | 40 | 006:04 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22011600060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 364 | 2022-01-16 | 14560 | keep | 0 | Jan | 2022 | 0.0099167 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-01-16 14:32 | 2022-01-16 15:46 | 1061 | 001:14 | T | NO SE REPORTO CAUSA | SE ABRIO INTERRUPTOR FUSIBLE FUNDIDO EN LA ALTA DE TRANSFORMADOR SE TRANSFIRIO 40% CARGA AL 1652-04 | S21011600129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 74 | 2022-01-16 | 78514 | keep | 0 | Jan | 2022 | 0.053476 | 0.00072264 | Sustained | FALSE | FALSE | Not_TMED_Event | 1061
SAN JUAN | 2022-01-16 14:32 | 2022-01-16 15:15 | 998 | 000:43 | T | NO SE REPORTO CAUSA | SE ABRIO INTERRUPTOR FUSIBLE FUNDIDO EN LA ALTA DE TRANSFORMADOR SE TRANSFIRIO CARGA AL 1652-05 | S21011600129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 43 | 2022-01-16 | 42914 | keep | 0 | Jan | 2022 | 0.029229 | 0.00067973 | Sustained | FALSE | FALSE | Not_TMED_Event | 998
SAN JUAN | 2022-01-16 14:33 | 2022-01-16 15:51 | 1397 | 001:18 | T | NO SE REPORTO CAUSA | SE ABRIO INTERRUPTOR FUSIBLE FUNDIDO EN LA ALTA DE TRANSFORMADOR SE TRANSFIRIO CARGA AL 1335-04 | S21011600129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2022-01-16 | 108966 | keep | 0 | Jan | 2022 | 0.074216 | 0.00095149 | Sustained | FALSE | FALSE | Not_TMED_Event | 1397
CANOVANAS | 2022-01-16 15:14 | 2022-01-16 16:19 | 50 | 001:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN C/L CRUCE X AVE | R22011600020 | New_Event |  |  | Include | Wildlife | 65 | 2022-01-16 | 3250 | keep | 0 | Jan | 2022 | 0.0022136 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-01-16 15:15 | 2022-01-16 20:28 | 150 | 005:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22011600064 | New_Event | Wire Down | Include | Include | Equipment | 313 | 2022-01-16 | 46950 | keep | 0 | Jan | 2022 | 0.031977 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-01-16 15:19 | 2022-01-16 17:14 | 100 | 001:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22011600014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2022-01-16 | 11500 | keep | 0 | Jan | 2022 | 0.0078326 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-01-16 15:46 | 2022-01-16 16:12 | 637 | 000:26 | P | NO SE REPORTO CAUSA | SE TRANSFIRIO 60% DE CARGA RESTANTE AL 1335-01 POR FUSIBLE FUNDIDO EN LA ALTA DE TRANSFORMADOR 100% EN SERVICIO | S21011600129 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 26 | 2022-01-16 | 16562 | keep | 0 | Jan | 2022 | 0.01128 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-01-16 15:57 | 2022-01-16 15:58 | 3070 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B22011600000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-16 | 3070 | keep | 0 | Jan | 2022 | 0.002091 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-01-16 15:58 | 2022-01-16 19:35 | 40 | 003:37 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B22011600029 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 217 | 2022-01-16 | 8680 | keep | 0 | Jan | 2022 | 0.0059119 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-01-16 16:00 | 2022-01-16 20:05 | 7 | 004:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR REMPLAZO CAJA QUEMADA | R22011600021 | New_Event | Cutout Failure | Include | Include | Equipment | 245 | 2022-01-16 | 1715 | keep | 0 | Jan | 2022 | 0.0011681 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-01-16 16:03 | 2022-01-16 19:45 | 3 | 003:42 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 15 KVA X 25 KVA | C22011600062 | New_Event | Service Transformer Failure | Include | Include | Equipment | 222 | 2022-01-16 | 666 | keep | 0 | Jan | 2022 | 0.00045361 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2022-01-16 16:28 | 2022-01-16 16:29 | 3296 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C22011600065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-16 | 3296 | keep | 0 | Jan | 2022 | 0.0022449 | 0.0022449 | Momentary | FALSE | FALSE | Not_TMED_Event | 3296
MAYAGÃœEZ | 2022-01-16 16:42 | 2022-01-16 18:57 | 200 | 002:15 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA REQUIERE DESGANCHE | M22011600080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2022-01-16 | 27000 | keep | 0 | Jan | 2022 | 0.01839 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-01-16 16:51 | 2022-01-17 10:20 | 1 | 017:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22011600083 | New_Event | Bad Weather | Include | Include | Weather | 1049 | 2022-01-16 | 1049 | keep | 0 | Jan | 2022 | 0.00071447 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-01-16 17:00 | 2022-01-16 18:08 | 40 | 001:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ABIERTO | M22011600085 | New_Event | Wire Down | Include | Include | Equipment | 68 | 2022-01-16 | 2720 | keep | 0 | Jan | 2022 | 0.0018526 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-01-16 17:01 | 2022-01-16 17:02 | 1417 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22011600086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-16 | 1417 | keep | 0 | Jan | 2022 | 0.00096511 | 0.00096511 | Momentary | FALSE | FALSE | Not_TMED_Event | 1417
MAYAGÃœEZ | 2022-01-16 17:03 | 2022-01-17 07:15 | 50 | 014:12 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22011600088 | New_Event | Bad Weather | Include | Include | Weather | 852 | 2022-01-16 | 42600 | keep | 0 | Jan | 2022 | 0.029015 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-01-16 17:06 | 2022-01-16 20:05 | 40 | 002:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN C/L CRUCE X AVE | R22011600026 | New_Event |  |  | Include | Wildlife | 179 | 2022-01-16 | 7160 | keep | 0 | Jan | 2022 | 0.0048766 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-01-16 17:30 | 2022-01-16 17:31 | 766 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 50% DE SU CARGA POR EL 1909-07, SOLO LLEVA EL 1709-05 | B22011600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-16 | 766 | keep | 0 | Jan | 2022 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2022-01-16 17:30 | 2022-01-16 17:31 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | CARGA TRANSFERIDA AL 1709-03 RECERRO INTERRUPTOR | B22011600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-16 | 2364 | keep | 0 | Jan | 2022 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
MAYAGÃœEZ | 2022-01-16 18:08 | 2022-01-16 19:25 | 51 | 001:17 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 7902-03 AUTORIZADO POR ING LUIS FENEQUE QUE ESTA LLEVANDO LA CARGA DEL 7902-02 PARA REPARAR PUENTE PRIMARIO EN EL 7902-02 | M22011600109 | Additional_clients | Wire Down | Include | Include | Equipment | 77 | 2022-01-16 | 3927 | keep | 0 | Jan | 2022 | 0.0026747 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-01-16 18:08 | 2022-01-16 19:25 | 721 | 001:17 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR AUTORIZADO POR ING LUIS FENEQUE ESTA LLEVANDO LA CARGA DEL 7902-02 Y SE VA A CERRAR UN PUENTE ABIERTO EN EL 7902-02 | M22011600109 | New_Event | Wire Down | Include | Include | Equipment | 77 | 2022-01-16 | 55517 | keep | 0 | Jan | 2022 | 0.037812 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
BAYAMON | 2022-01-16 18:15 | 2022-01-16 18:16 | 222 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO | S22011600000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-01-16 | 222 | keep | 0 | Jan | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-01-16 18:15 | 2022-01-16 18:16 | 4456 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | CARGA TRASFERIDA AL 1907-03 INTERRUPTOR RECERRO | S22011600000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-01-16 | 4456 | keep | 0 | Jan | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
BAYAMON | 2022-01-16 18:16 | 2022-01-17 09:02 | 45 | 014:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L 2 X 15 EN XMR SE REMPLAZO CAJA PRIMARIA Y PARARRAYOS | S22011600217 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 886 | 2022-01-16 | 39870 | keep | 0 | Jan | 2022 | 0.027155 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-01-16 18:46 | 2022-01-16 21:11 | 4 | 002:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN XMR REMPLAZO PORTAFUSIBLE | R22011600039 | New_Event | Cutout Failure | Include | Include | Equipment | 145 | 2022-01-16 | 580 | keep | 0 | Jan | 2022 | 0.00039504 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2022-01-16 18:55 | 2022-01-16 21:46 | 15 | 002:51 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22011600120 | New_Event | Bad Weather | Include | Include | Weather | 171 | 2022-01-16 | 2565 | keep | 0 | Jan | 2022 | 0.001747 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-01-16 19:04 | 2022-01-17 10:40 | 30 | 015:36 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22011600051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 936 | 2022-01-16 | 28080 | keep | 0 | Jan | 2022 | 0.019125 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-01-16 20:10 | 2022-01-16 22:35 | 80 | 002:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M22011600130 | New_Event | Bad Weather | Include | Include | Weather | 145 | 2022-01-16 | 11600 | keep | 0 | Jan | 2022 | 0.0079007 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-01-16 20:17 | 2022-01-17 07:15 | 15 | 010:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22011700022 | New_Event | Bad Weather | Include | Include | Weather | 658 | 2022-01-16 | 9870 | keep | 0 | Jan | 2022 | 0.0067224 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-01-16 20:19 | 2022-01-16 20:20 | 450 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22011600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-16 | 450 | keep | 0 | Jan | 2022 | 0.00030649 | 0.00030649 | Momentary | FALSE | FALSE | Not_TMED_Event | 450
SAN JUAN | 2022-01-16 20:52 | 2022-01-16 22:16 | 15 | 001:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S22011600221 | New_Event | Secondary Wire Down | Include | Include | Equipment | 84 | 2022-01-16 | 1260 | keep | 0 | Jan | 2022 | 0.00085818 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-01-16 21:25 | 2022-01-17 09:53 | 5 | 012:28 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | C22011600070 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 748 | 2022-01-16 | 3740 | keep | 0 | Jan | 2022 | 0.0025473 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-01-16 21:30 | 2022-01-17 13:01 | 12 | 015:31 | P | NO SE REPORTO CAUSA | 1X25 EN CORTE DE LINEA | S22011600228 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 931 | 2022-01-16 | 11172 | keep | 0 | Jan | 2022 | 0.0076092 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2022-01-16 22:47 | 2022-01-17 05:48 | 20 | 007:01 | P | DESGANCHE | 1 X 30 EN C/L | C22011600071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 421 | 2022-01-16 | 8420 | keep | 0 | Jan | 2022 | 0.0057348 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-01-16 23:50 | 2022-01-17 00:33 | 2705 | 000:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES PARA REPARAR NEUTRAL PRIMARIO ROTO | M22011600139 | New_Event | Wire Down | Include | Include | Equipment | 43 | 2022-01-16 | 116315 | keep | 0 | Jan | 2022 | 0.079222 | 0.0018424 | Sustained | FALSE | FALSE | Not_TMED_Event | 2705
CAGUAS | 2022-01-16 23:56 | 2022-01-17 12:26 | 40 | 012:30 | P | DESGANCHE | ABRIO C/L PARA REALIZAR DESGANCHE | C22011600072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 750 | 2022-01-16 | 30000 | keep | 0 | Jan | 2022 | 0.020433 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-01-17 00:33 | 2022-01-17 00:34 | 4882 | 000:01 | T | ERROR HUMANO | RECIERRE DE INTERRUPTOR | M22011700012 | New_Event | Human Error | Include | Include | Other | 1 | 2022-01-17 | 4882 | keep | 0 | Jan | 2022 | 0.0033251 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
VEGA BAJA | 2022-01-17 00:34 | 2022-01-17 08:11 | 35 | 007:37 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22011700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 457 | 2022-01-17 | 15995 | keep | 0 | Jan | 2022 | 0.010894 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2022-01-17 00:35 | 2022-01-17 00:37 | 4882 | 000:02 | T | ERROR HUMANO | SE ABRIO INTERRUPTOR POR SEGURIDAD A PETICION DE KEVIN MERCADO PARA PODER ABRIR MACHETE QUE AL CERRARLO QUEDO FUERA DE SU LUGAR Y PODERLO CERRAR CORRECTAMENTE | M22011700012 | 1st_after_momentary | Human Error | Include | Include | Other | 2 | 2022-01-17 | 9764 | keep | 0 | Jan | 2022 | 0.0066502 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
FAJARDO | 2022-01-17 01:27 | 2022-01-17 08:45 | 9 | 007:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR REPTIL | R22011700001 | New_Event |  |  | Include | Wildlife | 438 | 2022-01-17 | 3942 | keep | 0 | Jan | 2022 | 0.0026849 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-01-17 04:34 | 2022-01-17 04:35 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22011700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-01-17 | 990 | keep | 0 | Jan | 2022 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
BARRANQUITAS | 2022-01-17 05:48 | 2022-01-17 05:49 | 1604 | 000:01 | T | DESGANCHE | RECIERRE | C22011700000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-01-17 | 1604 | keep | 0 | Jan | 2022 | 0.0010925 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-01-17 05:49 | 2022-01-17 19:03 | 20 | 013:14 | P | DESGANCHE | 1 X 30 EN C/L | C22011600071 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 794 | 2022-01-17 | 15880 | keep | 0 | Jan | 2022 | 0.010816 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-01-17 05:49 | 2022-01-17 14:42 | 100 | 008:53 | P | DESGANCHE | 2 X 100 EN C/L | C22011700014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 533 | 2022-01-17 | 53300 | keep | 0 | Jan | 2022 | 0.036302 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-01-17 06:36 | 2022-01-17 09:32 | 25 | 002:56 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA DE PALMA SOBRE LAS LINEAS | A22011700003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2022-01-17 | 4400 | keep | 0 | Jan | 2022 | 0.0029968 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-01-17 07:07 | 2022-01-17 10:24 | 2 | 003:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 8 EN TRANSFORMADOR CRUCE DE BUSHING PRIMARIO EN POR ROHEDOR | P22011700007 | New_Event |  |  | Include | Wildlife | 197 | 2022-01-17 | 394 | keep | 0 | Jan | 2022 | 0.00026835 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-01-17 07:15 | 2022-01-17 07:16 | 4664 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR MAL TIEMPO VIENTOS FUERTES | M22011700020 | Additional_clients | Bad Weather | Include | Include | Weather | 1 | 2022-01-17 | 4664 | keep | 0 | Jan | 2022 | 0.0031766 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-01-17 07:16 | 2022-01-17 10:05 | 15 | 002:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22011700022 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 169 | 2022-01-17 | 2535 | keep | 0 | Jan | 2022 | 0.0017266 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-01-17 07:16 | 2022-01-17 10:20 | 50 | 003:04 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22011600088 | New_Event | Bad Weather | Include | Include | Weather | 184 | 2022-01-17 | 9200 | keep | 0 | Jan | 2022 | 0.0062661 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-01-17 07:40 | 2022-01-17 09:48 | 3 | 002:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTA FUSIBLE AVERIADO | P22011700009 | New_Event | Cutout Failure | Include | Include | Equipment | 128 | 2022-01-17 | 384 | keep | 0 | Jan | 2022 | 0.00026154 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2022-01-17 08:09 | 2022-01-17 08:26 | 60 | 000:17 | P | SOBRECARGA | 1 X 30 EN CORTE DE LINEA | R22011700003 | New_Event | Trip Due To Overload | Include | Include | Other | 17 | 2022-01-17 | 1020 | keep | 0 | Jan | 2022 | 0.00069472 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-01-17 08:27 | 2022-01-17 11:46 | 70 | 003:19 | P | DESGANCHE | 1 X 30 Y 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | C22011700072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2022-01-17 | 13930 | keep | 0 | Jan | 2022 | 0.0094877 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2022-01-17 08:27 | 2022-01-17 11:46 | 25 | 003:19 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | C22011700024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2022-01-17 | 4975 | keep | 0 | Jan | 2022 | 0.0033884 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-01-17 08:34 | 2022-01-17 11:07 | 25 | 002:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22011700007 | New_Event | Bad Weather | Include | Include | Weather | 153 | 2022-01-17 | 3825 | keep | 0 | Jan | 2022 | 0.0026052 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-01-17 08:41 | 2022-01-17 10:04 | 10 | 001:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C22011700026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 83 | 2022-01-17 | 830 | keep | 0 | Jan | 2022 | 0.00056531 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-01-17 08:54 | 2022-01-17 09:34 | 6 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO BAJANTE | B22011600057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2022-01-17 | 240 | keep | 0 | Jan | 2022 | 0.00016346 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-01-17 09:02 | 2022-01-17 09:07 | 222 | 000:05 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO 1907-03 AL HACER PRUEBA EN C/L LLEVA 1909-09 | S22011600217 | New_Event | Cutout Failure | Include | Include | Equipment | 5 | 2022-01-17 | 1110 | keep | 0 | Jan | 2022 | 0.00075602 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-01-17 09:02 | 2022-01-17 09:07 | 4456 | 000:05 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO 1907-03 AL HACER PRUEBA EN C/L LLEVA 1909-09 | S22011600217 | Additional_clients | Cutout Failure | Include | Include | Equipment | 5 | 2022-01-17 | 22280 | keep | 0 | Jan | 2022 | 0.015175 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-01-17 09:07 | 2022-01-17 09:08 | 45 | 000:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L 2 X 15 EN XMR SE REMPLAZO CAJA PRIMARIA Y PARARRAYOS | S22011600217 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 1 | 2022-01-17 | 45 | keep | 0 | Jan | 2022 | 3.0649e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-01-17 09:08 | 2022-01-17 09:11 | 222 | 000:03 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO INTERRPTOR 1907-03 POR CAJA EN FUEGO LLEVA 1909-09 | S22011600217 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 3 | 2022-01-17 | 666 | keep | 0 | Jan | 2022 | 0.00045361 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-01-17 09:08 | 2022-01-17 09:11 | 4456 | 000:03 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO INTERRPTOR 1907-03 POR CAJA EN FUEGO LLEVA 1909-09 | S22011600217 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 3 | 2022-01-17 | 13368 | keep | 0 | Jan | 2022 | 0.0091049 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
HUMACAO | 2022-01-17 09:10 | 2022-01-17 09:22 | 10 | 000:12 | P | NO SE REPORTO CAUSA | 1 X15 EN XMR | C22011600066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 12 | 2022-01-17 | 120 | keep | 0 | Jan | 2022 | 8.1731e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-01-17 09:11 | 2022-01-17 10:47 | 45 | 001:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L 2 X 15 EN XMR SE REMPLAZO CAJA PRIMARIA Y PARARRAYOS | S22011600217 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 96 | 2022-01-17 | 4320 | keep | 0 | Jan | 2022 | 0.0029423 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-01-17 09:12 | 2022-01-17 15:31 | 15 | 006:19 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR Y SE REALIZO DESGANCHE | S22011700026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 379 | 2022-01-17 | 5685 | keep | 0 | Jan | 2022 | 0.003872 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-01-17 09:15 | 2022-01-17 09:16 | 3431 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DEL INTERRUPTOR VEHICULO IMPACTO POSTE | A22011700010 | New_Event |  |  | Include | Wildlife | 1 | 2022-01-17 | 3431 | keep | 0 | Jan | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
MAYAGÃœEZ | 2022-01-17 09:16 | 2022-01-17 13:55 | 10 | 004:39 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA POR LA MISMA CAPACIDAD | M22011700031 | New_Event | Service Transformer Failure | Include | Include | Equipment | 279 | 2022-01-17 | 2790 | keep | 0 | Jan | 2022 | 0.0019003 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-17 09:16 | 2022-01-17 12:01 | 60 | 002:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA VEHICULO IMPACTO POSTE | A22011700011 | 1st_after_momentary |  |  | Include | Wildlife | 165 | 2022-01-17 | 9900 | keep | 0 | Jan | 2022 | 0.0067428 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-01-17 09:16 | 2022-01-17 10:27 | 6 | 001:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR Y SE REPARO BAJANTE | B22011700016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 71 | 2022-01-17 | 426 | keep | 0 | Jan | 2022 | 0.00029015 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-01-17 09:18 | 2022-01-17 12:53 | 12 | 003:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA QUE CONTRATISTA ENCABEZARA SECUNDARIA | R22011700016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 215 | 2022-01-17 | 2580 | keep | 0 | Jan | 2022 | 0.0017572 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-01-17 09:18 | 2022-01-17 12:19 | 27 | 003:01 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR CON DERRAME DE ACEITE DE 50 KVA X 50 KVA | R22011700015 | New_Event | Service Transformer Failure | Include | Include | Equipment | 181 | 2022-01-17 | 4887 | keep | 0 | Jan | 2022 | 0.0033285 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
UTUADO | 2022-01-17 09:24 | 2022-01-17 10:04 | 2 | 000:40 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22011700012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 40 | 2022-01-17 | 80 | keep | 0 | Jan | 2022 | 5.4488e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-01-17 09:27 | 2022-01-17 09:53 | 9 | 000:26 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22011600070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 26 | 2022-01-17 | 234 | keep | 0 | Jan | 2022 | 0.00015938 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-01-17 09:44 | 2022-01-17 18:07 | 100 | 008:23 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22011700033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 503 | 2022-01-17 | 50300 | keep | 0 | Jan | 2022 | 0.034259 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-01-17 09:47 | 2022-01-17 12:03 | 70 | 002:16 | P | DESGANCHE | 1X140 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22111700030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2022-01-17 | 9520 | keep | 0 | Jan | 2022 | 0.006484 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
FAJARDO | 2022-01-17 09:50 | 2022-01-17 10:36 | 9 | 000:46 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA DEL TRANSFORMADOR | R22011700022 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 46 | 2022-01-17 | 414 | keep | 0 | Jan | 2022 | 0.00028197 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
UTUADO | 2022-01-17 09:50 | 2022-01-17 12:44 | 25 | 002:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22011700017 | New_Event | Bad Weather | Include | Include | Weather | 174 | 2022-01-17 | 4350 | keep | 0 | Jan | 2022 | 0.0029628 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-01-17 09:52 | 2022-01-17 16:25 | 1 | 006:33 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA POR LA MISMA CAPACIDAD | A22011700018 | New_Event | Service Transformer Failure | Include | Include | Equipment | 393 | 2022-01-17 | 393 | keep | 0 | Jan | 2022 | 0.00026767 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-01-17 09:56 | 2022-01-17 13:09 | 4 | 003:13 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA X 25 KVA | R22011700020 | New_Event | Service Transformer Failure | Include | Include | Equipment | 193 | 2022-01-17 | 772 | keep | 0 | Jan | 2022 | 0.00052581 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-01-17 10:05 | 2022-01-17 15:58 | 70 | 005:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | R22011700023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 353 | 2022-01-17 | 24710 | keep | 0 | Jan | 2022 | 0.01683 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
YAUCO | 2022-01-17 10:14 | 2022-01-17 12:25 | 15 | 002:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA EN TRANSFORMADOR | P22011700017 | New_Event | Cutout Failure | Include | Include | Equipment | 131 | 2022-01-17 | 1965 | keep | 0 | Jan | 2022 | 0.0013384 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-01-17 10:15 | 2022-01-17 11:34 | 2216 | 001:19 | T | ERROR HUMANO | SE ABRIO CORTE DE LINEA PARA SECCIONALIZAR CONDUCTOR EN EL SUELO Y SE CERRO POR SCADA | B22011700022 | New_Event | Human Error | Include | Include | Other | 79 | 2022-01-17 | 175064 | keep | 0 | Jan | 2022 | 0.11924 | 0.0015093 | Sustained | FALSE | FALSE | Not_TMED_Event | 2216
CANOVANAS | 2022-01-17 10:17 | 2022-01-17 12:14 | 339 | 001:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | R22011700026 | New_Event |  |  | Include | Wildlife | 117 | 2022-01-17 | 39663 | keep | 0 | Jan | 2022 | 0.027014 | 0.00023089 | Sustained | FALSE | FALSE | Not_TMED_Event | 339
SAN JUAN | 2022-01-17 10:21 | 2022-01-17 11:23 | 60 | 001:02 | P | NO SE REPORTO CAUSA | SE PATRULLO NO SE ENCONTRO CONDICION SE CERRO POR SCADA LLEVA 15% DE SU CARGA | S22011700041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 62 | 2022-01-17 | 3720 | keep | 0 | Jan | 2022 | 0.0025337 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-01-17 10:28 | 2022-01-17 15:00 | 5 | 004:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M22011700044 | New_Event | Cutout Failure | Include | Include | Equipment | 272 | 2022-01-17 | 1360 | keep | 0 | Jan | 2022 | 0.00092629 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-01-17 10:33 | 2022-01-17 11:55 | 10 | 001:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO XMR PARA REPARAR SECUNDARIA | C22011700059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 82 | 2022-01-17 | 820 | keep | 0 | Jan | 2022 | 0.0005585 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-01-17 10:34 | 2022-01-17 19:19 | 50 | 008:45 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22011700022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 525 | 2022-01-17 | 26250 | keep | 0 | Jan | 2022 | 0.017879 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-01-17 10:43 | 2022-01-17 17:30 | 11 | 006:47 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE TRANSFORMADOR 37.5 KVA A 4160 VOLTS POR OTRO IGUAL CAPACIDAD Y VOLTAJE | P22011700020 | New_Event | Service Transformer Failure | Include | Include | Equipment | 407 | 2022-01-17 | 4477 | keep | 0 | Jan | 2022 | 0.0030493 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2022-01-17 10:58 | 2022-01-17 18:27 | 10 | 007:29 | P | TRANSFORMADOR AVERIADO | SE IDENTIFICO T-83 AVERIADO | B22011700023 | New_Event | Service Transformer Failure | Include | Include | Equipment | 449 | 2022-01-17 | 4490 | keep | 0 | Jan | 2022 | 0.0030581 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-01-17 10:59 | 2022-01-17 14:00 | 85 | 003:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO | M22011700047 | New_Event | Wire Down | Include | Include | Equipment | 181 | 2022-01-17 | 15385 | keep | 0 | Jan | 2022 | 0.010479 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
CANOVANAS | 2022-01-17 11:03 | 2022-01-17 15:07 | 1 | 004:04 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | R22011700030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 244 | 2022-01-17 | 244 | keep | 0 | Jan | 2022 | 0.00016619 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1