SAN JUAN | 2023-06-02 09:17 | 2023-06-02 10:10 | 41 | 0:53 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO TRAMO SOTERRADO AVERIADO DEL SU-13 @ MH-17A SJ-230602-01 - 95% EN SERVICIO | S23060200007 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 53 | 2023-06-02 | 2173 | keep | 0 | Jun | 2023 | 0.00148 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-06-02 09:26 | 2023-06-02 10:50 | 1 | 1:24 | P | OTRAS CAUSAS | 1 X 65 EN RISER FUSIBLE PODRDIDO | A23060200077 | New_Event | Other Causes | Include | Include | Other | 84 | 2023-06-02 | 84 | keep | 0 | Jun | 2023 | 5.7212e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-06-02 09:31 | 2023-06-02 13:30 | 6 | 3:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN XMR MAL TIEMPO LLUVIAS | P23060200269 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 239 | 2023-06-02 | 1434 | keep | 0 | Jun | 2023 | 0.00097669 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2023-06-02 09:36 | 2023-06-02 12:11 | 5 | 2:35 | P | MAL TIEMPO/RAYOS | 1 X 5 EN TRANSFORMADOR DESCARGA ELECTRICA | M23060200055 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 155 | 2023-06-02 | 775 | keep | 0 | Jun | 2023 | 0.00052785 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2023-06-02 09:37 | 2023-06-02 09:38 | 2635 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR | C2306020000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-06-02 | 2635 | keep | 0 | Jun | 2023 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2023-06-02 09:38 | 2023-06-02 14:35 | 441 | 4:57 | P | CONDUCTOR ARRIADO O CRUZADO | 3 X 80 EN C/L SE RETEZO LINEAS ARRIADAS Y SE ENDEREZO POSTE PRIMARIO | C23060200052 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 297 | 2023-06-02 | 130977 | keep | 0 | Jun | 2023 | 0.089208 | 0.00030036 | Sustained | FALSE | FALSE | Not_TMED_Event | 441
VEGA BAJA | 2023-06-02 09:51 | 2023-06-02 19:31 | 1500 | 9:40 | T | LINEA DE TRANSMISION 115KV | POSTE PRIMARIO PARTIDO LINEA DE TRANSMISION CRUZADA CON LINEA DE DISTRIBUCION SE SECCIONALIZO | A23060200087 | Additional_clients | 115 kV Transmission Line Source | Include | Include | Power supply | 580 | 2023-06-02 | 870000 | keep | 0 | Jun | 2023 | 0.59255 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-06-02 09:57 | 2023-06-02 09:59 | 2020 | 0:02 | P | CAUSAS EXTERNAS | DISPARO DEL 1658-14 SE RETIRO GLOBOS DE LAS LINEAS | R23060200046 | New_Event | Damage From Public | Include | Include | Public | 2 | 2023-06-02 | 4040 | keep | 0 | Jun | 2023 | 0.0027516 | 0.0013758 | Momentary | FALSE | FALSE | Not_TMED_Event | 2020
CANOVANAS | 2023-06-02 09:57 | 2023-06-02 09:59 | 1 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR LLEVA 90% DEL 1658-13 | R23060200046 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-06-02 | 2 | keep | 0 | Jun | 2023 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-06-02 09:59 | 2023-06-02 11:14 | 1010 | 1:15 | P | CAUSAS EXTERNAS | DISPARO 90% DE LAS CARGAS X 1658-14 SE SECCIONALIZO EL ALIMENTADOR SE RETIRO GLOBOS DE LAS LINEAS | R23060200049 | 1st_after_momentary | Damage From Public | Include | Include | Public | 75 | 2023-06-02 | 75750 | keep | 0 | Jun | 2023 | 0.051593 | 0.00068791 | Sustained | FALSE | FALSE | Not_TMED_Event | 1010
MAYAGÃœEZ | 2023-06-02 10:07 | 2023-06-02 11:40 | 50 | 1:33 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS DE LAS LINEAS | P23060200089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2023-06-02 | 4650 | keep | 0 | Jun | 2023 | 0.0031671 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-06-02 10:08 | 2023-06-02 14:44 | 50 | 4:36 | P | DESGANCHE | 1 X 65 EN C/L SE DESGANCHO | S23060200090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 276 | 2023-06-02 | 13800 | keep | 0 | Jun | 2023 | 0.0093991 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-06-02 10:10 | 2023-06-02 14:14 | 20 | 4:04 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO SOTERRADO AVERIADO DEL SU-13 @ MH-17A Y SE NORMALIZARON CARGAS MEDIANTE G.O.I. SJ-230602-01 - 100% EN SERVICIO | S23060200007 | New_Event | UG Cable Fault | Include | Include | Equipment | 244 | 2023-06-02 | 4880 | keep | 0 | Jun | 2023 | 0.0033237 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-06-02 10:24 | 2023-06-02 14:50 | 70 | 4:26 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M23060200067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2023-06-02 | 18620 | keep | 0 | Jun | 2023 | 0.012682 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2023-06-02 10:33 | 2023-06-02 11:25 | 7 | 0:52 | P | OTRAS CAUSAS | 1 X 15 EN TRANSFORMADOR FUISIBLE PODRIDO | A23060200102 | New_Event | Other Causes | Include | Include | Other | 52 | 2023-06-02 | 364 | keep | 0 | Jun | 2023 | 0.00024792 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2023-06-02 10:35 | 2023-06-02 19:55 | 1 | 9:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA 1 X 50 EN CORTE DE LINEA | P23060200306 | New_Event | Cutout Failure | Include | Include | Equipment | 560 | 2023-06-02 | 560 | keep | 0 | Jun | 2023 | 0.00038141 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-06-02 10:39 | 2023-06-02 13:30 | 50 | 2:51 | P | CAUSAS EXTERNAS | 2 X 50 EN CORTE DE LINEA CAMION CAUSO CRUCE DE LINEAS | M23060200069 | New_Event | Damage From Public | Include | Include | Public | 171 | 2023-06-02 | 8550 | keep | 0 | Jun | 2023 | 0.0058234 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-06-02 10:56 | 2023-06-02 14:15 | 60 | 3:19 | P | CAUSAS EXTERNAS | 1 X 80 EN CORTE DE LINEA CAMION IMPACTO POSTE Y CRUZO LINEAS | A23060200108 | New_Event | Damage From Public | Include | Include | Public | 199 | 2023-06-02 | 11940 | keep | 0 | Jun | 2023 | 0.0081323 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-06-02 11:08 | 2023-06-02 13:22 | 140 | 2:14 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA RADIAL PARA REPARAR PUENTE ABIERTO EN LA PRIMARIA | S23060200050 | New_Event | Primary Wire Break | Include | Include | Equipment | 134 | 2023-06-02 | 18760 | keep | 0 | Jun | 2023 | 0.012777 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
BAYAMON | 2023-06-02 11:08 | 2023-06-02 12:04 | 20 | 0:56 | P | DESGANCHE | 1 X 50 EN C/ Y DESGANCHE | B23060200170 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2023-06-02 | 1120 | keep | 0 | Jun | 2023 | 0.00076283 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2023-06-02 11:09 | 2023-06-02 14:59 | 80 | 3:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN CORTE DE LINEA POR MAL TIEMPO | P23060200324 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 230 | 2023-06-02 | 18400 | keep | 0 | Jun | 2023 | 0.012532 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-06-02 11:14 | 2023-06-02 11:15 | 556 | 0:01 | P | CAUSAS EXTERNAS | SJ-23062-50 SE RETIRO GLOBO CRUZANDO LAS LINEAS | R23060200049 | New_Event | Damage From Public | Include | Include | Public | 1 | 2023-06-02 | 556 | keep | 0 | Jun | 2023 | 0.00037869 | 0.00037869 | Momentary | FALSE | FALSE | Not_TMED_Event | 556
CANOVANAS | 2023-06-02 11:15 | 2023-06-02 12:03 | 50 | 0:48 | P | CAUSAS EXTERNAS | SJ-23062-50 SE RETIRO GLOBO CRUZANDO LAS LINEAS | R23060200049 | 1st_after_momentary | Damage From Public | Include | Include | Public | 48 | 2023-06-02 | 2400 | keep | 0 | Jun | 2023 | 0.0016346 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-06-02 11:16 | 2023-06-02 13:00 | 1 | 1:44 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23060200173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2023-06-02 | 104 | keep | 0 | Jun | 2023 | 7.0834e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-06-02 11:17 | 2023-06-02 17:00 | 20 | 5:43 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | A23060200116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 343 | 2023-06-02 | 6860 | keep | 0 | Jun | 2023 | 0.0046723 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-06-02 11:18 | 2023-06-02 17:30 | 10 | 6:12 | P | DESGANCHE | 1 X 30 EN C/L ,1 X 10 EN XMR, SE CERRO PUENTES ABIERTO Y DESGANCHE | C23060200074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 372 | 2023-06-02 | 3720 | keep | 0 | Jun | 2023 | 0.0025337 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-06-02 12:07 | 2023-06-02 14:43 | 10 | 2:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REPARAR SECUNDARIA TRASPATIO | S23060200129 | New_Event | Secondary Wire Break | Include | Include | Equipment | 156 | 2023-06-02 | 1560 | keep | 0 | Jun | 2023 | 0.0010625 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-06-02 12:22 | 2023-06-02 15:22 | 1 | 3:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | P23060200357 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 180 | 2023-06-02 | 180 | keep | 0 | Jun | 2023 | 0.0001226 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-06-02 12:24 | 2023-06-02 15:15 | 51 | 2:51 | P | DESGANCHE | 1 X 40 Y 1 X 30 EN C/L DESGANCHE | R23060200114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2023-06-02 | 8721 | keep | 0 | Jun | 2023 | 0.0059398 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
YAUCO | 2023-06-02 12:24 | 2023-06-03 13:10 | 1 | 24:46 | P | MAL TIEMPO/RAYOS | 3 X 100 EN C/L MAL TIEMPO RAYOS | P23060200471 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1486 | 2023-06-02 | 1486 | keep | 0 | Jun | 2023 | 0.0010121 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-06-02 12:41 | 2023-06-02 12:42 | 1501 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B23060200184 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-02 | 1501 | keep | 0 | Jun | 2023 | 0.0010223 | 0.0010223 | Momentary | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2023-06-02 12:50 | 2023-06-02 14:47 | 25 | 1:57 | P | DESGANCHE | 1 X 40 EN C/L SE DESGANCHO | B23060200187 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2023-06-02 | 2925 | keep | 0 | Jun | 2023 | 0.0019922 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-06-02 12:53 | 2023-06-02 17:08 | 150 | 4:15 | P | DESGANCHE | 1 X 100 EN CL DESGANCHE | M23060200106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 255 | 2023-06-02 | 38250 | keep | 0 | Jun | 2023 | 0.026052 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-06-02 12:58 | 2023-06-02 18:08 | 1 | 5:10 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 20 EN CL SE RETEZO LINEA PRIMARIA | P23060200371 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 310 | 2023-06-02 | 310 | keep | 0 | Jun | 2023 | 0.00021114 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-06-02 13:04 | 2023-06-02 15:40 | 1 | 2:36 | P | NO SE REPORTO CAUSA | 1 X 40 EN MONTURA 1 X 50 EN MEDICION Y 1 X 65 EN CL | P23060200026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 156 | 2023-06-02 | 156 | keep | 0 | Jun | 2023 | 0.00010625 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-06-02 13:12 | 2023-06-03 09:44 | 40 | 20:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO VIENTO | B23060200195 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1232 | 2023-06-02 | 49280 | keep | 0 | Jun | 2023 | 0.033564 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-06-02 13:13 | 2023-06-02 13:14 | 2435 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S23050200144 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-02 | 2435 | keep | 0 | Jun | 2023 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2023-06-02 13:28 | 2023-06-02 14:43 | 35 | 1:15 | P | DESGANCHE | 1 X 30 EN C/L SE DESGANCHO | B23060200199 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2023-06-02 | 2625 | keep | 0 | Jun | 2023 | 0.0017879 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2023-06-02 13:29 | 2023-06-03 14:00 | 49 | 24:31 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L | S23060200148 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1471 | 2023-06-02 | 72079 | keep | 0 | Jun | 2023 | 0.049093 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
SAN JUAN | 2023-06-02 13:51 | 2023-06-02 13:52 | 218 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2306020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-02 | 218 | keep | 0 | Jun | 2023 | 0.00014848 | 0.00014848 | Momentary | FALSE | FALSE | Not_TMED_Event | 218
SAN JUAN | 2023-06-02 13:55 | 2023-06-02 18:03 | 610 | 4:08 | P | CAUSAS EXTERNAS | DISPARO DE INTERRUPTOR - 60% DE SU CARGA POR 1106-04 SE SECCIONALIZO POSTE PRIMARIO PARTIDO POR UN TERCERO MEDIANTE G.O.I. SJ-230602-03 - 90% DE LA CARGA TOTAL DEL FEEDER EN SERVICIO | S23060200160 | New_Event | Damage From Public | Include | Include | Public | 248 | 2023-06-02 | 151280 | keep | 0 | Jun | 2023 | 0.10304 | 0.00041547 | Sustained | FALSE | FALSE | Not_TMED_Event | 610
ARECIBO | 2023-06-02 14:24 | 2023-06-02 17:08 | 30 | 2:44 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23060200160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2023-06-02 | 4920 | keep | 0 | Jun | 2023 | 0.003351 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-06-02 14:29 | 2023-06-02 14:30 | 562 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE SUB 5801 PASTILLO FUNDIÃ“ 1 FUSIBLE | P23060200411 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-02 | 562 | keep | 0 | Jun | 2023 | 0.00038278 | 0.00038278 | Momentary | FALSE | FALSE | Not_TMED_Event | 562
PONCE | 2023-06-02 14:29 | 2023-06-02 14:30 | 688 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE SUB 5801 PASTILLO FUNDIÃ“ 1 FUSIBLE | P23060200411 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-02 | 688 | keep | 0 | Jun | 2023 | 0.00046859 | 0.00046859 | Momentary | FALSE | FALSE | Not_TMED_Event | 688
PONCE | 2023-06-02 14:29 | 2023-06-02 14:30 | 658 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE SUB 5801 PASTILLO FUNDIÃ“ 1 FUSIBLE | P23060200411 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-02 | 658 | keep | 0 | Jun | 2023 | 0.00044816 | 0.00044816 | Momentary | FALSE | FALSE | Not_TMED_Event | 658
PONCE | 2023-06-02 14:29 | 2023-06-02 14:30 | 4009 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE NO SE REPORTA CAUSA SUB 5801 PASTILLO FUNDIO 1 FUSIBLE | P23060200411 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-02 | 4009 | keep | 0 | Jun | 2023 | 0.0027305 | 0.0027305 | Momentary | FALSE | FALSE | Not_TMED_Event | 4009
BARRANQUITAS | 2023-06-02 14:34 | 2023-06-02 17:53 | 50 | 3:19 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | C23060200114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2023-06-02 | 9950 | keep | 0 | Jun | 2023 | 0.0067769 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-06-02 14:35 | 2023-06-02 19:42 | 50 | 5:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | P23060200410 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 307 | 2023-06-02 | 15350 | keep | 0 | Jun | 2023 | 0.010455 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-06-02 14:38 | 2023-06-02 15:44 | 30 | 1:06 | P | ANIMAL | 1 X 30 EN C/L CRUCE POR AVE | B23060200218 | New_Event | Animals | Include | Include | Wildlife | 66 | 2023-06-02 | 1980 | keep | 0 | Jun | 2023 | 0.0013486 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-06-02 14:44 | 2023-06-02 19:39 | 30 | 4:55 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23060200169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 295 | 2023-06-02 | 8850 | keep | 0 | Jun | 2023 | 0.0060277 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-06-02 14:45 | 2023-06-02 16:25 | 20 | 1:40 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R23060200127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2023-06-02 | 2000 | keep | 0 | Jun | 2023 | 0.0013622 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-06-02 14:50 | 2023-06-02 14:51 | 918 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23060200116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-02 | 918 | keep | 0 | Jun | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
SAN JUAN | 2023-06-02 14:54 | 2023-06-02 18:28 | 247 | 3:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X100 EN C/L SE REMPLAZO CAJA PRIMARIA TRASPATIO | S23060200170 | New_Event | Cutout Failure | Include | Include | Equipment | 214 | 2023-06-02 | 52858 | keep | 0 | Jun | 2023 | 0.036001 | 0.00016823 | Sustained | FALSE | FALSE | Not_TMED_Event | 247
CANOVANAS | 2023-06-02 15:03 | 2023-06-02 17:10 | 22 | 2:07 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R23060200129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2023-06-02 | 2794 | keep | 0 | Jun | 2023 | 0.001903 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
BARRANQUITAS | 2023-06-02 15:11 | 2023-06-03 14:28 | 18 | 23:17 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA EVENTO TRANSFERIDO DE PONCE | P23060200437 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1397 | 2023-06-02 | 25146 | keep | 0 | Jun | 2023 | 0.017127 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
HUMACAO | 2023-06-02 15:14 | 2023-06-02 17:43 | 37 | 2:29 | P | CONDUCTOR ROTO O ABIERTO | SE ENCONTRO PUENTE ABIERTO EN ANCLADA | C23060200119 | New_Event | Primary Wire Break | Include | Include | Equipment | 149 | 2023-06-02 | 5513 | keep | 0 | Jun | 2023 | 0.0037549 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
CANOVANAS | 2023-06-02 15:26 | 2023-06-02 17:03 | 20 | 1:37 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN C/L SE RETIRO UN PEDAZO DE ALAMBRE CRUZANDO LA LINEA CON EL NEUTRAL. | R23060200132 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 97 | 2023-06-02 | 1940 | keep | 0 | Jun | 2023 | 0.0013213 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-06-02 15:30 | 2023-06-02 15:53 | 7 | 0:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C23060200121 | New_Event | Secondary Wire Break | Include | Include | Equipment | 23 | 2023-06-02 | 161 | keep | 0 | Jun | 2023 | 0.00010966 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-06-02 15:41 | 2023-06-02 16:50 | 25 | 1:09 | P | DESGANCHE | 1 X 20 EN C/L DESGANCHE | B23060200463 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 69 | 2023-06-02 | 1725 | keep | 0 | Jun | 2023 | 0.0011749 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-06-02 15:42 | 2023-06-02 15:43 | 1580 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 774 CLIENTES X 2604-03 | C23060200124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-02 | 1580 | keep | 0 | Jun | 2023 | 0.0010761 | 0.0010761 | Momentary | FALSE | FALSE | Not_TMED_Event | 1580
ARECIBO | 2023-06-02 15:51 | 2023-06-03 10:52 | 1 | 19:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A23060200185 | New_Event | Cutout Failure | Include | Include | Equipment | 1141 | 2023-06-02 | 1141 | keep | 0 | Jun | 2023 | 0.00077713 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-06-02 15:55 | 2023-06-02 15:56 | 1580 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 774 CLIENTES X 2604-03 | C2306020000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-02 | 1580 | keep | 0 | Jun | 2023 | 0.0010761 | 0.0010761 | Momentary | FALSE | FALSE | Not_TMED_Event | 1580
PONCE | 2023-06-02 16:13 | 2023-06-02 18:56 | 688 | 2:43 | S | LINEA DE TRANSMISION 38KV | SE RETIRA CARGA DE LA SUBESTACION PARA REMPLAZAR FUSIBLE DE ALTA FUNDIDO | P23060200492 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 163 | 2023-06-02 | 112144 | keep | 0 | Jun | 2023 | 0.076381 | 0.00046859 | Sustained | FALSE | FALSE | Not_TMED_Event | 688
PONCE | 2023-06-02 16:13 | 2023-06-02 18:56 | 658 | 2:43 | S | LINEA DE TRANSMISION 38KV | SE RETIRA CARGA DE LA SUBESTACION PARA REMPLAZAR FUSIBLE DE ALTA FUNDIDO | P23060200492 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 163 | 2023-06-02 | 107254 | keep | 0 | Jun | 2023 | 0.07305 | 0.00044816 | Sustained | FALSE | FALSE | Not_TMED_Event | 658
BAYAMON | 2023-06-02 16:23 | 2023-06-02 17:56 | 31 | 1:33 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | B23060200240 | New_Event | Animals | Include | Include | Wildlife | 93 | 2023-06-02 | 2883 | keep | 0 | Jun | 2023 | 0.0019636 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
BAYAMON | 2023-06-02 16:23 | 2023-06-02 17:36 | 200 | 1:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REMPLAZO CAJA | B23060200239 | New_Event | Cutout Failure | Include | Include | Equipment | 73 | 2023-06-02 | 14600 | keep | 0 | Jun | 2023 | 0.009944 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2023-06-02 16:32 | 2023-06-02 17:58 | 1 | 1:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO. | R23060200137 | New_Event | Secondary Wire Break | Include | Include | Equipment | 86 | 2023-06-02 | 86 | keep | 0 | Jun | 2023 | 5.8574e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-06-02 16:36 | 2023-06-02 18:08 | 100 | 1:32 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA POR AVE | P23060200496 | New_Event | Animals | Include | Include | Wildlife | 92 | 2023-06-02 | 9200 | keep | 0 | Jun | 2023 | 0.0062661 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-06-02 16:40 | 2023-06-02 18:15 | 40 | 1:35 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23060200154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2023-06-02 | 3800 | keep | 0 | Jun | 2023 | 0.0025882 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-06-02 16:51 | 2023-06-02 19:20 | 15 | 2:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA EVENTO TRANSFERIDO DE PONCE. | P23060200500 | New_Event | Secondary Wire Break | Include | Include | Equipment | 149 | 2023-06-02 | 2235 | keep | 0 | Jun | 2023 | 0.0015222 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-06-02 16:56 | 2023-06-02 19:30 | 15 | 2:34 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | A23060200200 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 154 | 2023-06-02 | 2310 | keep | 0 | Jun | 2023 | 0.0015733 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2023-06-02 16:57 | 2023-06-02 18:09 | 65 | 1:12 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | R23060200140 | New_Event | Animals | Include | Include | Wildlife | 72 | 2023-06-02 | 4680 | keep | 0 | Jun | 2023 | 0.0031875 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
GUAYAMA | 2023-06-02 17:04 | 2023-06-02 19:17 | 6 | 2:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO SECUNDARIA SE REGULO VOLTAJE Y CONECTORES EN TOMA | P23060200505 | New_Event | Secondary Wire Break | Include | Include | Equipment | 133 | 2023-06-02 | 798 | keep | 0 | Jun | 2023 | 0.00054351 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-06-02 17:32 | 2023-06-02 21:19 | 15 | 3:47 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA X 37.5KVA | A23060200208 | New_Event | Service Transformer Failure | Include | Include | Equipment | 227 | 2023-06-02 | 3405 | keep | 0 | Jun | 2023 | 0.0023191 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-06-02 17:43 | 2023-06-02 18:20 | 344 | 0:37 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO, SE CERRO PUENTE ABIERTO EN ANCLADA Y SE ENERGIZO 100% EN SERVICIO | C23060200119 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 37 | 2023-06-02 | 12728 | keep | 0 | Jun | 2023 | 0.008669 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-02 17:45 | 2023-06-03 12:21 | 35 | 18:36 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | B23060200281 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1116 | 2023-06-02 | 39060 | keep | 0 | Jun | 2023 | 0.026604 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2023-06-02 17:48 | 2023-06-03 07:45 | 65 | 13:57 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C23060200154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 837 | 2023-06-02 | 54405 | keep | 0 | Jun | 2023 | 0.037055 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2023-06-02 18:03 | 2023-06-03 16:03 | 152 | 22:00 | P | CAUSAS EXTERNAS | SE REMPLAZO POSTE PRIMARIO Y SE ABRE INTERRUPTOR PARA CERRA PUENTE | S23060200160 | Partial_restoration | Damage From Public | Include | Include | Public | 1320 | 2023-06-02 | 200640 | keep | 0 | Jun | 2023 | 0.13665 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-02 18:03 | 2023-06-03 11:13 | 99 | 17:10 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE DE LINEA A MACHETE | B23060200287 | New_Event | Primary Wire Break | Include | Include | Equipment | 1030 | 2023-06-02 | 101970 | keep | 0 | Jun | 2023 | 0.069451 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
PONCE | 2023-06-02 18:18 | 2023-06-02 20:38 | 70 | 2:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA PORTAFUSIBLE DEFECTUOSO | P23060200521 | New_Event | Cutout Failure | Include | Include | Equipment | 140 | 2023-06-02 | 9800 | keep | 0 | Jun | 2023 | 0.0066747 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2023-06-02 18:27 | 2023-06-03 08:02 | 30 | 13:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C23060200163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 815 | 2023-06-02 | 24450 | keep | 0 | Jun | 2023 | 0.016653 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-06-02 18:41 | 2023-06-02 19:49 | 30 | 1:08 | P | ANIMAL | 1 X 25 EN CORTE DE LINEA POR AVE | P23060200524 | New_Event | Animals | Include | Include | Wildlife | 68 | 2023-06-02 | 2040 | keep | 0 | Jun | 2023 | 0.0013894 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-06-02 18:47 | 2023-06-03 00:15 | 200 | 5:28 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE CREARON LA NOTA ES DE ISABELA | A23060200179 | New_Event | Vegetation Contact | Include | Include | Vegetation | 328 | 2023-06-02 | 65600 | keep | 0 | Jun | 2023 | 0.04468 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2023-06-02 18:49 | 2023-06-03 08:20 | 70 | 13:31 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M23060200180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 811 | 2023-06-02 | 56770 | keep | 0 | Jun | 2023 | 0.038666 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-06-02 19:03 | 2023-06-02 19:04 | 686 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S2306020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-02 | 686 | keep | 0 | Jun | 2023 | 0.00046723 | 0.00046723 | Momentary | FALSE | FALSE | Not_TMED_Event | 686
HUMACAO | 2023-06-02 19:16 | 2023-06-03 08:22 | 32 | 13:06 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | C23060200168 | New_Event | Animals | Include | Include | Wildlife | 786 | 2023-06-02 | 25152 | keep | 0 | Jun | 2023 | 0.017131 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
AGUADILLA | 2023-06-02 19:30 | 2023-06-03 13:44 | 4 | 18:14 | P | ANIMAL | 1 X 20 EN CL CRUCE DE FASE PRIMARIA POR IGUANA | A23060200219 | New_Event | Animals | Include | Include | Wildlife | 1094 | 2023-06-02 | 4376 | keep | 0 | Jun | 2023 | 0.0029805 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2023-06-02 19:31 | 2023-06-03 23:29 | 750 | 27:58 | P | LINEA DE TRANSMISION 115KV | REPARAR ALAMBRE PARTIDO Y REMPLAZO DE TORRE LINEA 36100 SOBRE ALIMENTADOR | A23060200038 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1678 | 2023-06-02 | 1258500 | keep | 0 | Jun | 2023 | 0.85716 | 0.00051082 | Sustained | FALSE | FALSE | Not_TMED_Event | 750
MAYAGÃœEZ | 2023-06-02 19:52 | 2023-06-02 21:23 | 140 | 1:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CL FUERTES VIENTOS | M23060100289 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 91 | 2023-06-02 | 12740 | keep | 0 | Jun | 2023 | 0.0086772 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
ARECIBO | 2023-06-02 19:52 | 2023-06-02 21:51 | 75 | 1:59 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | A23060200225 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2023-06-02 | 8925 | keep | 0 | Jun | 2023 | 0.0060788 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-06-02 21:12 | 2023-06-03 05:06 | 132 | 7:54 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | S23060200249 | New_Event | Vegetation Contact | Include | Include | Vegetation | 474 | 2023-06-02 | 62568 | keep | 0 | Jun | 2023 | 0.042615 | 8.9905e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 132
PONCE | 2023-06-02 21:12 | 2023-06-03 03:00 | 50 | 5:48 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | P23060200556 | New_Event | Vegetation Contact | Include | Include | Vegetation | 348 | 2023-06-02 | 17400 | keep | 0 | Jun | 2023 | 0.011851 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-06-02 21:47 | 2023-06-02 23:06 | 100 | 1:19 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | A23060200261 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2023-06-02 | 7900 | keep | 0 | Jun | 2023 | 0.0053807 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-06-02 21:50 | 2023-06-02 22:50 | 50 | 1:00 | P | OTRAS CAUSAS | 1 X 65 EN CORTE DE LINEA POR FUSIBLE OXIDADO | A23060200263 | New_Event | Other Causes | Include | Include | Other | 60 | 2023-06-02 | 3000 | keep | 0 | Jun | 2023 | 0.0020433 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-06-02 22:00 | 2023-06-03 04:55 | 50 | 6:55 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P23060200569 | New_Event | Vegetation Contact | Include | Include | Vegetation | 415 | 2023-06-02 | 20750 | keep | 0 | Jun | 2023 | 0.014133 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-06-02 22:20 | 2023-06-03 10:20 | 100 | 12:00 | P | ANIMAL | 1 X 50 Y 1 X 40 EN CL CRUCE POR NIDO DE AVES | A23060200271 | New_Event | Animals | Include | Include | Wildlife | 720 | 2023-06-02 | 72000 | keep | 0 | Jun | 2023 | 0.049039 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-06-02 22:40 | 2023-06-02 23:52 | 80 | 1:12 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23060200275 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 72 | 2023-06-02 | 5760 | keep | 0 | Jun | 2023 | 0.0039231 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2023-06-02 22:47 | 2023-06-03 03:00 | 30 | 4:13 | P | CAUSAS EXTERNAS | 1 X 50 EN C/L CARRO IMPACTO POSTE | P23060200578 | New_Event | Damage From Public | Include | Include | Public | 253 | 2023-06-02 | 7590 | keep | 0 | Jun | 2023 | 0.0051695 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-06-03 00:02 | 2023-06-03 04:48 | 154 | 4:46 | S | PROTECCION DEFECTUOSA | CEL51A2 OUTPUT TRIP SELLADO, RELAY SECUNDARIO AVERIADO SE DEJO TRABAJANDO ATRAVEZ DEL PRIMARIO | M23060300137 | New_Event | Protection Miscoordination | Include | Include | Other | 286 | 2023-06-03 | 44044 | keep | 0 | Jun | 2023 | 0.029998 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
AGUADILLA | 2023-06-03 00:02 | 2023-06-03 04:48 | 1261 | 4:46 | S | PROTECCION DEFECTUOSA | CEL51A2 OUTPUT TRIP SELLADO, RELAY SECUNDARIO AVERIADO SE DEJO TRABAJANDO ATRAVEZ DEL PRIMARIO | M23060300137 | New_Event | Protection Miscoordination | Include | Include | Other | 286 | 2023-06-03 | 360646 | keep | 0 | Jun | 2023 | 0.24563 | 0.00085886 | Sustained | FALSE | FALSE | Not_TMED_Event | 1261
AGUADILLA | 2023-06-03 00:02 | 2023-06-03 04:48 | 3894 | 4:46 | S | PROTECCION DEFECTUOSA | CEL51A2 OUTPUT TRIP SELLADO, RELAY SECUNDARIO AVERIADO SE DEJO TRABAJANDO ATRAVEZ DEL PRIMARIO | M23060300137 | New_Event | Protection Miscoordination | Include | Include | Other | 286 | 2023-06-03 | 1113684 | keep | 0 | Jun | 2023 | 0.75853 | 0.0026522 | Sustained | FALSE | FALSE | Not_TMED_Event | 3894
AGUADILLA | 2023-06-03 00:02 | 2023-06-03 04:48 | 997 | 4:46 | S | PROTECCION DEFECTUOSA | CEL51A2 OUTPUT TRIP SELLADO, RELAY SECUNDARIO AVERIADO SE DEJO TRABAJANDO ATRAVEZ DEL PRIMARIO | M23060300137 | New_Event | Protection Miscoordination | Include | Include | Other | 286 | 2023-06-03 | 285142 | keep | 0 | Jun | 2023 | 0.19421 | 0.00067905 | Sustained | FALSE | FALSE | Not_TMED_Event | 997
AGUADILLA | 2023-06-03 00:02 | 2023-06-03 04:48 | 1497 | 4:46 | S | PROTECCION DEFECTUOSA | CEL51A2 OUTPUT TRIP SELLADO, RELAY SECUNDARIO AVERIADO SE DEJO TRABAJANDO ATRAVEZ DEL PRIMARIO | M23060300137 | New_Event | Protection Miscoordination | Include | Include | Other | 286 | 2023-06-03 | 428142 | keep | 0 | Jun | 2023 | 0.29161 | 0.0010196 | Sustained | FALSE | FALSE | Not_TMED_Event | 1497
HUMACAO | 2023-06-03 00:08 | 2023-06-03 06:03 | 650 | 5:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | CAJA PRIMARIA DE 200 AMP. EN RISER QUEMADA, SE INSTALO PUENTE YA QUE NO HAY CAJAS DISPONIBLES. | C23060300002 | New_Event | Cutout Failure | Include | Include | Equipment | 355 | 2023-06-03 | 230750 | keep | 0 | Jun | 2023 | 0.15716 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
BAYAMON | 2023-06-03 00:10 | 2023-06-03 00:25 | 320 | 0:15 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | B23060300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2023-06-03 | 4800 | keep | 0 | Jun | 2023 | 0.0032693 | 0.00021795 | Sustained | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2023-06-03 00:17 | 2023-06-03 10:17 | 1078 | 10:00 | P | DESGANCHE | 1 X 140 EN C/L Y 3 X 140 EN C/L DESGANCHE DE BAMBUA MASIVO | B23060300007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 600 | 2023-06-03 | 646800 | keep | 0 | Jun | 2023 | 0.44053 | 0.00073422 | Sustained | FALSE | FALSE | Not_TMED_Event | 1078
CANOVANAS | 2023-06-03 00:21 | 2023-06-03 09:17 | 8 | 8:56 | P | DESGANCHE | 1 X 25 EN C/L | R23060300001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 536 | 2023-06-03 | 4288 | keep | 0 | Jun | 2023 | 0.0029205 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-06-03 01:01 | 2023-06-03 03:38 | 761 | 2:37 | T | DESGANCHE | DISPARO SE ABRIO CORTE DE LINEA HACIA ESTACION EXPERIMENTAL Y SE CERRO INTERRUPTOR 99% EN SERVICIO SE REALIZO DESGANCHE | S23060300003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2023-06-03 | 119477 | keep | 0 | Jun | 2023 | 0.081375 | 0.00051831 | Sustained | FALSE | FALSE | Not_TMED_Event | 761
AGUADILLA | 2023-06-03 01:05 | 2023-06-03 11:56 | 80 | 10:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CL SE REMPLAZO CAJA PRIMARIA EN CL | A23060300002 | New_Event | Cutout Failure | Include | Include | Equipment | 651 | 2023-06-03 | 52080 | keep | 0 | Jun | 2023 | 0.035471 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2023-06-03 01:40 | 2023-06-03 01:41 | 2280 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | C2306030000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-06-03 | 2280 | keep | 0 | Jun | 2023 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
BAYAMON | 2023-06-03 01:41 | 2023-06-03 13:15 | 46 | 11:34 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN C/L SE REMPLAZO AISLADOR | B23060300024 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 694 | 2023-06-03 | 31924 | keep | 0 | Jun | 2023 | 0.021743 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
BARRANQUITAS | 2023-06-03 01:41 | 2023-06-03 01:45 | 760 | 0:04 | P | DESGANCHE | CONDUCTOR PRIMARIO EN EL SUELO A CAUSA DE BAMBUAS EN LA LINEA | C2306030000X | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 4 | 2023-06-03 | 3040 | keep | 0 | Jun | 2023 | 0.0020705 | 0.00051763 | Momentary | FALSE | FALSE | Not_TMED_Event | 760
MAYAGÃœEZ | 2023-06-03 01:43 | 2023-06-06 18:04 | 32 | 88:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA FUERTES VIENTOS INFORMA ALFONSO GONZALEZ QUE CLIENTES LLEVAN 3 DIAS SIN SERVICIO EVENTO M23060300125 CLIENTE SIN SERVICIO CERRARON EL EVENTO | M23060600390 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 5301 | 2023-06-03 | 169632 | keep | 0 | Jun | 2023 | 0.11554 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
BARRANQUITAS | 2023-06-03 01:45 | 2023-06-03 01:46 | 2280 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | C2306030000X | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-06-03 | 2280 | keep | 0 | Jun | 2023 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2023-06-03 01:46 | 2023-06-03 01:52 | 760 | 0:06 | P | DESGANCHE | CONDUCTOR PRIMARIO EN EL SUELO A CAUSA DE BAMBUAS EN LA LINE | C2306030000X | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 6 | 2023-06-03 | 4560 | keep | 0 | Jun | 2023 | 0.0031058 | 0.00051763 | Sustained | FALSE | FALSE | Not_TMED_Event | 760
SAN JUAN | 2023-06-03 01:52 | 2023-06-03 01:55 | 225 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23060300005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-06-03 | 675 | keep | 0 | Jun | 2023 | 0.00045974 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
BARRANQUITAS | 2023-06-03 01:52 | 2023-06-03 09:24 | 2280 | 7:32 | T | DESGANCHE | CG-230603-01 SE LEVANTO CONDUCTOR PRIMARIO A CAUSA DE BAMBUAS EN LA LINEA | C23060300016 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 452 | 2023-06-03 | 1030560 | keep | 0 | Jun | 2023 | 0.70191 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-06-03 02:08 | 2023-06-03 20:44 | 100 | 18:36 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | M23060300051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1116 | 2023-06-03 | 111600 | keep | 0 | Jun | 2023 | 0.07601 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-06-03 02:18 | 2023-06-03 09:35 | 200 | 7:17 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS | M23060300136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 437 | 2023-06-03 | 87400 | keep | 0 | Jun | 2023 | 0.059528 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-06-03 02:48 | 2023-06-03 14:29 | 36 | 11:41 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | B23060300041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 701 | 2023-06-03 | 25236 | keep | 0 | Jun | 2023 | 0.017188 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
BARRANQUITAS | 2023-06-03 02:50 | 2023-06-03 08:41 | 300 | 5:51 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | B23060300038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 351 | 2023-06-03 | 105300 | keep | 0 | Jun | 2023 | 0.071719 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2023-06-03 03:27 | 2023-06-03 03:28 | 225 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23060300008 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 225 | keep | 0 | Jun | 2023 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
BAYAMON | 2023-06-03 03:28 | 2023-06-03 12:52 | 189 | 9:24 | P | DESGANCHE | 1 X 50 EN C/L Y 2 X 40 EN C/L DESGANCHE | B23060300053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 564 | 2023-06-03 | 106596 | keep | 0 | Jun | 2023 | 0.072602 | 0.00012873 | Sustained | FALSE | FALSE | Not_TMED_Event | 189
CAGUAS | 2023-06-03 03:30 | 2023-06-03 03:31 | 851 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 3103-02 LLEVANDO PARTE 3102-01 | C23060300045 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-03 | 851 | keep | 0 | Jun | 2023 | 0.00057961 | 0.00057961 | Momentary | FALSE | FALSE | Not_TMED_Event | 851
CAGUAS | 2023-06-03 03:30 | 2023-06-03 03:31 | 1922 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 3103-02 LLEVANDO PARTE 3102-01 | C23060300045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 1922 | keep | 0 | Jun | 2023 | 0.0013091 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
SAN JUAN | 2023-06-03 03:38 | 2023-06-04 13:40 | 7 | 34:02 | P | DESGANCHE | SE CIERRA EL 4 DE JUNIO 2023 C/L LUEGO DE PERSONAL REALIZARAN DESGANCHE Y NO SE CERRO TARDE EN LA NOCHE | S23060300003 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 2042 | 2023-06-03 | 14294 | keep | 0 | Jun | 2023 | 0.0097356 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-06-03 03:43 | 2023-06-03 10:20 | 7 | 6:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN TRANSFORMADOR | M23060300155 | New_Event | Cutout Failure | Include | Include | Equipment | 397 | 2023-06-03 | 2779 | keep | 0 | Jun | 2023 | 0.0018928 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2023-06-03 04:21 | 2023-06-03 12:00 | 75 | 7:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN SU MAL TIEMPO LLUVIAS | P23060300074 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 459 | 2023-06-03 | 34425 | keep | 0 | Jun | 2023 | 0.023447 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
UTUADO | 2023-06-03 05:00 | 2023-06-03 11:26 | 140 | 6:26 | P | DESGANCHE | 2 X 65 EN CL SE REALIZO DESGANCHE DE BAMBUS | A23060300007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 386 | 2023-06-03 | 54040 | keep | 0 | Jun | 2023 | 0.036806 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
CANOVANAS | 2023-06-03 05:04 | 2023-06-03 10:34 | 18 | 5:30 | P | DESGANCHE | 1 X 100 EN C/L | R23060300003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 330 | 2023-06-03 | 5940 | keep | 0 | Jun | 2023 | 0.0040457 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
AGUADILLA | 2023-06-03 05:11 | 2023-06-03 12:50 | 80 | 7:39 | P | ARBOL SOBRE LINEA | 1 X 80 EN CORTE DE LINEA SE ABRIO PUENTES PARA SECCIONALIZAR ARBOL SOBRE LINEA SE INSTALO TIERRAS QUEDA 1 CLIENTE SIN SERVICIO | M23060300163 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 459 | 2023-06-03 | 36720 | keep | 0 | Jun | 2023 | 0.02501 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-06-03 05:20 | 2023-06-03 05:22 | 1784 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO SE PROBO QUEDO EN SERVICIO 90% POR 1801-02 | B23060300000 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-06-03 | 3568 | keep | 0 | Jun | 2023 | 0.0024301 | 0.0012151 | Momentary | FALSE | FALSE | Not_TMED_Event | 1784
BAYAMON | 2023-06-03 05:20 | 2023-06-03 05:22 | 453 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO SE PROBO QUEDO EN SERVICIO 10% POR 1801-02 | B23060300000 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-06-03 | 906 | keep | 0 | Jun | 2023 | 0.00061707 | 0.00030854 | Momentary | FALSE | FALSE | Not_TMED_Event | 453
BAYAMON | 2023-06-03 05:20 | 2023-06-03 05:22 | 186 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO LLEVA 90% DEL 1711-04 Y 10% DEL 1717-01 | B23060300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-03 | 372 | keep | 0 | Jun | 2023 | 0.00025337 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
UTUADO | 2023-06-03 05:31 | 2023-06-03 21:01 | 80 | 15:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA POR FUERTE VIENTO | A23060300010 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 930 | 2023-06-03 | 74400 | keep | 0 | Jun | 2023 | 0.050674 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-06-03 05:36 | 2023-06-03 23:42 | 75 | 18:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA FUERTE VIENTO | A23060300011 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1086 | 2023-06-03 | 81450 | keep | 0 | Jun | 2023 | 0.055475 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2023-06-03 05:39 | 2023-06-03 11:25 | 50 | 5:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA FUERTES VIENTOS | M23060300200 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 346 | 2023-06-03 | 17300 | keep | 0 | Jun | 2023 | 0.011783 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-06-03 05:39 | 2023-06-03 11:15 | 80 | 5:36 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M23060300166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 336 | 2023-06-03 | 26880 | keep | 0 | Jun | 2023 | 0.018308 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-06-03 05:42 | 2023-06-03 13:15 | 20 | 7:33 | P | DESGANCHE | 1 X 80 EN CL DESGANCHE DE BAMBU | A23060300012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 453 | 2023-06-03 | 9060 | keep | 0 | Jun | 2023 | 0.0061707 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2023-06-03 05:47 | 2023-06-03 08:00 | 40 | 2:13 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P23060300085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2023-06-03 | 5320 | keep | 0 | Jun | 2023 | 0.0036234 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-06-03 05:58 | 2023-06-03 05:59 | 2126 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C23060300062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 2126 | keep | 0 | Jun | 2023 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
MAYAGÃœEZ | 2023-06-03 05:59 | 2023-06-03 12:20 | 50 | 6:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN CORTE DE LINEA FUERTES VIENTOS | M23060300167 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 381 | 2023-06-03 | 19050 | keep | 0 | Jun | 2023 | 0.012975 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-06-03 06:19 | 2023-06-03 09:25 | 22 | 3:06 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | C23060300065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2023-06-03 | 4092 | keep | 0 | Jun | 2023 | 0.002787 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
FAJARDO | 2023-06-03 06:36 | 2023-06-03 09:04 | 30 | 2:28 | P | DESGANCHE | 1 X 30 EN C/L | R23060300005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2023-06-03 | 4440 | keep | 0 | Jun | 2023 | 0.0030241 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2023-06-03 06:39 | 2023-06-03 12:25 | 200 | 5:46 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN CORTE DE LINEA SE REPARO BAJANTE DE CAJA A CONVERTIDOR | A23060300020 | New_Event | Primary Wire Break | Include | Include | Equipment | 346 | 2023-06-03 | 69200 | keep | 0 | Jun | 2023 | 0.047132 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2023-06-03 06:41 | 2023-06-03 06:42 | 1252 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO | M23060300170 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 1252 | keep | 0 | Jun | 2023 | 0.00085273 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
UTUADO | 2023-06-03 06:45 | 2023-06-04 07:58 | 15 | 25:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23060300022 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1513 | 2023-06-03 | 22695 | keep | 0 | Jun | 2023 | 0.015457 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2023-06-03 06:45 | 2023-06-03 06:46 | 1296 | 0:01 | P | ALIMENTADOR AMARRADO | RECERRO INTERRUPTOR 95% DE LA CARGA POR EL 9605-01 EN SERVICIO | C23060300079 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-03 | 1296 | keep | 0 | Jun | 2023 | 0.0008827 | 0.0008827 | Momentary | FALSE | FALSE | Not_TMED_Event | 1296
BARRANQUITAS | 2023-06-03 06:45 | 2023-06-03 06:46 | 2410 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23060300079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 2410 | keep | 0 | Jun | 2023 | 0.0016414 | 0.0016414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2410
VEGA BAJA | 2023-06-03 06:53 | 2023-06-03 11:53 | 80 | 5:00 | P | DESGANCHE | 1 X 65 EN CL DESGANCHE | A23060300023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 300 | 2023-06-03 | 24000 | keep | 0 | Jun | 2023 | 0.016346 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-06-03 06:56 | 2023-06-03 18:47 | 162 | 11:51 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | B23060300077 | New_Event | Animals | Include | Include | Wildlife | 711 | 2023-06-03 | 115182 | keep | 0 | Jun | 2023 | 0.07845 | 0.00011034 | Sustained | FALSE | FALSE | Not_TMED_Event | 162
HUMACAO | 2023-06-03 07:07 | 2023-06-03 07:08 | 4830 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 800 CLIENTES DE SU CARGA POR EL 3205-07 EN SERVICIO | C2306030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 4830 | keep | 0 | Jun | 2023 | 0.0032897 | 0.0032897 | Momentary | FALSE | FALSE | Not_TMED_Event | 4830
HUMACAO | 2023-06-03 07:07 | 2023-06-03 07:08 | 2126 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | DISPARO INTERRUPTOR CERRADO POR CONTROL | C23060300085 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-06-03 | 2126 | keep | 0 | Jun | 2023 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2023-06-03 07:08 | 2023-06-03 18:09 | 10 | 11:01 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO, ESTABA CERRADO CON HOT CLAMP EVENTO TRANSFERIDO DE PONCE A HUMACAO | P23060300191 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 661 | 2023-06-03 | 6610 | keep | 0 | Jun | 2023 | 0.004502 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-06-03 07:11 | 2023-06-03 19:45 | 7 | 12:34 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO Y LEVANTO SECUNDARIA | R23060300136 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 754 | 2023-06-03 | 5278 | keep | 0 | Jun | 2023 | 0.0035948 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-06-03 07:17 | 2023-06-03 07:18 | 3296 | 0:01 | T | DESGANCHE | DISPARO INTERRUPTOR LLEVA LA CARGA DEL 9602-04 Y 62 CLIENTES DEL 9602-03 POR LA VIA LIBRE D2023-4048 CERRADO POR CONTROL | C2306030000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-06-03 | 3296 | keep | 0 | Jun | 2023 | 0.0022449 | 0.0022449 | Momentary | FALSE | FALSE | Not_TMED_Event | 3296
BARRANQUITAS | 2023-06-03 07:17 | 2023-06-03 07:18 | 63 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR 5% DE LA CARGAR POR EL 9601-02 POR LA VIA LIBRE D2023-4048 CERRADO POR CONTROL | C2306030000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-03 | 63 | keep | 0 | Jun | 2023 | 4.2909e-05 | 4.2909e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 63
BARRANQUITAS | 2023-06-03 07:17 | 2023-06-03 07:18 | 2937 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR LLEVA LA CARGA DEL 9602-04 POR LA VIA LIBRE D2023-4048 CERRADO POR CONTROL | C2306030000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-03 | 2937 | keep | 0 | Jun | 2023 | 0.0020004 | 0.0020004 | Momentary | FALSE | FALSE | Not_TMED_Event | 2937
HUMACAO | 2023-06-03 07:29 | 2023-06-03 09:38 | 10 | 2:09 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C23060300096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2023-06-03 | 1290 | keep | 0 | Jun | 2023 | 0.00087861 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-06-03 07:39 | 2023-06-03 07:40 | 4944 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S23060300052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 4944 | keep | 0 | Jun | 2023 | 0.0033673 | 0.0033673 | Momentary | FALSE | FALSE | Not_TMED_Event | 4944
BAYAMON | 2023-06-03 07:47 | 2023-06-03 07:48 | 1533 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR | S23060300110 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-06-03 | 1533 | keep | 0 | Jun | 2023 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
BAYAMON | 2023-06-03 07:48 | 2023-06-03 13:04 | 11 | 5:16 | P | ANIMAL | 2 X 65 EN C/L CRUCE X AVE | S23060300059 | 1st_after_momentary | Animals | Include | Include | Wildlife | 316 | 2023-06-03 | 3476 | keep | 0 | Jun | 2023 | 0.0023675 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
ARECIBO | 2023-06-03 08:07 | 2023-06-03 13:50 | 70 | 5:43 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN CL SE REPARO LINEA PRIMARIA | A23060300045 | New_Event | Primary Wire Break | Include | Include | Equipment | 343 | 2023-06-03 | 24010 | keep | 0 | Jun | 2023 | 0.016353 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2023-06-03 08:08 | 2023-06-03 14:59 | 1 | 6:51 | P | DESGANCHE | DESGANCHE 1 X 50 EN CORTE DE LINEA | P23060300186 | New_Event | Vegetation Contact | Include | Include | Vegetation | 411 | 2023-06-03 | 411 | keep | 0 | Jun | 2023 | 0.00027993 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-06-03 08:12 | 2023-06-03 14:20 | 12 | 6:08 | P | DESCONECTIVO DEFECTUOSO | SE CAMBIO MACHETE 1 X 65 EN CORTE DE LINEA | P23060300187 | New_Event | Switch Failure | Include | Include | Equipment | 368 | 2023-06-03 | 4416 | keep | 0 | Jun | 2023 | 0.0030077 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-06-03 08:18 | 2023-06-03 10:24 | 25 | 2:06 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | P23060300197 | New_Event | Animals | Include | Include | Wildlife | 126 | 2023-06-03 | 3150 | keep | 0 | Jun | 2023 | 0.0021455 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2023-06-03 08:20 | 2023-06-03 16:57 | 85 | 8:37 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 3 X 50 EN C/L SE REEMPLAZO DE POSTE PARTIDO Y XMR | R23060300020 | New_Event | Primary Pole Failure | Include | Include | Equipment | 517 | 2023-06-03 | 43945 | keep | 0 | Jun | 2023 | 0.029931 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
AGUADILLA | 2023-06-03 08:24 | 2023-06-04 14:57 | 80 | 30:33 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23060300188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1833 | 2023-06-03 | 146640 | keep | 0 | Jun | 2023 | 0.099876 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-06-03 08:45 | 2023-06-03 10:10 | 150 | 1:25 | P | ANIMAL | 1 X 100 Y 1 X 65 EN C/LS CRUCE X REPTIL | R23060300017 | New_Event | Animals | Include | Include | Wildlife | 85 | 2023-06-03 | 12750 | keep | 0 | Jun | 2023 | 0.008684 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
GUAYAMA | 2023-06-03 08:47 | 2023-06-03 11:40 | 15 | 2:53 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P23060300223 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2023-06-03 | 2595 | keep | 0 | Jun | 2023 | 0.0017674 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-06-03 08:55 | 2023-06-03 18:23 | 112 | 9:28 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA DESGANCHE | S23060300074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 568 | 2023-06-03 | 63616 | keep | 0 | Jun | 2023 | 0.043329 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
MAYAGÃœEZ | 2023-06-03 08:57 | 2023-06-03 08:58 | 108 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23060300207 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 108 | keep | 0 | Jun | 2023 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
MAYAGÃœEZ | 2023-06-03 08:59 | 2023-06-03 09:00 | 1252 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23060300201 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 1252 | keep | 0 | Jun | 2023 | 0.00085273 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2023-06-03 09:04 | 2023-06-03 19:15 | 1252 | 10:11 | T | CONDUCTOR ARRIADO O CRUZADO | DISPARO DE INTERRUPTOR SE DESCRUZARON LINEAS PRIMARIAS | M23060300204 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 611 | 2023-06-03 | 764972 | keep | 0 | Jun | 2023 | 0.52102 | 0.00085273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1252
UTUADO | 2023-06-03 09:04 | 2023-06-03 16:30 | 180 | 7:26 | P | DESGANCHE | 1 X 140 EN CONVERTIDOR SE REALIZO DESGANCHE MASIVO | A23060300066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 446 | 2023-06-03 | 80280 | keep | 0 | Jun | 2023 | 0.054678 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
SAN JUAN | 2023-06-03 09:06 | 2023-06-03 19:29 | 80 | 10:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA VIENTOS | S23060300080 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 623 | 2023-06-03 | 49840 | keep | 0 | Jun | 2023 | 0.033946 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-06-03 09:12 | 2023-06-03 11:12 | 60 | 2:00 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R23060300023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2023-06-03 | 7200 | keep | 0 | Jun | 2023 | 0.0049039 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-06-03 09:14 | 2023-06-03 09:15 | 3894 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23060300206 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 3894 | keep | 0 | Jun | 2023 | 0.0026522 | 0.0026522 | Momentary | FALSE | FALSE | Not_TMED_Event | 3894
BARRANQUITAS | 2023-06-03 09:24 | 2023-06-03 10:52 | 2635 | 1:28 | S | DESGANCHE | CG-230603-01 SE RETIRO LA CARGA DE LA SUBESTACION PARA REEMPLAZAR FUSIBLE FUNDIDO EN EL 38KV EN LA OPERACION DE RECIERRE DEL 9902-02. JONNATHAN MENDEZ AUTORIZO A CATALA A REEMPLAZAR LOS FUSIBLES | C23060300202 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2023-06-03 | 231880 | keep | 0 | Jun | 2023 | 0.15793 | 0.0017947 | Sustained | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2023-06-03 09:24 | 2023-06-03 10:52 | 2280 | 1:28 | S | DESGANCHE | CG-230603-01 SE RETIRO LA CARGA DE LA SUBESTACION PARA REEMPLAZAR FUSIBLE FUNDIDO EN EL 38KV EN LA OPERACION DE RECIERRE DEL 9902-02. JONNATHAN MENDEZ AUTORIZO A CATALA A REEMPLAZAR LOS FUSIBLES | C23060300202 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 88 | 2023-06-03 | 200640 | keep | 0 | Jun | 2023 | 0.13665 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-06-03 09:24 | 2023-06-03 10:52 | 1617 | 1:28 | S | DESGANCHE | CG-230603-01 SE RETIRO LA CARGA DE LA SUBESTACION PARA REEMPLAZAR FUSIBLE FUNDIDO EN EL 38KV EN LA OPERACION DE RECIERRE DEL 9902-02. JONNATHAN MENDEZ AUTORIZO A CATALA A REEMPLAZAR LOS FUSIBLES | C23060300202 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2023-06-03 | 142296 | keep | 0 | Jun | 2023 | 0.096917 | 0.0011013 | Sustained | FALSE | FALSE | Not_TMED_Event | 1617
ARECIBO | 2023-06-03 09:26 | 2023-06-03 10:10 | 50 | 0:44 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE | A23060300079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 44 | 2023-06-03 | 2200 | keep | 0 | Jun | 2023 | 0.0014984 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-06-03 09:28 | 2023-06-03 09:29 | 252 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23060300149 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 252 | keep | 0 | Jun | 2023 | 0.00017164 | 0.00017164 | Momentary | FALSE | FALSE | Not_TMED_Event | 252
CAGUAS | 2023-06-03 09:30 | 2023-06-03 14:50 | 85 | 5:20 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | C23060300177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 320 | 2023-06-03 | 27200 | keep | 0 | Jun | 2023 | 0.018526 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
AGUADILLA | 2023-06-03 09:30 | 2023-06-03 14:20 | 40 | 4:50 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23060300209 | New_Event | Vegetation Contact | Include | Include | Vegetation | 290 | 2023-06-03 | 11600 | keep | 0 | Jun | 2023 | 0.0079007 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-06-03 09:44 | 2023-06-03 09:45 | 108 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23060300212 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 108 | keep | 0 | Jun | 2023 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
PONCE | 2023-06-03 09:50 | 2023-06-03 10:20 | 8 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23060300307 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-06-03 | 240 | keep | 0 | Jun | 2023 | 0.00016346 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-06-03 09:53 | 2023-06-03 13:18 | 996 | 3:25 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA EL 1401-10 LLEVA EL 1348-07 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 SE REALIZO DESGANCHE DEL 1348-07 SJ-230603-02 | S23060300094 | New_Event | Feeder Load Transferred | Include | Include | Other | 205 | 2023-06-03 | 204180 | keep | 0 | Jun | 2023 | 0.13907 | 0.00067837 | Sustained | FALSE | FALSE | Not_TMED_Event | 996
SAN JUAN | 2023-06-03 09:53 | 2023-06-03 13:18 | 1000 | 3:25 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA EL 1401-10 LLEVA EL 1348-07 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 SE REALIZO DESGANCHE DEL 1348-07 SJ-230603-02 | S23060300094 | New_Event | Feeder Load Transferred | Include | Include | Other | 205 | 2023-06-03 | 205000 | keep | 0 | Jun | 2023 | 0.13962 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2023-06-03 09:53 | 2023-06-03 13:18 | 278 | 3:25 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1424-08 LLEVA EL 1401-10 LLEVA EL 1348-07 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 SE REALIZO DESGANCHE DEL 1348-07 SJ-230603-02 | S23060300094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2023-06-03 | 56990 | keep | 0 | Jun | 2023 | 0.038816 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2023-06-03 09:53 | 2023-06-03 12:27 | 1295 | 2:34 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA EL 1401-10 LLEVA EL 1348-07 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 SE SECCIONALIZO DESGANCHE DEL 1348-07 SJ-230603-02 100% EN SERVICIO EL 1424-08 Y 1401-10 | S23060300094 | New_Event | Feeder Load Transferred | Include | Include | Other | 154 | 2023-06-03 | 199430 | keep | 0 | Jun | 2023 | 0.13583 | 0.00088202 | Sustained | FALSE | FALSE | Not_TMED_Event | 1295
SAN JUAN | 2023-06-03 09:53 | 2023-06-03 12:27 | 9 | 2:34 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA EL 1401-10 LLEVA EL 1348-07 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 SE SECCIONALIZO DESGANCHE DEL 1348-07 SJ-230603-02 100% EN SERVICIO EL 1424-08 Y 1401-10 | S23060300094 | New_Event | Feeder Load Transferred | Include | Include | Other | 154 | 2023-06-03 | 1386 | keep | 0 | Jun | 2023 | 0.000944 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
HUMACAO | 2023-06-03 10:00 | 2023-06-03 10:02 | 1089 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A RIO BLANCO | C23060300184 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-03 | 2178 | keep | 0 | Jun | 2023 | 0.0014834 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2023-06-03 10:00 | 2023-06-03 10:02 | 3896 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A RIO BLANCO | C23060300184 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-03 | 7792 | keep | 0 | Jun | 2023 | 0.0053071 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2023-06-03 10:00 | 2023-06-03 10:02 | 1467 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A RIO BLANCO | C23060300184 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-03 | 2934 | keep | 0 | Jun | 2023 | 0.0019983 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
MAYAGÃœEZ | 2023-06-03 10:02 | 2023-06-03 15:30 | 50 | 5:28 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA | M23060300323 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 328 | 2023-06-03 | 16400 | keep | 0 | Jun | 2023 | 0.01117 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-06-03 10:03 | 2023-06-03 11:45 | 30 | 1:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L PRINCIPAL MAL TIEMPO VIENTO | B23060300158 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 102 | 2023-06-03 | 3060 | keep | 0 | Jun | 2023 | 0.0020842 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-06-03 10:04 | 2023-06-03 11:50 | 40 | 1:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA FUERTES VIENTOS | M23060300219 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 106 | 2023-06-03 | 4240 | keep | 0 | Jun | 2023 | 0.0028878 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-06-03 10:05 | 2023-06-03 12:38 | 225 | 2:33 | T | DESGANCHE | SE ABRIO MACHETE PARA SECCIONALIZAR Y SE CERRO INTERRUPTOR 90% EN SERVICIO | S23060300102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2023-06-03 | 34425 | keep | 0 | Jun | 2023 | 0.023447 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
CAGUAS | 2023-06-03 10:08 | 2023-06-03 10:09 | 2448 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23060300186 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 2448 | keep | 0 | Jun | 2023 | 0.0016673 | 0.0016673 | Momentary | FALSE | FALSE | Not_TMED_Event | 2448
SAN JUAN | 2023-06-03 10:09 | 2023-06-03 10:11 | 1225 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S23060300103 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-03 | 2450 | keep | 0 | Jun | 2023 | 0.0016687 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2023-06-03 10:09 | 2023-06-03 10:11 | 1452 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S23060300103 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-03 | 2904 | keep | 0 | Jun | 2023 | 0.0019779 | 0.00098895 | Momentary | FALSE | FALSE | Not_TMED_Event | 1452
SAN JUAN | 2023-06-03 10:09 | 2023-06-03 10:11 | 462 | 0:02 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S23060300103 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-03 | 924 | keep | 0 | Jun | 2023 | 0.00062933 | 0.00031467 | Momentary | FALSE | FALSE | Not_TMED_Event | 462
SAN JUAN | 2023-06-03 10:09 | 2023-06-03 10:11 | 660 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S23060300105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-03 | 1320 | keep | 0 | Jun | 2023 | 0.00089905 | 0.00044952 | Momentary | FALSE | FALSE | Not_TMED_Event | 660
SAN JUAN | 2023-06-03 10:09 | 2023-06-03 10:11 | 435 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S23060300105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-03 | 870 | keep | 0 | Jun | 2023 | 0.00059255 | 0.00029628 | Momentary | FALSE | FALSE | Not_TMED_Event | 435
SAN JUAN | 2023-06-03 10:09 | 2023-06-03 10:11 | 259 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S23060300105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-03 | 518 | keep | 0 | Jun | 2023 | 0.00035281 | 0.0001764 | Momentary | FALSE | FALSE | Not_TMED_Event | 259
SAN JUAN | 2023-06-03 10:09 | 2023-06-03 10:11 | 686 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S23060300105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-03 | 1372 | keep | 0 | Jun | 2023 | 0.00093446 | 0.00046723 | Momentary | FALSE | FALSE | Not_TMED_Event | 686
SAN JUAN | 2023-06-03 10:09 | 2023-06-03 10:11 | 953 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S23060300105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-03 | 1906 | keep | 0 | Jun | 2023 | 0.0012982 | 0.00064908 | Momentary | FALSE | FALSE | Not_TMED_Event | 953
FAJARDO | 2023-06-03 10:13 | 2023-06-03 10:14 | 1234 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23060300037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 1234 | keep | 0 | Jun | 2023 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
AGUADILLA | 2023-06-03 10:13 | 2023-06-03 15:35 | 60 | 5:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR FUERTES VIENTOS | P23060300337 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 322 | 2023-06-03 | 19320 | keep | 0 | Jun | 2023 | 0.013159 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-06-03 10:13 | 2023-06-03 13:57 | 30 | 3:44 | P | DESGANCHE | 1 X 40 EN CL DESGANCHE | A23060300091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2023-06-03 | 6720 | keep | 0 | Jun | 2023 | 0.004577 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-06-03 10:14 | 2023-06-03 10:15 | 1452 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23060300117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 1452 | keep | 0 | Jun | 2023 | 0.00098895 | 0.00098895 | Momentary | FALSE | FALSE | Not_TMED_Event | 1452
FAJARDO | 2023-06-03 10:16 | 2023-06-03 12:35 | 2286 | 2:19 | T | DESGANCHE | SE REALIZO DESGANCHE DE PISO EN VARIOS PUNTOS | R23060300039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2023-06-03 | 317754 | keep | 0 | Jun | 2023 | 0.21642 | 0.001557 | Sustained | FALSE | FALSE | Not_TMED_Event | 2286
HUMACAO | 2023-06-03 10:17 | 2023-06-03 11:59 | 13 | 1:42 | P | ANIMAL | 1 X 20 EN CORTE DE LINEA CRUCE POR AVE | C23060300192 | New_Event | Animals | Include | Include | Wildlife | 102 | 2023-06-03 | 1326 | keep | 0 | Jun | 2023 | 0.00090313 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2023-06-03 10:19 | 2023-06-03 10:22 | 1225 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1203-01 LLEVA 75% DEL 1203-03 SE CERRO POR CONTROL | S23060300122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-06-03 | 3675 | keep | 0 | Jun | 2023 | 0.002503 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2023-06-03 10:19 | 2023-06-03 10:22 | 462 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1203-01 LLEVA 75% DEL 1203-03 SE CERRO POR CONTROL | S23060300122 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-06-03 | 1386 | keep | 0 | Jun | 2023 | 0.000944 | 0.00031467 | Momentary | FALSE | FALSE | Not_TMED_Event | 462
CANOVANAS | 2023-06-03 10:28 | 2023-06-03 14:02 | 99 | 3:34 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN ENTRADA Y SALIDA DE RISER | R23060300041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 214 | 2023-06-03 | 21186 | keep | 0 | Jun | 2023 | 0.01443 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
BAYAMON | 2023-06-03 10:29 | 2023-06-03 11:51 | 1313 | 1:22 | T | ARBOL SOBRE LINEA | SE RETIRO ARBOL SOBRE LINEA CON VARETA DESDE EL PISO | B23060300172 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 82 | 2023-06-03 | 107666 | keep | 0 | Jun | 2023 | 0.073331 | 0.00089428 | Sustained | FALSE | FALSE | Not_TMED_Event | 1313
SAN JUAN | 2023-06-03 10:33 | 2023-06-03 17:46 | 364 | 7:13 | P | DESGANCHE | 1 X 100 Y 1 X 80 EN CORTE DE LINEA DESGANCHE | S23060300135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 433 | 2023-06-03 | 157612 | keep | 0 | Jun | 2023 | 0.10735 | 0.00024792 | Sustained | FALSE | FALSE | Not_TMED_Event | 364
VEGA BAJA | 2023-06-03 10:33 | 2023-06-03 15:40 | 20 | 5:07 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | A23060300099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 307 | 2023-06-03 | 6140 | keep | 0 | Jun | 2023 | 0.0041819 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-06-03 10:34 | 2023-06-03 14:29 | 80 | 3:55 | P | DESGANCHE | 2 X 50 Y 1 X 65 EN C/L SE DESGANCHO | B23060300173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 235 | 2023-06-03 | 18800 | keep | 0 | Jun | 2023 | 0.012805 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2023-06-03 10:36 | 2023-06-03 18:45 | 100 | 8:09 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN DISTINTOS CORTES DE LINEA SE REALIZO DESGANCHE | A23060300100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 489 | 2023-06-03 | 48900 | keep | 0 | Jun | 2023 | 0.033306 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-06-03 10:40 | 2023-06-03 15:57 | 241 | 5:17 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | C23060300196 | New_Event | Primary Wire Break | Include | Include | Equipment | 317 | 2023-06-03 | 76397 | keep | 0 | Jun | 2023 | 0.052034 | 0.00016414 | Sustained | FALSE | FALSE | Not_TMED_Event | 241
VEGA BAJA | 2023-06-03 10:45 | 2023-06-03 18:30 | 10 | 7:45 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO BAMBUS DE LAS LINEAS | A23060300104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 465 | 2023-06-03 | 4650 | keep | 0 | Jun | 2023 | 0.0031671 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-06-03 10:47 | 2023-06-03 10:48 | 411 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M23060300244 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-06-03 | 411 | keep | 0 | Jun | 2023 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
ARECIBO | 2023-06-03 10:52 | 2023-06-03 10:53 | 3431 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | A23060300109 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2023-06-03 | 3431 | keep | 0 | Jun | 2023 | 0.0023368 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-06-03 10:53 | 2023-06-03 10:54 | 1 | 0:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A23060200185 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1 | 2023-06-03 | 1 | keep | 0 | Jun | 2023 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-06-03 10:54 | 2023-06-03 10:55 | 3431 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO | A23060300110 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1 | 2023-06-03 | 3431 | keep | 0 | Jun | 2023 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2023-06-03 10:55 | 2023-06-03 10:57 | 1 | 0:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A23060200185 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 2 | 2023-06-03 | 2 | keep | 0 | Jun | 2023 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-06-03 10:57 | 2023-06-03 17:29 | 36 | 6:32 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | B23060300176 | New_Event | Animals | Include | Include | Wildlife | 392 | 2023-06-03 | 14112 | keep | 0 | Jun | 2023 | 0.0096116 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
MAYAGÃœEZ | 2023-06-03 10:57 | 2023-06-03 10:58 | 411 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M23060300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-06-03 | 411 | keep | 0 | Jun | 2023 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
ARECIBO | 2023-06-03 10:57 | 2023-06-03 13:29 | 3431 | 2:32 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO INTERRUPTOR SE ENCONTRO CAJA PRIMARIA EN TRANSFORMADOR QUEMADA | A23060300111 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 152 | 2023-06-03 | 521512 | keep | 0 | Jun | 2023 | 0.3552 | 0.0023368 | Sustained | FALSE | FALSE | Not_TMED_Event | 3431
BAYAMON | 2023-06-03 10:58 | 2023-06-03 16:35 | 200 | 5:37 | P | DESGANCHE | 1 X 100 Y 3 X 140 EN C/L SE DESGANCHO | B23060300177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 337 | 2023-06-03 | 67400 | keep | 0 | Jun | 2023 | 0.045906 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-06-03 11:03 | 2023-06-03 11:04 | 652 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2306030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 652 | keep | 0 | Jun | 2023 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
CANOVANAS | 2023-06-03 11:04 | 2023-06-03 12:18 | 18 | 1:14 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN C/L SE RETEZO LINEAS | R23060300047 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 74 | 2023-06-03 | 1332 | keep | 0 | Jun | 2023 | 0.00090722 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
MAYAGÃœEZ | 2023-06-03 11:06 | 2023-06-03 17:58 | 411 | 6:52 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE RETIRO BAMBUS SOBRE LAS LINEAS | M23060300255 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 412 | 2023-06-03 | 169332 | keep | 0 | Jun | 2023 | 0.11533 | 0.00027993 | Sustained | FALSE | FALSE | Not_TMED_Event | 411
BAYAMON | 2023-06-03 11:09 | 2023-06-03 11:10 | 3871 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23060300186 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 3871 | keep | 0 | Jun | 2023 | 0.0026365 | 0.0026365 | Momentary | FALSE | FALSE | Not_TMED_Event | 3871
CANOVANAS | 2023-06-03 11:09 | 2023-06-03 12:45 | 157 | 1:36 | P | DESGANCHE | 2 X 100 EN C/L | R23060300049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2023-06-03 | 15072 | keep | 0 | Jun | 2023 | 0.010265 | 0.00010693 | Sustained | FALSE | FALSE | Not_TMED_Event | 157
MAYAGÃœEZ | 2023-06-03 11:09 | 2023-06-03 19:20 | 20 | 8:11 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | P23060300463 | New_Event | Animals | Include | Include | Wildlife | 491 | 2023-06-03 | 9820 | keep | 0 | Jun | 2023 | 0.0066884 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-06-03 11:10 | 2023-06-03 11:27 | 362 | 0:17 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1620-01 LLEVA 90% DEL 1336-10 LLEVA 60% DEL 1620-02 SE CONFIRMO PERSONAL FUERA Y SE CERRO POR CONTROL | S23060300178 | New_Event | Feeder Load Transferred | Include | Include | Other | 17 | 2023-06-03 | 6154 | keep | 0 | Jun | 2023 | 0.0041915 | 0.00024656 | Sustained | FALSE | FALSE | Not_TMED_Event | 362
BAYAMON | 2023-06-03 11:10 | 2023-06-03 11:28 | 1368 | 0:18 | T | NO SE REPORTO CAUSA | DISPARO SE VERIFICO EN EL CAMPO SE PROBO QUEDO EN SERVICIO | S23060300180 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 18 | 2023-06-03 | 24624 | keep | 0 | Jun | 2023 | 0.016771 | 0.00093174 | Sustained | FALSE | FALSE | Not_TMED_Event | 1368
SAN JUAN | 2023-06-03 11:10 | 2023-06-03 11:27 | 36 | 0:17 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-01 LLEVA 90% DEL 1336-10 LLEVA 60% DEL 1620-02 SE CONFIRMO PERSONAL FUERA Y SE CERRO POR CONTROL | S23060300178 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 17 | 2023-06-03 | 612 | keep | 0 | Jun | 2023 | 0.00041683 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2023-06-03 11:10 | 2023-06-03 11:27 | 2230 | 0:17 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1620-01 LLEVA 90% DEL 1336-10 LLEVA 60% DEL 1620-02 SE CONFIRMO PERSONAL FUERA Y SE CERRO POR CONTROL | S23060300178 | New_Event | Feeder Load Transferred | Include | Include | Other | 17 | 2023-06-03 | 37910 | keep | 0 | Jun | 2023 | 0.02582 | 0.0015188 | Sustained | FALSE | FALSE | Not_TMED_Event | 2230
BARRANQUITAS | 2023-06-03 11:14 | 2023-06-03 15:40 | 63 | 4:26 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C23060300214 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2023-06-03 | 16758 | keep | 0 | Jun | 2023 | 0.011414 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
CAGUAS | 2023-06-03 11:17 | 2023-06-03 14:50 | 59 | 3:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTO | C23060300220 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 213 | 2023-06-03 | 12567 | keep | 0 | Jun | 2023 | 0.0085593 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
SAN JUAN | 2023-06-03 11:26 | 2023-06-03 17:38 | 192 | 6:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA VIENTOS | S23060300197 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 372 | 2023-06-03 | 71424 | keep | 0 | Jun | 2023 | 0.048647 | 0.00013077 | Sustained | FALSE | FALSE | Not_TMED_Event | 192
CAGUAS | 2023-06-03 11:26 | 2023-06-03 11:27 | 2276 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23060300224 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 2276 | keep | 0 | Jun | 2023 | 0.0015502 | 0.0015502 | Momentary | FALSE | FALSE | Not_TMED_Event | 2276
UTUADO | 2023-06-03 11:26 | 2023-06-03 11:31 | 1405 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 CONDUCTORES ARRIADOS ENTRE ACB 1933A - ACB 1945B | A23060300125 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-06-03 | 7025 | keep | 0 | Jun | 2023 | 0.0047847 | 0.00095694 | Momentary | FALSE | FALSE | Not_TMED_Event | 1405
UTUADO | 2023-06-03 11:26 | 2023-06-03 11:31 | 669 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 CONDUCTORES ARRIADOS ENTRE ACB 1933A - ACB 1945B | A23060300125 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-06-03 | 3345 | keep | 0 | Jun | 2023 | 0.0022783 | 0.00045565 | Momentary | FALSE | FALSE | Not_TMED_Event | 669
UTUADO | 2023-06-03 11:26 | 2023-06-03 11:31 | 1527 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 CONDUCTORES ARRIADOS ENTRE ACB 1933A - ACB 1945B | A23060300125 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-06-03 | 7635 | keep | 0 | Jun | 2023 | 0.0052002 | 0.00104 | Momentary | FALSE | FALSE | Not_TMED_Event | 1527
UTUADO | 2023-06-03 11:26 | 2023-06-03 11:31 | 1054 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 CONDUCTORES ARRIADOS ENTRE ACB 1933A - ACB 1945B | A23060300125 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-06-03 | 5270 | keep | 0 | Jun | 2023 | 0.0035894 | 0.00071787 | Momentary | FALSE | FALSE | Not_TMED_Event | 1054
UTUADO | 2023-06-03 11:26 | 2023-06-03 11:31 | 932 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 CONDUCTORES ARRIADOS ENTRE ACB 1933A - ACB 1945B | A23060300125 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-06-03 | 4660 | keep | 0 | Jun | 2023 | 0.0031739 | 0.00063478 | Momentary | FALSE | FALSE | Not_TMED_Event | 932
UTUADO | 2023-06-03 11:26 | 2023-06-03 11:31 | 1633 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 CONDUCTORES ARRIADOS ENTRE ACB 1933A - ACB 1945B | A23060300126 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-06-03 | 8165 | keep | 0 | Jun | 2023 | 0.0055611 | 0.0011122 | Momentary | FALSE | FALSE | Not_TMED_Event | 1633
UTUADO | 2023-06-03 11:26 | 2023-06-03 11:31 | 1624 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 CONDUCTORES ARRIADOS ENTRE ACB 1933A - ACB 1945B | A23060300126 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-06-03 | 8120 | keep | 0 | Jun | 2023 | 0.0055305 | 0.0011061 | Momentary | FALSE | FALSE | Not_TMED_Event | 1624
BARRANQUITAS | 2023-06-03 11:27 | 2023-06-03 12:27 | 1246 | 1:00 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO CERRO POR CONTROL, CERRADO EN LA SUBESTACION EN SERVICIO | C23060300226 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 60 | 2023-06-03 | 74760 | keep | 0 | Jun | 2023 | 0.050919 | 0.00084864 | Sustained | FALSE | FALSE | Not_TMED_Event | 1246
SAN JUAN | 2023-06-03 11:28 | 2023-06-04 13:18 | 15 | 25:50 | P | DESGANCHE | 2 X 50 EN C/L SE REALIZO DESGANCHE | S23060300936 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1550 | 2023-06-03 | 23250 | keep | 0 | Jun | 2023 | 0.015835 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-06-03 11:29 | 2023-06-04 12:58 | 44 | 25:29 | P | DESGANCHE | 2X80 EN C/L DESGANCHE | B23060300191 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1529 | 2023-06-03 | 67276 | keep | 0 | Jun | 2023 | 0.045821 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
MAYAGÃœEZ | 2023-06-03 11:30 | 2023-06-03 11:31 | 574 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M23060300274 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 574 | keep | 0 | Jun | 2023 | 0.00039095 | 0.00039095 | Momentary | FALSE | FALSE | Not_TMED_Event | 574
MAYAGÃœEZ | 2023-06-03 11:30 | 2023-06-03 11:31 | 2493 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M23060300274 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 2493 | keep | 0 | Jun | 2023 | 0.001698 | 0.001698 | Momentary | FALSE | FALSE | Not_TMED_Event | 2493
MAYAGÃœEZ | 2023-06-03 11:30 | 2023-06-03 11:31 | 1415 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M23060300274 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 1415 | keep | 0 | Jun | 2023 | 0.00096375 | 0.00096375 | Momentary | FALSE | FALSE | Not_TMED_Event | 1415
MAYAGÃœEZ | 2023-06-03 11:30 | 2023-06-03 11:31 | 1428 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M23060300274 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 1428 | keep | 0 | Jun | 2023 | 0.0009726 | 0.0009726 | Momentary | FALSE | FALSE | Not_TMED_Event | 1428
MAYAGÃœEZ | 2023-06-03 11:30 | 2023-06-03 11:31 | 1036 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M23060300274 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 1036 | keep | 0 | Jun | 2023 | 0.00070561 | 0.00070561 | Momentary | FALSE | FALSE | Not_TMED_Event | 1036
MAYAGÃœEZ | 2023-06-03 11:30 | 2023-06-03 11:31 | 382 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300277 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 382 | keep | 0 | Jun | 2023 | 0.00026018 | 0.00026018 | Momentary | FALSE | FALSE | Not_TMED_Event | 382
MAYAGÃœEZ | 2023-06-03 11:30 | 2023-06-03 11:31 | 39 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300277 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 39 | keep | 0 | Jun | 2023 | 2.6563e-05 | 2.6563e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 39
MAYAGÃœEZ | 2023-06-03 11:30 | 2023-06-03 11:31 | 2366 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300280 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 2366 | keep | 0 | Jun | 2023 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
MAYAGÃœEZ | 2023-06-03 11:30 | 2023-06-03 11:31 | 1337 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300280 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 1337 | keep | 0 | Jun | 2023 | 0.00091062 | 0.00091062 | Momentary | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2023-06-03 11:30 | 2023-06-03 11:31 | 709 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300280 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 709 | keep | 0 | Jun | 2023 | 0.0004829 | 0.0004829 | Momentary | FALSE | FALSE | Not_TMED_Event | 709
UTUADO | 2023-06-03 11:31 | 2023-06-03 12:00 | 140 | 0:29 | P | DESGANCHE | 2 X 65 EN CL SE REALIZO DESGANCHE DE BAMBUS | A23060300007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 29 | 2023-06-03 | 4060 | keep | 0 | Jun | 2023 | 0.0027652 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
SAN JUAN | 2023-06-03 11:32 | 2023-06-03 21:29 | 12 | 9:57 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR DESGANCHE | S23060300203 | New_Event | Vegetation Contact | Include | Include | Vegetation | 597 | 2023-06-03 | 7164 | keep | 0 | Jun | 2023 | 0.0048794 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2023-06-03 11:38 | 2023-06-03 12:02 | 102 | 0:24 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C23060300233 | New_Event | Vegetation Contact | Include | Include | Vegetation | 24 | 2023-06-03 | 2448 | keep | 0 | Jun | 2023 | 0.0016673 | 6.9472e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 102
MAYAGÃœEZ | 2023-06-03 11:44 | 2023-06-03 18:05 | 200 | 6:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23060300284 | New_Event | Vegetation Contact | Include | Include | Vegetation | 381 | 2023-06-03 | 76200 | keep | 0 | Jun | 2023 | 0.051899 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2023-06-03 11:53 | 2023-06-03 13:28 | 128 | 1:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C23060300252 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2023-06-03 | 12160 | keep | 0 | Jun | 2023 | 0.0082821 | 8.718e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 128
BARRANQUITAS | 2023-06-03 11:53 | 2023-06-03 14:14 | 40 | 2:21 | P | DESGANCHE | 1 X 40 EN C/L | C23060300251 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2023-06-03 | 5640 | keep | 0 | Jun | 2023 | 0.0038414 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-06-03 11:56 | 2023-06-03 14:46 | 1089 | 2:50 | T | AISLADOR ROTO, PARTIDO O SAFADO | CG-230603-02 RECERRO INTERRUPTOR REALIZO LAS 3 OPERACIONES SE REEMPLAZO DISCO ROTO EN RISER DE SALIDA DEL ALIMENTADOR | C23060300258 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 170 | 2023-06-03 | 185130 | keep | 0 | Jun | 2023 | 0.12609 | 0.00074171 | Sustained | FALSE | FALSE | Not_TMED_Event | 1089
CAGUAS | 2023-06-03 11:57 | 2023-06-03 15:20 | 62 | 3:23 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE DESENRREDO CONDUCTORES CON LA VARETA | C23060300257 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 203 | 2023-06-03 | 12586 | keep | 0 | Jun | 2023 | 0.0085723 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
CANOVANAS | 2023-06-03 12:00 | 2023-06-03 12:03 | 1937 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CERRADO X CONTROL | R23060300058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-06-03 | 5811 | keep | 0 | Jun | 2023 | 0.0039578 | 0.0013193 | Momentary | FALSE | FALSE | Not_TMED_Event | 1937
BAYAMON | 2023-06-03 12:00 | 2023-06-03 12:04 | 61 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B23060300211 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-06-03 | 244 | keep | 0 | Jun | 2023 | 0.00016619 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
SAN JUAN | 2023-06-03 12:04 | 2023-06-03 12:05 | 1799 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23060300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 1799 | keep | 0 | Jun | 2023 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
UTUADO | 2023-06-03 12:04 | 2023-06-03 22:35 | 50 | 10:31 | P | CONDUCTOR ROTO O ABIERTO | 2 X 40 Y 2 X 30 EN DISTINTOS CORTES DE LINEA SE DESGANCHO Y SE REPARO LINEA PRIMARIAA ROTA | A23060300139 | New_Event | Primary Wire Break | Include | Include | Equipment | 631 | 2023-06-03 | 31550 | keep | 0 | Jun | 2023 | 0.021489 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-06-03 12:06 | 2023-06-03 15:36 | 100 | 3:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA POR FUERTES VIENTOS | M23060300296 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 210 | 2023-06-03 | 21000 | keep | 0 | Jun | 2023 | 0.014303 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-06-03 12:10 | 2023-06-03 12:11 | 1070 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23060300021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 1070 | keep | 0 | Jun | 2023 | 0.00072877 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
SAN JUAN | 2023-06-03 12:12 | 2023-06-03 12:13 | 1384 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 1000 | S23060300382 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 1384 | keep | 0 | Jun | 2023 | 0.00094264 | 0.00094264 | Momentary | FALSE | FALSE | Not_TMED_Event | 1384
SAN JUAN | 2023-06-03 12:12 | 2023-06-03 12:13 | 869 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LINEA 1000 | S23060300382 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 869 | keep | 0 | Jun | 2023 | 0.00059187 | 0.00059187 | Momentary | FALSE | FALSE | Not_TMED_Event | 869
CAGUAS | 2023-06-03 12:12 | 2023-06-03 12:13 | 906 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C2306030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 906 | keep | 0 | Jun | 2023 | 0.00061707 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
BAYAMON | 2023-06-03 12:13 | 2023-06-03 16:42 | 31 | 4:29 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO CONDUCTOR EN EL SUELO VER GOI BY-230603-03 | S23060300244 | New_Event | Primary Wire Break | Include | Include | Equipment | 269 | 2023-06-03 | 8339 | keep | 0 | Jun | 2023 | 0.0056797 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
MAYAGÃœEZ | 2023-06-03 12:14 | 2023-06-03 12:16 | 574 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300309 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-03 | 1148 | keep | 0 | Jun | 2023 | 0.0007819 | 0.00039095 | Momentary | FALSE | FALSE | Not_TMED_Event | 574
MAYAGÃœEZ | 2023-06-03 12:14 | 2023-06-03 12:16 | 2493 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300309 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-03 | 4986 | keep | 0 | Jun | 2023 | 0.0033959 | 0.001698 | Momentary | FALSE | FALSE | Not_TMED_Event | 2493
MAYAGÃœEZ | 2023-06-03 12:14 | 2023-06-03 12:16 | 1415 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300309 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-03 | 2830 | keep | 0 | Jun | 2023 | 0.0019275 | 0.00096375 | Momentary | FALSE | FALSE | Not_TMED_Event | 1415
MAYAGÃœEZ | 2023-06-03 12:14 | 2023-06-03 12:16 | 1428 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300309 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-03 | 2856 | keep | 0 | Jun | 2023 | 0.0019452 | 0.0009726 | Momentary | FALSE | FALSE | Not_TMED_Event | 1428
MAYAGÃœEZ | 2023-06-03 12:14 | 2023-06-03 12:16 | 1036 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300309 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-03 | 2072 | keep | 0 | Jun | 2023 | 0.0014112 | 0.00070561 | Momentary | FALSE | FALSE | Not_TMED_Event | 1036
MAYAGÃœEZ | 2023-06-03 12:14 | 2023-06-03 12:16 | 382 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300314 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-03 | 764 | keep | 0 | Jun | 2023 | 0.00052036 | 0.00026018 | Momentary | FALSE | FALSE | Not_TMED_Event | 382
MAYAGÃœEZ | 2023-06-03 12:14 | 2023-06-03 12:16 | 39 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300314 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-03 | 78 | keep | 0 | Jun | 2023 | 5.3125e-05 | 2.6563e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 39
MAYAGÃœEZ | 2023-06-03 12:14 | 2023-06-03 12:16 | 2366 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300317 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-03 | 4732 | keep | 0 | Jun | 2023 | 0.0032229 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
MAYAGÃœEZ | 2023-06-03 12:14 | 2023-06-03 12:16 | 1337 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300317 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-03 | 2674 | keep | 0 | Jun | 2023 | 0.0018212 | 0.00091062 | Momentary | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2023-06-03 12:14 | 2023-06-03 12:16 | 709 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300317 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-03 | 1418 | keep | 0 | Jun | 2023 | 0.00096579 | 0.0004829 | Momentary | FALSE | FALSE | Not_TMED_Event | 709
BARRANQUITAS | 2023-06-03 12:15 | 2023-06-03 17:02 | 114 | 4:47 | P | DESGANCHE | 1 X 50 Y 1 X 65 EN CORTES DE LINEA SE RETIRO BAMBUA DE LA LINEA | C23060300271 | New_Event | Vegetation Contact | Include | Include | Vegetation | 287 | 2023-06-03 | 32718 | keep | 0 | Jun | 2023 | 0.022284 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
BARRANQUITAS | 2023-06-03 12:16 | 2023-06-03 16:00 | 75 | 3:44 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | C23060300274 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2023-06-03 | 16800 | keep | 0 | Jun | 2023 | 0.011442 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2023-06-03 12:17 | 2023-06-03 18:30 | 60 | 6:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 40 Y 1 X 30 EN DISTINTOS CORTES DE LINEA POR FUERTE VIENTO | A23060300143 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 373 | 2023-06-03 | 22380 | keep | 0 | Jun | 2023 | 0.015243 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-06-03 12:18 | 2023-06-03 13:10 | 10 | 0:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR BAJANTE SECUNDARIO | R23060300060 | New_Event | Secondary Wire Break | Include | Include | Equipment | 52 | 2023-06-03 | 520 | keep | 0 | Jun | 2023 | 0.00035417 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-06-03 12:23 | 2023-06-03 13:48 | 574 | 1:25 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300335 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2023-06-03 | 48790 | keep | 0 | Jun | 2023 | 0.033231 | 0.00039095 | Sustained | FALSE | FALSE | Not_TMED_Event | 574
MAYAGÃœEZ | 2023-06-03 12:23 | 2023-06-03 13:48 | 2493 | 1:25 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300335 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2023-06-03 | 211905 | keep | 0 | Jun | 2023 | 0.14433 | 0.001698 | Sustained | FALSE | FALSE | Not_TMED_Event | 2493
MAYAGÃœEZ | 2023-06-03 12:23 | 2023-06-03 13:48 | 1415 | 1:25 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300335 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2023-06-03 | 120275 | keep | 0 | Jun | 2023 | 0.081919 | 0.00096375 | Sustained | FALSE | FALSE | Not_TMED_Event | 1415
MAYAGÃœEZ | 2023-06-03 12:23 | 2023-06-03 13:48 | 1428 | 1:25 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300335 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2023-06-03 | 121380 | keep | 0 | Jun | 2023 | 0.082671 | 0.0009726 | Sustained | FALSE | FALSE | Not_TMED_Event | 1428
MAYAGÃœEZ | 2023-06-03 12:23 | 2023-06-03 13:48 | 1036 | 1:25 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300335 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2023-06-03 | 88060 | keep | 0 | Jun | 2023 | 0.059977 | 0.00070561 | Sustained | FALSE | FALSE | Not_TMED_Event | 1036
MAYAGÃœEZ | 2023-06-03 12:23 | 2023-06-03 13:48 | 382 | 1:25 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300337 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2023-06-03 | 32470 | keep | 0 | Jun | 2023 | 0.022115 | 0.00026018 | Sustained | FALSE | FALSE | Not_TMED_Event | 382
MAYAGÃœEZ | 2023-06-03 12:23 | 2023-06-03 13:48 | 39 | 1:25 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300337 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2023-06-03 | 3315 | keep | 0 | Jun | 2023 | 0.0022578 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
MAYAGÃœEZ | 2023-06-03 12:23 | 2023-06-03 13:48 | 2366 | 1:25 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300338 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2023-06-03 | 201110 | keep | 0 | Jun | 2023 | 0.13698 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
MAYAGÃœEZ | 2023-06-03 12:23 | 2023-06-03 13:48 | 1337 | 1:25 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300338 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2023-06-03 | 113645 | keep | 0 | Jun | 2023 | 0.077403 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2023-06-03 12:23 | 2023-06-03 13:48 | 709 | 1:25 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M23060300338 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2023-06-03 | 60265 | keep | 0 | Jun | 2023 | 0.041046 | 0.0004829 | Sustained | FALSE | FALSE | Not_TMED_Event | 709
BAYAMON | 2023-06-03 12:23 | 2023-06-03 12:33 | 80 | 0:10 | P | DESGANCHE | 1 X 100 Y 2 X 80 EN C/L DESGANCHE | B23060300226 | New_Event | Vegetation Contact | Include | Include | Vegetation | 10 | 2023-06-03 | 800 | keep | 0 | Jun | 2023 | 0.00054488 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2023-06-03 12:26 | 2023-06-03 13:29 | 1296 | 1:03 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 18400 DE BARRANQUITAS AL ABANICO 95% DE LA CARGA POR EL 9605-01 EN SERVICIO | C23060300283 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 63 | 2023-06-03 | 81648 | keep | 0 | Jun | 2023 | 0.05561 | 0.0008827 | Sustained | FALSE | FALSE | Not_TMED_Event | 1296
BARRANQUITAS | 2023-06-03 12:26 | 2023-06-03 13:29 | 2410 | 1:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 18400 DE BARRANQUITAS AL ABANICO LLEVA 95% DEL 9602-03 EN SERVICIO | C23060300283 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 63 | 2023-06-03 | 151830 | keep | 0 | Jun | 2023 | 0.10341 | 0.0016414 | Sustained | FALSE | FALSE | Not_TMED_Event | 2410
BARRANQUITAS | 2023-06-03 12:26 | 2023-06-03 13:29 | 2826 | 1:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 18400 DE BARRANQUITAS AL ABANICO | C23060300283 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 63 | 2023-06-03 | 178038 | keep | 0 | Jun | 2023 | 0.12126 | 0.0019248 | Sustained | FALSE | FALSE | Not_TMED_Event | 2826
BAYAMON | 2023-06-03 12:28 | 2023-06-03 12:29 | 1070 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23060300233 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 1070 | keep | 0 | Jun | 2023 | 0.00072877 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2023-06-03 12:28 | 2023-06-03 12:33 | 257 | 0:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L 1 X 30 EN C/L FUERTES VIENTOS | B23060300231 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 5 | 2023-06-03 | 1285 | keep | 0 | Jun | 2023 | 0.00087521 | 0.00017504 | Momentary | FALSE | FALSE | Not_TMED_Event | 257
SAN JUAN | 2023-06-03 12:29 | 2023-06-03 16:07 | 760 | 3:38 | T | ALIMENTADOR AMARRADO | SE REMPLAZO MACHETE Y SE ENERGIZO CARGA SU CARGA POR 1201-01 | S23060300348 | New_Event | Feeder Load Transferred | Include | Include | Other | 218 | 2023-06-03 | 165680 | keep | 0 | Jun | 2023 | 0.11284 | 0.00051763 | Sustained | FALSE | FALSE | Not_TMED_Event | 760
BAYAMON | 2023-06-03 12:29 | 2023-06-03 12:34 | 1368 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23060300274 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-06-03 | 6840 | keep | 0 | Jun | 2023 | 0.0046587 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-03 12:30 | 2023-06-03 12:46 | 137 | 0:16 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR A PETICION DE PERSONAL PARA CERRAR PUENTE ABIERTO/REMPLAZAR MACHETE SJ-230603-03 - LLEVA EL 1201-02 - 90% DEL 1201-01 EN SERVICIO | S23060300348 | New_Event | Switch Failure | Include | Include | Equipment | 16 | 2023-06-03 | 2192 | keep | 0 | Jun | 2023 | 0.001493 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
BARRANQUITAS | 2023-06-03 12:30 | 2023-06-03 19:06 | 16 | 6:36 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | C23060300287 | New_Event | Vegetation Contact | Include | Include | Vegetation | 396 | 2023-06-03 | 6336 | keep | 0 | Jun | 2023 | 0.0043154 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2023-06-03 12:32 | 2023-06-03 14:55 | 1681 | 2:23 | T | NO SE REPORTO CAUSA | DISPARO SE ABRIO MACHETE PARA SECCIONALIZAR Y CERRAR INTERRUPTOR 70% EN SERVICIO | S23060300272 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 143 | 2023-06-03 | 240383 | keep | 0 | Jun | 2023 | 0.16372 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
BAYAMON | 2023-06-03 12:33 | 2023-06-03 12:34 | 4176 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | B23060300234 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-06-03 | 4176 | keep | 0 | Jun | 2023 | 0.0028443 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-03 12:34 | 2023-06-03 14:26 | 43 | 1:52 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23060300028 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 112 | 2023-06-03 | 4816 | keep | 0 | Jun | 2023 | 0.0032802 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
BAYAMON | 2023-06-03 12:34 | 2023-06-03 14:29 | 80 | 1:55 | P | DESGANCHE | 1 X 100 Y 2 X 80 EN C/L DESGANCHE | B23060300226 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2023-06-03 | 9200 | keep | 0 | Jun | 2023 | 0.0062661 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-06-03 12:34 | 2023-06-03 14:29 | 257 | 1:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L 1 X 30 EN C/L FUERTES VIENTOS | B23060300231 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 115 | 2023-06-03 | 29555 | keep | 0 | Jun | 2023 | 0.02013 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-06-03 12:35 | 2023-06-03 13:30 | 90 | 0:55 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBU | M23060300211 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2023-06-03 | 4950 | keep | 0 | Jun | 2023 | 0.0033714 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2023-06-03 12:38 | 2023-06-03 13:49 | 22 | 1:11 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETE 100% EN SERVICIO | S23060300102 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 71 | 2023-06-03 | 1562 | keep | 0 | Jun | 2023 | 0.0010639 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-03 12:45 | 2023-06-03 12:47 | 1501 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B23060300239 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-03 | 3002 | keep | 0 | Jun | 2023 | 0.0020446 | 0.0010223 | Momentary | FALSE | FALSE | Not_TMED_Event | 1501
CAGUAS | 2023-06-03 12:45 | 2023-06-04 17:52 | 85 | 29:07 | P | DESGANCHE | ABRIO MACHETES PARA DESGANCHAR Y LEVANTAR CONDUCTORES | C23060300291 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1747 | 2023-06-03 | 148495 | keep | 0 | Jun | 2023 | 0.10114 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
SAN JUAN | 2023-06-03 12:46 | 2023-06-03 16:07 | 13 | 3:21 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE Y SE ENERGIZO CARGA LLEVA 1201-02 | S23060300348 | Partial_restoration | Switch Failure | Include | Include | Equipment | 201 | 2023-06-03 | 2613 | keep | 0 | Jun | 2023 | 0.0017797 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-06-03 12:49 | 2023-06-03 13:19 | 1648 | 0:30 | T | ANIMAL | DISPARO DE INTERRUPTOR RR EN OFF PARA LA ORDEN 9002 LLEVA 20% DEL 2402-02 CERRADO ELECTRICAMENTE | R23060300061 | New_Event | Animals | Include | Include | Wildlife | 30 | 2023-06-03 | 49440 | keep | 0 | Jun | 2023 | 0.033673 | 0.0011224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-06-03 12:49 | 2023-06-03 13:19 | 838 | 0:30 | P | ALIMENTADOR AMARRADO | DISPARO DEL 2302-03 | R23060300061 | New_Event | Feeder Load Transferred | Include | Include | Other | 30 | 2023-06-03 | 25140 | keep | 0 | Jun | 2023 | 0.017123 | 0.00057076 | Sustained | FALSE | FALSE | Not_TMED_Event | 838
CANOVANAS | 2023-06-03 12:52 | 2023-06-03 17:42 | 36 | 4:50 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R23060300062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 290 | 2023-06-03 | 10440 | keep | 0 | Jun | 2023 | 0.0071106 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
AGUADILLA | 2023-06-03 12:54 | 2023-06-03 15:00 | 80 | 2:06 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23060300352 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2023-06-03 | 10080 | keep | 0 | Jun | 2023 | 0.0068654 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-06-03 12:55 | 2023-06-03 13:53 | 623 | 0:58 | P | DESGANCHE | 1 X 140 EN C/L SE DESGANCHO | B23060300244 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2023-06-03 | 36134 | keep | 0 | Jun | 2023 | 0.024611 | 0.00042432 | Sustained | FALSE | FALSE | Not_TMED_Event | 623
UTUADO | 2023-06-03 12:58 | 2023-06-04 00:28 | 150 | 11:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA POR FUERTE VIENTO | A23060300153 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 690 | 2023-06-03 | 103500 | keep | 0 | Jun | 2023 | 0.070493 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-06-03 13:02 | 2023-06-03 14:49 | 10 | 1:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23060300311 | New_Event | Secondary Wire Break | Include | Include | Equipment | 107 | 2023-06-03 | 1070 | keep | 0 | Jun | 2023 | 0.00072877 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-06-03 13:04 | 2023-06-04 00:37 | 50 | 11:33 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | B23060300252 | New_Event | Vegetation Contact | Include | Include | Vegetation | 693 | 2023-06-03 | 34650 | keep | 0 | Jun | 2023 | 0.0236 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-06-03 13:04 | 2023-06-03 13:05 | 2147 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | B23060300254 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-06-03 | 2147 | keep | 0 | Jun | 2023 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
CAGUAS | 2023-06-03 13:05 | 2023-06-03 13:06 | 777 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23060300302 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 777 | keep | 0 | Jun | 2023 | 0.00052921 | 0.00052921 | Momentary | FALSE | FALSE | Not_TMED_Event | 777
AGUADILLA | 2023-06-03 13:05 | 2023-06-03 16:40 | 100 | 3:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23060300544 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2023-06-03 | 21500 | keep | 0 | Jun | 2023 | 0.014644 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-06-03 13:05 | 2023-06-03 14:30 | 75 | 1:25 | P | DESGANCHE | 3 X 100 EN C/L | B23060300264 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 85 | 2023-06-03 | 6375 | keep | 0 | Jun | 2023 | 0.004342 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2023-06-03 13:06 | 2023-06-03 13:07 | 1352 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23060300363 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 1352 | keep | 0 | Jun | 2023 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2023-06-03 13:06 | 2023-06-03 13:07 | 871 | 0:01 | T | ALIMENTADOR AMARRADO | CARGA POR 6012-05 | M23060300363 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-03 | 871 | keep | 0 | Jun | 2023 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
SAN JUAN | 2023-06-03 13:08 | 2023-06-03 21:20 | 12 | 8:12 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR DESGANCHE | S23060300318 | New_Event | Vegetation Contact | Include | Include | Vegetation | 492 | 2023-06-03 | 5904 | keep | 0 | Jun | 2023 | 0.0040212 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-06-03 13:09 | 2023-06-03 14:29 | 3871 | 1:20 | T | CONDUCTOR ARRIADO O CRUZADO | SE DESCRUZARON LINEAS Y SE CERRO BKR POR CONTROL | B23060300259 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 80 | 2023-06-03 | 309680 | keep | 0 | Jun | 2023 | 0.21092 | 0.0026365 | Sustained | FALSE | FALSE | Not_TMED_Event | 3871
MAYAGÃœEZ | 2023-06-03 13:11 | 2023-06-03 13:12 | 4641 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23060300370 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 4641 | keep | 0 | Jun | 2023 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
ARECIBO | 2023-06-03 13:11 | 2023-06-03 17:10 | 30 | 3:59 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | P23060300549 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2023-06-03 | 7170 | keep | 0 | Jun | 2023 | 0.0048835 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2023-06-03 13:14 | 2023-06-03 14:21 | 6 | 1:07 | P | CONDUCTOR ROTO O ABIERTO | CERRO PUENTE DE LINEA A CAJA | R23060300064 | New_Event | Primary Wire Break | Include | Include | Equipment | 67 | 2023-06-03 | 402 | keep | 0 | Jun | 2023 | 0.0002738 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2023-06-03 13:17 | 2023-06-03 21:46 | 6 | 8:29 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA POR AVE | P23060300554 | New_Event | Animals | Include | Include | Wildlife | 509 | 2023-06-03 | 3054 | keep | 0 | Jun | 2023 | 0.0020801 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-06-03 13:18 | 2023-06-03 13:21 | 1420 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1526-02 LLEVA LA CARGA DEL 1530-06 SE CERRO POR CONTROL | S23060300323 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-06-03 | 4260 | keep | 0 | Jun | 2023 | 0.0029015 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
SAN JUAN | 2023-06-03 13:18 | 2023-06-03 13:21 | 437 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1526-02 LLEVA LA CARGA DEL 1530-06 SE CERRO POR CONTROL | S23060300323 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-06-03 | 1311 | keep | 0 | Jun | 2023 | 0.00089292 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
CANOVANAS | 2023-06-03 13:19 | 2023-06-03 16:10 | 129 | 2:51 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | R23060300070 | Partial_restoration | Animals | Include | Include | Wildlife | 171 | 2023-06-03 | 22059 | keep | 0 | Jun | 2023 | 0.015024 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-06-03 13:20 | 2023-06-03 21:25 | 150 | 8:05 | P | CAUSAS EXTERNAS | 1 X 100 Y 1 X 80 EN CORTES DE LINEA POR LINEAS PRIMARIAS ROBADAS | M23060300426 | New_Event | Damage From Public | Include | Include | Public | 485 | 2023-06-03 | 72750 | keep | 0 | Jun | 2023 | 0.04955 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-06-03 13:24 | 2023-06-03 13:27 | 3350 | 0:03 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR RR EN OFF H/O 9002 20% X 2302-03 | R23060300065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-06-03 | 10050 | keep | 0 | Jun | 2023 | 0.006845 | 0.0022817 | Momentary | FALSE | FALSE | Not_TMED_Event | 3350
BARRANQUITAS | 2023-06-03 13:28 | 2023-06-03 15:06 | 2192 | 1:38 | T | DESGANCHE | CG-230603-03 DISPARO INTERRUPTOR SE SECCIONALIZO CERRADO POR CONTROL EN SERVICIO 95% | C23060300315 | New_Event | Vegetation Contact | Include | Include | Vegetation | 98 | 2023-06-03 | 214816 | keep | 0 | Jun | 2023 | 0.14631 | 0.001493 | Sustained | FALSE | FALSE | Not_TMED_Event | 2192
ARECIBO | 2023-06-03 13:29 | 2023-06-03 13:41 | 1 | 0:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A23060200185 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 12 | 2023-06-03 | 12 | keep | 0 | Jun | 2023 | 8.1731e-06 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-03 13:30 | 2023-06-03 14:55 | 1368 | 1:25 | T | NO SE REPORTO CAUSA | DISPARO SE PATRULLO Y SE ABRIO MACHETE PARA SECCIOANLIZAR SE CERRO INTERRUPTOR 70% EN SERVICIO | S23060300335 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 85 | 2023-06-03 | 116280 | keep | 0 | Jun | 2023 | 0.079198 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-06-03 13:30 | 2023-06-04 08:06 | 6 | 18:36 | P | DESGANCHE | 1X15 EN XMR DESGANCHE PRIMARIO | B23060300270 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1116 | 2023-06-03 | 6696 | keep | 0 | Jun | 2023 | 0.0045606 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-06-03 13:33 | 2023-06-03 17:40 | 23 | 4:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 20 EN XMR SE REPARO SECUNDARIA | S23060300338 | New_Event | Secondary Wire Break | Include | Include | Equipment | 247 | 2023-06-03 | 5681 | keep | 0 | Jun | 2023 | 0.0038693 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
SAN JUAN | 2023-06-03 13:34 | 2023-06-03 13:42 | 4291 | 0:08 | T | FUEGO | DISPARO SEVERIFICO PERSONAL FUERA Y SE PROBO QUEDO EN SERVICIO | S23060300335 | New_Event | Fire | Include | Include | Public | 8 | 2023-06-03 | 34328 | keep | 0 | Jun | 2023 | 0.023381 | 0.0029226 | Sustained | FALSE | FALSE | Not_TMED_Event | 4291
CAGUAS | 2023-06-03 13:34 | 2023-06-03 17:08 | 173 | 3:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 Y 1 X 65 EN CORTES DE LINEA MAL TIEMPO VIENTOS | C23060300314 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 214 | 2023-06-03 | 37022 | keep | 0 | Jun | 2023 | 0.025216 | 0.00011783 | Sustained | FALSE | FALSE | Not_TMED_Event | 173
BARRANQUITAS | 2023-06-03 13:38 | 2023-06-03 18:17 | 98 | 4:39 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C23060300317 | New_Event | Vegetation Contact | Include | Include | Vegetation | 279 | 2023-06-03 | 27342 | keep | 0 | Jun | 2023 | 0.018623 | 6.6747e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 98
BAYAMON | 2023-06-03 13:40 | 2023-06-03 13:43 | 61 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B23060300275 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-06-03 | 183 | keep | 0 | Jun | 2023 | 0.00012464 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
ARECIBO | 2023-06-03 13:41 | 2023-06-03 13:42 | 3431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | A23060300165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 3431 | keep | 0 | Jun | 2023 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
AGUADILLA | 2023-06-03 13:42 | 2023-06-03 13:43 | 1047 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23060300391 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 1047 | keep | 0 | Jun | 2023 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
ARECIBO | 2023-06-03 13:42 | 2023-06-03 14:01 | 1 | 0:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A23060200185 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 19 | 2023-06-03 | 19 | keep | 0 | Jun | 2023 | 1.2941e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-03 13:47 | 2023-06-03 19:53 | 67 | 6:06 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO CAUSA | S23060300345 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 366 | 2023-06-03 | 24522 | keep | 0 | Jun | 2023 | 0.016702 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
BARRANQUITAS | 2023-06-03 13:48 | 2023-06-03 13:52 | 3296 | 0:04 | T | DESGANCHE | DISPARO INTERRUPTOR LLEVA LA CARGA DEL 9602-04 Y 5% DEL 9602-03 CERRADO POR CONTROL | C2306030000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 4 | 2023-06-03 | 13184 | keep | 0 | Jun | 2023 | 0.0089796 | 0.0022449 | Momentary | FALSE | FALSE | Not_TMED_Event | 3296
BARRANQUITAS | 2023-06-03 13:48 | 2023-06-03 13:52 | 63 | 0:04 | P | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR 5% DE LA CARGA POR EL 9601-02 CERRADO POR CONTROL | C2306030000X | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-06-03 | 252 | keep | 0 | Jun | 2023 | 0.00017164 | 4.2909e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 63
BARRANQUITAS | 2023-06-03 13:48 | 2023-06-03 13:52 | 2937 | 0:04 | T | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR CARGA POR EL 9601-02 CERRADO POR CONTROL | C2306030000X | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-06-03 | 11748 | keep | 0 | Jun | 2023 | 0.0080015 | 0.0020004 | Momentary | FALSE | FALSE | Not_TMED_Event | 2937
SAN JUAN | 2023-06-03 13:50 | 2023-06-03 13:53 | 590 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23060300349 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-06-03 | 1770 | keep | 0 | Jun | 2023 | 0.0012055 | 0.00040185 | Momentary | FALSE | FALSE | Not_TMED_Event | 590
BAYAMON | 2023-06-03 13:53 | 2023-06-03 13:54 | 2096 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | B23060300281 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-06-03 | 2096 | keep | 0 | Jun | 2023 | 0.0014276 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-03 13:54 | 2023-06-03 23:16 | 623 | 9:22 | P | DESGANCHE | 1 X 140 EN C/L SE DESGANCHO | B23060300244 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 562 | 2023-06-03 | 350126 | keep | 0 | Jun | 2023 | 0.23847 | 0.00042432 | Sustained | FALSE | FALSE | Not_TMED_Event | 623
SAN JUAN | 2023-06-03 13:55 | 2023-06-03 14:51 | 4291 | 0:56 | T | FUEGO | DISPARO ALIMENTADOR SE PATRULLO SE CONTROL FUEGO EN EL MONTE Y TIRO ALAMBRE EN EL PISO SE SECCIONALIZO Y SE CERRO N/O AL 1204-03 100% EN SERVICIO | S23060300000 | Partial_restoration | Fire | Include | Include | Public | 56 | 2023-06-03 | 240296 | keep | 0 | Jun | 2023 | 0.16366 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-06-03 13:55 | 2023-06-03 17:05 | 150 | 3:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 Y 1 X 100 EN CORTES DE LINEA POR FUERTES VIENTOS | M23060300399 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 190 | 2023-06-03 | 28500 | keep | 0 | Jun | 2023 | 0.019411 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2023-06-03 13:57 | 2023-06-03 17:40 | 60 | 3:43 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A23060300169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 223 | 2023-06-03 | 13380 | keep | 0 | Jun | 2023 | 0.0091131 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-06-03 13:58 | 2023-06-03 13:59 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2306030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 2234 | keep | 0 | Jun | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2023-06-03 14:00 | 2023-06-03 16:18 | 959 | 2:18 | T | ERROR HUMANO | PERSONAL DE CAMPO SOLICITA ABRIR INTERRUPTOR POR CONTROL POR ALAMBRE EN EL SUELO Y ESTE NO ERA EL FEEDER CARGA X 1904-07 | S23060300359 | New_Event | Human Error | Include | Include | Other | 138 | 2023-06-03 | 132342 | keep | 0 | Jun | 2023 | 0.090138 | 0.00065317 | Sustained | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-06-03 14:00 | 2023-06-03 16:18 | 1264 | 2:18 | T | ERROR HUMANO | PERSONAL DE CAMPO SOLICITA ABRIR INTERRUPTOR POR CONTROL POR ALAMBRE EN EL SUELO Y ESTE NO ERA EL FEEDER CARGA X 1904-07 | S23060300359 | New_Event | Human Error | Include | Include | Other | 138 | 2023-06-03 | 174432 | keep | 0 | Jun | 2023 | 0.1188 | 0.0008609 | Sustained | FALSE | FALSE | Not_TMED_Event | 1264
ARECIBO | 2023-06-03 14:01 | 2023-06-03 14:02 | 3431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23060300171 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 3431 | keep | 0 | Jun | 2023 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2023-06-03 14:02 | 2023-06-03 14:19 | 1 | 0:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A23060200185 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 17 | 2023-06-03 | 17 | keep | 0 | Jun | 2023 | 1.1579e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-03 14:03 | 2023-06-03 14:04 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2306030000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 2234 | keep | 0 | Jun | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
CAGUAS | 2023-06-03 14:05 | 2023-06-03 14:06 | 851 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 50% DE SU CARGA POR EL 3103-02 EN SERVICIO | C23060300348 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 851 | keep | 0 | Jun | 2023 | 0.00057961 | 0.00057961 | Momentary | FALSE | FALSE | Not_TMED_Event | 851
BARRANQUITAS | 2023-06-03 14:05 | 2023-06-03 14:08 | 2280 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CARGA POR 9902-03 POR B/I SE VERIFICO PERSONAL DE SUBESTACIONES FUERA, CERRADO POR CONTROL | C2306030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-06-03 | 6840 | keep | 0 | Jun | 2023 | 0.0046587 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2023-06-03 14:05 | 2023-06-03 14:08 | 1617 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVA EL 9902-02 POR B/I SE VERIFICO PERSONAL DE SUBESTACIONES FUERA, CERRADO POR CONTROL | C2306030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-06-03 | 4851 | keep | 0 | Jun | 2023 | 0.003304 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
SAN JUAN | 2023-06-03 14:06 | 2023-06-03 14:10 | 643 | 0:04 | T | ALIMENTADOR AMARRADO | DISPARO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1530-09 | S23060300366 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-06-03 | 2572 | keep | 0 | Jun | 2023 | 0.0017518 | 0.00043794 | Momentary | FALSE | FALSE | Not_TMED_Event | 643
SAN JUAN | 2023-06-03 14:06 | 2023-06-03 14:10 | 1310 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO LLEVA 1530-07 | S23060300366 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-06-03 | 5240 | keep | 0 | Jun | 2023 | 0.0035689 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
CAGUAS | 2023-06-03 14:08 | 2023-06-03 14:09 | 851 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVA 50% DE SU CARGA EN SERVICIO | C23060300354 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 851 | keep | 0 | Jun | 2023 | 0.00057961 | 0.00057961 | Momentary | FALSE | FALSE | Not_TMED_Event | 851
SAN JUAN | 2023-06-03 14:10 | 2023-06-03 16:16 | 50 | 2:06 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO CAUSA | S23060300379 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 126 | 2023-06-03 | 6300 | keep | 0 | Jun | 2023 | 0.0042909 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-06-03 14:13 | 2023-06-03 15:16 | 16 | 1:03 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO TRANSFORMASDOR PARA REPARAR TRIWIRE Y SE CAMBIO CALIBRE | P23060300594 | New_Event | Primary Wire Break | Include | Include | Equipment | 63 | 2023-06-03 | 1008 | keep | 0 | Jun | 2023 | 0.00068654 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BARRANQUITAS | 2023-06-03 14:14 | 2023-06-03 14:15 | 1604 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C2306030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 1604 | keep | 0 | Jun | 2023 | 0.0010925 | 0.0010925 | Momentary | FALSE | FALSE | Not_TMED_Event | 1604
BARRANQUITAS | 2023-06-03 14:15 | 2023-06-04 12:01 | 40 | 21:46 | P | DESGANCHE | 1 X 40 EN C/L | C23060300251 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1306 | 2023-06-03 | 52240 | keep | 0 | Jun | 2023 | 0.03558 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-06-03 14:17 | 2023-06-04 00:17 | 60 | 10:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR FUERTE VIENTO | A23060300181 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 600 | 2023-06-03 | 36000 | keep | 0 | Jun | 2023 | 0.024519 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2023-06-03 14:19 | 2023-06-03 14:20 | 3431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23060300183 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 3431 | keep | 0 | Jun | 2023 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2023-06-03 14:20 | 2023-06-03 14:21 | 1 | 0:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A23060200185 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 1 | 2023-06-03 | 1 | keep | 0 | Jun | 2023 | 6.811e-07 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-06-03 14:21 | 2023-06-03 14:22 | 3431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23060300185 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 3431 | keep | 0 | Jun | 2023 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2023-06-03 14:22 | 2023-06-03 14:25 | 1 | 0:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A23060200185 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 3 | 2023-06-03 | 3 | keep | 0 | Jun | 2023 | 2.0433e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-06-03 14:25 | 2023-06-03 14:26 | 3431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23060300188 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 3431 | keep | 0 | Jun | 2023 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2023-06-03 14:26 | 2023-06-03 14:33 | 1 | 0:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A23060200185 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 7 | 2023-06-03 | 7 | keep | 0 | Jun | 2023 | 4.7677e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-06-03 14:27 | 2023-06-03 14:28 | 4279 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23060300613 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 4279 | keep | 0 | Jun | 2023 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
MAYAGÃœEZ | 2023-06-03 14:27 | 2023-06-03 18:17 | 65 | 3:50 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE DESCRUZO LINEAS | M23060300230 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 230 | 2023-06-03 | 14950 | keep | 0 | Jun | 2023 | 0.010182 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2023-06-03 14:29 | 2023-06-03 14:30 | 959 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23060300322 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 959 | keep | 0 | Jun | 2023 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-06-03 14:29 | 2023-06-03 14:30 | 1382 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23060300322 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 1382 | keep | 0 | Jun | 2023 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2023-06-03 14:29 | 2023-06-03 14:30 | 663 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23060300322 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 663 | keep | 0 | Jun | 2023 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2023-06-03 14:29 | 2023-06-03 14:40 | 1514 | 0:11 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23060300321 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2023-06-03 | 16654 | keep | 0 | Jun | 2023 | 0.011343 | 0.0010312 | Sustained | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2023-06-03 14:29 | 2023-06-03 14:40 | 1105 | 0:11 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23060300321 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2023-06-03 | 12155 | keep | 0 | Jun | 2023 | 0.0082787 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2023-06-03 14:29 | 2023-06-03 14:30 | 4176 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23060300032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 4176 | keep | 0 | Jun | 2023 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2023-06-03 14:29 | 2023-06-03 14:30 | 252 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23060300032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 252 | keep | 0 | Jun | 2023 | 0.00017164 | 0.00017164 | Momentary | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2023-06-03 14:29 | 2023-06-03 14:30 | 2147 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23060300032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 2147 | keep | 0 | Jun | 2023 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2023-06-03 14:29 | 2023-06-03 14:30 | 2858 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23060300032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 2858 | keep | 0 | Jun | 2023 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
BAYAMON | 2023-06-03 14:30 | 2023-06-03 16:36 | 80 | 2:06 | P | DESGANCHE | 1 X 100 Y 2 X 80 EN C/L DESGANCHE | B23060300226 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 126 | 2023-06-03 | 10080 | keep | 0 | Jun | 2023 | 0.0068654 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-03 14:30 | 2023-06-04 05:24 | 257 | 14:54 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L 1 X 30 EN C/L FUERTES VIENTOS | B23060300231 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 894 | 2023-06-03 | 229758 | keep | 0 | Jun | 2023 | 0.15649 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-03 14:30 | 2023-06-03 18:06 | 75 | 3:36 | P | DESGANCHE | 3 X 100 EN C/L | B23060300264 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 216 | 2023-06-03 | 16200 | keep | 0 | Jun | 2023 | 0.011034 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-03 14:30 | 2023-06-03 17:23 | 80 | 2:53 | P | DESGANCHE | 2 X 50 Y 1 X 65 EN C/L SE DESGANCHO | B23060300173 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 173 | 2023-06-03 | 13840 | keep | 0 | Jun | 2023 | 0.0094264 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-03 14:31 | 2023-06-04 01:08 | 80 | 10:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA VIENTOS | B23060300309 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 637 | 2023-06-03 | 50960 | keep | 0 | Jun | 2023 | 0.034709 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2023-06-03 14:32 | 2023-06-03 20:02 | 139 | 5:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS | C23060300375 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 330 | 2023-06-03 | 45870 | keep | 0 | Jun | 2023 | 0.031242 | 9.4672e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 139
AGUADILLA | 2023-06-03 14:32 | 2023-06-04 09:30 | 100 | 18:58 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | M23060300421 | New_Event | Primary Wire Break | Include | Include | Equipment | 1138 | 2023-06-03 | 113800 | keep | 0 | Jun | 2023 | 0.077509 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-06-03 14:33 | 2023-06-03 14:34 | 3431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23060300192 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 3431 | keep | 0 | Jun | 2023 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2023-06-03 14:34 | 2023-06-03 14:50 | 1 | 0:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A23060200185 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 16 | 2023-06-03 | 16 | keep | 0 | Jun | 2023 | 1.0898e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-03 14:40 | 2023-06-04 08:14 | 36 | 17:34 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | B23060300041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1054 | 2023-06-03 | 37944 | keep | 0 | Jun | 2023 | 0.025843 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
GUAYAMA | 2023-06-03 14:40 | 2023-06-03 20:28 | 50 | 5:48 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZARON 3 MACHETES 900A | P23060300624 | New_Event | Switch Failure | Include | Include | Equipment | 348 | 2023-06-03 | 17400 | keep | 0 | Jun | 2023 | 0.011851 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-06-03 14:41 | 2023-06-03 15:00 | 4944 | 0:19 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23060300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 19 | 2023-06-03 | 93936 | keep | 0 | Jun | 2023 | 0.063979 | 0.0033673 | Sustained | FALSE | FALSE | Not_TMED_Event | 4944
BAYAMON | 2023-06-03 14:44 | 2023-06-03 14:45 | 3438 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2306030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 3438 | keep | 0 | Jun | 2023 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
SAN JUAN | 2023-06-03 14:45 | 2023-06-03 22:23 | 164 | 7:38 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO CAUSA | S23060300243 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 458 | 2023-06-03 | 75112 | keep | 0 | Jun | 2023 | 0.051158 | 0.0001117 | Sustained | FALSE | FALSE | Not_TMED_Event | 164
SAN JUAN | 2023-06-03 14:47 | 2023-06-03 14:48 | 4133 | 0:01 | T | DESGANCHE | RECERRO | S23060300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-06-03 | 4133 | keep | 0 | Jun | 2023 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
ARECIBO | 2023-06-03 14:50 | 2023-06-03 14:51 | 3431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23060300205 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 3431 | keep | 0 | Jun | 2023 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2023-06-03 14:51 | 2023-06-03 20:00 | 1 | 5:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A23060200185 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 309 | 2023-06-03 | 309 | keep | 0 | Jun | 2023 | 0.00021046 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-03 14:52 | 2023-06-03 14:53 | 4133 | 0:01 | T | DESGANCHE | RECERRO | S2306030000X | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-06-03 | 4133 | keep | 0 | Jun | 2023 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
BARRANQUITAS | 2023-06-03 14:52 | 2023-06-03 15:24 | 92 | 0:32 | P | DESGANCHE | 1 X 50 EN C/L | C23060300383 | New_Event | Vegetation Contact | Include | Include | Vegetation | 32 | 2023-06-03 | 2944 | keep | 0 | Jun | 2023 | 0.0020051 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
AGUADILLA | 2023-06-03 14:54 | 2023-06-03 18:10 | 60 | 3:16 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | M23060300438 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2023-06-03 | 11760 | keep | 0 | Jun | 2023 | 0.0080097 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-06-03 14:55 | 2023-06-03 15:56 | 504 | 1:01 | P | NO SE REPORTO CAUSA | SE PATRULLO NO SE REPORTO CAUSA Y SE CERRO MACHETE 100% EN SERVICIO | S23060300272 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 61 | 2023-06-03 | 30744 | keep | 0 | Jun | 2023 | 0.02094 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-03 14:55 | 2023-06-03 15:11 | 411 | 0:16 | P | NO SE REPORTO CAUSA | SE PATRULLO NO CAUSA Y SE CERRO MACHETE 100% EN SERVICIO | S23060300335 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 16 | 2023-06-03 | 6576 | keep | 0 | Jun | 2023 | 0.0044789 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-06-03 15:00 | 2023-06-03 23:31 | 60 | 8:31 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE SEPARO LINEAS CRUZADAS | P23060300651 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 511 | 2023-06-03 | 30660 | keep | 0 | Jun | 2023 | 0.020882 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-06-03 15:06 | 2023-06-03 23:35 | 110 | 8:29 | P | DESGANCHE | CG-230603-03 SE SECCIONALIZO ALIMENTADOR PARA DESGANCHAR Y SE CERRO MACHETES 100% EN SERVICIO. | C23060300315 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 509 | 2023-06-03 | 55990 | keep | 0 | Jun | 2023 | 0.038135 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-06-03 15:06 | 2023-06-03 15:20 | 61 | 0:14 | P | DESGANCHE | CG-230603-03 SE ABRIO FUSIBLE Y SE CERRO MACHETES PARA BAJAR LOS CLIENTES. SOLO SE QUEDAN 31 CLIENTES SIN SERVICIO HASTA QUE PERSONAL DESGANCHE | C23060300315 | New_Event | Vegetation Contact | Include | Include | Vegetation | 14 | 2023-06-03 | 854 | keep | 0 | Jun | 2023 | 0.00058166 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
ARECIBO | 2023-06-03 15:07 | 2023-06-04 08:40 | 30 | 17:33 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | A23060300214 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1053 | 2023-06-03 | 31590 | keep | 0 | Jun | 2023 | 0.021516 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-06-03 15:15 | 2023-06-03 15:16 | 4133 | 0:01 | T | DESGANCHE | RECERRO | S23060300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-06-03 | 4133 | keep | 0 | Jun | 2023 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
BAYAMON | 2023-06-03 15:15 | 2023-06-03 16:59 | 334 | 1:44 | P | DESGANCHE | 1 X 100 Y 1 X 50 EN C/L SE DESGANCHO | B23060300348 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2023-06-03 | 34736 | keep | 0 | Jun | 2023 | 0.023659 | 0.00022749 | Sustained | FALSE | FALSE | Not_TMED_Event | 334
CAGUAS | 2023-06-03 15:20 | 2023-06-03 21:10 | 130 | 5:50 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C23060300400 | New_Event | Vegetation Contact | Include | Include | Vegetation | 350 | 2023-06-03 | 45500 | keep | 0 | Jun | 2023 | 0.03099 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
BARRANQUITAS | 2023-06-03 15:20 | 2023-06-03 15:24 | 3296 | 0:04 | T | DESGANCHE | DISPARO INTERRUPTOR LLEVA LA CARGA 9601-02 Y 5% DEL 9602-04 CERRADO POR CONTROL | C2306030000X | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 4 | 2023-06-03 | 13184 | keep | 0 | Jun | 2023 | 0.0089796 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-06-03 15:20 | 2023-06-03 15:24 | 63 | 0:04 | P | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR 5% DE LA CARGA POR EL 9601-02 CERRADO POR CONTROL | C2306030000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 4 | 2023-06-03 | 252 | keep | 0 | Jun | 2023 | 0.00017164 | 4.2909e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 63
BARRANQUITAS | 2023-06-03 15:20 | 2023-06-03 15:24 | 2937 | 0:04 | T | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR 100% DE LA CARGA POR EL 9601-02 CERRADO POR CONTROL | C2306030000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 4 | 2023-06-03 | 11748 | keep | 0 | Jun | 2023 | 0.0080015 | 0.0020004 | Momentary | FALSE | FALSE | Not_TMED_Event | 2937
SAN JUAN | 2023-06-03 15:21 | 2023-06-03 15:22 | 4133 | 0:01 | T | DESGANCHE | RECERRO | S23060300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-06-03 | 4133 | keep | 0 | Jun | 2023 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
BARRANQUITAS | 2023-06-03 15:24 | 2023-06-03 20:32 | 61 | 5:08 | P | DESGANCHE | CG-230603-03 SE ABRIO FUSIBLE Y SE CERRO MACHETES PARA BAJAR LOS CLIENTES. SOLO SE QUEDAN 31 CLIENTES SIN SERVICIO HASTA QUE PERSONAL DESGANCHE | C23060300315 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 308 | 2023-06-03 | 18788 | keep | 0 | Jun | 2023 | 0.012796 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
BARRANQUITAS | 2023-06-03 15:24 | 2023-06-03 17:58 | 90 | 2:34 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C23060300396 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2023-06-03 | 13860 | keep | 0 | Jun | 2023 | 0.00944 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BARRANQUITAS | 2023-06-03 15:24 | 2023-06-04 12:39 | 92 | 21:15 | P | DESGANCHE | 1 X 50 EN C/L | C23060300383 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1275 | 2023-06-03 | 117300 | keep | 0 | Jun | 2023 | 0.079892 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-06-03 15:26 | 2023-06-03 20:15 | 89 | 4:49 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE VERIFICO INTERRUPTOR ABIERTO EN LA SUBESTACION YA QUE LA MISMA NO TIENE RTU SE ABRIO PUENTES PRIMARIOS PARA SECCIONALIZAR POSTE PRIMARIO ROTO Y SE CERRO EL INTERRUPTOR | A23060300391 | New_Event | Primary Pole Failure | Include | Include | Equipment | 289 | 2023-06-03 | 25721 | keep | 0 | Jun | 2023 | 0.017518 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
SAN JUAN | 2023-06-03 15:27 | 2023-06-03 16:45 | 4133 | 1:18 | T | DESGANCHE | DISPARO SE RETIRO BAMBUA CON VARETA DE PISO Y SE CERRO INTERRUPTOR 100% EN SERVICIO | S23060300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 78 | 2023-06-03 | 322374 | keep | 0 | Jun | 2023 | 0.21957 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
BAYAMON | 2023-06-03 15:33 | 2023-06-03 16:47 | 30 | 1:14 | P | DESGANCHE | 1 X 30 EN C/L SE DESGANCHO | B23060300365 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2023-06-03 | 2220 | keep | 0 | Jun | 2023 | 0.001512 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-06-03 15:34 | 2023-06-03 21:05 | 50 | 5:31 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23060300230 | New_Event | Vegetation Contact | Include | Include | Vegetation | 331 | 2023-06-03 | 16550 | keep | 0 | Jun | 2023 | 0.011272 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-06-03 15:48 | 2023-06-04 14:21 | 10 | 22:33 | P | CONDUCTOR ROTO O ABIERTO | REMPLAZO BAJANTE DE CAJA A XMR NO FUNDIO | C23060300430 | New_Event | Primary Wire Break | Include | Include | Equipment | 1353 | 2023-06-03 | 13530 | keep | 0 | Jun | 2023 | 0.0092152 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-06-03 15:55 | 2023-06-03 22:04 | 409 | 6:09 | P | DESGANCHE | 1 X 65 EN C/L 2 X 50 EN C/L DESGANCHE | C23060300435 | New_Event | Vegetation Contact | Include | Include | Vegetation | 369 | 2023-06-03 | 150921 | keep | 0 | Jun | 2023 | 0.10279 | 0.00027857 | Sustained | FALSE | FALSE | Not_TMED_Event | 409
SAN JUAN | 2023-06-03 15:57 | 2023-06-03 18:22 | 76 | 2:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 80 EN CORTE DE LINEA VIENTOS | S23060300543 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 145 | 2023-06-03 | 11020 | keep | 0 | Jun | 2023 | 0.0075057 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
CAGUAS | 2023-06-03 15:58 | 2023-06-03 19:20 | 285 | 3:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 Y 1 X 80 EN CORTES DE LINEA MAL TIEMPO VIENTO | C23060300438 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 202 | 2023-06-03 | 57570 | keep | 0 | Jun | 2023 | 0.039211 | 0.00019411 | Sustained | FALSE | FALSE | Not_TMED_Event | 285
SAN JUAN | 2023-06-03 16:03 | 2023-06-03 16:49 | 610 | 0:46 | P | CAUSAS EXTERNAS | SE ABRE INTERRUPTOR PARA CERRAR PUENTES PRIMARIO Y CERRAR INTERRUPTOR 100% EN SERVICIO | S23060200160 | Additional_clients | Damage From Public | Include | Include | Public | 46 | 2023-06-03 | 28060 | keep | 0 | Jun | 2023 | 0.019112 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-06-03 16:06 | 2023-06-03 18:42 | 40 | 2:36 | P | DESGANCHE | 1 X 40 EN C/L EVENTO TRANSFERIDO DE PONCE | P23060300735 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2023-06-03 | 6240 | keep | 0 | Jun | 2023 | 0.00425 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-06-03 16:06 | 2023-06-03 16:07 | 1342 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C2306030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 1342 | keep | 0 | Jun | 2023 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
ARECIBO | 2023-06-03 16:08 | 2023-06-03 19:20 | 25 | 3:12 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23060300239 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2023-06-03 | 4800 | keep | 0 | Jun | 2023 | 0.0032693 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2023-06-03 16:20 | 2023-06-03 16:21 | 1548 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23060300244 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 1548 | keep | 0 | Jun | 2023 | 0.0010543 | 0.0010543 | Momentary | FALSE | FALSE | Not_TMED_Event | 1548
SAN JUAN | 2023-06-03 16:23 | 2023-06-03 16:34 | 1984 | 0:11 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23060300570 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 11 | 2023-06-03 | 21824 | keep | 0 | Jun | 2023 | 0.014864 | 0.0013513 | Sustained | FALSE | FALSE | Not_TMED_Event | 1984
SAN JUAN | 2023-06-03 16:25 | 2023-06-03 19:34 | 137 | 3:09 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO Y NO OPERA LOCALMENTE NO POR MANIJA SE TRANSFIRIO CARGA AL 1342-04 | S23060300348 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 189 | 2023-06-03 | 25893 | keep | 0 | Jun | 2023 | 0.017636 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
SAN JUAN | 2023-06-03 16:25 | 2023-06-03 19:16 | 760 | 2:51 | T | ALIMENTADOR AMARRADO | DISPARO Y NO OPERA LOCALMENTE NO POR MANIJA SE TRANSFIRIO CARGA AL 1205-02 | S23060300348 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 171 | 2023-06-03 | 129960 | keep | 0 | Jun | 2023 | 0.088515 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-06-03 16:27 | 2023-06-03 23:41 | 428 | 7:14 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C23060300378 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 434 | 2023-06-03 | 185752 | keep | 0 | Jun | 2023 | 0.12651 | 0.00029151 | Sustained | FALSE | FALSE | Not_TMED_Event | 428
BARRANQUITAS | 2023-06-03 16:27 | 2023-06-03 23:07 | 428 | 6:40 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | C23060300471 | New_Event | Vegetation Contact | Include | Include | Vegetation | 400 | 2023-06-03 | 171200 | keep | 0 | Jun | 2023 | 0.1166 | 0.00029151 | Sustained | FALSE | FALSE | Not_TMED_Event | 428
ARECIBO | 2023-06-03 16:30 | 2023-06-03 23:52 | 15 | 7:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REQUIERE DESGANCHE | A23060300248 | New_Event | Vegetation Contact | Include | Include | Vegetation | 442 | 2023-06-03 | 6630 | keep | 0 | Jun | 2023 | 0.0045157 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2023-06-03 16:33 | 2023-06-03 21:17 | 179 | 4:44 | P | DESGANCHE | 2 X 65 Y 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C23060300479 | New_Event | Vegetation Contact | Include | Include | Vegetation | 284 | 2023-06-03 | 50836 | keep | 0 | Jun | 2023 | 0.034624 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
BARRANQUITAS | 2023-06-03 16:35 | 2023-06-03 16:36 | 1843 | 0:01 | T | CAUSAS EXTERNAS | RECERRO INTERRUPTOR EN SERVICIO | C23060300483 | New_Event | Damage From Public | Include | Include | Public | 1 | 2023-06-03 | 1843 | keep | 0 | Jun | 2023 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
BARRANQUITAS | 2023-06-03 16:35 | 2023-06-03 19:50 | 172 | 3:15 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | C23060300482 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2023-06-03 | 33540 | keep | 0 | Jun | 2023 | 0.022844 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
BARRANQUITAS | 2023-06-03 16:36 | 2023-06-03 20:12 | 472 | 3:36 | P | CAUSAS EXTERNAS | 1 X 140 EN CORTE DE LINEA CONDUCTOR PRIMARIO SE CRUZO CON MENSAJERO DE TELEFONO | C23060300488 | 1st_after_momentary | Damage From Public | Include | Include | Public | 216 | 2023-06-03 | 101952 | keep | 0 | Jun | 2023 | 0.069439 | 0.00032148 | Sustained | FALSE | FALSE | Not_TMED_Event | 472
BAYAMON | 2023-06-03 16:42 | 2023-06-03 20:57 | 31 | 4:15 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO CONDUCTOR EN EL SUELO VER GOI BY-230603-03 | S23060300244 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 255 | 2023-06-03 | 7905 | keep | 0 | Jun | 2023 | 0.0053841 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-06-03 16:44 | 2023-06-03 17:40 | 50 | 0:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23060300571 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2023-06-03 | 2800 | keep | 0 | Jun | 2023 | 0.0019071 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-06-03 16:49 | 2023-06-03 21:20 | 115 | 4:31 | P | CAUSAS EXTERNAS | SE ABRIO CORTE DE LINEA PARA PODER ABRIR PUENTE Y SECCIONALIZAR POSTE PRIMARIO IMPACTADO POR CAMION. SE REEMPLAZARA MAÃ‘ANA, QUEDARON 40 CLIENTES FUERA | C23060300495 | New_Event | Damage From Public | Include | Include | Public | 271 | 2023-06-03 | 31165 | keep | 0 | Jun | 2023 | 0.021226 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
PONCE | 2023-06-03 16:50 | 2023-06-03 16:51 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23060300792 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 2379 | keep | 0 | Jun | 2023 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
AGUADILLA | 2023-06-03 16:50 | 2023-06-03 18:20 | 60 | 1:30 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M23060300579 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2023-06-03 | 5400 | keep | 0 | Jun | 2023 | 0.0036779 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2023-06-03 16:54 | 2023-06-03 21:41 | 60 | 4:47 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23060300257 | New_Event | Vegetation Contact | Include | Include | Vegetation | 287 | 2023-06-03 | 17220 | keep | 0 | Jun | 2023 | 0.011728 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2023-06-03 17:01 | 2023-06-03 22:45 | 80 | 5:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA POR FUERTE VIENTO | A23060300261 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 344 | 2023-06-03 | 27520 | keep | 0 | Jun | 2023 | 0.018744 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-06-03 17:23 | 2023-06-03 17:24 | 2697 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23060300272 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 2697 | keep | 0 | Jun | 2023 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
BAYAMON | 2023-06-03 17:23 | 2023-06-03 17:24 | 2858 | 0:01 | T | DESGANCHE | RECERRO | B2306030000X | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-06-03 | 2858 | keep | 0 | Jun | 2023 | 0.0019466 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-06-03 17:24 | 2023-06-03 20:25 | 90 | 3:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23060300627 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2023-06-03 | 16290 | keep | 0 | Jun | 2023 | 0.011095 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2023-06-03 17:24 | 2023-06-03 18:26 | 80 | 1:02 | P | DESGANCHE | 2 X 50 Y 1 X 65 EN C/L SE DESGANCHO | B23060300173 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 62 | 2023-06-03 | 4960 | keep | 0 | Jun | 2023 | 0.0033782 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-06-03 17:27 | 2023-06-03 19:20 | 60 | 1:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR FUERTE VIENTO | A23060300274 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 113 | 2023-06-03 | 6780 | keep | 0 | Jun | 2023 | 0.0046178 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2023-06-03 17:29 | 2023-06-04 00:34 | 20 | 7:05 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REQUIERE DESGANCHE | A23060300275 | New_Event | Vegetation Contact | Include | Include | Vegetation | 425 | 2023-06-03 | 8500 | keep | 0 | Jun | 2023 | 0.0057893 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-06-03 17:36 | 2023-06-03 18:15 | 30 | 0:39 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23060300636 | New_Event | Vegetation Contact | Include | Include | Vegetation | 39 | 2023-06-03 | 1170 | keep | 0 | Jun | 2023 | 0.00079688 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-06-03 18:00 | 2023-06-04 08:28 | 35 | 14:28 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C23060300536 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 868 | 2023-06-03 | 30380 | keep | 0 | Jun | 2023 | 0.020692 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-06-03 18:02 | 2023-06-03 21:15 | 305 | 3:13 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA NO CAUSA | S23060300660 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 193 | 2023-06-03 | 58865 | keep | 0 | Jun | 2023 | 0.040093 | 0.00020773 | Sustained | FALSE | FALSE | Not_TMED_Event | 305
BAYAMON | 2023-06-03 18:02 | 2023-06-04 17:08 | 74 | 23:06 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN C/L AVERIA NUEVA DEL T-36 AL T-37 Y AVERIA VIEJA DEL T-37 AL T-34 | B23060300454 | New_Event | UG Cable Fault | Include | Include | Equipment | 1386 | 2023-06-03 | 102564 | keep | 0 | Jun | 2023 | 0.069856 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
VEGA BAJA | 2023-06-03 18:15 | 2023-06-04 13:12 | 25 | 18:57 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23060300295 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1137 | 2023-06-03 | 28425 | keep | 0 | Jun | 2023 | 0.01936 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-06-03 18:25 | 2023-06-03 18:42 | 1 | 0:17 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO BAJANTE DE LINEA A CAJA | B23060300469 | New_Event | Primary Wire Break | Include | Include | Equipment | 17 | 2023-06-03 | 17 | keep | 0 | Jun | 2023 | 1.1579e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-06-03 18:28 | 2023-06-04 10:35 | 25 | 16:07 | P | DESGANCHE | 1 X 30 EN CONVERTIDOR SE RETIRO BAMBUS SOBRE LAS LINEAS | A23060300300 | New_Event | Vegetation Contact | Include | Include | Vegetation | 967 | 2023-06-03 | 24175 | keep | 0 | Jun | 2023 | 0.016465 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-06-03 18:31 | 2023-06-04 06:39 | 116 | 12:08 | P | DESGANCHE | 1X80 EN C/L SE REFIRIO PARA DESGANCHE | S23060300689 | New_Event | Vegetation Contact | Include | Include | Vegetation | 728 | 2023-06-03 | 84448 | keep | 0 | Jun | 2023 | 0.057517 | 7.9007e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 116
PONCE | 2023-06-03 18:35 | 2023-06-03 21:50 | 159 | 3:15 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA POR DESGANCHE | P23060300902 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2023-06-03 | 31005 | keep | 0 | Jun | 2023 | 0.021117 | 0.00010829 | Sustained | FALSE | FALSE | Not_TMED_Event | 159
FAJARDO | 2023-06-03 18:44 | 2023-06-03 19:45 | 80 | 1:01 | P | DESGANCHE | 1 X 65 Y 1 X 30 EN C/L EVENTO TRANSFERIDO DE PONCE | P23060300917 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2023-06-03 | 4880 | keep | 0 | Jun | 2023 | 0.0033237 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
YAUCO | 2023-06-03 18:44 | 2023-06-03 20:30 | 150 | 1:46 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23060300720 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2023-06-03 | 15900 | keep | 0 | Jun | 2023 | 0.010829 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2023-06-03 18:44 | 2023-06-03 20:40 | 30 | 1:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR FUERTE VIENTO | A23060300306 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 116 | 2023-06-03 | 3480 | keep | 0 | Jun | 2023 | 0.0023702 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-06-03 18:45 | 2023-06-03 23:05 | 60 | 4:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR Y 1 X 100 EN CORTE DE LINEA SE REEMNPLAZO CAJA PRIMARIA DEFECTUOSA | M23060300721 | New_Event | Cutout Failure | Include | Include | Equipment | 260 | 2023-06-03 | 15600 | keep | 0 | Jun | 2023 | 0.010625 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-06-03 18:47 | 2023-06-03 21:05 | 60 | 2:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23060300722 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 138 | 2023-06-03 | 8280 | keep | 0 | Jun | 2023 | 0.0056395 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-06-03 18:47 | 2023-06-03 22:31 | 125 | 3:44 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO | M23060300723 | New_Event | Primary Wire Break | Include | Include | Equipment | 224 | 2023-06-03 | 28000 | keep | 0 | Jun | 2023 | 0.019071 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
MAYAGÃœEZ | 2023-06-03 18:56 | 2023-06-03 19:30 | 120 | 0:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA POR FUERTES VIENTOS | M23060300715 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 34 | 2023-06-03 | 4080 | keep | 0 | Jun | 2023 | 0.0027789 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
AGUADILLA | 2023-06-03 19:15 | 2023-06-03 19:16 | 3309 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR | A23060300318 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-06-03 | 3309 | keep | 0 | Jun | 2023 | 0.0022537 | 0.0022537 | Momentary | FALSE | FALSE | Not_TMED_Event | 3309
AGUADILLA | 2023-06-03 19:15 | 2023-06-03 19:16 | 713 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 7502-02 QUE LLEVA LA CARGA DEL 7502-03 | A23060300318 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-03 | 713 | keep | 0 | Jun | 2023 | 0.00048562 | 0.00048562 | Momentary | FALSE | FALSE | Not_TMED_Event | 713
AGUADILLA | 2023-06-03 19:16 | 2023-06-04 03:59 | 200 | 8:43 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA POR AVE | M23060300757 | New_Event | Animals | Include | Include | Wildlife | 523 | 2023-06-03 | 104600 | keep | 0 | Jun | 2023 | 0.071243 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2023-06-03 19:16 | 2023-06-03 23:19 | 1100 | 4:03 | P | CONDUCTOR ROTO O ABIERTO | SE DEJO CERRADO Y AMARRADOS LOS INTERRUPTORES 7502-02 Y 7502-03 POR PUENTE ABIERTO EN LA SALIDA DEL ALIMENTADOR 7502-02 Y OTRO PUENTE A PUNTO DE ABRIR EN LOS AUXILIARES DE BARRA DE INSPECCION DEL 7502-02 | A23060300340 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 243 | 2023-06-03 | 267300 | keep | 0 | Jun | 2023 | 0.18206 | 0.0007492 | Sustained | FALSE | FALSE | Not_TMED_Event | 1100
MAYAGÃœEZ | 2023-06-03 19:21 | 2023-06-03 22:10 | 35 | 2:49 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | M23060300762 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2023-06-03 | 5915 | keep | 0 | Jun | 2023 | 0.0040287 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BARRANQUITAS | 2023-06-03 19:22 | 2023-06-04 15:25 | 35 | 20:03 | P | DESGANCHE | 1 X 50 EN C/L | C23060300570 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1203 | 2023-06-03 | 42105 | keep | 0 | Jun | 2023 | 0.028678 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
FAJARDO | 2023-06-03 19:33 | 2023-06-03 21:25 | 200 | 1:52 | P | DESGANCHE | 2 X 80 Y 1 X 65 EN C/L | R23060300089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2023-06-03 | 22400 | keep | 0 | Jun | 2023 | 0.015257 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-06-03 19:37 | 2023-06-04 18:55 | 50 | 23:18 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S23060300736 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1398 | 2023-06-03 | 69900 | keep | 0 | Jun | 2023 | 0.047609 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-06-03 19:50 | 2023-06-04 10:30 | 5 | 14:40 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50 KVA X 50 KVA | R23060300091 | New_Event | Service Transformer Failure | Include | Include | Equipment | 880 | 2023-06-03 | 4400 | keep | 0 | Jun | 2023 | 0.0029968 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2023-06-03 19:50 | 2023-06-04 11:35 | 20 | 15:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | P23060300955 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 945 | 2023-06-03 | 18900 | keep | 0 | Jun | 2023 | 0.012873 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2023-06-03 19:51 | 2023-06-04 12:50 | 150 | 16:59 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA | A23060300343 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 1019 | 2023-06-03 | 152850 | keep | 0 | Jun | 2023 | 0.10411 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
UTUADO | 2023-06-03 19:52 | 2023-06-04 15:00 | 8 | 19:08 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23060300344 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1148 | 2023-06-03 | 9184 | keep | 0 | Jun | 2023 | 0.0062552 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-06-03 20:06 | 2023-06-04 06:37 | 200 | 10:31 | P | DESGANCHE | 1 X 100 EN CL DESGANCHE | M23060300803 | New_Event | Vegetation Contact | Include | Include | Vegetation | 631 | 2023-06-03 | 126200 | keep | 0 | Jun | 2023 | 0.085954 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2023-06-03 20:06 | 2023-06-04 10:15 | 8 | 14:09 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | A23060300348 | New_Event | Vegetation Contact | Include | Include | Vegetation | 849 | 2023-06-03 | 6792 | keep | 0 | Jun | 2023 | 0.004626 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-06-03 20:06 | 2023-06-03 22:58 | 200 | 2:52 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23060300498 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 172 | 2023-06-03 | 34400 | keep | 0 | Jun | 2023 | 0.02343 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2023-06-03 20:10 | 2023-06-03 21:12 | 3522 | 1:02 | T | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO AVERIA DE LINEAS PRIMARIAS PARTIDAS | M23060300806 | New_Event | Primary Wire Break | Include | Include | Equipment | 62 | 2023-06-03 | 218364 | keep | 0 | Jun | 2023 | 0.14873 | 0.0023988 | Sustained | FALSE | FALSE | Not_TMED_Event | 3522
BAYAMON | 2023-06-03 20:14 | 2023-06-03 20:46 | 200 | 0:32 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE EVENTO TRANSFERIDO DE PONCE | P23060300973 | New_Event | Vegetation Contact | Include | Include | Vegetation | 32 | 2023-06-03 | 6400 | keep | 0 | Jun | 2023 | 0.004359 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2023-06-03 20:19 | 2023-06-03 22:02 | 100 | 1:43 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REQUIERE DESGANCHE | A23060300358 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2023-06-03 | 10300 | keep | 0 | Jun | 2023 | 0.0070153 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-06-03 20:31 | 2023-06-03 20:34 | 4944 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23060300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-06-03 | 14832 | keep | 0 | Jun | 2023 | 0.010102 | 0.0033673 | Momentary | FALSE | FALSE | Not_TMED_Event | 4944
MAYAGÃœEZ | 2023-06-03 20:32 | 2023-06-04 11:10 | 40 | 14:38 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE EN SALIDA DE CONVERTIDOR | M23060300815 | New_Event | Primary Wire Break | Include | Include | Equipment | 878 | 2023-06-03 | 35120 | keep | 0 | Jun | 2023 | 0.02392 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-06-03 20:32 | 2023-06-03 23:25 | 31 | 2:53 | P | DESGANCHE | CG-230603-03 SE ABRIO FUSIBLE Y SE CERRO MACHETES. SE REALIZO DESGANCHE | C23060300315 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2023-06-03 | 5363 | keep | 0 | Jun | 2023 | 0.0036527 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
CANOVANAS | 2023-06-03 20:54 | 2023-06-04 01:19 | 200 | 4:25 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | R23060300109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 265 | 2023-06-03 | 53000 | keep | 0 | Jun | 2023 | 0.036098 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2023-06-03 20:55 | 2023-06-04 03:30 | 243 | 6:35 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R23060300619 | New_Event | Vegetation Contact | Include | Include | Vegetation | 395 | 2023-06-03 | 95985 | keep | 0 | Jun | 2023 | 0.065375 | 0.00016551 | Sustained | FALSE | FALSE | Not_TMED_Event | 243
BAYAMON | 2023-06-03 20:56 | 2023-06-04 09:14 | 31 | 12:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 2X50 EN C/L POR VIENTO FUERTE | B23060300529 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 738 | 2023-06-03 | 22878 | keep | 0 | Jun | 2023 | 0.015582 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
BAYAMON | 2023-06-03 20:57 | 2023-06-04 04:34 | 959 | 7:37 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | EN OPERACIONES CON 1901-05 QUEMO ALIMENTADOR Y FUNDIO 2 FUSIBLE DE LA ALTA 2 X 125 STD. Y SE REMPLAZO BUS SUPPORT SU CARGA POR 1904-07 | S23060300900 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 457 | 2023-06-03 | 438263 | keep | 0 | Jun | 2023 | 0.2985 | 0.00065317 | Sustained | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-06-03 20:57 | 2023-06-04 04:24 | 1297 | 7:27 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | EN OPERACIONES CON 1901-05 QUEMO INTERRUPTOR Y FUNDIO 2 FUSIBLE DE LA ALTA 2 X 125 STD. Y SE REMPLAZO BUS SUPPORT LLEVA 1901-03 | S23060300900 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 447 | 2023-06-03 | 579759 | keep | 0 | Jun | 2023 | 0.39487 | 0.00088338 | Sustained | FALSE | FALSE | Not_TMED_Event | 1297
BAYAMON | 2023-06-03 20:57 | 2023-06-04 04:24 | 451 | 7:27 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | EN OPERACIONES CON 1901-05 QUEMO INTERRUPTOR Y FUNDIO 2 FUSIBLE DE LA ALTA 2 X 125 STD. Y SE REMPLAZO BUS SUPPORT SU CARGA POR 1904-06 | S23060300900 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 447 | 2023-06-03 | 201597 | keep | 0 | Jun | 2023 | 0.13731 | 0.00030717 | Sustained | FALSE | FALSE | Not_TMED_Event | 451
BAYAMON | 2023-06-03 20:57 | 2023-06-04 04:34 | 1264 | 7:37 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | EN OPERACIONES CON 1901-05 QUEMO ALIMENTADOR Y FUNDIO 2 FUSIBLE DE LA ALTA 2 X 125 STD. Y SE REMPLAZO BUS SUPPORT SU CARGA POR 1904-07 | S23060300900 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 457 | 2023-06-03 | 577648 | keep | 0 | Jun | 2023 | 0.39343 | 0.0008609 | Sustained | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2023-06-03 20:57 | 2023-06-04 04:34 | 62 | 7:37 | P | INTERRUPTOR DEFECTUOSO O NO OPERA | EN OPERACIONES CON 1901-05 QUEMO INTERRUPTOR Y FUNDIO 2 FUSIBLE DE LA ALTA 2 X 125 STD. Y SE REMPLAZO BUS SUPPORT SU CARGA POR 1904-07 | S23060300900 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 457 | 2023-06-03 | 28334 | keep | 0 | Jun | 2023 | 0.019298 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
BAYAMON | 2023-06-03 21:07 | 2023-06-03 21:08 | 2956 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S2306030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 2956 | keep | 0 | Jun | 2023 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2023-06-03 21:08 | 2023-06-03 21:09 | 2435 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S2306030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-03 | 2435 | keep | 0 | Jun | 2023 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
ARECIBO | 2023-06-03 21:10 | 2023-06-03 22:40 | 75 | 1:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REQUIERE DESGANCHE | A23060300379 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2023-06-03 | 6750 | keep | 0 | Jun | 2023 | 0.0045974 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2023-06-03 21:14 | 2023-06-03 21:15 | 2231 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14700 | A23060300384 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 2231 | keep | 0 | Jun | 2023 | 0.0015195 | 0.0015195 | Momentary | FALSE | FALSE | Not_TMED_Event | 2231
VEGA BAJA | 2023-06-03 21:14 | 2023-06-03 21:15 | 1923 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14700 | A23060300384 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 1923 | keep | 0 | Jun | 2023 | 0.0013097 | 0.0013097 | Momentary | FALSE | FALSE | Not_TMED_Event | 1923
VEGA BAJA | 2023-06-03 21:14 | 2023-06-03 21:15 | 1066 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14700 | A23060300384 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 1066 | keep | 0 | Jun | 2023 | 0.00072605 | 0.00072605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1066
VEGA BAJA | 2023-06-03 21:14 | 2023-06-03 21:15 | 141 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14700 | A23060300384 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 141 | keep | 0 | Jun | 2023 | 9.6034e-05 | 9.6034e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 141
VEGA BAJA | 2023-06-03 21:14 | 2023-06-03 21:15 | 2107 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14700 | A23060300385 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 2107 | keep | 0 | Jun | 2023 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
VEGA BAJA | 2023-06-03 21:14 | 2023-06-03 21:15 | 308 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14700 | A23060300385 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 308 | keep | 0 | Jun | 2023 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2023-06-03 21:14 | 2023-06-03 21:15 | 2697 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14700 | A23060300385 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 2697 | keep | 0 | Jun | 2023 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
VEGA BAJA | 2023-06-03 21:14 | 2023-06-03 21:15 | 67 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14700 | A23060300385 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-03 | 67 | keep | 0 | Jun | 2023 | 4.5633e-05 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
HUMACAO | 2023-06-03 21:20 | 2023-06-04 14:15 | 40 | 16:55 | P | CAUSAS EXTERNAS | SE ABRIO CORTE DE LINEA PARA PODER ABRIR PUENTE Y SECCIONALIZAR POSTE PRIMARIO IMPACTADO POR CAMION. SE REEMPLAZARA MAÃ‘ANA, QUEDARON 40 CLIENTES FUERA | C23060300495 | Partial_restoration | Damage From Public | Include | Include | Public | 1015 | 2023-06-03 | 40600 | keep | 0 | Jun | 2023 | 0.027652 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-03 21:28 | 2023-06-04 | 4944 | 2:32 | T | DESGANCHE | SE PATRULLO SE ABRIO MACHETE PARA SECCIONALIZAR Y SE CERRO INTERRUPTOR 70% EN SERVICIO | S23060300829 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2023-06-03 | 751488 | keep | 0 | Jun | 2023 | 0.51184 | 0.0033673 | Sustained | FALSE | FALSE | Not_TMED_Event | 4944
BARRANQUITAS | 2023-06-03 21:53 | 2023-06-04 14:03 | 142 | 16:10 | P | DESGANCHE | 2 X 50 EN C/L | C23060300629 | New_Event | Vegetation Contact | Include | Include | Vegetation | 970 | 2023-06-03 | 137740 | keep | 0 | Jun | 2023 | 0.093814 | 9.6716e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 142
CAGUAS | 2023-06-03 21:56 | 2023-06-04 18:34 | 81 | 20:38 | P | DESGANCHE | 1 X 65 EN C/L | C23060300630 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1238 | 2023-06-03 | 100278 | keep | 0 | Jun | 2023 | 0.068299 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
ARECIBO | 2023-06-03 22:08 | 2023-06-04 09:30 | 100 | 11:22 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE MASIVO | A23060300399 | New_Event | Vegetation Contact | Include | Include | Vegetation | 682 | 2023-06-03 | 68200 | keep | 0 | Jun | 2023 | 0.046451 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-06-03 22:26 | 2023-06-04 10:48 | 125 | 12:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR FUERTE VIENTO | M23060300865 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 742 | 2023-06-03 | 92750 | keep | 0 | Jun | 2023 | 0.063172 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
MAYAGÃœEZ | 2023-06-03 22:33 | 2023-06-04 03:12 | 574 | 4:39 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 5600SUBESTACION NO DIO ALARMA SE VERIFICO EN SCADA LA HORA EL EVENTO SE CREO LUEGO | M23060400092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 279 | 2023-06-03 | 160146 | keep | 0 | Jun | 2023 | 0.10907 | 0.00039095 | Sustained | FALSE | FALSE | Not_TMED_Event | 574
MAYAGÃœEZ | 2023-06-03 22:33 | 2023-06-04 03:12 | 2493 | 4:39 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 5600 SUBESTACION NO DIO ALARMA SE VERIFICO EN SCADA LA HORA EL EVENTO SE CREO LUEGO | M23060400092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 279 | 2023-06-03 | 695547 | keep | 0 | Jun | 2023 | 0.47373 | 0.001698 | Sustained | FALSE | FALSE | Not_TMED_Event | 2493
MAYAGÃœEZ | 2023-06-03 22:33 | 2023-06-04 03:12 | 1415 | 4:39 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 5600 SUBESTACION NO DIO ALARMA SE VERIFICO EN SCADA LA HORA EL EVENTO SE CREO LUEGO | M23060400092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 279 | 2023-06-03 | 394785 | keep | 0 | Jun | 2023 | 0.26889 | 0.00096375 | Sustained | FALSE | FALSE | Not_TMED_Event | 1415
MAYAGÃœEZ | 2023-06-03 22:33 | 2023-06-04 03:12 | 1428 | 4:39 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 5600 SUBESTACION NO DIO ALARMA SE VERIFICO EN SCADA LA HORA EL EVENTO SE CREO LUEGO | M23060400092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 279 | 2023-06-03 | 398412 | keep | 0 | Jun | 2023 | 0.27136 | 0.0009726 | Sustained | FALSE | FALSE | Not_TMED_Event | 1428
MAYAGÃœEZ | 2023-06-03 22:33 | 2023-06-04 03:12 | 1036 | 4:39 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 5600 SUBESTACION NO DIO ALARMA SE VERIFICO EN SCADA LA HORA EL EVENTO SE CREO LUEGO | M23060400092 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 279 | 2023-06-03 | 289044 | keep | 0 | Jun | 2023 | 0.19687 | 0.00070561 | Sustained | FALSE | FALSE | Not_TMED_Event | 1036
MAYAGÃœEZ | 2023-06-03 22:33 | 2023-06-04 03:12 | 382 | 4:39 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 5600 | M23060400094 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 279 | 2023-06-03 | 106578 | keep | 0 | Jun | 2023 | 0.07259 | 0.00026018 | Sustained | FALSE | FALSE | Not_TMED_Event | 382
MAYAGÃœEZ | 2023-06-03 22:33 | 2023-06-04 03:12 | 39 | 4:39 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 5600 SUBESTACION NO DIO ALARMA SE VERIFICO EN SCADA LA HORA EL EVENTO SE CREO LUEGO | M23060400094 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 279 | 2023-06-03 | 10881 | keep | 0 | Jun | 2023 | 0.007411 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
ARECIBO | 2023-06-03 22:57 | 2023-06-04 09:45 | 250 | 10:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23060300408 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 648 | 2023-06-03 | 162000 | keep | 0 | Jun | 2023 | 0.11034 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
GUAYAMA | 2023-06-03 23:17 | 2023-06-04 09:39 | 65 | 10:22 | P | SOBRECARGA | 1 X 50 EN CORTE DE LINEA POR CARGA | P23060301074 | New_Event | Trip Due To Overload | Include | Include | Other | 622 | 2023-06-03 | 40430 | keep | 0 | Jun | 2023 | 0.027537 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2023-06-03 23:18 | 2023-06-04 02:20 | 483 | 3:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE LINEA POR VIENTOS | B23060300566 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 182 | 2023-06-03 | 87906 | keep | 0 | Jun | 2023 | 0.059872 | 0.00032897 | Sustained | FALSE | FALSE | Not_TMED_Event | 483
AGUADILLA | 2023-06-03 23:18 | 2023-06-03 23:19 | 713 | 0:01 | T | ALIMENTADOR AMARRADO | SE ABRIO EL INTERRUPTOR PARA CERRAR AMARRE ENTRE EL 7502-02 Y 7502-03 POR PUENTE PRIMARIO ABIERTO EN LA SALIDA DEL ALIMENTADOR 7502-02 | A23060400012 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-03 | 713 | keep | 0 | Jun | 2023 | 0.00048562 | 0.00048562 | Momentary | FALSE | FALSE | Not_TMED_Event | 713
BAYAMON | 2023-06-03 23:38 | 2023-06-04 11:43 | 120 | 12:05 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | B23060300570 | New_Event | Vegetation Contact | Include | Include | Vegetation | 725 | 2023-06-03 | 87000 | keep | 0 | Jun | 2023 | 0.059255 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2023-06-04 | 2023-06-04 00:34 | 1483 | 0:34 | P | DESGANCHE | SE RETIRO BAMBUA SOBRE LINEA CON VARETA DE PISO FTE. A FAIR VIEW Y SE CERRO MACHETE 100% EN SERVICIO | S23060300829 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 34 | 2023-06-04 | 50422 | keep | 0 | Jun | 2023 | 0.034342 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-06-04 | 2023-06-04 01:50 | 75 | 1:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR VIENTOS | A23060400016 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 110 | 2023-06-04 | 8250 | keep | 0 | Jun | 2023 | 0.005619 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
UTUADO | 2023-06-04 00:32 | 2023-06-04 01:55 | 40 | 1:23 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA DE SACO LINEA CRUZADA | A23060400003 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 83 | 2023-06-04 | 3320 | keep | 0 | Jun | 2023 | 0.0022612 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-06-04 00:38 | 2023-06-04 07:34 | 50 | 6:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | P23060400010 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 416 | 2023-06-04 | 20800 | keep | 0 | Jun | 2023 | 0.014167 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-06-04 00:40 | 2023-06-04 03:43 | 50 | 3:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X 50 EN CORTE DE LINEA VIENTOS | B23060400008 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 183 | 2023-06-04 | 9150 | keep | 0 | Jun | 2023 | 0.006232 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-06-04 01:21 | 2023-06-04 01:22 | 1802 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR EN SERVICIO | B2306040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 1802 | keep | 0 | Jun | 2023 | 0.0012273 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
BAYAMON | 2023-06-04 01:25 | 2023-06-04 09:42 | 31 | 8:17 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | B23060400018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 497 | 2023-06-04 | 15407 | keep | 0 | Jun | 2023 | 0.010494 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
BARRANQUITAS | 2023-06-04 01:35 | 2023-06-04 08:37 | 25 | 7:02 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN C/L RETEZO LINEA | C23060400029 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 422 | 2023-06-04 | 10550 | keep | 0 | Jun | 2023 | 0.0071856 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-06-04 03:23 | 2023-06-04 10:11 | 208 | 6:48 | P | CONDUCTOR ROTO O ABIERTO | PERSONAL SOLICITO ABRIR INTERRUPTOR MOMENTANEAMENTE COMO PARTE DE LAS OPERACIONES PARA REPARAR PUENTE PRIMARIO TRASPATIO - BY-230604-01 | B23060400050 | New_Event | Primary Wire Break | Include | Include | Equipment | 408 | 2023-06-04 | 84864 | keep | 0 | Jun | 2023 | 0.0578 | 0.00014167 | Sustained | FALSE | FALSE | Not_TMED_Event | 208
AGUADILLA | 2023-06-04 03:39 | 2023-06-04 15:00 | 200 | 11:21 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTES PRIMARIOS | M23060400091 | New_Event | Primary Wire Break | Include | Include | Equipment | 681 | 2023-06-04 | 136200 | keep | 0 | Jun | 2023 | 0.092765 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2023-06-04 03:47 | 2023-06-04 09:33 | 38 | 5:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L | C23060400050 | New_Event | Cutout Failure | Include | Include | Equipment | 346 | 2023-06-04 | 13148 | keep | 0 | Jun | 2023 | 0.008955 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
MAYAGÃœEZ | 2023-06-04 04:05 | 2023-06-04 09:53 | 1252 | 5:48 | T | MAL TIEMPO/LLUVIA O VIENTO | SE VERIFICO INTERRUPTOR ABIERTO EN LA SUBESTACION YA QUE LA MISMA TIENE EL RTU FUERA DE SERVICIO SE PATRULLO Y SE CERRO EL INTERRUPTOR EN LA SUBESTACION POR FUERTE VIENTO EN EL AREA | M23060400096 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 348 | 2023-06-04 | 435696 | keep | 0 | Jun | 2023 | 0.29675 | 0.00085273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1252
ARECIBO | 2023-06-04 04:16 | 2023-06-04 11:30 | 70 | 7:14 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23060400034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 434 | 2023-06-04 | 30380 | keep | 0 | Jun | 2023 | 0.020692 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2023-06-04 04:26 | 2023-06-04 11:05 | 60 | 6:39 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN CL BAJANTE DE NUETRAL PRIMARIO CRUZADO CON FASE PRIMARIA | M23060400104 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 399 | 2023-06-04 | 23940 | keep | 0 | Jun | 2023 | 0.016305 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-06-04 04:47 | 2023-06-04 08:58 | 70 | 4:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X50 EN C/L POR VIENTO FUERTE | B23060400064 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 251 | 2023-06-04 | 17570 | keep | 0 | Jun | 2023 | 0.011967 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-06-04 05:41 | 2023-06-04 18:03 | 214 | 12:22 | P | DESGANCHE | 1X 65 EN C/L POR BAMBUA | B23060400072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 742 | 2023-06-04 | 158788 | keep | 0 | Jun | 2023 | 0.10815 | 0.00014575 | Sustained | FALSE | FALSE | Not_TMED_Event | 214
BARRANQUITAS | 2023-06-04 05:51 | 2023-06-04 05:52 | 2826 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO BKR ENSERVICIO | C23060400077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 2826 | keep | 0 | Jun | 2023 | 0.0019248 | 0.0019248 | Momentary | FALSE | FALSE | Not_TMED_Event | 2826
BARRANQUITAS | 2023-06-04 05:59 | 2023-06-04 09:02 | 50 | 3:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L VIENTOS FUERTES | C23060400096 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 183 | 2023-06-04 | 9150 | keep | 0 | Jun | 2023 | 0.006232 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-06-04 06:01 | 2023-06-04 06:02 | 2635 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | C2306040000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-06-04 | 2635 | keep | 0 | Jun | 2023 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2023-06-04 06:02 | 2023-06-04 10:06 | 260 | 4:04 | P | DESGANCHE | 2 X 100 2 X 80 Y 2 X 30 EN C/LS | C23060400195 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 244 | 2023-06-04 | 63440 | keep | 0 | Jun | 2023 | 0.043209 | 0.00017708 | Sustained | FALSE | FALSE | Not_TMED_Event | 260
SAN JUAN | 2023-06-04 06:06 | 2023-06-04 06:07 | 4133 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2306040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 4133 | keep | 0 | Jun | 2023 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
AGUADILLA | 2023-06-04 06:15 | 2023-06-04 06:16 | 3041 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23060400122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 3041 | keep | 0 | Jun | 2023 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
BARRANQUITAS | 2023-06-04 06:16 | 2023-06-04 15:23 | 175 | 9:07 | P | DESGANCHE | 2 X 100 EN C/L | C23060400082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 547 | 2023-06-04 | 95725 | keep | 0 | Jun | 2023 | 0.065198 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
ARECIBO | 2023-06-04 06:30 | 2023-06-04 08:20 | 50 | 1:50 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | A23060400060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 110 | 2023-06-04 | 5500 | keep | 0 | Jun | 2023 | 0.003746 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-06-04 06:37 | 2023-06-04 06:38 | 411 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M23060400124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 411 | keep | 0 | Jun | 2023 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2023-06-04 06:38 | 2023-06-04 09:41 | 200 | 3:03 | P | DESGANCHE | 1 X 100 EN CL DESGANCHE | M23060300803 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2023-06-04 | 36600 | keep | 0 | Jun | 2023 | 0.024928 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-06-04 06:39 | 2023-06-04 08:45 | 35 | 2:06 | P | DESGANCHE | 2X80 EN C/L DESGANCHE | S23060400207 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2023-06-04 | 4410 | keep | 0 | Jun | 2023 | 0.0030036 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2023-06-04 06:42 | 2023-06-04 11:38 | 13 | 4:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | R23060400016 | New_Event | Cutout Failure | Include | Include | Equipment | 296 | 2023-06-04 | 3848 | keep | 0 | Jun | 2023 | 0.0026209 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BARRANQUITAS | 2023-06-04 06:43 | 2023-06-04 06:44 | 2280 | 0:01 | T | ARBOL SOBRE LINEA | RECIERRE DE INTERRUPTOR | C2306040000X | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1 | 2023-06-04 | 2280 | keep | 0 | Jun | 2023 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2023-06-04 06:45 | 2023-06-04 06:46 | 2280 | 0:01 | T | ARBOL SOBRE LINEA | RECIERRE DE INTERRUPTOR | C2306040000X | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 1 | 2023-06-04 | 2280 | keep | 0 | Jun | 2023 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
MAYAGÃœEZ | 2023-06-04 06:46 | 2023-06-04 06:47 | 108 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23060400127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 108 | keep | 0 | Jun | 2023 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
BARRANQUITAS | 2023-06-04 06:46 | 2023-06-04 13:30 | 70 | 6:44 | P | ARBOL SOBRE LINEA | 1 X 40 EN C/L RETIRO ARBOL DE LA LINEA | C23060400293 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 404 | 2023-06-04 | 28280 | keep | 0 | Jun | 2023 | 0.019261 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
YAUCO | 2023-06-04 06:52 | 2023-06-04 09:12 | 5 | 2:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR POR MAL TIEMPO | P23060400120 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 140 | 2023-06-04 | 700 | keep | 0 | Jun | 2023 | 0.00047677 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2023-06-04 07:05 | 2023-06-04 15:23 | 300 | 8:18 | P | DESGANCHE | 1 X 140 EN CONVERTIDOR POR DESGANCHE | P23060400068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 498 | 2023-06-04 | 149400 | keep | 0 | Jun | 2023 | 0.10176 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2023-06-04 07:10 | 2023-06-04 13:58 | 253 | 6:48 | P | ALIMENTADOR AMARRADO | SJ-230603-03 SE SECCIONALIZA PUENTE ABIERTO A LA SALIDA DEL 1205-02 QUE LLEVA 1201-02. | S23060400214 | New_Event | Feeder Load Transferred | Include | Include | Other | 408 | 2023-06-04 | 103224 | keep | 0 | Jun | 2023 | 0.070305 | 0.00017232 | Sustained | FALSE | FALSE | Not_TMED_Event | 253
SAN JUAN | 2023-06-04 07:10 | 2023-06-04 13:58 | 456 | 6:48 | P | CONDUCTOR ROTO O ABIERTO | SJ-230603-03 SE SECCIONALIZA PUENTE ABIERTO A LA SALIDA DEL 1205-02 QUE LLEVA 1201-02. | S23060400214 | New_Event | Primary Wire Break | Include | Include | Equipment | 408 | 2023-06-04 | 186048 | keep | 0 | Jun | 2023 | 0.12672 | 0.00031058 | Sustained | FALSE | FALSE | Not_TMED_Event | 456
UTUADO | 2023-06-04 07:11 | 2023-06-04 18:45 | 60 | 11:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23060400134 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 694 | 2023-06-04 | 41640 | keep | 0 | Jun | 2023 | 0.028361 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-06-04 07:12 | 2023-06-04 15:26 | 85 | 8:14 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S23060400215 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 494 | 2023-06-04 | 41990 | keep | 0 | Jun | 2023 | 0.028599 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
VEGA BAJA | 2023-06-04 07:14 | 2023-06-04 18:20 | 12 | 11:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23060400070 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 666 | 2023-06-04 | 7992 | keep | 0 | Jun | 2023 | 0.0054433 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2023-06-04 07:15 | 2023-06-04 08:40 | 20 | 1:25 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA EVENTO TRANSFERIDO DE PONCE | P23060400125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2023-06-04 | 1700 | keep | 0 | Jun | 2023 | 0.0011579 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2023-06-04 07:15 | 2023-06-04 15:55 | 25 | 8:40 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSO | A23060400030 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 520 | 2023-06-04 | 13000 | keep | 0 | Jun | 2023 | 0.0088542 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2023-06-04 07:17 | 2023-06-04 14:25 | 60 | 7:08 | P | DESGANCHE | 2 X 50 Y 1 X 40 EN CORTES DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23060400071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 428 | 2023-06-04 | 25680 | keep | 0 | Jun | 2023 | 0.017491 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2023-06-04 07:21 | 2023-06-04 07:22 | 1475 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P23060400129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 1475 | keep | 0 | Jun | 2023 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
ARECIBO | 2023-06-04 07:25 | 2023-06-04 13:15 | 10 | 5:50 | P | DESGANCHE | 1 X 30 EN CL DESGANCHE | M23060400137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 350 | 2023-06-04 | 3500 | keep | 0 | Jun | 2023 | 0.0023838 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-06-04 07:26 | 2023-06-04 07:29 | 2531 | 0:03 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | R2306040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-06-04 | 7593 | keep | 0 | Jun | 2023 | 0.0051716 | 0.0017239 | Momentary | FALSE | FALSE | Not_TMED_Event | 2531
AGUADILLA | 2023-06-04 07:28 | 2023-06-04 20:42 | 80 | 13:14 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN CL DESGANCHE | P23060400134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 794 | 2023-06-04 | 63520 | keep | 0 | Jun | 2023 | 0.043263 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2023-06-04 07:33 | 2023-06-04 19:15 | 125 | 11:42 | P | DESGANCHE | 2 X 100 EN C/L | C23060400143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 702 | 2023-06-04 | 87750 | keep | 0 | Jun | 2023 | 0.059766 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BARRANQUITAS | 2023-06-04 07:34 | 2023-06-04 09:36 | 150 | 2:02 | P | DESGANCHE | 2 X 80 EN C/L | C23060400104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2023-06-04 | 18300 | keep | 0 | Jun | 2023 | 0.012464 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2023-06-04 07:38 | 2023-06-04 14:05 | 20 | 6:27 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER NO SE IDENTIFICO CAUSA | A23060400076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 387 | 2023-06-04 | 7740 | keep | 0 | Jun | 2023 | 0.0052717 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-06-04 07:46 | 2023-06-04 16:54 | 15 | 9:08 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 40 EN C/L | S23060400231 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 548 | 2023-06-04 | 8220 | keep | 0 | Jun | 2023 | 0.0055986 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-06-04 07:47 | 2023-06-04 07:48 | 108 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23060400153 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 108 | keep | 0 | Jun | 2023 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
AGUADILLA | 2023-06-04 07:47 | 2023-06-04 07:48 | 569 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2500 | M23060400146 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-04 | 569 | keep | 0 | Jun | 2023 | 0.00038754 | 0.00038754 | Momentary | FALSE | FALSE | Not_TMED_Event | 569
AGUADILLA | 2023-06-04 07:47 | 2023-06-04 07:48 | 1245 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2500 | M23060400146 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-04 | 1245 | keep | 0 | Jun | 2023 | 0.00084796 | 0.00084796 | Momentary | FALSE | FALSE | Not_TMED_Event | 1245
AGUADILLA | 2023-06-04 07:47 | 2023-06-04 07:48 | 1155 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2500 | M23060400146 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-04 | 1155 | keep | 0 | Jun | 2023 | 0.00078667 | 0.00078667 | Momentary | FALSE | FALSE | Not_TMED_Event | 1155
AGUADILLA | 2023-06-04 07:47 | 2023-06-04 07:48 | 867 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2500 | M23060400147 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-04 | 867 | keep | 0 | Jun | 2023 | 0.00059051 | 0.00059051 | Momentary | FALSE | FALSE | Not_TMED_Event | 867
AGUADILLA | 2023-06-04 07:47 | 2023-06-04 07:48 | 257 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2500 | M23060400147 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-04 | 257 | keep | 0 | Jun | 2023 | 0.00017504 | 0.00017504 | Momentary | FALSE | FALSE | Not_TMED_Event | 257
AGUADILLA | 2023-06-04 07:47 | 2023-06-04 07:48 | 1336 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2500 | M23060400147 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-04 | 1336 | keep | 0 | Jun | 2023 | 0.00090994 | 0.00090994 | Momentary | FALSE | FALSE | Not_TMED_Event | 1336
AGUADILLA | 2023-06-04 07:47 | 2023-06-04 07:48 | 3315 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2500 | M23060400148 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-04 | 3315 | keep | 0 | Jun | 2023 | 0.0022578 | 0.0022578 | Momentary | FALSE | FALSE | Not_TMED_Event | 3315
AGUADILLA | 2023-06-04 07:47 | 2023-06-04 07:48 | 1718 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2500 | M23060400148 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-04 | 1718 | keep | 0 | Jun | 2023 | 0.0011701 | 0.0011701 | Momentary | FALSE | FALSE | Not_TMED_Event | 1718
UTUADO | 2023-06-04 07:47 | 2023-06-04 13:50 | 40 | 6:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 Y 1 X 30 EN CORTES DE LINEA DISTINTOS MAL TIEMPO VIENTOS FUERTES | P23060400151 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 363 | 2023-06-04 | 14520 | keep | 0 | Jun | 2023 | 0.0098895 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-06-04 07:53 | 2023-06-04 07:54 | 837 | 0:01 | T | ALIMENTADOR AMARRADO | CARGA TRANSFERIDA AL 1401-07 | S23060400233 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-04 | 837 | keep | 0 | Jun | 2023 | 0.00057008 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2023-06-04 07:53 | 2023-06-04 07:54 | 908 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | S23060400233 | S23060400233 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-06-04 | 908 | keep | 0 | Jun | 2023 | 0.00061843 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
SAN JUAN | 2023-06-04 07:54 | 2023-06-04 20:20 | 14 | 12:26 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN C/L SE REPARO CONDUCTOR | S23060400264 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 746 | 2023-06-04 | 10444 | keep | 0 | Jun | 2023 | 0.0071134 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2023-06-04 07:56 | 2023-06-04 07:57 | 108 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M23060400153 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 108 | keep | 0 | Jun | 2023 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
BARRANQUITAS | 2023-06-04 07:58 | 2023-06-04 16:05 | 65 | 8:07 | P | DESGANCHE | 1 X 80 EN C/L | C23060400117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 487 | 2023-06-04 | 31655 | keep | 0 | Jun | 2023 | 0.02156 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
UTUADO | 2023-06-04 07:58 | 2023-06-04 09:25 | 50 | 1:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 Y 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | P23060400156 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 87 | 2023-06-04 | 4350 | keep | 0 | Jun | 2023 | 0.0029628 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2023-06-04 07:58 | 2023-06-04 08:00 | 650 | 0:02 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23060400086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-04 | 1300 | keep | 0 | Jun | 2023 | 0.00088542 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
UTUADO | 2023-06-04 08:00 | 2023-06-04 13:45 | 15 | 5:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23060300022 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 345 | 2023-06-04 | 5175 | keep | 0 | Jun | 2023 | 0.0035247 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2023-06-04 08:01 | 2023-06-04 21:17 | 20 | 13:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA SOBRE LINEA | A23060400090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 796 | 2023-06-04 | 15920 | keep | 0 | Jun | 2023 | 0.010843 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-06-04 08:08 | 2023-06-04 12:34 | 50 | 4:26 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23060400177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2023-06-04 | 13300 | keep | 0 | Jun | 2023 | 0.0090586 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-06-04 08:09 | 2023-06-04 14:50 | 51 | 6:41 | P | DESGANCHE | 1 X 65 EN C/L | C23060400121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 401 | 2023-06-04 | 20451 | keep | 0 | Jun | 2023 | 0.013929 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
AGUADILLA | 2023-06-04 08:09 | 2023-06-04 16:30 | 80 | 8:21 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23060400157 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 501 | 2023-06-04 | 40080 | keep | 0 | Jun | 2023 | 0.027298 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-06-04 08:11 | 2023-06-04 18:30 | 85 | 10:19 | P | DESGANCHE | 2 X 50 EN C/L | C23060400122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 619 | 2023-06-04 | 52615 | keep | 0 | Jun | 2023 | 0.035836 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
ARECIBO | 2023-06-04 08:12 | 2023-06-04 16:20 | 2 | 8:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN TRANSFORMADOR | A23060400194 | New_Event | Cutout Failure | Include | Include | Equipment | 488 | 2023-06-04 | 976 | keep | 0 | Jun | 2023 | 0.00066475 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-06-04 08:16 | 2023-06-05 11:05 | 40 | 26:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B23060400111 | New_Event | Cutout Failure | Include | Include | Equipment | 1609 | 2023-06-04 | 64360 | keep | 0 | Jun | 2023 | 0.043835 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-06-04 08:20 | 2023-06-04 12:35 | 30 | 4:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L REMPLAZO CAJA QUEMADA | C23060400168 | New_Event | Cutout Failure | Include | Include | Equipment | 255 | 2023-06-04 | 7650 | keep | 0 | Jun | 2023 | 0.0052104 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-06-04 08:23 | 2023-06-04 08:24 | 271 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S23060400301 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 271 | keep | 0 | Jun | 2023 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
CANOVANAS | 2023-06-04 08:23 | 2023-06-04 13:20 | 14 | 4:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | R23060400020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 297 | 2023-06-04 | 4158 | keep | 0 | Jun | 2023 | 0.002832 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2023-06-04 08:23 | 2023-06-04 17:45 | 110 | 9:22 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23060400163 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 562 | 2023-06-04 | 61820 | keep | 0 | Jun | 2023 | 0.042105 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
MAYAGÃœEZ | 2023-06-04 08:25 | 2023-06-04 09:31 | 30 | 1:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR FUERTE VIENTO | P23060400173 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 66 | 2023-06-04 | 1980 | keep | 0 | Jun | 2023 | 0.0013486 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-06-04 08:26 | 2023-06-04 08:28 | 1380 | 0:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR CERRADO POR CONTROL | R23060400021 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2023-06-04 | 2760 | keep | 0 | Jun | 2023 | 0.0018798 | 0.00093991 | Momentary | FALSE | FALSE | Not_TMED_Event | 1380
BARRANQUITAS | 2023-06-04 08:34 | 2023-06-04 15:30 | 16 | 6:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR Y RELOCALIZAR SECUNDARIA | C23060400129 | New_Event | Secondary Wire Break | Include | Include | Equipment | 416 | 2023-06-04 | 6656 | keep | 0 | Jun | 2023 | 0.0045334 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2023-06-04 08:35 | 2023-06-04 11:48 | 200 | 3:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | HACIENDO PRUEBA EN C/L, PROBO MALO, CAJA AVERIADA INTERRUPTOR DISPARO Y SE CERRO POR SCADA | S23060400251 | New_Event | Cutout Failure | Include | Include | Equipment | 193 | 2023-06-04 | 38600 | keep | 0 | Jun | 2023 | 0.02629 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-06-04 08:38 | 2023-06-04 10:33 | 250 | 1:55 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | B23060400123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2023-06-04 | 28750 | keep | 0 | Jun | 2023 | 0.019581 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BARRANQUITAS | 2023-06-04 08:40 | 2023-06-04 08:41 | 2410 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23060400131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 2410 | keep | 0 | Jun | 2023 | 0.0016414 | 0.0016414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2410
CAGUAS | 2023-06-04 08:47 | 2023-06-04 10:30 | 42 | 1:43 | P | DESGANCHE | 1 X 65 EN C/L | C23060400142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2023-06-04 | 4326 | keep | 0 | Jun | 2023 | 0.0029464 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
HUMACAO | 2023-06-04 08:48 | 2023-06-04 10:17 | 48 | 1:29 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23060400143 | New_Event | Animals | Include | Include | Wildlife | 89 | 2023-06-04 | 4272 | keep | 0 | Jun | 2023 | 0.0029096 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
MAYAGÃœEZ | 2023-06-04 08:49 | 2023-06-04 12:05 | 20 | 3:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 30 EN CORTE DE LINEA POR FUERTE VIENTO | P23060400189 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 196 | 2023-06-04 | 3920 | keep | 0 | Jun | 2023 | 0.0026699 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-06-04 08:51 | 2023-06-04 09:34 | 10 | 0:43 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CL FUERTE VIENTO | M23060400178 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 43 | 2023-06-04 | 430 | keep | 0 | Jun | 2023 | 0.00029287 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-06-04 08:53 | 2023-06-04 15:09 | 4 | 6:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L POR VIENTOS | P23060400193 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 376 | 2023-06-04 | 1504 | keep | 0 | Jun | 2023 | 0.0010244 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2023-06-04 08:53 | 2023-06-04 09:33 | 1 | 0:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN RISER | P23060400194 | New_Event | Cutout Failure | Include | Include | Equipment | 40 | 2023-06-04 | 40 | keep | 0 | Jun | 2023 | 2.7244e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-06-04 08:58 | 2023-06-04 11:36 | 100 | 2:38 | P | ANIMAL | 1 X 80 Y 1 X 50 EN C/LS CRUCE X AVE | C23060400156 | New_Event | Animals | Include | Include | Wildlife | 158 | 2023-06-04 | 15800 | keep | 0 | Jun | 2023 | 0.010761 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-06-04 08:59 | 2023-06-04 13:56 | 120 | 4:57 | P | DESGANCHE | 1 X 65 EN C/L | C23060400158 | New_Event | Vegetation Contact | Include | Include | Vegetation | 297 | 2023-06-04 | 35640 | keep | 0 | Jun | 2023 | 0.024274 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
VEGA BAJA | 2023-06-04 09:04 | 2023-06-04 16:40 | 30 | 7:36 | P | TRANSFORMADOR AVERIADO | 1 X 30 EN CORTE DE LINEA SE SECCIONALIZO TRANSFORMADOR 50 KVA AVERIADO | A23060400107 | New_Event | Service Transformer Failure | Include | Include | Equipment | 456 | 2023-06-04 | 13680 | keep | 0 | Jun | 2023 | 0.0093174 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-06-04 09:06 | 2023-06-04 22:15 | 183 | 13:09 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23060400134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 789 | 2023-06-04 | 144387 | keep | 0 | Jun | 2023 | 0.098341 | 0.00012464 | Sustained | FALSE | FALSE | Not_TMED_Event | 183
AGUADILLA | 2023-06-04 09:07 | 2023-06-04 16:04 | 8 | 6:57 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE REPORTO CAUSA | M23060400186 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 417 | 2023-06-04 | 3336 | keep | 0 | Jun | 2023 | 0.0022721 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-06-04 09:13 | 2023-06-04 19:00 | 17 | 9:47 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHO Y LEVANTO CONDUCTOR | C23060400171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 587 | 2023-06-04 | 9979 | keep | 0 | Jun | 2023 | 0.0067967 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BARRANQUITAS | 2023-06-04 09:13 | 2023-06-04 09:41 | 130 | 0:28 | P | DESGANCHE | 2 X 65 EN C/L | C23060400171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 28 | 2023-06-04 | 3640 | keep | 0 | Jun | 2023 | 0.0024792 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
SAN JUAN | 2023-06-04 09:14 | 2023-06-04 13:45 | 842 | 4:31 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SJ-230604-01 BKR DEFECTUOSO SE TRANSFIRIO LA CARGA AL 1525-04 MEDIANTE AMARRE EXTERNO PARA QUE PERSONAL DE SUBESTACIONES TRABAJE EL BKR | S23060400285 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 271 | 2023-06-04 | 228182 | keep | 0 | Jun | 2023 | 0.15541 | 0.00057348 | Sustained | FALSE | FALSE | Not_TMED_Event | 842
BAYAMON | 2023-06-04 09:19 | 2023-06-04 18:13 | 18 | 8:54 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23060400288 | New_Event | Vegetation Contact | Include | Include | Vegetation | 534 | 2023-06-04 | 9612 | keep | 0 | Jun | 2023 | 0.0065467 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2023-06-04 09:20 | 2023-06-04 09:21 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2306040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 2234 | keep | 0 | Jun | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
SAN JUAN | 2023-06-04 09:27 | 2023-06-04 09:28 | 870 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S23060400301 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 870 | keep | 0 | Jun | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2023-06-04 09:28 | 2023-06-04 09:29 | 4944 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | DISPARO Y SE CERRO POR SCADA | S2306040000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-06-04 | 4944 | keep | 0 | Jun | 2023 | 0.0033673 | 0.0033673 | Momentary | FALSE | FALSE | Not_TMED_Event | 4944
BARRANQUITAS | 2023-06-04 09:29 | 2023-06-04 11:25 | 80 | 1:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L FUERTES VIENTOS | C23060400182 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 116 | 2023-06-04 | 9280 | keep | 0 | Jun | 2023 | 0.0063206 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-06-04 09:34 | 2023-06-04 09:35 | 4944 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | DISPARO Y SE CERRO POR SCADA | S2306040000X | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 1 | 2023-06-04 | 4944 | keep | 0 | Jun | 2023 | 0.0033673 | 0.0033673 | Momentary | FALSE | FALSE | Not_TMED_Event | 4944
MAYAGÃœEZ | 2023-06-04 09:34 | 2023-06-04 10:45 | 120 | 1:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA POR FUERTE VIENTO | M23060400199 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 71 | 2023-06-04 | 8520 | keep | 0 | Jun | 2023 | 0.0058029 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2023-06-04 09:35 | 2023-06-04 14:04 | 211 | 4:29 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L Y SE REPARO LINEA PARTIDA | S23060400303 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 269 | 2023-06-04 | 56759 | keep | 0 | Jun | 2023 | 0.038658 | 0.00014371 | Sustained | FALSE | FALSE | Not_TMED_Event | 211
GUAYAMA | 2023-06-04 09:37 | 2023-06-04 11:26 | 30 | 1:49 | P | SOBRECARGA | 1 X 80 EN CORTE DE LINEA POR CARGA | P23060400231 | New_Event | Trip Due To Overload | Include | Include | Other | 109 | 2023-06-04 | 3270 | keep | 0 | Jun | 2023 | 0.0022272 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-06-04 09:40 | 2023-06-04 12:40 | 40 | 3:00 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS DE LAS LINEAS | M23060400203 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2023-06-04 | 7200 | keep | 0 | Jun | 2023 | 0.0049039 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-06-04 09:41 | 2023-06-04 09:42 | 411 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPOPERACION Y QUEDA EN SERVICIO | M23060400204 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 411 | keep | 0 | Jun | 2023 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
BARRANQUITAS | 2023-06-04 09:41 | 2023-06-04 09:44 | 1617 | 0:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR | C2306040000X | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 3 | 2023-06-04 | 4851 | keep | 0 | Jun | 2023 | 0.003304 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-06-04 09:42 | 2023-06-04 12:39 | 200 | 2:57 | P | DESGANCHE | 1 X 100 EN CL DESGANCHE | M23060300803 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 177 | 2023-06-04 | 35400 | keep | 0 | Jun | 2023 | 0.024111 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-06-04 09:44 | 2023-06-04 10:10 | 130 | 0:26 | P | DESGANCHE | 2 X 65 EN C/L | C23060400171 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 26 | 2023-06-04 | 3380 | keep | 0 | Jun | 2023 | 0.0023021 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
BAYAMON | 2023-06-04 09:45 | 2023-06-04 15:26 | 18 | 5:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN XMR Y SE REPARO SECUNDARIA | B23060300153 | New_Event | Secondary Wire Break | Include | Include | Equipment | 341 | 2023-06-04 | 6138 | keep | 0 | Jun | 2023 | 0.0041806 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BARRANQUITAS | 2023-06-04 09:46 | 2023-06-04 19:08 | 10 | 9:22 | P | DESGANCHE | 1 X 25 EN C/L | C23060400191 | New_Event | Vegetation Contact | Include | Include | Vegetation | 562 | 2023-06-04 | 5620 | keep | 0 | Jun | 2023 | 0.0038278 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-06-04 09:46 | 2023-06-04 11:51 | 150 | 2:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA POR FUERTE VIENTO | M23060400209 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 125 | 2023-06-04 | 18750 | keep | 0 | Jun | 2023 | 0.012771 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-06-04 09:47 | 2023-06-04 09:48 | 1802 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S2306040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 1802 | keep | 0 | Jun | 2023 | 0.0012273 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
UTUADO | 2023-06-04 09:52 | 2023-06-04 18:40 | 50 | 8:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23060400120 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 528 | 2023-06-04 | 26400 | keep | 0 | Jun | 2023 | 0.017981 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-06-04 09:58 | 2023-06-04 19:50 | 54 | 9:52 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | S23060400325 | New_Event | Vegetation Contact | Include | Include | Vegetation | 592 | 2023-06-04 | 31968 | keep | 0 | Jun | 2023 | 0.021773 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
UTUADO | 2023-06-04 09:58 | 2023-06-04 16:00 | 150 | 6:02 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA Y SE CERRO TRIPSAVER | A23060400125 | New_Event | Primary Wire Break | Include | Include | Equipment | 362 | 2023-06-04 | 54300 | keep | 0 | Jun | 2023 | 0.036983 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-06-04 10:02 | 2023-06-04 20:10 | 5 | 10:08 | P | NO SE REPORTO CAUSA | SE ENCONTRO XMR ABIERTO Y NO SE REMPLAZO FUSIBLE | S23060400330 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 608 | 2023-06-04 | 3040 | keep | 0 | Jun | 2023 | 0.0020705 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-06-04 10:04 | 2023-06-04 10:05 | 1802 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S2306040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 1802 | keep | 0 | Jun | 2023 | 0.0012273 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
SAN JUAN | 2023-06-04 10:05 | 2023-06-04 10:06 | 1225 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DEL 1203-01 QUE LLEVA 75% DEL 1203-03 | S2306040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 1225 | keep | 0 | Jun | 2023 | 0.00083434 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2023-06-04 10:05 | 2023-06-04 10:06 | 75 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DEL 1203-01 QUE LLEVA 75% DEL 1203-03 | S2306040000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-04 | 75 | keep | 0 | Jun | 2023 | 5.1082e-05 | 5.1082e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 75
BARRANQUITAS | 2023-06-04 10:05 | 2023-06-04 10:06 | 2635 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | C2306040000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-06-04 | 2635 | keep | 0 | Jun | 2023 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
GUAYAMA | 2023-06-04 10:06 | 2023-06-04 18:31 | 8 | 8:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50KVA A 2400 POR UNO MISMA CAPACIDAD | P23060400258 | New_Event | Service Transformer Failure | Include | Include | Equipment | 505 | 2023-06-04 | 4040 | keep | 0 | Jun | 2023 | 0.0027516 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-06-04 10:06 | 2023-06-04 14:17 | 260 | 4:11 | P | DESGANCHE | 2 X 100 2 X 80 Y 2 X 30 EN C/LS | C23060400195 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 251 | 2023-06-04 | 65260 | keep | 0 | Jun | 2023 | 0.044448 | 0.00017708 | Sustained | FALSE | FALSE | Not_TMED_Event | 260
BARRANQUITAS | 2023-06-04 10:10 | 2023-06-04 10:12 | 1617 | 0:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR CERRADO X CONTROL | C2306040000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-06-04 | 3234 | keep | 0 | Jun | 2023 | 0.0022027 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
BAYAMON | 2023-06-04 10:11 | 2023-06-04 10:14 | 1501 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO/CERRO INTERRUPTOR A PETICION DEL PERSONAL DE CAMPO PARA REPARAR PUENTE PRIMARIO - TRASPATIO - BY-230604-01 | B23060400163 | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2023-06-04 | 4503 | keep | 0 | Jun | 2023 | 0.003067 | 0.0010223 | Momentary | FALSE | FALSE | Not_TMED_Event | 1501
BARRANQUITAS | 2023-06-04 10:12 | 2023-06-04 14:32 | 130 | 4:20 | P | DESGANCHE | 2 X 65 EN C/L | C23060400171 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 260 | 2023-06-04 | 33800 | keep | 0 | Jun | 2023 | 0.023021 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
BAYAMON | 2023-06-04 10:14 | 2023-06-04 11:22 | 1323 | 1:08 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO EN RISER CERCA DE LA SUBESTACION Y SE REPARO PUENTE PRIMARIO ABIERTO - TRASPATIO - BY-230604-01 | B23060400050 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 68 | 2023-06-04 | 89964 | keep | 0 | Jun | 2023 | 0.061274 | 0.00090109 | Sustained | FALSE | FALSE | Not_TMED_Event | 1323
BAYAMON | 2023-06-04 10:14 | 2023-06-05 15:38 | 10 | 29:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | S23060400336 | New_Event | Cutout Failure | Include | Include | Equipment | 1764 | 2023-06-04 | 17640 | keep | 0 | Jun | 2023 | 0.012015 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-06-04 10:15 | 2023-06-04 11:10 | 25 | 0:55 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23060400132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2023-06-04 | 1375 | keep | 0 | Jun | 2023 | 0.00093651 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-06-04 10:17 | 2023-06-04 17:28 | 30 | 7:11 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S23060400264 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 431 | 2023-06-04 | 12930 | keep | 0 | Jun | 2023 | 0.0088066 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-06-04 10:24 | 2023-06-04 15:42 | 100 | 5:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN C/L FUERTES VIENTOS | C23060400213 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 318 | 2023-06-04 | 31800 | keep | 0 | Jun | 2023 | 0.021659 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2023-06-04 10:25 | 2023-06-04 11:41 | 74 | 1:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L FUERTES VIENTOS | C23060400215 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 76 | 2023-06-04 | 5624 | keep | 0 | Jun | 2023 | 0.0038305 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
BARRANQUITAS | 2023-06-04 10:25 | 2023-06-04 16:24 | 227 | 5:59 | P | DESGANCHE | 2 X 100 EN C/L | C23060400214 | New_Event | Vegetation Contact | Include | Include | Vegetation | 359 | 2023-06-04 | 81493 | keep | 0 | Jun | 2023 | 0.055505 | 0.00015461 | Sustained | FALSE | FALSE | Not_TMED_Event | 227
VEGA BAJA | 2023-06-04 10:31 | 2023-06-05 13:16 | 190 | 26:45 | P | CONDUCTOR ARRIADO O CRUZADO | PUENTE PRIMARIO ABIERTO Y LINEAS PRIMARIAS CRUZADAS | A23060400146 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 1605 | 2023-06-04 | 304950 | keep | 0 | Jun | 2023 | 0.2077 | 0.00012941 | Sustained | FALSE | FALSE | Not_TMED_Event | 190
BAYAMON | 2023-06-04 10:34 | 2023-06-05 09:28 | 100 | 22:54 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN C/L MAL TIEMPO LLUVIAS | B23060400171 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1374 | 2023-06-04 | 137400 | keep | 0 | Jun | 2023 | 0.093583 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-06-04 10:34 | 2023-06-04 10:35 | 725 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR | C23060400218 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-06-04 | 725 | keep | 0 | Jun | 2023 | 0.00049379 | 0.00049379 | Momentary | FALSE | FALSE | Not_TMED_Event | 725
CAGUAS | 2023-06-04 10:35 | 2023-06-04 12:40 | 15 | 2:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L VIENTOS FUERTES | C23060400221 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 125 | 2023-06-04 | 1875 | keep | 0 | Jun | 2023 | 0.0012771 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-06-04 10:39 | 2023-06-04 11:15 | 75 | 0:36 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | A23060400150 | New_Event | Animals | Include | Include | Wildlife | 36 | 2023-06-04 | 2700 | keep | 0 | Jun | 2023 | 0.001839 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2023-06-04 10:41 | 2023-06-04 12:00 | 80 | 1:19 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE SECCIONALIZO LINEA CRUZADA | A23060400152 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 79 | 2023-06-04 | 6320 | keep | 0 | Jun | 2023 | 0.0043045 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2023-06-04 11:03 | 2023-06-04 12:48 | 49 | 1:45 | P | DESGANCHE | 2 X 40 EN C/L DESGANCHE | R23060400029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2023-06-04 | 5145 | keep | 0 | Jun | 2023 | 0.0035042 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
FAJARDO | 2023-06-04 11:04 | 2023-06-04 14:02 | 201 | 2:58 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | R23060400030 | New_Event | Animals | Include | Include | Wildlife | 178 | 2023-06-04 | 35778 | keep | 0 | Jun | 2023 | 0.024368 | 0.0001369 | Sustained | FALSE | FALSE | Not_TMED_Event | 201
BAYAMON | 2023-06-04 11:05 | 2023-06-04 11:09 | 580 | 0:04 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1708-02 LLEVA 30% DEL 1707-01 SE CERRO POR CONTROL | B23060400178 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-06-04 | 2320 | keep | 0 | Jun | 2023 | 0.0015801 | 0.00039504 | Momentary | FALSE | FALSE | Not_TMED_Event | 580
BAYAMON | 2023-06-04 11:05 | 2023-06-04 11:09 | 1715 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1708-02 LLEVA 30% DEL 1707-01 SE CERRO POR CONTROL | B23060400178 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-06-04 | 6860 | keep | 0 | Jun | 2023 | 0.0046723 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
PONCE | 2023-06-04 11:13 | 2023-06-04 11:14 | 1478 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23060400301 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 1478 | keep | 0 | Jun | 2023 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
VEGA BAJA | 2023-06-04 11:15 | 2023-06-04 11:18 | 3654 | 0:03 | T | ANIMAL | DISPARO INTERRUPTOR NO RECERRO SE CERRO POR CONTROL SCADA AVE CRUZO LINEAS | A23060400167 | Additional_clients | Animals | Include | Include | Wildlife | 3 | 2023-06-04 | 10962 | keep | 0 | Jun | 2023 | 0.0074662 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-06-04 11:18 | 2023-06-04 13:30 | 75 | 2:12 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | A23060400150 | 1st_after_momentary | Animals | Include | Include | Wildlife | 132 | 2023-06-04 | 9900 | keep | 0 | Jun | 2023 | 0.0067428 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
FAJARDO | 2023-06-04 11:19 | 2023-06-04 15:04 | 50 | 3:45 | P | DESGANCHE | 1 X 30 EN C/L Y DESGANCHE | R23060400032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2023-06-04 | 11250 | keep | 0 | Jun | 2023 | 0.0076623 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-06-04 11:19 | 2023-06-04 13:05 | 6 | 1:46 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE PRIMARIO EN CAJA DE TRANSFORMADOR | P23060400307 | New_Event | Primary Wire Break | Include | Include | Equipment | 106 | 2023-06-04 | 636 | keep | 0 | Jun | 2023 | 0.00043318 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-06-04 11:20 | 2023-06-04 12:00 | 60 | 0:40 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA DE EMERGENCIA POR LINEA PARTIDA ENERGIZADA EN EL SUELO | A23060400168 | New_Event | Primary Wire Break | Include | Include | Equipment | 40 | 2023-06-04 | 2400 | keep | 0 | Jun | 2023 | 0.0016346 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2023-06-04 11:20 | 2023-06-04 12:30 | 30 | 1:10 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | P23060400222 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 70 | 2023-06-04 | 2100 | keep | 0 | Jun | 2023 | 0.0014303 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-06-04 11:23 | 2023-06-05 00:37 | 44 | 13:14 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | B23060400183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 794 | 2023-06-04 | 34936 | keep | 0 | Jun | 2023 | 0.023795 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
BAYAMON | 2023-06-04 11:26 | 2023-06-04 11:27 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2306040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 2234 | keep | 0 | Jun | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BARRANQUITAS | 2023-06-04 11:27 | 2023-06-04 14:27 | 50 | 3:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN CORTE DE LINEA FUERTES VIENTOS | A23060400171 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 180 | 2023-06-04 | 9000 | keep | 0 | Jun | 2023 | 0.0061299 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-06-04 11:30 | 2023-06-04 15:58 | 30 | 4:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23060400250 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 268 | 2023-06-04 | 8040 | keep | 0 | Jun | 2023 | 0.005476 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-06-04 11:30 | 2023-06-04 12:45 | 9 | 1:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | A23060400139 | New_Event | Secondary Wire Break | Include | Include | Equipment | 75 | 2023-06-04 | 675 | keep | 0 | Jun | 2023 | 0.00045974 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2023-06-04 11:30 | 2023-06-04 17:30 | 60 | 6:00 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN CORTES DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | C23060400258 | New_Event | Vegetation Contact | Include | Include | Vegetation | 360 | 2023-06-04 | 21600 | keep | 0 | Jun | 2023 | 0.014712 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-06-04 11:32 | 2023-06-04 12:18 | 107 | 0:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L FUERTES VIENTOS | C23060400260 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 46 | 2023-06-04 | 4922 | keep | 0 | Jun | 2023 | 0.0033524 | 7.2877e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 107
HUMACAO | 2023-06-04 11:35 | 2023-06-04 11:36 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23060400262 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 2354 | keep | 0 | Jun | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
MAYAGÃœEZ | 2023-06-04 11:36 | 2023-06-04 13:15 | 150 | 1:39 | P | CONDUCTOR ARRIADO O CRUZADO | SE SEPARO LINEA PRIMARIAS CRUZADAS Y SE RESETEO RECLOSER DE LOS VIEJOS DE PREPA SON LOS CLIENTES | P23060400318 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 99 | 2023-06-04 | 14850 | keep | 0 | Jun | 2023 | 0.010114 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-06-04 11:36 | 2023-06-04 18:57 | 60 | 7:21 | P | DESGANCHE | 1 X 50 EN CL SE REALIZA DESGANCHE CRITICO | M23060400256 | New_Event | Vegetation Contact | Include | Include | Vegetation | 441 | 2023-06-04 | 26460 | keep | 0 | Jun | 2023 | 0.018022 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2023-06-04 11:36 | 2023-06-04 11:38 | 1633 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO L-1900 CONDUCTORES ARRIADOS ENTRE ACB 1933A - ACB 1945B | A23060500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-04 | 3266 | keep | 0 | Jun | 2023 | 0.0022245 | 0.0011122 | Momentary | FALSE | FALSE | Not_TMED_Event | 1633
UTUADO | 2023-06-04 11:36 | 2023-06-04 11:38 | 1624 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO L-1900 CONDUCTORES ARRIADOS ENTRE ACB 1933A - ACB 1945B | A23060500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-04 | 3248 | keep | 0 | Jun | 2023 | 0.0022122 | 0.0011061 | Momentary | FALSE | FALSE | Not_TMED_Event | 1624
CAGUAS | 2023-06-04 11:37 | 2023-06-04 17:37 | 150 | 6:00 | P | DESGANCHE | 2 X 80 Y 1 X 65 EN C/L | C23060400321 | New_Event | Vegetation Contact | Include | Include | Vegetation | 360 | 2023-06-04 | 54000 | keep | 0 | Jun | 2023 | 0.036779 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-06-04 11:46 | 2023-06-04 12:15 | 3 | 0:29 | P | DESGANCHE | 3 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE EVENTO TRANSFERIDO DE PONCE | P23060400328 | New_Event | Vegetation Contact | Include | Include | Vegetation | 29 | 2023-06-04 | 87 | keep | 0 | Jun | 2023 | 5.9255e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-06-04 11:46 | 2023-06-04 21:53 | 30 | 10:07 | P | DESGANCHE | 2 X 50 Y 2 X 100 EN CORTES DE LINEAS | B23060400186 | New_Event | Vegetation Contact | Include | Include | Vegetation | 607 | 2023-06-04 | 18210 | keep | 0 | Jun | 2023 | 0.012403 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-06-04 11:47 | 2023-06-04 13:52 | 15 | 2:05 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | C23060400267 | New_Event | Animals | Include | Include | Wildlife | 125 | 2023-06-04 | 1875 | keep | 0 | Jun | 2023 | 0.0012771 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-06-04 11:47 | 2023-06-04 15:46 | 150 | 3:59 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN C/LS | C23060400268 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2023-06-04 | 35850 | keep | 0 | Jun | 2023 | 0.024417 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2023-06-04 11:47 | 2023-06-04 13:11 | 137 | 1:24 | P | DESGANCHE | 2 X 40 EN C/L | C23060400269 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2023-06-04 | 11508 | keep | 0 | Jun | 2023 | 0.007838 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
SAN JUAN | 2023-06-04 11:48 | 2023-06-04 11:49 | 936 | 0:01 | P | ALIMENTADOR AMARRADO | HACIENDO PRUEBA EN C/L DE ORDEN 6002, PROBO MALO E INTERRUPTOR DISPARO SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA. 1336-08 LLEVA 15% DEL 1336-07 Y 20% DEL 1336-08 ESTA POR 1424-08 | S2306040000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-04 | 936 | keep | 0 | Jun | 2023 | 0.00063751 | 0.00063751 | Momentary | FALSE | FALSE | Not_TMED_Event | 936
SAN JUAN | 2023-06-04 11:48 | 2023-06-04 11:49 | 4232 | 0:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | HACIENDO PRUEBA EN C/L DE ORDEN 6002, PROBO MALO Y INTERRUPTOR DISPARO SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA. 1336-08 LLEVA 15% DEL 1336-07 Y 20% DEL 1336-08 ESTA POR 1424-08 | S2306040000X | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-06-04 | 4232 | keep | 0 | Jun | 2023 | 0.0028824 | 0.0028824 | Momentary | FALSE | FALSE | Not_TMED_Event | 4232
SAN JUAN | 2023-06-04 11:49 | 2023-06-04 12:17 | 200 | 0:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN C/L SE REMPLAZO CAJA PRIMARIA | S23060400251 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 28 | 2023-06-04 | 5600 | keep | 0 | Jun | 2023 | 0.0038141 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-06-04 11:53 | 2023-06-04 11:54 | 1368 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S2306040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 1368 | keep | 0 | Jun | 2023 | 0.00093174 | 0.00093174 | Momentary | FALSE | FALSE | Not_TMED_Event | 1368
AGUADILLA | 2023-06-04 11:54 | 2023-06-04 18:47 | 150 | 6:53 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CORTE DE LINEA | M23060400263 | New_Event | Primary Wire Break | Include | Include | Equipment | 413 | 2023-06-04 | 61950 | keep | 0 | Jun | 2023 | 0.042194 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2023-06-04 12:00 | 2023-06-04 19:35 | 175 | 7:35 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PARTIDA SE CERRO CORTE DE LINEA | A23060400194 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 455 | 2023-06-04 | 79625 | keep | 0 | Jun | 2023 | 0.054232 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-06-04 12:00 | 2023-06-04 14:00 | 15 | 2:00 | P | CONDUCTOR ARRIADO O CRUZADO | SE REPARO LINEA PRIMARIA ARRIADA SE CERRO CORTE DE LINEA | A23060400152 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 120 | 2023-06-04 | 1800 | keep | 0 | Jun | 2023 | 0.001226 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-06-04 12:06 | 2023-06-04 15:53 | 100 | 3:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CL FUERTE VIENTO | M23060400267 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 227 | 2023-06-04 | 22700 | keep | 0 | Jun | 2023 | 0.015461 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-06-04 12:17 | 2023-06-05 18:40 | 40 | 30:23 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S23060400403 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1823 | 2023-06-04 | 72920 | keep | 0 | Jun | 2023 | 0.049665 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-06-04 12:19 | 2023-06-04 18:30 | 7 | 6:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 SE REMPLAZO CAJA PRIMARIA EVENTO TRANSFERIDO | P23060400347 | New_Event | Cutout Failure | Include | Include | Equipment | 371 | 2023-06-04 | 2597 | keep | 0 | Jun | 2023 | 0.0017688 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-06-04 12:25 | 2023-06-04 23:23 | 3 | 10:58 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE EVENTO TRANSFERIDO DE PONCE | P23060400352 | New_Event | Animals | Include | Include | Wildlife | 658 | 2023-06-04 | 1974 | keep | 0 | Jun | 2023 | 0.0013445 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-06-04 12:26 | 2023-06-04 12:27 | 1514 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTRAL | B23060400196 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 1514 | keep | 0 | Jun | 2023 | 0.0010312 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
AGUADILLA | 2023-06-04 12:30 | 2023-06-04 19:34 | 100 | 7:04 | P | DESGANCHE | 1 X 65 EN CL DESGANCHE | M23060400276 | New_Event | Vegetation Contact | Include | Include | Vegetation | 424 | 2023-06-04 | 42400 | keep | 0 | Jun | 2023 | 0.028878 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-06-04 12:34 | 2023-06-04 12:37 | 959 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1904-07 LLEVA LA CARGA DEL 1901-01 LLEVA LA CARGA DEL 1901-04 LLEVA LA CARGA DEL 1901-05 SE CERRO POR CONTROL | S2306040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-06-04 | 2877 | keep | 0 | Jun | 2023 | 0.0019595 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-06-04 12:34 | 2023-06-04 12:37 | 1264 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1904-07 LLEVA LA CARGA DEL 1901-01 LLEVA LA CARGA DEL 1901-04 LLEVA LA CARGA DEL 1901-05 SE CERRO POR CONTROL | S2306040000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-06-04 | 3792 | keep | 0 | Jun | 2023 | 0.0025827 | 0.0008609 | Momentary | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2023-06-04 12:34 | 2023-06-04 12:37 | 62 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1904-07 LLEVA LA CARGA DEL 1901-01 LLEVA LA CARGA DEL 1901-04 LLEVA 10% DE LA CARGA DEL 1901-05 SE CERRO POR CONTROL | S2306040000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-06-04 | 186 | keep | 0 | Jun | 2023 | 0.00012668 | 4.2228e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 62
ARECIBO | 2023-06-04 12:35 | 2023-06-04 18:15 | 200 | 5:40 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA | A23060400206 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 340 | 2023-06-04 | 68000 | keep | 0 | Jun | 2023 | 0.046314 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-06-04 12:37 | 2023-06-05 10:19 | 50 | 21:42 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23060400177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1302 | 2023-06-04 | 65100 | keep | 0 | Jun | 2023 | 0.044339 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-06-04 12:39 | 2023-06-04 12:40 | 411 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23060400277 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 411 | keep | 0 | Jun | 2023 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2023-06-04 12:40 | 2023-06-04 13:39 | 200 | 0:59 | P | DESGANCHE | 1 X 100 EN CL DESGANCHE | M23060300803 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2023-06-04 | 11800 | keep | 0 | Jun | 2023 | 0.0080369 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2023-06-04 12:42 | 2023-06-04 16:02 | 500 | 3:20 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 Y 1 X 65 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA ARRIADA | M23060400278 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 200 | 2023-06-04 | 100000 | keep | 0 | Jun | 2023 | 0.06811 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
MAYAGÃœEZ | 2023-06-04 12:46 | 2023-06-04 16:45 | 200 | 3:59 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23060400280 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 239 | 2023-06-04 | 47800 | keep | 0 | Jun | 2023 | 0.032556 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2023-06-04 12:49 | 2023-06-04 16:47 | 20 | 3:58 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C23060400287 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 238 | 2023-06-04 | 4760 | keep | 0 | Jun | 2023 | 0.003242 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-06-04 12:51 | 2023-06-04 18:00 | 12 | 5:09 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA DE TRANSFORMADOR | A23060400148 | New_Event | Primary Wire Break | Include | Include | Equipment | 309 | 2023-06-04 | 3708 | keep | 0 | Jun | 2023 | 0.0025255 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-06-04 12:51 | 2023-06-04 17:18 | 12 | 4:27 | P | NO SE REPORTO CAUSA | 1 X 30 EN TRANSFORMADOR NO SE REPORTO CAUSA | A23060400211 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 267 | 2023-06-04 | 3204 | keep | 0 | Jun | 2023 | 0.0021822 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-06-04 12:57 | 2023-06-04 12:59 | 1501 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B23060400202 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-04 | 3002 | keep | 0 | Jun | 2023 | 0.0020446 | 0.0010223 | Momentary | FALSE | FALSE | Not_TMED_Event | 1501
AGUADILLA | 2023-06-04 13:00 | 2023-06-04 15:45 | 40 | 2:45 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 25 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA | M23060400283 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 165 | 2023-06-04 | 6600 | keep | 0 | Jun | 2023 | 0.0044952 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-06-04 13:03 | 2023-06-04 17:15 | 150 | 4:12 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23060400285 | New_Event | Vegetation Contact | Include | Include | Vegetation | 252 | 2023-06-04 | 37800 | keep | 0 | Jun | 2023 | 0.025745 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2023-06-04 13:08 | 2023-06-04 22:28 | 2 | 9:20 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA POR PARARRAYO CRUZADO | M23060400560 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 560 | 2023-06-04 | 1120 | keep | 0 | Jun | 2023 | 0.00076283 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-06-04 13:16 | 2023-06-04 14:09 | 40 | 0:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CL FUERTE VIENTO | P23060400374 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 53 | 2023-06-04 | 2120 | keep | 0 | Jun | 2023 | 0.0014439 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-06-04 13:25 | 2023-06-04 14:15 | 124 | 0:50 | P | CAUSAS EXTERNAS | REMPLAZO POSTE PRIMARIO PARTIDO POR CAMION | C23060400160 | New_Event | Damage From Public | Include | Include | Public | 50 | 2023-06-04 | 6200 | keep | 0 | Jun | 2023 | 0.0042228 | 8.4456e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 124
GUAYAMA | 2023-06-04 13:29 | 2023-06-04 16:03 | 6 | 2:34 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR POR DESGANCHE | P23060400380 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2023-06-04 | 924 | keep | 0 | Jun | 2023 | 0.00062933 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2023-06-04 13:30 | 2023-06-04 16:09 | 60 | 2:39 | P | ANIMAL | 1 X 50 SMU EN SU #1 ANIMAL | P23060400382 | New_Event | Animals | Include | Include | Wildlife | 159 | 2023-06-04 | 9540 | keep | 0 | Jun | 2023 | 0.0064977 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-06-04 13:33 | 2023-06-04 19:16 | 1 | 5:43 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER NO SE ENCONTRO CAUSA | M23060400305 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 343 | 2023-06-04 | 343 | keep | 0 | Jun | 2023 | 0.00023362 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-06-04 13:37 | 2023-06-04 16:05 | 40 | 2:28 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR IGUANA CRUZO BUSHING DE TRANSFORMADOR | A23060400232 | New_Event | Animals | Include | Include | Wildlife | 148 | 2023-06-04 | 5920 | keep | 0 | Jun | 2023 | 0.0040321 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-06-04 13:41 | 2023-06-04 18:21 | 85 | 4:40 | P | DESGANCHE | 2 X 65 Y 2 X 30 EN C/L DESGANCHE | B23060400210 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2023-06-04 | 23800 | keep | 0 | Jun | 2023 | 0.01621 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
HUMACAO | 2023-06-04 13:48 | 2023-06-04 14:59 | 18 | 1:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L FUERTES VIENTOS | C23060400310 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 71 | 2023-06-04 | 1278 | keep | 0 | Jun | 2023 | 0.00087044 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
ARECIBO | 2023-06-04 13:48 | 2023-06-04 14:45 | 20 | 0:57 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23060400238 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 57 | 2023-06-04 | 1140 | keep | 0 | Jun | 2023 | 0.00077645 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-06-04 13:50 | 2023-06-04 20:49 | 40 | 6:59 | P | DESGANCHE | 1 X 100 EN C/L | C23060400311 | New_Event | Vegetation Contact | Include | Include | Vegetation | 419 | 2023-06-04 | 16760 | keep | 0 | Jun | 2023 | 0.011415 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-06-04 13:51 | 2023-06-05 10:14 | 127 | 20:23 | P | ANIMAL | 1 X 50 EN C/L CRUCE X IGUANA | B23060400211 | New_Event | Animals | Include | Include | Wildlife | 1223 | 2023-06-04 | 155321 | keep | 0 | Jun | 2023 | 0.10579 | 8.6499e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 127
VEGA BAJA | 2023-06-04 13:53 | 2023-06-04 18:30 | 10 | 4:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA QUEMADA Y AISLADORES QUEMADOS | A23060400240 | New_Event | Cutout Failure | Include | Include | Equipment | 277 | 2023-06-04 | 2770 | keep | 0 | Jun | 2023 | 0.0018866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-06-04 13:58 | 2023-06-04 19:06 | 760 | 5:08 | T | ALIMENTADOR AMARRADO | SJ-230603-03 SE ABRIO AMARRE CONTRA 1205-02, SE CERRO PUENTES ABIERTOS EN LA SUBESTACION Y SE CERRO BKR EN SUBESTACION | S23060400214 | New_Event | Feeder Load Transferred | Include | Include | Other | 308 | 2023-06-04 | 234080 | keep | 0 | Jun | 2023 | 0.15943 | 0.00051763 | Sustained | FALSE | FALSE | Not_TMED_Event | 760
SAN JUAN | 2023-06-04 13:58 | 2023-06-04 15:53 | 456 | 1:55 | P | CONDUCTOR ROTO O ABIERTO | SJ-230603-03 SE ABRIO AMARRE DEL 1205-02 CON 1201-02, SE REPARO PUENTE ABIERTO EN LA SALIDA Y SE CERRO POR SCADA | S23060400214 | New_Event | Primary Wire Break | Include | Include | Equipment | 115 | 2023-06-04 | 52440 | keep | 0 | Jun | 2023 | 0.035717 | 0.00031058 | Sustained | FALSE | FALSE | Not_TMED_Event | 456
CANOVANAS | 2023-06-04 14:00 | 2023-06-04 20:55 | 40 | 6:55 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE | R23060400049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 415 | 2023-06-04 | 16600 | keep | 0 | Jun | 2023 | 0.011306 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-06-04 14:01 | 2023-06-04 17:35 | 76 | 3:34 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23060400457 | New_Event | Vegetation Contact | Include | Include | Vegetation | 214 | 2023-06-04 | 16264 | keep | 0 | Jun | 2023 | 0.011077 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
MAYAGÃœEZ | 2023-06-04 14:01 | 2023-06-04 14:02 | 1252 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M23060400326 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 1252 | keep | 0 | Jun | 2023 | 0.00085273 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2023-06-04 14:02 | 2023-06-04 16:18 | 100 | 2:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | P23060400376 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 136 | 2023-06-04 | 13600 | keep | 0 | Jun | 2023 | 0.0092629 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2023-06-04 14:02 | 2023-06-04 16:55 | 40 | 2:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23060400243 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 173 | 2023-06-04 | 6920 | keep | 0 | Jun | 2023 | 0.0047132 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-06-04 14:05 | 2023-06-04 14:06 | 725 | 0:01 | T | CONDUCTOR ARRIADO O CRUZADO | RECIERRE DE INTERRUPTOR | C23060400314 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 1 | 2023-06-04 | 725 | keep | 0 | Jun | 2023 | 0.00049379 | 0.00049379 | Momentary | FALSE | FALSE | Not_TMED_Event | 725
CAGUAS | 2023-06-04 14:06 | 2023-06-04 17:40 | 60 | 3:34 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN C/L LINEAS ARRIADAS | C23060400323 | 1st_after_momentary | Primary To Primary Contact | Include | Include | Equipment | 214 | 2023-06-04 | 12840 | keep | 0 | Jun | 2023 | 0.0087453 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-06-04 14:09 | 2023-06-05 10:00 | 10 | 19:51 | P | SECUNDARIA/DESGANCHE | DESGANCHE EN SECUNDARIA 1 X 10 EN XMR | C23060400316 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1191 | 2023-06-04 | 11910 | keep | 0 | Jun | 2023 | 0.0081118 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2023-06-04 14:25 | 2023-06-04 20:30 | 25 | 6:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23060400251 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 365 | 2023-06-04 | 9125 | keep | 0 | Jun | 2023 | 0.006215 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2023-06-04 14:27 | 2023-06-04 18:55 | 20 | 4:28 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23060400253 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2023-06-04 | 5360 | keep | 0 | Jun | 2023 | 0.0036507 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-06-04 14:27 | 2023-06-04 14:45 | 25 | 0:18 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO ENREDADERA SOBRE LINEAS | P23060400435 | New_Event | Vegetation Contact | Include | Include | Vegetation | 18 | 2023-06-04 | 450 | keep | 0 | Jun | 2023 | 0.00030649 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-06-04 14:30 | 2023-06-04 14:31 | 1380 | 0:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE BKR SE CERRO X CONTROL | R23060400052 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-06-04 | 1380 | keep | 0 | Jun | 2023 | 0.00093991 | 0.00093991 | Momentary | FALSE | FALSE | Not_TMED_Event | 1380
BARRANQUITAS | 2023-06-04 14:32 | 2023-06-04 16:00 | 30 | 1:28 | P | DESGANCHE | 1 X 30 EN C/L | C23060400333 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2023-06-04 | 2640 | keep | 0 | Jun | 2023 | 0.0017981 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-06-04 14:33 | 2023-06-04 14:34 | 1380 | 0:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE BKR SE CERRO X CONTROL | R23060400053 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2023-06-04 | 1380 | keep | 0 | Jun | 2023 | 0.00093991 | 0.00093991 | Momentary | FALSE | FALSE | Not_TMED_Event | 1380
UTUADO | 2023-06-04 14:36 | 2023-06-04 20:20 | 30 | 5:44 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CONVERTIDOR MAL TIEMPO DESCARGAS ELECTRICAS | A23060400255 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 344 | 2023-06-04 | 10320 | keep | 0 | Jun | 2023 | 0.0070289 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-06-04 14:37 | 2023-06-04 17:04 | 11 | 2:27 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN C/L RETEZO LINEA | C23060400337 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 147 | 2023-06-04 | 1617 | keep | 0 | Jun | 2023 | 0.0011013 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CANOVANAS | 2023-06-04 14:38 | 2023-06-04 14:40 | 1380 | 0:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE BKR SE CERRO X CONTROL | R23060400054 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 2 | 2023-06-04 | 2760 | keep | 0 | Jun | 2023 | 0.0018798 | 0.00093991 | Momentary | FALSE | FALSE | Not_TMED_Event | 1380
SAN JUAN | 2023-06-04 14:41 | 2023-06-04 15:56 | 1 | 1:15 | P | NO SE REPORTO CAUSA | 1 X 30 EN XMR EVENTO TRANSFERIDO | P23060400448 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 75 | 2023-06-04 | 75 | keep | 0 | Jun | 2023 | 5.1082e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-06-04 14:41 | 2023-06-05 12:34 | 60 | 21:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO VIENTOS | B23060400233 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1313 | 2023-06-04 | 78780 | keep | 0 | Jun | 2023 | 0.053657 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-06-04 14:44 | 2023-06-04 15:48 | 1380 | 1:04 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE BKR. SE DEJO FUERA PORQUE HIZO VARIAS OPERACIONES CORRIDAS. SE SECCIONALIZO MACHETE QUEMADO CON SJ-230604-51. ENTRO UN 95% EN SERVICIO | R23060400057 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 64 | 2023-06-04 | 88320 | keep | 0 | Jun | 2023 | 0.060154 | 0.00093991 | Sustained | FALSE | FALSE | Not_TMED_Event | 1380
BARRANQUITAS | 2023-06-04 14:52 | 2023-06-04 21:43 | 101 | 6:51 | P | ARBOL SOBRE LINEA | 2 X 40 2 X 50 Y 1 X 30 RETIRO ARBOL DE LAS LINEAS | C23060400383 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 411 | 2023-06-04 | 41511 | keep | 0 | Jun | 2023 | 0.028273 | 6.8791e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 101
UTUADO | 2023-06-04 15:00 | 2023-06-04 19:30 | 50 | 4:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGACNHE | A23060400268 | New_Event | Vegetation Contact | Include | Include | Vegetation | 270 | 2023-06-04 | 13500 | keep | 0 | Jun | 2023 | 0.0091948 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-06-04 15:02 | 2023-06-04 18:47 | 48 | 3:45 | P | DESGANCHE | SE ABRE CORTE DE LINEA SE LEVANTO ALAMBRE PRIMARIO QUE CAYO POR DESGANCHE Y SE CERRO CORTE DE LINEA | P23060400467 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2023-06-04 | 10800 | keep | 0 | Jun | 2023 | 0.0073558 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
BARRANQUITAS | 2023-06-04 15:13 | 2023-06-05 12:00 | 220 | 20:47 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 100 EN CORTE DE LINEA SE INTALO RIGIDO | C23060400360 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1247 | 2023-06-04 | 274340 | keep | 0 | Jun | 2023 | 0.18685 | 0.00014984 | Sustained | FALSE | FALSE | Not_TMED_Event | 220
BARRANQUITAS | 2023-06-04 15:13 | 2023-06-04 19:12 | 95 | 3:59 | P | DESGANCHE | 2 X 50 EN C/L | C23060400360 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2023-06-04 | 22705 | keep | 0 | Jun | 2023 | 0.015464 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
BAYAMON | 2023-06-04 15:15 | 2023-06-05 10:58 | 100 | 19:43 | P | DESGANCHE | 2X50 EN C/L, 3X15 EN OTRO C/L DESGANCHE | B23060400246 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1183 | 2023-06-04 | 118300 | keep | 0 | Jun | 2023 | 0.080574 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-06-04 15:19 | 2023-06-04 15:55 | 100 | 0:36 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M23060400365 | New_Event | Vegetation Contact | Include | Include | Vegetation | 36 | 2023-06-04 | 3600 | keep | 0 | Jun | 2023 | 0.0024519 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-06-04 15:24 | 2023-06-04 21:25 | 50 | 6:01 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE MASIVO | A23060400284 | New_Event | Vegetation Contact | Include | Include | Vegetation | 361 | 2023-06-04 | 18050 | keep | 0 | Jun | 2023 | 0.012294 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-06-04 15:35 | 2023-06-05 15:07 | 15 | 23:32 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23060400529 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1412 | 2023-06-04 | 21180 | keep | 0 | Jun | 2023 | 0.014426 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-06-04 15:40 | 2023-06-04 15:41 | 1615 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S2306040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 1615 | keep | 0 | Jun | 2023 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
FAJARDO | 2023-06-04 15:43 | 2023-06-04 16:05 | 25 | 0:22 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE EVENTO TRANSFERIDO DE PONCE | P23060400497 | New_Event | Vegetation Contact | Include | Include | Vegetation | 22 | 2023-06-04 | 550 | keep | 0 | Jun | 2023 | 0.0003746 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-06-04 15:48 | 2023-06-04 18:10 | 69 | 2:22 | P | DESCONECTIVO DEFECTUOSO | SJ-230604-51. SE REEMPLAZARON 2 MACHETES QUEMADOS. ENTRO EL 5% QUE FALTABA. 100% EN SERVICIO | R23060400057 | Partial_restoration | Switch Failure | Include | Include | Equipment | 142 | 2023-06-04 | 9798 | keep | 0 | Jun | 2023 | 0.0066734 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-06-04 15:50 | 2023-06-05 11:45 | 40 | 19:55 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE | A23060400293 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1195 | 2023-06-04 | 47800 | keep | 0 | Jun | 2023 | 0.032556 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-06-04 15:58 | 2023-06-04 16:38 | 14 | 0:40 | P | ANIMAL | 1 X 20 EN C/L CRUCE POR AVE | S23060400543 | New_Event | Animals | Include | Include | Wildlife | 40 | 2023-06-04 | 560 | keep | 0 | Jun | 2023 | 0.00038141 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
HUMACAO | 2023-06-04 16:05 | 2023-06-04 17:00 | 16 | 0:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | REMPLAZO CONECTORES EN BAJANTE SECUNDARIO | C23060400388 | New_Event | Secondary Wire Break | Include | Include | Equipment | 55 | 2023-06-04 | 880 | keep | 0 | Jun | 2023 | 0.00059936 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2023-06-04 16:09 | 2023-06-04 17:35 | 10 | 1:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | P23060400579 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 86 | 2023-06-04 | 860 | keep | 0 | Jun | 2023 | 0.00058574 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2023-06-04 16:12 | 2023-06-04 18:10 | 25 | 1:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23060400304 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 118 | 2023-06-04 | 2950 | keep | 0 | Jun | 2023 | 0.0020092 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-06-04 16:18 | 2023-06-05 12:19 | 100 | 20:01 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA Y 1 X 80 EN DIFERENTE CORTE DE LINEA POR DESCARGAS ELECTRICAS | M23060400101 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1201 | 2023-06-04 | 120100 | keep | 0 | Jun | 2023 | 0.0818 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-06-04 16:20 | 2023-06-05 10:43 | 8 | 18:23 | P | NO SE REPORTO CAUSA | 1X80 EN C/L (EVENTO TRANSFERIDO DE REGION-PONCE) | P23060400522 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1103 | 2023-06-04 | 8824 | keep | 0 | Jun | 2023 | 0.00601 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2023-06-04 16:22 | 2023-06-04 18:40 | 100 | 2:18 | P | TERMINACION SOTERRADA AVERIADA | SE REMPLAZO BUSHING EN TRANSFORMADOR Y TERMINACION PISTOLA 1 X 40 SMU EN SU-24 | P23060400525 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 138 | 2023-06-04 | 13800 | keep | 0 | Jun | 2023 | 0.0093991 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-06-04 16:24 | 2023-06-04 19:36 | 175 | 3:12 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 Y 1 X 80 EN C/LS FIJO CONDUCTOR EVENTO TRANSFERIDO DE BAYAMON | B23060400268 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 192 | 2023-06-04 | 33600 | keep | 0 | Jun | 2023 | 0.022885 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
BARRANQUITAS | 2023-06-04 16:45 | 2023-06-04 23:21 | 10 | 6:36 | P | DESGANCHE | 2 X 30 EN C/L DESGANCHE | C23060400399 | New_Event | Vegetation Contact | Include | Include | Vegetation | 396 | 2023-06-04 | 3960 | keep | 0 | Jun | 2023 | 0.0026971 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-06-04 16:47 | 2023-06-05 17:20 | 2 | 24:33 | P | AISLADOR ROTO, PARTIDO O SAFADO | 3 X 100 EN RISER SE REMPLAZO AISLADOR PARTIDO EVENTO TRANSFERIDO | P23060400546 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1473 | 2023-06-04 | 2946 | keep | 0 | Jun | 2023 | 0.0020065 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2023-06-04 16:49 | 2023-06-05 09:35 | 9 | 16:46 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA | R23060400074 | New_Event | Primary Wire Break | Include | Include | Equipment | 1006 | 2023-06-04 | 9054 | keep | 0 | Jun | 2023 | 0.0061666 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BARRANQUITAS | 2023-06-04 16:56 | 2023-06-04 19:01 | 38 | 2:05 | P | DESGANCHE | 2 X 50 EN C/L | C23060400404 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2023-06-04 | 4750 | keep | 0 | Jun | 2023 | 0.0032352 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
BAYAMON | 2023-06-04 17:08 | 2023-06-05 17:10 | 7 | 24:02 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVISIONAL AEREO @ T-37 | B23060300454 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1442 | 2023-06-04 | 10094 | keep | 0 | Jun | 2023 | 0.006875 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-06-04 17:13 | 2023-06-05 14:30 | 50 | 21:17 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 Y 1 X 40 EN DISTINTOS CORTES DE LINEA POR FUERTE VIENTO | P23060400561 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1277 | 2023-06-04 | 63850 | keep | 0 | Jun | 2023 | 0.043488 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-06-04 17:13 | 2023-06-04 18:30 | 60 | 1:17 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | P23060400563 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2023-06-04 | 4620 | keep | 0 | Jun | 2023 | 0.0031467 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-06-04 17:23 | 2023-06-05 10:23 | 50 | 17:00 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 80 EN CORTE DE LINEA LINEAS CRUZADAS | C23060400410 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 1020 | 2023-06-04 | 51000 | keep | 0 | Jun | 2023 | 0.034736 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-06-04 17:33 | 2023-06-05 12:46 | 10 | 19:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 REMPLAZO CAJA PRIMARIA | R23060400079 | New_Event | Cutout Failure | Include | Include | Equipment | 1153 | 2023-06-04 | 11530 | keep | 0 | Jun | 2023 | 0.007853 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-06-04 17:37 | 2023-06-05 14:45 | 8 | 21:08 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C23060400419 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1268 | 2023-06-04 | 10144 | keep | 0 | Jun | 2023 | 0.006909 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-06-04 17:41 | 2023-06-05 08:26 | 5 | 14:45 | P | ANIMAL | 1 X 8 EN TRANSFORMADOR CRUCE POR AVE | A23060400316 | New_Event | Animals | Include | Include | Wildlife | 885 | 2023-06-04 | 4425 | keep | 0 | Jun | 2023 | 0.0030138 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-06-04 17:51 | 2023-06-04 17:52 | 936 | 0:01 | P | ALIMENTADOR AMARRADO | SE DISPARO POR SEGURIDAD LA CAJA PRIMARIA NO TENIA EL ADAPTER PARA ABRIR CON LOADBUSTER FUE TRABAJADO CON LA ORDEN 6010 15% 1336-08 | S23060400457 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-04 | 936 | keep | 0 | Jun | 2023 | 0.00063751 | 0.00063751 | Momentary | FALSE | FALSE | Not_TMED_Event | 936
SAN JUAN | 2023-06-04 17:51 | 2023-06-04 17:52 | 4232 | 0:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE DISPARO POR SEGURIDAD LA CAJA PRIMARIA NO TENIA EL ADAPTER PARA ABRIR CON LOADBUSTER FUE TRABAJADO CON LA ORDEN 6010 LLEVA 15% 1336-10 90% POR 1424-08 | S23060400457 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-06-04 | 4232 | keep | 0 | Jun | 2023 | 0.0028824 | 0.0028824 | Momentary | FALSE | FALSE | Not_TMED_Event | 4232
MAYAGÃœEZ | 2023-06-04 17:58 | 2023-06-05 10:25 | 15 | 16:27 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 10 EN TRANSFORMADOR LINEA SECUNDARIA CRUZADA | M23060400451 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 987 | 2023-06-04 | 14805 | keep | 0 | Jun | 2023 | 0.010084 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-06-04 18:03 | 2023-06-04 19:30 | 15 | 1:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23060400323 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 87 | 2023-06-04 | 1305 | keep | 0 | Jun | 2023 | 0.00088883 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-06-04 18:14 | 2023-06-05 11:54 | 11 | 17:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 75 X 75 KVA | R23060400083 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1060 | 2023-06-04 | 11660 | keep | 0 | Jun | 2023 | 0.0079416 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2023-06-04 18:29 | 2023-06-04 18:47 | 23 | 0:18 | P | DESGANCHE | 2 X 30 EN C/L DESGANCHE | B23060400316 | New_Event | Vegetation Contact | Include | Include | Vegetation | 18 | 2023-06-04 | 414 | keep | 0 | Jun | 2023 | 0.00028197 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BAYAMON | 2023-06-04 18:35 | 2023-06-05 11:18 | 43 | 16:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L Y 1 X 15 EN XMR SE REEMPLAZO PORTAFUSIBLE | B23060400322 | New_Event | Cutout Failure | Include | Include | Equipment | 1003 | 2023-06-04 | 43129 | keep | 0 | Jun | 2023 | 0.029375 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
BAYAMON | 2023-06-04 18:40 | 2023-06-05 12:27 | 33 | 17:47 | T | CONDUCTOR ROTO O ABIERTO | SE ENCONTRO BKR ABIERTO EN LA SUBESTACION SE CERRO BKR EN EL CAMPO. NO TINE RTU LA SUBESTACION. SE UTILIZO HORA DEL EVENTO PARA LA INTERRUPCION. | B23060400328 | New_Event | Primary Wire Break | Include | Include | Equipment | 1067 | 2023-06-04 | 35211 | keep | 0 | Jun | 2023 | 0.023982 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
BAYAMON | 2023-06-04 18:40 | 2023-06-04 19:50 | 31 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23060400325 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2023-06-04 | 2170 | keep | 0 | Jun | 2023 | 0.001478 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
SAN JUAN | 2023-06-04 18:42 | 2023-06-05 13:01 | 40 | 18:19 | P | NO SE REPORTO CAUSA | 1X80 EN C/L | S23060400616 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1099 | 2023-06-04 | 43960 | keep | 0 | Jun | 2023 | 0.029941 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2023-06-04 18:50 | 2023-06-05 11:45 | 6 | 16:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO PORTAFUSIBLE QUEMADO 1 X 15 EN TRANSFORMADOR | P23060400619 | New_Event | Cutout Failure | Include | Include | Equipment | 1015 | 2023-06-04 | 6090 | keep | 0 | Jun | 2023 | 0.0041479 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-06-04 18:51 | 2023-06-04 20:23 | 37 | 1:32 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B23060400334 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 92 | 2023-06-04 | 3404 | keep | 0 | Jun | 2023 | 0.0023184 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
SAN JUAN | 2023-06-04 18:54 | 2023-06-05 13:39 | 80 | 18:45 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | S23060400623 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1125 | 2023-06-04 | 90000 | keep | 0 | Jun | 2023 | 0.061299 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2023-06-04 18:58 | 2023-06-05 07:20 | 20 | 12:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA Y SE ELIMINO CRUCETA DE TRANSFORMADOR | P23060400625 | New_Event | Cutout Failure | Include | Include | Equipment | 742 | 2023-06-04 | 14840 | keep | 0 | Jun | 2023 | 0.010107 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-06-04 18:59 | 2023-06-04 21:07 | 45 | 2:08 | P | DESGANCHE | 1X65 EN C/L Y DESGANCHE | S23060400627 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2023-06-04 | 5760 | keep | 0 | Jun | 2023 | 0.0039231 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-06-04 19:05 | 2023-06-04 21:18 | 496 | 2:13 | P | SOBRECARGA | 1 X 80 EN C/L POR CARGA | B23060400349 | New_Event | Trip Due To Overload | Include | Include | Other | 133 | 2023-06-04 | 65968 | keep | 0 | Jun | 2023 | 0.044931 | 0.00033782 | Sustained | FALSE | FALSE | Not_TMED_Event | 496
BAYAMON | 2023-06-04 19:06 | 2023-06-05 04:31 | 169 | 9:25 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23060400636 | New_Event | Vegetation Contact | Include | Include | Vegetation | 565 | 2023-06-04 | 95485 | keep | 0 | Jun | 2023 | 0.065034 | 0.00011511 | Sustained | FALSE | FALSE | Not_TMED_Event | 169
AGUADILLA | 2023-06-04 19:23 | 2023-06-05 11:52 | 150 | 16:29 | P | CONDUCTOR ROTO O ABIERTO | PUENTE PRIMARIO ABIERTO EN EL TRONCAL DEL ALIMENTADOR | M23060400476 | New_Event | Primary Wire Break | Include | Include | Equipment | 989 | 2023-06-04 | 148350 | keep | 0 | Jun | 2023 | 0.10104 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2023-06-04 19:30 | 2023-06-04 21:40 | 100 | 2:10 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23060400356 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2023-06-04 | 13000 | keep | 0 | Jun | 2023 | 0.0088542 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-06-04 19:39 | 2023-06-04 21:00 | 150 | 1:21 | P | SOBRECARGA | 1 X 100 EN CL SOBRECARGA | M23060400486 | New_Event | Trip Due To Overload | Include | Include | Other | 81 | 2023-06-04 | 12150 | keep | 0 | Jun | 2023 | 0.0082753 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-06-04 19:41 | 2023-06-04 22:49 | 25 | 3:08 | P | DESGANCHE | 1 X 30 EN C/L SE DESGANCHO | R23060400104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2023-06-04 | 4700 | keep | 0 | Jun | 2023 | 0.0032011 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-06-04 20:08 | 2023-06-04 22:24 | 10 | 2:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23060400668 | New_Event | Secondary Wire Break | Include | Include | Equipment | 136 | 2023-06-04 | 1360 | keep | 0 | Jun | 2023 | 0.00092629 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-06-04 20:10 | 2023-06-04 20:11 | 686 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2306040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 686 | keep | 0 | Jun | 2023 | 0.00046723 | 0.00046723 | Momentary | FALSE | FALSE | Not_TMED_Event | 686
SAN JUAN | 2023-06-04 20:19 | 2023-06-04 20:33 | 4944 | 0:14 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL | S2306040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 14 | 2023-06-04 | 69216 | keep | 0 | Jun | 2023 | 0.047143 | 0.0033673 | Sustained | FALSE | FALSE | Not_TMED_Event | 4944
SAN JUAN | 2023-06-04 20:28 | 2023-06-05 09:43 | 60 | 13:15 | P | NO SE REPORTO CAUSA | 1X25 EN C/L | S23060400068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 795 | 2023-06-04 | 47700 | keep | 0 | Jun | 2023 | 0.032488 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-06-04 20:31 | 2023-06-05 01:14 | 40 | 4:43 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23060400387 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 283 | 2023-06-04 | 11320 | keep | 0 | Jun | 2023 | 0.00771 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-06-04 20:36 | 2023-06-05 09:03 | 50 | 12:27 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO SE ENCONTRO CAUSA | A23060400390 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 747 | 2023-06-04 | 37350 | keep | 0 | Jun | 2023 | 0.025439 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-06-04 20:36 | 2023-06-05 02:02 | 8 | 5:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR POR PORTAFUSIBLE | A23060400391 | New_Event | Cutout Failure | Include | Include | Equipment | 326 | 2023-06-04 | 2608 | keep | 0 | Jun | 2023 | 0.0017763 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2023-06-04 20:41 | 2023-06-05 09:18 | 2 | 12:37 | P | DESGANCHE | 1 X 40 EN CL DESGANCHE | A23060400395 | New_Event | Vegetation Contact | Include | Include | Vegetation | 757 | 2023-06-04 | 1514 | keep | 0 | Jun | 2023 | 0.0010312 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2023-06-04 20:44 | 2023-06-04 21:50 | 120 | 1:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23060400398 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 66 | 2023-06-04 | 7920 | keep | 0 | Jun | 2023 | 0.0053943 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2023-06-04 20:50 | 2023-06-05 10:20 | 100 | 13:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23060400513 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 810 | 2023-06-04 | 81000 | keep | 0 | Jun | 2023 | 0.055169 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-06-04 20:56 | 2023-06-05 00:20 | 200 | 3:24 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA TOTAL Y SE CERRO PUENTE PRIMARIO RADIAL | C23060400507 | New_Event | Primary Wire Break | Include | Include | Equipment | 204 | 2023-06-04 | 40800 | keep | 0 | Jun | 2023 | 0.027789 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2023-06-04 21:07 | 2023-06-04 22:22 | 125 | 1:15 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23060400457 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 75 | 2023-06-04 | 9375 | keep | 0 | Jun | 2023 | 0.0063853 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2023-06-04 21:11 | 2023-06-04 21:45 | 4944 | 0:34 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL | S23060400704 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 34 | 2023-06-04 | 168096 | keep | 0 | Jun | 2023 | 0.11449 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-06-04 21:39 | 2023-06-04 23:10 | 60 | 1:31 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | A23060400457 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2023-06-04 | 5460 | keep | 0 | Jun | 2023 | 0.0037188 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2023-06-04 21:54 | 2023-06-05 13:53 | 30 | 15:59 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN CL SE FIJO BAJANTE DE LINEA A CAJA DE TRANSFORMADOR | A23060400470 | New_Event | Primary Wire Break | Include | Include | Equipment | 959 | 2023-06-04 | 28770 | keep | 0 | Jun | 2023 | 0.019595 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-06-04 21:57 | 2023-06-05 01:43 | 350 | 3:46 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | M23060400567 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2023-06-04 | 79100 | keep | 0 | Jun | 2023 | 0.053875 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
SAN JUAN | 2023-06-04 21:59 | 2023-06-05 05:18 | 371 | 7:19 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23060400770 | New_Event | Vegetation Contact | Include | Include | Vegetation | 439 | 2023-06-04 | 162869 | keep | 0 | Jun | 2023 | 0.11093 | 0.00025269 | Sustained | FALSE | FALSE | Not_TMED_Event | 371
AGUADILLA | 2023-06-04 21:59 | 2023-06-04 23:14 | 400 | 1:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE CAMBIO MASETILLA | M23060400569 | New_Event | Cutout Failure | Include | Include | Equipment | 75 | 2023-06-04 | 30000 | keep | 0 | Jun | 2023 | 0.020433 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
VEGA BAJA | 2023-06-04 22:00 | 2023-06-04 23:07 | 150 | 1:07 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | A23060400476 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2023-06-04 | 10050 | keep | 0 | Jun | 2023 | 0.006845 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-06-04 22:06 | 2023-06-05 19:41 | 49 | 21:35 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN C/L SE LEVANTO CONDUCTOR PRIMARIO | B23060400476 | New_Event | Primary Wire Break | Include | Include | Equipment | 1295 | 2023-06-04 | 63455 | keep | 0 | Jun | 2023 | 0.043219 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
GUAYAMA | 2023-06-04 22:18 | 2023-06-05 15:38 | 8 | 17:20 | P | NO SE REPORTO CAUSA | SE CERRO FUSIBLE Y TODO EN SERVICIO NO SE ENCONTRO NADA | P23060400783 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1040 | 2023-06-04 | 8320 | keep | 0 | Jun | 2023 | 0.0056667 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-06-04 22:21 | 2023-06-05 13:04 | 40 | 14:43 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23060400484 | New_Event | Vegetation Contact | Include | Include | Vegetation | 883 | 2023-06-04 | 35320 | keep | 0 | Jun | 2023 | 0.024056 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-06-04 22:28 | 2023-06-05 02:00 | 25 | 3:32 | P | DESGANCHE | 3 X 50 EN CL DESGANCHE | B23060400487 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2023-06-04 | 5300 | keep | 0 | Jun | 2023 | 0.0036098 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-06-04 22:34 | 2023-06-04 22:39 | 4944 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S23060400788 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-06-04 | 24720 | keep | 0 | Jun | 2023 | 0.016837 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-04 22:41 | 2023-06-04 22:42 | 3871 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B23060400491 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-04 | 3871 | keep | 0 | Jun | 2023 | 0.0026365 | 0.0026365 | Momentary | FALSE | FALSE | Not_TMED_Event | 3871
SAN JUAN | 2023-06-04 22:43 | 2023-06-05 14:50 | 10 | 16:07 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR Y SE REPARO BUSHING SECUNDARIO | S23060400795 | New_Event | Service Transformer Failure | Include | Include | Equipment | 967 | 2023-06-04 | 9670 | keep | 0 | Jun | 2023 | 0.0065862 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-06-04 22:48 | 2023-06-05 10:43 | 80 | 11:55 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE | A23060400501 | New_Event | Vegetation Contact | Include | Include | Vegetation | 715 | 2023-06-04 | 57200 | keep | 0 | Jun | 2023 | 0.038959 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-06-04 22:54 | 2023-06-05 00:47 | 106 | 1:53 | P | NO SE REPORTO CAUSA | 1 X 65 EN C.L NO CAUSA | B23060400495 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 113 | 2023-06-04 | 11978 | keep | 0 | Jun | 2023 | 0.0081582 | 7.2196e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 106
CANOVANAS | 2023-06-04 22:55 | 2023-06-04 22:56 | 7621 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR | R23060400153 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-06-04 | 7621 | keep | 0 | Jun | 2023 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
CANOVANAS | 2023-06-04 23:09 | 2023-06-04 23:10 | 7621 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO | R2306040000X | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 1 | 2023-06-04 | 7621 | keep | 0 | Jun | 2023 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
CANOVANAS | 2023-06-04 23:10 | 2023-06-04 23:28 | 500 | 0:18 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETE Y REPARO PUENTE DE MACHETE A LINEA | R23060400155 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 18 | 2023-06-04 | 9000 | keep | 0 | Jun | 2023 | 0.0061299 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
FAJARDO | 2023-06-04 23:16 | 2023-06-05 09:05 | 15 | 9:49 | P | CAUSAS EXTERNAS | 1 X 65 EN C/L VEHICULO IMPACTO POSTE | R23060400156 | New_Event | Damage From Public | Include | Include | Public | 589 | 2023-06-04 | 8835 | keep | 0 | Jun | 2023 | 0.0060175 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-06-04 23:24 | 2023-06-05 09:15 | 200 | 9:51 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE RETIRO BAMBU DE LAS LINEAS | M23060400604 | New_Event | Vegetation Contact | Include | Include | Vegetation | 591 | 2023-06-04 | 118200 | keep | 0 | Jun | 2023 | 0.080505 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2023-06-04 23:27 | 2023-06-05 09:45 | 100 | 10:18 | P | NO SE REPORTO CAUSA | 1 X 100 EN CL NO SE ENCONTRO CAUSA | A23060400508 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 618 | 2023-06-04 | 61800 | keep | 0 | Jun | 2023 | 0.042092 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-06-04 23:28 | 2023-06-04 23:29 | 7621 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO | R2306040000X | Additional_clients | Primary Wire Break | Include | Include | Equipment | 1 | 2023-06-04 | 7621 | keep | 0 | Jun | 2023 | 0.0051906 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-06-04 23:29 | 2023-06-05 03:14 | 500 | 3:45 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETE Y REPARO PUENTE DE MACHETE A LINEA | R23060400155 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 225 | 2023-06-04 | 112500 | keep | 0 | Jun | 2023 | 0.076623 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CAGUAS | 2023-06-05 00:04 | 2023-06-05 03:22 | 580 | 3:18 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | C23060500002 | New_Event | Animals | Include | Include | Wildlife | 198 | 2023-06-05 | 114840 | keep | 0 | Jun | 2023 | 0.078217 | 0.00039504 | Sustained | FALSE | FALSE | Not_TMED_Event | 580
SAN JUAN | 2023-06-05 00:09 | 2023-06-05 12:12 | 37 | 12:03 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | S23060500002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 723 | 2023-06-05 | 26751 | keep | 0 | Jun | 2023 | 0.01822 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
VEGA BAJA | 2023-06-05 00:14 | 2023-06-05 06:46 | 20 | 6:32 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | B23060500005 | New_Event | Animals | Include | Include | Wildlife | 392 | 2023-06-05 | 7840 | keep | 0 | Jun | 2023 | 0.0053398 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-06-05 00:19 | 2023-06-05 13:26 | 100 | 13:07 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA | M23060500004 | New_Event | Primary Wire Break | Include | Include | Equipment | 787 | 2023-06-05 | 78700 | keep | 0 | Jun | 2023 | 0.053602 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2023-06-05 00:42 | 2023-06-05 03:53 | 449 | 3:11 | T | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZA AVERIA ABRIENDO MACHETE FID 1001124473 | P23060500013 | New_Event | Primary Wire Break | Include | Include | Equipment | 191 | 2023-06-05 | 85759 | keep | 0 | Jun | 2023 | 0.05841 | 0.00030581 | Sustained | FALSE | FALSE | Not_TMED_Event | 449
BAYAMON | 2023-06-05 00:47 | 2023-06-05 00:50 | 3871 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B23060500022 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-06-05 | 11613 | keep | 0 | Jun | 2023 | 0.0079096 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-05 00:52 | 2023-06-05 02:58 | 28 | 2:06 | P | ANIMAL | 1 X 30 EN C/L CRUCE POR AVE | B23060500017 | New_Event | Animals | Include | Include | Wildlife | 126 | 2023-06-05 | 3528 | keep | 0 | Jun | 2023 | 0.0024029 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
VEGA BAJA | 2023-06-05 01:18 | 2023-06-05 02:58 | 180 | 1:40 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA POR AISLADOR PARTIDO | A23060500008 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 100 | 2023-06-05 | 18000 | keep | 0 | Jun | 2023 | 0.01226 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
VEGA BAJA | 2023-06-05 01:41 | 2023-06-05 07:54 | 50 | 6:13 | P | DESGANCHE | 1 X 30 EN CL DESGANCHE | A23060500009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 373 | 2023-06-05 | 18650 | keep | 0 | Jun | 2023 | 0.012702 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-06-05 01:43 | 2023-06-05 10:15 | 83 | 8:32 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO ABIERTO | M23060400567 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 512 | 2023-06-05 | 42496 | keep | 0 | Jun | 2023 | 0.028944 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-06-05 01:47 | 2023-06-05 11:00 | 140 | 9:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 140 EN SALIDA DE CONVERTIDOR FUERTE VIENTO | A23060500011 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 553 | 2023-06-05 | 77420 | keep | 0 | Jun | 2023 | 0.05273 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
HUMACAO | 2023-06-05 01:59 | 2023-06-05 05:09 | 640 | 3:10 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO DE INTERRUPTOR SE SECCIONALIZO BREAKER EN SUBESTACION SE REPARO ESCOBILLAS DEL MOTOR DEL BREAKER Y SE CARGO SPRING SE CERRO POR CONTROL 100% EN SERVICIO SE TRABAJO CON CG-230605-01 | C23060500023 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 190 | 2023-06-05 | 121600 | keep | 0 | Jun | 2023 | 0.082821 | 0.0004359 | Sustained | FALSE | FALSE | Not_TMED_Event | 640
BAYAMON | 2023-06-05 02:14 | 2023-06-05 02:15 | 5809 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B2306050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-05 | 5809 | keep | 0 | Jun | 2023 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
AGUADILLA | 2023-06-05 02:37 | 2023-06-05 13:30 | 80 | 10:53 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE | A23060500013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 653 | 2023-06-05 | 52240 | keep | 0 | Jun | 2023 | 0.03558 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-06-05 03:32 | 2023-06-05 03:33 | 320 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B2306050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-05 | 320 | keep | 0 | Jun | 2023 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
GUAYAMA | 2023-06-05 03:53 | 2023-06-05 13:24 | 6 | 9:31 | P | SOBRECARGA | 1 X 15 EN TRANSFORMADOR POR CARGA | P23060500061 | New_Event | Trip Due To Overload | Include | Include | Other | 571 | 2023-06-05 | 3426 | keep | 0 | Jun | 2023 | 0.0023334 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2023-06-05 03:53 | 2023-06-05 09:30 | 65 | 5:37 | P | CONDUCTOR ROTO O ABIERTO | SE CIERRA MACHETE FID 1001124473 Y SE ABRE MACHTE FID 1000052155 PARA REPARAR MACHETE | P23060500062 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 337 | 2023-06-05 | 21905 | keep | 0 | Jun | 2023 | 0.014919 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-05 05:18 | 2023-06-05 14:19 | 56 | 9:01 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | S23060500033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 541 | 2023-06-05 | 30296 | keep | 0 | Jun | 2023 | 0.020634 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
MAYAGÃœEZ | 2023-06-05 05:21 | 2023-06-05 11:40 | 200 | 6:19 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA DE CORTE DE LINEA | M23060500040 | New_Event | Primary Wire Break | Include | Include | Equipment | 379 | 2023-06-05 | 75800 | keep | 0 | Jun | 2023 | 0.051627 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2023-06-05 05:36 | 2023-06-05 09:50 | 100 | 4:14 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M23060500045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 254 | 2023-06-05 | 25400 | keep | 0 | Jun | 2023 | 0.0173 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-06-05 05:49 | 2023-06-05 05:50 | 3012 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23060500107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-05 | 3012 | keep | 0 | Jun | 2023 | 0.0020515 | 0.0020515 | Momentary | FALSE | FALSE | Not_TMED_Event | 3012
AGUADILLA | 2023-06-05 05:50 | 2023-06-05 10:40 | 250 | 4:50 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE REQUIERE DESGANCHE | M23060500054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 290 | 2023-06-05 | 72500 | keep | 0 | Jun | 2023 | 0.049379 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
HUMACAO | 2023-06-05 06:05 | 2023-06-05 08:14 | 736 | 2:09 | P | ANIMAL | 1 X 200 EN LA SALIDA DEL CONVERTIDOR CRUCE POR AVE | C23060500050 | New_Event | Animals | Include | Include | Wildlife | 129 | 2023-06-05 | 94944 | keep | 0 | Jun | 2023 | 0.064666 | 0.00050129 | Sustained | FALSE | FALSE | Not_TMED_Event | 736
BARRANQUITAS | 2023-06-05 06:06 | 2023-06-05 09:18 | 1 | 3:12 | P | DESGANCHE | 3 X 20 EN BANCO DE TRANSFORMADORES SE RETIRO BAMBUA DE LA LINEA EVENTRO TRANSFERIDO | P23060500081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2023-06-05 | 192 | keep | 0 | Jun | 2023 | 0.00013077 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-06-05 06:12 | 2023-06-05 11:33 | 50 | 5:21 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23060500036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 321 | 2023-06-05 | 16050 | keep | 0 | Jun | 2023 | 0.010932 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-06-05 06:15 | 2023-06-05 09:20 | 90 | 3:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23060500060 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 185 | 2023-06-05 | 16650 | keep | 0 | Jun | 2023 | 0.01134 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2023-06-05 06:20 | 2023-06-05 10:00 | 30 | 3:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23060400477 | New_Event | Secondary Wire Break | Include | Include | Equipment | 220 | 2023-06-05 | 6600 | keep | 0 | Jun | 2023 | 0.0044952 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-06-05 06:31 | 2023-06-05 11:36 | 74 | 5:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X100 EN C/L POR VIENTO | S23060500040 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 305 | 2023-06-05 | 22570 | keep | 0 | Jun | 2023 | 0.015372 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
HUMACAO | 2023-06-05 06:33 | 2023-06-05 09:11 | 11 | 2:38 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | C23060500057 | New_Event | Animals | Include | Include | Wildlife | 158 | 2023-06-05 | 1738 | keep | 0 | Jun | 2023 | 0.0011837 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2023-06-05 06:34 | 2023-06-05 12:19 | 30 | 5:45 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO | C23060500058 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 345 | 2023-06-05 | 10350 | keep | 0 | Jun | 2023 | 0.0070493 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-06-05 06:37 | 2023-06-05 10:47 | 10 | 4:10 | P | ANIMAL | 1 X 25 EN TRANSFORMADOR CRUCE POR AVE | A23060500041 | New_Event | Animals | Include | Include | Wildlife | 250 | 2023-06-05 | 2500 | keep | 0 | Jun | 2023 | 0.0017027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-06-05 06:42 | 2023-06-05 19:31 | 7 | 12:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | B23060500047 | New_Event | Cutout Failure | Include | Include | Equipment | 769 | 2023-06-05 | 5383 | keep | 0 | Jun | 2023 | 0.0036663 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-06-05 06:45 | 2023-06-05 10:10 | 100 | 3:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | P23060500099 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 205 | 2023-06-05 | 20500 | keep | 0 | Jun | 2023 | 0.013962 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-06-05 06:51 | 2023-06-05 15:00 | 18 | 8:09 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA Y 2 X 50 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A23060500043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 489 | 2023-06-05 | 8802 | keep | 0 | Jun | 2023 | 0.005995 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
ARECIBO | 2023-06-05 06:55 | 2023-06-05 11:14 | 180 | 4:19 | P | DESGANCHE | 1 X 80 EN CL DESGANCHE SE ABRIO PUENTES PPRIMARIOS | A23060500046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2023-06-05 | 46620 | keep | 0 | Jun | 2023 | 0.031753 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
BAYAMON | 2023-06-05 06:57 | 2023-06-05 12:30 | 227 | 5:33 | P | DESGANCHE | 1 X 40 Y 1 X80 EN C/L DESGANCHE | B23060500053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 333 | 2023-06-05 | 75591 | keep | 0 | Jun | 2023 | 0.051485 | 0.00015461 | Sustained | FALSE | FALSE | Not_TMED_Event | 227
MAYAGÃœEZ | 2023-06-05 07:00 | 2023-06-05 10:08 | 35 | 3:08 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | M23060500075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2023-06-05 | 6580 | keep | 0 | Jun | 2023 | 0.0044816 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2023-06-05 07:04 | 2023-06-05 10:16 | 35 | 3:12 | P | NO SE REPORTO CAUSA | 1 X 40 EN CL NO SE ENCONTRO CAUSA | A23060500047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 192 | 2023-06-05 | 6720 | keep | 0 | Jun | 2023 | 0.004577 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2023-06-05 07:07 | 2023-06-05 12:17 | 22 | 5:10 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1X65 EN C/L SE REMPLAZO AISLADOR PARTIDO | B23060500055 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 310 | 2023-06-05 | 6820 | keep | 0 | Jun | 2023 | 0.0046451 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
MAYAGÃœEZ | 2023-06-05 07:11 | 2023-06-05 19:05 | 150 | 11:54 | P | DESGANCHE | SE REPARO NEUTRAL PRIMARIO PARTIDO, SE REALIZO DESGANCHE Y SE CERRO CORTE DE LINEA | M23060500082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 714 | 2023-06-05 | 107100 | keep | 0 | Jun | 2023 | 0.072945 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
FAJARDO | 2023-06-05 07:12 | 2023-06-05 14:49 | 17 | 7:37 | P | DESGANCHE | 1 X 25 EN C/L EVENTO TRANSFERIDO DE PONCE | P23060500110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 457 | 2023-06-05 | 7769 | keep | 0 | Jun | 2023 | 0.0052914 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
MAYAGÃœEZ | 2023-06-05 07:17 | 2023-06-05 15:40 | 4 | 8:23 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REQUIERE DESGANCHE | P23060500112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 503 | 2023-06-05 | 2012 | keep | 0 | Jun | 2023 | 0.0013704 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
FAJARDO | 2023-06-05 07:21 | 2023-06-05 13:20 | 20 | 5:59 | P | ANIMAL | 1 X 50EN C/L 1X 25 EN C/L CRUCE POR AVE | R23060500112 | New_Event | Animals | Include | Include | Wildlife | 359 | 2023-06-05 | 7180 | keep | 0 | Jun | 2023 | 0.0048903 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-06-05 07:22 | 2023-06-05 18:32 | 60 | 11:10 | P | CABLE SOTERRADO AVERIADO | AVERIA NUEVA DEL T-9 A RISER Y AVERIA VIEJA T-11 A RISER CABLE SOTERRADO AVERIADO SE CONSTRUYO PROVISIONAL AERIO SE TRABAJO CON GOI SJ-230605-02 | S23060500053 | New_Event | UG Cable Fault | Include | Include | Equipment | 670 | 2023-06-05 | 40200 | keep | 0 | Jun | 2023 | 0.02738 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-06-05 07:22 | 2023-06-05 11:43 | 12 | 4:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23060500052 | New_Event | Secondary Wire Break | Include | Include | Equipment | 261 | 2023-06-05 | 3132 | keep | 0 | Jun | 2023 | 0.0021332 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-06-05 07:23 | 2023-06-05 09:21 | 100 | 1:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X80 EN C/L POR VIENTO | B23060500061 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 118 | 2023-06-05 | 11800 | keep | 0 | Jun | 2023 | 0.0080369 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-06-05 07:23 | 2023-06-05 16:30 | 40 | 9:07 | P | DESGANCHE | 1 X 40 Y 1 X 30 EN CORTES DE LINEA SE REALIZO DESGANCHE EVENTO TRANSFERIDO DE PONCE | P23060500115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 547 | 2023-06-05 | 21880 | keep | 0 | Jun | 2023 | 0.014902 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-06-05 07:25 | 2023-06-05 11:58 | 1 | 4:33 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR EVENTO TRANSFERIDO DE PONCE 1 X 20 C/L | P23060500119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 273 | 2023-06-05 | 273 | keep | 0 | Jun | 2023 | 0.00018594 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-06-05 07:29 | 2023-06-05 11:22 | 25 | 3:53 | P | ANIMAL | 1 X 100 EN C/ 1 X 80 EN C/L CRUCE POR AVE | R23060500113 | New_Event | Animals | Include | Include | Wildlife | 233 | 2023-06-05 | 5825 | keep | 0 | Jun | 2023 | 0.0039674 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-06-05 07:29 | 2023-06-05 13:20 | 1 | 5:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA AVERIADA EN CORTE DE LINEA | P23060500122 | New_Event | Cutout Failure | Include | Include | Equipment | 351 | 2023-06-05 | 351 | keep | 0 | Jun | 2023 | 0.00023906 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-06-05 07:41 | 2023-06-05 12:46 | 1 | 5:05 | P | DESGANCHE | 2 X 65 EN RISER SE RETIRO PENCAS DE LA LINEA | C23060500072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 305 | 2023-06-05 | 305 | keep | 0 | Jun | 2023 | 0.00020773 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-06-05 07:41 | 2023-06-05 10:49 | 14 | 3:08 | P | MAL TIEMPO/LLUVIA O VIENTO | SE RESETEO TRANSFORMADOR FUERTE VIENTO | B23060500073 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 188 | 2023-06-05 | 2632 | keep | 0 | Jun | 2023 | 0.0017926 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2023-06-05 07:47 | 2023-06-05 13:16 | 117 | 5:29 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA @ CAJA EN C/L NO FUNDIO | S23060500005 | New_Event | Primary Wire Break | Include | Include | Equipment | 329 | 2023-06-05 | 38493 | keep | 0 | Jun | 2023 | 0.026217 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
UTUADO | 2023-06-05 07:51 | 2023-06-05 12:26 | 30 | 4:35 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CL FUERTE VIENTO | A23060500063 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 275 | 2023-06-05 | 8250 | keep | 0 | Jun | 2023 | 0.005619 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-06-05 07:52 | 2023-06-05 15:55 | 5 | 8:03 | P | DESGANCHE | 1 X 15 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23060500113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 483 | 2023-06-05 | 2415 | keep | 0 | Jun | 2023 | 0.0016448 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2023-06-05 08:04 | 2023-06-05 13:42 | 13 | 5:38 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO PENCA DE LA LINEA | C23060500088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 338 | 2023-06-05 | 4394 | keep | 0 | Jun | 2023 | 0.0029927 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
ARECIBO | 2023-06-05 08:12 | 2023-06-05 10:00 | 1 | 1:48 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE | P23060500169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2023-06-05 | 108 | keep | 0 | Jun | 2023 | 7.3558e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-06-05 08:14 | 2023-06-05 13:20 | 14 | 5:06 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | C23060500114 | New_Event | Animals | Include | Include | Wildlife | 306 | 2023-06-05 | 4284 | keep | 0 | Jun | 2023 | 0.0029178 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CAGUAS | 2023-06-05 08:16 | 2023-06-05 16:45 | 14 | 8:29 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE SECUNDARIO | C23060500095 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 509 | 2023-06-05 | 7126 | keep | 0 | Jun | 2023 | 0.0048535 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BARRANQUITAS | 2023-06-05 08:19 | 2023-06-05 15:27 | 195 | 7:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTO | C23060500097 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 428 | 2023-06-05 | 83460 | keep | 0 | Jun | 2023 | 0.056844 | 0.00013281 | Sustained | FALSE | FALSE | Not_TMED_Event | 195
YAUCO | 2023-06-05 08:20 | 2023-06-05 09:49 | 80 | 1:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN DIFERENTES CORTES DE LINEA POR MAL TIEMPO | P23060500174 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 89 | 2023-06-05 | 7120 | keep | 0 | Jun | 2023 | 0.0048494 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-06-05 08:21 | 2023-06-05 16:56 | 6 | 8:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C23060500101 | New_Event | Cutout Failure | Include | Include | Equipment | 515 | 2023-06-05 | 3090 | keep | 0 | Jun | 2023 | 0.0021046 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-06-05 08:22 | 2023-06-05 15:33 | 40 | 7:11 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23060500073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 431 | 2023-06-05 | 17240 | keep | 0 | Jun | 2023 | 0.011742 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-06-05 08:22 | 2023-06-05 13:18 | 17 | 4:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C23060500052 | New_Event | Secondary Wire Break | Include | Include | Equipment | 296 | 2023-06-05 | 5032 | keep | 0 | Jun | 2023 | 0.0034273 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BARRANQUITAS | 2023-06-05 08:29 | 2023-06-05 16:00 | 12 | 7:31 | P | CAUSAS EXTERNAS | 1 X 30 EN CORTE DE LINEA SE RECORTO POSTE DE TELEFONO EN CONTACTO CON LA LINEA | C23060500107 | New_Event | Damage From Public | Include | Include | Public | 451 | 2023-06-05 | 5412 | keep | 0 | Jun | 2023 | 0.0036861 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2023-06-05 08:32 | 2023-06-05 10:35 | 4 | 2:03 | P | PROBLEMA DEL CLIENTE | SE ABRE EN MH-15 HACIA BARRAS SECAS PARA DESCONECTAR SERVICIO PARA TRABAJOS DE MANTENIMIENTO | P23060500224 | New_Event | Customer-Related Interruption | Include | Include | Public | 123 | 2023-06-05 | 492 | keep | 0 | Jun | 2023 | 0.0003351 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-06-05 08:36 | 2023-06-05 13:19 | 40 | 4:43 | P | DESGANCHE | 1X80 EN C/L DESGANCHE | S23060500078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2023-06-05 | 11320 | keep | 0 | Jun | 2023 | 0.00771 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-06-05 08:38 | 2023-06-05 13:47 | 1 | 5:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | R23060500131 | New_Event | Secondary Wire Break | Include | Include | Equipment | 309 | 2023-06-05 | 309 | keep | 0 | Jun | 2023 | 0.00021046 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-06-05 08:38 | 2023-06-05 15:45 | 8 | 7:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFROMADOR MA TIEMPO | P23060500197 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 427 | 2023-06-05 | 3416 | keep | 0 | Jun | 2023 | 0.0023266 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-06-05 08:39 | 2023-06-05 15:57 | 20 | 7:18 | P | NO SE REPORTO CAUSA | 2 X 30 EN RISER EVENTO TRANSFERIDO DE PONCE | P23060500199 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 438 | 2023-06-05 | 8760 | keep | 0 | Jun | 2023 | 0.0059664 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-06-05 08:39 | 2023-06-05 13:15 | 4 | 4:36 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR SE REPARO LINEAS SECUNDARIAS CRUZADAS | M23060500140 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 276 | 2023-06-05 | 1104 | keep | 0 | Jun | 2023 | 0.00075193 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-06-05 08:45 | 2023-06-05 10:25 | 40 | 1:40 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO EVENTO TRANSFERIDO | P23060500204 | New_Event | Primary Wire Break | Include | Include | Equipment | 100 | 2023-06-05 | 4000 | keep | 0 | Jun | 2023 | 0.0027244 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-06-05 08:59 | 2023-06-05 15:20 | 1 | 6:21 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER NO SE ENCONTRO CAUSA | M23060500153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 381 | 2023-06-05 | 381 | keep | 0 | Jun | 2023 | 0.0002595 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-06-05 09:00 | 2023-06-05 15:36 | 1 | 6:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | B23060500091 | New_Event | Cutout Failure | Include | Include | Equipment | 396 | 2023-06-05 | 396 | keep | 0 | Jun | 2023 | 0.00026971 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-06-05 09:01 | 2023-06-05 09:08 | 1225 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 EN PATRULLAJE AÃ‰REO EL 6/7/2023 SOLO SE REPORTAN DESGANCHES PREVENTIVOS PREFERENCIALES (PRIORITY). | S23060500099 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-06-05 | 8575 | keep | 0 | Jun | 2023 | 0.0058404 | 0.00083434 | Sustained | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2023-06-05 09:01 | 2023-06-05 09:08 | 1452 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 EN PATRULLAJE AÃ‰REO EL 6/7/2023 SOLO SE REPORTAN DESGANCHES PREVENTIVOS PREFERENCIALES (PRIORITY). | S23060500099 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-06-05 | 10164 | keep | 0 | Jun | 2023 | 0.0069227 | 0.00098895 | Sustained | FALSE | FALSE | Not_TMED_Event | 1452
SAN JUAN | 2023-06-05 09:01 | 2023-06-05 09:08 | 616 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 EN PATRULLAJE AÃ‰REO EL 6/7/2023 SOLO SE REPORTAN DESGANCHES PREVENTIVOS PREFERENCIALES (PRIORITY). | S23060500099 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-06-05 | 4312 | keep | 0 | Jun | 2023 | 0.0029369 | 0.00041955 | Sustained | FALSE | FALSE | Not_TMED_Event | 616
SAN JUAN | 2023-06-05 09:01 | 2023-06-05 09:08 | 660 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 EN PATRULLAJE AÃ‰REO EL 6/7/2023 SOLO SE REPORTAN DESGANCHES PREVENTIVOS PREFERENCIALES (PRIORITY). | S23060500100 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-06-05 | 4620 | keep | 0 | Jun | 2023 | 0.0031467 | 0.00044952 | Sustained | FALSE | FALSE | Not_TMED_Event | 660
SAN JUAN | 2023-06-05 09:01 | 2023-06-05 09:08 | 435 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 EN PATRULLAJE AÃ‰REO EL 6/7/2023 SOLO SE REPORTAN DESGANCHES PREVENTIVOS PREFERENCIALES (PRIORITY). | S23060500100 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-06-05 | 3045 | keep | 0 | Jun | 2023 | 0.0020739 | 0.00029628 | Sustained | FALSE | FALSE | Not_TMED_Event | 435
SAN JUAN | 2023-06-05 09:01 | 2023-06-05 09:08 | 259 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 EN PATRULLAJE AÃ‰REO EL 6/7/2023 SOLO SE REPORTAN DESGANCHES PREVENTIVOS PREFERENCIALES (PRIORITY). | S23060500100 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-06-05 | 1813 | keep | 0 | Jun | 2023 | 0.0012348 | 0.0001764 | Sustained | FALSE | FALSE | Not_TMED_Event | 259
SAN JUAN | 2023-06-05 09:01 | 2023-06-05 09:08 | 686 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 EN PATRULLAJE AÃ‰REO EL 6/7/2023 SOLO SE REPORTAN DESGANCHES PREVENTIVOS PREFERENCIALES (PRIORITY). | S23060500100 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-06-05 | 4802 | keep | 0 | Jun | 2023 | 0.0032706 | 0.00046723 | Sustained | FALSE | FALSE | Not_TMED_Event | 686
SAN JUAN | 2023-06-05 09:01 | 2023-06-05 09:08 | 953 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 EN PATRULLAJE AÃ‰REO EL 6/7/2023 SOLO SE REPORTAN DESGANCHES PREVENTIVOS PREFERENCIALES (PRIORITY). | S23060500100 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-06-05 | 6671 | keep | 0 | Jun | 2023 | 0.0045436 | 0.00064908 | Sustained | FALSE | FALSE | Not_TMED_Event | 953
VEGA BAJA | 2023-06-05 09:04 | 2023-06-05 15:45 | 20 | 6:41 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA | A23060500107 | New_Event | Service Transformer Failure | Include | Include | Equipment | 401 | 2023-06-05 | 8020 | keep | 0 | Jun | 2023 | 0.0054624 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2023-06-05 09:12 | 2023-06-05 09:13 | 1952 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23060500236 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-05 | 1952 | keep | 0 | Jun | 2023 | 0.0013295 | 0.0013295 | Momentary | FALSE | FALSE | Not_TMED_Event | 1952
SAN JUAN | 2023-06-05 09:14 | 2023-06-05 15:53 | 1 | 6:39 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S23060500101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 399 | 2023-06-05 | 399 | keep | 0 | Jun | 2023 | 0.00027176 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-06-05 09:24 | 2023-06-05 14:07 | 125 | 4:43 | P | DESGANCHE | 1 X 1OO EN C/L DESGANCHE | S23060500107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2023-06-05 | 35375 | keep | 0 | Jun | 2023 | 0.024094 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2023-06-05 09:26 | 2023-06-05 16:26 | 67 | 7:00 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | C23060500124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 420 | 2023-06-05 | 28140 | keep | 0 | Jun | 2023 | 0.019166 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
GUAYAMA | 2023-06-05 09:30 | 2023-06-05 13:00 | 35 | 3:30 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTES DE MACHETE FID 1000052155 | P23060500062 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 210 | 2023-06-05 | 7350 | keep | 0 | Jun | 2023 | 0.0050061 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-06-05 09:32 | 2023-06-05 12:08 | 28 | 2:36 | P | DESGANCHE | 2X40 EN C/L DESGANCHE | C23060500125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2023-06-05 | 4368 | keep | 0 | Jun | 2023 | 0.002975 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
BAYAMON | 2023-06-05 09:33 | 2023-06-05 09:34 | 2466 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SE CERRO POR CONTROL | B2306050000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-06-05 | 2466 | keep | 0 | Jun | 2023 | 0.0016796 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
BAYAMON | 2023-06-05 09:34 | 2023-06-05 13:04 | 112 | 3:30 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L Y LEVANTO ALAMBRE EN EL PISO Y SE ENERGIZO 100% EN SERVICIO | S23060500114 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 210 | 2023-06-05 | 23520 | keep | 0 | Jun | 2023 | 0.016019 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
BAYAMON | 2023-06-05 09:35 | 2023-06-05 12:25 | 120 | 2:50 | P | DESGANCHE | 1 X 65 EN C.L DESGANCHE | B23060500103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2023-06-05 | 20400 | keep | 0 | Jun | 2023 | 0.013894 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2023-06-05 09:37 | 2023-06-05 17:09 | 478 | 7:32 | T | ARBOL SOBRE LINEA | DISPARO DE BKR ARBOL CAYO SOBRE LINEA PERO SE PARTIO Y CAYO AL SUELO EN COORDINACION CON IVAN PERRUCHO QUE ERA EL EMPLEADO A CARGO SE VERIFICO PERSONAL FUERA Y SE ENERGIZO. | B2306050000X | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 452 | 2023-06-05 | 216056 | keep | 0 | Jun | 2023 | 0.14715 | 0.00032556 | Sustained | FALSE | FALSE | Not_TMED_Event | 478
UTUADO | 2023-06-05 09:42 | 2023-06-06 10:05 | 5 | 24:23 | P | TRANSFORMADOR AVERIADO | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BUSHING SECUNDARIO AVERIADO | A23060500313 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1463 | 2023-06-05 | 7315 | keep | 0 | Jun | 2023 | 0.0049822 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2023-06-05 09:51 | 2023-06-05 13:40 | 11 | 3:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO | C23060500134 | New_Event | Secondary Wire Break | Include | Include | Equipment | 229 | 2023-06-05 | 2519 | keep | 0 | Jun | 2023 | 0.0017157 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2023-06-05 09:53 | 2023-06-05 12:05 | 43 | 2:12 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23060500115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2023-06-05 | 5676 | keep | 0 | Jun | 2023 | 0.0038659 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
SAN JUAN | 2023-06-05 09:55 | 2023-06-05 17:14 | 10 | 7:19 | P | PROBLEMA DEL CLIENTE | SE ABRIO XMR Y DEJO FUERA 2 TOMAS DE CLIENTE AVERIADA | S23060500125 | New_Event | Customer-Related Interruption | Include | Include | Public | 439 | 2023-06-05 | 4390 | keep | 0 | Jun | 2023 | 0.00299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-06-05 09:58 | 2023-06-05 10:23 | 10 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REPARAR SECUNDARIA NO FUNDIO | S23060500124 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-06-05 | 250 | keep | 0 | Jun | 2023 | 0.00017027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-06-05 10:06 | 2023-06-05 15:11 | 85 | 5:05 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23060500123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 305 | 2023-06-05 | 25925 | keep | 0 | Jun | 2023 | 0.017657 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
YAUCO | 2023-06-05 10:08 | 2023-06-05 14:11 | 10 | 4:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTES SECUNDARIOS DE TRANSFORMADOR | P23060500276 | New_Event | Secondary Wire Break | Include | Include | Equipment | 243 | 2023-06-05 | 2430 | keep | 0 | Jun | 2023 | 0.0016551 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-06-05 10:13 | 2023-06-05 10:14 | 3332 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23060500127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-05 | 3332 | keep | 0 | Jun | 2023 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
PONCE | 2023-06-05 10:14 | 2023-06-05 12:56 | 1 | 2:42 | P | ANIMAL | 1 X 25 RISER POR AVE | P23060500285 | New_Event | Animals | Include | Include | Wildlife | 162 | 2023-06-05 | 162 | keep | 0 | Jun | 2023 | 0.00011034 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-06-05 10:29 | 2023-06-05 18:00 | 1 | 7:31 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | C23060500145 | New_Event | Primary Wire Break | Include | Include | Equipment | 451 | 2023-06-05 | 451 | keep | 0 | Jun | 2023 | 0.00030717 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-06-05 10:34 | 2023-06-05 10:59 | 15 | 0:25 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23060500139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 25 | 2023-06-05 | 375 | keep | 0 | Jun | 2023 | 0.00025541 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-06-05 10:36 | 2023-06-05 13:32 | 88 | 2:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO VIENTOS | B23060500141 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 176 | 2023-06-05 | 15488 | keep | 0 | Jun | 2023 | 0.010549 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
FAJARDO | 2023-06-05 10:36 | 2023-06-05 14:34 | 1 | 3:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA AVERIADA | R23060500150 | New_Event | Cutout Failure | Include | Include | Equipment | 238 | 2023-06-05 | 238 | keep | 0 | Jun | 2023 | 0.0001621 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-06-05 10:49 | 2023-06-05 10:52 | 679 | 0:03 | T | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA 1705-00 POR PUENTE ABIERTO EN LA LINEA 10700-01 Y SE CERRO LINEA DEL 10700-03. EN SERVICIO | B23060500150 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-06-05 | 2037 | keep | 0 | Jun | 2023 | 0.0013874 | 0.00046246 | Momentary | FALSE | FALSE | Not_TMED_Event | 679
BAYAMON | 2023-06-05 10:49 | 2023-06-05 10:52 | 949 | 0:03 | T | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA 1705-00 POR PUENTE ABIERTO EN LA LINEA 10700-01 Y SE CERRO LINEA DEL 10700-03. EN SERVICIO | B23060500151 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-06-05 | 2847 | keep | 0 | Jun | 2023 | 0.0019391 | 0.00064636 | Momentary | FALSE | FALSE | Not_TMED_Event | 949
BAYAMON | 2023-06-05 10:49 | 2023-06-05 10:52 | 67 | 0:03 | T | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA 1705-00 POR PUENTE ABIERTO EN LA LINEA 10700-01 Y SE CERRO LINEA DEL 10700-03. EN SERVICIO | B23060500152 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-06-05 | 201 | keep | 0 | Jun | 2023 | 0.0001369 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2023-06-05 10:49 | 2023-06-05 10:52 | 637 | 0:03 | T | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA 1705-00 POR PUENTE ABIERTO EN LA LINEA 10700-01 Y SE CERRO LINEA DEL 10700-03. EN SERVICIO | B23060500153 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-06-05 | 1911 | keep | 0 | Jun | 2023 | 0.0013016 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
UTUADO | 2023-06-05 10:52 | 2023-06-05 17:13 | 30 | 6:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR LLUVIAS | A23060500171 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 381 | 2023-06-05 | 11430 | keep | 0 | Jun | 2023 | 0.0077849 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-06-05 10:59 | 2023-06-05 13:13 | 4 | 2:14 | P | ANIMAL | 1 X 40 C/L 1 X15 EN XMR CRUCE POR AVE | R23060500157 | New_Event | Animals | Include | Include | Wildlife | 134 | 2023-06-05 | 536 | keep | 0 | Jun | 2023 | 0.00036507 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2023-06-05 11:00 | 2023-06-05 14:18 | 70 | 3:18 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE DETECTO CAUSA | M23060500243 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 198 | 2023-06-05 | 13860 | keep | 0 | Jun | 2023 | 0.00944 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2023-06-05 11:01 | 2023-06-05 14:00 | 6 | 2:59 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO AISLADOR ROTO | C23060500156 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 179 | 2023-06-05 | 1074 | keep | 0 | Jun | 2023 | 0.0007315 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-06-05 11:01 | 2023-06-05 16:01 | 173 | 5:00 | P | DESGANCHE | 1 X 80 EN C/L DEAGANCHE | B23060500159 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 300 | 2023-06-05 | 51900 | keep | 0 | Jun | 2023 | 0.035349 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-05 11:04 | 2023-06-05 17:42 | 83 | 6:38 | P | TRANSFORMADOR AVERIADO | SE ABRIO C/L PARA TRANSFERIR CARGA DE 1 XMR A OTRO TRASPATIO POR XMR AVERIADO | S23060500149 | New_Event | Service Transformer Failure | Include | Include | Equipment | 398 | 2023-06-05 | 33034 | keep | 0 | Jun | 2023 | 0.022499 | 5.6531e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 83
BAYAMON | 2023-06-05 11:05 | 2023-06-05 15:03 | 498 | 3:58 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23060500164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2023-06-05 | 118524 | keep | 0 | Jun | 2023 | 0.080726 | 0.00033919 | Sustained | FALSE | FALSE | Not_TMED_Event | 498
PONCE | 2023-06-05 11:06 | 2023-06-05 20:07 | 1 | 9:01 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5 A 2400 POR UNO MISMA CAPACIDAD | P23060500341 | New_Event | Service Transformer Failure | Include | Include | Equipment | 541 | 2023-06-05 | 541 | keep | 0 | Jun | 2023 | 0.00036847 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-06-05 11:08 | 2023-06-05 18:13 | 1 | 7:05 | P | DESGANCHE | 1 X 25 EN RISER DESGANCHE | A23060050183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 425 | 2023-06-05 | 425 | keep | 0 | Jun | 2023 | 0.00028947 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-06-05 11:14 | 2023-06-05 18:10 | 10 | 6:56 | P | DESGANCHE | SE CERRO PUENTES PRIMARIOS | A23060500046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 416 | 2023-06-05 | 4160 | keep | 0 | Jun | 2023 | 0.0028334 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-06-05 11:16 | 2023-06-05 15:28 | 72 | 4:12 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23060500171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 252 | 2023-06-05 | 18144 | keep | 0 | Jun | 2023 | 0.012358 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
CAGUAS | 2023-06-05 11:17 | 2023-06-05 14:05 | 1 | 2:48 | P | CAUSAS EXTERNAS | 3 X 50 EN CORTE DE LINEA SE RETIRO POSTE DE TELEFONO IMPACTADO POR CAMION EN LA TRIFASICA | C23060500165 | New_Event | Damage From Public | Include | Include | Public | 168 | 2023-06-05 | 168 | keep | 0 | Jun | 2023 | 0.00011442 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-06-05 11:21 | 2023-06-05 19:22 | 1 | 8:01 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR 1 X 15 | P23060500350 | New_Event | Primary Wire Break | Include | Include | Equipment | 481 | 2023-06-05 | 481 | keep | 0 | Jun | 2023 | 0.00032761 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-06-05 11:21 | 2023-06-05 17:03 | 123 | 5:42 | P | DESGANCHE | 1 X 15 Y 2 X 50 EN CORTES DE LINEA SE REALIZO DESGANCHE DE BAMBUA | C23060500167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 342 | 2023-06-05 | 42066 | keep | 0 | Jun | 2023 | 0.028651 | 8.3775e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 123
MAYAGÃœEZ | 2023-06-05 11:32 | 2023-06-05 21:45 | 65 | 10:13 | P | CRUCETA DEFECTUOSA O AVERIADA | SE REMPLAZO CRUCETA PARTIDA SE CERRO CORTE DE LINEA | M23060400252 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 613 | 2023-06-05 | 39845 | keep | 0 | Jun | 2023 | 0.027138 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
HUMACAO | 2023-06-05 11:42 | 2023-06-05 13:00 | 15 | 1:18 | P | CAUSAS EXTERNAS | SE REEMPLAZO POSTE SECUNDARIO IMPACTADO POR CAMION DE CONCRETERA | C23060500175 | New_Event | Damage From Public | Include | Include | Public | 78 | 2023-06-05 | 1170 | keep | 0 | Jun | 2023 | 0.00079688 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-06-05 11:43 | 2023-06-05 15:00 | 1 | 3:17 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | P23060500373 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2023-06-05 | 197 | keep | 0 | Jun | 2023 | 0.00013418 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-06-05 11:51 | 2023-06-05 18:39 | 23 | 6:48 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | S23060500166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 408 | 2023-06-05 | 9384 | keep | 0 | Jun | 2023 | 0.0063914 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
AGUADILLA | 2023-06-05 11:52 | 2023-06-05 14:02 | 1483 | 2:10 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR PARA REPARAR PUENTE PRIMARIO ABIERTO EN EL TRONCAL DEL ALIMENTADOR | M23060400476 | New_Event | Primary Wire Break | Include | Include | Equipment | 130 | 2023-06-05 | 192790 | keep | 0 | Jun | 2023 | 0.13131 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
BARRANQUITAS | 2023-06-05 11:53 | 2023-06-05 17:03 | 197 | 5:10 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE EVENTO TRANSFERIDO DE PONCE | P23060500606 | New_Event | Vegetation Contact | Include | Include | Vegetation | 310 | 2023-06-05 | 61070 | keep | 0 | Jun | 2023 | 0.041594 | 0.00013418 | Sustained | FALSE | FALSE | Not_TMED_Event | 197
CANOVANAS | 2023-06-05 11:59 | 2023-06-05 16:49 | 12 | 4:50 | P | SECUNDARIA/DESGANCHE | ABRIO XMR PARA LEVANTR SECUNDARIA Y 2 TOMAS AVERIADAS POR PALMA | R23060500183 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 290 | 2023-06-05 | 3480 | keep | 0 | Jun | 2023 | 0.0023702 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-06-05 12:00 | 2023-06-05 15:13 | 150 | 3:13 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | C23060500180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2023-06-05 | 28950 | keep | 0 | Jun | 2023 | 0.019718 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2023-06-05 12:04 | 2023-06-05 13:41 | 8 | 1:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZA PORTA FUSIBLE | P23060500392 | New_Event | Cutout Failure | Include | Include | Equipment | 97 | 2023-06-05 | 776 | keep | 0 | Jun | 2023 | 0.00052853 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-06-05 12:29 | 2023-06-05 14:38 | 18 | 2:09 | P | DESGANCHE | 1 X 4 0 EN C/L DESGANCHE | B23060500209 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2023-06-05 | 2322 | keep | 0 | Jun | 2023 | 0.0015815 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
MAYAGÃœEZ | 2023-06-05 12:34 | 2023-06-05 12:50 | 50 | 0:16 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBUS DE LAS LINEAS | P23060500413 | New_Event | Vegetation Contact | Include | Include | Vegetation | 16 | 2023-06-05 | 800 | keep | 0 | Jun | 2023 | 0.00054488 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-06-05 12:41 | 2023-06-05 15:26 | 50 | 2:45 | P | DESGANCHE | 1 X 100 EN C/L | R23060500173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2023-06-05 | 8250 | keep | 0 | Jun | 2023 | 0.005619 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-06-05 12:42 | 2023-06-05 12:43 | 686 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S2306050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-05 | 686 | keep | 0 | Jun | 2023 | 0.00046723 | 0.00046723 | Momentary | FALSE | FALSE | Not_TMED_Event | 686
BARRANQUITAS | 2023-06-05 12:42 | 2023-06-05 16:58 | 9 | 4:16 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE SECUNDARIO | C23060500202 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 256 | 2023-06-05 | 2304 | keep | 0 | Jun | 2023 | 0.0015692 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2023-06-05 12:45 | 2023-06-05 14:12 | 15 | 1:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA ROTA | M23060500290 | New_Event | Secondary Wire Break | Include | Include | Equipment | 87 | 2023-06-05 | 1305 | keep | 0 | Jun | 2023 | 0.00088883 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-06-05 12:51 | 2023-06-05 19:58 | 6 | 7:07 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | C23060500209 | New_Event | Animals | Include | Include | Wildlife | 427 | 2023-06-05 | 2562 | keep | 0 | Jun | 2023 | 0.001745 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2023-06-05 13:00 | 2023-06-05 13:33 | 40 | 0:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA FUERTES VIENTOS | P23060500442 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 33 | 2023-06-05 | 1320 | keep | 0 | Jun | 2023 | 0.00089905 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-06-05 13:02 | 2023-06-05 13:26 | 1 | 0:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO BANCO XMR Y SE REPARO TEASER EN BANCO TRIFASICO | B23060500219 | New_Event | Secondary Wire Break | Include | Include | Equipment | 24 | 2023-06-05 | 24 | keep | 0 | Jun | 2023 | 1.6346e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-06-05 13:06 | 2023-06-05 15:06 | 80 | 2:00 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23060500220 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2023-06-05 | 9600 | keep | 0 | Jun | 2023 | 0.0065385 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2023-06-05 13:09 | 2023-06-05 16:47 | 2 | 3:38 | P | ANIMAL | 1 X 8 EN XMR CRUCE X AVE REMPLAZO CAJA AVERIADA EVENTO TRANSFERIDO DE PONCE | P23060500452 | New_Event | Animals | Include | Include | Wildlife | 218 | 2023-06-05 | 436 | keep | 0 | Jun | 2023 | 0.00029696 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-06-05 13:10 | 2023-06-05 13:15 | 2802 | 0:05 | P | SOBRECARGA | SE REALIZO TRANSFERENCIA DE CARGA DEL ALIMENTADOR 6015-02 AL 6802-04 POR SOBRE CARGA EN LA SUBESTACION 6015 ESTAS SUBESTACIONES NO FASEAN | M23060500304 | New_Event | Trip Due To Overload | Include | Include | Other | 5 | 2023-06-05 | 14010 | keep | 0 | Jun | 2023 | 0.0095421 | 0.0019084 | Momentary | FALSE | FALSE | Not_TMED_Event | 2802
UTUADO | 2023-06-05 13:10 | 2023-06-05 15:17 | 10 | 2:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A23060500237 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2023-06-05 | 1270 | keep | 0 | Jun | 2023 | 0.00086499 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-06-05 13:14 | 2023-06-05 17:03 | 18 | 3:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A23060500240 | New_Event | Cutout Failure | Include | Include | Equipment | 229 | 2023-06-05 | 4122 | keep | 0 | Jun | 2023 | 0.0028075 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2023-06-05 13:16 | 2023-06-05 15:16 | 723 | 2:00 | T | ALIMENTADOR AMARRADO | LOCK OUT DE 1912-00 SE DESCONECTO SWITCH AVERIADO DEL PRESSURE RELEASE DEL LOAD TAP CHANGER Y SE ENERGIZO LA SUBESTACION 100% EN SERVICIO. CARGA X 1912-08 | S23060500213 | New_Event | Feeder Load Transferred | Include | Include | Other | 120 | 2023-06-05 | 86760 | keep | 0 | Jun | 2023 | 0.059092 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2023-06-05 13:16 | 2023-06-05 15:16 | 1976 | 2:00 | T | ALIMENTADOR AMARRADO | LOCK OUT DE 1912-00 SE DESCONECTO SWITCH AVERIADO DEL PRESSURE RELEASE DEL LOAD TAP CHANGER Y SE ENERGIZO LA SUBESTACION 100% EN SERVICIO. CARGA X 1912-08 | S23060500213 | New_Event | Feeder Load Transferred | Include | Include | Other | 120 | 2023-06-05 | 237120 | keep | 0 | Jun | 2023 | 0.1615 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2023-06-05 13:16 | 2023-06-05 15:16 | 57 | 2:00 | S | PROTECCION DEFECTUOSA | LOCK OUT SE DESCONECTO SWITCH AVERIADO DEL PRESSURE RELEASE DEL LOAD TAP CHANGER Y SE ENERGIZO LA SUBESTACION 100% EN SERVICIO. | S23060500213 | New_Event | Protection Miscoordination | Include | Include | Other | 120 | 2023-06-05 | 6840 | keep | 0 | Jun | 2023 | 0.0046587 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
BAYAMON | 2023-06-05 13:16 | 2023-06-05 15:16 | 577 | 2:00 | S | PROTECCION DEFECTUOSA | LOCK OUT SE DESCONECTO SWITCH AVERIADO DEL PRESSURE RELEASE DEL LOAD TAP CHANGER Y SE ENERGIZO LA SUBESTACION 100% EN SERVICIO. LLEVA EL 1711-02 Y 1711-05 | S23060500213 | New_Event | Protection Miscoordination | Include | Include | Other | 120 | 2023-06-05 | 69240 | keep | 0 | Jun | 2023 | 0.047159 | 0.00039299 | Sustained | FALSE | FALSE | Not_TMED_Event | 577
BAYAMON | 2023-06-05 13:16 | 2023-06-05 15:16 | 23 | 2:00 | S | PROTECCION DEFECTUOSA | LOCK OUT SE DESCONECTO SWITCH AVERIADO DEL PRESSURE RELEASE DEL LOAD TAP CHANGER Y SE ENERGIZO LA SUBESTACION 100% EN SERVICIO. | S23060500213 | New_Event | Protection Miscoordination | Include | Include | Other | 120 | 2023-06-05 | 2760 | keep | 0 | Jun | 2023 | 0.0018798 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
VEGA BAJA | 2023-06-05 13:16 | 2023-06-05 14:50 | 750 | 1:34 | P | CONDUCTOR ARRIADO O CRUZADO | SE ABRIO MACHETES PARA CERRAR PUENTE PRIMARIO Y SEPARAR LINEAS PRIMARIAS CRUZADAS | A23060400146 | Additional_clients | Primary To Primary Contact | Include | Include | Equipment | 94 | 2023-06-05 | 70500 | keep | 0 | Jun | 2023 | 0.048017 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-05 13:26 | 2023-06-05 16:18 | 3 | 2:52 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23060500245 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2023-06-05 | 516 | keep | 0 | Jun | 2023 | 0.00035145 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2023-06-05 13:28 | 2023-06-05 15:15 | 6 | 1:47 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | C23060500228 | New_Event | Animals | Include | Include | Wildlife | 107 | 2023-06-05 | 642 | keep | 0 | Jun | 2023 | 0.00043726 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-06-05 13:38 | 2023-06-05 14:30 | 50 | 0:52 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A23060500255 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 52 | 2023-06-05 | 2600 | keep | 0 | Jun | 2023 | 0.0017708 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-06-05 13:57 | 2023-06-05 18:32 | 120 | 4:35 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | C23060500236 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2023-06-05 | 33000 | keep | 0 | Jun | 2023 | 0.022476 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2023-06-05 14:00 | 2023-06-05 17:05 | 30 | 3:05 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN C/L SE RETEZO LINEA PRIMARIA | S23060500256 | New_Event | Primary Wire Break | Include | Include | Equipment | 185 | 2023-06-05 | 5550 | keep | 0 | Jun | 2023 | 0.0037801 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-06-05 14:04 | 2023-06-05 15:37 | 110 | 1:33 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C23060500238 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2023-06-05 | 10230 | keep | 0 | Jun | 2023 | 0.0069676 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
CAGUAS | 2023-06-05 14:15 | 2023-06-05 14:16 | 1271 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | C23060500240 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-06-05 | 1271 | keep | 0 | Jun | 2023 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
MAYAGÃœEZ | 2023-06-05 14:15 | 2023-06-06 15:05 | 1 | 24:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 5 EN TRANSFORMADOR NO SE REPORTO CAUSA RELACIONADO A EVENTO M23060500700 | M23060600320 | New_Event | Cutout Failure | Include | Include | Equipment | 1490 | 2023-06-05 | 1490 | keep | 0 | Jun | 2023 | 0.0010148 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-06-05 14:21 | 2023-06-05 15:21 | 1 | 1:00 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23060500349 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 60 | 2023-06-05 | 60 | keep | 0 | Jun | 2023 | 4.0866e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-06-05 14:25 | 2023-06-05 15:10 | 131 | 0:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA FURTE VIENTO | M23060500350 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 45 | 2023-06-05 | 5895 | keep | 0 | Jun | 2023 | 0.0040151 | 8.9224e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 131
AGUADILLA | 2023-06-05 14:25 | 2023-06-05 14:40 | 8 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | P23060500485 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2023-06-05 | 120 | keep | 0 | Jun | 2023 | 8.1731e-05 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2023-06-05 14:48 | 2023-06-05 17:12 | 50 | 2:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN CORTE DE LINEA FUSIBLE EL MISMO 1 X 65 | P23060500526 | New_Event | Cutout Failure | Include | Include | Equipment | 144 | 2023-06-05 | 7200 | keep | 0 | Jun | 2023 | 0.0049039 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-06-05 14:49 | 2023-06-05 14:50 | 959 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23060500346 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-05 | 959 | keep | 0 | Jun | 2023 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-06-05 14:49 | 2023-06-05 14:50 | 1382 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23060500346 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-05 | 1382 | keep | 0 | Jun | 2023 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2023-06-05 14:49 | 2023-06-05 14:50 | 663 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23060500346 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-05 | 663 | keep | 0 | Jun | 2023 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2023-06-05 14:49 | 2023-06-05 14:50 | 1514 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23060500345 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-05 | 1514 | keep | 0 | Jun | 2023 | 0.0010312 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2023-06-05 14:49 | 2023-06-05 14:50 | 1105 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23060500345 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-05 | 1105 | keep | 0 | Jun | 2023 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2023-06-05 14:49 | 2023-06-05 14:50 | 4176 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23060500348 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-05 | 4176 | keep | 0 | Jun | 2023 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2023-06-05 14:49 | 2023-06-05 14:50 | 252 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23060500348 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-05 | 252 | keep | 0 | Jun | 2023 | 0.00017164 | 0.00017164 | Momentary | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2023-06-05 14:49 | 2023-06-05 14:50 | 2147 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23060500348 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-05 | 2147 | keep | 0 | Jun | 2023 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2023-06-05 14:49 | 2023-06-05 14:50 | 2858 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23060500347 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-05 | 2858 | keep | 0 | Jun | 2023 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
FAJARDO | 2023-06-05 14:52 | 2023-06-05 16:05 | 2 | 1:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 5 EN XMR REMPLAZO POSTAFUSIBLE QUEMADO | R23060500193 | New_Event | Cutout Failure | Include | Include | Equipment | 73 | 2023-06-05 | 146 | keep | 0 | Jun | 2023 | 9.944e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2023-06-05 14:53 | 2023-06-05 18:23 | 4 | 3:30 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23060500344 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2023-06-05 | 840 | keep | 0 | Jun | 2023 | 0.00057212 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2023-06-05 14:55 | 2023-06-05 17:16 | 1117 | 2:21 | T | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO EN EL TRONCAL DEL ALIMENTADOR Y SE CERRO EL INETRRUPTOR LLEVA LA CARGA DEL 6404-02 | M23060500366 | New_Event | Primary Wire Break | Include | Include | Equipment | 141 | 2023-06-05 | 157497 | keep | 0 | Jun | 2023 | 0.10727 | 0.00076078 | Sustained | FALSE | FALSE | Not_TMED_Event | 1117
MAYAGÃœEZ | 2023-06-05 14:55 | 2023-06-05 17:16 | 1671 | 2:21 | T | ALIMENTADOR AMARRADO | CARGA POR 6404-01 | M23060500366 | New_Event | Feeder Load Transferred | Include | Include | Other | 141 | 2023-06-05 | 235611 | keep | 0 | Jun | 2023 | 0.16047 | 0.0011381 | Sustained | FALSE | FALSE | Not_TMED_Event | 1671
ARECIBO | 2023-06-05 14:58 | 2023-06-05 17:15 | 25 | 2:17 | P | ARBOL SOBRE LINEA | 1 X 65 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | A23060500298 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 137 | 2023-06-05 | 3425 | keep | 0 | Jun | 2023 | 0.0023328 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-06-05 15:00 | 2023-06-05 19:10 | 33 | 4:10 | P | DESGANCHE | 1 X 100 Y 1 X 65 EN CORTES DE LINEA | C23060500257 | New_Event | Vegetation Contact | Include | Include | Vegetation | 250 | 2023-06-05 | 8250 | keep | 0 | Jun | 2023 | 0.005619 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
CAGUAS | 2023-06-05 15:07 | 2023-06-05 16:00 | 1271 | 0:53 | T | DESCONECTIVO DEFECTUOSO | CG-230605-02 SE ABRIO INTERRUPTOR POR EMERGENCIA MACHETE QUEMADO EN SALIDA DEL RISER, SE TRANSFIRIO LA CARGA AL 3301-02 NO FASEA | C23060500261 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 53 | 2023-06-05 | 67363 | keep | 0 | Jun | 2023 | 0.045881 | 0.00086567 | Sustained | FALSE | FALSE | Not_TMED_Event | 1271
AGUADILLA | 2023-06-05 15:11 | 2023-06-05 18:00 | 8 | 2:49 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO 10 KVA X 37.5 KVA | P23060500553 | New_Event | Service Transformer Failure | Include | Include | Equipment | 169 | 2023-06-05 | 1352 | keep | 0 | Jun | 2023 | 0.00092084 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2023-06-05 15:17 | 2023-06-05 18:47 | 7 | 3:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR SECUNDARIA AVERIADA | R23060500188 | New_Event | Secondary Wire Break | Include | Include | Equipment | 210 | 2023-06-05 | 1470 | keep | 0 | Jun | 2023 | 0.0010012 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-06-05 15:20 | 2023-06-05 17:23 | 60 | 2:03 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE EVENTO TRANSFERIDO DE PONCE | P23060500569 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2023-06-05 | 7380 | keep | 0 | Jun | 2023 | 0.0050265 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-06-05 15:29 | 2023-06-05 18:40 | 100 | 3:11 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | B23060500366 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2023-06-05 | 19100 | keep | 0 | Jun | 2023 | 0.013009 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2023-06-05 15:38 | 2023-06-05 18:29 | 150 | 2:51 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO PUENTE PRMARIO HAY ALAMBRE PRIMARIO EN EL PISO 3 X 100 EN CORTE DE LINEA | P23060500519 | New_Event | Primary Wire Break | Include | Include | Equipment | 171 | 2023-06-05 | 25650 | keep | 0 | Jun | 2023 | 0.01747 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2023-06-05 15:41 | 2023-06-05 15:51 | 20 | 0:10 | P | DESGANCHE | DESGANCHE 1 X 20 EN TRASNFORMADOR | P23060500465 | New_Event | Vegetation Contact | Include | Include | Vegetation | 10 | 2023-06-05 | 200 | keep | 0 | Jun | 2023 | 0.00013622 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2023-06-05 15:42 | 2023-06-05 17:50 | 50 | 2:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A23060500038 | New_Event | Cutout Failure | Include | Include | Equipment | 128 | 2023-06-05 | 6400 | keep | 0 | Jun | 2023 | 0.004359 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-06-05 15:49 | 2023-06-05 18:05 | 76 | 2:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN RISER SE REEMPLAZO CAJA PRIMARIA | S23060500312 | New_Event | Cutout Failure | Include | Include | Equipment | 136 | 2023-06-05 | 10336 | keep | 0 | Jun | 2023 | 0.0070398 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
MAYAGÃœEZ | 2023-06-05 15:54 | 2023-06-05 18:25 | 300 | 2:31 | P | ARBOL SOBRE LINEA | 2 X 100 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEAS | M23060500402 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 151 | 2023-06-05 | 45300 | keep | 0 | Jun | 2023 | 0.030854 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2023-06-05 15:55 | 2023-06-05 16:59 | 28 | 1:04 | P | DESGANCHE | 1 X 10 EN C/L DESGANCHE | B23060500315 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2023-06-05 | 1792 | keep | 0 | Jun | 2023 | 0.0012205 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
AGUADILLA | 2023-06-05 16:04 | 2023-06-05 18:00 | 40 | 1:56 | P | OTRAS CAUSAS | 1 X 40 EN CORTE DE LINEA FUSIBLE ESTABA CORROIDO | A23060500323 | New_Event | Other Causes | Include | Include | Other | 116 | 2023-06-05 | 4640 | keep | 0 | Jun | 2023 | 0.0031603 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-06-05 16:06 | 2023-06-05 18:32 | 62 | 2:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN C/L SE REMPLAZO CAJA PRIMARIA QUEMADA | S23060500319 | New_Event | Cutout Failure | Include | Include | Equipment | 146 | 2023-06-05 | 9052 | keep | 0 | Jun | 2023 | 0.0061653 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
BAYAMON | 2023-06-05 16:14 | 2023-06-05 16:15 | 959 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DEL 1904-07 LLEVA 1901-01, 1901-04 Y 1901-05 | B2306050000X | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-06-05 | 959 | keep | 0 | Jun | 2023 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-06-05 16:14 | 2023-06-05 16:15 | 1264 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DEL 1904-07 LLEVA 1901-01, 1901-04 Y 1901-05 | B2306050000X | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-06-05 | 1264 | keep | 0 | Jun | 2023 | 0.0008609 | 0.0008609 | Momentary | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2023-06-05 16:14 | 2023-06-05 16:15 | 62 | 0:01 | P | DESCONECTIVO DEFECTUOSO | RECIERRE DEL 1904-07 LLEVA 1901-01, 1901-04 Y 1901-05 | B2306050000X | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-06-05 | 62 | keep | 0 | Jun | 2023 | 4.2228e-05 | 4.2228e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 62
AGUADILLA | 2023-06-05 16:20 | 2023-06-05 17:30 | 3 | 1:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN CORTE DE LINEA POR FUERTE VIENTO | A23060500333 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 70 | 2023-06-05 | 210 | keep | 0 | Jun | 2023 | 0.00014303 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2023-06-05 16:32 | 2023-06-05 23:15 | 11 | 6:43 | P | TRANSFORMADOR AVERIADO | REEMPLAZAR TRANSFORMADOR 37.5 KVA AVERIADO | A23060500335 | New_Event | Service Transformer Failure | Include | Include | Equipment | 403 | 2023-06-05 | 4433 | keep | 0 | Jun | 2023 | 0.0030193 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2023-06-05 16:33 | 2023-06-05 18:05 | 50 | 1:32 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23060500339 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2023-06-05 | 4600 | keep | 0 | Jun | 2023 | 0.003133 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-06-05 16:35 | 2023-06-05 17:38 | 5 | 1:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A23060500340 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 63 | 2023-06-05 | 315 | keep | 0 | Jun | 2023 | 0.00021455 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-06-05 16:37 | 2023-06-05 16:38 | 959 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DEL 1904-07 LLEVA 1901-01, 1901-04 Y 1901-05 | B2306050000X | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2023-06-05 | 959 | keep | 0 | Jun | 2023 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-06-05 16:37 | 2023-06-05 16:38 | 1264 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DEL 1904-07 LLEVA 1901-01, 1901-04 Y 1901-05 | B2306050000X | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2023-06-05 | 1264 | keep | 0 | Jun | 2023 | 0.0008609 | 0.0008609 | Momentary | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2023-06-05 16:37 | 2023-06-05 16:38 | 62 | 0:01 | P | DESCONECTIVO DEFECTUOSO | RECIERRE DEL 1904-07 LLEVA 1901-01, 1901-04 Y 1901-05 | B2306050000X | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2023-06-05 | 62 | keep | 0 | Jun | 2023 | 4.2228e-05 | 4.2228e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 62
BAYAMON | 2023-06-05 16:40 | 2023-06-05 18:19 | 60 | 1:39 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23060500385 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2023-06-05 | 5940 | keep | 0 | Jun | 2023 | 0.0040457 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-06-05 16:41 | 2023-06-05 19:00 | 60 | 2:19 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23060500352 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2023-06-05 | 8340 | keep | 0 | Jun | 2023 | 0.0056803 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-06-05 16:47 | 2023-06-05 18:05 | 1 | 1:18 | P | NO SE REPORTO CAUSA | 2 X 50 EN RISER EVENTO TRANSFERIDO DE PONCE | P23060500401 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2023-06-05 | 78 | keep | 0 | Jun | 2023 | 5.3125e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-06-05 16:48 | 2023-06-05 20:52 | 15 | 4:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | S23060500330 | New_Event | Secondary Wire Break | Include | Include | Equipment | 244 | 2023-06-05 | 3660 | keep | 0 | Jun | 2023 | 0.0024928 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-06-05 16:49 | 2023-06-05 16:51 | 1615 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S2306050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-05 | 3230 | keep | 0 | Jun | 2023 | 0.0021999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
AGUADILLA | 2023-06-05 16:53 | 2023-06-05 18:23 | 8 | 1:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA POR LA MISMA CAPACIDAD | A23060500363 | New_Event | Service Transformer Failure | Include | Include | Equipment | 90 | 2023-06-05 | 720 | keep | 0 | Jun | 2023 | 0.00049039 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-06-05 17:06 | 2023-06-05 18:00 | 25 | 0:54 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | C23060500298 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2023-06-05 | 1350 | keep | 0 | Jun | 2023 | 0.00091948 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-06-05 17:11 | 2023-06-06 17:15 | 30 | 24:04 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | M23060500428 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1444 | 2023-06-05 | 43320 | keep | 0 | Jun | 2023 | 0.029505 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-06-05 17:16 | 2023-06-05 17:17 | 57 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2306050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-05 | 57 | keep | 0 | Jun | 2023 | 3.8822e-05 | 3.8822e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 57
BAYAMON | 2023-06-05 17:18 | 2023-06-05 17:19 | 57 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2306050000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-05 | 57 | keep | 0 | Jun | 2023 | 3.8822e-05 | 3.8822e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 57
MAYAGÃœEZ | 2023-06-05 17:19 | 2023-06-05 19:56 | 12 | 2:37 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | P23060500657 | New_Event | Primary Wire Break | Include | Include | Equipment | 157 | 2023-06-05 | 1884 | keep | 0 | Jun | 2023 | 0.0012832 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2023-06-05 17:38 | 2023-06-05 17:40 | 1475 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE LE DIO PRUEBA QUEDO EN SERVICIO | P23060500673 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-05 | 2950 | keep | 0 | Jun | 2023 | 0.0020092 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
MAYAGÃœEZ | 2023-06-05 17:38 | 2023-06-05 18:30 | 4 | 0:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23060500438 | New_Event | Secondary Wire Break | Include | Include | Equipment | 52 | 2023-06-05 | 208 | keep | 0 | Jun | 2023 | 0.00014167 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-06-05 17:40 | 2023-06-05 19:08 | 100 | 1:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN C/L SE REMPLAZO AISLADOR | R23060500207 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 88 | 2023-06-05 | 8800 | keep | 0 | Jun | 2023 | 0.0059936 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-06-05 17:42 | 2023-06-05 17:46 | 1271 | 0:04 | T | DESCONECTIVO DEFECTUOSO | CG-230605-02 SE REEMPLAZO MACHETE QUEMADO EN RISER DE SALIDA DEL ALIMENTADOR, SE NORMALIZO LA CARGA **NO FASEA** | C23060500261 | Partial_restoration | Switch Failure | Include | Include | Equipment | 4 | 2023-06-05 | 5084 | keep | 0 | Jun | 2023 | 0.0034627 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-06-05 17:44 | 2023-06-05 19:40 | 200 | 1:56 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBUS DE LAS LINEAS | M23060500444 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2023-06-05 | 23200 | keep | 0 | Jun | 2023 | 0.015801 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2023-06-05 17:51 | 2023-06-05 19:00 | 115 | 1:09 | P | OTRAS CAUSAS | 1 X 40 EN CORTE DE LINEA POR ALTA TEMPERATURA | A23060500381 | New_Event | Other Causes | Include | Include | Other | 69 | 2023-06-05 | 7935 | keep | 0 | Jun | 2023 | 0.0054045 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
CAGUAS | 2023-06-05 18:06 | 2023-06-05 18:10 | 1 | 0:04 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | C23060500145 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 4 | 2023-06-05 | 4 | keep | 0 | Jun | 2023 | 2.7244e-06 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-06-05 18:23 | 2023-06-05 18:50 | 4607 | 0:27 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON EL RECIERRE EN OFF SE VERIFICO PERSONAL FUERA DE LAS LINEAS Y SE CERRO EL INTERRUPTOR | A23060500410 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 27 | 2023-06-05 | 124389 | keep | 0 | Jun | 2023 | 0.084721 | 0.0031378 | Sustained | FALSE | FALSE | Not_TMED_Event | 4607
BAYAMON | 2023-06-05 18:28 | 2023-06-05 21:37 | 100 | 3:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L POR VIENTOS | B23060500427 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 189 | 2023-06-05 | 18900 | keep | 0 | Jun | 2023 | 0.012873 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2023-06-05 18:34 | 2023-06-05 20:34 | 20 | 2:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | P23060500679 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 120 | 2023-06-05 | 2400 | keep | 0 | Jun | 2023 | 0.0016346 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2023-06-05 18:34 | 2023-06-05 19:04 | 15 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON BAJANTES SECUNDARIOS DE TRANSFORMADOR | P23060500682 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-06-05 | 450 | keep | 0 | Jun | 2023 | 0.00030649 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-06-05 18:40 | 2023-06-05 19:00 | 9 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS CERCA DE LINEA PRIMARIA | M23060500385 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-06-05 | 180 | keep | 0 | Jun | 2023 | 0.0001226 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2023-06-05 18:50 | 2023-06-05 20:15 | 8 | 1:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA POR LA MISMA CAPACIDAD | A23060500363 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 85 | 2023-06-05 | 680 | keep | 0 | Jun | 2023 | 0.00046314 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-05 19:11 | 2023-06-05 19:22 | 959 | 0:11 | T | DESCONECTIVO DEFECTUOSO | DISPARO DEL 1904-07 LLEVA 1901-01, 1901-04 Y 1901-05. SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL. | B2306050000X | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 11 | 2023-06-05 | 10549 | keep | 0 | Jun | 2023 | 0.0071849 | 0.00065317 | Sustained | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-06-05 19:11 | 2023-06-05 19:22 | 1264 | 0:11 | T | DESCONECTIVO DEFECTUOSO | DISPARO DEL 1904-07 LLEVA 1901-01, 1901-04 Y 1901-05. SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL. | B2306050000X | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 11 | 2023-06-05 | 13904 | keep | 0 | Jun | 2023 | 0.00947 | 0.0008609 | Sustained | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2023-06-05 19:11 | 2023-06-05 19:22 | 62 | 0:11 | P | DESCONECTIVO DEFECTUOSO | DISPARO DEL 1904-07 LLEVA 1901-01, 1901-04 Y 1901-05 SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL. | B2306050000X | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 11 | 2023-06-05 | 682 | keep | 0 | Jun | 2023 | 0.00046451 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
UTUADO | 2023-06-05 19:20 | 2023-06-05 21:35 | 50 | 2:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23060500426 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2023-06-05 | 6750 | keep | 0 | Jun | 2023 | 0.0045974 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-06-05 19:24 | 2023-06-05 21:47 | 200 | 2:23 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23060500453 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2023-06-05 | 28600 | keep | 0 | Jun | 2023 | 0.019479 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2023-06-05 19:33 | 2023-06-06 12:40 | 25 | 17:07 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | A23060500433 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1027 | 2023-06-05 | 25675 | keep | 0 | Jun | 2023 | 0.017487 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2023-06-05 19:38 | 2023-06-05 21:10 | 50 | 1:32 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | P23060500779 | New_Event | Animals | Include | Include | Wildlife | 92 | 2023-06-05 | 4600 | keep | 0 | Jun | 2023 | 0.003133 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-06-05 19:45 | 2023-06-05 23:43 | 80 | 3:58 | P | DESGANCHE | 1 X 140 EN C/L SE DESGANCHO | B23060500460 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2023-06-05 | 19040 | keep | 0 | Jun | 2023 | 0.012968 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-06-05 19:54 | 2023-06-05 19:55 | 959 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DEL 1904-07 LLEVA 1901-01, 1901-04 Y 1901-05 | B2306050000X | Partial_restoration | Switch Failure | Include | Include | Equipment | 1 | 2023-06-05 | 959 | keep | 0 | Jun | 2023 | 0.00065317 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-05 19:54 | 2023-06-05 19:55 | 1264 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DEL 1904-07 LLEVA 1901-01, 1901-04 Y 1901-05 | B2306050000X | Partial_restoration | Switch Failure | Include | Include | Equipment | 1 | 2023-06-05 | 1264 | keep | 0 | Jun | 2023 | 0.0008609 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-05 19:54 | 2023-06-05 19:55 | 62 | 0:01 | P | DESCONECTIVO DEFECTUOSO | RECIERRE DEL 1904-07 LLEVA 1901-01, 1901-04 Y 1901-05 | B2306050000X | Partial_restoration | Switch Failure | Include | Include | Equipment | 1 | 2023-06-05 | 62 | keep | 0 | Jun | 2023 | 4.2228e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-06-05 19:54 | 2023-06-05 21:50 | 70 | 1:56 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23060500444 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2023-06-05 | 8120 | keep | 0 | Jun | 2023 | 0.0055305 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2023-06-05 19:55 | 2023-06-05 22:27 | 75 | 2:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR VIENTOS | M23060500487 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 152 | 2023-06-05 | 11400 | keep | 0 | Jun | 2023 | 0.0077645 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-06-05 20:00 | 2023-06-05 22:34 | 959 | 2:34 | T | DESCONECTIVO DEFECTUOSO | MEDIANTE GOI BY-230605-04 SE REMPLAZO AUXILIAR DE LINEA DEL BKR LLEVA 1901-04 Y 10% 1901-05 | S23060500499 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 154 | 2023-06-05 | 147686 | keep | 0 | Jun | 2023 | 0.10059 | 0.00065317 | Sustained | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-06-05 20:00 | 2023-06-05 22:34 | 1264 | 2:34 | T | DESCONECTIVO DEFECTUOSO | MEDIANTE GOI BY-230605-04 SE REMPLAZO AUXILIAR DE LINEA DEL BKR | S23060500499 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 154 | 2023-06-05 | 194656 | keep | 0 | Jun | 2023 | 0.13258 | 0.0008609 | Sustained | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2023-06-05 20:00 | 2023-06-05 22:34 | 62 | 2:34 | P | DESCONECTIVO DEFECTUOSO | MEDIANTE GOI BY-230605-04 SE REMPLAZO AUXILIAR DE LINEA DEL BKR SOLO LLEVA EL 10% DE SU CARGA | S23060500499 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 154 | 2023-06-05 | 9548 | keep | 0 | Jun | 2023 | 0.0065031 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
AGUADILLA | 2023-06-05 20:10 | 2023-06-05 20:22 | 2658 | 0:12 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE VERIFICO PERSONAL FUERA DE LAS LINEAS Y SE VERIFICO CON FRANCISCO RODRIGUEZ DEL TOC PARA CERRAR EL INTERRUPTOR | M23060500495 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 12 | 2023-06-05 | 31896 | keep | 0 | Jun | 2023 | 0.021724 | 0.0018104 | Sustained | FALSE | FALSE | Not_TMED_Event | 2658
ARECIBO | 2023-06-05 20:13 | 2023-06-05 21:40 | 25 | 1:27 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23060500545 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2023-06-05 | 2175 | keep | 0 | Jun | 2023 | 0.0014814 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-06-05 20:20 | 2023-06-06 09:53 | 47 | 13:33 | P | DESGANCHE | 1 X 30 Y DESGANCHE | B23060500479 | New_Event | Vegetation Contact | Include | Include | Vegetation | 813 | 2023-06-05 | 38211 | keep | 0 | Jun | 2023 | 0.026025 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
BAYAMON | 2023-06-05 20:25 | 2023-06-06 01:18 | 60 | 4:53 | P | DESGANCHE | 1 X 50 EN C/L SE DESGANCHO | B23060500557 | New_Event | Vegetation Contact | Include | Include | Vegetation | 293 | 2023-06-05 | 17580 | keep | 0 | Jun | 2023 | 0.011974 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2023-06-05 20:25 | 2023-06-06 00:04 | 125 | 3:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA POR LLUVIA | A23060500504 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 219 | 2023-06-05 | 27375 | keep | 0 | Jun | 2023 | 0.018645 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
ARECIBO | 2023-06-05 20:26 | 2023-06-05 21:46 | 80 | 1:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23060500467 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2023-06-05 | 6400 | keep | 0 | Jun | 2023 | 0.004359 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-06-05 20:33 | 2023-06-05 20:38 | 2658 | 0:05 | T | NO SE REPORTO CAUSA | DISAPRO DEL INTERRUPTOR SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR | M23060500524 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-06-05 | 13290 | keep | 0 | Jun | 2023 | 0.0090518 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-06-05 20:38 | 2023-06-06 12:15 | 150 | 15:37 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23060500529 | New_Event | Vegetation Contact | Include | Include | Vegetation | 937 | 2023-06-05 | 140550 | keep | 0 | Jun | 2023 | 0.095728 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-06-05 20:41 | 2023-06-05 23:48 | 75 | 3:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA AISLADOR PARTIDO | M23060500531 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 187 | 2023-06-05 | 14025 | keep | 0 | Jun | 2023 | 0.0095524 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2023-06-05 20:43 | 2023-06-05 22:45 | 100 | 2:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA POR VIENTO | A23060500483 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 122 | 2023-06-05 | 12200 | keep | 0 | Jun | 2023 | 0.0083094 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-06-05 20:43 | 2023-06-05 21:28 | 60 | 0:45 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23060500484 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 45 | 2023-06-05 | 2700 | keep | 0 | Jun | 2023 | 0.001839 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-06-05 20:44 | 2023-06-06 01:20 | 40 | 4:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEPLAZO MASETILLA | M23060500538 | New_Event | Cutout Failure | Include | Include | Equipment | 276 | 2023-06-05 | 11040 | keep | 0 | Jun | 2023 | 0.0075193 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-06-05 20:44 | 2023-06-06 09:15 | 100 | 12:31 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REQUIERE DESGANCHE | A23060500487 | New_Event | Vegetation Contact | Include | Include | Vegetation | 751 | 2023-06-05 | 75100 | keep | 0 | Jun | 2023 | 0.05115 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-06-05 20:45 | 2023-06-05 23:30 | 100 | 2:45 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23060500491 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 165 | 2023-06-05 | 16500 | keep | 0 | Jun | 2023 | 0.011238 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-06-05 20:48 | 2023-06-06 00:10 | 64 | 3:22 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | M23060500544 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2023-06-05 | 12928 | keep | 0 | Jun | 2023 | 0.0088052 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
AGUADILLA | 2023-06-05 20:48 | 2023-06-05 23:55 | 400 | 3:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 140 EN CORTE DE LINEA SE REEMPLAZARON DOS MASETILLAS DEFECTUOSAS | M23060500543 | New_Event | Cutout Failure | Include | Include | Equipment | 187 | 2023-06-05 | 74800 | keep | 0 | Jun | 2023 | 0.050946 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2023-06-05 20:52 | 2023-06-05 21:13 | 60 | 0:21 | P | CABLE SOTERRADO AVERIADO | AVERIA NUEVA DEL T-9 A RISER Y AVERIA VIEJA T-11 A RISER CABLE SOTERRADO AVERIADO SE CONSTRUYO PROVISIONAL AERIO SE TRABAJO CON GOI SJ-230605-02 | S23060500053 | New_Event | UG Cable Fault | Include | Include | Equipment | 21 | 2023-06-05 | 1260 | keep | 0 | Jun | 2023 | 0.00085818 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-06-05 20:52 | 2023-06-05 21:13 | 62 | 0:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN C/L SE REMPLAZO CAJA PRIMARIA QUEMADA | S23060500319 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 21 | 2023-06-05 | 1302 | keep | 0 | Jun | 2023 | 0.00088679 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-05 21:00 | 2023-06-05 23:00 | 40 | 2:00 | P | DESGANCHE | 1 X 80 EN C/L SE DESGANCHO | S23060500612 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2023-06-05 | 4800 | keep | 0 | Jun | 2023 | 0.0032693 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-06-05 21:07 | 2023-06-06 00:10 | 103 | 3:03 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R23060500287 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2023-06-05 | 18849 | keep | 0 | Jun | 2023 | 0.012838 | 7.0153e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 103
SAN JUAN | 2023-06-05 21:11 | 2023-06-06 02:52 | 484 | 5:41 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO POUENTE ABIERTO MEDIANTE GOI SJ-230606-01 | S23060500634 | New_Event | Primary Wire Break | Include | Include | Equipment | 341 | 2023-06-05 | 165044 | keep | 0 | Jun | 2023 | 0.11241 | 0.00032965 | Sustained | FALSE | FALSE | Not_TMED_Event | 484
SAN JUAN | 2023-06-05 21:13 | 2023-06-05 22:01 | 4944 | 0:48 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE RESETIARON BANDERAS DEL BREAKER SE PROBO POR CONTROL Y QUEDO EN SERVICIO SE TRABAJO CON SWF-230605-03 | S23060500644 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 48 | 2023-06-05 | 237312 | keep | 0 | Jun | 2023 | 0.16163 | 0.0033673 | Sustained | FALSE | FALSE | Not_TMED_Event | 4944
AGUADILLA | 2023-06-05 21:14 | 2023-06-05 21:52 | 2658 | 0:38 | T | NO SE REPORTO CAUSA | SE SECCIONALIZO ALIMENTADOR Y SE CERRO INTERRUPTOR | M23060500599 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 38 | 2023-06-05 | 101004 | keep | 0 | Jun | 2023 | 0.068793 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-06-05 21:16 | 2023-06-05 22:22 | 1798 | 1:06 | T | CONDUCTOR ROTO O ABIERTO | SE ABREN INTERRUPTOR POR MANIOBRAS DE AMARRES PUENTE ABIERTO, MACHETES AVERIADOS Y PUNTO CALIENTES | A23060500598 | New_Event | Primary Wire Break | Include | Include | Equipment | 66 | 2023-06-05 | 118668 | keep | 0 | Jun | 2023 | 0.080824 | 0.0012246 | Sustained | FALSE | FALSE | Not_TMED_Event | 1798
AGUADILLA | 2023-06-05 21:16 | 2023-06-06 20:59 | 150 | 23:43 | P | DESGANCHE | 2 X 50 Y 1 X 65 EN DISTINTOS CORTE DE LINEA SE REALIZO DESGANCHE | A23060500528 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1423 | 2023-06-05 | 213450 | keep | 0 | Jun | 2023 | 0.14538 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-06-05 21:18 | 2023-06-06 10:05 | 200 | 12:47 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23060500607 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 767 | 2023-06-05 | 153400 | keep | 0 | Jun | 2023 | 0.10448 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2023-06-05 21:22 | 2023-06-06 00:12 | 600 | 2:50 | T | CONDUCTOR ROTO O ABIERTO | LINEA PRIMARIA PARTIDA EN TRONCAL DE ALIMENTADOR | A2306000534 | New_Event | Primary Wire Break | Include | Include | Equipment | 170 | 2023-06-05 | 102000 | keep | 0 | Jun | 2023 | 0.069472 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
AGUADILLA | 2023-06-05 21:35 | 2023-06-06 01:05 | 40 | 3:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | M23060500620 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2023-06-05 | 8400 | keep | 0 | Jun | 2023 | 0.0057212 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-06-05 21:47 | 2023-06-05 21:48 | 2064 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1205-03 | S2306050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-05 | 2064 | keep | 0 | Jun | 2023 | 0.0014058 | 0.0014058 | Momentary | FALSE | FALSE | Not_TMED_Event | 2064
BAYAMON | 2023-06-05 21:48 | 2023-06-06 10:32 | 18 | 12:44 | P | DESGANCHE | 1 X 40 1 X 50 C/L Y DESGANCHE | B23060500537 | New_Event | Vegetation Contact | Include | Include | Vegetation | 764 | 2023-06-05 | 13752 | keep | 0 | Jun | 2023 | 0.0093664 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
VEGA BAJA | 2023-06-05 21:59 | 2023-06-06 11:43 | 13 | 13:44 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 10KVA @ 50KVA | B23060500521 | New_Event | Service Transformer Failure | Include | Include | Equipment | 824 | 2023-06-05 | 10712 | keep | 0 | Jun | 2023 | 0.0072959 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2023-06-05 22:01 | 2023-06-05 22:22 | 60 | 0:21 | P | CABLE SOTERRADO AVERIADO | AVERIA NUEVA DEL T-9 A RISER Y AVERIA VIEJA T-11 A RISER CABLE SOTERRADO AVERIADO SE CONSTRUYO PROVISIONAL AERIO SE TRABAJO CON GOI SJ-230605-02 | S23060500053 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 21 | 2023-06-05 | 1260 | keep | 0 | Jun | 2023 | 0.00085818 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-06-05 22:08 | 2023-06-06 01:32 | 26 | 3:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA 1 X 65 EN C/L | R23060500322 | New_Event | Cutout Failure | Include | Include | Equipment | 204 | 2023-06-05 | 5304 | keep | 0 | Jun | 2023 | 0.0036125 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
GUAYAMA | 2023-06-05 22:16 | 2023-06-05 23:17 | 1945 | 1:01 | T | POWER TRANSFORMER AVERIADO | SE RETIRA CARGA TRANSFORMADOR CON WINDING TEMP DEBIDO BOMBA DE CIRCULACION DE ACEITE AVERIADA | P23060500929 | New_Event | Power Transformer Failure | Include | Include | Equipment | 61 | 2023-06-05 | 118645 | keep | 0 | Jun | 2023 | 0.080809 | 0.0013247 | Sustained | FALSE | FALSE | Not_TMED_Event | 1945
CANOVANAS | 2023-06-05 22:18 | 2023-06-06 02:15 | 63 | 3:57 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | R23060500331 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 237 | 2023-06-05 | 14931 | keep | 0 | Jun | 2023 | 0.010169 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
HUMACAO | 2023-06-05 22:18 | 2023-06-06 00:27 | 150 | 2:09 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C23060500441 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 129 | 2023-06-05 | 19350 | keep | 0 | Jun | 2023 | 0.013179 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-06-05 22:22 | 2023-06-05 22:50 | 4944 | 0:28 | T | NO SE REPORTO CAUSA | SE TRANSFIRIO LA CARGA AL 1204-01 POR B.I. QUEDO EN SERVICIO SE TRABAJO CON SWF-230605-03 | S23060500644 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 28 | 2023-06-05 | 138432 | keep | 0 | Jun | 2023 | 0.094285 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-05 22:31 | 2023-06-06 08:54 | 25 | 10:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 C/L MAL TIEMPO VIENTO | B23060500565 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 623 | 2023-06-05 | 15575 | keep | 0 | Jun | 2023 | 0.010608 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-06-05 22:55 | 2023-06-05 23:41 | 50 | 0:46 | P | DESGANCHE | 2 X 50 EN C/L SE DESGANCHO | B23060500581 | New_Event | Vegetation Contact | Include | Include | Vegetation | 46 | 2023-06-05 | 2300 | keep | 0 | Jun | 2023 | 0.0015665 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-06-05 23:06 | 2023-06-06 01:41 | 100 | 2:35 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR VIENTOS | M23060500686 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 155 | 2023-06-05 | 15500 | keep | 0 | Jun | 2023 | 0.010557 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-06-05 23:09 | 2023-06-06 10:25 | 30 | 11:16 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | A23060500600 | New_Event | Vegetation Contact | Include | Include | Vegetation | 676 | 2023-06-05 | 20280 | keep | 0 | Jun | 2023 | 0.013813 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-06-05 23:15 | 2023-06-06 01:06 | 4944 | 1:51 | T | NO SE REPORTO CAUSA | SE TRANSFIRIO 50% DE LA CARGA AL 1204-01 POR B.I | S2306050000X | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 111 | 2023-06-05 | 548784 | keep | 0 | Jun | 2023 | 0.37377 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-06-05 23:30 | 2023-06-06 14:15 | 650 | 14:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 100, 3 X 80 Y 1 X 140 EN CORTES DE LINEA SE REMPLAZO DOS CAJAS PRIMARIAS AVERIADAS | M23060500700 | New_Event | Cutout Failure | Include | Include | Equipment | 885 | 2023-06-05 | 575250 | keep | 0 | Jun | 2023 | 0.3918 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
GUAYAMA | 2023-06-05 23:57 | 2023-06-06 01:53 | 4132 | 1:56 | T | POWER TRANSFORMER AVERIADO | SE RETIRA CARGA A TRANSFORMADOR POR ALARMA DE WINDING TEMP ACTIVADA BOMBA DE CIRCULACION SISTEMA DE ENFRIAMIENTO AVERIADA | P23060501005 | New_Event | Power Transformer Failure | Include | Include | Equipment | 116 | 2023-06-05 | 479312 | keep | 0 | Jun | 2023 | 0.32646 | 0.0028143 | Sustained | FALSE | FALSE | Not_TMED_Event | 4132
MAYAGÃœEZ | 2023-06-05 23:57 | 2023-06-06 00:42 | 8 | 0:45 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR POR AVES | P23060501003 | New_Event | Animals | Include | Include | Wildlife | 45 | 2023-06-05 | 360 | keep | 0 | Jun | 2023 | 0.00024519 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2023-06-06 00:12 | 2023-06-06 01:05 | 1720 | 0:53 | T | CONDUCTOR ROTO O ABIERTO | GOI-AR-2300605-01 SE ABRE INTERRUPTOR PARA REPARAR LINEA PRIMARIA PARTIDA EN TRONCAL DE ALIMENTADOR | A23060600004 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 53 | 2023-06-06 | 91160 | keep | 0 | Jun | 2023 | 0.062089 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-06-06 00:33 | 2023-06-06 00:34 | 1234 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R2306060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-06 | 1234 | keep | 0 | Jun | 2023 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
CANOVANAS | 2023-06-06 00:41 | 2023-06-06 00:42 | 424 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R2306060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-06 | 424 | keep | 0 | Jun | 2023 | 0.00028878 | 0.00028878 | Momentary | FALSE | FALSE | Not_TMED_Event | 424
SAN JUAN | 2023-06-06 01:06 | 2023-06-06 01:36 | 1236 | 0:30 | P | NO SE REPORTO CAUSA | SE TRANSFIRIO 25% AL 1204-05 | S2306050000X | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 30 | 2023-06-06 | 37080 | keep | 0 | Jun | 2023 | 0.025255 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-06 01:28 | 2023-06-06 04:49 | 60 | 3:21 | P | DESGANCHE | 1 X 80 EN C/L SE DESGANCHO | B23060600034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2023-06-06 | 12060 | keep | 0 | Jun | 2023 | 0.008214 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-06-06 01:36 | 2023-06-06 01:38 | 1236 | 0:02 | P | NO SE REPORTO CAUSA | SE TRANSFIRIO 25% AL 1303-02 X 1346-05 | S2306050000X | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-06 | 2472 | keep | 0 | Jun | 2023 | 0.0016837 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-06-06 02:18 | 2023-06-06 02:19 | 2216 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B2306060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-06 | 2216 | keep | 0 | Jun | 2023 | 0.0015093 | 0.0015093 | Momentary | FALSE | FALSE | Not_TMED_Event | 2216
BAYAMON | 2023-06-06 02:22 | 2023-06-06 03:05 | 60 | 0:43 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B23060600053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 43 | 2023-06-06 | 2580 | keep | 0 | Jun | 2023 | 0.0017572 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-06-06 02:52 | 2023-06-06 03:55 | 1452 | 1:03 | T | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO CON GOI SJ-230606-01 | S23060500634 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 63 | 2023-06-06 | 91476 | keep | 0 | Jun | 2023 | 0.062304 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-06 02:55 | 2023-06-06 10:04 | 81 | 7:09 | P | DESGANCHE | 1X80 EN C/L DESGANCHE | S23060600128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 429 | 2023-06-06 | 34749 | keep | 0 | Jun | 2023 | 0.023667 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
ARECIBO | 2023-06-06 03:30 | 2023-06-06 11:08 | 75 | 7:38 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REQUIERE DESGANCHE | A23060600061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 458 | 2023-06-06 | 34350 | keep | 0 | Jun | 2023 | 0.023396 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2023-06-06 03:47 | 2023-06-06 09:26 | 100 | 5:39 | P | DESGANCHE | 1 X 100 EN CL DESGANCHE | M23060600061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 339 | 2023-06-06 | 33900 | keep | 0 | Jun | 2023 | 0.023089 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-06-06 03:59 | 2023-06-06 09:00 | 1 | 5:01 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A23060600072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 301 | 2023-06-06 | 301 | keep | 0 | Jun | 2023 | 0.00020501 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-06-06 05:36 | 2023-06-06 05:37 | 449 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | P23060600101 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-06-06 | 449 | keep | 0 | Jun | 2023 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
BAYAMON | 2023-06-06 06:12 | 2023-06-06 06:13 | 1784 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DEL 1801-02 CERRADO POR CONTROL 90 % POR 1801-02 | B2306060000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-06 | 1784 | keep | 0 | Jun | 2023 | 0.0012151 | 0.0012151 | Momentary | FALSE | FALSE | Not_TMED_Event | 1784
BAYAMON | 2023-06-06 06:12 | 2023-06-06 06:13 | 453 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1801-02 CERRADO POR CONTROL 10% POR 1801-02 | B2306060000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-06 | 453 | keep | 0 | Jun | 2023 | 0.00030854 | 0.00030854 | Momentary | FALSE | FALSE | Not_TMED_Event | 453
BAYAMON | 2023-06-06 06:12 | 2023-06-06 06:13 | 186 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL LLEVA 90% 1711-04 LLEVA 10% 1717-01 | B2306060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-06 | 186 | keep | 0 | Jun | 2023 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
AGUADILLA | 2023-06-06 06:20 | 2023-06-06 09:45 | 80 | 3:25 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23060600109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2023-06-06 | 16400 | keep | 0 | Jun | 2023 | 0.01117 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2023-06-06 06:28 | 2023-06-06 11:40 | 125 | 5:12 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO | M23060600110 | New_Event | Primary Wire Break | Include | Include | Equipment | 312 | 2023-06-06 | 39000 | keep | 0 | Jun | 2023 | 0.026563 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2023-06-06 06:30 | 2023-06-06 18:49 | 14 | 12:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | B23060600103 | New_Event | Secondary Wire Break | Include | Include | Equipment | 739 | 2023-06-06 | 10346 | keep | 0 | Jun | 2023 | 0.0070466 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CANOVANAS | 2023-06-06 06:33 | 2023-06-06 10:28 | 15 | 3:55 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R23060600075 | New_Event | Animals | Include | Include | Wildlife | 235 | 2023-06-06 | 3525 | keep | 0 | Jun | 2023 | 0.0024009 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-06-06 06:39 | 2023-06-06 09:37 | 81 | 2:58 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | S23060600128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 178 | 2023-06-06 | 14418 | keep | 0 | Jun | 2023 | 0.00982 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
CANOVANAS | 2023-06-06 07:12 | 2023-06-06 07:14 | 172 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S23060600240 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-06 | 344 | keep | 0 | Jun | 2023 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
MAYAGÃœEZ | 2023-06-06 07:18 | 2023-06-06 17:15 | 3 | 9:57 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA | M23060600123 | New_Event | Service Transformer Failure | Include | Include | Equipment | 597 | 2023-06-06 | 1791 | keep | 0 | Jun | 2023 | 0.0012198 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2023-06-06 07:25 | 2023-06-06 13:05 | 1 | 5:40 | P | NO SE REPORTO CAUSA | 1X 30 EN C/L | B23060600113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 340 | 2023-06-06 | 340 | keep | 0 | Jun | 2023 | 0.00023157 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-06-06 07:28 | 2023-06-06 11:08 | 97 | 3:40 | P | NO SE REPORTO CAUSA | 1X80 EN C/L | S23060600244 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 220 | 2023-06-06 | 21340 | keep | 0 | Jun | 2023 | 0.014535 | 6.6066e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 97
CAGUAS | 2023-06-06 07:31 | 2023-06-06 09:19 | 7 | 1:48 | P | SECUNDARIA/DESGANCHE | 1X 15 EN XMR DESGANCHE EN SECUNDARIA | C23060600132 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 108 | 2023-06-06 | 756 | keep | 0 | Jun | 2023 | 0.00051491 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-06-06 07:36 | 2023-06-06 07:38 | 2052 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1111-01 20% DE SU CARGA POR EL 1118-10 LLEVA LA CARGA DEL 1115-03 SE CERRO POR CONTROL | S23060600246 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-06 | 4104 | keep | 0 | Jun | 2023 | 0.0027952 | 0.0013976 | Momentary | FALSE | FALSE | Not_TMED_Event | 2052
SAN JUAN | 2023-06-06 07:36 | 2023-06-06 07:38 | 134 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1111-01 20% DE SU CARGA POR EL 1118-10 LLEVA LA CARGA DEL 1115-03 SE CERRO POR CONTROL | S23060600246 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-06-06 | 268 | keep | 0 | Jun | 2023 | 0.00018253 | 9.1267e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 134
CAGUAS | 2023-06-06 07:37 | 2023-06-06 18:42 | 52 | 11:05 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | C23060600136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 665 | 2023-06-06 | 34580 | keep | 0 | Jun | 2023 | 0.023552 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
CAGUAS | 2023-06-06 07:38 | 2023-06-06 10:43 | 90 | 3:05 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23060600137 | New_Event | Animals | Include | Include | Wildlife | 185 | 2023-06-06 | 16650 | keep | 0 | Jun | 2023 | 0.01134 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2023-06-06 07:39 | 2023-06-06 13:53 | 20 | 6:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO EN C/L Y SE REMPLAZO CAJA PRIMARIA NO FUNDIO | S23060600239 | New_Event | Cutout Failure | Include | Include | Equipment | 374 | 2023-06-06 | 7480 | keep | 0 | Jun | 2023 | 0.0050946 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-06-06 07:41 | 2023-06-06 12:10 | 4 | 4:29 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | P23060600144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 269 | 2023-06-06 | 1076 | keep | 0 | Jun | 2023 | 0.00073286 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2023-06-06 07:52 | 2023-06-06 11:45 | 1 | 3:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO VIENTOS FUERTES | P23060600149 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 233 | 2023-06-06 | 233 | keep | 0 | Jun | 2023 | 0.0001587 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-06-06 08:00 | 2023-06-06 19:38 | 50 | 11:38 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | B23060600021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 698 | 2023-06-06 | 34900 | keep | 0 | Jun | 2023 | 0.02377 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-06-06 08:12 | 2023-06-06 13:24 | 4 | 5:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C23060600151 | New_Event | Secondary Wire Break | Include | Include | Equipment | 312 | 2023-06-06 | 1248 | keep | 0 | Jun | 2023 | 0.00085001 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2023-06-06 08:17 | 2023-06-06 10:26 | 1245 | 2:09 | T | CRUCETA DEFECTUOSA O AVERIADA | SE SECCIONALIZO ALIMENTADOR CRUCETA PARTIDA EN TRONCAL DEL ALIMENTADOR | M23060600148 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 129 | 2023-06-06 | 160605 | keep | 0 | Jun | 2023 | 0.10939 | 0.00084796 | Sustained | FALSE | FALSE | Not_TMED_Event | 1245
UTUADO | 2023-06-06 08:31 | 2023-06-06 13:25 | 4 | 4:54 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 10 EN TRANSFORMADOR SE REMPLAZO BAJANTES SECUNDARIOS CRUZADOS | A23060600144 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 294 | 2023-06-06 | 1176 | keep | 0 | Jun | 2023 | 0.00080097 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-06-06 08:33 | 2023-06-06 12:00 | 1 | 3:27 | P | DESGANCHE | 1 X 25 EN C/L Y DESGANCHE | B23060600135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2023-06-06 | 207 | keep | 0 | Jun | 2023 | 0.00014099 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-06-06 08:35 | 2023-06-06 12:50 | 25 | 4:15 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN DISTINTOS CORTES DE LINEA SE REQUIERE DESGANCHE | A23060600146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 255 | 2023-06-06 | 6375 | keep | 0 | Jun | 2023 | 0.004342 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-06-06 08:39 | 2023-06-06 20:21 | 205 | 11:42 | P | DESGANCHE | SE ABRIO C/L POR DESGANCHE MASIVO | C23060600158 | New_Event | Vegetation Contact | Include | Include | Vegetation | 702 | 2023-06-06 | 143910 | keep | 0 | Jun | 2023 | 0.098016 | 0.00013962 | Sustained | FALSE | FALSE | Not_TMED_Event | 205
BARRANQUITAS | 2023-06-06 08:41 | 2023-06-06 11:40 | 4 | 2:59 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | P23060600175 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 179 | 2023-06-06 | 716 | keep | 0 | Jun | 2023 | 0.00048766 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-06-06 09:00 | 2023-06-06 11:00 | 40 | 2:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X80 EN C/L SE REMPLAZO CAJA PRIMARIA | S23060600265 | New_Event | Cutout Failure | Include | Include | Equipment | 120 | 2023-06-06 | 4800 | keep | 0 | Jun | 2023 | 0.0032693 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-06-06 09:00 | 2023-06-06 10:25 | 20 | 1:25 | P | CAUSAS EXTERNAS | SE ABRIO XMR PARA REPARAR PEDESTAL SECUNDARIO Y SECUNDARIA A CAUSA DE ESCAVADORA IMPACTO EL PEDESTAL | C23060600165 | New_Event | Damage From Public | Include | Include | Public | 85 | 2023-06-06 | 1700 | keep | 0 | Jun | 2023 | 0.0011579 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2023-06-06 09:02 | 2023-06-06 11:25 | 30 | 2:23 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBU DE LAS LINEAS | P23060600180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2023-06-06 | 4290 | keep | 0 | Jun | 2023 | 0.0029219 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-06-06 09:05 | 2023-06-06 15:25 | 1 | 6:20 | P | DESGANCHE | 1 X 65 EN RISER DESGANCHE | P23060600402 | New_Event | Vegetation Contact | Include | Include | Vegetation | 380 | 2023-06-06 | 380 | keep | 0 | Jun | 2023 | 0.00025882 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-06-06 09:06 | 2023-06-06 14:48 | 30 | 5:42 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | B23060600261 | New_Event | Animals | Include | Include | Wildlife | 342 | 2023-06-06 | 10260 | keep | 0 | Jun | 2023 | 0.006988 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-06-06 09:07 | 2023-06-06 13:45 | 1 | 4:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE SECCIONALIZO LINEA SECUNDARIA ROTA | A23060600156 | New_Event | Secondary Wire Break | Include | Include | Equipment | 278 | 2023-06-06 | 278 | keep | 0 | Jun | 2023 | 0.00018934 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-06-06 09:09 | 2023-06-06 14:23 | 60 | 5:14 | P | CONDUCTOR ROTO O ABIERTO | 3 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A23060600157 | New_Event | Primary Wire Break | Include | Include | Equipment | 314 | 2023-06-06 | 18840 | keep | 0 | Jun | 2023 | 0.012832 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-06-06 09:18 | 2023-06-06 13:40 | 30 | 4:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CL FUERTE VIENTO | M23060600185 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 262 | 2023-06-06 | 7860 | keep | 0 | Jun | 2023 | 0.0053534 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2023-06-06 09:30 | 2023-06-06 09:31 | 3718 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23060600201 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-06 | 3718 | keep | 0 | Jun | 2023 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
ARECIBO | 2023-06-06 09:37 | 2023-06-06 09:39 | 2201 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 | A23060600182 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-06 | 4402 | keep | 0 | Jun | 2023 | 0.0029982 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2023-06-06 09:37 | 2023-06-06 09:39 | 1986 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 | A23060600182 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-06 | 3972 | keep | 0 | Jun | 2023 | 0.0027053 | 0.0013527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1986
ARECIBO | 2023-06-06 09:37 | 2023-06-06 09:39 | 199 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 | A23060600182 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-06 | 398 | keep | 0 | Jun | 2023 | 0.00027108 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2023-06-06 09:37 | 2023-06-06 09:39 | 24 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 | A23060600182 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-06 | 48 | keep | 0 | Jun | 2023 | 3.2693e-05 | 1.6346e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 24
SAN JUAN | 2023-06-06 09:51 | 2023-06-06 12:33 | 1236 | 2:42 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR 1204-01 LLEVA SOLO 50% DEL 1204-04 SE SECCIONALIZO PARA REMPLAZAR POR DISCO PRIMARIO PARTIDO SJ-230605-03 - EN SERVICIO 20% DEL 1204-04 | S23060600284 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 162 | 2023-06-06 | 200232 | keep | 0 | Jun | 2023 | 0.13638 | 0.00084183 | Sustained | FALSE | FALSE | Not_TMED_Event | 1236
FAJARDO | 2023-06-06 09:52 | 2023-06-06 10:07 | 1 | 0:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN RISER SE REEMPLAZO PORTAFUSIBLE | R23060600098 | New_Event | Cutout Failure | Include | Include | Equipment | 15 | 2023-06-06 | 15 | keep | 0 | Jun | 2023 | 1.0216e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-06-06 10:00 | 2023-06-06 10:55 | 15 | 0:55 | P | DESGANCHE | 1 X 65 EN C/L Y DESGANCHE | S23060600250 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2023-06-06 | 825 | keep | 0 | Jun | 2023 | 0.0005619 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-06-06 10:02 | 2023-06-07 13:08 | 55 | 27:06 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23060600198 | New_Event | Animals | Include | Include | Wildlife | 1626 | 2023-06-06 | 89430 | keep | 0 | Jun | 2023 | 0.06091 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CAGUAS | 2023-06-06 10:12 | 2023-06-06 12:42 | 43 | 2:30 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23060600201 | New_Event | Animals | Include | Include | Wildlife | 150 | 2023-06-06 | 6450 | keep | 0 | Jun | 2023 | 0.0043931 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
MAYAGÃœEZ | 2023-06-06 10:12 | 2023-06-06 13:10 | 2 | 2:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR FUERTES VIENTOS | P23060600237 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 178 | 2023-06-06 | 356 | keep | 0 | Jun | 2023 | 0.00024247 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2023-06-06 10:13 | 2023-06-06 11:29 | 2720 | 1:16 | T | ANIMAL | SE ABRIO MACHETES PARA SECCIONALIZAR Y SE CERRO EL INTERRUPTOR SE CONTINUA PATRULLANDO, EN REUNION SEMANAL COMENTARON PARTE DE CULEBRA EN POSTE | A23060600190 | New_Event | Animals | Include | Include | Wildlife | 76 | 2023-06-06 | 206720 | keep | 0 | Jun | 2023 | 0.1408 | 0.0018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 2720
FAJARDO | 2023-06-06 10:14 | 2023-06-06 10:55 | 5 | 0:41 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | P23060600238 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 41 | 2023-06-06 | 205 | keep | 0 | Jun | 2023 | 0.00013962 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2023-06-06 10:20 | 2023-06-06 14:05 | 1 | 3:45 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | M23060600219 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2023-06-06 | 225 | keep | 0 | Jun | 2023 | 0.00015325 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-06-06 10:26 | 2023-06-06 13:13 | 800 | 2:47 | P | CRUCETA DEFECTUOSA O AVERIADA | SE SECCIONALIZO CRUCETA PARTIDA SE CERRO MACHETES | M23060600223 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 167 | 2023-06-06 | 133600 | keep | 0 | Jun | 2023 | 0.090994 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
BAYAMON | 2023-06-06 10:32 | 2023-06-06 11:44 | 25 | 1:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN XMR SE REEMPLAZO PORTAFUSIBLE QUEMADO | B23060600136 | New_Event | Cutout Failure | Include | Include | Equipment | 72 | 2023-06-06 | 1800 | keep | 0 | Jun | 2023 | 0.001226 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-06-06 10:49 | 2023-06-06 14:04 | 4 | 3:15 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 15KVA X 15KVA (EVENTO TRANSFERIDO DE REGION PONCE) | P23060600152 | New_Event | Service Transformer Failure | Include | Include | Equipment | 195 | 2023-06-06 | 780 | keep | 0 | Jun | 2023 | 0.00053125 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-06-06 10:50 | 2023-06-06 13:58 | 122 | 3:08 | P | NO SE REPORTO CAUSA | 1X80 EN C/L | S23060600319 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 188 | 2023-06-06 | 22936 | keep | 0 | Jun | 2023 | 0.015622 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
CANOVANAS | 2023-06-06 10:50 | 2023-06-06 13:07 | 120 | 2:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN RISER SE REEMPLAZO 2 CAJAS PRIMARIAS | R23060600103 | New_Event | Cutout Failure | Include | Include | Equipment | 137 | 2023-06-06 | 16440 | keep | 0 | Jun | 2023 | 0.011197 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CAGUAS | 2023-06-06 11:00 | 2023-06-06 12:20 | 65 | 1:20 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN C/L SE LEVANTO CONDUCTOR PRIMARIO EVENTO TRANSFERIDO | P23060600264 | New_Event | Primary Wire Break | Include | Include | Equipment | 80 | 2023-06-06 | 5200 | keep | 0 | Jun | 2023 | 0.0035417 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BARRANQUITAS | 2023-06-06 11:02 | 2023-06-06 11:52 | 5 | 0:50 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR PARA SE REPARO BUSHING SECUNDARIOS | C23060600216 | New_Event | Service Transformer Failure | Include | Include | Equipment | 50 | 2023-06-06 | 250 | keep | 0 | Jun | 2023 | 0.00017027 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-06-06 11:27 | 2023-06-06 13:39 | 72 | 2:12 | P | DESGANCHE | 1 X 30 C/L Y DESGANCHE | B23060600172 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2023-06-06 | 9504 | keep | 0 | Jun | 2023 | 0.0064731 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
ARECIBO | 2023-06-06 11:29 | 2023-06-06 13:00 | 1153 | 1:31 | P | ANIMAL | SE ABRIO MACHETES Y SE CERRO LOS MACHETES QUE SE HABIAN ABIERTO ANTERIORMENTE SE CONTINUA PATRULLANDO, EN REUNION SEMANAL COMENTARON PARTE DE CULEBRA EN POSTE | A23060600217 | Partial_restoration | Animals | Include | Include | Wildlife | 91 | 2023-06-06 | 104923 | keep | 0 | Jun | 2023 | 0.071463 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-06-06 11:32 | 2023-06-06 14:00 | 1 | 2:28 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | C23060600224 | New_Event | Animals | Include | Include | Wildlife | 148 | 2023-06-06 | 148 | keep | 0 | Jun | 2023 | 0.0001008 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-06-06 11:50 | 2023-06-06 20:01 | 6 | 8:11 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE XMR 15KVA X 50KVA | P23060600293 | New_Event | Service Transformer Failure | Include | Include | Equipment | 491 | 2023-06-06 | 2946 | keep | 0 | Jun | 2023 | 0.0020065 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-06-06 11:55 | 2023-06-06 14:02 | 112 | 2:07 | P | DESGANCHE | 1X80 EN C/L DESGANCHE | S23060600350 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2023-06-06 | 14224 | keep | 0 | Jun | 2023 | 0.0096879 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
CANOVANAS | 2023-06-06 11:57 | 2023-06-06 15:39 | 30 | 3:42 | P | DESGANCHE | 1 X 30 EN C/L | R23060600109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2023-06-06 | 6660 | keep | 0 | Jun | 2023 | 0.0045361 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2023-06-06 11:58 | 2023-06-06 16:24 | 1 | 4:26 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA PRIMARIA | P23060600295 | New_Event | Primary Wire Break | Include | Include | Equipment | 266 | 2023-06-06 | 266 | keep | 0 | Jun | 2023 | 0.00018117 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-06-06 12:01 | 2023-06-06 18:00 | 60 | 5:59 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23060600257 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 359 | 2023-06-06 | 21540 | keep | 0 | Jun | 2023 | 0.014671 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-06-06 12:04 | 2023-06-06 13:54 | 32 | 1:50 | P | DESGANCHE | 1 X 20 C/L Y DESGANCHE | B23060600181 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2023-06-06 | 3520 | keep | 0 | Jun | 2023 | 0.0023975 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
BARRANQUITAS | 2023-06-06 12:11 | 2023-06-06 19:49 | 2 | 7:38 | P | CONDUCTOR ROTO O ABIERTO | SE REEMPLAZO BAJANTE DE LINEA Y SE ENERGIZO | P23060600302 | New_Event | Primary Wire Break | Include | Include | Equipment | 458 | 2023-06-06 | 916 | keep | 0 | Jun | 2023 | 0.00062388 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-06-06 12:20 | 2023-06-06 12:21 | 2067 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23060600268 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-06 | 2067 | keep | 0 | Jun | 2023 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
SAN JUAN | 2023-06-06 12:33 | 2023-06-06 15:16 | 1393 | 2:43 | P | AISLADOR ROTO, PARTIDO O SAFADO | LLEVA SOLO 50% DEL 1204-04 SE REMPLAZO DISCO PRIMARIO PARTIDO SJ-230605-03 - EN SERVICIO TOTAL EL 30% QUE FALTABA POR ENTRAR DEL 1204-04 | S23060600284 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 163 | 2023-06-06 | 227059 | keep | 0 | Jun | 2023 | 0.15465 | 0.00094877 | Sustained | FALSE | FALSE | Not_TMED_Event | 1393
FAJARDO | 2023-06-06 12:46 | 2023-06-06 13:29 | 158 | 0:43 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | R23060600114 | New_Event | Animals | Include | Include | Wildlife | 43 | 2023-06-06 | 6794 | keep | 0 | Jun | 2023 | 0.0046274 | 0.00010761 | Sustained | FALSE | FALSE | Not_TMED_Event | 158
AGUADILLA | 2023-06-06 12:47 | 2023-06-06 19:35 | 3309 | 6:48 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR PARA REPARAR PUENTE PRIMARIO ABIERTO EN LA SALIDA DEL ALIMENTADOR | A23060600230 | New_Event | Primary Wire Break | Include | Include | Equipment | 408 | 2023-06-06 | 1350072 | keep | 0 | Jun | 2023 | 0.91953 | 0.0022537 | Sustained | FALSE | FALSE | Not_TMED_Event | 3309
AGUADILLA | 2023-06-06 12:47 | 2023-06-06 19:35 | 713 | 6:48 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR PARA CORREGIR PUNTO CALIENTE EN LOS MACHETES DE BARRA DE INSPECCION | A23060600230 | New_Event | Primary Wire Break | Include | Include | Equipment | 408 | 2023-06-06 | 290904 | keep | 0 | Jun | 2023 | 0.19813 | 0.00048562 | Sustained | FALSE | FALSE | Not_TMED_Event | 713
GUAYAMA | 2023-06-06 12:49 | 2023-06-06 12:50 | 527 | 0:01 | T | ANIMAL | RECIERRE | P23060600312 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-06-06 | 527 | keep | 0 | Jun | 2023 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
GUAYAMA | 2023-06-06 12:50 | 2023-06-06 16:09 | 1 | 3:19 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA AVE | P23060600322 | 1st_after_momentary | Animals | Include | Include | Wildlife | 199 | 2023-06-06 | 199 | keep | 0 | Jun | 2023 | 0.00013554 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-06-06 12:51 | 2023-06-06 14:04 | 10 | 1:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR CONECTORES SECUNDARIOS | C23060600238 | New_Event | Secondary Wire Break | Include | Include | Equipment | 73 | 2023-06-06 | 730 | keep | 0 | Jun | 2023 | 0.0004972 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-06-06 12:54 | 2023-06-06 12:55 | 58 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23060600368 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-06 | 58 | keep | 0 | Jun | 2023 | 3.9504e-05 | 3.9504e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 58
ARECIBO | 2023-06-06 13:00 | 2023-06-06 14:10 | 804 | 1:10 | P | ANIMAL | SE CERRO LOS MACHETES QUE SE HABIAN ABIERTO ANTERIORMENTE Y QUEDO TODO EN SERVICIO NO SE ENCONTRO CAUSA PARA EL DISPARO DEL INTERRUPTOR, EN REUNION SEMANAL COMENTARON PARTE DE CULEBRA EN POSTE | A23060600238 | Partial_restoration | Animals | Include | Include | Wildlife | 70 | 2023-06-06 | 56280 | keep | 0 | Jun | 2023 | 0.038332 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-06-06 13:02 | 2023-06-06 17:40 | 1 | 4:38 | P | ANIMAL | 1 X 20 EN C/L CRUCE X AVE | P23060600318 | New_Event | Animals | Include | Include | Wildlife | 278 | 2023-06-06 | 278 | keep | 0 | Jun | 2023 | 0.00018934 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-06-06 13:05 | 2023-06-06 15:00 | 10 | 1:55 | P | DESGANCHE | 1 X 20 EN XMR SE RETIRO ENDADERA EVENTO TRANSFERIDO | P23060600320 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2023-06-06 | 1150 | keep | 0 | Jun | 2023 | 0.00078326 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-06-06 13:07 | 2023-06-06 13:56 | 9 | 0:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CL Y SE REMPLAZO CAJA PRIMARIA QUEMADA | B23060600194 | New_Event | Cutout Failure | Include | Include | Equipment | 49 | 2023-06-06 | 441 | keep | 0 | Jun | 2023 | 0.00030036 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2023-06-06 13:13 | 2023-06-06 19:22 | 10 | 6:09 | P | CRUCETA DEFECTUOSA O AVERIADA | SE REMPLAZO CRUCETA PARTIDA Y SE CERRO PUENTES | M23060600288 | Partial_restoration | Primary Crossarm Failure | Include | Include | Equipment | 369 | 2023-06-06 | 3690 | keep | 0 | Jun | 2023 | 0.0025132 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-06 13:19 | 2023-06-06 13:20 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S2306060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-06 | 45 | keep | 0 | Jun | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2023-06-06 13:25 | 2023-06-06 14:05 | 250 | 0:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M23060600259 | New_Event | Cutout Failure | Include | Include | Equipment | 40 | 2023-06-06 | 10000 | keep | 0 | Jun | 2023 | 0.006811 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2023-06-06 13:33 | 2023-06-06 16:51 | 106 | 3:18 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO DE LINEA @ CAJA EN C/L (RADIAL) | S23060600381 | New_Event | Primary Wire Break | Include | Include | Equipment | 198 | 2023-06-06 | 20988 | keep | 0 | Jun | 2023 | 0.014295 | 7.2196e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 106
HUMACAO | 2023-06-06 13:35 | 2023-06-06 14:04 | 40 | 0:29 | P | ANIMAL | 1 X 80 EN SMU-20 EN SU-AD6 CRUCE X IGUANA | C23060600252 | New_Event | Animals | Include | Include | Wildlife | 29 | 2023-06-06 | 1160 | keep | 0 | Jun | 2023 | 0.00079007 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-06-06 13:36 | 2023-06-06 13:43 | 2126 | 0:07 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL SE VERIFICO PERSONAL FUERA | C23060600253 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2023-06-06 | 14882 | keep | 0 | Jun | 2023 | 0.010136 | 0.001448 | Sustained | FALSE | FALSE | Not_TMED_Event | 2126
UTUADO | 2023-06-06 13:44 | 2023-06-06 17:30 | 2 | 3:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA PARTIDA RELACIONADO A EVENTO A23060200179 | P23060600339 | New_Event | Secondary Wire Break | Include | Include | Equipment | 226 | 2023-06-06 | 452 | keep | 0 | Jun | 2023 | 0.00030786 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2023-06-06 13:45 | 2023-06-06 14:30 | 8 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA ROTA | A23060600225 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2023-06-06 | 360 | keep | 0 | Jun | 2023 | 0.00024519 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2023-06-06 13:47 | 2023-06-06 20:00 | 50 | 6:13 | P | CAUSAS EXTERNAS | 1 X 40 EN CONVERTIDOR PERSONAL DE CLARO IMPACTO POSTE CAUSANDO CRUCE DE LINEAS | A23060600247 | New_Event | Damage From Public | Include | Include | Public | 373 | 2023-06-06 | 18650 | keep | 0 | Jun | 2023 | 0.012702 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-06-06 13:50 | 2023-06-06 15:19 | 10 | 1:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23060600200 | New_Event | Secondary Wire Break | Include | Include | Equipment | 89 | 2023-06-06 | 890 | keep | 0 | Jun | 2023 | 0.00060617 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2023-06-06 14:00 | 2023-06-06 16:00 | 1 | 2:00 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REQUIERE DESGANCHE | A23060600263 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2023-06-06 | 120 | keep | 0 | Jun | 2023 | 8.1731e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-06-06 14:01 | 2023-06-06 14:02 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S2306060000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-06 | 45 | keep | 0 | Jun | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-06-06 14:04 | 2023-06-06 20:39 | 277 | 6:35 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23060600204 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 395 | 2023-06-06 | 109415 | keep | 0 | Jun | 2023 | 0.074522 | 0.00018866 | Sustained | FALSE | FALSE | Not_TMED_Event | 277
SAN JUAN | 2023-06-06 14:12 | 2023-06-06 14:23 | 4 | 0:11 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 15KVA X 15KVA (EVENTO TRANSFERIDO DE REGION PONCE) | P23060600152 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 11 | 2023-06-06 | 44 | keep | 0 | Jun | 2023 | 2.9968e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-06-06 14:12 | 2023-06-06 14:23 | 10 | 0:11 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR CONECTORES SECUNDARIOS | C23060600238 | Partial_restoration | Secondary Wire Break | Include | Include | Equipment | 11 | 2023-06-06 | 110 | keep | 0 | Jun | 2023 | 7.492e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-06-06 14:15 | 2023-06-06 14:23 | 40 | 0:08 | P | ANIMAL | 1 X 80 EN SMU-20 EN SU-AD6 CRUCE X IGUANA | C23060600252 | Partial_restoration | Animals | Include | Include | Wildlife | 8 | 2023-06-06 | 320 | keep | 0 | Jun | 2023 | 0.00021795 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-06 14:27 | 2023-06-06 14:31 | 4 | 0:04 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 15KVA X 15KVA (EVENTO TRANSFERIDO DE REGION PONCE) | P23060600152 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 4 | 2023-06-06 | 16 | keep | 0 | Jun | 2023 | 1.0898e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-06-06 14:28 | 2023-06-06 15:32 | 10 | 1:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR CONECTORES SECUNDARIOS | C23060600238 | Partial_restoration | Secondary Wire Break | Include | Include | Equipment | 64 | 2023-06-06 | 640 | keep | 0 | Jun | 2023 | 0.0004359 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-06-06 14:42 | 2023-06-06 18:40 | 60 | 3:58 | P | CONDUCTOR ROTO O ABIERTO | 3 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A23060600157 | New_Event | Primary Wire Break | Include | Include | Equipment | 238 | 2023-06-06 | 14280 | keep | 0 | Jun | 2023 | 0.009726 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-06-06 14:47 | 2023-06-06 16:55 | 1 | 2:08 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO SE REPORTO CAUSA | M23060600326 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 128 | 2023-06-06 | 128 | keep | 0 | Jun | 2023 | 8.718e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-06-06 14:49 | 2023-06-06 17:20 | 40 | 2:31 | P | ANIMAL | 1 X 80 EN SMU-20 EN SU-AD6 CRUCE X IGUANA | C23060600252 | Partial_restoration | Animals | Include | Include | Wildlife | 151 | 2023-06-06 | 6040 | keep | 0 | Jun | 2023 | 0.0041138 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-06-06 14:49 | 2023-06-06 21:13 | 200 | 6:24 | P | CONDUCTOR ROTO O ABIERTO | 3 X 50 EN C/L SE LLEVANTO CONDUCTOR PRIMARIO | C23060600335 | New_Event | Primary Wire Break | Include | Include | Equipment | 384 | 2023-06-06 | 76800 | keep | 0 | Jun | 2023 | 0.052308 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
GUAYAMA | 2023-06-06 14:54 | 2023-06-06 18:03 | 25 | 3:09 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P23060600395 | New_Event | Vegetation Contact | Include | Include | Vegetation | 189 | 2023-06-06 | 4725 | keep | 0 | Jun | 2023 | 0.0032182 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-06-06 15:00 | 2023-06-07 08:40 | 43 | 17:40 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | B23060600268 | New_Event | Animals | Include | Include | Wildlife | 1060 | 2023-06-06 | 45580 | keep | 0 | Jun | 2023 | 0.031044 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
BARRANQUITAS | 2023-06-06 15:00 | 2023-06-06 15:07 | 2280 | 0:07 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C2306060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2023-06-06 | 15960 | keep | 0 | Jun | 2023 | 0.01087 | 0.0015529 | Sustained | FALSE | FALSE | Not_TMED_Event | 2280
BAYAMON | 2023-06-06 15:01 | 2023-06-06 15:02 | 959 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1904-07 LLEVA 100% 1901-04 LLEVA 100% 1901-01 Y LLEVA 10% 1901-05 | B2306060000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-06 | 959 | keep | 0 | Jun | 2023 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-06-06 15:01 | 2023-06-06 15:02 | 1264 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1904-07 LLEVA 100% 1901-04 LLEVA 100% 1901-01 Y LLEVA 10% 1901-05 | B2306060000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-06 | 1264 | keep | 0 | Jun | 2023 | 0.0008609 | 0.0008609 | Momentary | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2023-06-06 15:01 | 2023-06-06 15:02 | 62 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1904-07 LLEVA 100% 1901-04 LLEVA 100% 1901-01 Y LLEVA 10% 1901-05 | B2306060000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-06 | 62 | keep | 0 | Jun | 2023 | 4.2228e-05 | 4.2228e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 62
AGUADILLA | 2023-06-06 15:05 | 2023-06-06 18:20 | 60 | 3:15 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO ALAMBRE PARTIDO Y SE CERRO CORTE DE LINEA | M23060600336 | New_Event | Primary Wire Break | Include | Include | Equipment | 195 | 2023-06-06 | 11700 | keep | 0 | Jun | 2023 | 0.0079688 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2023-06-06 15:16 | 2023-06-06 17:20 | 50 | 2:04 | P | DESGANCHE | 1 X 50 Y 1 X 65 EN DISTINTOS CORTES DE LINEA SE REQUIERE DESGANCHE | A23060600271 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2023-06-06 | 6200 | keep | 0 | Jun | 2023 | 0.0042228 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-06-06 15:23 | 2023-06-06 17:37 | 10 | 2:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C23060600372 | New_Event | Secondary Wire Break | Include | Include | Equipment | 134 | 2023-06-06 | 1340 | keep | 0 | Jun | 2023 | 0.00091267 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-06-06 15:24 | 2023-06-06 17:39 | 3 | 2:15 | P | ANIMAL | 1X15 EN XMR POR CULEBRA (SERPIENTE) EN LA LINEA | S23060600641 | New_Event | Animals | Include | Include | Wildlife | 135 | 2023-06-06 | 405 | keep | 0 | Jun | 2023 | 0.00027584 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2023-06-06 15:31 | 2023-06-06 16:04 | 6 | 0:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C23060600388 | New_Event | Secondary Wire Break | Include | Include | Equipment | 33 | 2023-06-06 | 198 | keep | 0 | Jun | 2023 | 0.00013486 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2023-06-06 15:58 | 2023-06-06 19:42 | 14 | 3:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA LEVANTAR SECUNDARIA | R23060600260 | New_Event | Secondary Wire Break | Include | Include | Equipment | 224 | 2023-06-06 | 3136 | keep | 0 | Jun | 2023 | 0.0021359 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
PONCE | 2023-06-06 16:04 | 2023-06-06 18:22 | 100 | 2:18 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO Y SE CERRO CORTE DE LINEA | P23060600453 | New_Event | Primary Wire Break | Include | Include | Equipment | 138 | 2023-06-06 | 13800 | keep | 0 | Jun | 2023 | 0.0093991 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-06-06 16:07 | 2023-06-07 07:06 | 45 | 14:59 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | C23060600439 | New_Event | Animals | Include | Include | Wildlife | 899 | 2023-06-06 | 40455 | keep | 0 | Jun | 2023 | 0.027554 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-06-06 16:18 | 2023-06-07 15:38 | 52 | 23:20 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN XMR SE CERRO PUENTE ABIERTO | S23060600498 | New_Event | Primary Wire Break | Include | Include | Equipment | 1400 | 2023-06-06 | 72800 | keep | 0 | Jun | 2023 | 0.049584 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
CAGUAS | 2023-06-06 16:21 | 2023-06-06 21:48 | 100 | 5:27 | P | DESGANCHE | 1 X 100 EN C/L | C23060600452 | New_Event | Vegetation Contact | Include | Include | Vegetation | 327 | 2023-06-06 | 32700 | keep | 0 | Jun | 2023 | 0.022272 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-06-06 16:24 | 2023-06-06 17:45 | 5 | 1:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 8 EN TRANSFORMADOR SE REPARO CONECTOR SECUNDARIO | A23060600310 | New_Event | Secondary Wire Break | Include | Include | Equipment | 81 | 2023-06-06 | 405 | keep | 0 | Jun | 2023 | 0.00027584 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-06-06 16:32 | 2023-06-06 16:33 | 959 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1904-07 LLEVA 100% 1901-04 LLEVA 100% 1901-01 Y LLEVA 10% 1901-05 | B2306060000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-06 | 959 | keep | 0 | Jun | 2023 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-06-06 16:32 | 2023-06-06 16:33 | 1264 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1904-07 LLEVA 100% 1901-04 LLEVA 100% 1901-01 Y LLEVA 10% 1901-05 | B2306060000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-06 | 1264 | keep | 0 | Jun | 2023 | 0.0008609 | 0.0008609 | Momentary | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2023-06-06 16:32 | 2023-06-06 16:33 | 62 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1904-07 LLEVA 100% 1901-04 LLEVA 100% 1901-01 Y LLEVA 10% 1901-05 | B2306060000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-06 | 62 | keep | 0 | Jun | 2023 | 4.2228e-05 | 4.2228e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 62
BAYAMON | 2023-06-06 16:43 | 2023-06-06 18:28 | 1 | 1:45 | P | TRANSFORMADOR AVERIADO | SE ELEMINO TRANSFORMADOR EN MONTURA Y SE DEJO CLIENTE EN SERVICIO | B23060600391 | New_Event | Service Transformer Failure | Include | Include | Equipment | 105 | 2023-06-06 | 105 | keep | 0 | Jun | 2023 | 7.1515e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-06-06 16:45 | 2023-06-06 20:45 | 80 | 4:00 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23060600496 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 240 | 2023-06-06 | 19200 | keep | 0 | Jun | 2023 | 0.013077 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-06-06 16:54 | 2023-06-06 17:59 | 6 | 1:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23060600411 | New_Event | Secondary Wire Break | Include | Include | Equipment | 65 | 2023-06-06 | 390 | keep | 0 | Jun | 2023 | 0.00026563 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-06-06 17:02 | 2023-06-06 20:30 | 30 | 3:28 | P | CONDUCTOR ROTO O ABIERTO | 2 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A23060600324 | New_Event | Primary Wire Break | Include | Include | Equipment | 208 | 2023-06-06 | 6240 | keep | 0 | Jun | 2023 | 0.00425 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-06-06 17:08 | 2023-06-06 17:09 | 1835 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23060600476 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-06 | 1835 | keep | 0 | Jun | 2023 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
SAN JUAN | 2023-06-06 17:15 | 2023-06-06 19:31 | 171 | 2:16 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | S23060600531 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2023-06-06 | 23256 | keep | 0 | Jun | 2023 | 0.01584 | 0.00011647 | Sustained | FALSE | FALSE | Not_TMED_Event | 171
MAYAGÃœEZ | 2023-06-06 17:19 | 2023-06-06 17:48 | 4 | 0:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23060600423 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 29 | 2023-06-06 | 116 | keep | 0 | Jun | 2023 | 7.9007e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2023-06-06 17:20 | 2023-06-06 17:21 | 1580 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE BKR | C23060600477 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-06 | 1580 | keep | 0 | Jun | 2023 | 0.0010761 | 0.0010761 | Momentary | FALSE | FALSE | Not_TMED_Event | 1580
HUMACAO | 2023-06-06 17:21 | 2023-06-06 19:01 | 40 | 1:40 | P | ANIMAL | 1 X 80 EN SMU-20 EN SU-AD6 CRUCE X IGUANA | C23060600252 | Partial_restoration | Animals | Include | Include | Wildlife | 100 | 2023-06-06 | 4000 | keep | 0 | Jun | 2023 | 0.0027244 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-06 17:24 | 2023-06-06 17:45 | 1 | 0:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23060600425 | New_Event | Secondary Wire Break | Include | Include | Equipment | 21 | 2023-06-06 | 21 | keep | 0 | Jun | 2023 | 1.4303e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-06-06 17:31 | 2023-06-06 17:50 | 15 | 0:19 | P | SECUNDARIA/OTROS | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS QUEMADAS | M23060600380 | New_Event |  |  |  |  | 19 | 2023-06-06 | 285 | keep | 0 | Jun | 2023 | 0.00019411 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-06-06 17:33 | 2023-06-06 17:35 | 1746 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B23060600429 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-06 | 3492 | keep | 0 | Jun | 2023 | 0.0023784 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
HUMACAO | 2023-06-06 18:01 | 2023-06-06 20:12 | 15 | 2:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR SE REMEPLAZO PORTAFUSIBLE | C23060600530 | New_Event | Cutout Failure | Include | Include | Equipment | 131 | 2023-06-06 | 1965 | keep | 0 | Jun | 2023 | 0.0013384 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-06-06 18:01 | 2023-06-06 19:35 | 1798 | 1:34 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA REPARAR PUNTO CALIENTE EN AUXILIAR DE LINEA DEL INTERRUPTOR | A23060600342 | New_Event | Switch Failure | Include | Include | Equipment | 94 | 2023-06-06 | 169012 | keep | 0 | Jun | 2023 | 0.11511 | 0.0012246 | Sustained | FALSE | FALSE | Not_TMED_Event | 1798
SAN JUAN | 2023-06-06 18:04 | 2023-06-06 19:26 | 14 | 1:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REPARAR/SUBIR SECUNDARIA DEL SUELO | S23060600551 | New_Event | Secondary Wire Break | Include | Include | Equipment | 82 | 2023-06-06 | 1148 | keep | 0 | Jun | 2023 | 0.0007819 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2023-06-06 18:32 | 2023-06-06 20:41 | 15 | 2:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BAJANTE SECUNDARIO | S23060600556 | New_Event | Secondary Wire Break | Include | Include | Equipment | 129 | 2023-06-06 | 1935 | keep | 0 | Jun | 2023 | 0.0013179 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-06-06 18:39 | 2023-06-06 18:43 | 817 | 0:04 | T | PROBLEMA DEL CLIENTE | SE ABRIO BKR A PETICION DE ANGEL ORTIZ PORQUE SUBESTACION PRIVADA SE ESTABA PRENDIENDO EN FUEGO. SE ABRIO RISER @ SUB PRIVADA Y SE CERRO POR CONTROL | C23060600501 | New_Event | Customer-Related Interruption | Include | Include | Public | 4 | 2023-06-06 | 3268 | keep | 0 | Jun | 2023 | 0.0022258 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
SAN JUAN | 2023-06-06 18:54 | 2023-06-06 18:55 | 627 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8900 SE PATRULLO Y NO SE ENCONTRÃ“ CAUSA. | S23060600660 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-06 | 627 | keep | 0 | Jun | 2023 | 0.00042705 | 0.00042705 | Momentary | FALSE | FALSE | Not_TMED_Event | 627
SAN JUAN | 2023-06-06 18:54 | 2023-06-06 18:55 | 293 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8900 SE PATRULLO Y NO SE ENCONTRÃ“ CAUSA. | S23060600660 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-06 | 293 | keep | 0 | Jun | 2023 | 0.00019956 | 0.00019956 | Momentary | FALSE | FALSE | Not_TMED_Event | 293
SAN JUAN | 2023-06-06 18:54 | 2023-06-06 18:55 | 761 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8900 SE PATRULLO Y NO SE ENCONTRÃ“ CAUSA. | S23060600660 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-06 | 761 | keep | 0 | Jun | 2023 | 0.00051831 | 0.00051831 | Momentary | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2023-06-06 18:54 | 2023-06-06 18:55 | 451 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8900 SE PATRULLO Y NO SE ENCONTRÃ“ CAUSA. | S23060600660 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-06 | 451 | keep | 0 | Jun | 2023 | 0.00030717 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
SAN JUAN | 2023-06-06 18:54 | 2023-06-06 18:55 | 837 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8900 SE PATRULLO Y NO SE ENCONTRÃ“ CAUSA. | S23060600724 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-06 | 837 | keep | 0 | Jun | 2023 | 0.00057008 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2023-06-06 18:54 | 2023-06-06 18:55 | 908 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8900 SE PATRULLO Y NO SE ENCONTRÃ“ CAUSA. | S23060600724 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-06 | 908 | keep | 0 | Jun | 2023 | 0.00061843 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
SAN JUAN | 2023-06-06 18:54 | 2023-06-06 18:55 | 135 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8900 SE PATRULLO Y NO SE ENCONTRÃ“ CAUSA. | S23060600724 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-06 | 135 | keep | 0 | Jun | 2023 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2023-06-06 18:54 | 2023-06-06 18:55 | 1 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8900 SE PATRULLO Y NO SE ENCONTRÃ“ CAUSA. | S23060600724 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-06 | 1 | keep | 0 | Jun | 2023 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-06-06 18:54 | 2023-06-06 18:55 | 1295 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8900 SE PATRULLO Y NO SE ENCONTRÃ“ CAUSA. | S23060600724 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-06 | 1295 | keep | 0 | Jun | 2023 | 0.00088202 | 0.00088202 | Momentary | FALSE | FALSE | Not_TMED_Event | 1295
SAN JUAN | 2023-06-06 18:54 | 2023-06-06 18:55 | 1498 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8900 | S23060600726 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-06 | 1498 | keep | 0 | Jun | 2023 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
SAN JUAN | 2023-06-06 18:54 | 2023-06-06 18:55 | 164 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8900 | S23060600726 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-06 | 164 | keep | 0 | Jun | 2023 | 0.0001117 | 0.0001117 | Momentary | FALSE | FALSE | Not_TMED_Event | 164
SAN JUAN | 2023-06-06 18:54 | 2023-06-06 18:55 | 533 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8900 | S23060600726 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-06 | 533 | keep | 0 | Jun | 2023 | 0.00036302 | 0.00036302 | Momentary | FALSE | FALSE | Not_TMED_Event | 533
SAN JUAN | 2023-06-06 18:54 | 2023-06-06 18:55 | 451 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8900 | S23060600726 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-06 | 451 | keep | 0 | Jun | 2023 | 0.00030717 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
SAN JUAN | 2023-06-06 18:54 | 2023-06-06 18:55 | 766 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8900 | S23060600726 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-06 | 766 | keep | 0 | Jun | 2023 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
SAN JUAN | 2023-06-06 18:54 | 2023-06-06 20:26 | 427 | 1:32 | S | LINEA DE TRANSMISION 38KV | OPERACION LINEA 8900 SE PATRULLO Y NO SE ENCONTRÃ“ CAUSA. | S23060600746 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 92 | 2023-06-06 | 39284 | keep | 0 | Jun | 2023 | 0.026756 | 0.00029083 | Sustained | FALSE | FALSE | Not_TMED_Event | 427
SAN JUAN | 2023-06-06 18:54 | 2023-06-06 21:53 | 716 | 2:59 | S | LINEA DE TRANSMISION 38KV | OPERACIÃ“N LINEA 8900 SE PATRULLO Y NO SE ENCONTRÃ“ CAUSA. | S23060600746 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 179 | 2023-06-06 | 128164 | keep | 0 | Jun | 2023 | 0.087292 | 0.00048766 | Sustained | FALSE | FALSE | Not_TMED_Event | 716
SAN JUAN | 2023-06-06 18:54 | 2023-06-06 20:26 | 867 | 1:32 | S | LINEA DE TRANSMISION 38KV | OPERACION LINEA 8900 SE PATRULLO Y NO SE ENCONTRÃ“ CAUSA. | S23060600746 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 92 | 2023-06-06 | 79764 | keep | 0 | Jun | 2023 | 0.054327 | 0.00059051 | Sustained | FALSE | FALSE | Not_TMED_Event | 867
SAN JUAN | 2023-06-06 18:54 | 2023-06-06 21:57 | 353 | 3:03 | S | LINEA DE TRANSMISION 38KV | OPERACION LINEA 8900 SE PATRULLO Y NO SE ENCONTRÃ“ CAUSA. | S23060600746 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 183 | 2023-06-06 | 64599 | keep | 0 | Jun | 2023 | 0.043998 | 0.00024043 | Sustained | FALSE | FALSE | Not_TMED_Event | 353
GUAYAMA | 2023-06-06 19:07 | 2023-06-06 19:18 | 30 | 0:11 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA POR AVE | P23060600663 | New_Event | Animals | Include | Include | Wildlife | 11 | 2023-06-06 | 330 | keep | 0 | Jun | 2023 | 0.00022476 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-06-06 19:12 | 2023-06-06 19:48 | 50 | 0:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L REMPLAZO CAJA QUEMADA EVENTO TRANSFERIDO DE PONCE | P23060600674 | New_Event | Cutout Failure | Include | Include | Equipment | 36 | 2023-06-06 | 1800 | keep | 0 | Jun | 2023 | 0.001226 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-06-06 19:20 | 2023-06-06 20:30 | 20 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA ROTA | A23060600356 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2023-06-06 | 1400 | keep | 0 | Jun | 2023 | 0.00095353 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-06-06 19:53 | 2023-06-07 13:47 | 20 | 17:54 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23060600510 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1074 | 2023-06-06 | 21480 | keep | 0 | Jun | 2023 | 0.01463 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-06-06 19:58 | 2023-06-06 20:28 | 25 | 0:30 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23060600524 | New_Event | Animals | Include | Include | Wildlife | 30 | 2023-06-06 | 750 | keep | 0 | Jun | 2023 | 0.00051082 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-06-06 20:03 | 2023-06-07 17:30 | 300 | 21:27 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | M23060600481 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1287 | 2023-06-06 | 386100 | keep | 0 | Jun | 2023 | 0.26297 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2023-06-06 20:07 | 2023-06-06 23:15 | 380 | 3:08 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B23060600521 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 188 | 2023-06-06 | 71440 | keep | 0 | Jun | 2023 | 0.048657 | 0.00025882 | Sustained | FALSE | FALSE | Not_TMED_Event | 380
BAYAMON | 2023-06-06 20:09 | 2023-06-07 00:18 | 269 | 4:09 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23060600522 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 249 | 2023-06-06 | 66981 | keep | 0 | Jun | 2023 | 0.04562 | 0.00018321 | Sustained | FALSE | FALSE | Not_TMED_Event | 269
AGUADILLA | 2023-06-06 20:09 | 2023-06-06 20:32 | 2658 | 0:23 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO RECERRO NO SE REPORTO CAUSA | M23060600487 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 23 | 2023-06-06 | 61134 | keep | 0 | Jun | 2023 | 0.041638 | 0.0018104 | Sustained | FALSE | FALSE | Not_TMED_Event | 2658
MAYAGÃœEZ | 2023-06-06 20:43 | 2023-06-07 05:09 | 50 | 8:26 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23060600500 | New_Event | Vegetation Contact | Include | Include | Vegetation | 506 | 2023-06-06 | 25300 | keep | 0 | Jun | 2023 | 0.017232 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-06-06 21:00 | 2023-06-06 21:03 | 2658 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO RECERRO NO SE REPORTO CAUSA | M23060600515 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-06-06 | 7974 | keep | 0 | Jun | 2023 | 0.0054311 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-06-06 21:21 | 2023-06-07 09:45 | 60 | 12:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CL FUERTE VIENTOS | M23060600535 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 744 | 2023-06-06 | 44640 | keep | 0 | Jun | 2023 | 0.030404 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-06-06 21:32 | 2023-06-06 21:55 | 60 | 0:23 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23060600578 | New_Event | Vegetation Contact | Include | Include | Vegetation | 23 | 2023-06-06 | 1380 | keep | 0 | Jun | 2023 | 0.00093991 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-06-06 21:34 | 2023-06-07 09:31 | 60 | 11:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REEMPLAZO A PORTA FUSIBLE | B23060600580 | New_Event | Cutout Failure | Include | Include | Equipment | 717 | 2023-06-06 | 43020 | keep | 0 | Jun | 2023 | 0.029301 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-06-06 21:58 | 2023-06-07 03:19 | 100 | 5:21 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23060600551 | New_Event | Vegetation Contact | Include | Include | Vegetation | 321 | 2023-06-06 | 32100 | keep | 0 | Jun | 2023 | 0.021863 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-06-06 22:10 | 2023-06-07 11:31 | 113 | 13:21 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23060600599 | New_Event | Vegetation Contact | Include | Include | Vegetation | 801 | 2023-06-06 | 90513 | keep | 0 | Jun | 2023 | 0.061648 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
SAN JUAN | 2023-06-06 22:11 | 2023-06-06 22:14 | 427 | 0:03 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S2306060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-06-06 | 1281 | keep | 0 | Jun | 2023 | 0.00087248 | 0.00029083 | Momentary | FALSE | FALSE | Not_TMED_Event | 427
BAYAMON | 2023-06-06 22:26 | 2023-06-07 11:33 | 211 | 13:07 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | B23060600613 | New_Event | Animals | Include | Include | Wildlife | 787 | 2023-06-06 | 166057 | keep | 0 | Jun | 2023 | 0.1131 | 0.00014371 | Sustained | FALSE | FALSE | Not_TMED_Event | 211
SAN JUAN | 2023-06-06 23:00 | 2023-06-07 09:35 | 60 | 10:35 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | S23060600804 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 635 | 2023-06-06 | 38100 | keep | 0 | Jun | 2023 | 0.02595 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-06-06 23:00 | 2023-06-06 23:02 | 215 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B230606000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-06 | 430 | keep | 0 | Jun | 2023 | 0.00029287 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
SAN JUAN | 2023-06-06 23:17 | 2023-06-07 00:48 | 60 | 1:31 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | P23060601010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 91 | 2023-06-06 | 5460 | keep | 0 | Jun | 2023 | 0.0037188 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-06-06 23:27 | 2023-06-07 02:26 | 200 | 2:59 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23060600604 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2023-06-06 | 35800 | keep | 0 | Jun | 2023 | 0.024383 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
GUAYAMA | 2023-06-06 23:34 | 2023-06-07 10:00 | 50 | 10:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REMPLAZO CAJA EN C/L QUEMADA | P23060601036 | New_Event | Cutout Failure | Include | Include | Equipment | 626 | 2023-06-06 | 31300 | keep | 0 | Jun | 2023 | 0.021318 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-06-06 23:46 | 2023-06-07 09:00 | 193 | 9:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 140 EN C/L SE REMPLAZO 3 CAJAS EN C/L | P23060601052 | New_Event | Cutout Failure | Include | Include | Equipment | 554 | 2023-06-06 | 106922 | keep | 0 | Jun | 2023 | 0.072824 | 0.00013145 | Sustained | FALSE | FALSE | Not_TMED_Event | 193
SAN JUAN | 2023-06-06 23:56 | 2023-06-07 09:49 | 3 | 9:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESPAEJE DE LINEA | P23060601067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 593 | 2023-06-06 | 1779 | keep | 0 | Jun | 2023 | 0.0012117 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2023-06-07 00:47 | 2023-06-07 09:15 | 40 | 8:28 | P | CONDUCTOR ROTO O ABIERTO | ALAMBRE PARTIDO | M23060700021 | New_Event | Primary Wire Break | Include | Include | Equipment | 508 | 2023-06-07 | 20320 | keep | 0 | Jun | 2023 | 0.01384 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-06-07 01:42 | 2023-06-07 11:46 | 50 | 10:04 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23060700040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 604 | 2023-06-07 | 30200 | keep | 0 | Jun | 2023 | 0.020569 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-06-07 02:37 | 2023-06-07 09:32 | 80 | 6:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23060700052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 415 | 2023-06-07 | 33200 | keep | 0 | Jun | 2023 | 0.022612 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2023-06-07 02:46 | 2023-06-07 10:00 | 100 | 7:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE AVERIADO | M23060700078 | New_Event | Cutout Failure | Include | Include | Equipment | 434 | 2023-06-07 | 43400 | keep | 0 | Jun | 2023 | 0.02956 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-06-07 03:22 | 2023-06-08 12:01 | 80 | 32:39 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | S23060700162 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1959 | 2023-06-07 | 156720 | keep | 0 | Jun | 2023 | 0.10674 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-06-07 03:33 | 2023-06-07 04:47 | 75 | 1:14 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23060700148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2023-06-07 | 5550 | keep | 0 | Jun | 2023 | 0.0037801 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
PONCE | 2023-06-07 04:15 | 2023-06-07 06:40 | 50 | 2:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA EN C/L | P23060700189 | New_Event | Cutout Failure | Include | Include | Equipment | 145 | 2023-06-07 | 7250 | keep | 0 | Jun | 2023 | 0.0049379 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-06-07 04:32 | 2023-06-07 09:23 | 100 | 4:51 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | A23060700100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 291 | 2023-06-07 | 29100 | keep | 0 | Jun | 2023 | 0.01982 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2023-06-07 04:37 | 2023-06-07 07:40 | 10 | 3:03 | P | ANIMAL | 1 X 15 EN XMR AVE CRUZO LINEAS | P23060700203 | New_Event | Animals | Include | Include | Wildlife | 183 | 2023-06-07 | 1830 | keep | 0 | Jun | 2023 | 0.0012464 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-06-07 05:54 | 2023-06-07 08:35 | 70 | 2:41 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23060700119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2023-06-07 | 11270 | keep | 0 | Jun | 2023 | 0.0076759 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
FAJARDO | 2023-06-07 06:10 | 2023-06-07 06:11 | 2286 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA 3100 DE DAGUAO A FAJARDO | R23060700156 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-07 | 2286 | keep | 0 | Jun | 2023 | 0.001557 | 0.001557 | Momentary | FALSE | FALSE | Not_TMED_Event | 2286
FAJARDO | 2023-06-07 06:10 | 2023-06-07 06:11 | 693 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA 3100 DE DAGUAO A FAJARDO | R23060700156 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-07 | 693 | keep | 0 | Jun | 2023 | 0.000472 | 0.000472 | Momentary | FALSE | FALSE | Not_TMED_Event | 693
FAJARDO | 2023-06-07 06:10 | 2023-06-07 06:11 | 1839 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA 5400 DE DAGUAO A CULEBRA POSIBLE OPERACION LENTA DEL BKR 3170 DAGUAO | R23060700151 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2023-06-07 | 1839 | keep | 0 | Jun | 2023 | 0.0012525 | 0.0012525 | Momentary | FALSE | FALSE | Not_TMED_Event | 1839
FAJARDO | 2023-06-07 06:10 | 2023-06-07 06:11 | 1778 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA 5400 DE DAGUAO A CULEBRA POSIBLE OPERACION LENTA DEL BKR 3170 DAGUAO | R23060700151 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2023-06-07 | 1778 | keep | 0 | Jun | 2023 | 0.001211 | 0.001211 | Momentary | FALSE | FALSE | Not_TMED_Event | 1778
FAJARDO | 2023-06-07 06:10 | 2023-06-07 06:11 | 1376 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA 5400 DE DAGUAO A CULEBRA POSIBLE OPERACION LENTA DEL BKR 3170 DAGUAO | R23060700151 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2023-06-07 | 1376 | keep | 0 | Jun | 2023 | 0.00093719 | 0.00093719 | Momentary | FALSE | FALSE | Not_TMED_Event | 1376
FAJARDO | 2023-06-07 06:10 | 2023-06-07 06:11 | 293 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA 5400 DE DAGUAO A CULEBRA POSIBLE OPERACION LENTA DEL BKR 3170 DAGUAO | R23060700155 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2023-06-07 | 293 | keep | 0 | Jun | 2023 | 0.00019956 | 0.00019956 | Momentary | FALSE | FALSE | Not_TMED_Event | 293
FAJARDO | 2023-06-07 06:10 | 2023-06-07 06:11 | 1215 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LA 5400 DE DAGUAO A CULEBRA POSIBLE OPERACION LENTA DEL BKR 3170 DAGUAO | R23060700155 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2023-06-07 | 1215 | keep | 0 | Jun | 2023 | 0.00082753 | 0.00082753 | Momentary | FALSE | FALSE | Not_TMED_Event | 1215
CANOVANAS | 2023-06-07 06:16 | 2023-06-07 12:09 | 9 | 5:53 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | R23060700157 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 353 | 2023-06-07 | 3177 | keep | 0 | Jun | 2023 | 0.0021638 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
FAJARDO | 2023-06-07 06:16 | 2023-06-07 09:10 | 255 | 2:54 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | R23060700153 | New_Event | Animals | Include | Include | Wildlife | 174 | 2023-06-07 | 44370 | keep | 0 | Jun | 2023 | 0.03022 | 0.00017368 | Sustained | FALSE | FALSE | Not_TMED_Event | 255
MAYAGÃœEZ | 2023-06-07 06:20 | 2023-06-07 10:05 | 40 | 3:45 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M23060700200 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2023-06-07 | 9000 | keep | 0 | Jun | 2023 | 0.0061299 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-06-07 06:23 | 2023-06-07 09:30 | 100 | 3:07 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23060700125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2023-06-07 | 18700 | keep | 0 | Jun | 2023 | 0.012736 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-06-07 06:27 | 2023-06-07 07:54 | 100 | 1:27 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23060700332 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2023-06-07 | 8700 | keep | 0 | Jun | 2023 | 0.0059255 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-06-07 06:33 | 2023-06-07 08:55 | 200 | 2:22 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23060700206 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 142 | 2023-06-07 | 28400 | keep | 0 | Jun | 2023 | 0.019343 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2023-06-07 06:38 | 2023-06-07 09:28 | 30 | 2:50 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER Y 1 X 65 EN SU | B23060700338 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 170 | 2023-06-07 | 5100 | keep | 0 | Jun | 2023 | 0.0034736 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-06-07 06:40 | 2023-06-07 09:10 | 200 | 2:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M23060700209 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2023-06-07 | 30000 | keep | 0 | Jun | 2023 | 0.020433 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2023-06-07 06:44 | 2023-06-07 10:01 | 175 | 3:17 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | R23060700173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 197 | 2023-06-07 | 34475 | keep | 0 | Jun | 2023 | 0.023481 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
PONCE | 2023-06-07 06:44 | 2023-06-07 10:05 | 40 | 3:21 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P23060700306 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2023-06-07 | 8040 | keep | 0 | Jun | 2023 | 0.005476 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-06-07 06:45 | 2023-06-07 12:12 | 50 | 5:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CL FUERTE VIENTO | M23060700212 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 327 | 2023-06-07 | 16350 | keep | 0 | Jun | 2023 | 0.011136 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-06-07 06:46 | 2023-06-07 07:22 | 233 | 0:36 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23060700344 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 36 | 2023-06-07 | 8388 | keep | 0 | Jun | 2023 | 0.005713 | 0.0001587 | Sustained | FALSE | FALSE | Not_TMED_Event | 233
FAJARDO | 2023-06-07 06:47 | 2023-06-07 06:48 | 2722 | 0:01 | T | ANIMAL | RECIERRE DE BKR | R2306070000X | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-06-07 | 2722 | keep | 0 | Jun | 2023 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
SAN JUAN | 2023-06-07 06:48 | 2023-06-07 10:48 | 10 | 4:00 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA PALOMA CRUZO FASE | S23060700422 | New_Event | Animals | Include | Include | Wildlife | 240 | 2023-06-07 | 2400 | keep | 0 | Jun | 2023 | 0.0016346 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-06-07 06:48 | 2023-06-07 10:27 | 8 | 3:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR Y REEMPLAZO DE PORTAFUSIBLE QUEMADO EVENTO TRANSFERIDO DE PONCE | P23060700307 | New_Event | Cutout Failure | Include | Include | Equipment | 219 | 2023-06-07 | 1752 | keep | 0 | Jun | 2023 | 0.0011933 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2023-06-07 06:48 | 2023-06-07 08:30 | 55 | 1:42 | P | ANIMAL | 1 X 65 EN C/L Y 1 X 40 EN C/L CRUCE X AVE | R23060700174 | 1st_after_momentary | Animals | Include | Include | Wildlife | 102 | 2023-06-07 | 5610 | keep | 0 | Jun | 2023 | 0.0038209 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
SAN JUAN | 2023-06-07 06:51 | 2023-06-07 15:35 | 10 | 8:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REPARO BANATE SECUNDARIO | S23060700423 | New_Event | Secondary Wire Break | Include | Include | Equipment | 524 | 2023-06-07 | 5240 | keep | 0 | Jun | 2023 | 0.0035689 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-06-07 06:52 | 2023-06-07 18:50 | 80 | 11:58 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | M23060700215 | New_Event | Vegetation Contact | Include | Include | Vegetation | 718 | 2023-06-07 | 57440 | keep | 0 | Jun | 2023 | 0.039122 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2023-06-07 06:56 | 2023-06-07 10:00 | 75 | 3:04 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P23060700310 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2023-06-07 | 13800 | keep | 0 | Jun | 2023 | 0.0093991 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2023-06-07 06:59 | 2023-06-07 09:40 | 130 | 2:41 | P | ANIMAL | 1 X 100 1 X 80 EN C/L CRUCE POR AVE | C23060700195 | New_Event | Animals | Include | Include | Wildlife | 161 | 2023-06-07 | 20930 | keep | 0 | Jun | 2023 | 0.014255 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
CANOVANAS | 2023-06-07 07:10 | 2023-06-07 09:25 | 128 | 2:15 | P | TRANSFORMADOR AVERIADO | 1 X 65 EN C/L. TANSFORMADOR AVERIADO FUNDIO C/L | R23060700189 | New_Event | Service Transformer Failure | Include | Include | Equipment | 135 | 2023-06-07 | 17280 | keep | 0 | Jun | 2023 | 0.011769 | 8.718e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 128
BAYAMON | 2023-06-07 07:12 | 2023-06-07 10:37 | 100 | 3:25 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | S23060700443 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2023-06-07 | 20500 | keep | 0 | Jun | 2023 | 0.013962 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-06-07 07:12 | 2023-06-07 12:50 | 14 | 5:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO | R23060700192 | New_Event | Secondary Wire Break | Include | Include | Equipment | 338 | 2023-06-07 | 4732 | keep | 0 | Jun | 2023 | 0.0032229 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2023-06-07 07:19 | 2023-06-07 12:54 | 181 | 5:35 | P | CONDUCTOR ROTO O ABIERTO | SECERRO PUENTE | S23060700447 | New_Event | Primary Wire Break | Include | Include | Equipment | 335 | 2023-06-07 | 60635 | keep | 0 | Jun | 2023 | 0.041298 | 0.00012328 | Sustained | FALSE | FALSE | Not_TMED_Event | 181
BAYAMON | 2023-06-07 07:27 | 2023-06-07 12:23 | 16 | 4:56 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | B23060700363 | New_Event | Animals | Include | Include | Wildlife | 296 | 2023-06-07 | 4736 | keep | 0 | Jun | 2023 | 0.0032257 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CANOVANAS | 2023-06-07 07:28 | 2023-06-07 09:39 | 45 | 2:11 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | R23060700203 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 131 | 2023-06-07 | 5895 | keep | 0 | Jun | 2023 | 0.0040151 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-06-07 07:32 | 2023-06-07 12:00 | 453 | 4:28 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | S23060700460 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2023-06-07 | 121404 | keep | 0 | Jun | 2023 | 0.082688 | 0.00030854 | Sustained | FALSE | FALSE | Not_TMED_Event | 453
VEGA BAJA | 2023-06-07 07:32 | 2023-06-07 10:45 | 26 | 3:13 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23060700370 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 193 | 2023-06-07 | 5018 | keep | 0 | Jun | 2023 | 0.0034177 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
MAYAGÃœEZ | 2023-06-07 07:35 | 2023-06-07 16:45 | 20 | 9:10 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50KVA | M23060700245 | New_Event | Service Transformer Failure | Include | Include | Equipment | 550 | 2023-06-07 | 11000 | keep | 0 | Jun | 2023 | 0.007492 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-06-07 07:40 | 2023-06-07 08:40 | 40 | 1:00 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R23060700212 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2023-06-07 | 2400 | keep | 0 | Jun | 2023 | 0.0016346 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-06-07 07:46 | 2023-06-07 11:03 | 1 | 3:17 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | R23060700217 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2023-06-07 | 197 | keep | 0 | Jun | 2023 | 0.00013418 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-06-07 07:50 | 2023-06-07 10:42 | 36 | 2:52 | P | DESGANCHE | 1 X 40 EN C/L Y 1 X 50 EN C/L DESGANCHE | R23060700219 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2023-06-07 | 6192 | keep | 0 | Jun | 2023 | 0.0042173 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
YAUCO | 2023-06-07 07:51 | 2023-06-07 12:10 | 1 | 4:19 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23060700248 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 259 | 2023-06-07 | 259 | keep | 0 | Jun | 2023 | 0.0001764 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-06-07 07:58 | 2023-06-07 11:14 | 10 | 3:16 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA RATON CRUZO FASE | S23060700481 | New_Event | Animals | Include | Include | Wildlife | 196 | 2023-06-07 | 1960 | keep | 0 | Jun | 2023 | 0.0013349 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-06-07 07:59 | 2023-06-07 08:01 | 1191 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | S23060700482 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-07 | 2382 | keep | 0 | Jun | 2023 | 0.0016224 | 0.00081118 | Momentary | FALSE | FALSE | Not_TMED_Event | 1191
CAGUAS | 2023-06-07 08:00 | 2023-06-07 11:18 | 70 | 3:18 | P | DESGANCHE | 1 X 100 EN C/L | C23060700224 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2023-06-07 | 13860 | keep | 0 | Jun | 2023 | 0.00944 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-06-07 08:13 | 2023-06-07 12:06 | 278 | 3:53 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN C/L POR CONDUCTOR CRUZADO | B23060700395 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 233 | 2023-06-07 | 64774 | keep | 0 | Jun | 2023 | 0.044117 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
ARECIBO | 2023-06-07 08:29 | 2023-06-07 13:00 | 60 | 4:31 | P | SOBRECARGA | 1 X 50 EN CL SOBRECARGA | A23060700192 | New_Event | Trip Due To Overload | Include | Include | Other | 271 | 2023-06-07 | 16260 | keep | 0 | Jun | 2023 | 0.011075 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-06-07 08:34 | 2023-06-07 16:21 | 8 | 7:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | REMPLAZO CONECTOR QUEMADO EN BAJANTE SECUNDARIO | C23060700257 | New_Event | Secondary Wire Break | Include | Include | Equipment | 467 | 2023-06-07 | 3736 | keep | 0 | Jun | 2023 | 0.0025446 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-06-07 08:42 | 2023-06-07 08:43 | 1894 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | R2306070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-07 | 1894 | keep | 0 | Jun | 2023 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
BARRANQUITAS | 2023-06-07 08:56 | 2023-06-07 08:57 | 1854 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23060700281 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-07 | 1854 | keep | 0 | Jun | 2023 | 0.0012628 | 0.0012628 | Momentary | FALSE | FALSE | Not_TMED_Event | 1854
BAYAMON | 2023-06-07 09:11 | 2023-06-07 12:47 | 179 | 3:36 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23060700451 | New_Event | Vegetation Contact | Include | Include | Vegetation | 216 | 2023-06-07 | 38664 | keep | 0 | Jun | 2023 | 0.026334 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
AGUADILLA | 2023-06-07 09:15 | 2023-06-07 14:10 | 100 | 4:55 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA REPARAR ALAMBRE PARTIDO | M23060700021 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 295 | 2023-06-07 | 29500 | keep | 0 | Jun | 2023 | 0.020092 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-07 09:23 | 2023-06-07 09:46 | 6 | 0:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23060700461 | New_Event | Secondary Wire Break | Include | Include | Equipment | 23 | 2023-06-07 | 138 | keep | 0 | Jun | 2023 | 9.3991e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-06-07 09:25 | 2023-06-07 11:14 | 14 | 1:49 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR QUEMADO DE 75 KVA X 75 KVA | R23060700278 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 109 | 2023-06-07 | 1526 | keep | 0 | Jun | 2023 | 0.0010394 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-06-07 09:30 | 2023-06-07 09:40 | 180 | 0:10 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SJ-230607-50 SE HICIERON OPERACIONES PARA SECCIONALIZAR POSTE PRIMARIO PARTIDO SE CERRO N/O CONTRA 2306-02 | R23060700291 | New_Event | Primary Pole Failure | Include | Include | Equipment | 10 | 2023-06-07 | 1800 | keep | 0 | Jun | 2023 | 0.001226 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
BAYAMON | 2023-06-07 09:32 | 2023-06-07 17:15 | 6 | 7:43 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 37.5 @ 37.5 | B23060700431 | New_Event | Service Transformer Failure | Include | Include | Equipment | 463 | 2023-06-07 | 2778 | keep | 0 | Jun | 2023 | 0.0018921 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2023-06-07 09:37 | 2023-06-07 10:00 | 4 | 0:23 | P | NO SE REPORTO CAUSA | 1 X 30 C/L NO CAUSA | P23060700486 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 23 | 2023-06-07 | 92 | keep | 0 | Jun | 2023 | 6.2661e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-06-07 09:39 | 2023-06-07 12:48 | 1 | 3:09 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO CAUSA | S23060700600 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 189 | 2023-06-07 | 189 | keep | 0 | Jun | 2023 | 0.00012873 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-06-07 09:40 | 2023-06-07 10:18 | 1 | 0:38 | P | ANIMAL | 1 SMU 20 DE 25AMP CRUCE X REPTIL | C23060700315 | New_Event | Animals | Include | Include | Wildlife | 38 | 2023-06-07 | 38 | keep | 0 | Jun | 2023 | 2.5882e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-06-07 09:43 | 2023-06-07 09:52 | 1058 | 0:09 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 20% DEL 1336-08 | S23060700606 | New_Event | Feeder Load Transferred | Include | Include | Other | 9 | 2023-06-07 | 9522 | keep | 0 | Jun | 2023 | 0.0064854 | 0.0007206 | Sustained | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2023-06-07 09:43 | 2023-06-07 09:52 | 1000 | 0:09 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 80% DEL 1348-06 | S23060700606 | New_Event | Feeder Load Transferred | Include | Include | Other | 9 | 2023-06-07 | 9000 | keep | 0 | Jun | 2023 | 0.0061299 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2023-06-07 09:43 | 2023-06-07 09:52 | 278 | 0:09 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% DEL 1348-07 | S23060700606 | New_Event | Feeder Load Transferred | Include | Include | Other | 9 | 2023-06-07 | 2502 | keep | 0 | Jun | 2023 | 0.0017041 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2023-06-07 09:43 | 2023-06-07 09:52 | 1295 | 0:09 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% DEL 1401-10 | S23060700606 | New_Event | Feeder Load Transferred | Include | Include | Other | 9 | 2023-06-07 | 11655 | keep | 0 | Jun | 2023 | 0.0079382 | 0.00088202 | Sustained | FALSE | FALSE | Not_TMED_Event | 1295
SAN JUAN | 2023-06-07 09:43 | 2023-06-07 09:52 | 9 | 0:09 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 100% DEL 1401-10 LLEVA 100% DEL 1348-07 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 | S23060700606 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2023-06-07 | 81 | keep | 0 | Jun | 2023 | 5.5169e-05 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2023-06-07 09:45 | 2023-06-07 10:12 | 1035 | 0:27 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SJ-230607-50 SE HICIERON OPERACIONES PARA SECCIONALIZAR POSTE PRIMARIO PARTIDO SE ABRIO PUENTE Y SE CERRO C/L ENTRANDO 283 CLTE | R23060700291 | New_Event | Primary Pole Failure | Include | Include | Equipment | 27 | 2023-06-07 | 27945 | keep | 0 | Jun | 2023 | 0.019033 | 0.00070493 | Sustained | FALSE | FALSE | Not_TMED_Event | 1035
YAUCO | 2023-06-07 09:57 | 2023-06-07 16:40 | 100 | 6:43 | P | CAUSAS EXTERNAS | 2 X 50 EN CORTE DE LINEA Y 1 X 8 EN TRANSFORMADOR VEHICULO CRUZO LINEAS | M23060700388 | New_Event | Damage From Public | Include | Include | Public | 403 | 2023-06-07 | 40300 | keep | 0 | Jun | 2023 | 0.027448 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-06-07 10:12 | 2023-06-07 17:20 | 752 | 7:08 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | REEMPLAZO DE POSTE PRIMARIO | R23060700291 | New_Event | Primary Pole Failure | Include | Include | Equipment | 428 | 2023-06-07 | 321856 | keep | 0 | Jun | 2023 | 0.21921 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
BAYAMON | 2023-06-07 10:25 | 2023-06-07 16:42 | 18 | 6:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B23060700557 | New_Event | Cutout Failure | Include | Include | Equipment | 377 | 2023-06-07 | 6786 | keep | 0 | Jun | 2023 | 0.0046219 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2023-06-07 10:25 | 2023-06-07 13:43 | 428 | 3:18 | P | DESGANCHE | 1 X 80 Y 1 X 100 EN C/L SE REALIZO DESGANCHE Y SE DESPGO PUENTE DE LINEA A CAJA QUE TOCABA EL POSTE | B23060700558 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2023-06-07 | 84744 | keep | 0 | Jun | 2023 | 0.057719 | 0.00029151 | Sustained | FALSE | FALSE | Not_TMED_Event | 428
CANOVANAS | 2023-06-07 10:25 | 2023-06-07 11:17 | 10 | 0:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | R23060700296 | New_Event | Cutout Failure | Include | Include | Equipment | 52 | 2023-06-07 | 520 | keep | 0 | Jun | 2023 | 0.00035417 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-06-07 10:26 | 2023-06-07 10:43 | 1 | 0:17 | P | NO SE REPORTO CAUSA | 1 X 15 EN MONTURA PRIVADA | B23060700560 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 17 | 2023-06-07 | 17 | keep | 0 | Jun | 2023 | 1.1579e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-06-07 10:28 | 2023-06-07 15:50 | 1 | 5:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 CAJAS PRIMARIAS | B23060700249 | New_Event | Cutout Failure | Include | Include | Equipment | 322 | 2023-06-07 | 322 | keep | 0 | Jun | 2023 | 0.00021931 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-06-07 10:30 | 2023-06-07 11:09 | 15 | 0:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR Y SE REPARO CONECTORES SECUNDARIOS | S23060700513 | New_Event | Secondary Wire Break | Include | Include | Equipment | 39 | 2023-06-07 | 585 | keep | 0 | Jun | 2023 | 0.00039844 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-06-07 10:44 | 2023-06-08 11:05 | 8 | 24:21 | P | ANIMAL | 1 X 15 EN MONTURA 1 X 65 EN C/L AVE CRUZO MONTURA | B23060700698 | New_Event | Animals | Include | Include | Wildlife | 1461 | 2023-06-07 | 11688 | keep | 0 | Jun | 2023 | 0.0079606 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-06-07 11:09 | 2023-06-07 14:18 | 1 | 3:09 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO CAUSA | S23060700827 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 189 | 2023-06-07 | 189 | keep | 0 | Jun | 2023 | 0.00012873 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-06-07 11:22 | 2023-06-07 13:06 | 9 | 1:44 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE DE LINEA A CAJA | S23060700711 | New_Event | Primary Wire Break | Include | Include | Equipment | 104 | 2023-06-07 | 936 | keep | 0 | Jun | 2023 | 0.00063751 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2023-06-07 11:24 | 2023-06-07 11:48 | 2 | 0:24 | P | DESGANCHE | 1 X 25 EN RISER SE REALIZO DESGANCHE EVENTO TRANSFERIDO DE PONCE | P23060700598 | New_Event | Vegetation Contact | Include | Include | Vegetation | 24 | 2023-06-07 | 48 | keep | 0 | Jun | 2023 | 3.2693e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-06-07 11:30 | 2023-06-07 19:05 | 100 | 7:35 | P | CONDUCTOR ARRIADO O CRUZADO | 3 X 80 EN CORTE DE LINEA SE RETEZO LINEA | M23060700449 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 455 | 2023-06-07 | 45500 | keep | 0 | Jun | 2023 | 0.03099 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-06-07 11:33 | 2023-06-07 13:43 | 25 | 2:10 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23060700454 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2023-06-07 | 3250 | keep | 0 | Jun | 2023 | 0.0022136 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-06-07 11:46 | 2023-06-07 14:00 | 381 | 2:14 | P | DESGANCHE | 2 X 100 EN CONVENTIDOR Y DESGANCHE | S23060700738 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2023-06-07 | 51054 | keep | 0 | Jun | 2023 | 0.034773 | 0.0002595 | Sustained | FALSE | FALSE | Not_TMED_Event | 381
BARRANQUITAS | 2023-06-07 11:52 | 2023-06-07 15:42 | 1 | 3:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L REMPLAZO CAJA QUEMADA EVENTO TRANSFERIDO DE ARECIBO | A23060700326 | New_Event | Cutout Failure | Include | Include | Equipment | 230 | 2023-06-07 | 230 | keep | 0 | Jun | 2023 | 0.00015665 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-06-07 12:05 | 2023-06-07 13:09 | 1 | 1:04 | P | OTRAS CAUSAS | SE REMPLAZO LOS EQUIPOS DE MEDICION | C23060700402 | New_Event | Other Causes | Include | Include | Other | 64 | 2023-06-07 | 64 | keep | 0 | Jun | 2023 | 4.359e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-06-07 12:10 | 2023-06-07 15:00 | 50 | 2:50 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | A23060700331 | New_Event | Animals | Include | Include | Wildlife | 170 | 2023-06-07 | 8500 | keep | 0 | Jun | 2023 | 0.0057893 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-06-07 12:13 | 2023-06-07 14:40 | 12 | 2:27 | P | ANIMAL | 1 X 10 EN XMR CRUCE POR AVE | C23060700405 | New_Event | Animals | Include | Include | Wildlife | 147 | 2023-06-07 | 1764 | keep | 0 | Jun | 2023 | 0.0012015 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-06-07 12:15 | 2023-06-07 14:38 | 1 | 2:23 | P | DESGANCHE | 1 X 30 EN C/L Y DESGANCHE | B23060700635 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2023-06-07 | 143 | keep | 0 | Jun | 2023 | 9.7397e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-06-07 12:20 | 2023-06-08 07:35 | 88 | 19:15 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | C23060700410 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1155 | 2023-06-07 | 101640 | keep | 0 | Jun | 2023 | 0.069227 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
SAN JUAN | 2023-06-07 12:23 | 2023-06-07 21:35 | 15 | 9:12 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 50KVA | S23060700770 | New_Event | Service Transformer Failure | Include | Include | Equipment | 552 | 2023-06-07 | 8280 | keep | 0 | Jun | 2023 | 0.0056395 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2023-06-07 12:30 | 2023-06-07 19:37 | 9 | 7:07 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE Y LINEAS SECUNDARIAS | P23060700664 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 427 | 2023-06-07 | 3843 | keep | 0 | Jun | 2023 | 0.0026174 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2023-06-07 12:32 | 2023-06-07 13:10 | 1 | 0:38 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO SECUNDARIA ROTA | C23060700415 | New_Event | Primary Wire Break | Include | Include | Equipment | 38 | 2023-06-07 | 38 | keep | 0 | Jun | 2023 | 2.5882e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-06-07 12:36 | 2023-06-07 18:15 | 16 | 5:39 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA X 37.5 KVA | A23060700341 | New_Event | Service Transformer Failure | Include | Include | Equipment | 339 | 2023-06-07 | 5424 | keep | 0 | Jun | 2023 | 0.0036943 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2023-06-07 12:39 | 2023-06-07 12:40 | 6136 | 0:01 | T | NO SE REPORTO CAUSA | RCIERRE | B23060700656 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-07 | 6136 | keep | 0 | Jun | 2023 | 0.0041792 | 0.0041792 | Momentary | FALSE | FALSE | Not_TMED_Event | 6136
VEGA BAJA | 2023-06-07 12:41 | 2023-06-07 13:39 | 10 | 0:58 | P | SECUNDARIA/OTROS | SE ABRIO XMR Y SE REEMPLAZO PEDESTAL | B23060700653 | New_Event |  |  |  |  | 58 | 2023-06-07 | 580 | keep | 0 | Jun | 2023 | 0.00039504 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-06-07 12:43 | 2023-06-07 18:41 | 10 | 5:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR BARRA EN PEDESTAL | C23060700420 | New_Event | Secondary Wire Break | Include | Include | Equipment | 358 | 2023-06-07 | 3580 | keep | 0 | Jun | 2023 | 0.0024383 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-06-07 12:49 | 2023-06-07 16:39 | 1 | 3:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | S23060700789 | New_Event | Vegetation Contact | Include | Include | Vegetation | 230 | 2023-06-07 | 230 | keep | 0 | Jun | 2023 | 0.00015665 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-06-07 12:51 | 2023-06-07 14:00 | 10 | 1:09 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23060700663 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 69 | 2023-06-07 | 690 | keep | 0 | Jun | 2023 | 0.00046996 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-06-07 12:52 | 2023-06-07 13:46 | 6 | 0:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZARON 2 BARRAS SECUNDARIAS | R23060700344 | New_Event | Secondary Wire Break | Include | Include | Equipment | 54 | 2023-06-07 | 324 | keep | 0 | Jun | 2023 | 0.00022067 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-06-07 12:54 | 2023-06-07 14:38 | 1 | 1:44 | P | ANIMAL | 1 X 25 EN AEREO PROVICIONAL CRUCE POR AVE | B23060700666 | New_Event | Animals | Include | Include | Wildlife | 104 | 2023-06-07 | 104 | keep | 0 | Jun | 2023 | 7.0834e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-06-07 12:56 | 2023-06-07 13:47 | 1 | 0:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR PORTA FUSIBLE AVERIADO | A23060700348 | New_Event | Cutout Failure | Include | Include | Equipment | 51 | 2023-06-07 | 51 | keep | 0 | Jun | 2023 | 3.4736e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-06-07 12:57 | 2023-06-07 14:49 | 10 | 1:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | S23060700461 | New_Event | Secondary Wire Break | Include | Include | Equipment | 112 | 2023-06-07 | 1120 | keep | 0 | Jun | 2023 | 0.00076283 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-06-07 13:03 | 2023-06-07 13:09 | 1058 | 0:06 | P | ALIMENTADOR AMARRADO | DISPARO SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL 20% POR 1424-08 | S23060700795 | New_Event | Feeder Load Transferred | Include | Include | Other | 6 | 2023-06-07 | 6348 | keep | 0 | Jun | 2023 | 0.0043236 | 0.0007206 | Sustained | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2023-06-07 13:03 | 2023-06-07 13:09 | 1000 | 0:06 | P | ALIMENTADOR AMARRADO | DISPARO SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL 80% POR 1424-08 | S23060700795 | New_Event | Feeder Load Transferred | Include | Include | Other | 6 | 2023-06-07 | 6000 | keep | 0 | Jun | 2023 | 0.0040866 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2023-06-07 13:03 | 2023-06-07 13:09 | 278 | 0:06 | T | ALIMENTADOR AMARRADO | DISPARO SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL SU CARGA POR 1424-08 | S23060700795 | New_Event | Feeder Load Transferred | Include | Include | Other | 6 | 2023-06-07 | 1668 | keep | 0 | Jun | 2023 | 0.0011361 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2023-06-07 13:03 | 2023-06-07 13:09 | 1295 | 0:06 | T | ALIMENTADOR AMARRADO | DISPARO SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL SU CARGA POR 1424-08 | S23060700795 | New_Event | Feeder Load Transferred | Include | Include | Other | 6 | 2023-06-07 | 7770 | keep | 0 | Jun | 2023 | 0.0052921 | 0.00088202 | Sustained | FALSE | FALSE | Not_TMED_Event | 1295
SAN JUAN | 2023-06-07 13:03 | 2023-06-07 13:09 | 9 | 0:06 | T | NO SE REPORTO CAUSA | DISPARO SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL LLEVA 100% DEL 1401-10 LLEVA 100% DEL 1348-07 LLEVA 80% DEL 1348-06 Y 20% DEL 1336-08 | S23060700795 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2023-06-07 | 54 | keep | 0 | Jun | 2023 | 3.6779e-05 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2023-06-07 13:10 | 2023-06-07 17:18 | 15 | 4:08 | P | ANIMAL | 1 X 50 CRUCE POR AVE | B23060700675 | New_Event | Animals | Include | Include | Wildlife | 248 | 2023-06-07 | 3720 | keep | 0 | Jun | 2023 | 0.0025337 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-06-07 13:15 | 2023-06-07 13:45 | 45 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO | S23060700788 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-06-07 | 1350 | keep | 0 | Jun | 2023 | 0.00091948 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BARRANQUITAS | 2023-06-07 13:17 | 2023-06-07 13:20 | 3296 | 0:03 | T | NO SE REPORTO CAUSA | SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL LLEVA EL 9602-04 | C2306070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-06-07 | 9888 | keep | 0 | Jun | 2023 | 0.0067347 | 0.0022449 | Momentary | FALSE | FALSE | Not_TMED_Event | 3296
BARRANQUITAS | 2023-06-07 13:17 | 2023-06-07 13:20 | 2937 | 0:03 | T | ALIMENTADOR AMARRADO | SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL 9601-02 LLEVA EL 9602-04 | C2306070000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-06-07 | 8811 | keep | 0 | Jun | 2023 | 0.0060011 | 0.0020004 | Momentary | FALSE | FALSE | Not_TMED_Event | 2937
CANOVANAS | 2023-06-07 13:20 | 2023-06-07 15:36 | 20 | 2:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN XMR SE REMEPLAZO BAJANTE SECUNDARIO | P23060700702 | New_Event | Secondary Wire Break | Include | Include | Equipment | 136 | 2023-06-07 | 2720 | keep | 0 | Jun | 2023 | 0.0018526 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-06-07 13:29 | 2023-06-07 13:30 | 3350 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE BKR 20% DE SU CARGA ESTA X 2302-03 | R23060700352 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-07 | 3350 | keep | 0 | Jun | 2023 | 0.0022817 | 0.0022817 | Momentary | FALSE | FALSE | Not_TMED_Event | 3350
SAN JUAN | 2023-06-07 13:31 | 2023-06-07 13:32 | 2 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2306070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-07 | 2 | keep | 0 | Jun | 2023 | 1.3622e-06 | 1.3622e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2023-06-07 13:39 | 2023-06-07 20:13 | 50 | 6:34 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN C/L Y 1 X 8 EN XMR SE LEVANTO NEUTRAL PRIMARIO | C23060700438 | New_Event | Primary Wire Break | Include | Include | Equipment | 394 | 2023-06-07 | 19700 | keep | 0 | Jun | 2023 | 0.013418 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-06-07 13:45 | 2023-06-07 14:15 | 1 | 0:30 | P | NO SE REPORTO CAUSA | 2 SUM-20 DE 50 EN SU-5 NO CAUSA EVENTO TRANSFERIDO | P23060700715 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 30 | 2023-06-07 | 30 | keep | 0 | Jun | 2023 | 2.0433e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-06-07 13:56 | 2023-06-07 18:15 | 40 | 4:19 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A23060700364 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2023-06-07 | 10360 | keep | 0 | Jun | 2023 | 0.0070561 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-06-07 13:58 | 2023-06-07 14:20 | 60 | 0:22 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | R23060700357 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 22 | 2023-06-07 | 1320 | keep | 0 | Jun | 2023 | 0.00089905 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-06-07 14:02 | 2023-06-07 15:00 | 6 | 0:58 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | R23060700358 | New_Event | Animals | Include | Include | Wildlife | 58 | 2023-06-07 | 348 | keep | 0 | Jun | 2023 | 0.00023702 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-06-07 14:12 | 2023-06-07 15:37 | 12 | 1:25 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | R23060700359 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 85 | 2023-06-07 | 1020 | keep | 0 | Jun | 2023 | 0.00069472 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-06-07 14:12 | 2023-06-07 16:00 | 50 | 1:48 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23060700710 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2023-06-07 | 5400 | keep | 0 | Jun | 2023 | 0.0036779 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-06-07 14:20 | 2023-06-07 17:34 | 8 | 3:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REEMPLAZO CAJA PRIMARIA | C23060700450 | New_Event | Cutout Failure | Include | Include | Equipment | 194 | 2023-06-07 | 1552 | keep | 0 | Jun | 2023 | 0.0010571 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2023-06-07 14:24 | 2023-06-07 16:50 | 8 | 2:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 2 X 15 EN TRANSFORMADOR SE REPARO LINEAS SECUNDARIAS ROTAS | A23060700319 | New_Event | Secondary Wire Break | Include | Include | Equipment | 146 | 2023-06-07 | 1168 | keep | 0 | Jun | 2023 | 0.00079552 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-06-07 14:25 | 2023-06-07 17:00 | 10 | 2:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REMPLAZO BAJANTE SECUNDARIO | B23060700717 | New_Event | Secondary Wire Break | Include | Include | Equipment | 155 | 2023-06-07 | 1550 | keep | 0 | Jun | 2023 | 0.0010557 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-06-07 14:26 | 2023-06-07 16:46 | 1 | 2:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 50 EN RISER SE REEMPLAZO CAJA PRIMARIA | P23060700732 | New_Event | Cutout Failure | Include | Include | Equipment | 140 | 2023-06-07 | 140 | keep | 0 | Jun | 2023 | 9.5353e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-06-07 14:37 | 2023-06-07 18:12 | 129 | 3:35 | P | ANIMAL | 1 X 65 EN C/L 1 X 80 EN C/L Y 1 X 100 C/L CRUCE X AVE REMPLAZO CAJA AVERIADA | C23060700457 | New_Event | Animals | Include | Include | Wildlife | 215 | 2023-06-07 | 27735 | keep | 0 | Jun | 2023 | 0.01889 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
VEGA BAJA | 2023-06-07 14:40 | 2023-06-07 21:50 | 30 | 7:10 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA | A23060700381 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 430 | 2023-06-07 | 12900 | keep | 0 | Jun | 2023 | 0.0087861 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-06-07 14:45 | 2023-06-07 15:30 | 2 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | S23060700825 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2023-06-07 | 90 | keep | 0 | Jun | 2023 | 6.1299e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-06-07 14:45 | 2023-06-07 17:14 | 8 | 2:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR SE REMPLAZO SECUNDARIA | B23060700722 | New_Event | Secondary Wire Break | Include | Include | Equipment | 149 | 2023-06-07 | 1192 | keep | 0 | Jun | 2023 | 0.00081187 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-06-07 14:52 | 2023-06-07 17:21 | 1 | 2:29 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | M23060700553 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 149 | 2023-06-07 | 149 | keep | 0 | Jun | 2023 | 0.00010148 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-06-07 14:54 | 2023-06-07 16:35 | 200 | 1:41 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23060700556 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2023-06-07 | 20200 | keep | 0 | Jun | 2023 | 0.013758 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-06-07 15:06 | 2023-06-07 17:33 | 13 | 2:27 | P | ANIMAL | 1 X 50 EN TRANSFORMADOR PICHON CRUZO FASE | S23060700841 | New_Event | Animals | Include | Include | Wildlife | 147 | 2023-06-07 | 1911 | keep | 0 | Jun | 2023 | 0.0013016 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-06-07 15:06 | 2023-06-08 02:49 | 28 | 11:43 | P | SOBRECARGA | 1 X 30 EN C/L POR CARGA | S23060700840 | New_Event | Trip Due To Overload | Include | Include | Other | 703 | 2023-06-07 | 19684 | keep | 0 | Jun | 2023 | 0.013407 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
AGUADILLA | 2023-06-07 15:14 | 2023-06-07 18:20 | 200 | 3:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE AVERIADO | A23060700396 | New_Event | Cutout Failure | Include | Include | Equipment | 186 | 2023-06-07 | 37200 | keep | 0 | Jun | 2023 | 0.025337 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2023-06-07 15:15 | 2023-06-07 19:45 | 25 | 4:30 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M23060700574 | New_Event | Vegetation Contact | Include | Include | Vegetation | 270 | 2023-06-07 | 6750 | keep | 0 | Jun | 2023 | 0.0045974 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-06-07 15:45 | 2023-06-07 18:37 | 100 | 2:52 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO CAUSA | S23060700852 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 172 | 2023-06-07 | 17200 | keep | 0 | Jun | 2023 | 0.011715 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-06-07 15:46 | 2023-06-08 04:07 | 60 | 12:21 | P | OTRAS CAUSAS | 1X65 EN C/L POR CARGA POR TEMPERATURA | B23060700751 | New_Event | Other Causes | Include | Include | Other | 741 | 2023-06-07 | 44460 | keep | 0 | Jun | 2023 | 0.030282 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2023-06-07 15:50 | 2023-06-07 16:18 | 8 | 0:28 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A23060700412 | New_Event | Vegetation Contact | Include | Include | Vegetation | 28 | 2023-06-07 | 224 | keep | 0 | Jun | 2023 | 0.00015257 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-06-07 16:04 | 2023-06-07 18:20 | 100 | 2:16 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23060700601 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 136 | 2023-06-07 | 13600 | keep | 0 | Jun | 2023 | 0.0092629 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-06-07 16:16 | 2023-06-07 16:17 | 199 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23060700428 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-07 | 199 | keep | 0 | Jun | 2023 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
SAN JUAN | 2023-06-07 16:20 | 2023-06-07 16:45 | 1 | 0:25 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE TRANSFORMADOR PARA CERRAR PUENTE DE LINEA A CAJA TRANSFORMADOR S23060700687 | S23060700898 | New_Event | Primary Wire Break | Include | Include | Equipment | 25 | 2023-06-07 | 25 | keep | 0 | Jun | 2023 | 1.7027e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-06-07 16:26 | 2023-06-07 17:42 | 10 | 1:16 | P | DESGANCHE | 1 X 80 EN C/L Y DESGANCHE | B23060700776 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2023-06-07 | 760 | keep | 0 | Jun | 2023 | 0.00051763 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-06-07 16:35 | 2023-06-07 20:39 | 10 | 4:04 | P | TRANSFORMADOR AVERIADO | 1 X 15 EN XMR REEMPLAZO DE XMR 37.5KVA X 37.5KVA | P23060700797 | New_Event | Service Transformer Failure | Include | Include | Equipment | 244 | 2023-06-07 | 2440 | keep | 0 | Jun | 2023 | 0.0016619 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-06-07 16:50 | 2023-06-07 17:30 | 7 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REMPLAZO DE BAJANTE SECUANDARIO | B23060700916 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2023-06-07 | 280 | keep | 0 | Jun | 2023 | 0.00019071 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-06-07 16:56 | 2023-06-07 18:00 | 1 | 1:04 | P | PROBLEMA DEL CLIENTE | PROBLEMA INTERNO DEL CLIENTE | S23060700919 | New_Event | Customer-Related Interruption | Include | Include | Public | 64 | 2023-06-07 | 64 | keep | 0 | Jun | 2023 | 4.359e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-06-07 17:20 | 2023-06-07 17:40 | 1035 | 0:20 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO MACHETES PARA CERRAR PUENTES ABIERTOS | R23060700291 | Additional_clients | Primary Pole Failure | Include | Include | Equipment | 20 | 2023-06-07 | 20700 | keep | 0 | Jun | 2023 | 0.014099 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-07 17:30 | 2023-06-07 17:31 | 959 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DEL 1904-07 CARGA POR 1904-07 | B2306070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-07 | 959 | keep | 0 | Jun | 2023 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-06-07 17:30 | 2023-06-07 17:31 | 1264 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1904-07 CARGA POR 1904-07 | B2306070000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-07 | 1264 | keep | 0 | Jun | 2023 | 0.0008609 | 0.0008609 | Momentary | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2023-06-07 17:30 | 2023-06-07 17:31 | 620 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1904-07 CARGA POR 1904-07 | B2306070000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-07 | 620 | keep | 0 | Jun | 2023 | 0.00042228 | 0.00042228 | Momentary | FALSE | FALSE | Not_TMED_Event | 620
BAYAMON | 2023-06-07 17:31 | 2023-06-07 19:48 | 7 | 2:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REMPLAZO DE BAJANTE SECUANDARIO | B23060700916 | Partial_restoration | Secondary Wire Break | Include | Include | Equipment | 137 | 2023-06-07 | 959 | keep | 0 | Jun | 2023 | 0.00065317 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-06-07 17:40 | 2023-06-07 17:48 | 180 | 0:08 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REALIZO OPERACONES PARA NORMALIZAR | R23060700291 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 8 | 2023-06-07 | 1440 | keep | 0 | Jun | 2023 | 0.00098078 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-06-07 17:58 | 2023-06-07 19:33 | 1 | 1:35 | P | DESGANCHE | 2 X 50 EN RISER | C23060700531 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2023-06-07 | 95 | keep | 0 | Jun | 2023 | 6.4704e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-06-07 18:23 | 2023-06-07 19:10 | 15 | 0:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO BAJANTES SECUNDARIOS Y SECUNDARIA | R23060700187 | New_Event | Secondary Wire Break | Include | Include | Equipment | 47 | 2023-06-07 | 705 | keep | 0 | Jun | 2023 | 0.00048017 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-06-07 18:30 | 2023-06-07 21:10 | 200 | 2:40 | P | SOBRECARGA | 2 X 140 EN CORTE DE LINEA SE MIDIO AMPERAJE, UNA FASE MIDIO 134AMP Y LA OTRA 40AMP Y TENIAN FUSIBLE DE 100AMP | M23060700642 | New_Event | Trip Due To Overload | Include | Include | Other | 160 | 2023-06-07 | 32000 | keep | 0 | Jun | 2023 | 0.021795 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-06-07 18:46 | 2023-06-07 19:05 | 52 | 0:19 | P | DESGANCHE | 2 X 100 EN CONVERTIDOR DESGANCHE | S23060700984 | New_Event | Vegetation Contact | Include | Include | Vegetation | 19 | 2023-06-07 | 988 | keep | 0 | Jun | 2023 | 0.00067292 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
CAGUAS | 2023-06-07 18:50 | 2023-06-07 20:38 | 17 | 1:48 | P | CAUSAS EXTERNAS | ABRIO XMR PARA LEVANTAR SECUNDARIA AVERIADA POR CAMION Y REMPLAZO BAJANTE SECUNDARIO | C23060700558 | New_Event | Damage From Public | Include | Include | Public | 108 | 2023-06-07 | 1836 | keep | 0 | Jun | 2023 | 0.0012505 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
GUAYAMA | 2023-06-07 18:50 | 2023-06-07 20:03 | 25 | 1:13 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO | P23060700916 | New_Event | Primary Wire Break | Include | Include | Equipment | 73 | 2023-06-07 | 1825 | keep | 0 | Jun | 2023 | 0.001243 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2023-06-07 18:56 | 2023-06-07 20:48 | 417 | 1:52 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA POR DESGANCHE | P23060700921 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2023-06-07 | 46704 | keep | 0 | Jun | 2023 | 0.03181 | 0.00028402 | Sustained | FALSE | FALSE | Not_TMED_Event | 417
BARRANQUITAS | 2023-06-07 19:00 | 2023-06-07 20:03 | 16 | 1:03 | P | TRANSFORMADOR AVERIADO | SE SECCIONALIZO XMR AVERIADO Y SE TRANSFIRIO LA CARGA | C23060700561 | New_Event | Service Transformer Failure | Include | Include | Equipment | 63 | 2023-06-07 | 1008 | keep | 0 | Jun | 2023 | 0.00068654 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
AGUADILLA | 2023-06-07 19:00 | 2023-06-07 19:10 | 10 | 0:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON BARRAS SECUNDARIAS AVERIADAS SE CERRO TRANSFORMADOR | A23060700479 | New_Event | Secondary Wire Break | Include | Include | Equipment | 10 | 2023-06-07 | 100 | keep | 0 | Jun | 2023 | 6.811e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-06-07 19:14 | 2023-06-07 21:26 | 16 | 2:12 | P | NO SE REPORTO CAUSA | 1 X 80 C/L | B23060700876 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 132 | 2023-06-07 | 2112 | keep | 0 | Jun | 2023 | 0.0014385 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2023-06-07 19:25 | 2023-06-08 19:18 | 10 | 23:53 | P | CABLE SOTERRADO AVERIADO | BY - 230608-01 SE REPARO TRAMO SOTERRADO AVERIADO DEL SU-17 @ T-11 | B23060700895 | New_Event | UG Cable Fault | Include | Include | Equipment | 1433 | 2023-06-07 | 14330 | keep | 0 | Jun | 2023 | 0.0097601 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-06-07 19:28 | 2023-06-07 22:16 | 86 | 2:48 | P | DESGANCHE | 1 X 100 EN C/L DESGANCE | S23060701005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2023-06-07 | 14448 | keep | 0 | Jun | 2023 | 0.0098405 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
CANOVANAS | 2023-06-07 19:33 | 2023-06-07 21:11 | 13 | 1:38 | P | TRANSFORMADOR AVERIADO | 1 X 8 EN XMR SE REEMPLAZO XMR DE 37.5KVA X 37.5KVA | R23060700471 | New_Event | Service Transformer Failure | Include | Include | Equipment | 98 | 2023-06-07 | 1274 | keep | 0 | Jun | 2023 | 0.00086772 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2023-06-07 19:43 | 2023-06-07 22:56 | 65 | 3:13 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B23060700915 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 193 | 2023-06-07 | 12545 | keep | 0 | Jun | 2023 | 0.0085443 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
PONCE | 2023-06-07 20:09 | 2023-06-07 20:17 | 1952 | 0:08 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | P23060700993 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2023-06-07 | 15616 | keep | 0 | Jun | 2023 | 0.010636 | 0.0013295 | Sustained | FALSE | FALSE | Not_TMED_Event | 1952
MAYAGÃœEZ | 2023-06-07 20:14 | 2023-06-07 22:33 | 100 | 2:19 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23060700699 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2023-06-07 | 13900 | keep | 0 | Jun | 2023 | 0.0094672 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-06-07 20:21 | 2023-06-07 21:16 | 466 | 0:55 | T | ALIMENTADOR AMARRADO | RELEVO POR DEFICIENCIA GENERACION CARGA POR 1116-04 | S23060701055 | New_Event | Feeder Load Transferred | Include | Include | Other | 55 | 2023-06-07 | 25630 | keep | 0 | Jun | 2023 | 0.017456 | 0.00031739 | Sustained | FALSE | FALSE | Not_TMED_Event | 466
ARECIBO | 2023-06-07 20:22 | 2023-06-07 21:32 | 12 | 1:10 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR NO SE REPORTO CAUSA | A23060700505 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 70 | 2023-06-07 | 840 | keep | 0 | Jun | 2023 | 0.00057212 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2023-06-07 20:26 | 2023-06-07 22:00 | 60 | 1:34 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | A23060700506 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 94 | 2023-06-07 | 5640 | keep | 0 | Jun | 2023 | 0.0038414 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-06-07 20:33 | 2023-06-08 08:40 | 11 | 12:07 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | A23060700508 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 727 | 2023-06-07 | 7997 | keep | 0 | Jun | 2023 | 0.0054467 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2023-06-07 20:39 | 2023-06-08 02:06 | 100 | 5:27 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23060700721 | New_Event | Vegetation Contact | Include | Include | Vegetation | 327 | 2023-06-07 | 32700 | keep | 0 | Jun | 2023 | 0.022272 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-06-07 20:54 | 2023-06-07 21:42 | 250 | 0:48 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A23060700516 | New_Event | Vegetation Contact | Include | Include | Vegetation | 48 | 2023-06-07 | 12000 | keep | 0 | Jun | 2023 | 0.0081731 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2023-06-07 20:55 | 2023-06-07 22:17 | 28 | 1:22 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23060700109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 82 | 2023-06-07 | 2296 | keep | 0 | Jun | 2023 | 0.0015638 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
SAN JUAN | 2023-06-07 20:55 | 2023-06-08 02:25 | 172 | 5:30 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S23060701095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 330 | 2023-06-07 | 56760 | keep | 0 | Jun | 2023 | 0.038659 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
ARECIBO | 2023-06-07 20:58 | 2023-06-07 22:20 | 8 | 1:22 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA CRUZADA | A23060700518 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 82 | 2023-06-07 | 656 | keep | 0 | Jun | 2023 | 0.0004468 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-06-07 21:00 | 2023-06-08 03:14 | 200 | 6:14 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23060700734 | New_Event | Vegetation Contact | Include | Include | Vegetation | 374 | 2023-06-07 | 74800 | keep | 0 | Jun | 2023 | 0.050946 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-06-07 21:01 | 2023-06-08 13:19 | 120 | 16:18 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | S23060701104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 978 | 2023-06-07 | 117360 | keep | 0 | Jun | 2023 | 0.079933 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CAGUAS | 2023-06-07 21:01 | 2023-06-08 10:08 | 112 | 13:07 | P | CABLE SOTERRADO AVERIADO | AVERIA DEL SU12 AL SU13 SE CERRO N/O DEL SU15 AL SU13 | C23060700595 | New_Event | UG Cable Fault | Include | Include | Equipment | 787 | 2023-06-07 | 88144 | keep | 0 | Jun | 2023 | 0.060034 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
VEGA BAJA | 2023-06-07 21:05 | 2023-06-07 23:43 | 150 | 2:38 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B23060700983 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 158 | 2023-06-07 | 23700 | keep | 0 | Jun | 2023 | 0.016142 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-06-07 21:14 | 2023-06-08 10:03 | 7 | 12:49 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR AVE CRUZO LINEAS | M23060700752 | New_Event | Animals | Include | Include | Wildlife | 769 | 2023-06-07 | 5383 | keep | 0 | Jun | 2023 | 0.0036663 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-06-07 21:18 | 2023-06-07 22:39 | 341 | 1:21 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B23060700993 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2023-06-07 | 27621 | keep | 0 | Jun | 2023 | 0.018813 | 0.00023225 | Sustained | FALSE | FALSE | Not_TMED_Event | 341
AGUADILLA | 2023-06-07 21:20 | 2023-06-07 23:18 | 400 | 1:58 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23060700758 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2023-06-07 | 47200 | keep | 0 | Jun | 2023 | 0.032148 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
MAYAGÃœEZ | 2023-06-07 21:46 | 2023-06-08 02:24 | 50 | 4:38 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | M23060700802 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 278 | 2023-06-07 | 13900 | keep | 0 | Jun | 2023 | 0.0094672 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-06-07 21:52 | 2023-06-08 04:53 | 30 | 7:01 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE LINEA A CAJA 1X100 | S23060701140 | New_Event | Primary Wire Break | Include | Include | Equipment | 421 | 2023-06-07 | 12630 | keep | 0 | Jun | 2023 | 0.0086022 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-06-07 21:58 | 2023-06-08 00:55 | 100 | 2:57 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/ | B23060701018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 177 | 2023-06-07 | 17700 | keep | 0 | Jun | 2023 | 0.012055 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-06-07 22:02 | 2023-06-08 09:52 | 14 | 11:50 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L SE REEMPLAZO DISCO PARTIDO. | R23060700529 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 710 | 2023-06-07 | 9940 | keep | 0 | Jun | 2023 | 0.0067701 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2023-06-07 22:08 | 2023-06-08 01:36 | 15 | 3:28 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23060701023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 208 | 2023-06-07 | 3120 | keep | 0 | Jun | 2023 | 0.002125 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-06-07 22:45 | 2023-06-08 01:22 | 150 | 2:37 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23060700868 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2023-06-07 | 23550 | keep | 0 | Jun | 2023 | 0.01604 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-06-07 22:52 | 2023-06-07 22:54 | 603 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 9206-09 | B23060701036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-07 | 1206 | keep | 0 | Jun | 2023 | 0.0008214 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
BAYAMON | 2023-06-07 22:52 | 2023-06-07 22:54 | 6 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 9206-08 | B23060701036 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-06-07 | 12 | keep | 0 | Jun | 2023 | 8.1731e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-06-07 23:03 | 2023-06-08 01:30 | 100 | 2:27 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | M23060700878 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2023-06-07 | 14700 | keep | 0 | Jun | 2023 | 0.010012 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-06-07 23:05 | 2023-06-08 01:38 | 40 | 2:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23060700880 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2023-06-07 | 6120 | keep | 0 | Jun | 2023 | 0.0041683 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2023-06-07 23:07 | 2023-06-07 23:08 | 1234 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R2306070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-07 | 1234 | keep | 0 | Jun | 2023 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
SAN JUAN | 2023-06-07 23:44 | 2023-06-08 10:43 | 112 | 10:59 | P | DESGANCHE | 1 X 50 EN RISER 1 X 65 EN CORTE DE LINEA DESGANCHE | S23060701143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 659 | 2023-06-07 | 73808 | keep | 0 | Jun | 2023 | 0.05027 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
AGUADILLA | 2023-06-07 23:50 | 2023-06-08 10:40 | 500 | 10:50 | P | DESGANCHE | SE AISLO LA AVERIA Y SE ENERGIZO PARTE DE LA CARGA A TRAVES DE UN NORMALLY-OPEN | M23060700895 | New_Event | Vegetation Contact | Include | Include | Vegetation | 650 | 2023-06-07 | 325000 | keep | 0 | Jun | 2023 | 0.22136 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
AGUADILLA | 2023-06-07 23:54 | 2023-06-08 11:00 | 8 | 11:06 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 10 KVA X 15 KVA | M23060700896 | New_Event | Service Transformer Failure | Include | Include | Equipment | 666 | 2023-06-07 | 5328 | keep | 0 | Jun | 2023 | 0.0036289 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-06-08 00:46 | 2023-06-08 11:25 | 50 | 10:39 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO CAUSA | S23060800004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 639 | 2023-06-08 | 31950 | keep | 0 | Jun | 2023 | 0.021761 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-06-08 01:26 | 2023-06-08 11:20 | 16 | 9:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B23060800005 | New_Event | Cutout Failure | Include | Include | Equipment | 594 | 2023-06-08 | 9504 | keep | 0 | Jun | 2023 | 0.0064731 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
ARECIBO | 2023-06-08 01:34 | 2023-06-08 15:20 | 8 | 13:46 | P | OTRAS CAUSAS | 1 X 20 EN TRANSFORMADOR FUSOBLE PODRIDO | A23060800002 | New_Event | Other Causes | Include | Include | Other | 826 | 2023-06-08 | 6608 | keep | 0 | Jun | 2023 | 0.0045007 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-06-08 01:39 | 2023-06-08 14:07 | 18 | 12:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23060800006 | New_Event | Secondary Wire Break | Include | Include | Equipment | 748 | 2023-06-08 | 13464 | keep | 0 | Jun | 2023 | 0.0091703 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
ARECIBO | 2023-06-08 02:22 | 2023-06-08 09:05 | 60 | 6:43 | P | OTRAS CAUSAS | 1 X 65 EN CORTE DE LINEA FUSIBLE CORROIDO | A23060800004 | New_Event | Other Causes | Include | Include | Other | 403 | 2023-06-08 | 24180 | keep | 0 | Jun | 2023 | 0.016469 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-06-08 02:29 | 2023-06-08 05:24 | 75 | 2:55 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A23060800005 | New_Event | Primary Wire Break | Include | Include | Equipment | 175 | 2023-06-08 | 13125 | keep | 0 | Jun | 2023 | 0.0089394 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2023-06-08 03:04 | 2023-06-08 07:28 | 40 | 4:24 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23060800004 | New_Event | Animals | Include | Include | Wildlife | 264 | 2023-06-08 | 10560 | keep | 0 | Jun | 2023 | 0.0071924 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-06-08 04:00 | 2023-06-08 14:31 | 40 | 10:31 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23060800013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 631 | 2023-06-08 | 25240 | keep | 0 | Jun | 2023 | 0.017191 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-06-08 04:25 | 2023-06-08 09:28 | 114 | 5:03 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | S23060800017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 303 | 2023-06-08 | 34542 | keep | 0 | Jun | 2023 | 0.023526 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
BARRANQUITAS | 2023-06-08 05:40 | 2023-06-08 18:08 | 15 | 12:28 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 15 A 25KVA | C23060800007 | New_Event | Service Transformer Failure | Include | Include | Equipment | 748 | 2023-06-08 | 11220 | keep | 0 | Jun | 2023 | 0.0076419 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-06-08 05:55 | 2023-06-08 12:30 | 80 | 6:35 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CORTE DE LINEA | M23060800019 | New_Event | Primary Wire Break | Include | Include | Equipment | 395 | 2023-06-08 | 31600 | keep | 0 | Jun | 2023 | 0.021523 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-06-08 06:00 | 2023-06-08 06:02 | 3708 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 75% DE SU CARGA | S23060800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-08 | 7416 | keep | 0 | Jun | 2023 | 0.005051 | 0.0025255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3708
AGUADILLA | 2023-06-08 06:11 | 2023-06-08 13:15 | 40 | 7:04 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23060800021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 424 | 2023-06-08 | 16960 | keep | 0 | Jun | 2023 | 0.011551 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-06-08 06:39 | 2023-06-08 13:00 | 350 | 6:21 | P | CONDUCTOR ROTO O ABIERTO | ALAMBRE PARTIDO | M23060800023 | New_Event | Primary Wire Break | Include | Include | Equipment | 381 | 2023-06-08 | 133350 | keep | 0 | Jun | 2023 | 0.090824 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
MAYAGÃœEZ | 2023-06-08 06:44 | 2023-06-08 12:05 | 200 | 5:21 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23060800025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 321 | 2023-06-08 | 64200 | keep | 0 | Jun | 2023 | 0.043726 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2023-06-08 07:00 | 2023-06-08 09:13 | 7 | 2:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR Y SE REEMPLAZO CAJA PRIMARIA. | R23060800005 | New_Event | Cutout Failure | Include | Include | Equipment | 133 | 2023-06-08 | 931 | keep | 0 | Jun | 2023 | 0.0006341 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-06-08 07:10 | 2023-06-08 15:25 | 8 | 8:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA QUEMADA | C23060800017 | New_Event | Cutout Failure | Include | Include | Equipment | 495 | 2023-06-08 | 3960 | keep | 0 | Jun | 2023 | 0.0026971 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-06-08 07:11 | 2023-06-08 08:00 | 3 | 0:49 | P | ANIMAL | 1 X 50 EN SU-A POR AVE | B23060800026 | New_Event | Animals | Include | Include | Wildlife | 49 | 2023-06-08 | 147 | keep | 0 | Jun | 2023 | 0.00010012 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2023-06-08 07:19 | 2023-06-08 14:55 | 45 | 7:36 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | M23060800039 | New_Event | Animals | Include | Include | Wildlife | 456 | 2023-06-08 | 20520 | keep | 0 | Jun | 2023 | 0.013976 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
HUMACAO | 2023-06-08 07:23 | 2023-06-08 08:28 | 30 | 1:05 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | P23060800029 | New_Event | Animals | Include | Include | Wildlife | 65 | 2023-06-08 | 1950 | keep | 0 | Jun | 2023 | 0.0013281 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-06-08 07:46 | 2023-06-08 09:45 | 10 | 1:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN XMR SE REMPLAZO PORTAFUSIBLES | B23060800036 | New_Event | Cutout Failure | Include | Include | Equipment | 119 | 2023-06-08 | 1190 | keep | 0 | Jun | 2023 | 0.0008105 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-06-08 07:50 | 2023-06-08 15:01 | 10 | 7:11 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFOMADOR QUEMADO DE 25 X 50KVA | C23060800083 | New_Event | Service Transformer Failure | Include | Include | Equipment | 431 | 2023-06-08 | 4310 | keep | 0 | Jun | 2023 | 0.0029355 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-06-08 07:53 | 2023-06-08 15:50 | 15 | 7:57 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | A23060800027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 477 | 2023-06-08 | 7155 | keep | 0 | Jun | 2023 | 0.0048732 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-06-08 07:56 | 2023-06-08 12:25 | 1 | 4:29 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | B23060800037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 269 | 2023-06-08 | 269 | keep | 0 | Jun | 2023 | 0.00018321 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-06-08 07:57 | 2023-06-08 10:44 | 30 | 2:47 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN C/L FIJO CONDUCTOR | P23060800044 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 167 | 2023-06-08 | 5010 | keep | 0 | Jun | 2023 | 0.0034123 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-06-08 08:02 | 2023-06-08 08:06 | 1058 | 0:04 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% DEL 1401-10 LLEVA 100% DEL 1348-7 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 | S23060800064 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-06-08 | 4232 | keep | 0 | Jun | 2023 | 0.0028824 | 0.0007206 | Momentary | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2023-06-08 08:02 | 2023-06-08 08:06 | 1000 | 0:04 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% DEL 1401-10 LLEVA 100% DEL 1348-7 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 | S23060800064 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-06-08 | 4000 | keep | 0 | Jun | 2023 | 0.0027244 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2023-06-08 08:02 | 2023-06-08 08:06 | 278 | 0:04 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% DEL 1401-10 LLEVA 100% DEL 1348-7 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 | S23060800064 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-06-08 | 1112 | keep | 0 | Jun | 2023 | 0.00075738 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2023-06-08 08:02 | 2023-06-08 08:06 | 1295 | 0:04 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% DEL 1401-10 LLEVA 100% DEL 1348-7 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 | S23060800064 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-06-08 | 5180 | keep | 0 | Jun | 2023 | 0.0035281 | 0.00088202 | Momentary | FALSE | FALSE | Not_TMED_Event | 1295
SAN JUAN | 2023-06-08 08:02 | 2023-06-08 08:06 | 9 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 100% DEL 1401-10 LLEVA 100% DEL 1348-7 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 | S23060800064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-06-08 | 36 | keep | 0 | Jun | 2023 | 2.4519e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2023-06-08 08:04 | 2023-06-08 08:06 | 2531 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO POR CONTROL | R2306080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-08 | 5062 | keep | 0 | Jun | 2023 | 0.0034477 | 0.0017239 | Momentary | FALSE | FALSE | Not_TMED_Event | 2531
SAN JUAN | 2023-06-08 08:06 | 2023-06-08 12:21 | 50 | 4:15 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO CAUSA | S23060800092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 255 | 2023-06-08 | 12750 | keep | 0 | Jun | 2023 | 0.008684 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-06-08 08:09 | 2023-06-08 14:18 | 50 | 6:09 | P | CABLE SOTERRADO AVERIADO | 1 X 25 SM4 EN SU 2 AVERIA NUEVA DE T9@ T8 AVERIA VIEJA DE T6 A T7 | R23060800010 | New_Event | UG Cable Fault | Include | Include | Equipment | 369 | 2023-06-08 | 18450 | keep | 0 | Jun | 2023 | 0.012566 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-06-08 08:11 | 2023-06-08 09:04 | 20 | 0:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L Y SE REEMPLAZO CAJA PRIMARIA | R23060800012 | New_Event | Cutout Failure | Include | Include | Equipment | 53 | 2023-06-08 | 1060 | keep | 0 | Jun | 2023 | 0.00072196 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-06-08 08:25 | 2023-06-08 15:08 | 120 | 6:43 | P | DESGANCHE | 1 X 40 Y 1 X 65 EN CORTES DE LINEA | C23060800025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 403 | 2023-06-08 | 48360 | keep | 0 | Jun | 2023 | 0.032938 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
UTUADO | 2023-06-08 08:26 | 2023-06-08 12:05 | 1 | 3:39 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | A23060800033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 219 | 2023-06-08 | 219 | keep | 0 | Jun | 2023 | 0.00014916 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-06-08 08:30 | 2023-06-08 12:45 | 4 | 4:15 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTES PRIMARIOS | M23060800072 | New_Event | Primary Wire Break | Include | Include | Equipment | 255 | 2023-06-08 | 1020 | keep | 0 | Jun | 2023 | 0.00069472 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2023-06-08 08:30 | 2023-06-08 10:53 | 30 | 2:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | M23060800071 | New_Event | Cutout Failure | Include | Include | Equipment | 143 | 2023-06-08 | 4290 | keep | 0 | Jun | 2023 | 0.0029219 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-06-08 08:30 | 2023-06-08 08:55 | 8 | 0:25 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS AVERIADAS | M23060800012 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 25 | 2023-06-08 | 200 | keep | 0 | Jun | 2023 | 0.00013622 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-06-08 08:52 | 2023-06-08 18:40 | 8 | 9:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO BAJANTE SECUNDARIO QUEMADO | C23060800033 | New_Event | Secondary Wire Break | Include | Include | Equipment | 588 | 2023-06-08 | 4704 | keep | 0 | Jun | 2023 | 0.0032039 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-06-08 08:57 | 2023-06-08 11:57 | 60 | 3:00 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR CULEBRA | R23060800020 | New_Event | Animals | Include | Include | Wildlife | 180 | 2023-06-08 | 10800 | keep | 0 | Jun | 2023 | 0.0073558 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2023-06-08 08:59 | 2023-06-08 11:25 | 30 | 2:26 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSO | A23060800040 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 146 | 2023-06-08 | 4380 | keep | 0 | Jun | 2023 | 0.0029832 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-06-08 08:59 | 2023-06-08 12:06 | 54 | 3:07 | P | ANIMAL | 1 X 30 EN C/L AVE CRUZADA | B23060800054 | New_Event | Animals | Include | Include | Wildlife | 187 | 2023-06-08 | 10098 | keep | 0 | Jun | 2023 | 0.0068777 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
CANOVANAS | 2023-06-08 09:00 | 2023-06-08 13:06 | 7 | 4:06 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTES SECUNDARIOS. | R23060800021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 246 | 2023-06-08 | 1722 | keep | 0 | Jun | 2023 | 0.0011728 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2023-06-08 09:05 | 2023-06-08 12:30 | 10 | 3:25 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA DE TRANSFORMADOR | A23060800057 | New_Event | Primary Wire Break | Include | Include | Equipment | 205 | 2023-06-08 | 2050 | keep | 0 | Jun | 2023 | 0.0013962 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-06-08 09:07 | 2023-06-08 17:48 | 105 | 8:41 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23060800058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 521 | 2023-06-08 | 54705 | keep | 0 | Jun | 2023 | 0.037259 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
UTUADO | 2023-06-08 09:12 | 2023-06-08 14:25 | 75 | 5:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA FUERTES VIENTOS | A23060800042 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 313 | 2023-06-08 | 23475 | keep | 0 | Jun | 2023 | 0.015989 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BARRANQUITAS | 2023-06-08 09:21 | 2023-06-08 19:10 | 5 | 9:49 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | C23060800046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 589 | 2023-06-08 | 2945 | keep | 0 | Jun | 2023 | 0.0020058 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-06-08 09:23 | 2023-06-08 12:37 | 24 | 3:14 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO PM DE 75 KVA POR 75 KVA | R23060800029 | New_Event | Service Transformer Failure | Include | Include | Equipment | 194 | 2023-06-08 | 4656 | keep | 0 | Jun | 2023 | 0.0031712 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
SAN JUAN | 2023-06-08 09:31 | 2023-06-08 13:18 | 101 | 3:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA | S23060800107 | New_Event | Cutout Failure | Include | Include | Equipment | 227 | 2023-06-08 | 22927 | keep | 0 | Jun | 2023 | 0.015615 | 6.8791e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 101
BAYAMON | 2023-06-08 09:34 | 2023-06-08 11:00 | 6 | 1:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REPARO SECUNDARIA | S23060800108 | New_Event | Secondary Wire Break | Include | Include | Equipment | 86 | 2023-06-08 | 516 | keep | 0 | Jun | 2023 | 0.00035145 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-06-08 10:00 | 2023-06-08 10:15 | 48 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO | S23060800015 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2023-06-08 | 720 | keep | 0 | Jun | 2023 | 0.00049039 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
BAYAMON | 2023-06-08 10:01 | 2023-06-08 19:03 | 130 | 9:02 | P | CAUSAS EXTERNAS | 3 X 80 SE REMPAZO POSTE PRIMARIO IMPACTADO POR CAMION | P23060800118 | New_Event | Damage From Public | Include | Include | Public | 542 | 2023-06-08 | 70460 | keep | 0 | Jun | 2023 | 0.04799 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
SAN JUAN | 2023-06-08 10:05 | 2023-06-08 12:52 | 20 | 2:47 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER NO CAUSA | S23060800123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 167 | 2023-06-08 | 3340 | keep | 0 | Jun | 2023 | 0.0022749 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-06-08 10:08 | 2023-06-08 10:09 | 1709 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23060800060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-08 | 1709 | keep | 0 | Jun | 2023 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
CAGUAS | 2023-06-08 10:09 | 2023-06-08 15:22 | 112 | 5:13 | P | CABLE SOTERRADO AVERIADO | AVERIA DEL SU12 AL SU13 SE CERRO N/O DEL SU15 AL SU13 | C23060700595 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 313 | 2023-06-08 | 35056 | keep | 0 | Jun | 2023 | 0.023876 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-06-08 10:12 | 2023-06-08 13:40 | 30 | 3:28 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO PALMA | A23060800068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2023-06-08 | 6240 | keep | 0 | Jun | 2023 | 0.00425 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-06-08 10:15 | 2023-06-08 11:30 | 8 | 1:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO Y SE LEVANTO SECUNDARIO | S23060701143 | New_Event | Secondary Wire Break | Include | Include | Equipment | 75 | 2023-06-08 | 600 | keep | 0 | Jun | 2023 | 0.00040866 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2023-06-08 10:22 | 2023-06-08 18:56 | 5 | 8:34 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE PRIMARIO Y 3 X 30 EN C/L | R23060800039 | New_Event | Primary Pole Failure | Include | Include | Equipment | 514 | 2023-06-08 | 2570 | keep | 0 | Jun | 2023 | 0.0017504 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2023-06-08 10:29 | 2023-06-08 15:34 | 70 | 5:05 | P | DESGANCHE | EVENTO TRANSFERIDO DE PONCE 1 X 40 EN CORTE DE LINEA | P23060800162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 305 | 2023-06-08 | 21350 | keep | 0 | Jun | 2023 | 0.014541 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2023-06-08 10:36 | 2023-06-08 16:00 | 3 | 5:24 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR POSTE SECUNDARIO PARTIDO | M23060800158 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 324 | 2023-06-08 | 972 | keep | 0 | Jun | 2023 | 0.00066202 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2023-06-08 10:40 | 2023-06-08 16:25 | 225 | 5:45 | P | DESGANCHE | 1 X 200 EN CONVERTIDOR SE REALIZO DESGANCHE MASIVO | M23060700895 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 345 | 2023-06-08 | 77625 | keep | 0 | Jun | 2023 | 0.05287 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-06-08 10:47 | 2023-06-08 16:00 | 1 | 5:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN RISER | A23060800088 | New_Event | Cutout Failure | Include | Include | Equipment | 313 | 2023-06-08 | 313 | keep | 0 | Jun | 2023 | 0.00021318 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-06-08 10:53 | 2023-06-08 10:54 | 4882 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23060800172 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-08 | 4882 | keep | 0 | Jun | 2023 | 0.0033251 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
SAN JUAN | 2023-06-08 10:54 | 2023-06-08 12:11 | 716 | 1:17 | T | CAUSAS EXTERNAS | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S23060800151 | New_Event | Damage From Public | Include | Include | Public | 77 | 2023-06-08 | 55132 | keep | 0 | Jun | 2023 | 0.03755 | 0.00048766 | Sustained | FALSE | FALSE | Not_TMED_Event | 716
AGUADILLA | 2023-06-08 10:54 | 2023-06-08 12:40 | 30 | 1:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | M23060800071 | New_Event | Cutout Failure | Include | Include | Equipment | 106 | 2023-06-08 | 3180 | keep | 0 | Jun | 2023 | 0.0021659 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-06-08 11:06 | 2023-06-08 12:51 | 8 | 1:45 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA DESGANCHE | C23060800148 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 105 | 2023-06-08 | 840 | keep | 0 | Jun | 2023 | 0.00057212 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-06-08 11:09 | 2023-06-08 11:10 | 427 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISAPARO LINEA 10100 AL DISPARAR EL ALIMENTADOR 1531-02 POR POSTE PARTIDO POR CAMION SE AFECTO MOMENTANEAMENTE LINEA 10100 | S23060800169 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-08 | 427 | keep | 0 | Jun | 2023 | 0.00029083 | 0.00029083 | Momentary | FALSE | FALSE | Not_TMED_Event | 427
SAN JUAN | 2023-06-08 11:09 | 2023-06-08 11:10 | 867 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10100 AL DISPARAR EL ALIMENTADOR 1531-02 POR POSTE PARTIDO POR CAMION SE AFECTO MOMENTANEAMENTE LINEA 10100 | S23060800169 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-08 | 867 | keep | 0 | Jun | 2023 | 0.00059051 | 0.00059051 | Momentary | FALSE | FALSE | Not_TMED_Event | 867
SAN JUAN | 2023-06-08 11:09 | 2023-06-08 11:10 | 353 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISAPARO LINEA 10100 AL DISPARAR EL ALIMENTADOR 1531-02 POR POSTE PARTIDO POR CAMION SE AFECTO MOMENTANEAMENTE LINEA 10100 | S23060800169 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-08 | 353 | keep | 0 | Jun | 2023 | 0.00024043 | 0.00024043 | Momentary | FALSE | FALSE | Not_TMED_Event | 353
CANOVANAS | 2023-06-08 11:10 | 2023-06-08 13:54 | 99 | 2:44 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R23060800050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2023-06-08 | 16236 | keep | 0 | Jun | 2023 | 0.011058 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
BAYAMON | 2023-06-08 11:11 | 2023-06-08 12:04 | 2 | 0:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 30 EN C/L MAL TIEMPO VIENTOS | B23060800090 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 53 | 2023-06-08 | 106 | keep | 0 | Jun | 2023 | 7.2196e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2023-06-08 11:19 | 2023-06-08 13:45 | 7 | 2:26 | P | TRANSFORMADOR AVERIADO | SE ELIMINO XMR AVERIADO Y SE TRANSFIRIO LA CARGA. | C23060800082 | New_Event | Service Transformer Failure | Include | Include | Equipment | 146 | 2023-06-08 | 1022 | keep | 0 | Jun | 2023 | 0.00069608 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-06-08 11:22 | 2023-06-08 13:49 | 119 | 2:27 | P | DESGANCHE | DESGANCHE 2 X 100 EN CORTE DE LINEA | S23060800176 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2023-06-08 | 17493 | keep | 0 | Jun | 2023 | 0.011914 | 8.105e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 119
BAYAMON | 2023-06-08 11:29 | 2023-06-08 11:30 | 1270 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO Y SE CERRO POR SCADA 80% DEL 1711-01 POR EL 1717-03 | B23060800094 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-08 | 1270 | keep | 0 | Jun | 2023 | 0.00086499 | 0.00086499 | Momentary | FALSE | FALSE | Not_TMED_Event | 1270
BAYAMON | 2023-06-08 11:29 | 2023-06-08 11:30 | 4431 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA LLEVA 80% 1711-01 | B23060800094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-08 | 4431 | keep | 0 | Jun | 2023 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
MAYAGÃœEZ | 2023-06-08 11:34 | 2023-06-08 13:50 | 100 | 2:16 | P | ARBOL SOBRE LINEA | 3 X 80 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | M23060800192 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 136 | 2023-06-08 | 13600 | keep | 0 | Jun | 2023 | 0.0092629 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-06-08 11:41 | 2023-06-08 16:23 | 19 | 4:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON 500 PIES DE CONDUCTOR SECUNDARIO DETERIORADO | C23060800087 | New_Event | Secondary Wire Break | Include | Include | Equipment | 282 | 2023-06-08 | 5358 | keep | 0 | Jun | 2023 | 0.0036493 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2023-06-08 11:46 | 2023-06-08 15:28 | 72 | 3:42 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23060800098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2023-06-08 | 15984 | keep | 0 | Jun | 2023 | 0.010887 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
SAN JUAN | 2023-06-08 11:57 | 2023-06-08 13:45 | 40 | 1:48 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S23060800191 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2023-06-08 | 4320 | keep | 0 | Jun | 2023 | 0.0029423 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-06-08 12:11 | 2023-06-08 12:54 | 114 | 0:43 | P | CAUSAS EXTERNAS | SE SECCIONALIZO TRAMO Y SE LEVANTO CONDUCTOR PRIMARIO Y SE REEMPLAZO POSTES PRIMARIO AVERIA A ACUSA DE IMPACTO POR CAMION SJ-230608-01 | S23060800151 | Partial_restoration | Damage From Public | Include | Include | Public | 43 | 2023-06-08 | 4902 | keep | 0 | Jun | 2023 | 0.0033387 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-06-08 12:21 | 2023-06-08 15:07 | 10 | 2:46 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y SE REPARO CONECTORES SECUNDARIOS. SE REALIZO DEGANCHE SECUNDARIO | R23060800058 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 166 | 2023-06-08 | 1660 | keep | 0 | Jun | 2023 | 0.0011306 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-06-08 12:26 | 2023-06-08 14:00 | 100 | 1:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23060800217 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 94 | 2023-06-08 | 9400 | keep | 0 | Jun | 2023 | 0.0064023 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-06-08 12:28 | 2023-06-08 16:53 | 20 | 4:25 | P | DESGANCHE | 1 X 15 EN XMR 1 X 100 C/L Y DESGANCHE | B23060800109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 265 | 2023-06-08 | 5300 | keep | 0 | Jun | 2023 | 0.0036098 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-06-08 12:35 | 2023-06-08 14:38 | 1 | 2:03 | P | DESGANCHE | 1 X 20 EN C/L SE REALIZO DESPEJE DE LINEA EVENTO TRANSFERIDO DE PONCE | P23060800196 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2023-06-08 | 123 | keep | 0 | Jun | 2023 | 8.3775e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-06-08 12:37 | 2023-06-08 16:57 | 18 | 4:20 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR NO SE REPORTO CAUSA | A23060800113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 260 | 2023-06-08 | 4680 | keep | 0 | Jun | 2023 | 0.0031875 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
MAYAGÃœEZ | 2023-06-08 12:49 | 2023-06-08 15:05 | 4 | 2:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 8 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M23060800228 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 136 | 2023-06-08 | 544 | keep | 0 | Jun | 2023 | 0.00037052 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2023-06-08 12:50 | 2023-06-08 13:05 | 113 | 0:15 | P | SOBRECARGA | SE ABRIO C/L PARA DIVIDIR LAS CARGAS PARA BALANCEAR ALIMENTADOR | B23060800108 | New_Event | Trip Due To Overload | Include | Include | Other | 15 | 2023-06-08 | 1695 | keep | 0 | Jun | 2023 | 0.0011545 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
AGUADILLA | 2023-06-08 12:52 | 2023-06-08 18:20 | 50 | 5:28 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CORTE DE LINEA | M23060800230 | New_Event | Primary Wire Break | Include | Include | Equipment | 328 | 2023-06-08 | 16400 | keep | 0 | Jun | 2023 | 0.01117 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-06-08 12:53 | 2023-06-09 13:04 | 40 | 24:11 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | C23060800284 | New_Event | Animals | Include | Include | Wildlife | 1451 | 2023-06-08 | 58040 | keep | 0 | Jun | 2023 | 0.039531 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-06-08 13:00 | 2023-06-08 18:50 | 125 | 5:50 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA REPARAR ALAMBRE PARTIDO | M23060800023 | New_Event | Primary Wire Break | Include | Include | Equipment | 350 | 2023-06-08 | 43750 | keep | 0 | Jun | 2023 | 0.029798 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
CANOVANAS | 2023-06-08 13:04 | 2023-06-08 15:19 | 126 | 2:15 | P | DESGANCHE | 2 X 50 EN C/L SE REALIZO DESGANCHE | R23060800061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2023-06-08 | 17010 | keep | 0 | Jun | 2023 | 0.011585 | 8.5818e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 126
BAYAMON | 2023-06-08 13:08 | 2023-06-08 13:09 | 4431 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA LLEVA 80% 1711-01 | B2306080000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-08 | 4431 | keep | 0 | Jun | 2023 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
BAYAMON | 2023-06-08 13:20 | 2023-06-08 13:21 | 1270 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO Y SE CERRO POR SCADA 80% DEL 1711-01 POR EL 1717-03 | B2306080000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-08 | 1270 | keep | 0 | Jun | 2023 | 0.00086499 | 0.00086499 | Momentary | FALSE | FALSE | Not_TMED_Event | 1270
SAN JUAN | 2023-06-08 13:41 | 2023-06-08 17:01 | 114 | 3:20 | P | CAUSAS EXTERNAS | SE SECCIONALIZO TRAMO Y SE LEVANTO CONDUCTOR PRIMARIO Y SE REEMPLAZO POSTES PRIMARIO AVERIA DE IMPACTO POR CAMION SJ-230608-01 | S23060800151 | Partial_restoration | Damage From Public | Include | Include | Public | 200 | 2023-06-08 | 22800 | keep | 0 | Jun | 2023 | 0.015529 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-08 13:49 | 2023-06-08 17:28 | 10 | 3:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABROP XMR Y SE REPARO BAJANTE SECUNDARIO | P23060800225 | New_Event | Secondary Wire Break | Include | Include | Equipment | 219 | 2023-06-08 | 2190 | keep | 0 | Jun | 2023 | 0.0014916 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-06-08 14:16 | 2023-06-08 20:57 | 8 | 6:41 | P | NO SE REPORTO CAUSA | 1X20 EN XMR NO CAUSA | S23060800238 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 401 | 2023-06-08 | 3208 | keep | 0 | Jun | 2023 | 0.002185 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-06-08 14:16 | 2023-06-08 15:24 | 36 | 1:08 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE EVENTO TRANSFERIDO | P23060800243 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2023-06-08 | 2448 | keep | 0 | Jun | 2023 | 0.0016673 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CANOVANAS | 2023-06-08 14:18 | 2023-06-08 19:17 | 20 | 4:59 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERRADO DE T9 @ T8 SJ-230608-50 | R23060800010 | New_Event | UG Cable Fault | Include | Include | Equipment | 299 | 2023-06-08 | 5980 | keep | 0 | Jun | 2023 | 0.004073 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-06-08 14:20 | 2023-06-08 14:50 | 6 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M23060800234 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-06-08 | 180 | keep | 0 | Jun | 2023 | 0.0001226 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2023-06-08 14:35 | 2023-06-08 16:10 | 40 | 1:35 | P | NO SE REPORTO CAUSA | 1 X 40 EN REGULADOR NO SE REPORTO CAUSA | M23060800265 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 95 | 2023-06-08 | 3800 | keep | 0 | Jun | 2023 | 0.0025882 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-06-08 14:37 | 2023-06-08 17:53 | 60 | 3:16 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA CRUCE X AVE | C23060800254 | New_Event | Animals | Include | Include | Wildlife | 196 | 2023-06-08 | 11760 | keep | 0 | Jun | 2023 | 0.0080097 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-06-08 14:38 | 2023-06-08 18:14 | 39 | 3:36 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C23060800112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 216 | 2023-06-08 | 8424 | keep | 0 | Jun | 2023 | 0.0057375 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
FAJARDO | 2023-06-08 14:47 | 2023-06-08 17:20 | 5 | 2:33 | P | ANIMAL | SE RETIRO CULEBRA Y SE CERRO XMR (NO FUNDIO) EVENTO TRANSFERIDO DE PONCE | P23060800062 | New_Event | Animals | Include | Include | Wildlife | 153 | 2023-06-08 | 765 | keep | 0 | Jun | 2023 | 0.00052104 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-06-08 14:51 | 2023-06-09 12:49 | 8 | 21:58 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE | S23060800247 | New_Event | Primary Wire Break | Include | Include | Equipment | 1318 | 2023-06-08 | 10544 | keep | 0 | Jun | 2023 | 0.0071815 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-06-08 14:51 | 2023-06-08 19:15 | 6 | 4:24 | P | PROBLEMA DEL CLIENTE | 1 X 10 EN TRANSFORMADOR SE RETIRO CONTADOR DE UNA RESIDENCIA PARA QUE CLILENTE REPARARA | M23060800273 | New_Event | Customer-Related Interruption | Include | Include | Public | 264 | 2023-06-08 | 1584 | keep | 0 | Jun | 2023 | 0.0010789 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-06-08 15:06 | 2023-06-08 15:36 | 4 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE LLEVO PUENTE A LA CAJA Y 1X20 EN XMR | S23060800250 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-06-08 | 120 | keep | 0 | Jun | 2023 | 8.1731e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-06-08 15:13 | 2023-06-08 15:40 | 2 | 0:27 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR | B23060800148 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 27 | 2023-06-08 | 54 | keep | 0 | Jun | 2023 | 3.6779e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-06-08 15:14 | 2023-06-08 16:37 | 1037 | 1:23 | T | TERMINACION SOTERRADA AVERIADA | SE ENCONTRO TERMINACION SOTERRADA AVERIADA | M23060800288 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 83 | 2023-06-08 | 86071 | keep | 0 | Jun | 2023 | 0.058623 | 0.0007063 | Sustained | FALSE | FALSE | Not_TMED_Event | 1037
SAN JUAN | 2023-06-08 15:17 | 2023-06-08 15:41 | 15 | 0:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO SE REPARO BAJANTE SECUNDARIO | S23060800253 | New_Event | Secondary Wire Break | Include | Include | Equipment | 24 | 2023-06-08 | 360 | keep | 0 | Jun | 2023 | 0.00024519 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-06-08 15:22 | 2023-06-08 15:23 | 1709 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23060800123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-08 | 1709 | keep | 0 | Jun | 2023 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
CAGUAS | 2023-06-08 15:23 | 2023-06-08 15:44 | 112 | 0:21 | P | CABLE SOTERRADO AVERIADO | AVERIA DEL SU12 AL SU13 SE CERRO N/O DEL SU15 AL SU13 | C23060700595 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 21 | 2023-06-08 | 2352 | keep | 0 | Jun | 2023 | 0.0016019 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-06-08 15:25 | 2023-06-08 17:38 | 50 | 2:13 | P | ANIMAL | 1 X 30 Y 1 X 50 EN CORTES DE LINEA CRUCE CON AVE | C23060800125 | New_Event | Animals | Include | Include | Wildlife | 133 | 2023-06-08 | 6650 | keep | 0 | Jun | 2023 | 0.0045293 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-06-08 15:34 | 2023-06-08 16:45 | 5 | 1:11 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 C/L CRUCE DE CONDUCTOR | B23060800152 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 71 | 2023-06-08 | 355 | keep | 0 | Jun | 2023 | 0.00024179 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-06-08 15:44 | 2023-06-08 15:45 | 1709 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23060800133 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-08 | 1709 | keep | 0 | Jun | 2023 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
CAGUAS | 2023-06-08 15:45 | 2023-06-08 19:18 | 112 | 3:33 | P | CABLE SOTERRADO AVERIADO | AVERIA DEL SU12 AL SU13 SE CERRO N/O DEL SU15 AL SU13 | C23060700595 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 213 | 2023-06-08 | 23856 | keep | 0 | Jun | 2023 | 0.016248 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-06-08 15:50 | 2023-06-08 15:55 | 12 | 0:05 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR AVERIADO Y SE NORMALIZO CARGA QUE SE HABIA TRANSFERIDO A XMR CERCANO | R23060800081 | New_Event | Service Transformer Failure | Include | Include | Equipment | 5 | 2023-06-08 | 60 | keep | 0 | Jun | 2023 | 4.0866e-05 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2023-06-08 15:53 | 2023-06-08 18:44 | 1 | 2:51 | P | DESGANCHE | 1 X 40 EN C/L SE REALIZO DESGANCHE Y SE REEMPLAZO CAJA PRIMARIA EVENTO TRANSFERIDO DE PONCE | P23060800289 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2023-06-08 | 171 | keep | 0 | Jun | 2023 | 0.00011647 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-06-08 16:04 | 2023-06-08 18:02 | 20 | 1:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO TOMAS ABIERTAS SECUNDARIAS | C23060800138 | New_Event | Secondary Wire Break | Include | Include | Equipment | 118 | 2023-06-08 | 2360 | keep | 0 | Jun | 2023 | 0.0016074 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-06-08 16:19 | 2023-06-09 19:37 | 92 | 27:18 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN C/L Y SE LEVANTO CONDUCTOR DEL SUELO. | B23060800164 | New_Event | Primary Wire Break | Include | Include | Equipment | 1638 | 2023-06-08 | 150696 | keep | 0 | Jun | 2023 | 0.10264 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
BARRANQUITAS | 2023-06-08 16:38 | 2023-06-08 18:21 | 731 | 1:43 | P | CONDUCTOR ROTO O ABIERTO | CONDUCTOR EN EL SUELO | C23060800147 | New_Event | Primary Wire Break | Include | Include | Equipment | 103 | 2023-06-08 | 75293 | keep | 0 | Jun | 2023 | 0.051282 | 0.00049788 | Sustained | FALSE | FALSE | Not_TMED_Event | 731
BAYAMON | 2023-06-08 16:43 | 2023-06-08 20:57 | 9 | 4:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE CERRO PUENTE DE CAJA A XMR | S23060800265 | New_Event | Secondary Wire Break | Include | Include | Equipment | 254 | 2023-06-08 | 2286 | keep | 0 | Jun | 2023 | 0.001557 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2023-06-08 16:43 | 2023-06-08 16:44 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23060800084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-08 | 4085 | keep | 0 | Jun | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
UTUADO | 2023-06-08 16:52 | 2023-06-08 19:50 | 150 | 2:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN CORTE DE LINEA | A23060800164 | New_Event | Cutout Failure | Include | Include | Equipment | 178 | 2023-06-08 | 26700 | keep | 0 | Jun | 2023 | 0.018185 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-06-08 16:58 | 2023-06-09 12:06 | 62 | 19:08 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA CERRAR PUENTE ABIERTO | S23060800270 | New_Event | Primary Wire Break | Include | Include | Equipment | 1148 | 2023-06-08 | 71176 | keep | 0 | Jun | 2023 | 0.048478 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
SAN JUAN | 2023-06-08 17:08 | 2023-06-08 19:23 | 75 | 2:15 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU-47 Y 1 X 100 EN RISER | S23060800274 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 135 | 2023-06-08 | 10125 | keep | 0 | Jun | 2023 | 0.0068961 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2023-06-08 17:09 | 2023-06-08 19:44 | 1444 | 2:35 | T | TERMINACION SOTERRADA AVERIADA | SE SECCIONALIZO AVERIA Y SE CERRO EL INTERRUPTOR | M23060800328 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 155 | 2023-06-08 | 223820 | keep | 0 | Jun | 2023 | 0.15244 | 0.0009835 | Sustained | FALSE | FALSE | Not_TMED_Event | 1444
BARRANQUITAS | 2023-06-08 17:16 | 2023-06-08 17:17 | 2725 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500/4800 | C23060800169 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-08 | 2725 | keep | 0 | Jun | 2023 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2023-06-08 17:16 | 2023-06-08 17:17 | 1834 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500/4800 | C23060800169 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-08 | 1834 | keep | 0 | Jun | 2023 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2023-06-08 17:16 | 2023-06-08 17:17 | 1437 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500/4800 | C23060800169 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-08 | 1437 | keep | 0 | Jun | 2023 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2023-06-08 17:16 | 2023-06-08 17:17 | 2565 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500/4800 | C23060800170 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-08 | 2565 | keep | 0 | Jun | 2023 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2023-06-08 17:16 | 2023-06-08 17:17 | 3565 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500/4800 | C23060800170 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-08 | 3565 | keep | 0 | Jun | 2023 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
BAYAMON | 2023-06-08 17:18 | 2023-06-09 22:16 | 41 | 28:58 | P | CABLE SOTERRADO AVERIADO | SE INSTALO AEREO PROVISIONAL DEL SU-9 @ T-3 BY-230609-01 | B23060800175 | New_Event | UG Cable Fault | Include | Include | Equipment | 1738 | 2023-06-08 | 71258 | keep | 0 | Jun | 2023 | 0.048533 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
BAYAMON | 2023-06-08 17:23 | 2023-06-08 23:55 | 129 | 6:32 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | B23060800176 | New_Event | Animals | Include | Include | Wildlife | 392 | 2023-06-08 | 50568 | keep | 0 | Jun | 2023 | 0.034442 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
BAYAMON | 2023-06-08 17:30 | 2023-06-09 16:45 | 20 | 23:15 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO - TRASPATIO - DE LINEA @ TAP MONIFASICO NO FUNDIO | B23060800179 | New_Event | Primary Wire Break | Include | Include | Equipment | 1395 | 2023-06-08 | 27900 | keep | 0 | Jun | 2023 | 0.019003 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-06-08 17:39 | 2023-06-09 03:11 | 213 | 9:32 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23060800182 | New_Event | Vegetation Contact | Include | Include | Vegetation | 572 | 2023-06-08 | 121836 | keep | 0 | Jun | 2023 | 0.082982 | 0.00014507 | Sustained | FALSE | FALSE | Not_TMED_Event | 213
BAYAMON | 2023-06-08 17:40 | 2023-06-09 14:04 | 8 | 20:24 | P | NO SE REPORTO CAUSA | 1X80 EN RISER | B23060800183 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1224 | 2023-06-08 | 9792 | keep | 0 | Jun | 2023 | 0.0066693 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2023-06-08 17:49 | 2023-06-08 17:50 | 3431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23060800188 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-08 | 3431 | keep | 0 | Jun | 2023 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
BAYAMON | 2023-06-08 17:50 | 2023-06-08 19:33 | 36 | 1:43 | P | ARBOL SOBRE LINEA | SE ABRIO C/L PARA RETIRAR ARBOL SOBRE LINEA | B23060800188 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 103 | 2023-06-08 | 3708 | keep | 0 | Jun | 2023 | 0.0025255 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2023-06-08 17:54 | 2023-06-08 17:55 | 1 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2306080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-08 | 1 | keep | 0 | Jun | 2023 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-06-08 17:56 | 2023-06-08 21:57 | 24 | 4:01 | T | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO TRAMO Y SE CERRO POR SCADA SJ-230608-03 Y ENTRO 20% EN SERVICIO | S23060800028 | New_Event | UG Cable Fault | Include | Include | Equipment | 241 | 2023-06-08 | 5784 | keep | 0 | Jun | 2023 | 0.0039395 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BARRANQUITAS | 2023-06-08 18:21 | 2023-06-08 18:22 | 2192 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR EN EL SUELO | C23060800147 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 1 | 2023-06-08 | 2192 | keep | 0 | Jun | 2023 | 0.001493 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-06-08 18:22 | 2023-06-08 19:57 | 731 | 1:35 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR DEL SUELO | C23060800147 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 95 | 2023-06-08 | 69445 | keep | 0 | Jun | 2023 | 0.047299 | 0.00049788 | Sustained | FALSE | FALSE | Not_TMED_Event | 731
BAYAMON | 2023-06-08 18:29 | 2023-06-08 18:30 | 959 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DEL 1904-07 CARGA POR 1904-07 | B2306080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-08 | 959 | keep | 0 | Jun | 2023 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-06-08 18:29 | 2023-06-08 18:30 | 1264 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1904-07 CARGA POR 1904-07 | B2306080000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-08 | 1264 | keep | 0 | Jun | 2023 | 0.0008609 | 0.0008609 | Momentary | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2023-06-08 18:29 | 2023-06-08 18:30 | 620 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1904-07 CARGA POR 1904-07 | B2306080000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-08 | 620 | keep | 0 | Jun | 2023 | 0.00042228 | 0.00042228 | Momentary | FALSE | FALSE | Not_TMED_Event | 620
BAYAMON | 2023-06-08 18:40 | 2023-06-08 18:41 | 959 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DEL 1904-07 CARGA POR 1904-07 | B2306080000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-08 | 959 | keep | 0 | Jun | 2023 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-06-08 18:40 | 2023-06-08 18:41 | 1264 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1904-07 CARGA POR 1904-07 | B2306080000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-08 | 1264 | keep | 0 | Jun | 2023 | 0.0008609 | 0.0008609 | Momentary | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2023-06-08 18:40 | 2023-06-08 18:41 | 620 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1904-07 CARGA POR 1904-07 | B2306080000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-08 | 620 | keep | 0 | Jun | 2023 | 0.00042228 | 0.00042228 | Momentary | FALSE | FALSE | Not_TMED_Event | 620
SAN JUAN | 2023-06-08 19:37 | 2023-06-08 22:19 | 80 | 2:42 | P | DESGANCHE | 1 X 67 EN C/L DESGANCHE | S23060800327 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2023-06-08 | 12960 | keep | 0 | Jun | 2023 | 0.008827 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-06-08 19:39 | 2023-06-09 01:50 | 350 | 6:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE QUEMADO | M23060800383 | New_Event | Cutout Failure | Include | Include | Equipment | 371 | 2023-06-08 | 129850 | keep | 0 | Jun | 2023 | 0.08844 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
MAYAGÃœEZ | 2023-06-08 19:44 | 2023-06-08 23:08 | 30 | 3:24 | P | TERMINACION SOTERRADA AVERIADA | REPARACION DE TERMINACION SOTERRADA | M23060800403 | Partial_restoration | UG Cable Termination Failure | Include | Include | Equipment | 204 | 2023-06-08 | 6120 | keep | 0 | Jun | 2023 | 0.0041683 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-06-08 19:59 | 2023-06-08 20:22 | 33 | 0:23 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR DESGANCHE SECUNDARIO | C23060800247 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 23 | 2023-06-08 | 759 | keep | 0 | Jun | 2023 | 0.00051695 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
SAN JUAN | 2023-06-08 20:05 | 2023-06-08 20:30 | 60 | 0:25 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE EVENTO TRANSFERIDO DE PONCE | P23060800547 | New_Event | Vegetation Contact | Include | Include | Vegetation | 25 | 2023-06-08 | 1500 | keep | 0 | Jun | 2023 | 0.0010216 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-06-08 20:10 | 2023-06-08 21:25 | 100 | 1:15 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | C23060800248 | New_Event | Animals | Include | Include | Wildlife | 75 | 2023-06-08 | 7500 | keep | 0 | Jun | 2023 | 0.0051082 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-06-08 20:39 | 2023-06-09 00:08 | 114 | 3:29 | P | CAUSAS EXTERNAS | SE SECCIONALIZO TRAMO Y SE LEVANTO CONDUCTOR PRIMARIO Y SE REEMPLAZO POSTES PRIMARIO AVERIA DE IMPACTO POR CAMION SJ-230608-01 | S23060800151 | Partial_restoration | Damage From Public | Include | Include | Public | 209 | 2023-06-08 | 23826 | keep | 0 | Jun | 2023 | 0.016228 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-06-08 20:39 | 2023-06-08 22:17 | 200 | 1:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M23060800417 | New_Event | Cutout Failure | Include | Include | Equipment | 98 | 2023-06-08 | 19600 | keep | 0 | Jun | 2023 | 0.013349 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2023-06-08 20:40 | 2023-06-09 00:50 | 51 | 4:10 | T | ALIMENTADOR AMARRADO | RELEVO DE CARGA PROGRAMADO DEFICIENCIA EN GENERACION SU CARGA POR EL 7902-01 QUE SE ABRIO EN EL RELEVO | M23060800492 | New_Event | Feeder Load Transferred | Include | Include | Other | 250 | 2023-06-08 | 12750 | keep | 0 | Jun | 2023 | 0.008684 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
SAN JUAN | 2023-06-08 20:57 | 2023-06-08 22:19 | 1236 | 1:22 | P | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 25% DE SU CARGA POR EL 1303-02 CONDUCTOR SAFADO ENTRE VILLA BETINA Y QUEBRADA NEGRITO | S23060800345 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 82 | 2023-06-08 | 101352 | keep | 0 | Jun | 2023 | 0.06903 | 0.00084183 | Sustained | FALSE | FALSE | Not_TMED_Event | 1236
SAN JUAN | 2023-06-08 20:57 | 2023-06-08 22:19 | 60 | 1:22 | P | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 45% DE SU CARGA POR EL 1303-02 CONDUCTOR SAFADO ENTRE VILLA BETINA Y QUEBRADA NEGRITO | S23060800345 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 82 | 2023-06-08 | 4920 | keep | 0 | Jun | 2023 | 0.003351 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-06-08 21:36 | 2023-06-08 21:39 | 1681 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 CONDUCTOR SAFADO ENTRE VILLA BETINA Y QUEBRADA NEGRITO | S23060800345 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-06-08 | 5043 | keep | 0 | Jun | 2023 | 0.0034348 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2023-06-08 21:36 | 2023-06-08 21:39 | 2435 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 LLEVA 25% DEL 1204-04 LLEVA 45% DEL 1401-08 CONDUCTOR SAFADO ENTRE VILLA BETINA Y QUEBRADA NEGRITO | S23060800345 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-06-08 | 7305 | keep | 0 | Jun | 2023 | 0.0049754 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2023-06-08 21:36 | 2023-06-08 21:39 | 726 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 CONDUCTOR SAFADO ENTRE VILLA BETINA Y QUEBRADA NEGRITO | S23060800345 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-06-08 | 2178 | keep | 0 | Jun | 2023 | 0.0014834 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2023-06-08 21:36 | 2023-06-08 21:39 | 225 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 CONDUCTOR SAFADO ENTRE VILLA BETINA Y QUEBRADA NEGRITO | S23060800345 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-06-08 | 675 | keep | 0 | Jun | 2023 | 0.00045974 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2023-06-08 21:36 | 2023-06-08 21:39 | 870 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 CONDUCTOR SAFADO ENTRE VILLA BETINA Y QUEBRADA NEGRITO | S23060800345 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-06-08 | 2610 | keep | 0 | Jun | 2023 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BARRANQUITAS | 2023-06-08 21:54 | 2023-06-09 01:41 | 150 | 3:47 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C23060800268 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 227 | 2023-06-08 | 34050 | keep | 0 | Jun | 2023 | 0.023191 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-06-08 21:54 | 2023-06-09 00:54 | 120 | 3:00 | P | ANIMAL | CRUCE POR AVE 1 X 100 EN C/L | B23060800307 | New_Event | Animals | Include | Include | Wildlife | 180 | 2023-06-08 | 21600 | keep | 0 | Jun | 2023 | 0.014712 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2023-06-08 21:57 | 2023-06-11 17:45 | 19 | 67:48 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO TRAMO SE REALIZO PRUEBA A CABLE Y SE REPARO SJ-230608-03 | S23060800028 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 4068 | 2023-06-08 | 77292 | keep | 0 | Jun | 2023 | 0.052643 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-06-08 21:58 | 2023-06-09 08:57 | 60 | 10:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CL FUERTE VIENTOS | M23060800483 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 659 | 2023-06-08 | 39540 | keep | 0 | Jun | 2023 | 0.026931 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2023-06-08 21:59 | 2023-06-09 00:34 | 65 | 2:35 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P23060800671 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 155 | 2023-06-08 | 10075 | keep | 0 | Jun | 2023 | 0.006862 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
AGUADILLA | 2023-06-08 22:03 | 2023-06-09 08:37 | 64 | 10:34 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | M23060800484 | New_Event | Vegetation Contact | Include | Include | Vegetation | 634 | 2023-06-08 | 40576 | keep | 0 | Jun | 2023 | 0.027636 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
UTUADO | 2023-06-08 22:03 | 2023-06-09 14:40 | 25 | 16:37 | P | DESGANCHE | 1 X 25 EN SALIDA DE CONVERTIDOR SE RETIRO BAMBU | A23060800323 | New_Event | Vegetation Contact | Include | Include | Vegetation | 997 | 2023-06-08 | 24925 | keep | 0 | Jun | 2023 | 0.016976 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2023-06-08 22:08 | 2023-06-09 02:25 | 150 | 4:17 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | A23060800327 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 257 | 2023-06-08 | 38550 | keep | 0 | Jun | 2023 | 0.026256 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2023-06-08 22:12 | 2023-06-09 03:15 | 20 | 5:03 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | A23060800331 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 303 | 2023-06-08 | 6060 | keep | 0 | Jun | 2023 | 0.0041274 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-06-08 22:15 | 2023-06-09 02:10 | 100 | 3:55 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23060800493 | New_Event | Vegetation Contact | Include | Include | Vegetation | 235 | 2023-06-08 | 23500 | keep | 0 | Jun | 2023 | 0.016006 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-06-08 22:17 | 2023-06-09 11:35 | 7 | 13:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR PORTA FUSIBLE AVERIADO | M23060800495 | New_Event | Cutout Failure | Include | Include | Equipment | 798 | 2023-06-08 | 5586 | keep | 0 | Jun | 2023 | 0.0038046 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-06-08 22:19 | 2023-06-09 13:20 | 9 | 15:01 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE CAJA A XMR | S23060800265 | New_Event | Primary Wire Break | Include | Include | Equipment | 901 | 2023-06-08 | 8109 | keep | 0 | Jun | 2023 | 0.005523 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2023-06-08 22:19 | 2023-06-09 08:08 | 75 | 9:49 | P | DESGANCHE | 1 X 50 EN C/L DEGANCHE | C23060800277 | New_Event | Vegetation Contact | Include | Include | Vegetation | 589 | 2023-06-08 | 44175 | keep | 0 | Jun | 2023 | 0.030087 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-06-08 22:19 | 2023-06-09 13:39 | 57 | 15:20 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23060800315 | New_Event | Vegetation Contact | Include | Include | Vegetation | 920 | 2023-06-08 | 52440 | keep | 0 | Jun | 2023 | 0.035717 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
YAUCO | 2023-06-08 22:21 | 2023-06-09 02:45 | 43 | 4:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA FUERTE LLUVIA | P23060800687 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 264 | 2023-06-08 | 11352 | keep | 0 | Jun | 2023 | 0.0077318 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
MAYAGÃœEZ | 2023-06-08 22:21 | 2023-06-09 10:35 | 200 | 12:14 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23060800499 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 734 | 2023-06-08 | 146800 | keep | 0 | Jun | 2023 | 0.099985 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-06-08 22:22 | 2023-06-09 13:47 | 8 | 15:25 | P | NO SE REPORTO CAUSA | 1X20 EN XMR NO CAUSA | S23060800238 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 925 | 2023-06-08 | 7400 | keep | 0 | Jun | 2023 | 0.0050401 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-06-08 22:34 | 2023-06-09 00:41 | 200 | 2:07 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | A23060800342 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 127 | 2023-06-08 | 25400 | keep | 0 | Jun | 2023 | 0.0173 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2023-06-08 22:39 | 2023-06-09 02:18 | 70 | 3:39 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23060800344 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2023-06-08 | 15330 | keep | 0 | Jun | 2023 | 0.010441 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2023-06-08 22:41 | 2023-06-09 00:05 | 150 | 1:24 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23060800515 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2023-06-08 | 12600 | keep | 0 | Jun | 2023 | 0.0085818 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-06-08 22:45 | 2023-06-09 04:24 | 122 | 5:39 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR Y 1 X 65 EN C/L | B23060800326 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 339 | 2023-06-08 | 41358 | keep | 0 | Jun | 2023 | 0.028169 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
BAYAMON | 2023-06-08 23:32 | 2023-06-09 05:45 | 225 | 6:13 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23060800343 | New_Event | Vegetation Contact | Include | Include | Vegetation | 373 | 2023-06-08 | 83925 | keep | 0 | Jun | 2023 | 0.057161 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2023-06-09 | 2023-06-09 00:01 | 643 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1530-09 | S23060900001 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-09 | 643 | keep | 0 | Jun | 2023 | 0.00043794 | 0.00043794 | Momentary | FALSE | FALSE | Not_TMED_Event | 643
SAN JUAN | 2023-06-09 | 2023-06-09 00:01 | 1310 | 0:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1530-07 | S23060900001 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-06-09 | 1310 | keep | 0 | Jun | 2023 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
SAN JUAN | 2023-06-09 00:01 | 2023-06-09 13:02 | 214 | 13:01 | P | ALIMENTADOR AMARRADO | SE ENCONTRO MACHETE QUEMADO EN SALIDA ALIMENTADOR 1530-09 | S23060900157 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 781 | 2023-06-09 | 167134 | keep | 0 | Jun | 2023 | 0.11383 | 0.00014575 | Sustained | FALSE | FALSE | Not_TMED_Event | 214
SAN JUAN | 2023-06-09 00:01 | 2023-06-09 13:02 | 437 | 13:01 | P | DESCONECTIVO DEFECTUOSO | 1 X 50 EN C/L SE REEMPLAZO MACHETE QUEMADO SJ-230609-02 | S23060900157 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 781 | 2023-06-09 | 341297 | keep | 0 | Jun | 2023 | 0.23246 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
VEGA BAJA | 2023-06-09 00:19 | 2023-06-09 07:25 | 40 | 7:06 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23060900004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 426 | 2023-06-09 | 17040 | keep | 0 | Jun | 2023 | 0.011606 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2023-06-09 01:05 | 2023-06-09 05:10 | 315 | 4:05 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE ENCONTRO NADA | P23060900013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 245 | 2023-06-09 | 77175 | keep | 0 | Jun | 2023 | 0.052564 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
HUMACAO | 2023-06-09 01:16 | 2023-06-09 01:17 | 776 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2306090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-09 | 776 | keep | 0 | Jun | 2023 | 0.00052853 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
AGUADILLA | 2023-06-09 01:26 | 2023-06-09 03:00 | 100 | 1:34 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | P23060900016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 94 | 2023-06-09 | 9400 | keep | 0 | Jun | 2023 | 0.0064023 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-06-09 01:36 | 2023-06-09 02:20 | 10 | 0:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23060900027 | New_Event | Secondary Wire Break | Include | Include | Equipment | 44 | 2023-06-09 | 440 | keep | 0 | Jun | 2023 | 0.00029968 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-06-09 01:53 | 2023-06-09 10:15 | 10 | 8:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 15 EN XMR SE REEMPLAZARON DOS CAJAS PRIMARIAS. | P23060900018 | New_Event | Cutout Failure | Include | Include | Equipment | 502 | 2023-06-09 | 5020 | keep | 0 | Jun | 2023 | 0.0034191 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-06-09 01:56 | 2023-06-09 01:57 | 396 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23060900019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-09 | 396 | keep | 0 | Jun | 2023 | 0.00026971 | 0.00026971 | Momentary | FALSE | FALSE | Not_TMED_Event | 396
SAN JUAN | 2023-06-09 02:18 | 2023-06-09 02:19 | 60 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 10% DEL 1420-03 | S23060900032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-09 | 60 | keep | 0 | Jun | 2023 | 4.0866e-05 | 4.0866e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-06-09 02:18 | 2023-06-09 02:19 | 54 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 10% DE SU CARGA POR EL 1420-02 | S23060900032 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-09 | 54 | keep | 0 | Jun | 2023 | 3.6779e-05 | 3.6779e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 54
SAN JUAN | 2023-06-09 02:21 | 2023-06-09 11:45 | 15 | 9:24 | P | NO SE REPORTO CAUSA | 2 X 100 EN RISER Y 2 X 80 EN CORTE DE LINEA | S23060900033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 564 | 2023-06-09 | 8460 | keep | 0 | Jun | 2023 | 0.0057621 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2023-06-09 02:46 | 2023-06-09 07:34 | 43 | 4:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA FUERTE LLUVIA | P23060800687 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 288 | 2023-06-09 | 12384 | keep | 0 | Jun | 2023 | 0.0084347 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-06-09 03:22 | 2023-06-09 03:23 | 2178 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 3015-07 LLEVA EL 3103-05 | C2306090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-09 | 2178 | keep | 0 | Jun | 2023 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
HUMACAO | 2023-06-09 03:23 | 2023-06-09 04:40 | 518 | 1:17 | P | DESGANCHE | 2 X 80 EN C/L Y 1 X 100 EN C/L DESGACHE | C23060900011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2023-06-09 | 39886 | keep | 0 | Jun | 2023 | 0.027166 | 0.00035281 | Sustained | FALSE | FALSE | Not_TMED_Event | 518
PONCE | 2023-06-09 03:33 | 2023-06-09 06:48 | 30 | 3:15 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO | P23060900043 | New_Event | Primary Wire Break | Include | Include | Equipment | 195 | 2023-06-09 | 5850 | keep | 0 | Jun | 2023 | 0.0039844 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-06-09 04:19 | 2023-06-09 09:36 | 40 | 5:17 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23060900012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 317 | 2023-06-09 | 12680 | keep | 0 | Jun | 2023 | 0.0086363 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-06-09 04:21 | 2023-06-09 12:09 | 30 | 7:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTES SECUNDAROS | B23060900013 | New_Event | Secondary Wire Break | Include | Include | Equipment | 468 | 2023-06-09 | 14040 | keep | 0 | Jun | 2023 | 0.0095626 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-06-09 04:31 | 2023-06-09 04:32 | 918 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2306090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-09 | 918 | keep | 0 | Jun | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2023-06-09 04:35 | 2023-06-09 10:16 | 239 | 5:41 | P | NO SE REPORTO CAUSA | 2 X 100 EN RISER | C23060900054 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 341 | 2023-06-09 | 81499 | keep | 0 | Jun | 2023 | 0.055509 | 0.00016278 | Sustained | FALSE | FALSE | Not_TMED_Event | 239
YAUCO | 2023-06-09 04:45 | 2023-06-09 09:05 | 30 | 4:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 CL FUERTES VIENTOS | P23060900047 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 260 | 2023-06-09 | 7800 | keep | 0 | Jun | 2023 | 0.0053125 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2023-06-09 05:17 | 2023-06-09 15:00 | 80 | 9:43 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23060900010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 583 | 2023-06-09 | 46640 | keep | 0 | Jun | 2023 | 0.031766 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-06-09 05:21 | 2023-06-09 09:44 | 59 | 4:23 | P | ANIMAL | 1X65 @ LA ENTRADA DE RISER, 1X50 @ LA SALIDA DE RISER CRUCE POR AVE | R23060900011 | New_Event | Animals | Include | Include | Wildlife | 263 | 2023-06-09 | 15517 | keep | 0 | Jun | 2023 | 0.010569 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
BARRANQUITAS | 2023-06-09 05:42 | 2023-06-09 06:59 | 2280 | 1:17 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO PARA REALIZAR DESGANCHE 15% EN SERVICIO | C23060900058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2023-06-09 | 175560 | keep | 0 | Jun | 2023 | 0.11957 | 0.0015529 | Sustained | FALSE | FALSE | Not_TMED_Event | 2280
BAYAMON | 2023-06-09 06:06 | 2023-06-09 16:29 | 10 | 10:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REPARAR BAJANTE SECUNDARIO ROTO EN XMR | B23060900023 | New_Event | Secondary Wire Break | Include | Include | Equipment | 623 | 2023-06-09 | 6230 | keep | 0 | Jun | 2023 | 0.0042432 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-06-09 06:08 | 2023-06-10 09:20 | 14 | 27:12 | P | SECUNDARIA/DESGANCHE | SE REPARO SECUNDARIA DESGANCHE | B23060900024 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1632 | 2023-06-09 | 22848 | keep | 0 | Jun | 2023 | 0.015562 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
VEGA BAJA | 2023-06-09 06:08 | 2023-06-09 11:30 | 50 | 5:22 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23060900014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 322 | 2023-06-09 | 16100 | keep | 0 | Jun | 2023 | 0.010966 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-06-09 06:17 | 2023-06-09 09:07 | 30 | 2:50 | P | DESGANCHE | 1X40 EN C/L DESGANCHE | R23060900013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2023-06-09 | 5100 | keep | 0 | Jun | 2023 | 0.0034736 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2023-06-09 06:22 | 2023-06-09 06:23 | 1945 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23060900055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-09 | 1945 | keep | 0 | Jun | 2023 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
BAYAMON | 2023-06-09 06:34 | 2023-06-09 10:26 | 21 | 3:52 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23060900026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2023-06-09 | 4872 | keep | 0 | Jun | 2023 | 0.0033183 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
SAN JUAN | 2023-06-09 06:38 | 2023-06-09 09:59 | 1236 | 3:21 | P | ALIMENTADOR AMARRADO | DISPARO 0050 SE INSPECCIONO SE ENCONTRO RELE DE NEUTRAL 1303-05 SE TRANSFIRIO CARGA AL 1303-4 Y SE ENERGIZO TRANSFORMADOR | S23060900080 | New_Event | Feeder Load Transferred | Include | Include | Other | 201 | 2023-06-09 | 248436 | keep | 0 | Jun | 2023 | 0.16921 | 0.00084183 | Sustained | FALSE | FALSE | Not_TMED_Event | 1236
SAN JUAN | 2023-06-09 06:38 | 2023-06-09 09:59 | 1681 | 3:21 | S | PROTECCION DEFECTUOSA | DISPARO 0050 SE INSPECCIONO SE ENCONTRO RELE DE NEUTRAL DEFECTUOSO Y NO OPERO 1303-05 SE TRANSFIRIO CARGA AL 1303-4 Y SE ENERGIZO TRANSFORMADOR Y DEMAS CARGAS | S23060900080 | New_Event | Protection Miscoordination | Include | Include | Other | 201 | 2023-06-09 | 337881 | keep | 0 | Jun | 2023 | 0.23013 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2023-06-09 06:38 | 2023-06-09 09:59 | 2435 | 3:21 | S | PROTECCION DEFECTUOSA | DISPARO 0050 SE INSPECCIONO SE ENCONTRO RELE DE NEUTRAL DEFECTUOSO Y NO OPERO, 1303-05 SE TRANSFIRIO CARGA AL 1303-4 Y SE ENERGIZO TRANSFORMADOR Y DEMAS CARGAS LLEVA 25% DE 1204-04 Y 45% DEL 1401-08 | S23060900080 | New_Event | Protection Miscoordination | Include | Include | Other | 201 | 2023-06-09 | 489435 | keep | 0 | Jun | 2023 | 0.33335 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2023-06-09 06:38 | 2023-06-09 09:59 | 726 | 3:21 | S | PROTECCION DEFECTUOSA | DISPARO 0050 SE INSPECCIONO SE ENCONTRO RELE DE NEUTRAL DEFECTUOSO Y NO OPERO, 1303-05 SE TRANSFIRIO CARGA AL 1303-4 Y SE ENERGIZO TRANSFORMADOR Y DEMAS CARGAS | S23060900080 | New_Event | Protection Miscoordination | Include | Include | Other | 201 | 2023-06-09 | 145926 | keep | 0 | Jun | 2023 | 0.09939 | 0.00049448 | Sustained | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2023-06-09 06:38 | 2023-06-09 09:59 | 225 | 3:21 | S | PROTECCION DEFECTUOSA | DISPARO 0050 SE INSPECCIONO SE ENCONTRO RELE DE NEUTRAL 1303-05 SE TRANSFIRIO CARGA AL 1303-4 Y SE ENERGIZO TRANSFORMADOR Y DEMAS CARGAS | S23060900080 | New_Event | Protection Miscoordination | Include | Include | Other | 201 | 2023-06-09 | 45225 | keep | 0 | Jun | 2023 | 0.030803 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2023-06-09 06:38 | 2023-06-09 09:59 | 870 | 3:21 | S | PROTECCION DEFECTUOSA | DISPARO 0050 SE INSPECCIONO SE ENCONTRO RELE DE NEUTRAL DEFECTUOSO Y NO OPERO, 1303-05 SE TRANSFIRIO CARGA AL 1303-4 Y SE ENERGIZO TRANSFORMADOR Y DEMAS CARGAS | S23060900080 | New_Event | Protection Miscoordination | Include | Include | Other | 201 | 2023-06-09 | 174870 | keep | 0 | Jun | 2023 | 0.1191 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2023-06-09 06:38 | 2023-06-09 09:59 | 60 | 3:21 | P | ALIMENTADOR AMARRADO | DISPARO 0050 SE INSPECCIONO SE ENCONTRO RELE DE NEUTRAL 1303-05 SE TRANSFIRIO CARGA AL 1303-4 Y SE ENERGIZO TRANSFORMADOR Y DEMAS CARGAS LLEVA 25% DE 1204-04 Y 45% DEL 1401-08 | S23060900080 | New_Event | Feeder Load Transferred | Include | Include | Other | 201 | 2023-06-09 | 12060 | keep | 0 | Jun | 2023 | 0.008214 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-06-09 06:39 | 2023-06-09 10:43 | 14 | 4:04 | P | NO SE REPORTO CAUSA | 1X15 EN XMR | R23060900014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 244 | 2023-06-09 | 3416 | keep | 0 | Jun | 2023 | 0.0023266 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2023-06-09 06:49 | 2023-06-09 11:23 | 13 | 4:34 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | B23060900019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 274 | 2023-06-09 | 3562 | keep | 0 | Jun | 2023 | 0.0024261 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2023-06-09 06:55 | 2023-06-09 06:58 | 10211 | 0:03 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO SE PROBO QUEDO EN SERVICIO | S23060900000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 3 | 2023-06-09 | 30633 | keep | 0 | Jun | 2023 | 0.020864 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2023-06-09 06:56 | 2023-06-09 06:57 | 137 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 1201-02 LLEVA SU CARGA Y LA DEL 1201-01 | S23060900113 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-09 | 137 | keep | 0 | Jun | 2023 | 9.331e-05 | 9.331e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 137
SAN JUAN | 2023-06-09 06:56 | 2023-06-09 06:57 | 760 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 1201-02 LLEVA SU CARGA Y LA DEL 1201-01 PUENTE ABIERTO ENTRE ACB 3139A - ACB 3141 | S23060900113 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-09 | 760 | keep | 0 | Jun | 2023 | 0.00051763 | 0.00051763 | Momentary | FALSE | FALSE | Not_TMED_Event | 760
SAN JUAN | 2023-06-09 06:56 | 2023-06-09 06:57 | 1225 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA DE TRANSMICION 1203-01 LLEVA 75% DEL 1203-03 PUENTE ABIERTO ENTRE ACB 3139A - ACB 3141 | S23060900113 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-09 | 1225 | keep | 0 | Jun | 2023 | 0.00083434 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2023-06-09 06:56 | 2023-06-09 06:57 | 1452 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA DE TRANSMICION 1203-01 LLEVA 75% DEL 1203-03 PUENTE ABIERTO ENTRE ACB 3139A - ACB 3141 | S23060900113 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-09 | 1452 | keep | 0 | Jun | 2023 | 0.00098895 | 0.00098895 | Momentary | FALSE | FALSE | Not_TMED_Event | 1452
SAN JUAN | 2023-06-09 06:56 | 2023-06-09 06:57 | 462 | 0:01 | P | LINEA DE TRANSMISION 38KV | RECIERRE LINEA DE TRANSMICION 1203-01 LLEVA 75% DEL 1203-03 PUENTE ABIERTO ENTRE ACB 3139A - ACB 3141 | S23060900113 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-09 | 462 | keep | 0 | Jun | 2023 | 0.00031467 | 0.00031467 | Momentary | FALSE | FALSE | Not_TMED_Event | 462
SAN JUAN | 2023-06-09 06:58 | 2023-06-09 16:42 | 1 | 9:44 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR Y 1 X 65 EN C/L EVENTO TRANSFERIDO DE CAROLINA | R23060900033 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 584 | 2023-06-09 | 584 | keep | 0 | Jun | 2023 | 0.00039776 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-06-09 06:59 | 2023-06-09 09:00 | 1938 | 2:01 | P | DESGANCHE | SE REALIZO DESGANCHE 100% EN SERVICIO | C23060900058 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 121 | 2023-06-09 | 234498 | keep | 0 | Jun | 2023 | 0.15972 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-09 07:08 | 2023-06-09 22:23 | 12 | 15:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR SE REPARO BAJANTE SECUNDARIO | B23060900036 | New_Event | Secondary Wire Break | Include | Include | Equipment | 915 | 2023-06-09 | 10980 | keep | 0 | Jun | 2023 | 0.0074784 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2023-06-09 07:08 | 2023-06-09 07:09 | 527 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23060900072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-09 | 527 | keep | 0 | Jun | 2023 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
AGUADILLA | 2023-06-09 07:08 | 2023-06-09 11:10 | 60 | 4:02 | P | NO SE REPORTO CAUSA | 1 X 65 EN CL NO SE ENCONTRO CAUSA | M23060900032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 242 | 2023-06-09 | 14520 | keep | 0 | Jun | 2023 | 0.0098895 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-06-09 07:11 | 2023-06-09 12:30 | 70 | 5:19 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | M23060900033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 319 | 2023-06-09 | 22330 | keep | 0 | Jun | 2023 | 0.015209 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2023-06-09 07:12 | 2023-06-09 10:44 | 8 | 3:32 | P | CABLE SOTERRADO AVERIADO | 1X25 DE RISER @ T-10 AVERIA NUEVA: DEL T-10 @ T-11 AVERIA VIEJA: DEL T-13 @ T-12 FUERA DE SERVICIO: T-11 & T-12 (SE REFIRIO AL DISTRITO) | R23060900017 | New_Event | UG Cable Fault | Include | Include | Equipment | 212 | 2023-06-09 | 1696 | keep | 0 | Jun | 2023 | 0.0011551 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-06-09 07:25 | 2023-06-09 12:10 | 80 | 4:45 | P | NO SE REPORTO CAUSA | 1 X 50 EN CL NO SE ENCONTRO CAUSA | M23060900038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 285 | 2023-06-09 | 22800 | keep | 0 | Jun | 2023 | 0.015529 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-06-09 07:25 | 2023-06-09 12:25 | 20 | 5:00 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMA | A23060900026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 300 | 2023-06-09 | 6000 | keep | 0 | Jun | 2023 | 0.0040866 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-06-09 07:25 | 2023-06-09 12:33 | 30 | 5:08 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMA | A23060900027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 308 | 2023-06-09 | 9240 | keep | 0 | Jun | 2023 | 0.0062933 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-06-09 07:37 | 2023-06-09 21:37 | 67 | 14:00 | P | ANIMAL | 1X65 EN C/L CRUCE POR AVE | B23060900044 | New_Event | Animals | Include | Include | Wildlife | 840 | 2023-06-09 | 56280 | keep | 0 | Jun | 2023 | 0.038332 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
SAN JUAN | 2023-06-09 07:38 | 2023-06-09 16:58 | 41 | 9:20 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE Y SE REPARO PUENTE PRIMARIO ABIERTO | S23060900175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 560 | 2023-06-09 | 22960 | keep | 0 | Jun | 2023 | 0.015638 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
HUMACAO | 2023-06-09 07:42 | 2023-06-09 07:44 | 3701 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 EN PATRULLAJE AEREO EL 6/8/2023 SOLO SE REPORTARON DESGANCHES PREVENTIVOS Y PREVENTIVOS PREFERENCIAL (PRIORITY) | C23060900063 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-09 | 7402 | keep | 0 | Jun | 2023 | 0.0050415 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
HUMACAO | 2023-06-09 07:42 | 2023-06-09 07:44 | 989 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 EN PATRULLAJE AEREO EL 6/8/2023 SOLO SE REPORTARON DESGANCHES PREVENTIVOS Y PREVENTIVOS PREFERENCIAL (PRIORITY) | C23060900063 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-09 | 1978 | keep | 0 | Jun | 2023 | 0.0013472 | 0.0006736 | Momentary | FALSE | FALSE | Not_TMED_Event | 989
HUMACAO | 2023-06-09 07:42 | 2023-06-09 07:44 | 1467 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 EN PATRULLAJE AEREO EL 6/8/2023 SOLO SE REPORTARON DESGANCHES PREVENTIVOS Y PREVENTIVOS PREFERENCIAL (PRIORITY) | C23060900063 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-09 | 2934 | keep | 0 | Jun | 2023 | 0.0019983 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
VEGA BAJA | 2023-06-09 07:46 | 2023-06-09 14:00 | 40 | 6:14 | P | ANIMAL | 1 X 40 EN CL CRUCE POR AVE | A23060900030 | New_Event | Animals | Include | Include | Wildlife | 374 | 2023-06-09 | 14960 | keep | 0 | Jun | 2023 | 0.010189 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-06-09 07:55 | 2023-06-09 11:15 | 20 | 3:20 | P | NO SE REPORTO CAUSA | 1 X 15 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23060900033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 200 | 2023-06-09 | 4000 | keep | 0 | Jun | 2023 | 0.0027244 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-06-09 08:05 | 2023-06-09 12:39 | 2 | 4:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | P23060900100 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 274 | 2023-06-09 | 548 | keep | 0 | Jun | 2023 | 0.00037324 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2023-06-09 08:05 | 2023-06-09 12:30 | 7 | 4:25 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REQUIERE DESGANCHE | A23060900034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 265 | 2023-06-09 | 1855 | keep | 0 | Jun | 2023 | 0.0012634 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-06-09 08:24 | 2023-06-09 10:26 | 12 | 2:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REMPLAZAR BAJANTE SECUNDARIO | R23060800135 | New_Event | Secondary Wire Break | Include | Include | Equipment | 122 | 2023-06-09 | 1464 | keep | 0 | Jun | 2023 | 0.00099712 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-06-09 08:26 | 2023-06-10 09:42 | 1 | 25:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN RISER MAL TIEMPO | B23060900060 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1516 | 2023-06-09 | 1516 | keep | 0 | Jun | 2023 | 0.0010325 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-06-09 08:34 | 2023-06-09 09:48 | 6 | 1:14 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | M23060900059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 74 | 2023-06-09 | 444 | keep | 0 | Jun | 2023 | 0.00030241 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2023-06-09 08:46 | 2023-06-09 15:07 | 12 | 6:21 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | C23060900084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 381 | 2023-06-09 | 4572 | keep | 0 | Jun | 2023 | 0.003114 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2023-06-09 08:46 | 2023-06-09 14:41 | 30 | 5:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | TRABAJAR ELIMINANDO CABLE PROVICIONAL AEREO | P23060900125 | New_Event | Secondary Wire Break | Include | Include | Equipment | 355 | 2023-06-09 | 10650 | keep | 0 | Jun | 2023 | 0.0072537 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2023-06-09 08:50 | 2023-06-09 21:30 | 45 | 12:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA FUERTES VIENTOS | A23060900043 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 760 | 2023-06-09 | 34200 | keep | 0 | Jun | 2023 | 0.023293 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2023-06-09 08:55 | 2023-06-09 18:25 | 100 | 9:30 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE PRIMARIO EN CAJA DE CORTE DE LINEA | M23060900064 | New_Event | Primary Wire Break | Include | Include | Equipment | 570 | 2023-06-09 | 57000 | keep | 0 | Jun | 2023 | 0.038822 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2023-06-09 09:10 | 2023-06-09 14:09 | 5 | 4:59 | P | PARARRAYOS DEFECTUOSO | SE ELIMINO PARARRAYO EN MONTURA TRIFASICA 1 X 65 EN CORTE DE LINEA | P23060900140 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 299 | 2023-06-09 | 1495 | keep | 0 | Jun | 2023 | 0.0010182 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-06-09 09:18 | 2023-06-09 13:05 | 357 | 3:47 | P | DESGANCHE | 1 80 Y 1 X 100 EN C/L DESGANCHE | C23060900092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2023-06-09 | 81039 | keep | 0 | Jun | 2023 | 0.055195 | 0.00024315 | Sustained | FALSE | FALSE | Not_TMED_Event | 357
BARRANQUITAS | 2023-06-09 09:32 | 2023-06-09 12:30 | 12 | 2:58 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE XMR POR DERRAME DE ACEITE DE 75KVA X 50KVA | C23060900100 | New_Event | Service Transformer Failure | Include | Include | Equipment | 178 | 2023-06-09 | 2136 | keep | 0 | Jun | 2023 | 0.0014548 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-06-09 09:33 | 2023-06-09 15:16 | 90 | 5:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2X100 EN C/L SE REMPLAZARON (2) CAJAS PRIMARIAS QUEMADAS | B23060900094 | New_Event | Cutout Failure | Include | Include | Equipment | 343 | 2023-06-09 | 30870 | keep | 0 | Jun | 2023 | 0.021025 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
AGUADILLA | 2023-06-09 09:34 | 2023-06-09 12:29 | 6 | 2:55 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REMOVIO BAMUS SOBRE TRANSFORMADOR | P23060900154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2023-06-09 | 1050 | keep | 0 | Jun | 2023 | 0.00071515 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-06-09 09:56 | 2023-06-09 13:53 | 150 | 3:57 | P | DESGANCHE | 2 X 100 EN C/L SE REALIZO DESGANCHE | S23060900343 | New_Event | Vegetation Contact | Include | Include | Vegetation | 237 | 2023-06-09 | 35550 | keep | 0 | Jun | 2023 | 0.024213 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-06-09 09:59 | 2023-06-09 10:57 | 225 | 0:58 | T | DESGANCHE | SE RETIRO BAMBUAS CON VARETA DEL PISO Y SE CERRO INTERRUPTOR 100% EN SERVICIO Y 80% DEL 1303-05 | S2306090000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2023-06-09 | 13050 | keep | 0 | Jun | 2023 | 0.0088883 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2023-06-09 09:59 | 2023-06-09 10:57 | 696 | 0:58 | P | ALIMENTADOR AMARRADO | SE RETIRO BAMBUAS CON VARETA DEL PISO Y SE CERRO INTERRUPTOR 1303-04 100% EN SERVICIO Y LLEVA 80% DEL 1303-05 | S2306090000X | New_Event | Feeder Load Transferred | Include | Include | Other | 58 | 2023-06-09 | 40368 | keep | 0 | Jun | 2023 | 0.027494 | 0.00047404 | Sustained | FALSE | FALSE | Not_TMED_Event | 696
CAGUAS | 2023-06-09 10:03 | 2023-06-09 14:25 | 125 | 4:22 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L NO CAUSA | C23060900104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 262 | 2023-06-09 | 32750 | keep | 0 | Jun | 2023 | 0.022306 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2023-06-09 10:04 | 2023-06-09 12:42 | 31 | 2:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23060900108 | New_Event | Secondary Wire Break | Include | Include | Equipment | 158 | 2023-06-09 | 4898 | keep | 0 | Jun | 2023 | 0.003336 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
BAYAMON | 2023-06-09 10:08 | 2023-06-09 13:00 | 16 | 2:52 | P | CABLE SOTERRADO AVERIADO | BY-230609-02 SE AISLO LA AVERIA Y SE CERRO MACHETES | B23060900109 | New_Event | UG Cable Fault | Include | Include | Equipment | 172 | 2023-06-09 | 2752 | keep | 0 | Jun | 2023 | 0.0018744 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2023-06-09 10:11 | 2023-06-09 16:46 | 40 | 6:35 | P | SOBRECARGA | 1 X 50 EN CL SOBRECARGA | M23060900077 | New_Event | Trip Due To Overload | Include | Include | Other | 395 | 2023-06-09 | 15800 | keep | 0 | Jun | 2023 | 0.010761 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-06-09 10:17 | 2023-06-09 14:52 | 231 | 4:35 | P | SECUNDARIA/DESGANCHE | 1X100 EN C/L DESGANCHE SECUNDARIO | B23060900112 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 275 | 2023-06-09 | 63525 | keep | 0 | Jun | 2023 | 0.043267 | 0.00015733 | Sustained | FALSE | FALSE | Not_TMED_Event | 231
BAYAMON | 2023-06-09 10:25 | 2023-06-09 11:54 | 4 | 1:29 | P | DESGANCHE | 1 X 15 EN XMR | B23060900183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2023-06-09 | 356 | keep | 0 | Jun | 2023 | 0.00024247 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-06-09 10:30 | 2023-06-09 12:30 | 12 | 2:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO XMR Y SE REMPLAZO CAJA PRIMARIA Y AISLADOR | R23060900024 | New_Event | Cutout Failure | Include | Include | Equipment | 120 | 2023-06-09 | 1440 | keep | 0 | Jun | 2023 | 0.00098078 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-06-09 10:42 | 2023-06-09 12:45 | 3 | 2:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA QUEMADA PRIMARIA EN RISER | P23060900191 | New_Event | Cutout Failure | Include | Include | Equipment | 123 | 2023-06-09 | 369 | keep | 0 | Jun | 2023 | 0.00025132 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-06-09 10:44 | 2023-06-10 20:28 | 30 | 33:44 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL AEREO HACIA A T-11 | R23060900017 | New_Event | UG Cable Fault | Include | Include | Equipment | 2024 | 2023-06-09 | 60720 | keep | 0 | Jun | 2023 | 0.041356 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2023-06-09 10:44 | 2023-06-09 11:36 | 12 | 0:52 | P | ANIMAL | 1X20 EN XMR CRUCE POR AVE | R23060900028 | New_Event | Animals | Include | Include | Wildlife | 52 | 2023-06-09 | 624 | keep | 0 | Jun | 2023 | 0.000425 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-06-09 10:51 | 2023-06-09 12:43 | 137 | 1:52 | S | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA PARA CERRAR PUENTE LINEA 3600 | S23060900382 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 112 | 2023-06-09 | 15344 | keep | 0 | Jun | 2023 | 0.010451 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
SAN JUAN | 2023-06-09 10:51 | 2023-06-09 12:43 | 760 | 1:52 | S | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA PARA CERRAR PUENTE LINEA 3600 | S23060900382 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 112 | 2023-06-09 | 85120 | keep | 0 | Jun | 2023 | 0.057975 | 0.00051763 | Sustained | FALSE | FALSE | Not_TMED_Event | 760
VEGA BAJA | 2023-06-09 10:57 | 2023-06-09 16:30 | 25 | 5:33 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A23060900079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 333 | 2023-06-09 | 8325 | keep | 0 | Jun | 2023 | 0.0056701 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2023-06-09 11:06 | 2023-06-09 14:50 | 40 | 3:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CL SE REMPLAZO CAJA PRIMARIA | A23060900089 | New_Event | Cutout Failure | Include | Include | Equipment | 224 | 2023-06-09 | 8960 | keep | 0 | Jun | 2023 | 0.0061026 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-06-09 11:15 | 2023-06-09 12:54 | 40 | 1:39 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | S23060900388 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2023-06-09 | 3960 | keep | 0 | Jun | 2023 | 0.0026971 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-06-09 11:15 | 2023-06-09 11:16 | 3431 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR | A23060900086 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-06-09 | 3431 | keep | 0 | Jun | 2023 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2023-06-09 11:16 | 2023-06-09 12:07 | 70 | 0:51 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A23060900092 | 1st_after_momentary | Animals | Include | Include | Wildlife | 51 | 2023-06-09 | 3570 | keep | 0 | Jun | 2023 | 0.0024315 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2023-06-09 11:31 | 2023-06-09 15:40 | 60 | 4:09 | P | SOBRECARGA | 1 X 140 EN CL SOBRECARGA | M23060900098 | New_Event | Trip Due To Overload | Include | Include | Other | 249 | 2023-06-09 | 14940 | keep | 0 | Jun | 2023 | 0.010176 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-06-09 11:39 | 2023-06-09 12:05 | 1681 | 0:26 | T | NO SE REPORTO CAUSA | DISPARO TENIA R/R OFF SE VERIFICO PERSONAL FUERA SE PROBO POR CONTROL QUEDO EN SERVICIO | S23060900407 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 26 | 2023-06-09 | 43706 | keep | 0 | Jun | 2023 | 0.029768 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
CANOVANAS | 2023-06-09 11:41 | 2023-06-09 13:36 | 12 | 1:55 | P | NO SE REPORTO CAUSA | 1X10 EN XMR | R23060900032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2023-06-09 | 1380 | keep | 0 | Jun | 2023 | 0.00093991 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-06-09 11:50 | 2023-06-09 12:50 | 1498 | 1:00 | T | ALIMENTADOR AMARRADO | SE CERRO BKR LOCALMENTE 1421-02 LLEVA 1421-01 | S23060900410 | New_Event | Feeder Load Transferred | Include | Include | Other | 60 | 2023-06-09 | 89880 | keep | 0 | Jun | 2023 | 0.061217 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
SAN JUAN | 2023-06-09 11:50 | 2023-06-09 12:50 | 164 | 1:00 | T | NO SE REPORTO CAUSA | SE CERRO BKR LOCALMENTE LLEVA 1421-01 | S23060900410 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 60 | 2023-06-09 | 9840 | keep | 0 | Jun | 2023 | 0.006702 | 0.0001117 | Sustained | FALSE | FALSE | Not_TMED_Event | 164
GUAYAMA | 2023-06-09 11:53 | 2023-06-09 11:54 | 449 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | P23060900225 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-06-09 | 449 | keep | 0 | Jun | 2023 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
CANOVANAS | 2023-06-09 12:02 | 2023-06-09 12:51 | 11 | 0:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REPARAR BARRA ABIERTA EN PEDESTAL | R23060900033 | New_Event | Secondary Wire Break | Include | Include | Equipment | 49 | 2023-06-09 | 539 | keep | 0 | Jun | 2023 | 0.00036711 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
PONCE | 2023-06-09 12:03 | 2023-06-09 12:04 | 2113 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23060900225 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-09 | 2113 | keep | 0 | Jun | 2023 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
SAN JUAN | 2023-06-09 12:04 | 2023-06-09 14:10 | 6 | 2:06 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L Y SE REPARO PUENTE PRIMARIO 1 X 80 1X 65 | S23060900420 | New_Event | Primary Wire Break | Include | Include | Equipment | 126 | 2023-06-09 | 756 | keep | 0 | Jun | 2023 | 0.00051491 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2023-06-09 12:04 | 2023-06-09 14:10 | 44 | 2:06 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | R23060900034 | New_Event | Animals | Include | Include | Wildlife | 126 | 2023-06-09 | 5544 | keep | 0 | Jun | 2023 | 0.003776 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
CANOVANAS | 2023-06-09 12:05 | 2023-06-09 15:16 | 10 | 3:11 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMX Y SE REPARO BAJANTES SECUNDARIO | R23060900035 | New_Event | Secondary Wire Break | Include | Include | Equipment | 191 | 2023-06-09 | 1910 | keep | 0 | Jun | 2023 | 0.0013009 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-06-09 12:07 | 2023-06-09 12:08 | 3431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | A23060900103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-09 | 3431 | keep | 0 | Jun | 2023 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2023-06-09 12:08 | 2023-06-09 13:54 | 70 | 1:46 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A23060900092 | Partial_restoration | Animals | Include | Include | Wildlife | 106 | 2023-06-09 | 7420 | keep | 0 | Jun | 2023 | 0.0050537 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-06-09 12:08 | 2023-06-09 17:40 | 30 | 5:32 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23060900151 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 332 | 2023-06-09 | 9960 | keep | 0 | Jun | 2023 | 0.0067837 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-06-09 12:12 | 2023-06-09 14:48 | 2 | 2:36 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L PARA CERRAR PUENTE PRIMARIO LINEA A CAJA EN XMR EVENTO TRANSFERIDO | P23060900233 | New_Event | Primary Wire Break | Include | Include | Equipment | 156 | 2023-06-09 | 312 | keep | 0 | Jun | 2023 | 0.0002125 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2023-06-09 12:24 | 2023-06-09 15:13 | 10 | 2:49 | P | DESGANCHE | 1 X 20 EN C/L | C23060900133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2023-06-09 | 1690 | keep | 0 | Jun | 2023 | 0.0011511 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2023-06-09 12:27 | 2023-06-09 20:10 | 40 | 7:43 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CONVERTIDOR FUERTES VIENTOS | A23060900109 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 463 | 2023-06-09 | 18520 | keep | 0 | Jun | 2023 | 0.012614 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-06-09 12:31 | 2023-06-09 13:10 | 7 | 0:39 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C23060900134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 39 | 2023-06-09 | 273 | keep | 0 | Jun | 2023 | 0.00018594 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-06-09 12:36 | 2023-06-09 12:56 | 8 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C23060900136 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-06-09 | 160 | keep | 0 | Jun | 2023 | 0.00010898 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-06-09 12:38 | 2023-06-09 12:45 | 878 | 0:07 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE VERIFICO PERSONAL FUERA CERRADO POR SCADA | B23060900156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2023-06-09 | 6146 | keep | 0 | Jun | 2023 | 0.004186 | 0.000598 | Sustained | FALSE | FALSE | Not_TMED_Event | 878
CAGUAS | 2023-06-09 12:51 | 2023-06-09 15:36 | 60 | 2:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L REPORTAN FUERTES VIENTOS | C23060900143 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 165 | 2023-06-09 | 9900 | keep | 0 | Jun | 2023 | 0.0067428 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-06-09 12:58 | 2023-06-10 13:31 | 40 | 24:33 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA PUENTE ABIERTO | A23060900118 | New_Event | Primary Wire Break | Include | Include | Equipment | 1473 | 2023-06-09 | 58920 | keep | 0 | Jun | 2023 | 0.04013 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-06-09 13:00 | 2023-06-09 14:43 | 8 | 1:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZARON CONECTORES SECUNDARIOS | S23060900459 | New_Event | Secondary Wire Break | Include | Include | Equipment | 103 | 2023-06-09 | 824 | keep | 0 | Jun | 2023 | 0.00056122 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-06-09 13:00 | 2023-06-09 19:07 | 12 | 6:07 | P | CABLE SOTERRADO AVERIADO | SE PULSO/REPARO TRAMO SOTERRADO AVERIADO DEL T-33-A @ T-34 MEDIANTE GOI BY-230609-02 | B23060900109 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 367 | 2023-06-09 | 4404 | keep | 0 | Jun | 2023 | 0.0029995 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-06-09 13:00 | 2023-06-09 15:10 | 1 | 2:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN MONTURA FUERTES VIENTOS | M23060900126 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 130 | 2023-06-09 | 130 | keep | 0 | Jun | 2023 | 8.8542e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-06-09 13:02 | 2023-06-09 14:18 | 643 | 1:16 | T | ALIMENTADOR AMARRADO | SE ABRIO INTERRUPTOR PARA REEMPLAZO DE MACHETE EN SALIDA DE ALIMENTADOR CARGA POR 1530-09 SJ-230609-02 | S23060900157 | Additional_clients | Feeder Load Transferred | Include | Include | Other | 76 | 2023-06-09 | 48868 | keep | 0 | Jun | 2023 | 0.033284 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-09 13:02 | 2023-06-09 14:18 | 1310 | 1:16 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA REEMPLAZO DE MACHETE EN SALIDA DE ALIMENTADOR LLEVA CARGA 1530-07 SJ-230609-02 | S23060900157 | Additional_clients | Switch Failure | Include | Include | Equipment | 76 | 2023-06-09 | 99560 | keep | 0 | Jun | 2023 | 0.06781 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-09 13:06 | 2023-06-10 15:57 | 40 | 26:51 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L PARA CERRAR PUENTE PRIMARIO DE LINEA @ CAJA EN C/L | B23060900168 | New_Event | Primary Wire Break | Include | Include | Equipment | 1611 | 2023-06-09 | 64440 | keep | 0 | Jun | 2023 | 0.04389 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-06-09 13:06 | 2023-06-09 21:23 | 107 | 8:17 | P | DESGANCHE | 1 X 80 EN C/L SE REALIZO DESGANCHE | S23060900464 | New_Event | Vegetation Contact | Include | Include | Vegetation | 497 | 2023-06-09 | 53179 | keep | 0 | Jun | 2023 | 0.03622 | 7.2877e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 107
BAYAMON | 2023-06-09 13:07 | 2023-06-09 14:43 | 1 | 1:36 | P | TRANSFORMADOR AVERIADO | 1X30 EN RISER SE COMPLETO NIVEL DE ACEITE AL TRANSFORMADOR | B23060900169 | New_Event | Service Transformer Failure | Include | Include | Equipment | 96 | 2023-06-09 | 96 | keep | 0 | Jun | 2023 | 6.5385e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-06-09 13:14 | 2023-06-09 14:29 | 4133 | 1:15 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA 30% EN SERVICIO SJ-230609-03 | S23060900481 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 75 | 2023-06-09 | 309975 | keep | 0 | Jun | 2023 | 0.21112 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2023-06-09 13:15 | 2023-06-09 15:25 | 40 | 2:10 | P | DESGANCHE | 2 X 50 EN C/L SE DESGANCHO | C23060900149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2023-06-09 | 5200 | keep | 0 | Jun | 2023 | 0.0035417 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-06-09 13:15 | 2023-06-09 13:50 | 4 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | A23060900056 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2023-06-09 | 140 | keep | 0 | Jun | 2023 | 9.5353e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2023-06-09 13:22 | 2023-06-09 16:48 | 15 | 3:26 | P | DESGANCHE | 2 X 50 EN C/L SE DESGANCHO | C23060900151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2023-06-09 | 3090 | keep | 0 | Jun | 2023 | 0.0021046 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-06-09 13:39 | 2023-06-09 19:56 | 15 | 6:17 | P | CRUCETA DEFECTUOSA O AVERIADA | SE ABRIO MONTURA DE XMR PARA REEMPLAZO DE CRUCETA PARTIDA | S23060900486 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 377 | 2023-06-09 | 5655 | keep | 0 | Jun | 2023 | 0.0038516 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-06-09 13:49 | 2023-06-10 10:56 | 1 | 21:07 | P | ANIMAL | 1 X 15 EN MONTURA 1 X 40 EN RISER POR AVE | S23060900493 | New_Event | Animals | Include | Include | Wildlife | 1267 | 2023-06-09 | 1267 | keep | 0 | Jun | 2023 | 0.00086295 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-06-09 13:57 | 2023-06-09 13:58 | 449 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | P23060900288 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2023-06-09 | 449 | keep | 0 | Jun | 2023 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
BAYAMON | 2023-06-09 13:58 | 2023-06-09 13:59 | 1408 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE BKR EN SERVICIO LLEVA 1714-02 | B2306090000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-09 | 1408 | keep | 0 | Jun | 2023 | 0.00095898 | 0.00095898 | Momentary | FALSE | FALSE | Not_TMED_Event | 1408
BAYAMON | 2023-06-09 13:58 | 2023-06-09 13:59 | 455 | 0:01 | T | DESGANCHE | RECIERRE DE BKR EN SERVICIO LLEVA 1714-02 | B2306090000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-06-09 | 455 | keep | 0 | Jun | 2023 | 0.0003099 | 0.0003099 | Momentary | FALSE | FALSE | Not_TMED_Event | 455
BAYAMON | 2023-06-09 13:59 | 2023-06-10 08:49 | 40 | 18:50 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23060900187 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1130 | 2023-06-09 | 45200 | keep | 0 | Jun | 2023 | 0.030786 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-06-09 14:03 | 2023-06-09 16:07 | 20 | 2:04 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P23060900293 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 124 | 2023-06-09 | 2480 | keep | 0 | Jun | 2023 | 0.0016891 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-06-09 14:11 | 2023-06-09 14:13 | 4381 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO REALIZA RECIERRE SE COLOCA RR EN OFF Y SE REALIZA PRUEBA QUEDANDO EN SERVICIO | M23060900145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-09 | 8762 | keep | 0 | Jun | 2023 | 0.0059678 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
BAYAMON | 2023-06-09 14:18 | 2023-06-09 14:19 | 2858 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23060900193 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-09 | 2858 | keep | 0 | Jun | 2023 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
MAYAGÃœEZ | 2023-06-09 14:23 | 2023-06-09 17:39 | 100 | 3:16 | P | DESGANCHE | 1 X 140 EN CL DESGANCHE | M23060900149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2023-06-09 | 19600 | keep | 0 | Jun | 2023 | 0.013349 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-06-09 14:26 | 2023-06-09 15:54 | 40 | 1:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO DE CAJA PRIMARIA | R23060900043 | New_Event | Cutout Failure | Include | Include | Equipment | 88 | 2023-06-09 | 3520 | keep | 0 | Jun | 2023 | 0.0023975 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-06-09 14:27 | 2023-06-10 10:54 | 15 | 20:27 | P | DESGANCHE | 1 X 40 EN CORTE LINEA DESGANCHE | P23060900304 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1227 | 2023-06-09 | 18405 | keep | 0 | Jun | 2023 | 0.012536 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-06-09 14:29 | 2023-06-09 14:40 | 2893 | 0:11 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO ALIMENTADOR POR AISLADOR PARTIDO 60% EN SERVICIO SJ-230609-03 | S23060900481 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 11 | 2023-06-09 | 31823 | keep | 0 | Jun | 2023 | 0.021675 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-09 14:34 | 2023-06-09 15:27 | 8 | 0:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REPARAR SECUNDARIA | B23060900198 | New_Event | Secondary Wire Break | Include | Include | Equipment | 53 | 2023-06-09 | 424 | keep | 0 | Jun | 2023 | 0.00028878 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-06-09 14:40 | 2023-06-09 15:48 | 1653 | 1:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO ALIMENTADOR POR AISLADOR PARTIDO 90% EN SERVICIO SJ-230609-03 | S23060900481 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 68 | 2023-06-09 | 112404 | keep | 0 | Jun | 2023 | 0.076558 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-06-09 14:50 | 2023-06-09 18:47 | 449 | 3:57 | T | DESCONECTIVO DEFECTUOSO | SE CAMBIARON MACHETES QUEMADOS | P23060900291 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 237 | 2023-06-09 | 106413 | keep | 0 | Jun | 2023 | 0.072477 | 0.00030581 | Sustained | FALSE | FALSE | Not_TMED_Event | 449
BARRANQUITAS | 2023-06-09 14:51 | 2023-06-09 18:00 | 1 | 3:09 | P | NO SE REPORTO CAUSA | 1 X 15 EN MONTURA DE XMR | C23060900170 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 189 | 2023-06-09 | 189 | keep | 0 | Jun | 2023 | 0.00012873 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-06-09 14:55 | 2023-06-09 16:13 | 30 | 1:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA Y 1X100 EN C/L ENVENTO TRANSFERIDO | P23060900319 | New_Event | Cutout Failure | Include | Include | Equipment | 78 | 2023-06-09 | 2340 | keep | 0 | Jun | 2023 | 0.0015938 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-06-09 15:00 | 2023-06-09 17:47 | 19 | 2:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C23060900177 | New_Event | Secondary Wire Break | Include | Include | Equipment | 167 | 2023-06-09 | 3173 | keep | 0 | Jun | 2023 | 0.0021611 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
MAYAGÃœEZ | 2023-06-09 15:26 | 2023-06-09 18:10 | 10 | 2:44 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO SE REPORTO CAUSA | M23060900177 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 164 | 2023-06-09 | 1640 | keep | 0 | Jun | 2023 | 0.001117 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-06-09 15:33 | 2023-06-09 20:18 | 12 | 4:45 | P | TRANSFORMADOR AVERIADO | XMR AVERIADO SE REFIERE PARA REMPLAZO, SE PASO LA CARGA A OTRO XMR | C23060900199 | New_Event | Service Transformer Failure | Include | Include | Equipment | 285 | 2023-06-09 | 3420 | keep | 0 | Jun | 2023 | 0.0023293 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-06-09 15:47 | 2023-06-09 17:38 | 15 | 1:51 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO XMR PARA RETEZAR LINEA SECUNDARIA | C23060900204 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 111 | 2023-06-09 | 1665 | keep | 0 | Jun | 2023 | 0.001134 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-06-09 15:48 | 2023-06-09 17:19 | 413 | 1:31 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR PARTIDO Y SE ABRIO PUENTE HACIA ESTRUCTURA ABANDONADA SJ-230609-03 | S23060900481 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 91 | 2023-06-09 | 37583 | keep | 0 | Jun | 2023 | 0.025598 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-06-09 15:51 | 2023-06-09 17:29 | 1 | 1:38 | P | OTRAS CAUSAS | 2 X 20 EN CL SE REPORTA BAJO VOLTAJE EN LINEA PRIMARIA POR CONSIGUIENTE LA BOMBA TRUFASICA DE LA AAA NO FUNCIONA | M23060900182 | New_Event | Other Causes | Include | Include | Other | 98 | 2023-06-09 | 98 | keep | 0 | Jun | 2023 | 6.6747e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-06-09 15:56 | 2023-06-10 17:34 | 1 | 25:38 | P | ANIMAL | 1X25 EN XMR - CRUCE POR AVE | B23060900214 | New_Event | Animals | Include | Include | Wildlife | 1538 | 2023-06-09 | 1538 | keep | 0 | Jun | 2023 | 0.0010475 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-06-09 15:57 | 2023-06-10 10:10 | 60 | 18:13 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | 1 X 50 EN CORTE LINEA SE LIBERA LINEA PRIMARIA ATACHADA A POSTE TELEFONICA PARTIDO Y SE COLOCA TIGUERO SE RECOMIENDA INSTALACION POSTE PRIMARIO METAL 40 PIES | M23060900185 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 1093 | 2023-06-09 | 65580 | keep | 0 | Jun | 2023 | 0.044666 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2023-06-09 15:59 | 2023-06-09 19:10 | 50 | 3:11 | P | DESGANCHE | 1 X 30 EN SALIDA DE CONVERTIDOR SE RETIRO BAMBUS | A23060900150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2023-06-09 | 9550 | keep | 0 | Jun | 2023 | 0.0065045 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-06-09 16:00 | 2023-06-09 19:49 | 10 | 3:49 | P | ANIMAL | 1X25 EN C/L POR CULEBRA (SERPIENTE) EN LA LINEA (EVENTO TRANSFERIDO DESDE PONCE) | P23060900034 | New_Event | Animals | Include | Include | Wildlife | 229 | 2023-06-09 | 2290 | keep | 0 | Jun | 2023 | 0.0015597 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-06-09 16:07 | 2023-06-09 17:16 | 50 | 1:09 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | C23060900208 | New_Event | Animals | Include | Include | Wildlife | 69 | 2023-06-09 | 3450 | keep | 0 | Jun | 2023 | 0.0023498 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-06-09 16:08 | 2023-06-09 23:41 | 70 | 7:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REEMPLAZO CAJA PRIMARIA | B23060900222 | New_Event | Cutout Failure | Include | Include | Equipment | 453 | 2023-06-09 | 31710 | keep | 0 | Jun | 2023 | 0.021598 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-06-09 16:14 | 2023-06-10 11:20 | 499 | 19:06 | P | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALAMBRE EN EL PISO SE ABRIO MACHETE LLEVA 1421-1 Y 50% DEL 1531-02 | S23060900592 | New_Event | Feeder Load Transferred | Include | Include | Other | 1146 | 2023-06-09 | 571854 | keep | 0 | Jun | 2023 | 0.38949 | 0.00033987 | Sustained | FALSE | FALSE | Not_TMED_Event | 499
SAN JUAN | 2023-06-09 16:14 | 2023-06-10 11:20 | 54 | 19:06 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO ALAMBRE EN EL PISO SE ABRIO MACHETE LLEVA 1421-1 Y 50% DEL 1531-02 | S23060900592 | New_Event | Primary Wire Break | Include | Include | Equipment | 1146 | 2023-06-09 | 61884 | keep | 0 | Jun | 2023 | 0.042149 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
SAN JUAN | 2023-06-09 16:14 | 2023-06-10 11:20 | 119 | 19:06 | P | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALAMBRE EN EL PISO SE ABRIO MACHETE LLEVA 1421-1 Y 50% DEL 1531-02 | S23060900592 | New_Event | Feeder Load Transferred | Include | Include | Other | 1146 | 2023-06-09 | 136374 | keep | 0 | Jun | 2023 | 0.092884 | 8.105e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 119
BARRANQUITAS | 2023-06-09 16:15 | 2023-06-09 20:21 | 10 | 4:06 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | P23060900343 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 246 | 2023-06-09 | 2460 | keep | 0 | Jun | 2023 | 0.0016755 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-06-09 16:16 | 2023-06-09 18:26 | 72 | 2:10 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO PUENTE PRIMARIO ABIERTO EN TRONCAL | S23060900678 | New_Event | Primary Wire Break | Include | Include | Equipment | 130 | 2023-06-09 | 9360 | keep | 0 | Jun | 2023 | 0.0063751 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
SAN JUAN | 2023-06-09 16:20 | 2023-06-10 22:21 | 25 | 30:01 | P | DESGANCHE | 2X65 EN C/L DESGANCHE (EVENTO TRANSFERIDO) | P23060900332 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1801 | 2023-06-09 | 45025 | keep | 0 | Jun | 2023 | 0.030666 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-06-09 16:23 | 2023-06-09 20:05 | 20 | 3:42 | P | DESGANCHE | 2 X 40 EN C/L Y SE REALIZO DESGANCHE | S23060900595 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2023-06-09 | 4440 | keep | 0 | Jun | 2023 | 0.0030241 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-06-09 16:36 | 2023-06-11 10:23 | 15 | 41:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | S23060900601 | New_Event | Cutout Failure | Include | Include | Equipment | 2507 | 2023-06-09 | 37605 | keep | 0 | Jun | 2023 | 0.025613 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-06-09 16:42 | 2023-06-09 20:58 | 213 | 4:16 | P | NO SE REPORTO CAUSA | 1X80 EN C/L | B23060900230 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 256 | 2023-06-09 | 54528 | keep | 0 | Jun | 2023 | 0.037139 | 0.00014507 | Sustained | FALSE | FALSE | Not_TMED_Event | 213
UTUADO | 2023-06-09 16:44 | 2023-06-09 18:40 | 1521 | 1:56 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO CORTE DE LINEA PARA SECCIONALIZAR POSTE FUERA DE USO QUE CAYO SOBRE ALIMENTADOR, SE CERRO INTERRUPTOR MANUAL ELECTRICO (RTU DOWN) | M23060900160 | New_Event | Primary Pole Failure | Include | Include | Equipment | 116 | 2023-06-09 | 176436 | keep | 0 | Jun | 2023 | 0.12017 | 0.0010359 | Sustained | FALSE | FALSE | Not_TMED_Event | 1521
BAYAMON | 2023-06-09 16:48 | 2023-06-10 17:00 | 40 | 24:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON (2) CAJAS PRIMARIAS MEDIANTE GOI BY-230609-01 | S23060900605 | New_Event | Cutout Failure | Include | Include | Equipment | 1452 | 2023-06-09 | 58080 | keep | 0 | Jun | 2023 | 0.039558 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-06-09 16:52 | 2023-06-09 16:53 | 340 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO 3103-02 LLEVA 20% DEL 3102-01 | C2306090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-09 | 340 | keep | 0 | Jun | 2023 | 0.00023157 | 0.00023157 | Momentary | FALSE | FALSE | Not_TMED_Event | 340
CAGUAS | 2023-06-09 16:52 | 2023-06-09 16:53 | 1922 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 20% DEL 3102-01 | C2306090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-09 | 1922 | keep | 0 | Jun | 2023 | 0.0013091 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
VEGA BAJA | 2023-06-09 16:53 | 2023-06-09 18:39 | 80 | 1:46 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A23060900168 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2023-06-09 | 8480 | keep | 0 | Jun | 2023 | 0.0057757 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-06-09 16:58 | 2023-06-09 18:50 | 200 | 1:52 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE | M23060900203 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2023-06-09 | 22400 | keep | 0 | Jun | 2023 | 0.015257 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2023-06-09 17:01 | 2023-06-09 21:00 | 10 | 3:59 | P | NO SE REPORTO CAUSA | 1 X 15 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23060900172 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 239 | 2023-06-09 | 2390 | keep | 0 | Jun | 2023 | 0.0016278 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-06-09 17:13 | 2023-06-09 18:08 | 1 | 0:55 | P | NO SE REPORTO CAUSA | 1 X 10 EN BANCO XMR | R23060900057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 55 | 2023-06-09 | 55 | keep | 0 | Jun | 2023 | 3.746e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-06-09 17:22 | 2023-06-09 19:44 | 80 | 2:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA 1 X 65 EN CORTE DE LINEA | P23060900373 | New_Event | Cutout Failure | Include | Include | Equipment | 142 | 2023-06-09 | 11360 | keep | 0 | Jun | 2023 | 0.0077372 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2023-06-09 17:22 | 2023-06-09 18:27 | 200 | 1:05 | P | SOBRECARGA | 1 X 140 EN CORTE DE LINEA POR CARGA | P23060900374 | New_Event | Trip Due To Overload | Include | Include | Other | 65 | 2023-06-09 | 13000 | keep | 0 | Jun | 2023 | 0.0088542 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2023-06-09 17:23 | 2023-06-09 20:41 | 40 | 3:18 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C23060900219 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 198 | 2023-06-09 | 7920 | keep | 0 | Jun | 2023 | 0.0053943 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-06-09 17:24 | 2023-06-09 18:25 | 20 | 1:01 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | M23060900211 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 61 | 2023-06-09 | 1220 | keep | 0 | Jun | 2023 | 0.00083094 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-06-09 17:26 | 2023-06-10 05:15 | 12 | 11:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARA SECUNDARIA | B23060900240 | New_Event | Secondary Wire Break | Include | Include | Equipment | 709 | 2023-06-09 | 8508 | keep | 0 | Jun | 2023 | 0.0057948 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2023-06-09 17:53 | 2023-06-09 19:53 | 60 | 2:00 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE LINEA NO SE ENCONTO CAUSA | A23060900197 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2023-06-09 | 7200 | keep | 0 | Jun | 2023 | 0.0049039 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-06-09 17:54 | 2023-06-09 20:45 | 35 | 2:51 | P | DESGANCHE | 1 X 50 EN COERTE DE LINEA DESGANCHE | M23060900220 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2023-06-09 | 5985 | keep | 0 | Jun | 2023 | 0.0040764 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BARRANQUITAS | 2023-06-09 17:59 | 2023-06-09 18:00 | 3296 | 0:01 | T | NO SE REPORTO CAUSA | LEVA 9602-04 | C2306090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-09 | 3296 | keep | 0 | Jun | 2023 | 0.0022449 | 0.0022449 | Momentary | FALSE | FALSE | Not_TMED_Event | 3296
BARRANQUITAS | 2023-06-09 17:59 | 2023-06-09 18:00 | 2937 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO Y SE CERRO POR CONTROL EL 9601-02 | C2306090000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-09 | 2937 | keep | 0 | Jun | 2023 | 0.0020004 | 0.0020004 | Momentary | FALSE | FALSE | Not_TMED_Event | 2937
CANOVANAS | 2023-06-09 18:01 | 2023-06-09 18:33 | 1648 | 0:32 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 2302-03 LLEVA 20% 2402-02 SE VERIFICO BANDERAS DEL BKR Y SE CERRO EN SUBESTACION 100% EN SERVICIO | R23060900061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 32 | 2023-06-09 | 52736 | keep | 0 | Jun | 2023 | 0.035918 | 0.0011224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-06-09 18:01 | 2023-06-09 18:33 | 837 | 0:32 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 2302-03 LLEVA 20% 2402-02 SE VERIFICO BANDERAS DEL BKR Y SE CERRO EN SUBESTACION 100% EN SERVICIO | R23060900061 | New_Event | Feeder Load Transferred | Include | Include | Other | 32 | 2023-06-09 | 26784 | keep | 0 | Jun | 2023 | 0.018242 | 0.00057008 | Sustained | FALSE | FALSE | Not_TMED_Event | 837
CAGUAS | 2023-06-09 18:01 | 2023-06-09 18:44 | 35 | 0:43 | P | ANIMAL | 1X65 EN C/L CRUCE POR AVE | C23060900226 | New_Event | Animals | Include | Include | Wildlife | 43 | 2023-06-09 | 1505 | keep | 0 | Jun | 2023 | 0.001025 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2023-06-09 18:01 | 2023-06-09 18:44 | 35 | 0:43 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | C23060900226 | New_Event | Animals | Include | Include | Wildlife | 43 | 2023-06-09 | 1505 | keep | 0 | Jun | 2023 | 0.001025 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
FAJARDO | 2023-06-09 18:06 | 2023-06-09 18:31 | 40 | 0:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIAS | R23060900062 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 25 | 2023-06-09 | 1000 | keep | 0 | Jun | 2023 | 0.0006811 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-06-09 18:23 | 2023-06-09 20:23 | 31 | 2:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA PORTAFUSIBLE DERRETIDO | P23060900445 | New_Event | Cutout Failure | Include | Include | Equipment | 120 | 2023-06-09 | 3720 | keep | 0 | Jun | 2023 | 0.0025337 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
SAN JUAN | 2023-06-09 18:26 | 2023-06-09 18:28 | 553 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S23060900630 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-09 | 1106 | keep | 0 | Jun | 2023 | 0.00075329 | 0.00037665 | Momentary | FALSE | FALSE | Not_TMED_Event | 553
PONCE | 2023-06-09 18:26 | 2023-06-09 19:30 | 20 | 1:04 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P23060900447 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2023-06-09 | 1280 | keep | 0 | Jun | 2023 | 0.0008718 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-06-09 18:26 | 2023-06-09 21:35 | 100 | 3:09 | P | SOBRECARGA | 1 X 65 EN CL SOBRECARGA SE RECOMIENDA TRANSPOSICION DE FASES | M23060900226 | New_Event | Trip Due To Overload | Include | Include | Other | 189 | 2023-06-09 | 18900 | keep | 0 | Jun | 2023 | 0.012873 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-06-09 18:28 | 2023-06-11 10:55 | 72 | 40:27 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO PUENTE PRIMARIO ABIERTO EN TRONCAL | S23060900678 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 2427 | 2023-06-09 | 174744 | keep | 0 | Jun | 2023 | 0.11902 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-06-09 18:29 | 2023-06-09 20:37 | 150 | 2:08 | P | DESGANCHE | 2 X 100 EN CORTE LINEA DESGANCHE | M23060900228 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2023-06-09 | 19200 | keep | 0 | Jun | 2023 | 0.013077 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
UTUADO | 2023-06-09 18:40 | 2023-06-10 14:30 | 300 | 19:50 | P | FUEGO | EN POSTE Y AREA, POSTE PRIMARIO PARTIDO Y SE REPARO LINEA PRIMARIA ROTA | A23060900160 | New_Event | Fire | Include | Include | Public | 1190 | 2023-06-09 | 357000 | keep | 0 | Jun | 2023 | 0.24315 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
AGUADILLA | 2023-06-09 18:53 | 2023-06-10 11:09 | 175 | 16:16 | P | DESGANCHE | 2 X 50 EN CORTE LINEA DESGANCHE | M23060900244 | New_Event | Vegetation Contact | Include | Include | Vegetation | 976 | 2023-06-09 | 170800 | keep | 0 | Jun | 2023 | 0.11633 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
BAYAMON | 2023-06-09 19:03 | 2023-06-10 15:41 | 5 | 20:38 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1X10 EN XMR SE REPARO SECUNDARIA | S23060900645 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 1238 | 2023-06-09 | 6190 | keep | 0 | Jun | 2023 | 0.004216 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-06-09 19:18 | 2023-06-10 15:27 | 7 | 20:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR REPARO SECUNDARIA | C23060900238 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1209 | 2023-06-09 | 8463 | keep | 0 | Jun | 2023 | 0.0057641 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2023-06-09 19:23 | 2023-06-09 21:19 | 40 | 1:56 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | B23060900257 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2023-06-09 | 4640 | keep | 0 | Jun | 2023 | 0.0031603 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-06-09 19:31 | 2023-06-10 12:20 | 40 | 16:49 | P | DESGANCHE | 1 X 40 EN C/L | C23060900239 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1009 | 2023-06-09 | 40360 | keep | 0 | Jun | 2023 | 0.027489 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-06-09 19:32 | 2023-06-09 19:37 | 3309 | 0:05 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA INSTALAR PUENTE POR PUNTO CALIENTE EN CONECTOR DE MACHETE | A23060900216 | New_Event | Switch Failure | Include | Include | Equipment | 5 | 2023-06-09 | 16545 | keep | 0 | Jun | 2023 | 0.011269 | 0.0022537 | Momentary | FALSE | FALSE | Not_TMED_Event | 3309
BAYAMON | 2023-06-09 19:37 | 2023-06-09 19:38 | 2735 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23060900259 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-09 | 2735 | keep | 0 | Jun | 2023 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
MAYAGÃœEZ | 2023-06-09 19:38 | 2023-06-09 23:45 | 300 | 4:07 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | M23060900275 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 247 | 2023-06-09 | 74100 | keep | 0 | Jun | 2023 | 0.050469 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2023-06-09 19:38 | 2023-06-10 12:25 | 92 | 16:47 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN C/L Y SE LEVANTO CONDUCTOR DEL SUELO. | B23060800164 | New_Event | Primary Wire Break | Include | Include | Equipment | 1007 | 2023-06-09 | 92644 | keep | 0 | Jun | 2023 | 0.063099 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
BAYAMON | 2023-06-09 19:42 | 2023-06-10 09:33 | 7 | 13:51 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23060900261 | New_Event | Secondary Wire Break | Include | Include | Equipment | 831 | 2023-06-09 | 5817 | keep | 0 | Jun | 2023 | 0.0039619 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2023-06-09 19:45 | 2023-06-10 12:45 | 60 | 17:00 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23060900220 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1020 | 2023-06-09 | 61200 | keep | 0 | Jun | 2023 | 0.041683 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2023-06-09 19:46 | 2023-06-10 10:48 | 20 | 15:02 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA POR AVES | A23060900221 | New_Event | Animals | Include | Include | Wildlife | 902 | 2023-06-09 | 18040 | keep | 0 | Jun | 2023 | 0.012287 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-06-09 19:51 | 2023-06-09 21:45 | 30 | 1:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23060900224 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2023-06-09 | 3420 | keep | 0 | Jun | 2023 | 0.0023293 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-06-09 19:52 | 2023-06-10 00:36 | 129 | 4:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | C23060900242 | New_Event | Cutout Failure | Include | Include | Equipment | 284 | 2023-06-09 | 36636 | keep | 0 | Jun | 2023 | 0.024953 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
ARECIBO | 2023-06-09 20:01 | 2023-06-09 20:50 | 40 | 0:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A23060900232 | New_Event | Vegetation Contact | Include | Include | Vegetation | 49 | 2023-06-09 | 1960 | keep | 0 | Jun | 2023 | 0.0013349 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-06-09 20:02 | 2023-06-09 21:58 | 60 | 1:56 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C23060900244 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2023-06-09 | 6960 | keep | 0 | Jun | 2023 | 0.0047404 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-06-09 20:04 | 2023-06-10 11:51 | 4 | 15:47 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE PRIMARIO EVENTO TRANSFERIDO DE PONCE | P23060900498 | New_Event | Vegetation Contact | Include | Include | Vegetation | 947 | 2023-06-09 | 3788 | keep | 0 | Jun | 2023 | 0.00258 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2023-06-09 20:13 | 2023-06-09 21:38 | 17 | 1:25 | P | CAUSAS EXTERNAS | 1 X 30 EN TRANSFORMADOR CAMION IMPACTA POSTE Y MOVIMIENTO DE LINEAS ABRE TRANSFORMADOR | P23060900506 | New_Event | Damage From Public | Include | Include | Public | 85 | 2023-06-09 | 1445 | keep | 0 | Jun | 2023 | 0.00098418 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BARRANQUITAS | 2023-06-09 20:16 | 2023-06-10 08:31 | 6 | 12:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN XMR TOMA AVERIADA | C23060900247 | New_Event | Secondary Wire Break | Include | Include | Equipment | 735 | 2023-06-09 | 4410 | keep | 0 | Jun | 2023 | 0.0030036 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2023-06-09 20:21 | 2023-06-09 21:56 | 48 | 1:35 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIAS | R23060900071 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 95 | 2023-06-09 | 4560 | keep | 0 | Jun | 2023 | 0.0031058 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
CANOVANAS | 2023-06-09 20:27 | 2023-06-10 10:17 | 12 | 13:50 | P | DESGANCHE | 2 X 50 EN C/L SE RETIRO RAMA EVENTO TRANSFERIDO DE PONCE | P23060900514 | New_Event | Vegetation Contact | Include | Include | Vegetation | 830 | 2023-06-09 | 9960 | keep | 0 | Jun | 2023 | 0.0067837 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-06-09 20:33 | 2023-06-10 01:16 | 2000 | 4:43 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | MEDIANTE GOI SJ-230609-50 SE SECCIONALIZO SU-11A | R23060900075 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 283 | 2023-06-09 | 566000 | keep | 0 | Jun | 2023 | 0.3855 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
SAN JUAN | 2023-06-09 20:37 | 2023-06-11 10:25 | 20 | 37:48 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA CORTE DE LINEA | S23060900678 | New_Event | Primary Wire Break | Include | Include | Equipment | 2268 | 2023-06-09 | 45360 | keep | 0 | Jun | 2023 | 0.030894 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-06-09 20:39 | 2023-06-09 22:54 | 60 | 2:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23060900265 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2023-06-09 | 8100 | keep | 0 | Jun | 2023 | 0.0055169 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-06-09 20:41 | 2023-06-10 02:54 | 261 | 6:13 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 Y 2 X 100 EN C/C SE LEVANTO CONDUCTOR PRIMARIO | B23060900278 | New_Event | Primary Wire Break | Include | Include | Equipment | 373 | 2023-06-09 | 97353 | keep | 0 | Jun | 2023 | 0.066307 | 0.00017777 | Sustained | FALSE | FALSE | Not_TMED_Event | 261
HUMACAO | 2023-06-09 20:56 | 2023-06-09 23:00 | 160 | 2:04 | P | ANIMAL | 1 X 50 Y 1 X 40 EN C/L CRUCE POR AVE | C23060900255 | New_Event | Animals | Include | Include | Wildlife | 124 | 2023-06-09 | 19840 | keep | 0 | Jun | 2023 | 0.013513 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
AGUADILLA | 2023-06-09 21:06 | 2023-06-10 03:48 | 69 | 6:42 | T | CONDUCTOR ROTO O ABIERTO | SE REPARARARON LINEAS PRIMARIAS PARTIDAS Y SE CERRO PUENTE PRIMARIO ABIERTO | M23060900314 | New_Event | Primary Wire Break | Include | Include | Equipment | 402 | 2023-06-09 | 27738 | keep | 0 | Jun | 2023 | 0.018892 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
BAYAMON | 2023-06-09 21:19 | 2023-06-10 00:15 | 200 | 2:56 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23060900284 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2023-06-09 | 35200 | keep | 0 | Jun | 2023 | 0.023975 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2023-06-09 21:19 | 2023-06-09 22:46 | 150 | 1:27 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | P23060900538 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2023-06-09 | 13050 | keep | 0 | Jun | 2023 | 0.0088883 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2023-06-09 21:21 | 2023-06-10 00:50 | 50 | 3:29 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23060900320 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2023-06-09 | 10450 | keep | 0 | Jun | 2023 | 0.0071174 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-06-09 21:24 | 2023-06-09 22:35 | 36 | 1:11 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C23060900257 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 71 | 2023-06-09 | 2556 | keep | 0 | Jun | 2023 | 0.0017409 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
ARECIBO | 2023-06-09 21:27 | 2023-06-09 21:28 | 1218 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23060900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-09 | 1218 | keep | 0 | Jun | 2023 | 0.00082957 | 0.00082957 | Momentary | FALSE | FALSE | Not_TMED_Event | 1218
CAGUAS | 2023-06-09 21:28 | 2023-06-09 21:29 | 476 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23060900261 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-09 | 476 | keep | 0 | Jun | 2023 | 0.0003242 | 0.0003242 | Momentary | FALSE | FALSE | Not_TMED_Event | 476
CAGUAS | 2023-06-09 21:28 | 2023-06-09 21:29 | 1655 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23060900261 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-09 | 1655 | keep | 0 | Jun | 2023 | 0.0011272 | 0.0011272 | Momentary | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2023-06-09 21:28 | 2023-06-09 21:29 | 361 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23060900261 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-09 | 361 | keep | 0 | Jun | 2023 | 0.00024588 | 0.00024588 | Momentary | FALSE | FALSE | Not_TMED_Event | 361
CAGUAS | 2023-06-09 21:28 | 2023-06-09 21:29 | 2842 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23060900261 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-09 | 2842 | keep | 0 | Jun | 2023 | 0.0019357 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
MAYAGÃœEZ | 2023-06-09 21:35 | 2023-06-10 12:40 | 150 | 15:05 | P | SOBRECARGA | 1 X 100 EN CORTE DE LINEA SOBRECARGA | M23060900327 | New_Event | Trip Due To Overload | Include | Include | Other | 905 | 2023-06-09 | 135750 | keep | 0 | Jun | 2023 | 0.092459 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2023-06-09 21:38 | 2023-06-09 21:39 | 1361 | 0:01 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 20% DE SU CARGA X 3103-02 | C23060900260 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-09 | 1361 | keep | 0 | Jun | 2023 | 0.00092697 | 0.00092697 | Momentary | FALSE | FALSE | Not_TMED_Event | 1361
CAGUAS | 2023-06-09 21:38 | 2023-06-09 21:39 | 918 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23060900260 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-09 | 918 | keep | 0 | Jun | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2023-06-09 21:38 | 2023-06-09 21:39 | 1725 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C2306090000X | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-09 | 1725 | keep | 0 | Jun | 2023 | 0.0011749 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
ARECIBO | 2023-06-09 21:51 | 2023-06-10 13:03 | 30 | 15:12 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | A23060900282 | New_Event | Vegetation Contact | Include | Include | Vegetation | 912 | 2023-06-09 | 27360 | keep | 0 | Jun | 2023 | 0.018635 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-06-09 22:02 | 2023-06-10 02:14 | 50 | 4:12 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23060900267 | New_Event | Animals | Include | Include | Wildlife | 252 | 2023-06-09 | 12600 | keep | 0 | Jun | 2023 | 0.0085818 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-06-09 22:10 | 2023-06-10 08:52 | 7 | 10:42 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | M23060900340 | New_Event | Animals | Include | Include | Wildlife | 642 | 2023-06-09 | 4494 | keep | 0 | Jun | 2023 | 0.0030608 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-06-09 22:43 | 2023-06-10 10:14 | 40 | 11:31 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | P23060900573 | New_Event | Vegetation Contact | Include | Include | Vegetation | 691 | 2023-06-09 | 27640 | keep | 0 | Jun | 2023 | 0.018825 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-06-09 23:09 | 2023-06-10 01:28 | 75 | 2:19 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23060900291 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2023-06-09 | 10425 | keep | 0 | Jun | 2023 | 0.0071004 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2023-06-10 00:02 | 2023-06-10 09:54 | 220 | 9:52 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO SE TARDO POR QUE ENCONTARON CAMPER Y CARRETON OBSTRUYENDO AREA DE TRABAJO | A23061000001 | New_Event | Primary Wire Break | Include | Include | Equipment | 592 | 2023-06-10 | 130240 | keep | 0 | Jun | 2023 | 0.088706 | 0.00014984 | Sustained | FALSE | FALSE | Not_TMED_Event | 220
SAN JUAN | 2023-06-10 00:32 | 2023-06-10 04:58 | 1681 | 4:26 | T | ARBOL SOBRE LINEA | DISPARO ALIMENTADOR ARBOL CAYO SOBRE FASE TUMBO 4 POSTES Y SE SECCIONALIZO 5% EN SERVICIO | S23061000005 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 266 | 2023-06-10 | 447146 | keep | 0 | Jun | 2023 | 0.30455 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2023-06-10 00:32 | 2023-06-10 06:00 | 2435 | 5:28 | T | ARBOL SOBRE LINEA | DISPARO ALIMENTADOR ARBOL CAYO SOBRE FASE TUMBO 4 POSTES 15% EN SERVICIO POR 1204-02 | S23061000005 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 328 | 2023-06-10 | 798680 | keep | 0 | Jun | 2023 | 0.54398 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2023-06-10 00:32 | 2023-06-10 07:35 | 60 | 7:03 | P | ALIMENTADOR AMARRADO | DISPARO 1303-2 ARBOL SOBRE LINEA TUMBO 4 POSTES Y DEVOLVIO CARGA 45% DE 1401-8 | S23061000112 | New_Event | Feeder Load Transferred | Include | Include | Other | 423 | 2023-06-10 | 25380 | keep | 0 | Jun | 2023 | 0.017286 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-06-10 01:35 | 2023-06-10 12:10 | 30 | 10:35 | P | CONDUCTOR ROTO O ABIERTO | ALAMBRE PARTIDO | M23061000002 | New_Event | Primary Wire Break | Include | Include | Equipment | 635 | 2023-06-10 | 19050 | keep | 0 | Jun | 2023 | 0.012975 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-06-10 02:12 | 2023-06-10 08:51 | 9 | 6:39 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A23061000004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 399 | 2023-06-10 | 3591 | keep | 0 | Jun | 2023 | 0.0024458 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2023-06-10 02:14 | 2023-06-10 02:15 | 476 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23061000013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-10 | 476 | keep | 0 | Jun | 2023 | 0.0003242 | 0.0003242 | Momentary | FALSE | FALSE | Not_TMED_Event | 476
CAGUAS | 2023-06-10 02:14 | 2023-06-10 02:15 | 1655 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23061000013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-10 | 1655 | keep | 0 | Jun | 2023 | 0.0011272 | 0.0011272 | Momentary | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2023-06-10 02:14 | 2023-06-10 02:15 | 361 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23061000013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-10 | 361 | keep | 0 | Jun | 2023 | 0.00024588 | 0.00024588 | Momentary | FALSE | FALSE | Not_TMED_Event | 361
CAGUAS | 2023-06-10 02:14 | 2023-06-10 02:15 | 2842 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23061000013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-10 | 2842 | keep | 0 | Jun | 2023 | 0.0019357 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
CAGUAS | 2023-06-10 02:14 | 2023-06-10 02:15 | 1361 | 0:01 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 20% DE SU CARGA X 3103-02 | C23061000012 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-10 | 1361 | keep | 0 | Jun | 2023 | 0.00092697 | 0.00092697 | Momentary | FALSE | FALSE | Not_TMED_Event | 1361
CAGUAS | 2023-06-10 02:14 | 2023-06-10 02:15 | 918 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23061000012 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-10 | 918 | keep | 0 | Jun | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2023-06-10 02:14 | 2023-06-10 02:15 | 1725 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23061000014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-10 | 1725 | keep | 0 | Jun | 2023 | 0.0011749 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
CAGUAS | 2023-06-10 02:15 | 2023-06-10 14:14 | 50 | 11:59 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23060900267 | New_Event | Animals | Include | Include | Wildlife | 719 | 2023-06-10 | 35950 | keep | 0 | Jun | 2023 | 0.024485 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-06-10 02:46 | 2023-06-10 17:03 | 10 | 14:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1X20 EN XMR SE REMPLAZO BAJANTE SECUNDARIO EN XMR | B23061000001 | New_Event | Secondary Wire Break | Include | Include | Equipment | 857 | 2023-06-10 | 8570 | keep | 0 | Jun | 2023 | 0.005837 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-06-10 03:03 | 2023-06-10 03:04 | 3464 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R2306100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-10 | 3464 | keep | 0 | Jun | 2023 | 0.0023593 | 0.0023593 | Momentary | FALSE | FALSE | Not_TMED_Event | 3464
SAN JUAN | 2023-06-10 03:07 | 2023-06-10 03:12 | 225 | 0:05 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVA 1303-05 | S23061000114 | New_Event | Feeder Load Transferred | Include | Include | Other | 5 | 2023-06-10 | 1125 | keep | 0 | Jun | 2023 | 0.00076623 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2023-06-10 03:07 | 2023-06-10 03:12 | 870 | 0:05 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR 1303-04 SE CERRO POR CONTROL LLEVA 1303-05 | S23061000114 | New_Event | Primary Wire Break | Include | Include | Equipment | 5 | 2023-06-10 | 4350 | keep | 0 | Jun | 2023 | 0.0029628 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CANOVANAS | 2023-06-10 03:09 | 2023-06-10 16:47 | 20 | 13:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN C/L Y 1 X 20 EN XMR SE REMPLAZO PORTAFUSIBLE | R23061000014 | New_Event | Cutout Failure | Include | Include | Equipment | 818 | 2023-06-10 | 16360 | keep | 0 | Jun | 2023 | 0.011143 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-06-10 03:18 | 2023-06-10 07:23 | 10 | 4:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA DESGANCHE | B23060900003 | New_Event | Secondary Wire Break | Include | Include | Equipment | 245 | 2023-06-10 | 2450 | keep | 0 | Jun | 2023 | 0.0016687 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2023-06-10 03:33 | 2023-06-10 03:34 | 1945 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23061000015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-10 | 1945 | keep | 0 | Jun | 2023 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
BAYAMON | 2023-06-10 03:38 | 2023-06-10 12:47 | 122 | 9:09 | P | DESGANCHE | SE ABRIO C/L TOTAL PARA DESGANCHE Y SE REEMPLAZO LA CAJA PRIMARIA AVERIADA. | B23061000004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 549 | 2023-06-10 | 66978 | keep | 0 | Jun | 2023 | 0.045618 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
SAN JUAN | 2023-06-10 03:40 | 2023-06-10 04:29 | 225 | 0:49 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1303-04 SE SECCIONALIZO CONDUCTOR EN EL SUELO DEL 1303-05 Y SE CERRO POR CONTROL. | S23061000118 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 49 | 2023-06-10 | 11025 | keep | 0 | Jun | 2023 | 0.0075091 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-10 03:40 | 2023-06-10 04:29 | 870 | 0:49 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR 1303-04 SE SECCIONALIZO CONDUCTOR EN EL SUELO DEL 1303-05 Y SE CERRO POR CONTROL. ENTRO 60% EN SERVICIO | S23061000118 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 49 | 2023-06-10 | 42630 | keep | 0 | Jun | 2023 | 0.029035 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-06-10 03:48 | 2023-06-10 19:15 | 1 | 15:27 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO ALAMBRE PARTIDO Y SE CERRO PUENTES | M23060900314 | New_Event | Primary Wire Break | Include | Include | Equipment | 927 | 2023-06-10 | 927 | keep | 0 | Jun | 2023 | 0.00063138 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-06-10 04:23 | 2023-06-10 05:59 | 349 | 1:36 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO LINEA 500 OPERACION LENTA DEL BKR 0210 OCASIONA DISPARO DE BARRA #2 38KV PONCE TC. LINEA 0500 OPERA RADIAL. | P23061000057 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 96 | 2023-06-10 | 33504 | keep | 0 | Jun | 2023 | 0.022819 | 0.0002377 | Sustained | FALSE | FALSE | Not_TMED_Event | 349
PONCE | 2023-06-10 04:23 | 2023-06-10 05:59 | 653 | 1:36 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO LINEA 500 OPERACION LENTA DEL BKR 0210 OCASIONA DISPARO DE BARRA #2 38KV PONCE TC. LINEA 0500 OPERA RADIAL. | P23061000057 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 96 | 2023-06-10 | 62688 | keep | 0 | Jun | 2023 | 0.042697 | 0.00044476 | Sustained | FALSE | FALSE | Not_TMED_Event | 653
PONCE | 2023-06-10 04:23 | 2023-06-10 05:59 | 860 | 1:36 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO LINEA 500 OPERACION LENTA DEL BKR 0210 OCASIONA DISPARO DE BARRA #2 38KV PONCE TC. LINEA 0500 OPERA RADIAL. | P23061000057 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 96 | 2023-06-10 | 82560 | keep | 0 | Jun | 2023 | 0.056231 | 0.00058574 | Sustained | FALSE | FALSE | Not_TMED_Event | 860
PONCE | 2023-06-10 04:28 | 2023-06-10 09:00 | 234 | 4:32 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 NO SE ENCONTRÃ“ CAUSA DE AVERÃA EN LINEA 0200. OPERACIÃ“N LENTA DEL BKR 0210 OCASIONA DISPARO DE BARRA #2 38KV PONCE TC. | P23061000059 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 272 | 2023-06-10 | 63648 | keep | 0 | Jun | 2023 | 0.04335 | 0.00015938 | Sustained | FALSE | FALSE | Not_TMED_Event | 234
PONCE | 2023-06-10 04:28 | 2023-06-10 09:00 | 2468 | 4:32 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 NO SE ENCONTRÃ“ CAUSA DE AVERÃA EN LINEA 0200. OPERACIÃ“N LENTA DEL BKR 0210 OCASIONA DISPARO DE BARRA #2 38KV PONCE TC. | P23061000059 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 272 | 2023-06-10 | 671296 | keep | 0 | Jun | 2023 | 0.45722 | 0.0016809 | Sustained | FALSE | FALSE | Not_TMED_Event | 2468
SAN JUAN | 2023-06-10 04:29 | 2023-06-10 04:57 | 323 | 0:28 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO PUENTES PARA SECCIONALIZAR CONDUCTOR EN EL SUELO Y SE CERRO MACHETES 98% EN SERVICIO | S23061000118 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 28 | 2023-06-10 | 9044 | keep | 0 | Jun | 2023 | 0.0061598 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-06-10 04:50 | 2023-06-10 14:18 | 473 | 9:28 | P | CONDUCTOR ROTO O ABIERTO | ABRIO MACHETES PARA LEVANTAR CONDUCTOR | C23061000007 | New_Event | Primary Wire Break | Include | Include | Equipment | 568 | 2023-06-10 | 268664 | keep | 0 | Jun | 2023 | 0.18299 | 0.00032216 | Sustained | FALSE | FALSE | Not_TMED_Event | 473
SAN JUAN | 2023-06-10 04:57 | 2023-06-10 08:34 | 17 | 3:37 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA PRIMARIA | S23061000279 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 217 | 2023-06-10 | 3689 | keep | 0 | Jun | 2023 | 0.0025126 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-10 04:58 | 2023-06-10 08:29 | 1597 | 3:31 | P | ARBOL SOBRE LINEA | SE SECCIONALIZO ARBOL QUE CAYO SOBRE FASE TUMBO 4 POSTES SE PASO CARGA AL 1346-02 CERRADO FID-31759834. 90% EN SERVICIO | S23061000005 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 211 | 2023-06-10 | 336967 | keep | 0 | Jun | 2023 | 0.22951 | 0.0010877 | Sustained | FALSE | FALSE | Not_TMED_Event | 1597
FAJARDO | 2023-06-10 04:59 | 2023-06-10 10:07 | 40 | 5:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L Y SE REEMPLAZO AISLADOR EVENTO TRANSFERIDO DE PONCE | P23061000049 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 308 | 2023-06-10 | 12320 | keep | 0 | Jun | 2023 | 0.0083911 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2023-06-10 05:38 | 2023-06-10 05:40 | 75 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR ESTA POR EL 5 SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P23061000064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-10 | 150 | keep | 0 | Jun | 2023 | 0.00010216 | 5.1082e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-06-10 05:39 | 2023-06-10 14:14 | 90 | 8:35 | P | DESGANCHE | 1X100 EN C/L DESGANCHE | S23061000129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 515 | 2023-06-10 | 46350 | keep | 0 | Jun | 2023 | 0.031569 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CAGUAS | 2023-06-10 05:48 | 2023-06-10 17:26 | 21 | 11:38 | P | DESGANCHE | 1 X 50 EN C/L | C23061000011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 698 | 2023-06-10 | 14658 | keep | 0 | Jun | 2023 | 0.0099835 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BARRANQUITAS | 2023-06-10 05:56 | 2023-06-10 09:57 | 98 | 4:01 | P | DESGANCHE | 2 X 50 EN C/L | C23061000015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2023-06-10 | 23618 | keep | 0 | Jun | 2023 | 0.016086 | 6.6747e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 98
SAN JUAN | 2023-06-10 06:00 | 2023-06-10 07:35 | 2070 | 1:35 | P | ARBOL SOBRE LINEA | SE SECICONALIZO ARBOL CAYO SOBRE FASE TUMBO 4 POSTES. SE TRANSFIRIO CARGA AL 1401-08. 55% EN SERVICIO. | S23061000005 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 95 | 2023-06-10 | 196650 | keep | 0 | Jun | 2023 | 0.13394 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-06-10 06:08 | 2023-06-10 06:10 | 1879 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CERRADO X CONTROL | C23061000016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-10 | 3758 | keep | 0 | Jun | 2023 | 0.0025596 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
HUMACAO | 2023-06-10 06:11 | 2023-06-10 06:12 | 3 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23061000017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-10 | 3 | keep | 0 | Jun | 2023 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-06-10 06:38 | 2023-06-11 08:19 | 45 | 25:41 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | B23061000009 | New_Event | Animals | Include | Include | Wildlife | 1541 | 2023-06-10 | 69345 | keep | 0 | Jun | 2023 | 0.047231 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2023-06-10 06:48 | 2023-06-10 09:30 | 30 | 2:42 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE LINEA A CAJA EVENTO TRANSFERIDO DE PONCE | P23061000073 | New_Event | Primary Wire Break | Include | Include | Equipment | 162 | 2023-06-10 | 4860 | keep | 0 | Jun | 2023 | 0.0033101 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-06-10 06:54 | 2023-06-10 12:28 | 48 | 5:34 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO DE CAJA A LINEA EN C/L | R23061000019 | New_Event | Primary Wire Break | Include | Include | Equipment | 334 | 2023-06-10 | 16032 | keep | 0 | Jun | 2023 | 0.010919 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
AGUADILLA | 2023-06-10 06:58 | 2023-06-10 10:00 | 100 | 3:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | M23061000011 | New_Event | Cutout Failure | Include | Include | Equipment | 182 | 2023-06-10 | 18200 | keep | 0 | Jun | 2023 | 0.012396 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-06-10 07:00 | 2023-06-10 07:01 | 1937 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | R23061000020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-10 | 1937 | keep | 0 | Jun | 2023 | 0.0013193 | 0.0013193 | Momentary | FALSE | FALSE | Not_TMED_Event | 1937
SAN JUAN | 2023-06-10 07:03 | 2023-06-10 13:00 | 105 | 5:57 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE DE LINEA A CAJA | S23061000163 | New_Event | Primary Wire Break | Include | Include | Equipment | 357 | 2023-06-10 | 37485 | keep | 0 | Jun | 2023 | 0.025531 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
BAYAMON | 2023-06-10 07:08 | 2023-06-10 12:11 | 8 | 5:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA AVERIADA. | S23061000166 | New_Event | Secondary Wire Break | Include | Include | Equipment | 303 | 2023-06-10 | 2424 | keep | 0 | Jun | 2023 | 0.001651 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2023-06-10 07:12 | 2023-06-10 07:13 | 1571 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23061000020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-10 | 1571 | keep | 0 | Jun | 2023 | 0.00107 | 0.00107 | Momentary | FALSE | FALSE | Not_TMED_Event | 1571
BAYAMON | 2023-06-10 07:20 | 2023-06-10 08:18 | 58 | 0:58 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE. | B23061000010 | New_Event | Animals | Include | Include | Wildlife | 58 | 2023-06-10 | 3364 | keep | 0 | Jun | 2023 | 0.0022912 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
YAUCO | 2023-06-10 07:26 | 2023-06-10 16:05 | 25 | 8:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA FUERTES VIENTOS | M23061000113 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 519 | 2023-06-10 | 12975 | keep | 0 | Jun | 2023 | 0.0088372 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-06-10 07:31 | 2023-06-10 09:41 | 250 | 2:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN CL FUERTES VIENTOS | M23061000015 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 130 | 2023-06-10 | 32500 | keep | 0 | Jun | 2023 | 0.022136 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2023-06-10 07:35 | 2023-06-10 07:39 | 1096 | 0:04 | P | ARBOL SOBRE LINEA | SE SECICONALIZO ARBOL CAYO SOBRE FASE TUMBO 4 POSTES. SE TRANSFIRIO CARGA AL 1204-02. 95% EN SERVICIO | S23061000005 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 4 | 2023-06-10 | 4384 | keep | 0 | Jun | 2023 | 0.0029859 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-10 07:39 | 2023-06-10 09:07 | 122 | 1:28 | P | ARBOL SOBRE LINEA | SE SECCIONALIZO ARBOL CAYO SOBRE FASE TUMBO 4 POSTES 98% EN SERVICIO POR 1204-02 | S23061000005 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 88 | 2023-06-10 | 10736 | keep | 0 | Jun | 2023 | 0.0073122 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
ARECIBO | 2023-06-10 07:48 | 2023-06-10 16:35 | 40 | 8:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A23061000014 | New_Event | Cutout Failure | Include | Include | Equipment | 527 | 2023-06-10 | 21080 | keep | 0 | Jun | 2023 | 0.014357 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-06-10 07:49 | 2023-06-10 10:53 | 60 | 3:04 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L EVENTO TRANSFERIDO DE PONCE | P23061000086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 184 | 2023-06-10 | 11040 | keep | 0 | Jun | 2023 | 0.0075193 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-06-10 07:53 | 2023-06-10 07:55 | 817 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECIERRA CERRADO X CONTROL | C23061000026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-10 | 1634 | keep | 0 | Jun | 2023 | 0.0011129 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
VEGA BAJA | 2023-06-10 08:06 | 2023-06-10 18:29 | 100 | 10:23 | P | DESGANCHE | 1X140 EN C/L DESGANCHE | B23061000023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 623 | 2023-06-10 | 62300 | keep | 0 | Jun | 2023 | 0.042432 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2023-06-10 08:07 | 2023-06-10 10:17 | 20 | 2:10 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | P23061000093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2023-06-10 | 2600 | keep | 0 | Jun | 2023 | 0.0017708 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2023-06-10 08:11 | 2023-06-10 11:10 | 50 | 2:59 | P | ANIMAL | 1 X 65 EN C/L AVE CRUZO LINEAS | P23061000096 | New_Event | Animals | Include | Include | Wildlife | 179 | 2023-06-10 | 8950 | keep | 0 | Jun | 2023 | 0.0060958 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-06-10 08:16 | 2023-06-10 10:56 | 4 | 2:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 200 EN CORTE DE LINEA FUERTES VIENTOS | P23061000097 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 160 | 2023-06-10 | 640 | keep | 0 | Jun | 2023 | 0.0004359 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-06-10 08:18 | 2023-06-10 11:01 | 40 | 2:43 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | B23061000003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2023-06-10 | 6520 | keep | 0 | Jun | 2023 | 0.0044407 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-06-10 08:26 | 2023-06-10 10:07 | 16 | 1:41 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | C23061000034 | New_Event | Animals | Include | Include | Wildlife | 101 | 2023-06-10 | 1616 | keep | 0 | Jun | 2023 | 0.0011007 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2023-06-10 08:26 | 2023-06-10 11:30 | 3 | 3:04 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE LINEA NO SE ENCONTRO CAUSA | P23061000099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 184 | 2023-06-10 | 552 | keep | 0 | Jun | 2023 | 0.00037596 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-06-10 08:29 | 2023-06-10 09:10 | 168 | 0:41 | P | ARBOL SOBRE LINEA | SE SECCIONALIZO TRAMO SE PASO CARGA AL 1346-02 CERRADO FID-33533413. 98% EN SERVICIO | S23061000005 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 41 | 2023-06-10 | 6888 | keep | 0 | Jun | 2023 | 0.0046914 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-10 08:34 | 2023-06-10 08:38 | 84 | 0:04 | P | LINEA DE TRANSMISION 115KV | CCE EN V.L. ABRIO 36210 SE LE NOTIFICO AL ING. TURNO ALICEA QUE 1303-00 ESTABA FUERA INDICARON QUE CERRARIAN LA LINEA, SE ENCONTRO MOD-36265 INDICABA EN SCADA CERRADO PERO ESTABA ABIERTO EN EL CAMPO (CÃMARAS ABIERTAS) LLEVA 5% DE SU CARGA | S23061000269 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-06-10 | 336 | keep | 0 | Jun | 2023 | 0.00022885 | 5.7212e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 84
SAN JUAN | 2023-06-10 08:34 | 2023-06-10 08:38 | 726 | 0:04 | S | ERROR HUMANO | CCE EN V.L. ABRIO 36210 SE LE NOTIFICO AL ING. TURNO ALICEA QUE 1303-00 ESTABA FUERA INDICARON QUE CERRARIAN LA LINEA, SE ENCONTRO MOD-36265 INDICABA EN SCADA CERRADO PERO ESTABA ABIERTO EN EL CAMPO | S23061000269 | New_Event | Human Error | Include | Include | Other | 4 | 2023-06-10 | 2904 | keep | 0 | Jun | 2023 | 0.0019779 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2023-06-10 08:34 | 2023-06-10 08:38 | 225 | 0:04 | S | LINEA DE TRANSMISION 115KV | CCE EN V.L. ABRIO 36210 SE LE NOTIFICO AL ING. TURNO ALICEA QUE 1303-00 ESTABA FUERA INDICARON QUE CERRARIAN LA LINEA, SE ENCONTRO MOD-36265 INDICABA EN SCADA CERRADO PERO ESTABA ABIERTO EN EL CAMPO (CÃMARAS ABIERTAS) | S23061000269 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-06-10 | 900 | keep | 0 | Jun | 2023 | 0.00061299 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2023-06-10 08:34 | 2023-06-10 08:38 | 870 | 0:04 | S | LINEA DE TRANSMISION 115KV | CCE EN V.L. ABRIO 36210 SE LE NOTIFICO AL ING. TURNO ALICEA QUE 1303-00 ESTABA FUERA INDICARON QUE CERRARIAN LA LINEA, SE ENCONTRÃ“ MOD-36265 INDICABA EN SCADA CERRADO PERO ESTABA ABIERTO EN EL CAMPO (CÃMARAS ABIERTAS) | S23061000269 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-06-10 | 3480 | keep | 0 | Jun | 2023 | 0.0023702 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2023-06-10 08:38 | 2023-06-11 13:35 | 17 | 28:57 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA PRIMARIA | S23061000279 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1737 | 2023-06-10 | 29529 | keep | 0 | Jun | 2023 | 0.020112 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-06-10 08:41 | 2023-06-10 12:49 | 96 | 4:08 | P | DESGANCHE | 1 X 50 EN C/L Y SE REALIZO DESGANCHE | R23061000021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 248 | 2023-06-10 | 23808 | keep | 0 | Jun | 2023 | 0.016216 | 6.5385e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 96
AGUADILLA | 2023-06-10 08:42 | 2023-06-10 08:43 | 3041 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M23061000037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-10 | 3041 | keep | 0 | Jun | 2023 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
CAGUAS | 2023-06-10 08:45 | 2023-06-10 08:46 | 4634 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23061000035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-10 | 4634 | keep | 0 | Jun | 2023 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
BARRANQUITAS | 2023-06-10 08:55 | 2023-06-10 08:58 | 870 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CERRADO X CONTROL | C23061000037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-06-10 | 2610 | keep | 0 | Jun | 2023 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CAGUAS | 2023-06-10 09:04 | 2023-06-10 16:18 | 171 | 7:14 | P | DESGANCHE | 2 X 65 EN C/L | C23061000040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 434 | 2023-06-10 | 74214 | keep | 0 | Jun | 2023 | 0.050547 | 0.00011647 | Sustained | FALSE | FALSE | Not_TMED_Event | 171
SAN JUAN | 2023-06-10 09:07 | 2023-06-10 20:20 | 49 | 11:13 | P | ARBOL SOBRE LINEA | SE RETIRO ARBOL Y SE REMPLAZO 4 POSTES Y SE CERO INTERRUPTOR 100% EN SERVICIO. | S23061000112 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 673 | 2023-06-10 | 32977 | keep | 0 | Jun | 2023 | 0.02246 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-10 09:08 | 2023-06-10 13:15 | 158 | 4:07 | P | TRANSFORMADOR AVERIADO | SE ABRIO C/L TOTAL PARA REEMPLAZAR XMR TRASPATIO. | B23061000028 | New_Event | Service Transformer Failure | Include | Include | Equipment | 247 | 2023-06-10 | 39026 | keep | 0 | Jun | 2023 | 0.02658 | 0.00010761 | Sustained | FALSE | FALSE | Not_TMED_Event | 158
SAN JUAN | 2023-06-10 09:10 | 2023-06-10 19:28 | 49 | 10:18 | P | ARBOL SOBRE LINEA | SE RETIRO ARBOL Y SE REMPLAZO 4 POSTE Y SE CERRO MACHETE 100% EN SERVICIO | S23061000005 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 618 | 2023-06-10 | 30282 | keep | 0 | Jun | 2023 | 0.020625 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-06-10 09:11 | 2023-06-10 15:20 | 45 | 6:09 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | A23061000030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 369 | 2023-06-10 | 16605 | keep | 0 | Jun | 2023 | 0.01131 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2023-06-10 09:17 | 2023-06-10 14:20 | 100 | 5:03 | P | ANIMAL | 1 X 30 1 X 65 1X 80 EN DISTINTOS CORTES DE LINEA AVCE CRUZO FASE A TIERRA | A23061000035 | New_Event | Animals | Include | Include | Wildlife | 303 | 2023-06-10 | 30300 | keep | 0 | Jun | 2023 | 0.020637 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-06-10 09:36 | 2023-06-10 15:26 | 10 | 5:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | A23061000042 | New_Event | Cutout Failure | Include | Include | Equipment | 350 | 2023-06-10 | 3500 | keep | 0 | Jun | 2023 | 0.0023838 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-06-10 10:00 | 2023-06-10 21:05 | 70 | 11:05 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23061000147 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 665 | 2023-06-10 | 46550 | keep | 0 | Jun | 2023 | 0.031705 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2023-06-10 10:12 | 2023-06-10 10:13 | 3630 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO SE REALIZA PRUEBA Y QUEDA EN SERVCIO | M23061000070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-10 | 3630 | keep | 0 | Jun | 2023 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
BAYAMON | 2023-06-10 10:15 | 2023-06-10 12:37 | 278 | 2:22 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | B23061000042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2023-06-10 | 39476 | keep | 0 | Jun | 2023 | 0.026887 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
MAYAGÃœEZ | 2023-06-10 10:18 | 2023-06-10 13:00 | 400 | 2:42 | P | SOBRECARGA | 1 X 80 Y 1 X 50 EN CORTE LINEA SOBRECARGA | M23061000072 | New_Event | Trip Due To Overload | Include | Include | Other | 162 | 2023-06-10 | 64800 | keep | 0 | Jun | 2023 | 0.044135 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
CANOVANAS | 2023-06-10 10:22 | 2023-06-10 14:38 | 15 | 4:16 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R23061000037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 256 | 2023-06-10 | 3840 | keep | 0 | Jun | 2023 | 0.0026154 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-06-10 10:38 | 2023-06-10 14:22 | 65 | 3:44 | P | DESGANCHE | 1X30 EN C/L DESGANCHE (EVENTO TRANSFERIDO DE REGION-PONCE) | P23061000156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2023-06-10 | 14560 | keep | 0 | Jun | 2023 | 0.0099167 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
FAJARDO | 2023-06-10 10:49 | 2023-06-10 14:31 | 66 | 3:42 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA | R23061000038 | New_Event | Primary Wire Break | Include | Include | Equipment | 222 | 2023-06-10 | 14652 | keep | 0 | Jun | 2023 | 0.0099794 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
MAYAGÃœEZ | 2023-06-10 10:52 | 2023-06-10 14:55 | 80 | 4:03 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M23061000099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2023-06-10 | 19440 | keep | 0 | Jun | 2023 | 0.01324 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-06-10 11:19 | 2023-06-10 23:11 | 60 | 11:52 | P | ANIMAL | 1X65 EN C/L CRUCE POR AVE | B23061000053 | New_Event | Animals | Include | Include | Wildlife | 712 | 2023-06-10 | 42720 | keep | 0 | Jun | 2023 | 0.029096 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-06-10 11:20 | 2023-06-10 14:02 | 1498 | 2:42 | T | ALIMENTADOR AMARRADO | SE LEVANTO LINEA PRIMARIA EN TRAMO 1421-02 Y SE CERRO MACHETE SU CARGA POR 1421-02 | S23060900592 | New_Event | Feeder Load Transferred | Include | Include | Other | 162 | 2023-06-10 | 242676 | keep | 0 | Jun | 2023 | 0.16529 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
SAN JUAN | 2023-06-10 11:20 | 2023-06-10 14:02 | 164 | 2:42 | T | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA PRIMARIA EN TRAMO 1421-02 Y SE CERRO MACHETE 100% EN SERVICIO | S23060900592 | New_Event | Primary Wire Break | Include | Include | Equipment | 162 | 2023-06-10 | 26568 | keep | 0 | Jun | 2023 | 0.018095 | 0.0001117 | Sustained | FALSE | FALSE | Not_TMED_Event | 164
SAN JUAN | 2023-06-10 11:20 | 2023-06-10 14:02 | 358 | 2:42 | P | ALIMENTADOR AMARRADO | SE LEVANTO LINEA PRIMARIA Y SE CERRO MACHETE 50% POR 1421-02 | S23060900592 | New_Event | Feeder Load Transferred | Include | Include | Other | 162 | 2023-06-10 | 57996 | keep | 0 | Jun | 2023 | 0.039501 | 0.00024383 | Sustained | FALSE | FALSE | Not_TMED_Event | 358
PONCE | 2023-06-10 11:33 | 2023-06-10 11:34 | 1078 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE NO CAUSA | P23061000173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-10 | 1078 | keep | 0 | Jun | 2023 | 0.00073422 | 0.00073422 | Momentary | FALSE | FALSE | Not_TMED_Event | 1078
FAJARDO | 2023-06-10 11:34 | 2023-06-10 12:07 | 13 | 0:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REEMPLAZO CAJA PRIMARIA | R23061000039 | New_Event | Cutout Failure | Include | Include | Equipment | 33 | 2023-06-10 | 429 | keep | 0 | Jun | 2023 | 0.00029219 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2023-06-10 11:48 | 2023-06-10 13:08 | 75 | 1:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE LINEA VIENTOS FUERTES | M23061000092 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 80 | 2023-06-10 | 6000 | keep | 0 | Jun | 2023 | 0.0040866 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2023-06-10 11:51 | 2023-06-10 15:32 | 60 | 3:41 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A23061000067 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 221 | 2023-06-10 | 13260 | keep | 0 | Jun | 2023 | 0.0090313 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-06-10 11:53 | 2023-06-10 11:56 | 870 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CERRADO X CONTROL | C23061000063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-06-10 | 2610 | keep | 0 | Jun | 2023 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
HUMACAO | 2023-06-10 11:57 | 2023-06-10 13:31 | 25 | 1:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L FUERTES VIENTOS | C23061000065 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 94 | 2023-06-10 | 2350 | keep | 0 | Jun | 2023 | 0.0016006 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2023-06-10 12:10 | 2023-06-10 15:05 | 77 | 2:55 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA REPARAR ALAMBRE PARTIDO | M23061000002 | New_Event | Primary Wire Break | Include | Include | Equipment | 175 | 2023-06-10 | 13475 | keep | 0 | Jun | 2023 | 0.0091778 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
AGUADILLA | 2023-06-10 12:12 | 2023-06-10 15:40 | 7 | 3:28 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE ZAFADO DE CAJA A TRANSFORMADOR | P23061000192 | New_Event | Primary Wire Break | Include | Include | Equipment | 208 | 2023-06-10 | 1456 | keep | 0 | Jun | 2023 | 0.00099167 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-06-10 12:16 | 2023-06-10 12:18 | 2531 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1619-03 CON 50% DE SU CARGA TRANSFERIDA. SE CERRO POR SCADA | R23061000040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-10 | 5062 | keep | 0 | Jun | 2023 | 0.0034477 | 0.0017239 | Momentary | FALSE | FALSE | Not_TMED_Event | 2531
SAN JUAN | 2023-06-10 12:20 | 2023-06-10 12:29 | 1487 | 0:09 | P | DESGANCHE | DISPARO ALIMENTADOR LLEVA 40% DE SU CARGA SE PROBO QUEDO EN SERVICIO | S23061000299 | New_Event | Vegetation Contact | Include | Include | Vegetation | 9 | 2023-06-10 | 13383 | keep | 0 | Jun | 2023 | 0.0091151 | 0.0010128 | Sustained | FALSE | FALSE | Not_TMED_Event | 1487
SAN JUAN | 2023-06-10 12:26 | 2023-06-10 13:41 | 84 | 1:15 | P | DESCONECTIVO DEFECTUOSO | SE ABRE INTERRUPTOR PARA REMPLAZAR MACHETE EN ENTRADA CONVERTIDOR SALIENDO DE SUBEST. LLEVA 5% DE SU CARGA | S23061000301 | New_Event | Switch Failure | Include | Include | Equipment | 75 | 2023-06-10 | 6300 | keep | 0 | Jun | 2023 | 0.0042909 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
MAYAGÃœEZ | 2023-06-10 12:27 | 2023-06-10 12:28 | 1097 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO | M23061000101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-10 | 1097 | keep | 0 | Jun | 2023 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
SAN JUAN | 2023-06-10 12:29 | 2023-06-10 21:06 | 158 | 8:37 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23061000312 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 517 | 2023-06-10 | 81686 | keep | 0 | Jun | 2023 | 0.055636 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-06-10 12:30 | 2023-06-10 12:31 | 1510 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23061000070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-10 | 1510 | keep | 0 | Jun | 2023 | 0.0010285 | 0.0010285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1510
CAGUAS | 2023-06-10 12:31 | 2023-06-10 18:07 | 115 | 5:36 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L | C23061000069 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 336 | 2023-06-10 | 38640 | keep | 0 | Jun | 2023 | 0.026318 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
MAYAGÃœEZ | 2023-06-10 12:31 | 2023-06-10 12:55 | 4664 | 0:24 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR RR EN OFF POR TRABAJOS EN ALIMENTADOR SE CONFIRMO PERSONAL FUERA DE LINEA PRIMARIA Y SE REALIZO PRUEBA A INTERRUPTOR | M23061000102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 24 | 2023-06-10 | 111936 | keep | 0 | Jun | 2023 | 0.076239 | 0.0031766 | Sustained | FALSE | FALSE | Not_TMED_Event | 4664
ARECIBO | 2023-06-10 12:33 | 2023-06-10 17:35 | 80 | 5:02 | P | ANIMAL | 1 X 25 Y 1 X 50 EN DISTINTOS CORTE DE LINEA AVE CRUZO FASE A TIERRA | A23061000075 | New_Event | Animals | Include | Include | Wildlife | 302 | 2023-06-10 | 24160 | keep | 0 | Jun | 2023 | 0.016455 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2023-06-10 12:56 | 2023-06-10 14:58 | 5 | 2:02 | P | DESGANCHE | 1 X 20 EN C/L DESGANCHE EVENTO TRANSFERIDO | P23061000215 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2023-06-10 | 610 | keep | 0 | Jun | 2023 | 0.00041547 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2023-06-10 13:03 | 2023-06-10 15:26 | 214 | 2:23 | P | DESGANCHE | 1 X 100 EN C/L | C23061000089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2023-06-10 | 30602 | keep | 0 | Jun | 2023 | 0.020843 | 0.00014575 | Sustained | FALSE | FALSE | Not_TMED_Event | 214
SAN JUAN | 2023-06-10 13:05 | 2023-06-10 16:25 | 12 | 3:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR BAJANTE Y CONECTORES SECUNDARIOS TRANSFERICO DE PONCE | P23061000243 | New_Event | Secondary Wire Break | Include | Include | Equipment | 200 | 2023-06-10 | 2400 | keep | 0 | Jun | 2023 | 0.0016346 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-06-10 13:05 | 2023-06-10 13:10 | 1984 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23061000320 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-06-10 | 9920 | keep | 0 | Jun | 2023 | 0.0067565 | 0.0013513 | Momentary | FALSE | FALSE | Not_TMED_Event | 1984
CAGUAS | 2023-06-10 13:18 | 2023-06-10 16:33 | 66 | 3:15 | P | DESGANCHE | 1 X 50 EN C/L | C23061000100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2023-06-10 | 12870 | keep | 0 | Jun | 2023 | 0.0087657 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
PONCE | 2023-06-10 13:26 | 2023-06-10 17:30 | 100 | 4:04 | P | CONDUCTOR ROTO O ABIERTO | 3 X 65 EN C/L SE REPARO ALAMBRES PRIMARIOS | P23061000254 | New_Event | Primary Wire Break | Include | Include | Equipment | 244 | 2023-06-10 | 24400 | keep | 0 | Jun | 2023 | 0.016619 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2023-06-10 13:26 | 2023-06-10 14:00 | 40 | 0:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 Y 1 X 20 EN C/LS MAL TIEMPO LLUVIAS | P23061000232 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 34 | 2023-06-10 | 1360 | keep | 0 | Jun | 2023 | 0.00092629 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-06-10 13:27 | 2023-06-10 15:53 | 53 | 2:26 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R23061000045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2023-06-10 | 7738 | keep | 0 | Jun | 2023 | 0.0052703 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
BAYAMON | 2023-06-10 13:29 | 2023-06-10 19:37 | 31 | 6:08 | P | DESGANCHE | 1X40 EN C/L DESGANCHE | B23061000066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 368 | 2023-06-10 | 11408 | keep | 0 | Jun | 2023 | 0.0077699 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
SAN JUAN | 2023-06-10 13:39 | 2023-06-10 16:04 | 10 | 2:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA Y 2 X 15 EN TRANSFORMADOR | S23061000344 | New_Event | Cutout Failure | Include | Include | Equipment | 145 | 2023-06-10 | 1450 | keep | 0 | Jun | 2023 | 0.00098759 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-06-10 13:41 | 2023-06-10 16:00 | 614 | 2:19 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA DESGANCHE | S23061000331 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2023-06-10 | 85346 | keep | 0 | Jun | 2023 | 0.058129 | 0.00041819 | Sustained | FALSE | FALSE | Not_TMED_Event | 614
MAYAGÃœEZ | 2023-06-10 13:49 | 2023-06-10 15:10 | 60 | 1:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA FUERTES VIENTOS | M23061000120 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 81 | 2023-06-10 | 4860 | keep | 0 | Jun | 2023 | 0.0033101 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-06-10 13:56 | 2023-06-11 08:13 | 10 | 18:17 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN TRANSFORMADOR SE REALIZO DESGANCHE | M23061000121 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1097 | 2023-06-10 | 10970 | keep | 0 | Jun | 2023 | 0.0074716 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2023-06-10 14:12 | 2023-06-10 17:45 | 50 | 3:33 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23061000089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2023-06-10 | 10650 | keep | 0 | Jun | 2023 | 0.0072537 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-06-10 14:18 | 2023-06-10 14:19 | 2468 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 9101-04 LLEVA LA CARGA DEL 9101-03 | B23061000071 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-10 | 2468 | keep | 0 | Jun | 2023 | 0.0016809 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
VEGA BAJA | 2023-06-10 14:18 | 2023-06-10 14:19 | 1494 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9101-04 LLEVA LA CARGA DEL 9101-03 | B23061000071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-10 | 1494 | keep | 0 | Jun | 2023 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
VEGA BAJA | 2023-06-10 14:24 | 2023-06-10 16:23 | 14 | 1:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REMPLAZAR BAJANTES SECUNDARIOS | B23060900143 | New_Event | Secondary Wire Break | Include | Include | Equipment | 119 | 2023-06-10 | 1666 | keep | 0 | Jun | 2023 | 0.0011347 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2023-06-10 14:30 | 2023-06-11 12:49 | 1 | 22:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR BARRA EN PEDESTAL SECUNDARIA AVERIADA | P23061000261 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1339 | 2023-06-10 | 1339 | keep | 0 | Jun | 2023 | 0.00091199 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-06-10 14:37 | 2023-06-10 14:38 | 338 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S23061000342 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-10 | 338 | keep | 0 | Jun | 2023 | 0.00023021 | 0.00023021 | Momentary | FALSE | FALSE | Not_TMED_Event | 338
BAYAMON | 2023-06-10 14:45 | 2023-06-10 15:37 | 10 | 0:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REPARAR BAJANTE SECUNDARIO | B23061000074 | New_Event | Secondary Wire Break | Include | Include | Equipment | 52 | 2023-06-10 | 520 | keep | 0 | Jun | 2023 | 0.00035417 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-06-10 14:52 | 2023-06-11 10:00 | 6 | 19:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE LINEA SE REMPLAZO CAJA PRIMARIA EN CORTE LINEA | A23061000095 | New_Event | Cutout Failure | Include | Include | Equipment | 1148 | 2023-06-10 | 6888 | keep | 0 | Jun | 2023 | 0.0046914 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2023-06-10 15:06 | 2023-06-10 16:15 | 6 | 1:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR SECUNDARIA AVERIADA | C23060900180 | New_Event | Secondary Wire Break | Include | Include | Equipment | 69 | 2023-06-10 | 414 | keep | 0 | Jun | 2023 | 0.00028197 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-06-10 15:20 | 2023-06-10 16:22 | 19 | 1:02 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR PARA REMPLAZO XMR 50KVA X 50KVA | S23061000354 | New_Event | Service Transformer Failure | Include | Include | Equipment | 62 | 2023-06-10 | 1178 | keep | 0 | Jun | 2023 | 0.00080233 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
MAYAGÃœEZ | 2023-06-10 15:20 | 2023-06-11 15:00 | 35 | 23:40 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M23061000134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1420 | 2023-06-10 | 49700 | keep | 0 | Jun | 2023 | 0.03385 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2023-06-10 15:32 | 2023-06-11 11:24 | 120 | 19:52 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE LINEA SE CERRO PUENTE PRIMARIO | M23061000136 | New_Event | Primary Wire Break | Include | Include | Equipment | 1192 | 2023-06-10 | 143040 | keep | 0 | Jun | 2023 | 0.097424 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BARRANQUITAS | 2023-06-10 15:35 | 2023-06-10 17:43 | 595 | 2:08 | P | DESGANCHE | 3 X 100 EN C/L | C23061000135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2023-06-10 | 76160 | keep | 0 | Jun | 2023 | 0.051872 | 0.00040525 | Sustained | FALSE | FALSE | Not_TMED_Event | 595
BAYAMON | 2023-06-10 15:40 | 2023-06-11 09:19 | 10 | 17:39 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | P23061000286 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1059 | 2023-06-10 | 10590 | keep | 0 | Jun | 2023 | 0.0072128 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-06-10 15:47 | 2023-06-10 19:41 | 10 | 3:54 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L 1 X 15 EN XMR SE REMPLAZO AISLADOR EVENTO TRANSFERIDO | P23061000288 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 234 | 2023-06-10 | 2340 | keep | 0 | Jun | 2023 | 0.0015938 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-06-10 16:00 | 2023-06-10 18:53 | 24 | 2:53 | P | PROBLEMA DEL CLIENTE | 1 X 65 EN RISER AVERIA TRANSCLOUSURE A PISO 3 SE ORIENTO CLIENTE | S23061000293 | New_Event | Customer-Related Interruption | Include | Include | Public | 173 | 2023-06-10 | 4152 | keep | 0 | Jun | 2023 | 0.0028279 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
HUMACAO | 2023-06-10 16:13 | 2023-06-10 17:35 | 17 | 1:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | REMPLAZO BAJANTES SECUNDARIO | C23061000145 | New_Event | Secondary Wire Break | Include | Include | Equipment | 82 | 2023-06-10 | 1394 | keep | 0 | Jun | 2023 | 0.00094945 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2023-06-10 16:25 | 2023-06-10 21:09 | 15 | 4:44 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO EN C/L PARA REPARAR BAJANTE PRIMARIO DE CAJA @ XMR | B23061000087 | New_Event | Primary Wire Break | Include | Include | Equipment | 284 | 2023-06-10 | 4260 | keep | 0 | Jun | 2023 | 0.0029015 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-06-10 16:29 | 2023-06-10 16:30 | 1022 | 0:01 | T | ARBOL SOBRE LINEA | SE ABRIO INTERRUPTOR PARA ABRIR MACHETES Y SECCIONALIZAR ARBOL CAIDO SOBRE LINEA PRIMARIA Y PRENDIDO EN FUEGO Y SE CERRO EL INTERRUPTOR | A23061000112 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1 | 2023-06-10 | 1022 | keep | 0 | Jun | 2023 | 0.00069608 | 0.00069608 | Momentary | FALSE | FALSE | Not_TMED_Event | 1022
ARECIBO | 2023-06-10 16:30 | 2023-06-10 18:10 | 30 | 1:40 | P | ARBOL SOBRE LINEA | SE RETIRO ARBOL CAIDO SOBRE LAS LINEAS PRIMARIAS Y SE CERRO LOS MACHETES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR LA AVERIA | A23061000115 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 100 | 2023-06-10 | 3000 | keep | 0 | Jun | 2023 | 0.0020433 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-06-10 16:32 | 2023-06-10 16:54 | 25 | 0:22 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R23061000061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 22 | 2023-06-10 | 550 | keep | 0 | Jun | 2023 | 0.0003746 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-06-10 16:41 | 2023-06-10 16:44 | 17 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23061000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-06-10 | 51 | keep | 0 | Jun | 2023 | 3.4736e-05 | 1.1579e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 17
CANOVANAS | 2023-06-10 16:46 | 2023-06-10 16:48 | 2179 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | R23061000062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-10 | 4358 | keep | 0 | Jun | 2023 | 0.0029682 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
MAYAGÃœEZ | 2023-06-10 17:02 | 2023-06-10 20:05 | 1 | 3:03 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | P23061000313 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2023-06-10 | 183 | keep | 0 | Jun | 2023 | 0.00012464 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-06-10 17:03 | 2023-06-11 07:07 | 11 | 14:04 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | B23061000093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 844 | 2023-06-10 | 9284 | keep | 0 | Jun | 2023 | 0.0063233 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CANOVANAS | 2023-06-10 17:20 | 2023-06-10 20:33 | 42 | 3:13 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R23061000066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2023-06-10 | 8106 | keep | 0 | Jun | 2023 | 0.005521 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
BAYAMON | 2023-06-10 17:21 | 2023-06-10 17:22 | 2402 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23061000095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-10 | 2402 | keep | 0 | Jun | 2023 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
UTUADO | 2023-06-10 17:22 | 2023-06-11 09:20 | 50 | 15:58 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEAS SE RETIRO BAMBU DE LAS LINEAS | A23061000121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 958 | 2023-06-10 | 47900 | keep | 0 | Jun | 2023 | 0.032624 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-06-10 17:35 | 2023-06-11 09:48 | 1 | 16:13 | P | ANIMAL | 1 X 15 EN MONTURA CRUCE POR AVE | S23061000380 | New_Event | Animals | Include | Include | Wildlife | 973 | 2023-06-10 | 973 | keep | 0 | Jun | 2023 | 0.00066271 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-06-10 17:36 | 2023-06-10 20:29 | 404 | 2:53 | P | ANIMAL | 1X100 EN C/L CRUCE POR AVE | B23061000099 | New_Event | Animals | Include | Include | Wildlife | 173 | 2023-06-10 | 69892 | keep | 0 | Jun | 2023 | 0.047603 | 0.00027516 | Sustained | FALSE | FALSE | Not_TMED_Event | 404
AGUADILLA | 2023-06-10 17:51 | 2023-06-10 17:52 | 1047 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23061000154 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-10 | 1047 | keep | 0 | Jun | 2023 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
ARECIBO | 2023-06-10 17:54 | 2023-06-10 21:45 | 30 | 3:51 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE REPARO LINEA PRIMARIA ROTA | A23061000126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 231 | 2023-06-10 | 6930 | keep | 0 | Jun | 2023 | 0.00472 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-06-10 18:40 | 2023-06-10 19:30 | 14 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | S23061000396 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2023-06-10 | 700 | keep | 0 | Jun | 2023 | 0.00047677 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
VEGA BAJA | 2023-06-10 18:45 | 2023-06-10 19:08 | 7 | 0:23 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO TRANSFORMADOR Y SE REPARO NEUTRAL ZAFADO DE TRANSFORMADOR | P23061000348 | New_Event | Primary Wire Break | Include | Include | Equipment | 23 | 2023-06-10 | 161 | keep | 0 | Jun | 2023 | 0.00010966 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-06-10 18:55 | 2023-06-11 12:30 | 20 | 17:35 | P | DESGANCHE | 1 X 40 EN C/L | C23061000167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1055 | 2023-06-10 | 21100 | keep | 0 | Jun | 2023 | 0.014371 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-06-10 19:21 | 2023-06-11 14:40 | 6 | 19:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23061000110 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1159 | 2023-06-10 | 6954 | keep | 0 | Jun | 2023 | 0.0047363 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-06-10 19:21 | 2023-06-11 01:53 | 203 | 6:32 | P | ANIMAL | 1X65 EN C/L CRUCE POR AVE | B23061000111 | New_Event | Animals | Include | Include | Wildlife | 392 | 2023-06-10 | 79576 | keep | 0 | Jun | 2023 | 0.054199 | 0.00013826 | Sustained | FALSE | FALSE | Not_TMED_Event | 203
FAJARDO | 2023-06-10 19:22 | 2023-06-11 09:21 | 6 | 13:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN XMR Y SE REPARO BAJANTE SECUNDARIO | R23061000084 | New_Event | Secondary Wire Break | Include | Include | Equipment | 839 | 2023-06-10 | 5034 | keep | 0 | Jun | 2023 | 0.0034286 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-06-10 19:30 | 2023-06-10 23:57 | 35 | 4:27 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO EN C/L PARA CERRAR PUENTE DE LINEA @ CAJA | B23061000114 | New_Event | Primary Wire Break | Include | Include | Equipment | 267 | 2023-06-10 | 9345 | keep | 0 | Jun | 2023 | 0.0063648 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2023-06-10 19:34 | 2023-06-10 19:35 | 107 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23061000164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-10 | 107 | keep | 0 | Jun | 2023 | 7.2877e-05 | 7.2877e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 107
BAYAMON | 2023-06-10 19:37 | 2023-06-11 09:09 | 9 | 13:32 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23061000115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 812 | 2023-06-10 | 7308 | keep | 0 | Jun | 2023 | 0.0049774 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2023-06-10 19:54 | 2023-06-11 11:00 | 75 | 15:06 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE LINEA SE FIJO LINEA PRIMARIA CRUZADA A AISLADOR | A23061000137 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 906 | 2023-06-10 | 67950 | keep | 0 | Jun | 2023 | 0.04628 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2023-06-10 20:03 | 2023-06-10 20:04 | 918 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23061000174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-10 | 918 | keep | 0 | Jun | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2023-06-10 20:10 | 2023-06-10 22:15 | 243 | 2:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN RISER MAL TIEMPO LLUVIA | C23061000177 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 125 | 2023-06-10 | 30375 | keep | 0 | Jun | 2023 | 0.020688 | 0.00016551 | Sustained | FALSE | FALSE | Not_TMED_Event | 243
HUMACAO | 2023-06-10 20:37 | 2023-06-10 20:38 | 2299 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23061000183 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-10 | 2299 | keep | 0 | Jun | 2023 | 0.0015658 | 0.0015658 | Momentary | FALSE | FALSE | Not_TMED_Event | 2299
HUMACAO | 2023-06-10 20:43 | 2023-06-10 20:44 | 2299 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23061000183 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-10 | 2299 | keep | 0 | Jun | 2023 | 0.0015658 | 0.0015658 | Momentary | FALSE | FALSE | Not_TMED_Event | 2299
HUMACAO | 2023-06-10 20:47 | 2023-06-10 20:48 | 2299 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23061000184 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-10 | 2299 | keep | 0 | Jun | 2023 | 0.0015658 | 0.0015658 | Momentary | FALSE | FALSE | Not_TMED_Event | 2299
HUMACAO | 2023-06-10 20:54 | 2023-06-10 20:55 | 2299 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23061000187 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-10 | 2299 | keep | 0 | Jun | 2023 | 0.0015658 | 0.0015658 | Momentary | FALSE | FALSE | Not_TMED_Event | 2299
PONCE | 2023-06-10 21:00 | 2023-06-11 12:00 | 100 | 15:00 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO | P23061000427 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 900 | 2023-06-10 | 90000 | keep | 0 | Jun | 2023 | 0.061299 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-10 21:05 | 2023-06-10 21:14 | 1512 | 0:09 | P | ARBOL SOBRE LINEA | SE ABRE INTERRUPTOR 1346-02 PARA NORMALIZAR CARGA DEL 1303-01 SE ABRIO N/O Y SE CERRO MACHETE 100% POR SU CARGA | S23061000000 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 9 | 2023-06-10 | 13608 | keep | 0 | Jun | 2023 | 0.0092683 | 0.0010298 | Sustained | FALSE | FALSE | Not_TMED_Event | 1512
SAN JUAN | 2023-06-10 21:05 | 2023-06-10 21:12 | 276 | 0:07 | T | ALIMENTADOR AMARRADO | SE ABRE INTERRUPTOR PARA NORMALIZAR CARGA DEL 1303-01 90% DE SU CARGA LLEVA 15% DE SU CARGA LLEVA 1346-06, LLEVA 40% DEL 1346-03, LLEVA 80% DEL 1346-5 | S23061000000 | New_Event | Feeder Load Transferred | Include | Include | Other | 7 | 2023-06-10 | 1932 | keep | 0 | Jun | 2023 | 0.0013159 | 0.00018798 | Sustained | FALSE | FALSE | Not_TMED_Event | 276
SAN JUAN | 2023-06-10 21:05 | 2023-06-10 21:12 | 968 | 0:07 | P | ALIMENTADOR AMARRADO | SE ABRE INTERRUPTOR PARA NORMALIZAR CARGA DEL 1303-01 40% POR 1346-02 | S23061000000 | New_Event | Feeder Load Transferred | Include | Include | Other | 7 | 2023-06-10 | 6776 | keep | 0 | Jun | 2023 | 0.0046151 | 0.0006593 | Sustained | FALSE | FALSE | Not_TMED_Event | 968
SAN JUAN | 2023-06-10 21:05 | 2023-06-10 21:12 | 737 | 0:07 | P | ALIMENTADOR AMARRADO | SE ABRE INTERRUPTOR PARA NORMALIZAR CARGA DEL 1303-01 80% POR 1346-02 | S23061000000 | New_Event | Feeder Load Transferred | Include | Include | Other | 7 | 2023-06-10 | 5159 | keep | 0 | Jun | 2023 | 0.0035138 | 0.00050197 | Sustained | FALSE | FALSE | Not_TMED_Event | 737
SAN JUAN | 2023-06-10 21:05 | 2023-06-10 21:12 | 1598 | 0:07 | T | ALIMENTADOR AMARRADO | SE ABRE INTERRUPTOR PARA NORMALIZAR CARGA DEL 1303-01 90% DE SU CARGA LLEVA 15% DE SU CARGA LLEVA 1346-06, LLEVA 40% DEL 1346-03, LLEVA 80% DEL 1346-5 | S23061000000 | New_Event | Feeder Load Transferred | Include | Include | Other | 7 | 2023-06-10 | 11186 | keep | 0 | Jun | 2023 | 0.0076187 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
CAGUAS | 2023-06-10 21:20 | 2023-06-11 14:06 | 4 | 16:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN C/L FUERTES VIENTOS | C23061000196 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1006 | 2023-06-10 | 4024 | keep | 0 | Jun | 2023 | 0.0027407 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-06-10 22:06 | 2023-06-10 22:41 | 251 | 0:35 | P | NO SE REPORTO CAUSA | 1X100 EN C/L (EVENTO TRANSFERIDO) | P23061000431 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 35 | 2023-06-10 | 8785 | keep | 0 | Jun | 2023 | 0.0059834 | 0.00017095 | Sustained | FALSE | FALSE | Not_TMED_Event | 251
VEGA BAJA | 2023-06-10 22:16 | 2023-06-11 02:04 | 40 | 3:48 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | B23061000129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 228 | 2023-06-10 | 9120 | keep | 0 | Jun | 2023 | 0.0062116 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-06-10 22:17 | 2023-06-11 14:30 | 50 | 16:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L REMPLAZO CAJA AVERIADA | C23061000202 | New_Event | Cutout Failure | Include | Include | Equipment | 973 | 2023-06-10 | 48650 | keep | 0 | Jun | 2023 | 0.033135 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2023-06-10 22:17 | 2023-06-11 13:40 | 3 | 15:23 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO | P23061000432 | New_Event | Service Transformer Failure | Include | Include | Equipment | 923 | 2023-06-10 | 2769 | keep | 0 | Jun | 2023 | 0.001886 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2023-06-10 22:37 | 2023-06-11 09:47 | 150 | 11:10 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CL SE REPARO BAJANTE PRIMARIO EN CORTE LINEA | M23061000190 | New_Event | Primary Wire Break | Include | Include | Equipment | 670 | 2023-06-10 | 100500 | keep | 0 | Jun | 2023 | 0.06845 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-06-10 22:43 | 2023-06-11 04:58 | 84 | 6:15 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | B23061000085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 375 | 2023-06-10 | 31500 | keep | 0 | Jun | 2023 | 0.021455 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
CAGUAS | 2023-06-10 22:44 | 2023-06-10 22:45 | 2178 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR SPARE LLEVA EL 3103-05 | C2306100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-10 | 2178 | keep | 0 | Jun | 2023 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
SAN JUAN | 2023-06-11 00:43 | 2023-06-11 00:45 | 513 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1118-10 LLEVA 20% DEL 1111-01 SE CERRO POR CONTROL | S23061100001 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-06-11 | 1026 | keep | 0 | Jun | 2023 | 0.0006988 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2023-06-11 00:43 | 2023-06-11 00:45 | 2782 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1118-10 LLEVA 20% DEL 1111-01 SE CERRO POR CONTROL | S23061100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-11 | 5564 | keep | 0 | Jun | 2023 | 0.0037896 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
SAN JUAN | 2023-06-11 01:20 | 2023-06-11 03:15 | 19 | 1:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REPARAR SECUNDARIA PARTIDA | S23061100004 | New_Event | Secondary Wire Break | Include | Include | Equipment | 115 | 2023-06-11 | 2185 | keep | 0 | Jun | 2023 | 0.0014882 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2023-06-11 01:28 | 2023-06-11 14:19 | 70 | 12:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X50 EN C/L SE REMPLAZO PORTAFUSIBLE | S23061100005 | New_Event | Cutout Failure | Include | Include | Equipment | 771 | 2023-06-11 | 53970 | keep | 0 | Jun | 2023 | 0.036759 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2023-06-11 02:16 | 2023-06-11 07:24 | 50 | 5:08 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23061100002 | New_Event | Animals | Include | Include | Wildlife | 308 | 2023-06-11 | 15400 | keep | 0 | Jun | 2023 | 0.010489 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-06-11 03:39 | 2023-06-11 03:40 | 125 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | C2306110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-11 | 125 | keep | 0 | Jun | 2023 | 8.5137e-05 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2023-06-11 03:40 | 2023-06-11 08:21 | 40 | 4:41 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C23061100008 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 281 | 2023-06-11 | 11240 | keep | 0 | Jun | 2023 | 0.0076555 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-06-11 04:08 | 2023-06-11 04:09 | 3295 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B23061100003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-11 | 3295 | keep | 0 | Jun | 2023 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2023-06-11 05:04 | 2023-06-11 09:45 | 15 | 4:41 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 C/L Y SE CERRO PUENTE DE LINEA A CAJA | B23061100004 | New_Event | Primary Wire Break | Include | Include | Equipment | 281 | 2023-06-11 | 4215 | keep | 0 | Jun | 2023 | 0.0028708 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-06-11 05:06 | 2023-06-11 09:06 | 36 | 4:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REEMPLAZO CAJA PRIMARIA AVERIADA. | S23061100011 | New_Event | Cutout Failure | Include | Include | Equipment | 240 | 2023-06-11 | 8640 | keep | 0 | Jun | 2023 | 0.0058847 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
GUAYAMA | 2023-06-11 05:10 | 2023-06-11 05:11 | 4132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23061100008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-11 | 4132 | keep | 0 | Jun | 2023 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
UTUADO | 2023-06-11 06:03 | 2023-06-11 06:04 | 650 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE REALIZA PRUEBA Y QUEDA EN SERVICIO | A23061100002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-11 | 650 | keep | 0 | Jun | 2023 | 0.00044271 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
AGUADILLA | 2023-06-11 06:08 | 2023-06-11 08:53 | 10 | 2:45 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR POR PALOMA | M23061100005 | New_Event | Animals | Include | Include | Wildlife | 165 | 2023-06-11 | 1650 | keep | 0 | Jun | 2023 | 0.0011238 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-06-11 06:15 | 2023-06-11 14:36 | 90 | 8:21 | P | DESGANCHE | 1X80 EN C/L DESGANCHE | S23061100014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 501 | 2023-06-11 | 45090 | keep | 0 | Jun | 2023 | 0.030711 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
HUMACAO | 2023-06-11 06:25 | 2023-06-11 06:26 | 551 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23061100011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-11 | 551 | keep | 0 | Jun | 2023 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
VEGA BAJA | 2023-06-11 07:01 | 2023-06-11 14:14 | 55 | 7:13 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 SE REMPLAZO AISLADOR PARTIDO | B23061100011 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 433 | 2023-06-11 | 23815 | keep | 0 | Jun | 2023 | 0.01622 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
AGUADILLA | 2023-06-11 07:10 | 2023-06-11 10:45 | 1 | 3:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES AVERIADO | A23061100004 | New_Event | Cutout Failure | Include | Include | Equipment | 215 | 2023-06-11 | 215 | keep | 0 | Jun | 2023 | 0.00014644 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-06-11 07:53 | 2023-06-11 13:56 | 30 | 6:03 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | C23061100016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 363 | 2023-06-11 | 10890 | keep | 0 | Jun | 2023 | 0.0074171 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2023-06-11 08:11 | 2023-06-11 09:05 | 55 | 0:54 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R23061100007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2023-06-11 | 2970 | keep | 0 | Jun | 2023 | 0.0020229 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CANOVANAS | 2023-06-11 08:33 | 2023-06-11 11:34 | 2 | 3:01 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHE EVENTO TRANSFERIDO DE PONCE | P23061100031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2023-06-11 | 362 | keep | 0 | Jun | 2023 | 0.00024656 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-06-11 08:43 | 2023-06-11 08:44 | 73 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO 5% 1404-07 SE PROBO QUEDO EN SERVICIO | S23061100000 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-11 | 73 | keep | 0 | Jun | 2023 | 4.972e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
SAN JUAN | 2023-06-11 08:43 | 2023-06-11 08:44 | 1357 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 5% DEL 1112-04 SE PROBO QUEDO EN SERVICIO | S23061100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-11 | 1357 | keep | 0 | Jun | 2023 | 0.00092425 | 0.00092425 | Momentary | FALSE | FALSE | Not_TMED_Event | 1357
CANOVANAS | 2023-06-11 08:46 | 2023-06-11 13:46 | 40 | 5:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y AISLADOR 1 X 50 EN C/L EVENTO TRANSFERIDO | P23061100034 | New_Event | Cutout Failure | Include | Include | Equipment | 300 | 2023-06-11 | 12000 | keep | 0 | Jun | 2023 | 0.0081731 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-06-11 08:57 | 2023-06-12 10:30 | 1 | 25:33 | P | CONDUCTOR ROTO O ABIERTO | SE REPARA BAJANTE DE LINEA A CAJA DE TRANSFORMADOR | M23061100022 | New_Event | Primary Wire Break | Include | Include | Equipment | 1533 | 2023-06-11 | 1533 | keep | 0 | Jun | 2023 | 0.0010441 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-06-11 09:03 | 2023-06-11 15:50 | 25 | 6:47 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA DE CORTE DE LINEA | P23061100036 | New_Event | Primary Wire Break | Include | Include | Equipment | 407 | 2023-06-11 | 10175 | keep | 0 | Jun | 2023 | 0.0069301 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-06-11 09:07 | 2023-06-11 15:21 | 120 | 6:14 | P | DESGANCHE | 2X100 EN C/L PRINCIPAL Y 2X30 DE RISER @ BANCO DE XMRS BOMBAS A.A.A. DESGANCHE | S23061100032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 374 | 2023-06-11 | 44880 | keep | 0 | Jun | 2023 | 0.030568 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
FAJARDO | 2023-06-11 09:27 | 2023-06-11 09:48 | 6 | 0:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN XMR Y SE REPARO BAJANTE SECUNDARIO | R23061000084 | Partial_restoration | Secondary Wire Break | Include | Include | Equipment | 21 | 2023-06-11 | 126 | keep | 0 | Jun | 2023 | 8.5818e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-06-11 09:29 | 2023-06-11 09:46 | 10 | 0:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | R23061000060 | New_Event | Secondary Wire Break | Include | Include | Equipment | 17 | 2023-06-11 | 170 | keep | 0 | Jun | 2023 | 0.00011579 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-06-11 10:00 | 2023-06-11 18:00 | 38 | 8:00 | P | DESGANCHE | 2 X 100 EN C/L SE REPARO ALAMBRES PRIMARIOS POR DESGANCHE | P23061100060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 480 | 2023-06-11 | 18240 | keep | 0 | Jun | 2023 | 0.012423 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
VEGA BAJA | 2023-06-11 10:03 | 2023-06-11 12:47 | 1 | 2:44 | P | ANIMAL | 2 X 15 EN TRANSFORMADOR AVE CRUZO FASES A TIERRA | P23061100063 | New_Event | Animals | Include | Include | Wildlife | 164 | 2023-06-11 | 164 | keep | 0 | Jun | 2023 | 0.0001117 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-06-11 10:12 | 2023-06-11 10:41 | 19 | 0:29 | P | PARARRAYOS DEFECTUOSO | 1 X 40 Y 1 X 65 EN C/L SE ELIMINO PARARRAYO | R23061100029 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 29 | 2023-06-11 | 551 | keep | 0 | Jun | 2023 | 0.00037528 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
AGUADILLA | 2023-06-11 10:16 | 2023-06-11 12:00 | 60 | 1:44 | P | DESGANCHE | 1 X 80 EN CORTE LINEA DESGANCHE | M23061100041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2023-06-11 | 6240 | keep | 0 | Jun | 2023 | 0.00425 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2023-06-11 10:21 | 2023-06-11 16:00 | 150 | 5:39 | P | CAUSAS EXTERNAS | 1 X 65 EN CORTE DE LINEA PERSONA DESGANCHANDO DEJO CAER ARBOL SOBRE LINEAS Y CAUSO CRUCE DE LINEAS | A23061100013 | New_Event | Damage From Public | Include | Include | Public | 339 | 2023-06-11 | 50850 | keep | 0 | Jun | 2023 | 0.034634 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2023-06-11 10:22 | 2023-06-11 11:52 | 20 | 1:30 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | M23061100042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2023-06-11 | 1800 | keep | 0 | Jun | 2023 | 0.001226 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-06-11 10:33 | 2023-06-11 11:33 | 1 | 1:00 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | C23061100073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 60 | 2023-06-11 | 60 | keep | 0 | Jun | 2023 | 4.0866e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-06-11 10:35 | 2023-06-11 12:20 | 7 | 1:45 | P | ANIMAL | 2 X 100 EN C/L AVE CRUZO LINEAS EVENTO TRANSFERIDO | P23061100075 | New_Event | Animals | Include | Include | Wildlife | 105 | 2023-06-11 | 735 | keep | 0 | Jun | 2023 | 0.00050061 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2023-06-11 10:49 | 2023-06-11 12:45 | 1 | 1:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | M23061100044 | New_Event | Secondary Wire Break | Include | Include | Equipment | 116 | 2023-06-11 | 116 | keep | 0 | Jun | 2023 | 7.9007e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-06-11 10:55 | 2023-06-11 12:00 | 452 | 1:05 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO EN TRONCAL Y SE CERRO MACHETE | S23061100050 | New_Event | Primary Wire Break | Include | Include | Equipment | 65 | 2023-06-11 | 29380 | keep | 0 | Jun | 2023 | 0.020011 | 0.00030786 | Sustained | FALSE | FALSE | Not_TMED_Event | 452
BAYAMON | 2023-06-11 10:59 | 2023-06-11 12:09 | 25 | 1:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L SE REEMPLAZO CAJA PRMARIA. | S23061100051 | New_Event | Cutout Failure | Include | Include | Equipment | 70 | 2023-06-11 | 1750 | keep | 0 | Jun | 2023 | 0.0011919 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-06-11 11:01 | 2023-06-11 14:13 | 18 | 3:12 | P | NO SE REPORTO CAUSA | 1 X 40 EN AEREO PROVISIONAL | R23061100033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 192 | 2023-06-11 | 3456 | keep | 0 | Jun | 2023 | 0.0023539 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
YAUCO | 2023-06-11 11:07 | 2023-06-11 12:50 | 200 | 1:43 | P | DESGANCHE | 2 X 200 EN C/L DESGANCHE | P23061100099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2023-06-11 | 20600 | keep | 0 | Jun | 2023 | 0.014031 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-06-11 11:10 | 2023-06-11 11:12 | 4431 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO POR SCADA | B2306110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-11 | 8862 | keep | 0 | Jun | 2023 | 0.0060359 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
BAYAMON | 2023-06-11 11:23 | 2023-06-11 16:17 | 10 | 4:54 | P | ANIMAL | 1 X 15 EN C/L SE REMPLAZO CAJA PRIMARIA CRUCE DE IGUANA | B23061100031 | New_Event | Animals | Include | Include | Wildlife | 294 | 2023-06-11 | 2940 | keep | 0 | Jun | 2023 | 0.0020024 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-06-11 11:27 | 2023-06-11 15:53 | 266 | 4:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN C/L SE REMPLAZO CAJA QUEMADA EN C/L | P23061100108 | New_Event | Cutout Failure | Include | Include | Equipment | 266 | 2023-06-11 | 70756 | keep | 0 | Jun | 2023 | 0.048192 | 0.00018117 | Sustained | FALSE | FALSE | Not_TMED_Event | 266
BARRANQUITAS | 2023-06-11 11:43 | 2023-06-11 11:58 | 5 | 0:15 | P | NO SE REPORTO CAUSA | 1 X 8 EN XMR | C23061100063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2023-06-11 | 75 | keep | 0 | Jun | 2023 | 5.1082e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-06-11 12:05 | 2023-06-11 16:46 | 8 | 4:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1X20 EN XMR Y SE REPARO SECUNDARIA | S23061100070 | New_Event | Secondary Wire Break | Include | Include | Equipment | 281 | 2023-06-11 | 2248 | keep | 0 | Jun | 2023 | 0.0015311 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2023-06-11 12:11 | 2023-06-11 13:09 | 110 | 0:58 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R23061100042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2023-06-11 | 6380 | keep | 0 | Jun | 2023 | 0.0043454 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
SAN JUAN | 2023-06-11 12:14 | 2023-06-11 16:37 | 200 | 4:23 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO/LEVANTO CONDUCTOR PRIMARIO DEL SUELO MEDIANTE G.O.I. SJ-230611-02 | S23061000338 | New_Event | Primary Wire Break | Include | Include | Equipment | 263 | 2023-06-11 | 52600 | keep | 0 | Jun | 2023 | 0.035826 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2023-06-11 12:16 | 2023-06-11 16:40 | 30 | 4:24 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | P23061100136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 264 | 2023-06-11 | 7920 | keep | 0 | Jun | 2023 | 0.0053943 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-06-11 12:33 | 2023-06-11 16:01 | 146 | 3:28 | P | DESGANCHE | 2 X 65 EN C/L | C23061100072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2023-06-11 | 30368 | keep | 0 | Jun | 2023 | 0.020684 | 9.944e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 146
BAYAMON | 2023-06-11 12:37 | 2023-06-11 17:26 | 55 | 4:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA PRIMARIA | S23061100087 | New_Event | Cutout Failure | Include | Include | Equipment | 289 | 2023-06-11 | 15895 | keep | 0 | Jun | 2023 | 0.010826 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
GUAYAMA | 2023-06-11 12:46 | 2023-06-11 15:00 | 50 | 2:14 | P | ANIMAL | 1 X 40 EN C/L AVE CRUZO LINEAS | P23061100144 | New_Event | Animals | Include | Include | Wildlife | 134 | 2023-06-11 | 6700 | keep | 0 | Jun | 2023 | 0.0045633 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-06-11 13:01 | 2023-06-11 13:28 | 5 | 0:27 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFOMADOR DESGANCHE | M23061100053 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 27 | 2023-06-11 | 135 | keep | 0 | Jun | 2023 | 9.1948e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-06-11 13:12 | 2023-06-11 15:00 | 109 | 1:48 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R23061100051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2023-06-11 | 11772 | keep | 0 | Jun | 2023 | 0.0080179 | 7.4239e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 109
SAN JUAN | 2023-06-11 13:27 | 2023-06-11 15:11 | 60 | 1:44 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO EN C/L PARA REPARAR PUENTE PRIMARIO - TRASPATIO (ABRIERON C/L TOTAL A LAS 13:27 DEL 06/11/23) | S23060900508 | New_Event | Primary Wire Break | Include | Include | Equipment | 104 | 2023-06-11 | 6240 | keep | 0 | Jun | 2023 | 0.00425 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-06-11 13:35 | 2023-06-11 14:57 | 5 | 1:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | REMPLAZO BAJANTE SECUNDARIO Y INSTALO VARILLA DE GROUND | C23061100078 | New_Event | Secondary Wire Break | Include | Include | Equipment | 82 | 2023-06-11 | 410 | keep | 0 | Jun | 2023 | 0.00027925 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2023-06-11 13:53 | 2023-06-11 15:01 | 57 | 1:08 | P | ANIMAL | 1 X 30 EN CORTE DE LNEA Y 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | R23061100055 | New_Event | Animals | Include | Include | Wildlife | 68 | 2023-06-11 | 3876 | keep | 0 | Jun | 2023 | 0.0026399 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
AGUADILLA | 2023-06-11 14:06 | 2023-06-11 14:14 | 1 | 0:08 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A23061100025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2023-06-11 | 8 | keep | 0 | Jun | 2023 | 5.4488e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-06-11 14:08 | 2023-06-11 14:59 | 18 | 0:51 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REMPLAZAR BAJANTE SECUNDARIO | S23061100103 | New_Event | Secondary Wire Break | Include | Include | Equipment | 51 | 2023-06-11 | 918 | keep | 0 | Jun | 2023 | 0.00062525 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2023-06-11 14:13 | 2023-06-11 18:00 | 68 | 3:47 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | S23061100104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2023-06-11 | 15436 | keep | 0 | Jun | 2023 | 0.010513 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
AGUADILLA | 2023-06-11 14:21 | 2023-06-11 17:50 | 1 | 3:29 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A23061100025 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 209 | 2023-06-11 | 209 | keep | 0 | Jun | 2023 | 0.00014235 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-06-11 14:46 | 2023-06-11 15:56 | 1336 | 1:10 | T | DESGANCHE | SE RETIRO RAMA SOBRE LINEAS PRIMARIAS SE CERRO INTERRUPTOR | M23061100061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2023-06-11 | 93520 | keep | 0 | Jun | 2023 | 0.063696 | 0.00090994 | Sustained | FALSE | FALSE | Not_TMED_Event | 1336
HUMACAO | 2023-06-11 14:52 | 2023-06-11 15:36 | 9 | 0:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | REMPLAZO CONECTORES EN EL BAJANTE SECUNDARIO BAJO TAP 5 @ 2 QUEDO EN 123/146V | C23061100122 | New_Event | Secondary Wire Break | Include | Include | Equipment | 44 | 2023-06-11 | 396 | keep | 0 | Jun | 2023 | 0.00026971 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
YAUCO | 2023-06-11 14:59 | 2023-06-11 20:00 | 100 | 5:01 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN C/L | P23061100212 | New_Event | Primary Wire Break | Include | Include | Equipment | 301 | 2023-06-11 | 30100 | keep | 0 | Jun | 2023 | 0.020501 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2023-06-11 15:09 | 2023-06-11 15:10 | 1394 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 16500 DE FAJARDO TC A DOS MARINA | R23061100075 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-11 | 1394 | keep | 0 | Jun | 2023 | 0.00094945 | 0.00094945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1394
FAJARDO | 2023-06-11 15:09 | 2023-06-11 15:10 | 412 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 16500 DE FAJARDO TC A DOS MARINA | R23061100075 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-11 | 412 | keep | 0 | Jun | 2023 | 0.00028061 | 0.00028061 | Momentary | FALSE | FALSE | Not_TMED_Event | 412
AGUADILLA | 2023-06-11 15:09 | 2023-06-11 17:15 | 200 | 2:06 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23061100067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2023-06-11 | 25200 | keep | 0 | Jun | 2023 | 0.017164 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-06-11 15:20 | 2023-06-11 16:52 | 40 | 1:32 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | B23061100059 | New_Event | Animals | Include | Include | Wildlife | 92 | 2023-06-11 | 3680 | keep | 0 | Jun | 2023 | 0.0025064 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-06-11 15:27 | 2023-06-12 07:11 | 10 | 15:44 | P | OTRAS CAUSAS | 1 X 15 EN TRANSFORMADOR POR FUSIBLE CORROIDO | A23061100036 | New_Event | Other Causes | Include | Include | Other | 944 | 2023-06-11 | 9440 | keep | 0 | Jun | 2023 | 0.0064295 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-06-11 15:32 | 2023-06-11 17:02 | 110 | 1:30 | P | DESGANCHE | 1 X 50 EN CORTE LINEA DESGANCHE | M23061100079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2023-06-11 | 9900 | keep | 0 | Jun | 2023 | 0.0067428 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
ARECIBO | 2023-06-11 15:34 | 2023-06-11 19:25 | 30 | 3:51 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE RETRIRO ALUMBRADO QUE ESTABA CRUZANDO CON LA LINEA PRIMARIA | A23061100037 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 231 | 2023-06-11 | 6930 | keep | 0 | Jun | 2023 | 0.00472 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-06-11 15:51 | 2023-06-11 16:40 | 11 | 0:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA LEVANTAR SECUNDARIA | R23061100079 | New_Event | Secondary Wire Break | Include | Include | Equipment | 49 | 2023-06-11 | 539 | keep | 0 | Jun | 2023 | 0.00036711 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2023-06-11 15:54 | 2023-06-11 17:49 | 8 | 1:55 | P | DESGANCHE | 1X15 EN XMR DESGANCHE PRIMARIO | S23061100135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2023-06-11 | 920 | keep | 0 | Jun | 2023 | 0.00062661 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2023-06-11 16:00 | 2023-06-11 18:35 | 50 | 2:35 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN C/L SE REPARO ALAMBRE PRIMARIO PARTIDO | P23061100239 | New_Event | Primary Wire Break | Include | Include | Equipment | 155 | 2023-06-11 | 7750 | keep | 0 | Jun | 2023 | 0.0052785 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-06-11 16:12 | 2023-06-11 16:13 | 959 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1904-07 LLEVA LA CARGA DEL 1901-01 LLEVA LA CARGA DEL 1901-04 LLEVA 10% DEL 1901-05 | S2306110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-11 | 959 | keep | 0 | Jun | 2023 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-06-11 16:12 | 2023-06-11 16:13 | 1264 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1904-07 LLEVA LA CARGA DEL 1901-01 LLEVA LA CARGA DEL 1901-04 LLEVA 10% DEL 1901-05 | S2306110000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-11 | 1264 | keep | 0 | Jun | 2023 | 0.0008609 | 0.0008609 | Momentary | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2023-06-11 16:12 | 2023-06-11 16:13 | 62 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1904-07 LLEVA LA CARGA DEL 1901-01 LLEVA LA CARGA DEL 1901-04 LLEVA 10% DEL 1901-05 | S2306110000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-11 | 62 | keep | 0 | Jun | 2023 | 4.2228e-05 | 4.2228e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 62
BAYAMON | 2023-06-11 16:14 | 2023-06-11 16:16 | 1588 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B2306110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-11 | 3176 | keep | 0 | Jun | 2023 | 0.0021632 | 0.0010816 | Momentary | FALSE | FALSE | Not_TMED_Event | 1588
PONCE | 2023-06-11 16:18 | 2023-06-12 07:15 | 40 | 14:57 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA PALOMA CRUZO FASE | P23061100243 | New_Event | Animals | Include | Include | Wildlife | 897 | 2023-06-11 | 35880 | keep | 0 | Jun | 2023 | 0.024438 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-06-11 16:26 | 2023-06-12 12:20 | 8 | 19:54 | P | TRANSFORMADOR AVERIADO | SE ABRE MONTURA DE TRANSFORMADOR Y SE REEMPLAZA TRANSFORMADOR AVERIADO | A23061100038 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1194 | 2023-06-11 | 9552 | keep | 0 | Jun | 2023 | 0.0065058 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-06-11 16:41 | 2023-06-12 13:11 | 5 | 20:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REMPLAZO CAJA AVERIADA | C23061100131 | New_Event | Cutout Failure | Include | Include | Equipment | 1230 | 2023-06-11 | 6150 | keep | 0 | Jun | 2023 | 0.0041887 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-06-11 16:45 | 2023-06-11 16:46 | 878 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | B23061100079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-11 | 878 | keep | 0 | Jun | 2023 | 0.000598 | 0.000598 | Momentary | FALSE | FALSE | Not_TMED_Event | 878
BARRANQUITAS | 2023-06-11 16:54 | 2023-06-12 07:07 | 71 | 14:13 | P | DESGANCHE | 1 X 30 EN C/L | C23061100133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 853 | 2023-06-11 | 60563 | keep | 0 | Jun | 2023 | 0.041249 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
BAYAMON | 2023-06-11 16:59 | 2023-06-11 18:24 | 60 | 1:25 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23061100082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2023-06-11 | 5100 | keep | 0 | Jun | 2023 | 0.0034736 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-06-11 17:12 | 2023-06-11 17:19 | 3 | 0:07 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R23061100080 | New_Event | Animals | Include | Include | Wildlife | 7 | 2023-06-11 | 21 | keep | 0 | Jun | 2023 | 1.4303e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-06-11 17:22 | 2023-06-11 18:01 | 84 | 0:39 | P | DESGANCHE | 1X100 EN C/L DESGANCHE | S23061100165 | New_Event | Vegetation Contact | Include | Include | Vegetation | 39 | 2023-06-11 | 3276 | keep | 0 | Jun | 2023 | 0.0022313 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
SAN JUAN | 2023-06-11 17:45 | 2023-06-11 19:00 | 5 | 1:15 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO TRAMO PARA HACER PRUEBA DE CABLE Y REMPLAZAR BARRA EN SU-6 SJ-230608-03 100% EN SERVICIO | S23060800028 | New_Event | UG Cable Fault | Include | Include | Equipment | 75 | 2023-06-11 | 375 | keep | 0 | Jun | 2023 | 0.00025541 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-06-11 17:52 | 2023-06-11 23:10 | 145 | 5:18 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L PARA LEVANTAR ALAMBRE PRIMARIO EN EL SUELO Y REMPLAZO DE CAJA PRIMARIA 1 X 80 C/L 1 X 100 C/L | S23061100131 | New_Event | Primary Wire Break | Include | Include | Equipment | 318 | 2023-06-11 | 46110 | keep | 0 | Jun | 2023 | 0.031405 | 9.8759e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 145
SAN JUAN | 2023-06-11 17:52 | 2023-06-11 19:31 | 10 | 1:39 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO EN XMR PARA CERRAR PUENTE PRIMARIO DE CAJA @ LINEA - TRASPATIO | S23061100170 | New_Event | Primary Wire Break | Include | Include | Equipment | 99 | 2023-06-11 | 990 | keep | 0 | Jun | 2023 | 0.00067428 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-06-11 17:54 | 2023-06-12 12:07 | 15 | 18:13 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R23061100081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1093 | 2023-06-11 | 16395 | keep | 0 | Jun | 2023 | 0.011167 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-06-11 17:56 | 2023-06-12 14:49 | 40 | 20:53 | P | CAUSAS EXTERNAS | 2X65 EN C/L POR PERSONAL AJENO A LUMA ENERGY REALIZANDO LABORES DE DESGANCHE | S23061100171 | New_Event | Damage From Public | Include | Include | Public | 1253 | 2023-06-11 | 50120 | keep | 0 | Jun | 2023 | 0.034137 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-06-11 17:59 | 2023-06-11 18:28 | 2 | 0:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | R23061100082 | New_Event | Secondary Wire Break | Include | Include | Equipment | 29 | 2023-06-11 | 58 | keep | 0 | Jun | 2023 | 3.9504e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-06-11 18:28 | 2023-06-12 10:36 | 66 | 16:08 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L PARA REPARAR NEUTRAL PRIMARIO | B23061100095 | New_Event | Primary Wire Break | Include | Include | Equipment | 968 | 2023-06-11 | 63888 | keep | 0 | Jun | 2023 | 0.043514 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
BAYAMON | 2023-06-11 18:34 | 2023-06-11 20:34 | 250 | 2:00 | P | SOBRECARGA | 1 X 100 EN C/L POR CARGA | B23061100104 | New_Event | Trip Due To Overload | Include | Include | Other | 120 | 2023-06-11 | 30000 | keep | 0 | Jun | 2023 | 0.020433 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
PONCE | 2023-06-11 18:41 | 2023-06-11 20:30 | 15 | 1:49 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE PRIMARIO EN XMR | P23061100293 | New_Event | Primary Wire Break | Include | Include | Equipment | 109 | 2023-06-11 | 1635 | keep | 0 | Jun | 2023 | 0.0011136 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-06-11 18:53 | 2023-06-11 18:54 | 2126 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CERRADO X CONTROL | C23061100140 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-11 | 2126 | keep | 0 | Jun | 2023 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
MAYAGÃœEZ | 2023-06-11 18:58 | 2023-06-12 14:14 | 1 | 19:16 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR DESCARGA ELECTRICA | M23061100094 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1156 | 2023-06-11 | 1156 | keep | 0 | Jun | 2023 | 0.00078735 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-06-11 18:58 | 2023-06-12 08:30 | 15 | 13:32 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE DE CAJA PRIMARIA A BUSHING EN TRANSFORMADOR | M23061100093 | New_Event | Primary Wire Break | Include | Include | Equipment | 812 | 2023-06-11 | 12180 | keep | 0 | Jun | 2023 | 0.0082957 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-06-11 19:00 | 2023-06-11 21:42 | 51 | 2:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L FUERTES VIENTOS | C23061100141 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 162 | 2023-06-11 | 8262 | keep | 0 | Jun | 2023 | 0.0056272 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2023-06-11 19:01 | 2023-06-12 12:05 | 40 | 17:04 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23061100096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1024 | 2023-06-11 | 40960 | keep | 0 | Jun | 2023 | 0.027898 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2023-06-11 19:05 | 2023-06-12 06:35 | 45 | 11:30 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA PAJARO CRUZO FASE | P23061100296 | New_Event | Animals | Include | Include | Wildlife | 690 | 2023-06-11 | 31050 | keep | 0 | Jun | 2023 | 0.021148 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
VEGA BAJA | 2023-06-11 19:06 | 2023-06-11 19:07 | 3000 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23061100110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-11 | 3000 | keep | 0 | Jun | 2023 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
SAN JUAN | 2023-06-11 19:15 | 2023-06-12 12:59 | 52 | 17:44 | P | DESGANCHE | 1X50 EN C/L DESGANCHE | S23061100190 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1064 | 2023-06-11 | 55328 | keep | 0 | Jun | 2023 | 0.037684 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
UTUADO | 2023-06-11 19:16 | 2023-06-12 09:51 | 25 | 14:35 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CONVERTIDO POR MAL TIEMPO | A23061100052 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 875 | 2023-06-11 | 21875 | keep | 0 | Jun | 2023 | 0.014899 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-06-11 19:20 | 2023-06-13 15:10 | 3 | 43:50 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA @ CAJA EN C/L | S23061100191 | New_Event | Primary Wire Break | Include | Include | Equipment | 2630 | 2023-06-11 | 7890 | keep | 0 | Jun | 2023 | 0.0053738 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2023-06-11 19:22 | 2023-06-12 08:16 | 25 | 12:54 | P | DESGANCHE | 1 X 30 EN C/L | R23061100084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 774 | 2023-06-11 | 19350 | keep | 0 | Jun | 2023 | 0.013179 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2023-06-11 19:27 | 2023-06-12 10:56 | 8 | 15:29 | P | TRANSFORMADOR AVERIADO | T - 11 AVERIADO CERRO N/O EN EL T - 10 | C23061100144 | New_Event | Service Transformer Failure | Include | Include | Equipment | 929 | 2023-06-11 | 7432 | keep | 0 | Jun | 2023 | 0.0050619 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-06-11 19:33 | 2023-06-12 12:29 | 8 | 16:56 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | B23061100125 | New_Event | Primary Wire Break | Include | Include | Equipment | 1016 | 2023-06-11 | 8128 | keep | 0 | Jun | 2023 | 0.0055359 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-06-11 19:56 | 2023-06-11 22:31 | 70 | 2:35 | P | SOBRECARGA | 1 X 65 EN C/L POR CARGA | B23061100138 | New_Event | Trip Due To Overload | Include | Include | Other | 155 | 2023-06-11 | 10850 | keep | 0 | Jun | 2023 | 0.0073899 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2023-06-11 20:12 | 2023-06-11 23:24 | 468 | 3:12 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO DE LINEA A CAJA | C23061100158 | New_Event | Primary Wire Break | Include | Include | Equipment | 192 | 2023-06-11 | 89856 | keep | 0 | Jun | 2023 | 0.061201 | 0.00031875 | Sustained | FALSE | FALSE | Not_TMED_Event | 468
VEGA BAJA | 2023-06-11 20:16 | 2023-06-12 00:22 | 35 | 4:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA Y 1 X 50 EN C/L | B23061100145 | New_Event | Cutout Failure | Include | Include | Equipment | 246 | 2023-06-11 | 8610 | keep | 0 | Jun | 2023 | 0.0058642 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2023-06-11 20:25 | 2023-06-11 23:00 | 400 | 2:35 | P | SOBRECARGA | 1 X 100 EN CORTE DE LINEA SOBRECARGA | M23061100118 | New_Event | Trip Due To Overload | Include | Include | Other | 155 | 2023-06-11 | 62000 | keep | 0 | Jun | 2023 | 0.042228 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
AGUADILLA | 2023-06-11 20:40 | 2023-06-11 20:42 | 4607 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR LINEAS ZAFADAS DE AISLADORES | A23061100060 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2023-06-11 | 9214 | keep | 0 | Jun | 2023 | 0.0062756 | 0.0031378 | Momentary | FALSE | FALSE | Not_TMED_Event | 4607
AGUADILLA | 2023-06-11 20:52 | 2023-06-12 19:06 | 1 | 22:14 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA PARTIDA Y SE CERRO CORTE DE LINEA | A23061100066 | New_Event | Primary Wire Break | Include | Include | Equipment | 1334 | 2023-06-11 | 1334 | keep | 0 | Jun | 2023 | 0.00090858 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-06-11 21:27 | 2023-06-12 07:24 | 29 | 9:57 | P | ANIMAL | 1 X 25 EN C/L CRUCE X AVE | C23061100168 | New_Event | Animals | Include | Include | Wildlife | 597 | 2023-06-11 | 17313 | keep | 0 | Jun | 2023 | 0.011792 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
CANOVANAS | 2023-06-11 21:34 | 2023-06-11 23:50 | 42 | 2:16 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO AISLADOR POR RIGIDO | R23061100098 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 136 | 2023-06-11 | 5712 | keep | 0 | Jun | 2023 | 0.0038904 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
CANOVANAS | 2023-06-11 21:48 | 2023-06-12 09:36 | 10 | 11:48 | P | TRANSFORMADOR AVERIADO | 1 X 25 EN PROVISIONAL AEREO NO CAUSA | R23061100104 | New_Event | Service Transformer Failure | Include | Include | Equipment | 708 | 2023-06-11 | 7080 | keep | 0 | Jun | 2023 | 0.0048222 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-06-11 22:11 | 2023-06-11 22:12 | 1835 | 0:01 | T | ANIMAL | RECIERRE DE BKR | C23061100170 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-06-11 | 1835 | keep | 0 | Jun | 2023 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
HUMACAO | 2023-06-11 22:12 | 2023-06-12 00:36 | 75 | 2:24 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23061100173 | 1st_after_momentary | Animals | Include | Include | Wildlife | 144 | 2023-06-11 | 10800 | keep | 0 | Jun | 2023 | 0.0073558 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2023-06-11 22:56 | 2023-06-12 08:59 | 6 | 10:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR Y SE REPARAN CONEXIONES SECUNDARIAS | A23061100070 | New_Event | Secondary Wire Break | Include | Include | Equipment | 603 | 2023-06-11 | 3618 | keep | 0 | Jun | 2023 | 0.0024642 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2023-06-11 23:02 | 2023-06-12 09:50 | 100 | 10:48 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R23061100111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 648 | 2023-06-11 | 64800 | keep | 0 | Jun | 2023 | 0.044135 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-06-11 23:17 | 2023-06-11 23:20 | 1590 | 0:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 DE CAGUAS TC SE ENCONTRÃ“ GATO QUEMADO | C23061100177 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2023-06-11 | 4770 | keep | 0 | Jun | 2023 | 0.0032488 | 0.0010829 | Momentary | FALSE | FALSE | Not_TMED_Event | 1590
CAGUAS | 2023-06-11 23:17 | 2023-06-11 23:20 | 1 | 0:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 DE CAGUAS TC SE ENCONTRÃ“ GATO QUEMADO | C23061100177 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2023-06-11 | 3 | keep | 0 | Jun | 2023 | 2.0433e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-06-11 23:17 | 2023-06-11 23:20 | 1510 | 0:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 DE CAGUAS TC SE ENCONTRÃ“ GATO QUEMADO | C23061100177 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2023-06-11 | 4530 | keep | 0 | Jun | 2023 | 0.0030854 | 0.0010285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1510
CAGUAS | 2023-06-11 23:17 | 2023-06-11 23:20 | 166 | 0:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 DE CAGUAS TC SE ENCONTRÃ“ GATO QUEMADO | C23061100177 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2023-06-11 | 498 | keep | 0 | Jun | 2023 | 0.00033919 | 0.00011306 | Momentary | FALSE | FALSE | Not_TMED_Event | 166
CAGUAS | 2023-06-11 23:17 | 2023-06-11 23:20 | 1153 | 0:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 DE CAGUAS TC SE ENCONTRÃ“ GATO QUEMADO | C23061100178 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2023-06-11 | 3459 | keep | 0 | Jun | 2023 | 0.0023559 | 0.0007853 | Momentary | FALSE | FALSE | Not_TMED_Event | 1153
CAGUAS | 2023-06-11 23:17 | 2023-06-11 23:20 | 1709 | 0:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 DE CAGUAS TC SE ENCONTRÃ“ GATO QUEMADO | C23061100178 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2023-06-11 | 5127 | keep | 0 | Jun | 2023 | 0.003492 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
CAGUAS | 2023-06-11 23:17 | 2023-06-11 23:20 | 1320 | 0:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 DE CAGUAS TC SE ENCONTRÃ“ GATO QUEMADO | C23061100178 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2023-06-11 | 3960 | keep | 0 | Jun | 2023 | 0.0026971 | 0.00089905 | Momentary | FALSE | FALSE | Not_TMED_Event | 1320
BAYAMON | 2023-06-11 23:49 | 2023-06-12 11:50 | 65 | 12:01 | P | NO SE REPORTO CAUSA | 1X100 EN AEREO PROVISIONAL | S23061100227 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 721 | 2023-06-11 | 46865 | keep | 0 | Jun | 2023 | 0.03192 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2023-06-11 23:54 | 2023-06-12 01:02 | 196 | 1:08 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23061100128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 68 | 2023-06-11 | 13328 | keep | 0 | Jun | 2023 | 0.0090776 | 0.00013349 | Sustained | FALSE | FALSE | Not_TMED_Event | 196
BAYAMON | 2023-06-11 23:56 | 2023-06-12 09:13 | 58 | 9:17 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | B23061100155 | New_Event | Animals | Include | Include | Wildlife | 557 | 2023-06-11 | 32306 | keep | 0 | Jun | 2023 | 0.022003 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
BAYAMON | 2023-06-12 02:25 | 2023-06-12 11:58 | 1 | 9:33 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER HACIA ANTENAS DE LIBERTY | P23061200004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 573 | 2023-06-12 | 573 | keep | 0 | Jun | 2023 | 0.00039027 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-06-12 03:11 | 2023-06-12 12:13 | 100 | 9:02 | P | DESGANCHE | 1 X 80 EN CORTE LINEA SE REALIZO DESGANCHE | M23061200014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 542 | 2023-06-12 | 54200 | keep | 0 | Jun | 2023 | 0.036915 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2023-06-12 04:41 | 2023-06-12 04:42 | 2126 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO X CONTROL | C23061200009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-12 | 2126 | keep | 0 | Jun | 2023 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
PONCE | 2023-06-12 05:47 | 2023-06-12 05:48 | 4009 | 0:01 | S | NO SE REPORTO CAUSA | RECIERRE PORTATIL #14 | P23061200016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-12 | 4009 | keep | 0 | Jun | 2023 | 0.0027305 | 0.0027305 | Momentary | FALSE | FALSE | Not_TMED_Event | 4009
CANOVANAS | 2023-06-12 05:55 | 2023-06-12 09:14 | 80 | 3:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X100 EN C/L SE REMPLAZO CAJA PRIMARIA | R23061200006 | New_Event | Cutout Failure | Include | Include | Equipment | 199 | 2023-06-12 | 15920 | keep | 0 | Jun | 2023 | 0.010843 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-06-12 06:15 | 2023-06-12 10:14 | 50 | 3:59 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE LINEA PARARRAYO DEFECTUOSO | M23061200009 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 239 | 2023-06-12 | 11950 | keep | 0 | Jun | 2023 | 0.0081391 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-06-12 06:16 | 2023-06-12 07:54 | 60 | 1:38 | P | DESGANCHE | 1 X 10 EN C/L DESGANCHE | C23061200011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 98 | 2023-06-12 | 5880 | keep | 0 | Jun | 2023 | 0.0040048 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-06-12 06:25 | 2023-06-12 06:26 | 1702 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23061200015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-12 | 1702 | keep | 0 | Jun | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
BAYAMON | 2023-06-12 06:40 | 2023-06-12 09:55 | 15 | 3:15 | P | ANIMAL | 1 X 30 EN C/L CRUCE POR AVE | B23061200005 | New_Event | Animals | Include | Include | Wildlife | 195 | 2023-06-12 | 2925 | keep | 0 | Jun | 2023 | 0.0019922 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-06-12 07:01 | 2023-06-12 07:02 | 1827 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23061200020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-12 | 1827 | keep | 0 | Jun | 2023 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
UTUADO | 2023-06-12 07:03 | 2023-06-12 10:55 | 2 | 3:52 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR LINEA CRUZADA | A23061200010 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 232 | 2023-06-12 | 464 | keep | 0 | Jun | 2023 | 0.00031603 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2023-06-12 07:39 | 2023-06-12 13:46 | 22 | 6:07 | P | DESGANCHE | DESGANCHO Y REPARO PUENTE DE CAJA A LINEA NO FUNDIO | C23061200027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 367 | 2023-06-12 | 8074 | keep | 0 | Jun | 2023 | 0.0054992 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
BAYAMON | 2023-06-12 07:44 | 2023-06-12 16:16 | 50 | 8:32 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23061200066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 512 | 2023-06-12 | 25600 | keep | 0 | Jun | 2023 | 0.017436 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-06-12 08:08 | 2023-06-12 11:00 | 60 | 2:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 Y 1 X 40 EN CORTES DE LINEA SE REMPLAZO AISLADORES ROTOS | M23061200014 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 172 | 2023-06-12 | 10320 | keep | 0 | Jun | 2023 | 0.0070289 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-06-12 08:09 | 2023-06-12 10:30 | 261 | 2:21 | P | DESGANCHE | 1 X 100 EN C/L | R23061200026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2023-06-12 | 36801 | keep | 0 | Jun | 2023 | 0.025065 | 0.00017777 | Sustained | FALSE | FALSE | Not_TMED_Event | 261
MAYAGÃœEZ | 2023-06-12 08:11 | 2023-06-12 16:05 | 100 | 7:54 | P | ARBOL SOBRE LINEA | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23061200015 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 474 | 2023-06-12 | 47400 | keep | 0 | Jun | 2023 | 0.032284 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2023-06-12 08:22 | 2023-06-12 12:35 | 15 | 4:13 | P | SECUNDARIA/DESGANCHE | 1 X 30 EN TRANSFORMADOR DESGANCHE SECUNDARIO | P23061200045 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 253 | 2023-06-12 | 3795 | keep | 0 | Jun | 2023 | 0.0025848 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-06-12 08:29 | 2023-06-12 10:05 | 50 | 1:36 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA REQUIERE DESGANCHE | M23061200018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2023-06-12 | 4800 | keep | 0 | Jun | 2023 | 0.0032693 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-06-12 08:35 | 2023-06-12 15:15 | 7 | 6:40 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR AVE CRUZO BUSHING | M23061200022 | New_Event | Animals | Include | Include | Wildlife | 400 | 2023-06-12 | 2800 | keep | 0 | Jun | 2023 | 0.0019071 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-06-12 08:50 | 2023-06-12 13:14 | 82 | 4:24 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23061200018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 264 | 2023-06-12 | 21648 | keep | 0 | Jun | 2023 | 0.014744 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
BAYAMON | 2023-06-12 09:07 | 2023-06-13 06:48 | 1 | 21:41 | P | DESGANCHE | 2 X 20 EN RISER DESGANCHE | B23061200023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1301 | 2023-06-12 | 1301 | keep | 0 | Jun | 2023 | 0.00088611 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-06-12 09:17 | 2023-06-12 09:50 | 67 | 0:33 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE CON PUNTO CALIENTE EN CORTE DE LINEA | P23061200070 | New_Event | Primary Wire Break | Include | Include | Equipment | 33 | 2023-06-12 | 2211 | keep | 0 | Jun | 2023 | 0.0015059 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
SAN JUAN | 2023-06-12 09:24 | 2023-06-12 09:26 | 590 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S23061200079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-12 | 1180 | keep | 0 | Jun | 2023 | 0.00080369 | 0.00040185 | Momentary | FALSE | FALSE | Not_TMED_Event | 590
CANOVANAS | 2023-06-12 09:26 | 2023-06-12 13:45 | 4 | 4:19 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER Y 1 SMU 20 DE 30AMP DEL SU A AL T-42 | R23061200043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 259 | 2023-06-12 | 1036 | keep | 0 | Jun | 2023 | 0.00070561 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-06-12 09:35 | 2023-06-12 10:45 | 25 | 1:10 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23061200030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2023-06-12 | 1750 | keep | 0 | Jun | 2023 | 0.0011919 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-06-12 09:36 | 2023-06-13 16:42 | 29 | 31:06 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO PM/T-125 DE 75 KVA X 75 KVA Y SE CERRO AEREO PROVISIONAL | R23061100104 | Additional_clients | Service Transformer Failure | Include | Include | Equipment | 1866 | 2023-06-12 | 54114 | keep | 0 | Jun | 2023 | 0.036857 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-06-12 09:41 | 2023-06-12 18:45 | 193 | 9:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | C23061200059 | New_Event | Cutout Failure | Include | Include | Equipment | 544 | 2023-06-12 | 104992 | keep | 0 | Jun | 2023 | 0.07151 | 0.00013145 | Sustained | FALSE | FALSE | Not_TMED_Event | 193
YAUCO | 2023-06-12 09:49 | 2023-06-12 14:29 | 30 | 4:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | P23061200088 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 280 | 2023-06-12 | 8400 | keep | 0 | Jun | 2023 | 0.0057212 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-06-12 10:00 | 2023-06-12 11:00 | 340 | 1:00 | P | CONDUCTOR ROTO O ABIERTO | ABRIO C/L PARA REPARAR CONDUCTOR PRIMARIO Y ENDEREZAR POSTE | C23061200063 | New_Event | Primary Wire Break | Include | Include | Equipment | 60 | 2023-06-12 | 20400 | keep | 0 | Jun | 2023 | 0.013894 | 0.00023157 | Sustained | FALSE | FALSE | Not_TMED_Event | 340
BAYAMON | 2023-06-12 10:12 | 2023-06-12 10:30 | 1 | 0:18 | P | PROBLEMA DEL CLIENTE | 1 X 20 EN MONTURA SE REPORTA PROBLEMA INTERIOR | B23061200036 | New_Event | Customer-Related Interruption | Include | Include | Public | 18 | 2023-06-12 | 18 | keep | 0 | Jun | 2023 | 1.226e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-06-12 10:18 | 2023-06-12 16:50 | 1 | 6:32 | P | ANIMAL | 2 X 25 EN CORTE DE LINEA Y 1 X 20 EN TRANSFORMADOR CRUCE POR AVE | C23061200073 | New_Event | Animals | Include | Include | Wildlife | 392 | 2023-06-12 | 392 | keep | 0 | Jun | 2023 | 0.00026699 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-06-12 10:22 | 2023-06-12 12:25 | 4 | 2:03 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23061200077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 123 | 2023-06-12 | 492 | keep | 0 | Jun | 2023 | 0.0003351 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2023-06-12 10:22 | 2023-06-12 11:42 | 80 | 1:20 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23061200039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 80 | 2023-06-12 | 6400 | keep | 0 | Jun | 2023 | 0.004359 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2023-06-12 10:27 | 2023-06-12 13:37 | 70 | 3:10 | P | NO SE REPORTO CAUSA | 1 X 140 EN SALIDA DE CONVERTIDOR SOBRECARGA | M23061200054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 190 | 2023-06-12 | 13300 | keep | 0 | Jun | 2023 | 0.0090586 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-06-12 10:47 | 2023-06-12 11:43 | 100 | 0:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO EN RISER PARA REMPLAZAR CAJA PRIMARIA NO FUNDIO | S23061000472 | New_Event | Cutout Failure | Include | Include | Equipment | 56 | 2023-06-12 | 5600 | keep | 0 | Jun | 2023 | 0.0038141 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-06-12 10:47 | 2023-06-13 20:37 | 12 | 33:50 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE RETEZO LINEAS Y SE ASEGURO POSTE SE CERRO C/L | B23061200056 | New_Event | Primary Pole Failure | Include | Include | Equipment | 2030 | 2023-06-12 | 24360 | keep | 0 | Jun | 2023 | 0.016591 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-06-12 10:48 | 2023-06-12 20:27 | 15 | 9:39 | P | NO SE REPORTO CAUSA | 1X30 EN BANCO DE XMRS | S23061200105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 579 | 2023-06-12 | 8685 | keep | 0 | Jun | 2023 | 0.0059153 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-06-12 10:56 | 2023-06-12 17:35 | 3 | 6:39 | P | TRANSFORMADOR AVERIADO | CG-230612-01 SE REEMPLAZO TRANSFORMADOR T-11 DE 37.5 KVA X 37.5 KVA | C23061200144 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 399 | 2023-06-12 | 1197 | keep | 0 | Jun | 2023 | 0.00081527 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-06-12 11:00 | 2023-06-12 15:03 | 2 | 4:03 | P | CONDUCTOR ROTO O ABIERTO | SE CAMBIO CAJA PRIMARIA Y PUNTE PRIMARIO EN RISER | P23061200115 | New_Event | Primary Wire Break | Include | Include | Equipment | 243 | 2023-06-12 | 486 | keep | 0 | Jun | 2023 | 0.00033101 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
GUAYAMA | 2023-06-12 11:08 | 2023-06-12 11:09 | 584 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23061200119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-12 | 584 | keep | 0 | Jun | 2023 | 0.00039776 | 0.00039776 | Momentary | FALSE | FALSE | Not_TMED_Event | 584
AGUADILLA | 2023-06-12 11:13 | 2023-06-12 12:08 | 33 | 0:55 | P | CONDUCTOR ROTO O ABIERTO | ALAMBRE PRIMARIO PARTIDO SE ABRIO INTERRUPTOR PARA REPARAR | M23061200077 | New_Event | Primary Wire Break | Include | Include | Equipment | 55 | 2023-06-12 | 1815 | keep | 0 | Jun | 2023 | 0.0012362 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
ARECIBO | 2023-06-12 11:19 | 2023-06-12 19:45 | 1 | 8:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZA CAJA PRIMARIA QUEMADA | P23061200125 | New_Event | Cutout Failure | Include | Include | Equipment | 506 | 2023-06-12 | 506 | keep | 0 | Jun | 2023 | 0.00034463 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-06-12 11:40 | 2023-06-13 08:24 | 1 | 20:44 | P | DESGANCHE | 1 X 50 EN C/L EVENTO TRANSFERIDO DE PONCE | P23061200136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1244 | 2023-06-12 | 1244 | keep | 0 | Jun | 2023 | 0.00084728 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-06-12 11:41 | 2023-06-12 12:48 | 169 | 1:07 | P | CAUSAS EXTERNAS | 2 X 100 EN C/L CAMION SACUDIO LAS LINEAS | C23061200106 | New_Event | Damage From Public | Include | Include | Public | 67 | 2023-06-12 | 11323 | keep | 0 | Jun | 2023 | 0.007712 | 0.00011511 | Sustained | FALSE | FALSE | Not_TMED_Event | 169
BARRANQUITAS | 2023-06-12 11:42 | 2023-06-12 11:44 | 1617 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL | C2306120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-12 | 3234 | keep | 0 | Jun | 2023 | 0.0022027 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
CAGUAS | 2023-06-12 11:52 | 2023-06-12 15:33 | 154 | 3:41 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C23061200108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2023-06-12 | 34034 | keep | 0 | Jun | 2023 | 0.02318 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
CAGUAS | 2023-06-12 11:52 | 2023-06-12 21:43 | 63 | 9:51 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTO | C23061200109 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 591 | 2023-06-12 | 37233 | keep | 0 | Jun | 2023 | 0.025359 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
BAYAMON | 2023-06-12 11:58 | 2023-06-12 12:27 | 40 | 0:29 | P | ARBOL SOBRE LINEA | SE RETIRO ARBOL SOBRE LA LINEA 1 X 80 EN C/L | S23061200127 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 29 | 2023-06-12 | 1160 | keep | 0 | Jun | 2023 | 0.00079007 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-06-12 12:00 | 2023-06-12 13:00 | 1 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA TRIFASICA PARA REPARAR PUENTES SECUNDARIOS | P23061200145 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2023-06-12 | 60 | keep | 0 | Jun | 2023 | 4.0866e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-06-12 12:01 | 2023-06-12 14:25 | 10 | 2:24 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR Y SE SECCIONALIZO POSTE SECUNDARIO | B23061200075 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 144 | 2023-06-12 | 1440 | keep | 0 | Jun | 2023 | 0.00098078 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-06-12 12:08 | 2023-06-12 15:30 | 12 | 3:22 | P | NO SE REPORTO CAUSA | TRANSFORMADOR AUTO PROTEGIDO, SE NORMALIZO | C23061200118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 202 | 2023-06-12 | 2424 | keep | 0 | Jun | 2023 | 0.001651 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-06-12 12:08 | 2023-06-12 17:00 | 99 | 4:52 | T | CONDUCTOR ROTO O ABIERTO | GOI MY-230612-01A SE REPARO LINEA PRIMARIA Y SE COLOCO INTERRUPTOR EN SERVICIO | M23061200107 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 292 | 2023-06-12 | 28908 | keep | 0 | Jun | 2023 | 0.019689 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-06-12 12:09 | 2023-06-12 13:13 | 22 | 1:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR SECUNDARIA Y TOMA | C23061200119 | New_Event | Secondary Wire Break | Include | Include | Equipment | 64 | 2023-06-12 | 1408 | keep | 0 | Jun | 2023 | 0.00095898 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
GUAYAMA | 2023-06-12 12:10 | 2023-06-12 16:48 | 1 | 4:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA POR VIENTOS | P23061200293 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 278 | 2023-06-12 | 278 | keep | 0 | Jun | 2023 | 0.00018934 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-06-12 12:17 | 2023-06-13 12:45 | 100 | 24:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | S23061200135 | New_Event | Cutout Failure | Include | Include | Equipment | 1468 | 2023-06-12 | 146800 | keep | 0 | Jun | 2023 | 0.099985 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-06-12 12:18 | 2023-06-12 15:46 | 20 | 3:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE LINEA FUERTES VIENTOS | M23061200108 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 208 | 2023-06-12 | 4160 | keep | 0 | Jun | 2023 | 0.0028334 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-06-12 12:21 | 2023-06-12 14:10 | 120 | 1:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | M23061200111 | New_Event | Cutout Failure | Include | Include | Equipment | 109 | 2023-06-12 | 13080 | keep | 0 | Jun | 2023 | 0.0089087 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2023-06-12 12:22 | 2023-06-13 12:05 | 7 | 23:43 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO 15 KVA / 4.16KV | M23061200113 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1423 | 2023-06-12 | 9961 | keep | 0 | Jun | 2023 | 0.0067844 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-06-12 12:27 | 2023-06-12 16:28 | 1 | 4:01 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER HACIA ANTENAS DE LIBERTY | P23061200004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 241 | 2023-06-12 | 241 | keep | 0 | Jun | 2023 | 0.00016414 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-06-12 12:28 | 2023-06-12 15:46 | 20 | 3:18 | P | ARBOL SOBRE LINEA | 2 X 50 EN C/L SE RETIRO ARBOL | R23061200058 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 198 | 2023-06-12 | 3960 | keep | 0 | Jun | 2023 | 0.0026971 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-06-12 12:32 | 2023-06-12 20:12 | 57 | 7:40 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 50 Y 1 X 40 EN CORTES DE LINEA SE REALIZO DESGANCHE Y SE ABRIO C/L PARA SECCIONALIZAR POSTE | R23061200060 | New_Event | Primary Pole Failure | Include | Include | Equipment | 460 | 2023-06-12 | 26220 | keep | 0 | Jun | 2023 | 0.017858 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
PONCE | 2023-06-12 12:32 | 2023-06-12 14:43 | 100 | 2:11 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE CORTE DE LINEA | P23061200166 | New_Event | Primary Wire Break | Include | Include | Equipment | 131 | 2023-06-12 | 13100 | keep | 0 | Jun | 2023 | 0.0089224 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-06-12 12:39 | 2023-06-12 15:18 | 12 | 2:39 | P | NO SE REPORTO CAUSA | 1X100 EN RISER | S23061200142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 159 | 2023-06-12 | 1908 | keep | 0 | Jun | 2023 | 0.0012995 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2023-06-12 12:51 | 2023-06-12 14:43 | 80 | 1:52 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C23061200131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2023-06-12 | 8960 | keep | 0 | Jun | 2023 | 0.0061026 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-06-12 12:53 | 2023-06-12 20:51 | 9 | 7:58 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO EL T-345 | R23061200063 | New_Event | Service Transformer Failure | Include | Include | Equipment | 478 | 2023-06-12 | 4302 | keep | 0 | Jun | 2023 | 0.0029301 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2023-06-12 12:59 | 2023-06-12 13:51 | 3957 | 0:52 | T | ANIMAL | SE RETIRO AVE DE LA LINEA A VARETA (DESDE EL SUELO) MEDIANTE SWITCHING FORM SJ-230612-01 Y SE CERRO POR CONTROL | S23061200152 | New_Event | Animals | Include | Include | Wildlife | 52 | 2023-06-12 | 205764 | keep | 0 | Jun | 2023 | 0.14014 | 0.0026951 | Sustained | FALSE | FALSE | Not_TMED_Event | 3957
PONCE | 2023-06-12 13:10 | 2023-06-12 18:06 | 25 | 4:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA 2 X 25 EN TRANSFORMADOR | P23061200182 | New_Event | Secondary Wire Break | Include | Include | Equipment | 296 | 2023-06-12 | 7400 | keep | 0 | Jun | 2023 | 0.0050401 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-06-12 13:13 | 2023-06-12 19:12 | 178 | 5:59 | P | ANIMAL | 2X65 EN C/L POR IGUANA EN LA LINEA (EVENTO TRANSFERIDO) | C23061200133 | New_Event | Animals | Include | Include | Wildlife | 359 | 2023-06-12 | 63902 | keep | 0 | Jun | 2023 | 0.043523 | 0.00012123 | Sustained | FALSE | FALSE | Not_TMED_Event | 178
MAYAGÃœEZ | 2023-06-12 13:26 | 2023-06-12 16:55 | 50 | 3:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23061200043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2023-06-12 | 10450 | keep | 0 | Jun | 2023 | 0.0071174 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-06-12 13:28 | 2023-06-12 16:16 | 60 | 2:48 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR | A23061200059 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 168 | 2023-06-12 | 10080 | keep | 0 | Jun | 2023 | 0.0068654 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-06-12 13:37 | 2023-06-13 17:15 | 25 | 27:38 | P | CABLE SOTERRADO AVERIADO | AVERIA NUEVA DEL T-27 @ T-8 SE CERRO N/O DEL T-5 @ T-4 | S23061200175 | New_Event | UG Cable Fault | Include | Include | Equipment | 1658 | 2023-06-12 | 41450 | keep | 0 | Jun | 2023 | 0.028231 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-06-12 13:51 | 2023-06-12 15:58 | 2388 | 2:07 | P | ANIMAL | SE CERRO PB 1908-03A (RADIAL) | S23061200190 | Partial_restoration | Animals | Include | Include | Wildlife | 127 | 2023-06-12 | 303276 | keep | 0 | Jun | 2023 | 0.20656 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-06-12 14:05 | 2023-06-12 21:15 | 59 | 7:10 | P | CONDUCTOR ROTO O ABIERTO | PUENTE PRIMARIO ABIERTO SE ABRE CORTE LINEA EN TRONCAL BO LA TEA PARA CERRAR EL MISMO | M23061200239 | New_Event | Primary Wire Break | Include | Include | Equipment | 430 | 2023-06-12 | 25370 | keep | 0 | Jun | 2023 | 0.017279 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
MAYAGÃœEZ | 2023-06-12 14:05 | 2023-06-12 18:30 | 80 | 4:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES VERIFICADO EN BITACORA Y | M23061200156 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 265 | 2023-06-12 | 21200 | keep | 0 | Jun | 2023 | 0.014439 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-06-12 14:13 | 2023-06-13 05:38 | 34 | 15:25 | P | DESGANCHE | 1 X65 2 X 50 C/L Y DESGANCHE | B23061200104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 925 | 2023-06-12 | 31450 | keep | 0 | Jun | 2023 | 0.02142 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
UTUADO | 2023-06-12 14:17 | 2023-06-12 18:22 | 200 | 4:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR VIENTOS | A23061200068 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 245 | 2023-06-12 | 49000 | keep | 0 | Jun | 2023 | 0.033374 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2023-06-12 14:22 | 2023-06-13 08:16 | 1 | 17:54 | P | ANIMAL | 2 X 15 EN RISER CRUCE X AVE | R23061200075 | New_Event | Animals | Include | Include | Wildlife | 1074 | 2023-06-12 | 1074 | keep | 0 | Jun | 2023 | 0.0007315 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-06-12 14:26 | 2023-06-12 18:25 | 200 | 3:59 | P | ANIMAL | 1 X 80 Y 1 X 65 EN C/L AVE CRUZO LINEAS | R23061200077 | New_Event | Animals | Include | Include | Wildlife | 239 | 2023-06-12 | 47800 | keep | 0 | Jun | 2023 | 0.032556 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2023-06-12 14:36 | 2023-06-12 14:38 | 1380 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO 2306-02 Y SE CERRO POR SCADA | R23061200078 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2023-06-12 | 2760 | keep | 0 | Jun | 2023 | 0.0018798 | 0.00093991 | Momentary | FALSE | FALSE | Not_TMED_Event | 1380
CANOVANAS | 2023-06-12 14:38 | 2023-06-12 16:53 | 250 | 2:15 | P | CONDUCTOR ROTO O ABIERTO | 1 X 140 Y 1 X 80 EN C/L SE REPARO PUENTE ABIERTO | R23061200079 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 135 | 2023-06-12 | 33750 | keep | 0 | Jun | 2023 | 0.022987 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
ARECIBO | 2023-06-12 14:42 | 2023-06-12 17:48 | 30 | 3:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA POR FUERTES VIENTO | A23061200077 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 186 | 2023-06-12 | 5580 | keep | 0 | Jun | 2023 | 0.0038005 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-06-12 14:45 | 2023-06-12 14:46 | 3046 | 0:01 | T | DESGANCHE | RECIERRE 1646-03 LLEVA 1647-10 Y 15% 1647-09 | R23061200084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-06-12 | 3046 | keep | 0 | Jun | 2023 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
CANOVANAS | 2023-06-12 14:45 | 2023-06-12 14:46 | 307 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE 1646-03 LLEVA 1647-10 Y 15% 1647-09 | R23061200084 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-12 | 307 | keep | 0 | Jun | 2023 | 0.0002091 | 0.0002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 307
CANOVANAS | 2023-06-12 14:45 | 2023-06-12 14:46 | 61 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE 1646-03 LLEVA 1647-10 Y 15% 1647-09 | R23061200084 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-12 | 61 | keep | 0 | Jun | 2023 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2023-06-12 14:45 | 2023-06-12 23:11 | 100 | 8:26 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23061200118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 506 | 2023-06-12 | 50600 | keep | 0 | Jun | 2023 | 0.034463 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-06-12 14:46 | 2023-06-12 22:05 | 187 | 7:19 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R23061200098 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 439 | 2023-06-12 | 82093 | keep | 0 | Jun | 2023 | 0.055913 | 0.00012736 | Sustained | FALSE | FALSE | Not_TMED_Event | 187
BAYAMON | 2023-06-12 14:49 | 2023-06-12 19:29 | 87 | 4:40 | P | DESGANCHE | 1 X 65 Y DESGANCHE | B23061200125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2023-06-12 | 24360 | keep | 0 | Jun | 2023 | 0.016591 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
VEGA BAJA | 2023-06-12 14:51 | 2023-06-12 14:52 | 3387 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B23061200129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-12 | 3387 | keep | 0 | Jun | 2023 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
SAN JUAN | 2023-06-12 14:53 | 2023-06-13 00:45 | 20 | 9:52 | P | DESGANCHE | 2 X 65 C/L Y DESGANCHE | S23061200233 | New_Event | Vegetation Contact | Include | Include | Vegetation | 592 | 2023-06-12 | 11840 | keep | 0 | Jun | 2023 | 0.0080642 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-06-12 14:55 | 2023-06-12 17:53 | 40 | 2:58 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN C/L SE REPARO CONDUCTOR PRIMARIO EN EL SUELO RADIAL | B23061200130 | New_Event | Primary Wire Break | Include | Include | Equipment | 178 | 2023-06-12 | 7120 | keep | 0 | Jun | 2023 | 0.0048494 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-06-12 15:09 | 2023-06-12 15:10 | 959 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23061200136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-12 | 959 | keep | 0 | Jun | 2023 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
HUMACAO | 2023-06-12 15:11 | 2023-06-12 18:00 | 1 | 2:49 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE EVENTO TRANSFERIDO DE PONCE A HUMACAO | P23061200258 | New_Event | Animals | Include | Include | Wildlife | 169 | 2023-06-12 | 169 | keep | 0 | Jun | 2023 | 0.00011511 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-06-12 15:16 | 2023-06-12 15:17 | 2466 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S23061200243 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-12 | 2466 | keep | 0 | Jun | 2023 | 0.0016796 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
CANOVANAS | 2023-06-12 15:19 | 2023-06-12 15:20 | 4154 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23061200103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-12 | 4154 | keep | 0 | Jun | 2023 | 0.0028293 | 0.0028293 | Momentary | FALSE | FALSE | Not_TMED_Event | 4154
SAN JUAN | 2023-06-12 15:21 | 2023-06-13 12:00 | 50 | 20:39 | P | DESGANCHE | DESGANCHE 1 X 100 EN C/L | S23061200249 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1239 | 2023-06-12 | 61950 | keep | 0 | Jun | 2023 | 0.042194 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-06-12 15:21 | 2023-06-12 22:45 | 184 | 7:24 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 100 EN CORTE DE LINEA SE REEMPLAZO DISCO PARTIDO | C23061200178 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 444 | 2023-06-12 | 81696 | keep | 0 | Jun | 2023 | 0.055643 | 0.00012532 | Sustained | FALSE | FALSE | Not_TMED_Event | 184
VEGA BAJA | 2023-06-12 15:27 | 2023-06-12 15:29 | 3387 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B23061200146 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-12 | 6774 | keep | 0 | Jun | 2023 | 0.0046137 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
CANOVANAS | 2023-06-12 15:28 | 2023-06-13 09:50 | 1 | 18:22 | P | SECUNDARIA/DESGANCHE | 2 X 5 EN XMR DESGANCHE EVENTO TRANSFERIDO DE PONCE | P23061200265 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1102 | 2023-06-12 | 1102 | keep | 0 | Jun | 2023 | 0.00075057 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-06-12 15:40 | 2023-06-12 19:48 | 6 | 4:08 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE LEVANTO AEREO PROVISIONAL | C23061200161 | New_Event | Primary Wire Break | Include | Include | Equipment | 248 | 2023-06-12 | 1488 | keep | 0 | Jun | 2023 | 0.0010135 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-06-12 15:44 | 2023-06-12 16:30 | 155 | 0:46 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRE CORTE DE LINEA PARA REEMPLAZO DE POSTE PARTIDO | A23061200091 | New_Event | Primary Pole Failure | Include | Include | Equipment | 46 | 2023-06-12 | 7130 | keep | 0 | Jun | 2023 | 0.0048562 | 0.00010557 | Sustained | FALSE | FALSE | Not_TMED_Event | 155
MAYAGÃœEZ | 2023-06-12 15:47 | 2023-06-12 16:55 | 4 | 1:08 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | P23061200278 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 68 | 2023-06-12 | 272 | keep | 0 | Jun | 2023 | 0.00018526 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-06-12 15:52 | 2023-06-13 13:09 | 10 | 21:17 | P | DESGANCHE | 1X25 EN XMR DESGANCHE PRIMARIO | S23061200262 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1277 | 2023-06-12 | 12770 | keep | 0 | Jun | 2023 | 0.0086976 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-06-12 15:53 | 2023-06-12 17:46 | 40 | 1:53 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23061200099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 113 | 2023-06-12 | 4520 | keep | 0 | Jun | 2023 | 0.0030786 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-06-12 16:00 | 2023-06-12 20:35 | 75 | 4:35 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B23061200160 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 275 | 2023-06-12 | 20625 | keep | 0 | Jun | 2023 | 0.014048 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2023-06-12 16:26 | 2023-06-12 18:40 | 10 | 2:14 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | M23061200194 | New_Event | Animals | Include | Include | Wildlife | 134 | 2023-06-12 | 1340 | keep | 0 | Jun | 2023 | 0.00091267 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-06-12 16:27 | 2023-06-13 00:06 | 93 | 7:39 | P | DESGANCHE | 1 X 65 EN C/L Y DESGANCHE | B23061200173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 459 | 2023-06-12 | 42687 | keep | 0 | Jun | 2023 | 0.029074 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
BAYAMON | 2023-06-12 16:28 | 2023-06-12 16:29 | 959 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1904-07 LLEVA 100% 1901-01 LLEVA 100% 1901-04 LLEVA 10% 1901-05 | S2306120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-12 | 959 | keep | 0 | Jun | 2023 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-06-12 16:28 | 2023-06-12 16:29 | 1264 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1904-07 LLEVA 100% 1901-01 LLEVA 100% 1901-04 LLEVA 10% 1901-05 | S2306120000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-12 | 1264 | keep | 0 | Jun | 2023 | 0.0008609 | 0.0008609 | Momentary | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2023-06-12 16:28 | 2023-06-12 16:29 | 62 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1904-07 LLEVA 100% 1901-01 LLEVA 100% 1901-04 LLEVA 10% 1901-05 | S2306120000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-12 | 62 | keep | 0 | Jun | 2023 | 4.2228e-05 | 4.2228e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 62
UTUADO | 2023-06-12 16:28 | 2023-06-12 19:26 | 50 | 2:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR VIENTOS | A23061200110 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 178 | 2023-06-12 | 8900 | keep | 0 | Jun | 2023 | 0.0060617 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-06-12 16:29 | 2023-06-13 13:10 | 6 | 20:41 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHE | S23061200093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1241 | 2023-06-12 | 7446 | keep | 0 | Jun | 2023 | 0.0050714 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-06-12 16:29 | 2023-06-13 14:28 | 1 | 21:59 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER HACIA ANTENAS DE LIBERTY EVENTO TRANSFERIDO | P23061200004 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 1319 | 2023-06-12 | 1319 | keep | 0 | Jun | 2023 | 0.00089836 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-12 16:31 | 2023-06-13 00:37 | 75 | 8:06 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S23061200283 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 486 | 2023-06-12 | 36450 | keep | 0 | Jun | 2023 | 0.024826 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-06-12 16:33 | 2023-06-12 17:08 | 10 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23061200177 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2023-06-12 | 350 | keep | 0 | Jun | 2023 | 0.00023838 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-06-12 16:38 | 2023-06-13 17:15 | 200 | 24:37 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | C23061200171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1477 | 2023-06-12 | 295400 | keep | 0 | Jun | 2023 | 0.2012 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2023-06-12 16:42 | 2023-06-13 09:42 | 30 | 17:00 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23061200172 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1020 | 2023-06-12 | 30600 | keep | 0 | Jun | 2023 | 0.020842 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-06-12 16:45 | 2023-06-13 12:53 | 1 | 20:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2X20 EN RISER SE REMPLAZO EL PORTAFUSIBLE (EVENTO TRANSFERIDO) | P23061200299 | New_Event | Cutout Failure | Include | Include | Equipment | 1208 | 2023-06-12 | 1208 | keep | 0 | Jun | 2023 | 0.00082276 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-06-12 17:21 | 2023-06-12 21:04 | 200 | 3:43 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE CORTE DE LINEA Y SE CIERRA PUENTE | A23061200134 | New_Event | Primary Wire Break | Include | Include | Equipment | 223 | 2023-06-12 | 44600 | keep | 0 | Jun | 2023 | 0.030377 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-06-12 17:46 | 2023-06-12 23:12 | 1 | 5:26 | P | DESGANCHE | 1 X 20 XMR Y DESGANCHE EVENTO TRANSFERIDO DE PONCE | P23061100280 | New_Event | Vegetation Contact | Include | Include | Vegetation | 326 | 2023-06-12 | 326 | keep | 0 | Jun | 2023 | 0.00022204 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-06-12 17:53 | 2023-06-12 21:45 | 35 | 3:52 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R23061200121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2023-06-12 | 8120 | keep | 0 | Jun | 2023 | 0.0055305 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-06-12 17:57 | 2023-06-13 11:09 | 87 | 17:12 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | S23061200308 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1032 | 2023-06-12 | 89784 | keep | 0 | Jun | 2023 | 0.061151 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
CAGUAS | 2023-06-12 18:00 | 2023-06-12 18:27 | 3 | 0:27 | P | TRANSFORMADOR AVERIADO | CG-230612-01 SE REEMPLAZO BUSHING PRIMARIO EN T-10 HACIA T-11 SE USO CG-230612-01 INTERRUPCION NO TIENE QUE VER CON ANTERIOR | C23061200144 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 27 | 2023-06-12 | 81 | keep | 0 | Jun | 2023 | 5.5169e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-06-12 18:13 | 2023-06-12 20:58 | 15 | 2:45 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA POR AVE | A23061200143 | New_Event | Animals | Include | Include | Wildlife | 165 | 2023-06-12 | 2475 | keep | 0 | Jun | 2023 | 0.0016857 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-06-12 18:29 | 2023-06-12 22:29 | 30 | 4:00 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23061200144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2023-06-12 | 7200 | keep | 0 | Jun | 2023 | 0.0049039 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-06-12 18:48 | 2023-06-13 15:51 | 6 | 21:03 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE PRIMARIO EVENTO TRANSFERIDO DE PONCE | P23061200335 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1263 | 2023-06-12 | 7578 | keep | 0 | Jun | 2023 | 0.0051613 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-06-12 18:57 | 2023-06-13 16:21 | 23 | 21:24 | P | DESGANCHE | 1X80 EN C/L DESGANCHE | S23061200318 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1284 | 2023-06-12 | 29532 | keep | 0 | Jun | 2023 | 0.020114 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BAYAMON | 2023-06-12 19:00 | 2023-06-13 00:53 | 286 | 5:53 | P | DESGANCHE | 2 X 50 EN C/L Y DESGANCHE | B23061200209 | New_Event | Vegetation Contact | Include | Include | Vegetation | 353 | 2023-06-12 | 100958 | keep | 0 | Jun | 2023 | 0.068762 | 0.00019479 | Sustained | FALSE | FALSE | Not_TMED_Event | 286
SAN JUAN | 2023-06-12 19:04 | 2023-06-13 02:35 | 113 | 7:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | S23061200322 | New_Event | Cutout Failure | Include | Include | Equipment | 451 | 2023-06-12 | 50963 | keep | 0 | Jun | 2023 | 0.034711 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
BAYAMON | 2023-06-12 19:29 | 2023-06-12 19:30 | 959 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 EN PATRULLAJE AÃ‰REO EL 6/14/2023 SE ENCONTRARON 14 PUNTOS DE DESGANCHE "PRIORITY" Y 3 PUNTOS PREVENTIVOS. DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200217 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 959 | keep | 0 | Jun | 2023 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-06-12 19:29 | 2023-06-12 19:30 | 1382 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 EN PATRULLAJE AÃ‰REO EL 6/14/2023 SE ENCONTRARON 14 PUNTOS DE DESGANCHE "PRIORITY" Y 3 PUNTOS PREVENTIVOS. DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200217 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 1382 | keep | 0 | Jun | 2023 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2023-06-12 19:29 | 2023-06-12 19:30 | 663 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 EN PATRULLAJE AÃ‰REO EL 6/14/2023 SE ENCONTRARON 14 PUNTOS DE DESGANCHE "PRIORITY" Y 3 PUNTOS PREVENTIVOS. DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200217 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 663 | keep | 0 | Jun | 2023 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2023-06-12 19:29 | 2023-06-12 19:30 | 514 | 0:01 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 BKR 1708-02 LLEVA 30% 1707-01 | B23061200218 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 514 | keep | 0 | Jun | 2023 | 0.00035008 | 0.00035008 | Momentary | FALSE | FALSE | Not_TMED_Event | 514
BAYAMON | 2023-06-12 19:29 | 2023-06-12 19:30 | 1715 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 BKR 1708-02 LLEVA 30% 1707-01 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200218 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 1715 | keep | 0 | Jun | 2023 | 0.0011681 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2023-06-12 19:29 | 2023-06-12 19:30 | 1498 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 EN PATRULLAJE AÃ‰REO EL 6/14/2023 SE ENCONTRARON 14 PUNTOS DE DESGANCHE "PRIORITY" Y 3 PUNTOS PREVENTIVOS. DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200218 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 1498 | keep | 0 | Jun | 2023 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2023-06-12 19:29 | 2023-06-12 19:30 | 1221 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 EN PATRULLAJE AÃ‰REO EL 6/14/2023 SE ENCONTRARON 14 PUNTOS DE DESGANCHE "PRIORITY" Y 3 PUNTOS PREVENTIVOS. DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200218 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 1221 | keep | 0 | Jun | 2023 | 0.00083162 | 0.00083162 | Momentary | FALSE | FALSE | Not_TMED_Event | 1221
BAYAMON | 2023-06-12 19:29 | 2023-06-12 19:30 | 1100 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 EN PATRULLAJE AÃ‰REO EL 6/14/2023 SE ENCONTRARON 14 PUNTOS DE DESGANCHE "PRIORITY" Y 3 PUNTOS PREVENTIVOS. DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200218 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 1100 | keep | 0 | Jun | 2023 | 0.0007492 | 0.0007492 | Momentary | FALSE | FALSE | Not_TMED_Event | 1100
BAYAMON | 2023-06-12 19:29 | 2023-06-12 19:30 | 1514 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 EN PATRULLAJE AÃ‰REO EL 6/14/2023 SE ENCONTRARON 14 PUNTOS DE DESGANCHE "PRIORITY" Y 3 PUNTOS PREVENTIVOS. DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200234 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 1514 | keep | 0 | Jun | 2023 | 0.0010312 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2023-06-12 19:29 | 2023-06-12 19:30 | 1105 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 EN PATRULLAJE AÃ‰REO EL 6/14/2023 SE ENCONTRARON 14 PUNTOS DE DESGANCHE "PRIORITY" Y 3 PUNTOS PREVENTIVOS. DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200234 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 1105 | keep | 0 | Jun | 2023 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2023-06-12 19:29 | 2023-06-12 19:30 | 4176 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 EN PATRULLAJE AÃ‰REO EL 6/14/2023 SE ENCONTRARON 14 PUNTOS DE DESGANCHE "PRIORITY" Y 3 PUNTOS PREVENTIVOS. DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200220 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 4176 | keep | 0 | Jun | 2023 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2023-06-12 19:29 | 2023-06-12 19:30 | 252 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 EN PATRULLAJE AÃ‰REO EL 6/14/2023 SE ENCONTRARON 14 PUNTOS DE DESGANCHE "PRIORITY" Y 3 PUNTOS PREVENTIVOS. DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200220 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 252 | keep | 0 | Jun | 2023 | 0.00017164 | 0.00017164 | Momentary | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2023-06-12 19:29 | 2023-06-12 19:30 | 2147 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 EN PATRULLAJE AÃ‰REO EL 6/14/2023 SE ENCONTRARON 14 PUNTOS DE DESGANCHE "PRIORITY" Y 3 PUNTOS PREVENTIVOS. DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200220 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 2147 | keep | 0 | Jun | 2023 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2023-06-12 19:29 | 2023-06-12 19:30 | 2858 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 EN PATRULLAJE AÃ‰REO EL 6/14/2023 SE ENCONTRARON 14 PUNTOS DE DESGANCHE "PRIORITY" Y 3 PUNTOS PREVENTIVOS. DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200221 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 2858 | keep | 0 | Jun | 2023 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
BAYAMON | 2023-06-12 19:30 | 2023-06-12 19:48 | 87 | 0:18 | P | DESGANCHE | 1 X 65 Y DESGANCHE | B23061200125 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 18 | 2023-06-12 | 1566 | keep | 0 | Jun | 2023 | 0.0010666 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-06-12 19:31 | 2023-06-12 22:41 | 100 | 3:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA DE CORTE DE LINEA 1 X 100 | P23061200348 | New_Event | Cutout Failure | Include | Include | Equipment | 190 | 2023-06-12 | 19000 | keep | 0 | Jun | 2023 | 0.012941 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-06-12 19:48 | 2023-06-12 19:49 | 959 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 EN PATRULLAJE AÃ‰REO EL 6/14/2023 SE ENCONTRARON 14 PUNTOS DE DESGANCHE "PRIORITY" Y 3 PUNTOS PREVENTIVOS. DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200222 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 959 | keep | 0 | Jun | 2023 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-06-12 19:48 | 2023-06-12 19:49 | 1382 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200222 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 1382 | keep | 0 | Jun | 2023 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2023-06-12 19:48 | 2023-06-12 19:49 | 663 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 EN PATRULLAJE AÃ‰REO EL 6/14/2023 SE ENCONTRARON 14 PUNTOS DE DESGANCHE "PRIORITY" Y 3 PUNTOS PREVENTIVOS. DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200222 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 663 | keep | 0 | Jun | 2023 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2023-06-12 19:48 | 2023-06-12 19:49 | 514 | 0:01 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 BKR 1708-02 LLEVA 30% 1707-01 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200223 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 514 | keep | 0 | Jun | 2023 | 0.00035008 | 0.00035008 | Momentary | FALSE | FALSE | Not_TMED_Event | 514
BAYAMON | 2023-06-12 19:48 | 2023-06-12 19:49 | 1715 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 BKR 1708-02 LLEVA 30% 1707-01 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200021 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 1715 | keep | 0 | Jun | 2023 | 0.0011681 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2023-06-12 19:48 | 2023-06-12 19:49 | 1498 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 EN PATRULLAJE AÃ‰REO EL 6/14/2023 SE ENCONTRARON 14 PUNTOS DE DESGANCHE "PRIORITY" Y 3 PUNTOS PREVENTIVOS. DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200223 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 1498 | keep | 0 | Jun | 2023 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2023-06-12 19:48 | 2023-06-12 19:49 | 1221 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 EN PATRULLAJE AÃ‰REO EL 6/14/2023 SE ENCONTRARON 14 PUNTOS DE DESGANCHE "PRIORITY" Y 3 PUNTOS PREVENTIVOS. DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200223 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 1221 | keep | 0 | Jun | 2023 | 0.00083162 | 0.00083162 | Momentary | FALSE | FALSE | Not_TMED_Event | 1221
BAYAMON | 2023-06-12 19:48 | 2023-06-12 19:49 | 1100 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 EN PATRULLAJE AÃ‰REO EL 6/14/2023 SE ENCONTRARON 14 PUNTOS DE DESGANCHE "PRIORITY" Y 3 PUNTOS PREVENTIVOS. DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200223 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 1100 | keep | 0 | Jun | 2023 | 0.0007492 | 0.0007492 | Momentary | FALSE | FALSE | Not_TMED_Event | 1100
BAYAMON | 2023-06-12 19:48 | 2023-06-12 19:49 | 1514 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 EN PATRULLAJE AÃ‰REO EL 6/14/2023 SE ENCONTRARON 14 PUNTOS DE DESGANCHE "PRIORITY" Y 3 PUNTOS PREVENTIVOS. DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200224 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 1514 | keep | 0 | Jun | 2023 | 0.0010312 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2023-06-12 19:48 | 2023-06-12 19:49 | 1105 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 EN PATRULLAJE AÃ‰REO EL 6/14/2023 SE ENCONTRARON 14 PUNTOS DE DESGANCHE "PRIORITY" Y 3 PUNTOS PREVENTIVOS. DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200224 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 1105 | keep | 0 | Jun | 2023 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2023-06-12 19:48 | 2023-06-12 19:49 | 4176 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 EN PATRULLAJE AÃ‰REO EL 6/14/2023 SE ENCONTRARON 14 PUNTOS DE DESGANCHE "PRIORITY" Y 3 PUNTOS PREVENTIVOS. DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200225 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 4176 | keep | 0 | Jun | 2023 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2023-06-12 19:48 | 2023-06-12 19:49 | 252 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 EN PATRULLAJE AÃ‰REO EL 6/14/2023 SE ENCONTRARON 14 PUNTOS DE DESGANCHE "PRIORITY" Y 3 PUNTOS PREVENTIVOS. DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200225 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 252 | keep | 0 | Jun | 2023 | 0.00017164 | 0.00017164 | Momentary | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2023-06-12 19:48 | 2023-06-12 19:49 | 2147 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 EN PATRULLAJE AÃ‰REO EL 6/14/2023 SE ENCONTRARON 14 PUNTOS DE DESGANCHE "PRIORITY" Y 3 PUNTOS PREVENTIVOS. DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200225 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 2147 | keep | 0 | Jun | 2023 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2023-06-12 19:48 | 2023-06-12 19:49 | 2858 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 EN PATRULLAJE AÃ‰REO EL 6/14/2023 SE ENCONTRARON 14 PUNTOS DE DESGANCHE "PRIORITY" Y 3 PUNTOS PREVENTIVOS. DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061200226 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-12 | 2858 | keep | 0 | Jun | 2023 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
BAYAMON | 2023-06-12 19:49 | 2023-06-13 07:08 | 87 | 11:19 | P | DESGANCHE | 1 X 65 Y DESGANCHE | B23061200125 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 679 | 2023-06-12 | 59073 | keep | 0 | Jun | 2023 | 0.040234 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-06-12 19:54 | 2023-06-12 21:15 | 200 | 1:21 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA POR RAMA DE PALMA | A23061200161 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2023-06-12 | 16200 | keep | 0 | Jun | 2023 | 0.011034 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
GUAYAMA | 2023-06-12 19:55 | 2023-06-13 03:45 | 120 | 7:50 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO Y 1 X 100 EN CORTE DE LINEA | P23061200372 | New_Event | Primary Wire Break | Include | Include | Equipment | 470 | 2023-06-12 | 56400 | keep | 0 | Jun | 2023 | 0.038414 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2023-06-12 19:57 | 2023-06-12 22:10 | 200 | 2:13 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23061200215 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2023-06-12 | 26600 | keep | 0 | Jun | 2023 | 0.018117 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-06-12 20:03 | 2023-06-13 15:19 | 15 | 19:16 | P | DESGANCHE | 1 X 30 EN C/L DSGANCHE DE BAMBUAS | B23061200384 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1156 | 2023-06-12 | 17340 | keep | 0 | Jun | 2023 | 0.01181 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-06-12 20:12 | 2023-06-13 17:15 | 18 | 21:03 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE VERIFICO CORTE DE LINEA ABIERTO PARA ABRIR PUENTE Y SECCIONALIZAR POSTE PRIMARIO PARTIDO PARA QUE MAÃ‘ANA SE REMPLACE EL MISMO YA QUE LA GRUA NO ENTRA. SE DEJO UN TRANSFORMADOR FUERA 8 CLIENTES | R23061200060 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 1263 | 2023-06-12 | 22734 | keep | 0 | Jun | 2023 | 0.015484 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-12 20:20 | 2023-06-12 20:21 | 74 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S2306120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-12 | 74 | keep | 0 | Jun | 2023 | 5.0401e-05 | 5.0401e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 74
MAYAGÃœEZ | 2023-06-12 20:35 | 2023-06-13 10:15 | 60 | 13:40 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23061200252 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 820 | 2023-06-12 | 49200 | keep | 0 | Jun | 2023 | 0.03351 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2023-06-12 20:35 | 2023-06-12 20:52 | 80 | 0:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A23061200172 | New_Event | Cutout Failure | Include | Include | Equipment | 17 | 2023-06-12 | 1360 | keep | 0 | Jun | 2023 | 0.00092629 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-06-12 20:41 | 2023-06-12 22:05 | 74 | 1:24 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | CERRADO POR CONTROL SE PARULLO NO SE ENCONTRO CAUSA DEL DISPARO | S23061200362 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 84 | 2023-06-12 | 6216 | keep | 0 | Jun | 2023 | 0.0042337 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
SAN JUAN | 2023-06-12 20:42 | 2023-06-12 20:43 | 4133 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23061200363 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-12 | 4133 | keep | 0 | Jun | 2023 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
BAYAMON | 2023-06-12 20:54 | 2023-06-13 11:18 | 150 | 14:24 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE DE LINEA A CAJA | B23061200241 | New_Event | Primary Wire Break | Include | Include | Equipment | 864 | 2023-06-12 | 129600 | keep | 0 | Jun | 2023 | 0.08827 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-06-12 21:15 | 2023-06-12 22:30 | 371 | 1:15 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO Y SE CERRO CORTE DE LINEA | M23061200239 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 75 | 2023-06-12 | 27825 | keep | 0 | Jun | 2023 | 0.018951 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-12 21:53 | 2023-06-12 21:55 | 2052 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1111-01 20% DE SU CARGA POR 1118-10 LLEVA LA CARGA DEL 1115-03 SE CERRO POR CONTROL | S23061200384 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-12 | 4104 | keep | 0 | Jun | 2023 | 0.0027952 | 0.0013976 | Momentary | FALSE | FALSE | Not_TMED_Event | 2052
SAN JUAN | 2023-06-12 21:53 | 2023-06-12 21:55 | 134 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1111-01 20% DE SU CARGA POR 1118-10 LLEVA LA CARGA DEL 1115-03 SE CERRO POR CONTROL | S23061200384 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-06-12 | 268 | keep | 0 | Jun | 2023 | 0.00018253 | 9.1267e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 134
SAN JUAN | 2023-06-12 21:53 | 2023-06-13 15:29 | 25 | 17:36 | P | SECUNDARIA/DESGANCHE | 1X20 EN XMR Y 1X20 EN OTRO XMR DESGANCHE SECUNDARIO | S23061200381 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1056 | 2023-06-12 | 26400 | keep | 0 | Jun | 2023 | 0.017981 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-06-12 22:09 | 2023-06-12 22:10 | 1307 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE PERTENECE A BAYAMON | S23061200298 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-12 | 1307 | keep | 0 | Jun | 2023 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
SAN JUAN | 2023-06-12 22:29 | 2023-06-12 22:30 | 74 | 0:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | RECIERRE | S2306120000X | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2023-06-12 | 74 | keep | 0 | Jun | 2023 | 5.0401e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-12 22:31 | 2023-06-12 23:39 | 74 | 1:08 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SJ-230612-03 SE DISPARO EL BKR A PETICION DE JUAN CARLOS PARA SECCIONALIZAR TRAMO 40% EN SERVICIO | S23061200362 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 68 | 2023-06-12 | 5032 | keep | 0 | Jun | 2023 | 0.0034273 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
HUMACAO | 2023-06-12 22:33 | 2023-06-13 12:12 | 15 | 13:39 | P | TERMINACION SOTERRADA AVERIADA | SE LIMPIO CONTAMINACION EN TERMINACION Y SE REEMPLAZO SMU-20 X 25 EN SU-5B4 | C23061200226 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 819 | 2023-06-12 | 12285 | keep | 0 | Jun | 2023 | 0.0083673 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-06-12 22:37 | 2023-06-13 01:21 | 400 | 2:44 | P | SOBRECARGA | 1 X 140 EN CORTE DE LINEA SOBRECARGA | M23061200326 | New_Event | Trip Due To Overload | Include | Include | Other | 164 | 2023-06-12 | 65600 | keep | 0 | Jun | 2023 | 0.04468 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
MAYAGÃœEZ | 2023-06-12 22:42 | 2023-06-13 01:15 | 400 | 2:33 | P | SOBRECARGA | 1 X 100 EN CORTE DE LINEA SOBRECARGA | M23061200241 | New_Event | Trip Due To Overload | Include | Include | Other | 153 | 2023-06-12 | 61200 | keep | 0 | Jun | 2023 | 0.041683 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
CANOVANAS | 2023-06-12 23:33 | 2023-06-13 13:35 | 40 | 14:02 | P | DESGANCHE | 1 X 50 EN C/L | R23061200170 | New_Event | Vegetation Contact | Include | Include | Vegetation | 842 | 2023-06-12 | 33680 | keep | 0 | Jun | 2023 | 0.022939 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-06-12 23:39 | 2023-06-13 00:08 | 44 | 0:29 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SJ-230612-03 DE DEJO SECCIONALIZADO TRAMO POR CONTAMINACION EN SU 100 % EN SERVICIO | S23061200362 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 29 | 2023-06-12 | 1276 | keep | 0 | Jun | 2023 | 0.00086908 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-06-12 23:47 | 2023-06-13 12:58 | 8 | 13:11 | P | ANIMAL | 1 X 30 EN C/L SE RETIRO NIDO DE CAJA PRIMARIA | C23061200229 | New_Event | Animals | Include | Include | Wildlife | 791 | 2023-06-12 | 6328 | keep | 0 | Jun | 2023 | 0.00431 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2023-06-12 23:47 | 2023-06-13 07:35 | 75 | 7:48 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | P23061200510 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 468 | 2023-06-12 | 35100 | keep | 0 | Jun | 2023 | 0.023906 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
YAUCO | 2023-06-13 00:26 | 2023-06-13 07:30 | 31 | 7:04 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO CAUSA | P23061300001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 424 | 2023-06-13 | 13144 | keep | 0 | Jun | 2023 | 0.0089523 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
AGUADILLA | 2023-06-13 00:32 | 2023-06-13 10:35 | 30 | 10:03 | P | DESGANCHE | 1 X 40 EN CORTE LINEA SE SECCIONALIZO ALIMENTADOR QUE REQUIERE DESGANCHE | M23061300002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 603 | 2023-06-13 | 18090 | keep | 0 | Jun | 2023 | 0.012321 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-06-13 00:58 | 2023-06-13 00:59 | 3464 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | R2306130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-13 | 3464 | keep | 0 | Jun | 2023 | 0.0023593 | 0.0023593 | Momentary | FALSE | FALSE | Not_TMED_Event | 3464
BAYAMON | 2023-06-13 01:03 | 2023-06-13 13:22 | 8 | 12:19 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | B23061300003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 739 | 2023-06-13 | 5912 | keep | 0 | Jun | 2023 | 0.0040266 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2023-06-13 01:18 | 2023-06-13 08:48 | 40 | 7:30 | P | DESGANCHE | 1 X 65 EN C/L | R23061300001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 450 | 2023-06-13 | 18000 | keep | 0 | Jun | 2023 | 0.01226 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-06-13 01:25 | 2023-06-13 02:40 | 206 | 1:15 | P | ANIMAL | 1 X 65 C/L CRUCE X AVE | B23061300006 | New_Event | Animals | Include | Include | Wildlife | 75 | 2023-06-13 | 15450 | keep | 0 | Jun | 2023 | 0.010523 | 0.00014031 | Sustained | FALSE | FALSE | Not_TMED_Event | 206
CANOVANAS | 2023-06-13 01:52 | 2023-06-13 01:53 | 3046 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR LLEVA EL 1647-10 Y 15% DEL 1647-09 | R23061300003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-13 | 3046 | keep | 0 | Jun | 2023 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
CANOVANAS | 2023-06-13 01:52 | 2023-06-13 01:53 | 61 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE BKR 1646-03 LLEVA EL 100% DEL 1647-10 | R23061300003 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-13 | 61 | keep | 0 | Jun | 2023 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
CANOVANAS | 2023-06-13 01:55 | 2023-06-13 01:56 | 308 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE BKR 1646-03 LLEVA 15% DEL 1647-09 | R23061300003 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-13 | 308 | keep | 0 | Jun | 2023 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
CAGUAS | 2023-06-13 02:47 | 2023-06-13 02:48 | 853 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | C2306130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-13 | 853 | keep | 0 | Jun | 2023 | 0.00058097 | 0.00058097 | Momentary | FALSE | FALSE | Not_TMED_Event | 853
CAGUAS | 2023-06-13 02:48 | 2023-06-13 08:04 | 185 | 5:16 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | C23061300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 316 | 2023-06-13 | 58460 | keep | 0 | Jun | 2023 | 0.039817 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
FAJARDO | 2023-06-13 02:59 | 2023-06-13 12:19 | 48 | 9:20 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L REEMPLAZO 4 DISCOS | R23061300005 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 560 | 2023-06-13 | 26880 | keep | 0 | Jun | 2023 | 0.018308 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
SAN JUAN | 2023-06-13 03:10 | 2023-06-13 03:23 | 6 | 0:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REMPLAZAR CONEXIONES DE BAJANTE SECUNDARIO | S23061300007 | New_Event | Secondary Wire Break | Include | Include | Equipment | 13 | 2023-06-13 | 78 | keep | 0 | Jun | 2023 | 5.3125e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-06-13 03:26 | 2023-06-13 04:14 | 20 | 0:48 | P | ARBOL SOBRE LINEA | 2X 50 SE RETIRO ARBOR SOBRE LINEA | B23061300010 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 48 | 2023-06-13 | 960 | keep | 0 | Jun | 2023 | 0.00065385 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-06-13 03:32 | 2023-06-13 16:42 | 188 | 13:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2X100 EN C/L SE REMPLAZO CAJA PRIMARIA | S23061300009 | New_Event | Cutout Failure | Include | Include | Equipment | 790 | 2023-06-13 | 148520 | keep | 0 | Jun | 2023 | 0.10116 | 0.00012805 | Sustained | FALSE | FALSE | Not_TMED_Event | 188
BARRANQUITAS | 2023-06-13 03:35 | 2023-06-13 03:36 | 870 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE BKR SE CERRO X CONTROL | C23061300011 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-06-13 | 870 | keep | 0 | Jun | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BARRANQUITAS | 2023-06-13 03:39 | 2023-06-13 03:41 | 870 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE BKR SE CERRO X CONTROL | C23061300012 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 2 | 2023-06-13 | 1740 | keep | 0 | Jun | 2023 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
MAYAGÃœEZ | 2023-06-13 03:41 | 2023-06-13 03:42 | 3147 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23061300011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-13 | 3147 | keep | 0 | Jun | 2023 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | Not_TMED_Event | 3147
BARRANQUITAS | 2023-06-13 03:43 | 2023-06-13 03:45 | 870 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE BKR SE CERRO X CONTROL | C23061300014 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 2 | 2023-06-13 | 1740 | keep | 0 | Jun | 2023 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CANOVANAS | 2023-06-13 03:52 | 2023-06-13 11:12 | 53 | 7:20 | P | DESGANCHE | 1 X 50 EN C/L | R23061300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 440 | 2023-06-13 | 23320 | keep | 0 | Jun | 2023 | 0.015883 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
ARECIBO | 2023-06-13 03:56 | 2023-06-13 03:57 | 1883 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23061300001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-13 | 1883 | keep | 0 | Jun | 2023 | 0.0012825 | 0.0012825 | Momentary | FALSE | FALSE | Not_TMED_Event | 1883
BAYAMON | 2023-06-13 04:10 | 2023-06-13 19:26 | 20 | 15:16 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO Y SE CERRO PUENTE A PRIMARIA | B23061300012 | New_Event | Primary Pole Failure | Include | Include | Equipment | 916 | 2023-06-13 | 18320 | keep | 0 | Jun | 2023 | 0.012478 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-06-13 04:16 | 2023-06-13 11:00 | 12 | 6:44 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | C23061300020 | New_Event | Animals | Include | Include | Wildlife | 404 | 2023-06-13 | 4848 | keep | 0 | Jun | 2023 | 0.003302 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2023-06-13 04:42 | 2023-06-13 04:43 | 1945 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23061300012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-13 | 1945 | keep | 0 | Jun | 2023 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
GUAYAMA | 2023-06-13 04:46 | 2023-06-13 04:47 | 1945 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23061300013 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-13 | 1945 | keep | 0 | Jun | 2023 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
VEGA BAJA | 2023-06-13 05:43 | 2023-06-13 15:49 | 20 | 10:06 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A23061300002 | New_Event | Animals | Include | Include | Wildlife | 606 | 2023-06-13 | 12120 | keep | 0 | Jun | 2023 | 0.0082549 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-06-13 05:49 | 2023-06-13 09:40 | 50 | 3:51 | P | NO SE REPORTO CAUSA | 2 X 25 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23061300003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 231 | 2023-06-13 | 11550 | keep | 0 | Jun | 2023 | 0.0078667 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-06-13 05:56 | 2023-06-13 10:20 | 7 | 4:24 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | R23061300007 | New_Event | Animals | Include | Include | Wildlife | 264 | 2023-06-13 | 1848 | keep | 0 | Jun | 2023 | 0.0012587 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-06-13 06:25 | 2023-06-13 06:26 | 1879 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR CONTROL | C23061300032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-13 | 1879 | keep | 0 | Jun | 2023 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
HUMACAO | 2023-06-13 06:35 | 2023-06-13 09:33 | 32 | 2:58 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN C/L REEMPLAZO DE PIN PON POLE Y REPARAR NEUTRAL | C23061300036 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 178 | 2023-06-13 | 5696 | keep | 0 | Jun | 2023 | 0.0038795 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
AGUADILLA | 2023-06-13 06:35 | 2023-06-13 12:55 | 8 | 6:20 | P | DESGANCHE | 1 X 15 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | A23061300005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 380 | 2023-06-13 | 3040 | keep | 0 | Jun | 2023 | 0.0020705 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-06-13 06:43 | 2023-06-13 06:46 | 5290 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-09 LLEVA LA CARGA DEL 1338-08 SE CERRO POR CONTROL | S23061300030 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-06-13 | 15870 | keep | 0 | Jun | 2023 | 0.010809 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2023-06-13 06:43 | 2023-06-13 06:46 | 207 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-09 LLEVA LA CARGA DEL 1338-08 SE CERRO POR CONTROL | S2306130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-06-13 | 621 | keep | 0 | Jun | 2023 | 0.00042296 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2023-06-13 06:43 | 2023-06-13 06:44 | 601 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 17400 ESTA ENLAZADA CON LINEA 7300. | S23061300034 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 601 | keep | 0 | Jun | 2023 | 0.00040934 | 0.00040934 | Momentary | FALSE | FALSE | Not_TMED_Event | 601
SAN JUAN | 2023-06-13 06:43 | 2023-06-13 06:44 | 640 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 17400 ESTA ENLAZADA CON LINEA 7300. | S23061300034 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 640 | keep | 0 | Jun | 2023 | 0.0004359 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
SAN JUAN | 2023-06-13 06:43 | 2023-06-13 06:44 | 1699 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 17400 ESTA ENLAZADA CON LINEA 7300. | S23061300034 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 1699 | keep | 0 | Jun | 2023 | 0.0011572 | 0.0011572 | Momentary | FALSE | FALSE | Not_TMED_Event | 1699
SAN JUAN | 2023-06-13 06:43 | 2023-06-13 06:44 | 892 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 17400 ESTA ENLAZADA CON LINEA 7300. | S23061300034 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 892 | keep | 0 | Jun | 2023 | 0.00060754 | 0.00060754 | Momentary | FALSE | FALSE | Not_TMED_Event | 892
SAN JUAN | 2023-06-13 06:43 | 2023-06-13 06:44 | 1066 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 17400 ESTA ENLAZADA CON LINEA 7300. | S23061300034 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 1066 | keep | 0 | Jun | 2023 | 0.00072605 | 0.00072605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1066
CAGUAS | 2023-06-13 06:44 | 2023-06-13 12:00 | 70 | 5:16 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23061300039 | New_Event | Animals | Include | Include | Wildlife | 316 | 2023-06-13 | 22120 | keep | 0 | Jun | 2023 | 0.015066 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BARRANQUITAS | 2023-06-13 06:57 | 2023-06-13 06:59 | 870 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C23061300040 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 2 | 2023-06-13 | 1740 | keep | 0 | Jun | 2023 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BARRANQUITAS | 2023-06-13 06:59 | 2023-06-13 13:00 | 500 | 6:01 | P | CONDUCTOR ROTO O ABIERTO | CG-230613-02 SE ENCONTRO PUENTE ABIERTO SE CERRO AMARRE CONTRA EL 3602-02 | C23061300092 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 361 | 2023-06-13 | 180500 | keep | 0 | Jun | 2023 | 0.12294 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
PONCE | 2023-06-13 07:00 | 2023-06-13 10:44 | 5 | 3:44 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR 10 KVA A 2.4 KVA AVERIADO | P23061300025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 224 | 2023-06-13 | 1120 | keep | 0 | Jun | 2023 | 0.00076283 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2023-06-13 07:31 | 2023-06-13 12:25 | 2 | 4:54 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER NO SE ENCONTRO CAUSA | A23061300007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 294 | 2023-06-13 | 588 | keep | 0 | Jun | 2023 | 0.00040048 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2023-06-13 07:49 | 2023-06-13 12:39 | 10 | 4:50 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | C23061300056 | New_Event | Animals | Include | Include | Wildlife | 290 | 2023-06-13 | 2900 | keep | 0 | Jun | 2023 | 0.0019752 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-06-13 07:49 | 2023-06-13 13:59 | 75 | 6:10 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23061300048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 370 | 2023-06-13 | 27750 | keep | 0 | Jun | 2023 | 0.0189 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
PONCE | 2023-06-13 07:52 | 2023-06-13 07:53 | 752 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23061300049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-13 | 752 | keep | 0 | Jun | 2023 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
SAN JUAN | 2023-06-13 07:58 | 2023-06-13 18:28 | 1 | 10:30 | P | NO SE REPORTO CAUSA | 2X50 DE RISER @ TRANSCLOSURE | S23061300050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 630 | 2023-06-13 | 630 | keep | 0 | Jun | 2023 | 0.00042909 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-06-13 08:06 | 2023-06-13 08:07 | 67 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B23061300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-13 | 67 | keep | 0 | Jun | 2023 | 4.5633e-05 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
HUMACAO | 2023-06-13 08:06 | 2023-06-13 14:11 | 30 | 6:05 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | C23061300059 | New_Event | Primary Wire Break | Include | Include | Equipment | 365 | 2023-06-13 | 10950 | keep | 0 | Jun | 2023 | 0.007458 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-06-13 08:06 | 2023-06-13 10:31 | 189 | 2:25 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C23061300060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2023-06-13 | 27405 | keep | 0 | Jun | 2023 | 0.018665 | 0.00012873 | Sustained | FALSE | FALSE | Not_TMED_Event | 189
ARECIBO | 2023-06-13 08:07 | 2023-06-13 14:20 | 16 | 6:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | A23061300008 | New_Event | Cutout Failure | Include | Include | Equipment | 373 | 2023-06-13 | 5968 | keep | 0 | Jun | 2023 | 0.0040648 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CANOVANAS | 2023-06-13 08:14 | 2023-06-13 14:35 | 11 | 6:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO LLUVIA | R23061300018 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 381 | 2023-06-13 | 4191 | keep | 0 | Jun | 2023 | 0.0028545 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
UTUADO | 2023-06-13 08:21 | 2023-06-13 11:20 | 60 | 2:59 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | A23061300014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2023-06-13 | 10740 | keep | 0 | Jun | 2023 | 0.007315 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2023-06-13 08:25 | 2023-06-13 09:58 | 20 | 1:33 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23061300017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2023-06-13 | 1860 | keep | 0 | Jun | 2023 | 0.0012668 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2023-06-13 08:27 | 2023-06-13 13:51 | 100 | 5:24 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE NEUTRAL ABIERTO | P23061300062 | New_Event | Primary Wire Break | Include | Include | Equipment | 324 | 2023-06-13 | 32400 | keep | 0 | Jun | 2023 | 0.022067 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-06-13 08:32 | 2023-06-13 18:41 | 19 | 10:09 | P | DESGANCHE | 1 X 40 EN C/L 1 X 20 C/L DESGANCHE | B23061300030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 609 | 2023-06-13 | 11571 | keep | 0 | Jun | 2023 | 0.007881 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
PONCE | 2023-06-13 08:33 | 2023-06-13 14:59 | 5 | 6:26 | P | SOBRECARGA | 1 X 50 EN RISER POR CARGA | P23061300067 | New_Event | Trip Due To Overload | Include | Include | Other | 386 | 2023-06-13 | 1930 | keep | 0 | Jun | 2023 | 0.0013145 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2023-06-13 08:45 | 2023-06-13 10:02 | 7 | 1:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EL TRANSFORMADOR PARA REMPLAZAR EL BAJANTE SECUNDARIO | R23061300029 | New_Event | Secondary Wire Break | Include | Include | Equipment | 77 | 2023-06-13 | 539 | keep | 0 | Jun | 2023 | 0.00036711 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
YAUCO | 2023-06-13 08:50 | 2023-06-13 11:05 | 1 | 2:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZARON TRES AISLADORES 1 X 80 EN CORTE DE LINEA | P23061300071 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 135 | 2023-06-13 | 135 | keep | 0 | Jun | 2023 | 9.1948e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-06-13 09:03 | 2023-06-13 09:47 | 8 | 0:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUDNARIA | C23061300001 | New_Event | Secondary Wire Break | Include | Include | Equipment | 44 | 2023-06-13 | 352 | keep | 0 | Jun | 2023 | 0.00023975 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-06-13 09:11 | 2023-06-13 09:13 | 4304 | 0:02 | T | ANIMAL | DISPARO DE INTERRUPTOR RR NO NORMALIZA POR SCADA SE REALIZA PUEBA Y QUEDA EN SERVICIO | M23061300037 | New_Event | Animals | Include | Include | Wildlife | 2 | 2023-06-13 | 8608 | keep | 0 | Jun | 2023 | 0.0058629 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
MAYAGÃœEZ | 2023-06-13 09:13 | 2023-06-13 13:10 | 50 | 3:57 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | M23061300045 | 1st_after_momentary | Animals | Include | Include | Wildlife | 237 | 2023-06-13 | 11850 | keep | 0 | Jun | 2023 | 0.008071 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-06-13 09:21 | 2023-06-13 11:01 | 8 | 1:40 | P | DESGANCHE | 1 X 40 EN C/L EVENTO TRANSFERIDO DE PONCE | P23061300085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2023-06-13 | 800 | keep | 0 | Jun | 2023 | 0.00054488 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-06-13 09:26 | 2023-06-13 13:30 | 4 | 4:04 | P | ANIMAL | 2 X 80 EN C/L CRUCE X AVE EVENTO TRANSFERIDO DE PONCE | P23061300090 | New_Event | Animals | Include | Include | Wildlife | 244 | 2023-06-13 | 976 | keep | 0 | Jun | 2023 | 0.00066475 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2023-06-13 09:29 | 2023-06-13 09:32 | 661 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR SCADA | P23061300093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-06-13 | 1983 | keep | 0 | Jun | 2023 | 0.0013506 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
SAN JUAN | 2023-06-13 09:30 | 2023-06-13 14:27 | 35 | 4:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR Y SE REPARO SECUNDARIA EN VARIOS PUNTOS EVENTO TRANSFERIDO DE PONCE | P23061200134 | New_Event | Secondary Wire Break | Include | Include | Equipment | 297 | 2023-06-13 | 10395 | keep | 0 | Jun | 2023 | 0.00708 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2023-06-13 09:41 | 2023-06-13 16:49 | 25 | 7:08 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO POSTE PRIMARIO | R23061300031 | New_Event | Primary Pole Failure | Include | Include | Equipment | 428 | 2023-06-13 | 10700 | keep | 0 | Jun | 2023 | 0.0072877 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-06-13 09:44 | 2023-06-13 14:39 | 12 | 4:55 | P | ANIMAL | 1 X 65 EN C/L AVES | B23061300098 | New_Event | Animals | Include | Include | Wildlife | 295 | 2023-06-13 | 3540 | keep | 0 | Jun | 2023 | 0.0024111 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-06-13 09:45 | 2023-06-13 20:05 | 23 | 10:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR SE REPARO SECUNDARIA | B23061300047 | New_Event | Secondary Wire Break | Include | Include | Equipment | 620 | 2023-06-13 | 14260 | keep | 0 | Jun | 2023 | 0.0097124 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
YAUCO | 2023-06-13 09:54 | 2023-06-13 12:05 | 75 | 2:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE LINEA FUERTE BRISA | P23061300108 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 131 | 2023-06-13 | 9825 | keep | 0 | Jun | 2023 | 0.0066918 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-06-13 09:55 | 2023-06-13 09:57 | 1356 | 0:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CERRO POR CONTROL | S23061300105 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2023-06-13 | 2712 | keep | 0 | Jun | 2023 | 0.0018471 | 0.00092357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1356
SAN JUAN | 2023-06-13 09:57 | 2023-06-13 15:49 | 100 | 5:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3X100 EN C/L Y SE REMPLAZO CAJA PRIMARIA | S23061300111 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 352 | 2023-06-13 | 35200 | keep | 0 | Jun | 2023 | 0.023975 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-06-13 09:59 | 2023-06-13 10:00 | 3046 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA EL 1647-10 Y 15% DEL 1647-09 | R23061300035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-13 | 3046 | keep | 0 | Jun | 2023 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
CANOVANAS | 2023-06-13 09:59 | 2023-06-13 10:00 | 308 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DEL 1646-03 LLEVA EL 15% DEL 1647-09 | R23061300035 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-13 | 308 | keep | 0 | Jun | 2023 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
CANOVANAS | 2023-06-13 09:59 | 2023-06-13 10:00 | 61 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DEL 1646-03 LLEVA EL 100% DEL 1647-10 | R23061300035 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-13 | 61 | keep | 0 | Jun | 2023 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
SAN JUAN | 2023-06-13 10:01 | 2023-06-13 15:44 | 12 | 5:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 2X20 EN XMR Y SE REPARO/LEVANTO SECUNDARIA DEL SUELO | S23061300108 | New_Event | Secondary Wire Break | Include | Include | Equipment | 343 | 2023-06-13 | 4116 | keep | 0 | Jun | 2023 | 0.0028034 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2023-06-13 10:06 | 2023-06-13 14:10 | 3 | 4:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | P23061300118 | New_Event | Cutout Failure | Include | Include | Equipment | 244 | 2023-06-13 | 732 | keep | 0 | Jun | 2023 | 0.00049856 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-06-13 10:17 | 2023-06-13 13:32 | 1 | 3:15 | P | ANIMAL | 1 X 25 EN XMR CRUCE POR GATO EVENTO TRANSFERIDO DE PONCE | P23061300125 | New_Event | Animals | Include | Include | Wildlife | 195 | 2023-06-13 | 195 | keep | 0 | Jun | 2023 | 0.00013281 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-06-13 10:18 | 2023-06-13 12:51 | 32 | 2:33 | P | DESGANCHE | 1 X 140 EN C/L DESGANCHE | C23061300094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2023-06-13 | 4896 | keep | 0 | Jun | 2023 | 0.0033346 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
MAYAGÃœEZ | 2023-06-13 10:22 | 2023-06-13 16:45 | 125 | 6:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M23061300057 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 383 | 2023-06-13 | 47875 | keep | 0 | Jun | 2023 | 0.032607 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
FAJARDO | 2023-06-13 10:23 | 2023-06-13 11:41 | 100 | 1:18 | P | CAUSAS EXTERNAS | 3 X 80 EN C/L SE LEVANTO CONDUCTOR QUE PERSONAL DEL MUNICIPIO TUMBO DESGANCHANDO | R23061300036 | New_Event | Damage From Public | Include | Include | Public | 78 | 2023-06-13 | 7800 | keep | 0 | Jun | 2023 | 0.0053125 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-06-13 10:35 | 2023-06-13 16:10 | 15 | 5:35 | P | DESGANCHE | SE DESGANCHO SE RETIRO TAGS Y SE CERRO CORTE DE LINEA | M23061300002 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 335 | 2023-06-13 | 5025 | keep | 0 | Jun | 2023 | 0.0034225 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-06-13 10:42 | 2023-06-13 18:55 | 1 | 8:13 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO TEASER DE BOMBA | P23061300137 | New_Event | Primary Wire Break | Include | Include | Equipment | 493 | 2023-06-13 | 493 | keep | 0 | Jun | 2023 | 0.00033578 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-06-13 10:48 | 2023-06-13 11:19 | 20 | 0:31 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR Y SE REPARO PUENTE SECUNDARIO ABIERTO TRASPATIO | S23061100204 | New_Event | Secondary Wire Break | Include | Include | Equipment | 31 | 2023-06-13 | 620 | keep | 0 | Jun | 2023 | 0.00042228 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-06-13 10:48 | 2023-06-13 10:49 | 2468 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 9101-04 LLEVA 9101-03 | B23061300069 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-13 | 2468 | keep | 0 | Jun | 2023 | 0.0016809 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
VEGA BAJA | 2023-06-13 10:48 | 2023-06-13 10:49 | 1494 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9101-04 LLEVA 9101-03 | B23061300069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-13 | 1494 | keep | 0 | Jun | 2023 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
SAN JUAN | 2023-06-13 10:59 | 2023-06-13 11:01 | 362 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1620-01 LLEVA 90% DEL 1336-10 LLEVA 60% DEL 1620-02 SE CERRO POR CONTROL | S23061300148 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-06-13 | 724 | keep | 0 | Jun | 2023 | 0.00049311 | 0.00024656 | Momentary | FALSE | FALSE | Not_TMED_Event | 362
SAN JUAN | 2023-06-13 10:59 | 2023-06-13 11:01 | 36 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-01 LLEVA 90% DEL 1336-10 LLEVA 60% DEL 1620-02 SE CERRO POR CONTROL | S23061300148 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-13 | 72 | keep | 0 | Jun | 2023 | 4.9039e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2023-06-13 10:59 | 2023-06-13 11:01 | 2230 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1620-01 LLEVA 90% DEL 1336-10 LLEVA 60% DEL 1620-02 SE CERRO POR CONTROL | S23061300148 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-06-13 | 4460 | keep | 0 | Jun | 2023 | 0.0030377 | 0.0015188 | Momentary | FALSE | FALSE | Not_TMED_Event | 2230
SAN JUAN | 2023-06-13 11:03 | 2023-06-15 15:15 | 1 | 52:12 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINE A CAJA. | S23061300078 | New_Event | Primary Wire Break | Include | Include | Equipment | 3132 | 2023-06-13 | 3132 | keep | 0 | Jun | 2023 | 0.0021332 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-06-13 11:23 | 2023-06-13 19:30 | 90 | 8:07 | P | DESGANCHE | 2X100 EN C/L DESGANCHE EVENTO TRANSFERIDO DE PONCE | P23061300159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 487 | 2023-06-13 | 43830 | keep | 0 | Jun | 2023 | 0.029852 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2023-06-13 11:23 | 2023-06-13 12:13 | 7 | 0:50 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | R23061300042 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 50 | 2023-06-13 | 350 | keep | 0 | Jun | 2023 | 0.00023838 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-06-13 11:28 | 2023-06-13 19:30 | 75 | 8:02 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO | C23061300124 | New_Event | Primary Wire Break | Include | Include | Equipment | 482 | 2023-06-13 | 36150 | keep | 0 | Jun | 2023 | 0.024622 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2023-06-13 11:33 | 2023-06-14 13:35 | 1 | 26:02 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50KVA | M23061300071 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1562 | 2023-06-13 | 1562 | keep | 0 | Jun | 2023 | 0.0010639 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-06-13 11:35 | 2023-06-13 12:51 | 2 | 1:16 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE SECUNDARIO | C23061300127 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 76 | 2023-06-13 | 152 | keep | 0 | Jun | 2023 | 0.00010353 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-06-13 11:38 | 2023-06-13 20:05 | 21 | 8:27 | P | ANIMAL | 1 X 50 EN C/L AVE | B23061300075 | New_Event | Animals | Include | Include | Wildlife | 507 | 2023-06-13 | 10647 | keep | 0 | Jun | 2023 | 0.0072516 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BAYAMON | 2023-06-13 11:38 | 2023-06-13 14:14 | 312 | 2:36 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | S23061300168 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2023-06-13 | 48672 | keep | 0 | Jun | 2023 | 0.03315 | 0.0002125 | Sustained | FALSE | FALSE | Not_TMED_Event | 312
GUAYAMA | 2023-06-13 11:44 | 2023-06-13 14:53 | 44 | 3:09 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO NEUTRAL PRIMARIO | P23061300167 | New_Event | Primary Wire Break | Include | Include | Equipment | 189 | 2023-06-13 | 8316 | keep | 0 | Jun | 2023 | 0.005664 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
MAYAGÃœEZ | 2023-06-13 11:51 | 2023-06-13 13:55 | 10 | 2:04 | P | ANIMAL | 1 X 5 EN TRANSFORMADOR AVE CRUZO BUSHING | M23061300075 | New_Event | Animals | Include | Include | Wildlife | 124 | 2023-06-13 | 1240 | keep | 0 | Jun | 2023 | 0.00084456 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-06-13 11:54 | 2023-06-13 15:40 | 8 | 3:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | REPARAR LINEA SECUNDARIA SOTERRADA | P23061300172 | New_Event | Secondary Wire Break | Include | Include | Equipment | 226 | 2023-06-13 | 1808 | keep | 0 | Jun | 2023 | 0.0012314 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-06-13 11:55 | 2023-06-13 12:25 | 6 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABREN CAJAS EN TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS AVERIADOS | M23061300049 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-06-13 | 180 | keep | 0 | Jun | 2023 | 0.0001226 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2023-06-13 11:57 | 2023-06-13 14:35 | 30 | 2:38 | P | CAUSAS EXTERNAS | 1 X 30 EN CORTE LINEA GLOBO ENTRE FASES PRIMARIAS | M26061300076 | New_Event | Damage From Public | Include | Include | Public | 158 | 2023-06-13 | 4740 | keep | 0 | Jun | 2023 | 0.0032284 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-06-13 11:57 | 2023-06-13 18:57 | 8 | 7:00 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR EVENTO TRANSFERIDO DE PONCE | P23061300173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 420 | 2023-06-13 | 3360 | keep | 0 | Jun | 2023 | 0.0022885 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2023-06-13 12:14 | 2023-06-13 13:20 | 11 | 1:06 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR | P23061300179 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 66 | 2023-06-13 | 726 | keep | 0 | Jun | 2023 | 0.00049448 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2023-06-13 12:16 | 2023-06-13 14:38 | 11 | 2:22 | P | OTRAS CAUSAS | SE ABRIO EN XMR PARA DAR PUNTO DE CONEXION | B23061300078 | New_Event | Other Causes | Include | Include | Other | 142 | 2023-06-13 | 1562 | keep | 0 | Jun | 2023 | 0.0010639 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2023-06-13 12:18 | 2023-06-13 17:29 | 43 | 5:11 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO PUENTE PRIMARIO EN ANCLADA - TRASPATIO - NO FUNDIO | S23061300177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 311 | 2023-06-13 | 13373 | keep | 0 | Jun | 2023 | 0.0091083 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
CANOVANAS | 2023-06-13 12:18 | 2023-06-13 13:29 | 20 | 1:11 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | R23061300047 | New_Event | Animals | Include | Include | Wildlife | 71 | 2023-06-13 | 1420 | keep | 0 | Jun | 2023 | 0.00096716 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-06-13 12:29 | 2023-06-13 18:41 | 20 | 6:12 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23061300157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 372 | 2023-06-13 | 7440 | keep | 0 | Jun | 2023 | 0.0050674 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-06-13 12:31 | 2023-06-13 20:23 | 10 | 7:52 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B23061300081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 472 | 2023-06-13 | 4720 | keep | 0 | Jun | 2023 | 0.0032148 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-06-13 12:33 | 2023-06-13 12:46 | 20 | 0:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN C/L REMPLAZO PORTUFISIBLE | R23061300049 | New_Event | Cutout Failure | Include | Include | Equipment | 13 | 2023-06-13 | 260 | keep | 0 | Jun | 2023 | 0.00017708 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-06-13 12:33 | 2023-06-13 15:44 | 5 | 3:11 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE SECUNDARIO | C23061300147 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 191 | 2023-06-13 | 955 | keep | 0 | Jun | 2023 | 0.00065045 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-06-13 12:39 | 2023-06-13 16:01 | 20 | 3:22 | P | NO SE REPORTO CAUSA | 1X20 EN BANCO DE XMRS | S23061300189 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 202 | 2023-06-13 | 4040 | keep | 0 | Jun | 2023 | 0.0027516 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-06-13 12:51 | 2023-06-13 12:52 | 6197 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | C2306130000X | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-06-13 | 6197 | keep | 0 | Jun | 2023 | 0.0042207 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-06-13 12:52 | 2023-06-13 13:10 | 32 | 0:18 | P | DESGANCHE | 1 X 140 EN C/L | C23061300094 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 18 | 2023-06-13 | 576 | keep | 0 | Jun | 2023 | 0.00039231 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
CAGUAS | 2023-06-13 12:52 | 2023-06-13 16:58 | 2 | 4:06 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE SECUNDARIO | C23061300127 | Partial_restoration | Secondary Vegetation | Include | Include | Vegetation | 246 | 2023-06-13 | 492 | keep | 0 | Jun | 2023 | 0.0003351 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-06-13 13:00 | 2023-06-13 16:10 | 167 | 3:10 | P | CONDUCTOR ROTO O ABIERTO | CG-230613-02 SE TRABAJO CONDICION DE PUENTE ABIERTO EN ANCLADA Y SE NORMALIZARON LAS CARGAS 100% EN SERVICIO | C23061300092 | New_Event | Primary Wire Break | Include | Include | Equipment | 190 | 2023-06-13 | 31730 | keep | 0 | Jun | 2023 | 0.021611 | 0.00011374 | Sustained | FALSE | FALSE | Not_TMED_Event | 167
HUMACAO | 2023-06-13 13:15 | 2023-06-13 15:38 | 5 | 2:23 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23061300164 | New_Event | Animals | Include | Include | Wildlife | 143 | 2023-06-13 | 715 | keep | 0 | Jun | 2023 | 0.00048698 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2023-06-13 13:16 | 2023-06-13 15:00 | 40 | 1:44 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23061300165 | New_Event | Animals | Include | Include | Wildlife | 104 | 2023-06-13 | 4160 | keep | 0 | Jun | 2023 | 0.0028334 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-06-13 13:25 | 2023-06-13 18:15 | 100 | 4:50 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE LINEA SE RETEZO LINEA PRIMARIA | M23061300092 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 290 | 2023-06-13 | 29000 | keep | 0 | Jun | 2023 | 0.019752 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-06-13 13:28 | 2023-06-13 16:00 | 61 | 2:32 | P | DESGANCHE | 1 X 65 EN C/L SE RETIRO BAMBUAS | B23061300088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2023-06-13 | 9272 | keep | 0 | Jun | 2023 | 0.0063151 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2023-06-13 13:30 | 2023-06-13 19:26 | 15 | 5:56 | P | DESGANCHE | 2 X 40 EN C/L SE DESGANCHO | B23061300089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 356 | 2023-06-13 | 5340 | keep | 0 | Jun | 2023 | 0.003637 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-06-13 13:30 | 2023-06-13 14:55 | 1 | 1:25 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE SECUNDARIO | C23061300172 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 85 | 2023-06-13 | 85 | keep | 0 | Jun | 2023 | 5.7893e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-06-13 13:39 | 2023-06-13 16:35 | 8 | 2:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN CORTE DE LINEA | M23061300097 | New_Event | Cutout Failure | Include | Include | Equipment | 176 | 2023-06-13 | 1408 | keep | 0 | Jun | 2023 | 0.00095898 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2023-06-13 13:41 | 2023-06-13 17:20 | 50 | 3:39 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23061300078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2023-06-13 | 10950 | keep | 0 | Jun | 2023 | 0.007458 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-06-13 13:50 | 2023-06-13 19:29 | 65 | 5:39 | P | ARBOL SOBRE LINEA | 1 X 80 EN C/L SE RETIRO ARBOL ENCIMA DE LINEAS | B23061300096 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 339 | 2023-06-13 | 22035 | keep | 0 | Jun | 2023 | 0.015008 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2023-06-13 13:50 | 2023-06-13 18:02 | 6 | 4:12 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE DESGANCHO Y SE REPARO SECUNDARIA | B23061300096 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 252 | 2023-06-13 | 1512 | keep | 0 | Jun | 2023 | 0.0010298 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-06-13 14:03 | 2023-06-14 11:27 | 15 | 21:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO CONECTORES SECUNDARIO | S23061300211 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1284 | 2023-06-13 | 19260 | keep | 0 | Jun | 2023 | 0.013118 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2023-06-13 14:04 | 2023-06-13 14:55 | 18 | 0:51 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | R23061300058 | New_Event | Animals | Include | Include | Wildlife | 51 | 2023-06-13 | 918 | keep | 0 | Jun | 2023 | 0.00062525 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2023-06-13 14:10 | 2023-06-13 15:22 | 114 | 1:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X100 EN C/L Y 1X25 EN XMR SE REMPLAZO EL PORTAFUSIBLE | S23061300214 | New_Event | Cutout Failure | Include | Include | Equipment | 72 | 2023-06-13 | 8208 | keep | 0 | Jun | 2023 | 0.0055904 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
ARECIBO | 2023-06-13 14:13 | 2023-06-13 14:14 | 232 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23061300082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-13 | 232 | keep | 0 | Jun | 2023 | 0.00015801 | 0.00015801 | Momentary | FALSE | FALSE | Not_TMED_Event | 232
VEGA BAJA | 2023-06-13 14:13 | 2023-06-13 18:50 | 10 | 4:37 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR AVE CRUZO FASE A TIERRA | A23061300079 | New_Event | Animals | Include | Include | Wildlife | 277 | 2023-06-13 | 2770 | keep | 0 | Jun | 2023 | 0.0018866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-06-13 14:13 | 2023-06-13 18:03 | 25 | 3:50 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23061300198 | New_Event | Vegetation Contact | Include | Include | Vegetation | 230 | 2023-06-13 | 5750 | keep | 0 | Jun | 2023 | 0.0039163 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2023-06-13 14:15 | 2023-06-13 14:16 | 1607 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23061300081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-13 | 1607 | keep | 0 | Jun | 2023 | 0.0010945 | 0.0010945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1607
VEGA BAJA | 2023-06-13 14:20 | 2023-06-13 14:31 | 2 | 0:11 | P | CAUSAS EXTERNAS | SE ABRIO XMR SE REPARO SECUNDARIA OCASIONADO POR CONTACTO ELECTRICO DE PERSONAL DE TELEFONIA CON EVENTO DE SIT PEL B23061300084 | B23061300104 | New_Event | Damage From Public | Include | Include | Public | 11 | 2023-06-13 | 22 | keep | 0 | Jun | 2023 | 1.4984e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2023-06-13 14:30 | 2023-06-13 14:31 | 232 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR | A23061300084 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-06-13 | 232 | keep | 0 | Jun | 2023 | 0.00015801 | 0.00015801 | Momentary | FALSE | FALSE | Not_TMED_Event | 232
ARECIBO | 2023-06-13 14:31 | 2023-06-13 15:34 | 65 | 1:03 | P | DESGANCHE | 1 X 30 EN CORTE LINEA DESGANCHE | A23061300083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2023-06-13 | 4095 | keep | 0 | Jun | 2023 | 0.0027891 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
VEGA BAJA | 2023-06-13 14:31 | 2023-06-13 14:33 | 3387 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B23061300107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-13 | 6774 | keep | 0 | Jun | 2023 | 0.0046137 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
VEGA BAJA | 2023-06-13 14:33 | 2023-06-13 15:16 | 2 | 0:43 | P | CAUSAS EXTERNAS | SE ABRIO XMR SE REPARO SECUNDARIA OCASIONADO POR CONTACTO ELECTRICO DE PERSONAL DE TELEFONIA CON EVENTO DE SIT PEL B23061300084 | B23061300104 | Partial_restoration | Damage From Public | Include | Include | Public | 43 | 2023-06-13 | 86 | keep | 0 | Jun | 2023 | 5.8574e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-13 14:36 | 2023-06-13 16:59 | 70 | 2:23 | P | DESGANCHE | 1X100 EN C/L DESGANCHE | S23061300220 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2023-06-13 | 10010 | keep | 0 | Jun | 2023 | 0.0068178 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2023-06-13 14:47 | 2023-06-13 14:48 | 232 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR | A23061300085 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-06-13 | 232 | keep | 0 | Jun | 2023 | 0.00015801 | 0.00015801 | Momentary | FALSE | FALSE | Not_TMED_Event | 232
BARRANQUITAS | 2023-06-13 14:48 | 2023-06-14 08:20 | 42 | 17:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L MAL TIEMPO VIENTOS | C23061300206 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1052 | 2023-06-13 | 44184 | keep | 0 | Jun | 2023 | 0.030094 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
SAN JUAN | 2023-06-13 14:54 | 2023-06-13 19:11 | 38 | 4:17 | P | DESGANCHE | 2X65 EN C/L DESGANCHE | S23061300224 | New_Event | Vegetation Contact | Include | Include | Vegetation | 257 | 2023-06-13 | 9766 | keep | 0 | Jun | 2023 | 0.0066516 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
ARECIBO | 2023-06-13 14:54 | 2023-06-13 14:55 | 232 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR | A23061300086 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-06-13 | 232 | keep | 0 | Jun | 2023 | 0.00015801 | 0.00015801 | Momentary | FALSE | FALSE | Not_TMED_Event | 232
VEGA BAJA | 2023-06-13 14:58 | 2023-06-13 14:59 | 2216 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B23061300114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-13 | 2216 | keep | 0 | Jun | 2023 | 0.0015093 | 0.0015093 | Momentary | FALSE | FALSE | Not_TMED_Event | 2216
HUMACAO | 2023-06-13 15:00 | 2023-06-13 18:53 | 1 | 3:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN RISER SE REMPLAZO CAJA PRIMARIA Y PORTAFUSIBLE | C23061300211 | New_Event | Cutout Failure | Include | Include | Equipment | 233 | 2023-06-13 | 233 | keep | 0 | Jun | 2023 | 0.0001587 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-06-13 15:07 | 2023-06-13 16:56 | 232 | 1:49 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE REPARO AISLADOR ZAFADO Y SE CERRO EL INTERRUPTOR | A23061300087 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 109 | 2023-06-13 | 25288 | keep | 0 | Jun | 2023 | 0.017224 | 0.00015801 | Sustained | FALSE | FALSE | Not_TMED_Event | 232
SAN JUAN | 2023-06-13 15:16 | 2023-06-13 15:19 | 513 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1118-10 LLEVA 20% DEL 1111-01 SE CERRO POR CONTROL | S23061300227 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-06-13 | 1539 | keep | 0 | Jun | 2023 | 0.0010482 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2023-06-13 15:16 | 2023-06-13 15:19 | 2782 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1118-10 LLEVA 20% DEL 1111-01 SE CERRO POR CONTROL | S23061300227 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-06-13 | 8346 | keep | 0 | Jun | 2023 | 0.0056844 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
SAN JUAN | 2023-06-13 15:24 | 2023-06-13 18:12 | 26 | 2:48 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | S23061300229 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2023-06-13 | 4368 | keep | 0 | Jun | 2023 | 0.002975 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
HUMACAO | 2023-06-13 15:37 | 2023-06-13 16:33 | 10 | 0:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C23061300217 | New_Event | Secondary Wire Break | Include | Include | Equipment | 56 | 2023-06-13 | 560 | keep | 0 | Jun | 2023 | 0.00038141 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-06-13 15:47 | 2023-06-13 18:00 | 100 | 2:13 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | R23061300067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2023-06-13 | 13300 | keep | 0 | Jun | 2023 | 0.0090586 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-06-13 15:57 | 2023-06-13 15:58 | 4291 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S2306130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-13 | 4291 | keep | 0 | Jun | 2023 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
ARECIBO | 2023-06-13 16:00 | 2023-06-13 22:09 | 50 | 6:09 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A23061300098 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 369 | 2023-06-13 | 18450 | keep | 0 | Jun | 2023 | 0.012566 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-06-13 16:04 | 2023-06-13 16:35 | 100 | 0:31 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23061300148 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 31 | 2023-06-13 | 3100 | keep | 0 | Jun | 2023 | 0.0021114 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-06-13 16:12 | 2023-06-13 20:30 | 50 | 4:18 | P | DESGANCHE | 1 X 30 EN CORTE LINEA SE REALIZO DESGANCHE | A23061300101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 258 | 2023-06-13 | 12900 | keep | 0 | Jun | 2023 | 0.0087861 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-06-13 16:22 | 2023-06-13 16:23 | 271 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S23061300243 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-13 | 271 | keep | 0 | Jun | 2023 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
PONCE | 2023-06-13 16:40 | 2023-06-13 18:45 | 12 | 2:05 | P | CAUSAS EXTERNAS | 1 X 10 EN TRANSFORMADOR POR IMPACTO CAMION A POSTE | P23061300261 | New_Event | Damage From Public | Include | Include | Public | 125 | 2023-06-13 | 1500 | keep | 0 | Jun | 2023 | 0.0010216 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-06-13 16:40 | 2023-06-13 19:47 | 18 | 3:07 | P | ANIMAL | 1 X 30 EN CORTE LINEA CRUCE DE FASE PRIMARIA POR AVE | A23061300108 | New_Event | Animals | Include | Include | Wildlife | 187 | 2023-06-13 | 3366 | keep | 0 | Jun | 2023 | 0.0022926 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CAGUAS | 2023-06-13 16:51 | 2023-06-14 15:25 | 10 | 22:34 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE DE LINEA A CAJA PRIMARIA EN XMR | C23061300229 | New_Event | Primary Wire Break | Include | Include | Equipment | 1354 | 2023-06-13 | 13540 | keep | 0 | Jun | 2023 | 0.009222 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-06-13 16:51 | 2023-06-13 17:20 | 10 | 0:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTES SECUNDARIOS | A23061300046 | New_Event | Secondary Wire Break | Include | Include | Equipment | 29 | 2023-06-13 | 290 | keep | 0 | Jun | 2023 | 0.00019752 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-06-13 17:00 | 2023-06-13 18:51 | 6 | 1:51 | P | SECUNDARIA/DESGANCHE | SE ABRE XMR EL 13 DE JUNIO 2023 SE DESGANCHO Y SE REPARO SECUNDARIA TRASPATIO | 223000000000 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 111 | 2023-06-13 | 666 | keep | 0 | Jun | 2023 | 0.00045361 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-06-13 17:11 | 2023-06-13 18:59 | 3766 | 1:48 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | SJ-230613-50 EN DISPARO DEL 2306-01 SE LLEVO LA PORTATIL, SE DEJO INTERRUPTOR SECCIONALIZADO Y SE TRANSFIRIO LA CARGA AL 2305-04 | R23061300082 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 108 | 2023-06-13 | 406728 | keep | 0 | Jun | 2023 | 0.27702 | 0.002565 | Sustained | FALSE | FALSE | Not_TMED_Event | 3766
CANOVANAS | 2023-06-13 17:11 | 2023-06-13 18:59 | 1380 | 1:48 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | SJ-230613-50 EN DISPARO DEL 2306-01 SE LLEVO LA PORTATIL, SE DEJO INTERRUPTOR SECCIONALIZADO Y SE TRANSFIRIO LA CARGA AL 2305-04 | R23061300082 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 108 | 2023-06-13 | 149040 | keep | 0 | Jun | 2023 | 0.10151 | 0.00093991 | Sustained | FALSE | FALSE | Not_TMED_Event | 1380
SAN JUAN | 2023-06-13 17:12 | 2023-06-13 17:44 | 20 | 0:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO EN C/L PARA REPARAR BAJANTE DE LINEA @ CAJA EN C/L | S23061300250 | New_Event | Cutout Failure | Include | Include | Equipment | 32 | 2023-06-13 | 640 | keep | 0 | Jun | 2023 | 0.0004359 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-06-13 17:15 | 2023-06-14 17:05 | 8 | 23:50 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE PRIMARIO Y SE CERRO PUENTE | R23061200060 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 1430 | 2023-06-13 | 11440 | keep | 0 | Jun | 2023 | 0.0077917 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-13 17:28 | 2023-06-14 09:42 | 25 | 16:14 | P | CONDUCTOR ROTO O ABIERTO | CON GOI BY-230614-03 SE CERRO PUENTE ABIERTO EN LA SALIDA DEL ALIMENTADOR | B23061300134 | New_Event | Primary Wire Break | Include | Include | Equipment | 974 | 2023-06-13 | 24350 | keep | 0 | Jun | 2023 | 0.016585 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2023-06-13 17:33 | 2023-06-14 10:13 | 30 | 16:40 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23061300127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1000 | 2023-06-13 | 30000 | keep | 0 | Jun | 2023 | 0.020433 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-06-13 17:41 | 2023-06-13 19:32 | 70 | 1:51 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 80 EN CORTE LINEA SE ELIMINO POSTE PRIMARIO PARTIDO Y SE RETEZO LINEA PRIMARIA | A23061300128 | New_Event | Primary Pole Failure | Include | Include | Equipment | 111 | 2023-06-13 | 7770 | keep | 0 | Jun | 2023 | 0.0052921 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2023-06-13 17:43 | 2023-06-13 19:08 | 25 | 1:25 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23061300236 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2023-06-13 | 2125 | keep | 0 | Jun | 2023 | 0.0014473 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2023-06-13 17:46 | 2023-06-14 09:21 | 6 | 15:35 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | A23061300131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 935 | 2023-06-13 | 5610 | keep | 0 | Jun | 2023 | 0.0038209 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-06-13 17:46 | 2023-06-13 22:55 | 12 | 5:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A23061300130 | New_Event | Cutout Failure | Include | Include | Equipment | 309 | 2023-06-13 | 3708 | keep | 0 | Jun | 2023 | 0.0025255 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-06-13 17:58 | 2023-06-14 00:37 | 36 | 6:39 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S23061300256 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 399 | 2023-06-13 | 14364 | keep | 0 | Jun | 2023 | 0.0097833 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
ARECIBO | 2023-06-13 18:00 | 2023-06-13 23:06 | 10 | 5:06 | P | CAUSAS EXTERNAS | 1 X 30 EN CORTE DE LINEA CAMION CAUSO QUE LAS LINEAS SE CRUZARAN | A23061300134 | New_Event | Damage From Public | Include | Include | Public | 306 | 2023-06-13 | 3060 | keep | 0 | Jun | 2023 | 0.0020842 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-06-13 18:10 | 2023-06-14 05:46 | 5 | 11:36 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | R23061300303 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 696 | 2023-06-13 | 3480 | keep | 0 | Jun | 2023 | 0.0023702 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-06-13 18:17 | 2023-06-13 21:17 | 4133 | 3:00 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE DESPEGO AISLADOR DE CRUCETA MEDIANTE SWITCHING-FORM SJ-230613-01 Y SE CERRO POR CONTROL | S23061300261 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 180 | 2023-06-13 | 743940 | keep | 0 | Jun | 2023 | 0.50669 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
CANOVANAS | 2023-06-13 18:29 | 2023-06-13 21:40 | 46 | 3:11 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | R23061300088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2023-06-13 | 8786 | keep | 0 | Jun | 2023 | 0.0059841 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
PONCE | 2023-06-13 18:30 | 2023-06-13 19:21 | 5 | 0:51 | P | PARARRAYOS DEFECTUOSO | 1 SMU DE 25AMP EN SU POR PARARRAYO QUEMADO | P23061300315 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 51 | 2023-06-13 | 255 | keep | 0 | Jun | 2023 | 0.00017368 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2023-06-13 18:47 | 2023-06-13 20:27 | 40 | 1:40 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE LINEA DESCARGA ELECTRICA | M23061300181 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 100 | 2023-06-13 | 4000 | keep | 0 | Jun | 2023 | 0.0027244 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-06-13 18:53 | 2023-06-13 18:57 | 959 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE 1904-07 Y LLEVA 1901-01 LLEVA 1901-04 LLEVA 10% DEL 1901-05 | S2306130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-06-13 | 3836 | keep | 0 | Jun | 2023 | 0.0026127 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-06-13 18:53 | 2023-06-13 18:57 | 1264 | 0:04 | T | ALIMENTADOR AMARRADO | DISPARO DE 1904-07 Y LLEVA 1901-01 LLEVA 1901-04 LLEVA 10% DEL 1901-05 | S2306130000X | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-06-13 | 5056 | keep | 0 | Jun | 2023 | 0.0034436 | 0.0008609 | Momentary | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2023-06-13 18:53 | 2023-06-13 18:57 | 62 | 0:04 | P | ALIMENTADOR AMARRADO | DISPARO DE 1904-07 Y LLEVA 1901-01 LLEVA 1901-04 LLEVA 10% DEL 1901-05 | S2306130000X | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-06-13 | 248 | keep | 0 | Jun | 2023 | 0.00016891 | 4.2228e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 62
BAYAMON | 2023-06-13 18:53 | 2023-06-13 18:54 | 2956 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S23061300283 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-13 | 2956 | keep | 0 | Jun | 2023 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2023-06-13 18:59 | 2023-06-14 05:04 | 45 | 10:05 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE | B23061300153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 605 | 2023-06-13 | 27225 | keep | 0 | Jun | 2023 | 0.018543 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2023-06-13 18:59 | 2023-06-13 19:35 | 380 | 0:36 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | R23061300092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 36 | 2023-06-13 | 13680 | keep | 0 | Jun | 2023 | 0.0093174 | 0.00025882 | Sustained | FALSE | FALSE | Not_TMED_Event | 380
BAYAMON | 2023-06-13 19:03 | 2023-06-14 01:43 | 144 | 6:40 | P | NO SE REPORTO CAUSA | 1 X 15 E XMR | S23061300298 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 400 | 2023-06-13 | 57600 | keep | 0 | Jun | 2023 | 0.039231 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
SAN JUAN | 2023-06-13 19:04 | 2023-06-13 22:27 | 201 | 3:23 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S23061300300 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 203 | 2023-06-13 | 40803 | keep | 0 | Jun | 2023 | 0.027791 | 0.0001369 | Sustained | FALSE | FALSE | Not_TMED_Event | 201
HUMACAO | 2023-06-13 19:24 | 2023-06-13 20:27 | 100 | 1:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L SE REEMPLAZO PORTAFUSIBLE EVENTO TRANSFERIDO DE PONCE | P23061300345 | New_Event | Cutout Failure | Include | Include | Equipment | 63 | 2023-06-13 | 6300 | keep | 0 | Jun | 2023 | 0.0042909 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-06-13 19:26 | 2023-06-13 19:27 | 959 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300164 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 959 | keep | 0 | Jun | 2023 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-06-13 19:26 | 2023-06-13 19:27 | 1382 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300164 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 1382 | keep | 0 | Jun | 2023 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2023-06-13 19:26 | 2023-06-13 19:27 | 663 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300164 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 663 | keep | 0 | Jun | 2023 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2023-06-13 19:26 | 2023-06-13 19:27 | 580 | 0:01 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 30% POR 1708-02 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300169 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 580 | keep | 0 | Jun | 2023 | 0.00039504 | 0.00039504 | Momentary | FALSE | FALSE | Not_TMED_Event | 580
BAYAMON | 2023-06-13 19:26 | 2023-06-13 19:27 | 1715 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300169 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 1715 | keep | 0 | Jun | 2023 | 0.0011681 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2023-06-13 19:26 | 2023-06-13 19:27 | 1498 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300169 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 1498 | keep | 0 | Jun | 2023 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2023-06-13 19:26 | 2023-06-13 19:27 | 1221 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300169 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 1221 | keep | 0 | Jun | 2023 | 0.00083162 | 0.00083162 | Momentary | FALSE | FALSE | Not_TMED_Event | 1221
BAYAMON | 2023-06-13 19:26 | 2023-06-13 19:27 | 1100 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300169 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 1100 | keep | 0 | Jun | 2023 | 0.0007492 | 0.0007492 | Momentary | FALSE | FALSE | Not_TMED_Event | 1100
BAYAMON | 2023-06-13 19:26 | 2023-06-13 19:27 | 1514 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300168 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 1514 | keep | 0 | Jun | 2023 | 0.0010312 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2023-06-13 19:26 | 2023-06-13 19:27 | 1105 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300168 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 1105 | keep | 0 | Jun | 2023 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2023-06-13 19:26 | 2023-06-13 19:27 | 4176 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300165 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 4176 | keep | 0 | Jun | 2023 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2023-06-13 19:26 | 2023-06-13 19:27 | 252 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300165 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 252 | keep | 0 | Jun | 2023 | 0.00017164 | 0.00017164 | Momentary | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2023-06-13 19:26 | 2023-06-13 19:27 | 2147 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300165 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 2147 | keep | 0 | Jun | 2023 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2023-06-13 19:26 | 2023-06-13 19:27 | 2858 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300167 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 2858 | keep | 0 | Jun | 2023 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
BAYAMON | 2023-06-13 19:27 | 2023-06-13 19:50 | 15 | 0:23 | P | DESGANCHE | 2 X 40 EN C/L SE DESGANCHO | B23061300089 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 23 | 2023-06-13 | 345 | keep | 0 | Jun | 2023 | 0.00023498 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-13 19:27 | 2023-06-13 19:50 | 20 | 0:23 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO Y SE CERRO PUENTE A PRIMARIA | B23061300012 | New_Event | Primary Pole Failure | Include | Include | Equipment | 23 | 2023-06-13 | 460 | keep | 0 | Jun | 2023 | 0.0003133 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-06-13 19:41 | 2023-06-14 13:30 | 20 | 17:49 | P | CRUCETA DEFECTUOSA O AVERIADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CRUCETA PARTIDA | M23061300194 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 1069 | 2023-06-13 | 21380 | keep | 0 | Jun | 2023 | 0.014562 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-06-13 19:44 | 2023-06-13 22:17 | 400 | 2:33 | P | SOBRECARGA | 1 X 140 EN CORTE DE LINEA SOBRECARGA | M23061300195 | New_Event | Trip Due To Overload | Include | Include | Other | 153 | 2023-06-13 | 61200 | keep | 0 | Jun | 2023 | 0.041683 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
MAYAGÃœEZ | 2023-06-13 19:47 | 2023-06-14 09:10 | 1 | 13:23 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | M23061300197 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 803 | 2023-06-13 | 803 | keep | 0 | Jun | 2023 | 0.00054692 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-06-13 19:48 | 2023-06-13 19:49 | 723 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1711-02 QUE LLEVA 1711-05 | B2306130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-13 | 723 | keep | 0 | Jun | 2023 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2023-06-13 19:48 | 2023-06-13 19:49 | 1976 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO 1711-02 QUE LLEVA 1711-05 | B2306130000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-13 | 1976 | keep | 0 | Jun | 2023 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2023-06-13 19:50 | 2023-06-13 19:51 | 959 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300164 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 959 | keep | 0 | Jun | 2023 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-06-13 19:50 | 2023-06-13 19:51 | 1382 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300164 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 1382 | keep | 0 | Jun | 2023 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2023-06-13 19:50 | 2023-06-13 19:51 | 663 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300164 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 663 | keep | 0 | Jun | 2023 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2023-06-13 19:50 | 2023-06-13 19:51 | 580 | 0:01 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 30% POR 1708-02 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300169 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 580 | keep | 0 | Jun | 2023 | 0.00039504 | 0.00039504 | Momentary | FALSE | FALSE | Not_TMED_Event | 580
BAYAMON | 2023-06-13 19:50 | 2023-06-13 19:51 | 1715 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300169 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 1715 | keep | 0 | Jun | 2023 | 0.0011681 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2023-06-13 19:50 | 2023-06-13 19:51 | 1498 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300169 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 1498 | keep | 0 | Jun | 2023 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2023-06-13 19:50 | 2023-06-13 19:51 | 1221 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300169 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 1221 | keep | 0 | Jun | 2023 | 0.00083162 | 0.00083162 | Momentary | FALSE | FALSE | Not_TMED_Event | 1221
BAYAMON | 2023-06-13 19:50 | 2023-06-13 19:51 | 1100 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300169 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 1100 | keep | 0 | Jun | 2023 | 0.0007492 | 0.0007492 | Momentary | FALSE | FALSE | Not_TMED_Event | 1100
BAYAMON | 2023-06-13 19:50 | 2023-06-13 19:51 | 1514 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300168 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 1514 | keep | 0 | Jun | 2023 | 0.0010312 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2023-06-13 19:50 | 2023-06-13 19:51 | 1105 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300168 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 1105 | keep | 0 | Jun | 2023 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2023-06-13 19:50 | 2023-06-13 19:51 | 4176 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300165 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 4176 | keep | 0 | Jun | 2023 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2023-06-13 19:50 | 2023-06-13 19:51 | 252 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300165 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 252 | keep | 0 | Jun | 2023 | 0.00017164 | 0.00017164 | Momentary | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2023-06-13 19:50 | 2023-06-13 19:51 | 2147 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300165 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 2147 | keep | 0 | Jun | 2023 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2023-06-13 19:50 | 2023-06-13 19:51 | 2858 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300167 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 2858 | keep | 0 | Jun | 2023 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
BAYAMON | 2023-06-13 19:51 | 2023-06-13 20:45 | 15 | 0:54 | P | DESGANCHE | 2 X 40 EN C/L SE DESGANCHO | B23061300089 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 54 | 2023-06-13 | 810 | keep | 0 | Jun | 2023 | 0.00055169 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-06-13 19:51 | 2023-06-13 21:03 | 10 | 1:12 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR EVENTO TRANSFERIDO DE PONCE | P23061300360 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 72 | 2023-06-13 | 720 | keep | 0 | Jun | 2023 | 0.00049039 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-06-13 19:51 | 2023-06-13 20:45 | 20 | 0:54 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO Y SE CERRO PUENTE A PRIMARIA | B23061300012 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 54 | 2023-06-13 | 1080 | keep | 0 | Jun | 2023 | 0.00073558 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-13 20:15 | 2023-06-13 20:16 | 1799 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S2306130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-13 | 1799 | keep | 0 | Jun | 2023 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
CAGUAS | 2023-06-13 20:24 | 2023-06-13 20:25 | 1271 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23061300257 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-13 | 1271 | keep | 0 | Jun | 2023 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
BAYAMON | 2023-06-13 20:31 | 2023-06-14 00:43 | 139 | 4:12 | P | DESGANCHE | 1 X 50 EN C/L | B23061300197 | New_Event | Vegetation Contact | Include | Include | Vegetation | 252 | 2023-06-13 | 35028 | keep | 0 | Jun | 2023 | 0.023857 | 9.4672e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 139
ARECIBO | 2023-06-13 20:41 | 2023-06-13 22:55 | 6 | 2:14 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A23061300160 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 134 | 2023-06-13 | 804 | keep | 0 | Jun | 2023 | 0.0005476 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-06-13 20:45 | 2023-06-13 20:46 | 959 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300164 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 959 | keep | 0 | Jun | 2023 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-06-13 20:45 | 2023-06-13 20:46 | 1382 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300164 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 1382 | keep | 0 | Jun | 2023 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2023-06-13 20:45 | 2023-06-13 20:46 | 663 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300164 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 663 | keep | 0 | Jun | 2023 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2023-06-13 20:45 | 2023-06-13 20:46 | 580 | 0:01 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 30% POR 1708-02 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | S23061300169 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 580 | keep | 0 | Jun | 2023 | 0.00039504 | 0.00039504 | Momentary | FALSE | FALSE | Not_TMED_Event | 580
BAYAMON | 2023-06-13 20:45 | 2023-06-13 20:46 | 1715 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300169 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 1715 | keep | 0 | Jun | 2023 | 0.0011681 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2023-06-13 20:45 | 2023-06-13 20:46 | 1498 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300169 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 1498 | keep | 0 | Jun | 2023 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2023-06-13 20:45 | 2023-06-13 20:46 | 1221 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300169 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 1221 | keep | 0 | Jun | 2023 | 0.00083162 | 0.00083162 | Momentary | FALSE | FALSE | Not_TMED_Event | 1221
BAYAMON | 2023-06-13 20:45 | 2023-06-13 20:46 | 1100 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300169 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 1100 | keep | 0 | Jun | 2023 | 0.0007492 | 0.0007492 | Momentary | FALSE | FALSE | Not_TMED_Event | 1100
BAYAMON | 2023-06-13 20:45 | 2023-06-13 20:46 | 1514 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300168 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 1514 | keep | 0 | Jun | 2023 | 0.0010312 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2023-06-13 20:45 | 2023-06-13 20:46 | 1105 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300168 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 1105 | keep | 0 | Jun | 2023 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2023-06-13 20:45 | 2023-06-13 20:46 | 4176 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300165 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 4176 | keep | 0 | Jun | 2023 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2023-06-13 20:45 | 2023-06-13 20:46 | 252 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300165 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 252 | keep | 0 | Jun | 2023 | 0.00017164 | 0.00017164 | Momentary | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2023-06-13 20:45 | 2023-06-13 20:46 | 2147 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300165 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 2147 | keep | 0 | Jun | 2023 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2023-06-13 20:45 | 2023-06-13 20:46 | 2858 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 10000 DISPARA ERRONEAMENTE EN 480 AMPERES POR SETTING. | B23061300167 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-13 | 2858 | keep | 0 | Jun | 2023 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
BAYAMON | 2023-06-13 20:46 | 2023-06-14 07:15 | 15 | 10:29 | P | DESGANCHE | 2 X 40 EN C/L SE DESGANCHO | B23061300089 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 629 | 2023-06-13 | 9435 | keep | 0 | Jun | 2023 | 0.0064261 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-13 20:46 | 2023-06-14 13:50 | 20 | 17:04 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO Y SE CERRO PUENTE A PRIMARIA | B23061300012 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 1024 | 2023-06-13 | 20480 | keep | 0 | Jun | 2023 | 0.013949 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-13 20:57 | 2023-06-14 04:00 | 10 | 7:03 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S23061300338 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 423 | 2023-06-13 | 4230 | keep | 0 | Jun | 2023 | 0.002881 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-06-13 21:08 | 2023-06-14 08:47 | 15 | 11:39 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M23061300214 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 699 | 2023-06-13 | 10485 | keep | 0 | Jun | 2023 | 0.0071413 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-06-13 21:17 | 2023-06-14 09:27 | 9 | 12:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 8 EN XMR REPARO BAJANTE SECUNDARIO | R23061300134 | New_Event | Secondary Wire Break | Include | Include | Equipment | 730 | 2023-06-13 | 6570 | keep | 0 | Jun | 2023 | 0.0044748 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2023-06-13 21:21 | 2023-06-14 00:18 | 70 | 2:57 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23061300216 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 177 | 2023-06-13 | 12390 | keep | 0 | Jun | 2023 | 0.0084388 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2023-06-13 21:29 | 2023-06-13 21:30 | 3902 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR | C23061300266 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-06-13 | 3902 | keep | 0 | Jun | 2023 | 0.0026576 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
HUMACAO | 2023-06-13 21:30 | 2023-06-14 00:15 | 1630 | 2:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 Y 1 X 200 EN CLS MAL TIEMPOS LLUVIAS | C23061300270 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 165 | 2023-06-13 | 268950 | keep | 0 | Jun | 2023 | 0.18318 | 0.0011102 | Sustained | FALSE | FALSE | Not_TMED_Event | 1630
AGUADILLA | 2023-06-13 21:30 | 2023-06-14 01:40 | 45 | 4:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M23061300219 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 250 | 2023-06-13 | 11250 | keep | 0 | Jun | 2023 | 0.0076623 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-06-13 21:38 | 2023-06-14 16:10 | 47 | 18:32 | P | DESGANCHE | 1 X25 EN CORTE 1 X 50 EN C/L DESGANCHE | S23061300348 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1112 | 2023-06-13 | 52264 | keep | 0 | Jun | 2023 | 0.035597 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
BAYAMON | 2023-06-13 22:01 | 2023-06-14 11:22 | 179 | 13:21 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L 1 X 40 EN C/L 1 X 12 EN PM 4 | B23061300230 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 801 | 2023-06-13 | 143379 | keep | 0 | Jun | 2023 | 0.097655 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
BARRANQUITAS | 2023-06-13 22:10 | 2023-06-14 01:12 | 1246 | 3:02 | T | CAUSAS EXTERNAS | CG-230613-03 POSTE PARTIDO SE DISPARO EL BKR POR SEGURIDAD A PETICION DE HAROLD ORTIZ. SE SECCIONALIZO POSTE PARTIDO POSIBLEMENTE POR MAQUINARIA Y SE CERRO BKR ENTRANDO UN 44% 553 CLIENTES EN SERVICIO | C23061300291 | New_Event | Damage From Public | Include | Include | Public | 182 | 2023-06-13 | 226772 | keep | 0 | Jun | 2023 | 0.15445 | 0.00084864 | Sustained | FALSE | FALSE | Not_TMED_Event | 1246
GUAYAMA | 2023-06-13 22:13 | 2023-06-13 22:14 | 1945 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23061300426 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-13 | 1945 | keep | 0 | Jun | 2023 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
AGUADILLA | 2023-06-13 22:32 | 2023-06-14 10:00 | 15 | 11:28 | P | CONDUCTOR ROTO O ABIERTO | 1 X 10 EN TRANSFORMADOR SE REPARO PUENTE ABIERTO | M23061300226 | New_Event | Primary Wire Break | Include | Include | Equipment | 688 | 2023-06-13 | 10320 | keep | 0 | Jun | 2023 | 0.0070289 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-06-13 22:51 | 2023-06-14 19:47 | 10 | 20:56 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN C/L Y SE CERRO PUENTE DE LINEA A CAJA Y SE REEMPLAZO PORTA FUSIBLE. | S23061300354 | New_Event | Primary Wire Break | Include | Include | Equipment | 1256 | 2023-06-13 | 12560 | keep | 0 | Jun | 2023 | 0.0085546 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-06-13 23:04 | 2023-06-14 11:14 | 4 | 12:10 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23061300295 | New_Event | Vegetation Contact | Include | Include | Vegetation | 730 | 2023-06-13 | 2920 | keep | 0 | Jun | 2023 | 0.0019888 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2023-06-13 23:32 | 2023-06-14 08:10 | 80 | 8:38 | P | CONDUCTOR ROTO O ABIERTO | NEUTRAL COMUN EN EL PISO 3 X 65 EN CORTE DE LINEA | P23061300434 | New_Event | Primary Wire Break | Include | Include | Equipment | 518 | 2023-06-13 | 41440 | keep | 0 | Jun | 2023 | 0.028225 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2023-06-13 23:38 | 2023-06-14 02:08 | 90 | 2:30 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA | R23061300178 | New_Event | Primary Wire Break | Include | Include | Equipment | 150 | 2023-06-13 | 13500 | keep | 0 | Jun | 2023 | 0.0091948 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
AGUADILLA | 2023-06-14 00:09 | 2023-06-14 13:45 | 10 | 13:36 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23061400108 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 816 | 2023-06-14 | 8160 | keep | 0 | Jun | 2023 | 0.0055577 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-06-14 00:18 | 2023-06-14 04:54 | 2 | 4:36 | P | DESGANCHE | 1 X80 Y DESGACHE | S23061400001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 276 | 2023-06-14 | 552 | keep | 0 | Jun | 2023 | 0.00037596 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-06-14 00:30 | 2023-06-14 09:28 | 13 | 8:58 | P | DESGANCHE | DESGANCHE 1 X 30 EN C/L | B23061400001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 538 | 2023-06-14 | 6994 | keep | 0 | Jun | 2023 | 0.0047636 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CAGUAS | 2023-06-14 00:32 | 2023-06-14 00:33 | 853 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | C23061400003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-14 | 853 | keep | 0 | Jun | 2023 | 0.00058097 | 0.00058097 | Momentary | FALSE | FALSE | Not_TMED_Event | 853
BARRANQUITAS | 2023-06-14 01:12 | 2023-06-14 18:15 | 693 | 17:03 | P | CAUSAS EXTERNAS | CG-230613-03 SE REEMPLAZO POSTE PARTIDO 100% EN SERVICIO RELACIONADO A EVENTO C23061300291 | C23061400010 | Partial_restoration | Damage From Public | Include | Include | Public | 1023 | 2023-06-14 | 708939 | keep | 0 | Jun | 2023 | 0.48286 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-14 01:59 | 2023-06-14 02:00 | 2402 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2306140000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-14 | 2402 | keep | 0 | Jun | 2023 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
FAJARDO | 2023-06-14 02:29 | 2023-06-14 03:09 | 3003 | 0:40 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SJ-230614-50 DISPARO DE BKR NO CIERRA POR CONTROL, SE DEJO TRANSFERIDO AL 2002-02 SE CERRO N/O FRENTE A LA SUBESTACION | R23061400010 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 40 | 2023-06-14 | 120120 | keep | 0 | Jun | 2023 | 0.081813 | 0.0020453 | Sustained | FALSE | FALSE | Not_TMED_Event | 3003
CAGUAS | 2023-06-14 03:03 | 2023-06-14 03:04 | 861 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE BKR 3103-02 LLEVA 50% DEL 3102-01 (861 CLTS) | C2306140000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-14 | 861 | keep | 0 | Jun | 2023 | 0.00058642 | 0.00058642 | Momentary | FALSE | FALSE | Not_TMED_Event | 861
CAGUAS | 2023-06-14 03:03 | 2023-06-14 03:04 | 1922 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR LLEVA 50% DEL 3102-01 (861 CLTS) | C2306140000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-14 | 1922 | keep | 0 | Jun | 2023 | 0.0013091 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
VEGA BAJA | 2023-06-14 03:17 | 2023-06-14 03:19 | 215 | 0:02 | T | DESGANCHE | DISPARO CERRADO POR CONTROL | B2306140000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-06-14 | 430 | keep | 0 | Jun | 2023 | 0.00029287 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2023-06-14 03:19 | 2023-06-14 07:47 | 49 | 4:28 | P | DESGANCHE | DESGANCHE 1 X 100 EN C/L | B23061400006 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 268 | 2023-06-14 | 13132 | keep | 0 | Jun | 2023 | 0.0089441 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
SAN JUAN | 2023-06-14 03:36 | 2023-06-14 14:15 | 40 | 10:39 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S23061400005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 639 | 2023-06-14 | 25560 | keep | 0 | Jun | 2023 | 0.017409 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-06-14 04:30 | 2023-06-14 08:00 | 150 | 3:30 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | C23061400014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2023-06-14 | 31500 | keep | 0 | Jun | 2023 | 0.021455 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2023-06-14 04:43 | 2023-06-14 08:30 | 407 | 3:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ENCONTRO PUENTE ABIERTO Y CAJA PRIMARIA QUEMADA | C23061400016 | New_Event | Cutout Failure | Include | Include | Equipment | 227 | 2023-06-14 | 92389 | keep | 0 | Jun | 2023 | 0.062926 | 0.00027721 | Sustained | FALSE | FALSE | Not_TMED_Event | 407
FAJARDO | 2023-06-14 05:02 | 2023-06-14 05:03 | 4098 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | R23061400013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-14 | 4098 | keep | 0 | Jun | 2023 | 0.0027911 | 0.0027911 | Momentary | FALSE | FALSE | Not_TMED_Event | 4098
GUAYAMA | 2023-06-14 05:42 | 2023-06-14 11:39 | 30 | 5:57 | P | CONDUCTOR ROTO O ABIERTO | SE RECONECTO PUENTE SAFADO EN CORTE DE LINEA | P23061400017 | New_Event | Primary Wire Break | Include | Include | Equipment | 357 | 2023-06-14 | 10710 | keep | 0 | Jun | 2023 | 0.0072945 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-06-14 05:46 | 2023-06-14 05:47 | 4154 | 0:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | R23061400015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-06-14 | 4154 | keep | 0 | Jun | 2023 | 0.0028293 | 0.0028293 | Momentary | FALSE | FALSE | Not_TMED_Event | 4154
CANOVANAS | 2023-06-14 05:47 | 2023-06-14 05:51 | 5 | 0:04 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | R23061300303 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 4 | 2023-06-14 | 20 | keep | 0 | Jun | 2023 | 1.3622e-05 | 3.4055e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-06-14 05:51 | 2023-06-14 08:38 | 4154 | 2:47 | T | DESGANCHE | SE SECCIONALIZO EL ALIMENTADOR | R23061400017 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 167 | 2023-06-14 | 693718 | keep | 0 | Jun | 2023 | 0.47249 | 0.0028293 | Sustained | FALSE | FALSE | Not_TMED_Event | 4154
BAYAMON | 2023-06-14 05:58 | 2023-06-14 05:59 | 4431 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2306140000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-14 | 4431 | keep | 0 | Jun | 2023 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
SAN JUAN | 2023-06-14 06:03 | 2023-06-14 14:31 | 36 | 8:28 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | S23061400008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 508 | 2023-06-14 | 18288 | keep | 0 | Jun | 2023 | 0.012456 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CAGUAS | 2023-06-14 06:03 | 2023-06-14 12:30 | 180 | 6:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MA TIEMPO VIENTOS | C23061400023 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 387 | 2023-06-14 | 69660 | keep | 0 | Jun | 2023 | 0.047445 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
VEGA BAJA | 2023-06-14 06:12 | 2023-06-14 08:15 | 40 | 2:03 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA IGUANA CRUZO LINEAS | A23061400002 | New_Event | Animals | Include | Include | Wildlife | 123 | 2023-06-14 | 4920 | keep | 0 | Jun | 2023 | 0.003351 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-06-14 07:01 | 2023-06-14 07:02 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2306140000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-14 | 45 | keep | 0 | Jun | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-06-14 07:10 | 2023-06-14 16:00 | 20 | 8:50 | P | CABLE SOTERRADO AVERIADO | 2 RBA DE 50 AMPS EN SU-1 SE CERRO N/O A TRAVES DEL T-4 AVERIA NUEVA DE SU-1 AL T-5 | S23061400012 | New_Event | UG Cable Fault | Include | Include | Equipment | 530 | 2023-06-14 | 10600 | keep | 0 | Jun | 2023 | 0.0072196 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-06-14 07:15 | 2023-06-14 07:16 | 4456 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S2306140000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-14 | 4456 | keep | 0 | Jun | 2023 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
CAGUAS | 2023-06-14 07:15 | 2023-06-14 14:54 | 100 | 7:39 | P | ANIMAL | 1 X 140 EN C/L CRUCE X AVE | C23061400048 | New_Event | Animals | Include | Include | Wildlife | 459 | 2023-06-14 | 45900 | keep | 0 | Jun | 2023 | 0.031262 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-06-14 07:18 | 2023-06-14 10:48 | 9 | 3:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A23061400006 | New_Event | Cutout Failure | Include | Include | Equipment | 210 | 2023-06-14 | 1890 | keep | 0 | Jun | 2023 | 0.0012873 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2023-06-14 07:32 | 2023-06-14 11:40 | 2 | 4:08 | P | MAL TIEMPO/RAYOS | 1 X 8 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | P23061400058 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 248 | 2023-06-14 | 496 | keep | 0 | Jun | 2023 | 0.00033782 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2023-06-14 07:33 | 2023-06-14 10:00 | 103 | 2:27 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABREN PUENTES PRIMARIOS PARA SECCIONALIZAR POSTE PRIMARIO PARTIDO 2 X 65 EN CORTE DE LINEA | P23061400059 | New_Event | Primary Pole Failure | Include | Include | Equipment | 147 | 2023-06-14 | 15141 | keep | 0 | Jun | 2023 | 0.010312 | 7.0153e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 103
CANOVANAS | 2023-06-14 07:38 | 2023-06-14 13:05 | 30 | 5:27 | P | DESGANCHE | 1 X 30 EN C/L | R23061400026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 327 | 2023-06-14 | 9810 | keep | 0 | Jun | 2023 | 0.0066815 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-06-14 07:40 | 2023-06-14 21:18 | 12 | 13:38 | P | DESGANCHE | 1 X 25 EN XMR Y 30 EN C/L DESGANCHE | C23061400058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 818 | 2023-06-14 | 9816 | keep | 0 | Jun | 2023 | 0.0066856 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-06-14 07:41 | 2023-06-14 07:42 | 6136 | 0:01 | T | OTRAS CAUSAS | SE ABRIO INTERRUPTOR POR CONTROL COMO PARTE DE LA VIA LIBRE D2023-4344 REALIZAR OPERACION DEL PASO 2 NO REPRESENTA SEGURIDAD POR LO INCOMODO QUE QUEDAN INFORMA CRUZ MARTINEZ | B2306140000X | New_Event | Other Causes | Include | Include | Other | 1 | 2023-06-14 | 6136 | keep | 0 | Jun | 2023 | 0.0041792 | 0.0041792 | Momentary | FALSE | FALSE | Not_TMED_Event | 6136
SAN JUAN | 2023-06-14 07:41 | 2023-06-14 12:20 | 75 | 4:39 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA EVENTO TRANSFERIDO DE PONCE | P23061400063 | New_Event | Primary Wire Break | Include | Include | Equipment | 279 | 2023-06-14 | 20925 | keep | 0 | Jun | 2023 | 0.014252 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
GUAYAMA | 2023-06-14 07:42 | 2023-06-14 09:45 | 60 | 2:03 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA SE ELIMINO PARARRAYO | P23061400064 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 123 | 2023-06-14 | 7380 | keep | 0 | Jun | 2023 | 0.0050265 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-06-14 07:47 | 2023-06-14 13:05 | 15 | 5:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE ZAFADO DE LINEA A CAJA DE TRANSFORMADOR | M23061400015 | New_Event | Secondary Wire Break | Include | Include | Equipment | 318 | 2023-06-14 | 4770 | keep | 0 | Jun | 2023 | 0.0032488 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-06-14 07:49 | 2023-06-14 14:00 | 278 | 6:11 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C23061400061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 371 | 2023-06-14 | 103138 | keep | 0 | Jun | 2023 | 0.070247 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
GUAYAMA | 2023-06-14 07:52 | 2023-06-14 17:00 | 20 | 9:08 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO NEUTRAL PRIMARIO | P23061400071 | New_Event | Primary Wire Break | Include | Include | Equipment | 548 | 2023-06-14 | 10960 | keep | 0 | Jun | 2023 | 0.0074648 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2023-06-14 08:00 | 2023-06-14 13:40 | 52 | 5:40 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN CORTE DE LINEA FASE CRUZADA | P23061400078 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 340 | 2023-06-14 | 17680 | keep | 0 | Jun | 2023 | 0.012042 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
SAN JUAN | 2023-06-14 08:03 | 2023-06-15 12:14 | 10 | 28:11 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR DESGANCHE | S23061400023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1691 | 2023-06-14 | 16910 | keep | 0 | Jun | 2023 | 0.011517 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-06-14 08:03 | 2023-06-14 14:52 | 10 | 6:49 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE DESGANCHO Y SE REPARO SECUNDARIA | S23061400024 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 409 | 2023-06-14 | 4090 | keep | 0 | Jun | 2023 | 0.0027857 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-06-14 08:03 | 2023-06-14 11:27 | 10 | 3:24 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | POSTE SECUNDARIO PARTIDO SE REPARO LINEA SECUNDARIA Y SE RELOCALIZO | A23061400007 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 204 | 2023-06-14 | 2040 | keep | 0 | Jun | 2023 | 0.0013894 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-06-14 08:06 | 2023-06-14 17:03 | 19 | 8:57 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO DE LINEA A CAJA | C23061400066 | New_Event | Primary Wire Break | Include | Include | Equipment | 537 | 2023-06-14 | 10203 | keep | 0 | Jun | 2023 | 0.0069492 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2023-06-14 08:13 | 2023-06-15 10:37 | 30 | 26:24 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE LINEA | S23061400027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1584 | 2023-06-14 | 47520 | keep | 0 | Jun | 2023 | 0.032366 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-06-14 08:17 | 2023-06-14 08:18 | 1352 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23061400021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-14 | 1352 | keep | 0 | Jun | 2023 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2023-06-14 08:24 | 2023-06-14 14:30 | 80 | 6:06 | P | DESGANCHE | 1 X 40 Y 1 X 30 EN CORTES DE LINEA DISTINTOS SE RETIRO RAMAS SOBRE LAS LINEAS | M23061400023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 366 | 2023-06-14 | 29280 | keep | 0 | Jun | 2023 | 0.019942 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-06-14 08:25 | 2023-06-15 01:14 | 68 | 16:49 | P | DESGANCHE | 1 X 100 C /L DESGANCHE | S23061400274 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1009 | 2023-06-14 | 68612 | keep | 0 | Jun | 2023 | 0.046731 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
PONCE | 2023-06-14 08:25 | 2023-06-14 11:04 | 33 | 2:39 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA PAJARO CRUZO FASE | P23061400102 | New_Event | Animals | Include | Include | Wildlife | 159 | 2023-06-14 | 5247 | keep | 0 | Jun | 2023 | 0.0035737 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
PONCE | 2023-06-14 08:26 | 2023-06-14 13:05 | 21 | 4:39 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA ANIMAL | P23061400104 | New_Event | Animals | Include | Include | Wildlife | 279 | 2023-06-14 | 5859 | keep | 0 | Jun | 2023 | 0.0039905 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
FAJARDO | 2023-06-14 08:29 | 2023-06-14 16:20 | 14 | 7:51 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE COMPAÃ‘IA WRIGHT TREE SERVICE | R23061400034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 471 | 2023-06-14 | 6594 | keep | 0 | Jun | 2023 | 0.0044911 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
HUMACAO | 2023-06-14 08:30 | 2023-06-14 09:38 | 1427 | 1:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO C/L TOTAL PARA TRABAJAR REEMPLAZO DE CAJA PRIMARIA QUEMADA, BAJANTE QUEMADO. | C23061400016 | Additional_clients | Cutout Failure | Include | Include | Equipment | 68 | 2023-06-14 | 97036 | keep | 0 | Jun | 2023 | 0.066091 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-06-14 08:30 | 2023-06-14 19:32 | 70 | 11:02 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23061400069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 662 | 2023-06-14 | 46340 | keep | 0 | Jun | 2023 | 0.031562 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2023-06-14 08:32 | 2023-06-14 15:22 | 100 | 6:50 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23061400070 | New_Event | Animals | Include | Include | Wildlife | 410 | 2023-06-14 | 41000 | keep | 0 | Jun | 2023 | 0.027925 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-06-14 08:36 | 2023-06-14 12:35 | 1 | 3:59 | P | ANIMAL | 2 X 20 EN MONTURA 2 X 40 EN SU-2 CRUCE POR AVE | B23061400111 | New_Event | Animals | Include | Include | Wildlife | 239 | 2023-06-14 | 239 | keep | 0 | Jun | 2023 | 0.00016278 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-06-14 08:38 | 2023-06-14 10:16 | 2077 | 1:38 | P | DESGANCHE | SE DESGANCHO Y CERRO PUENTE SJ-230614-51 | R23061400017 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 98 | 2023-06-14 | 203546 | keep | 0 | Jun | 2023 | 0.13863 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-06-14 08:40 | 2023-06-14 09:45 | 3 | 1:05 | P | PROBLEMA DEL CLIENTE | SE ABRE EN VACUM SWITCH PARA PODER CONECTAR CABLE Y REGRESAR SERVICIO | P23061400121 | New_Event | Customer-Related Interruption | Include | Include | Public | 65 | 2023-06-14 | 195 | keep | 0 | Jun | 2023 | 0.00013281 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-06-14 08:43 | 2023-06-14 08:44 | 2708 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23061400050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-14 | 2708 | keep | 0 | Jun | 2023 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
BARRANQUITAS | 2023-06-14 08:44 | 2023-06-14 09:45 | 25 | 1:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO EVENTO TRANSFERIDO DE PONCE | P23061400123 | New_Event | Secondary Wire Break | Include | Include | Equipment | 61 | 2023-06-14 | 1525 | keep | 0 | Jun | 2023 | 0.0010387 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2023-06-14 08:44 | 2023-06-14 08:45 | 3332 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2306140000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-14 | 3332 | keep | 0 | Jun | 2023 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
BAYAMON | 2023-06-14 08:48 | 2023-06-14 13:01 | 63 | 4:13 | P | NO SE REPORTO CAUSA | 1 X 25 EN SU-4 | B23061400039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 253 | 2023-06-14 | 15939 | keep | 0 | Jun | 2023 | 0.010856 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
CANOVANAS | 2023-06-14 08:52 | 2023-06-14 08:54 | 2106 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CERRADO X CONTROL | R2306140000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-14 | 4212 | keep | 0 | Jun | 2023 | 0.0028688 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
SAN JUAN | 2023-06-14 08:55 | 2023-06-15 12:18 | 6 | 27:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIAS | S23061400045 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1643 | 2023-06-14 | 9858 | keep | 0 | Jun | 2023 | 0.0067142 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-06-14 09:08 | 2023-06-14 09:09 | 3597 | 0:01 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL | B23061400051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-06-14 | 3597 | keep | 0 | Jun | 2023 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2023-06-14 09:09 | 2023-06-14 16:23 | 30 | 7:14 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23061400203 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 434 | 2023-06-14 | 13020 | keep | 0 | Jun | 2023 | 0.0088679 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2023-06-14 09:14 | 2023-06-14 12:48 | 125 | 3:34 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE HIZO DESGANCHE | P23061400156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 214 | 2023-06-14 | 26750 | keep | 0 | Jun | 2023 | 0.018219 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
VEGA BAJA | 2023-06-14 09:31 | 2023-06-14 14:29 | 15 | 4:58 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE REPARARON LINEAS SECUNDARIAS CRUZADAS | A23061400056 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 298 | 2023-06-14 | 4470 | keep | 0 | Jun | 2023 | 0.0030445 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-06-14 09:34 | 2023-06-14 11:35 | 11 | 2:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO TRAMO LINEA SECUNDARIA | S23061400051 | New_Event | Secondary Wire Break | Include | Include | Equipment | 121 | 2023-06-14 | 1331 | keep | 0 | Jun | 2023 | 0.00090654 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BARRANQUITAS | 2023-06-14 09:39 | 2023-06-14 15:19 | 20 | 5:40 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE EVENTO TRANSFERIDO DE PONCE | P23061400180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 340 | 2023-06-14 | 6800 | keep | 0 | Jun | 2023 | 0.0046314 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-06-14 09:42 | 2023-06-14 11:07 | 74 | 1:25 | T | CONDUCTOR ROTO O ABIERTO | CON GOI BY-230614-03 SE CERRO PUENTE ABIERTO | B23061300134 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 85 | 2023-06-14 | 6290 | keep | 0 | Jun | 2023 | 0.0042841 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-06-14 09:49 | 2023-06-14 18:48 | 80 | 8:59 | P | ANIMAL | 1 X 65 Y 1 X 50 EN C/L CRUCE X AVE | C23061400095 | New_Event | Animals | Include | Include | Wildlife | 539 | 2023-06-14 | 43120 | keep | 0 | Jun | 2023 | 0.029369 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-06-14 10:00 | 2023-06-14 11:15 | 16 | 1:15 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 25KVA POR 37.5KVA | S23061400061 | New_Event | Service Transformer Failure | Include | Include | Equipment | 75 | 2023-06-14 | 1200 | keep | 0 | Jun | 2023 | 0.00081731 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
PONCE | 2023-06-14 10:00 | 2023-06-14 20:30 | 50 | 10:30 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO PARTIDO | P23061400209 | New_Event | Primary Pole Failure | Include | Include | Equipment | 630 | 2023-06-14 | 31500 | keep | 0 | Jun | 2023 | 0.021455 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-06-14 10:06 | 2023-06-15 11:55 | 1 | 25:49 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50KVA | A23061400099 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1549 | 2023-06-14 | 1549 | keep | 0 | Jun | 2023 | 0.001055 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-06-14 10:08 | 2023-06-14 13:25 | 250 | 3:17 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23061400060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2023-06-14 | 49250 | keep | 0 | Jun | 2023 | 0.033544 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2023-06-14 10:09 | 2023-06-14 13:00 | 390 | 2:51 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN C/L Y AISLADOR | S23061400065 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 171 | 2023-06-14 | 66690 | keep | 0 | Jun | 2023 | 0.045422 | 0.00026563 | Sustained | FALSE | FALSE | Not_TMED_Event | 390
YAUCO | 2023-06-14 10:10 | 2023-06-14 10:30 | 1 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE ZAFADO | M23061300225 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-06-14 | 20 | keep | 0 | Jun | 2023 | 1.3622e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-06-14 10:10 | 2023-06-14 11:55 | 5 | 1:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | A23061300154 | New_Event | Secondary Wire Break | Include | Include | Equipment | 105 | 2023-06-14 | 525 | keep | 0 | Jun | 2023 | 0.00035758 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-06-14 10:16 | 2023-06-14 12:10 | 5 | 1:54 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | R23061300303 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 114 | 2023-06-14 | 570 | keep | 0 | Jun | 2023 | 0.00038822 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-06-14 10:23 | 2023-06-15 08:19 | 1 | 21:56 | P | ANIMAL | 1 X 20 EN XMR CRUCE X AVE | C23061400104 | New_Event | Animals | Include | Include | Wildlife | 1316 | 2023-06-14 | 1316 | keep | 0 | Jun | 2023 | 0.00089632 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-06-14 10:42 | 2023-06-14 11:04 | 1 | 0:22 | P | PROBLEMA DEL CLIENTE | 1 X 65 EN TRANSCLOSURE POR CONTAMINACION EN SUBESTACION PRIVADA | B23061400078 | New_Event | Customer-Related Interruption | Include | Include | Public | 22 | 2023-06-14 | 22 | keep | 0 | Jun | 2023 | 1.4984e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-06-14 10:49 | 2023-06-14 13:10 | 200 | 2:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23061400070 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 141 | 2023-06-14 | 28200 | keep | 0 | Jun | 2023 | 0.019207 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
GUAYAMA | 2023-06-14 10:51 | 2023-06-14 14:50 | 1 | 3:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN C/L MAL TIEMPO VIENTOS | P23061400222 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 239 | 2023-06-14 | 239 | keep | 0 | Jun | 2023 | 0.00016278 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-06-14 10:55 | 2023-06-14 13:25 | 2 | 2:30 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS | A23061400044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2023-06-14 | 300 | keep | 0 | Jun | 2023 | 0.00020433 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2023-06-14 11:00 | 2023-06-14 12:35 | 25 | 1:35 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | P23061400233 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2023-06-14 | 2375 | keep | 0 | Jun | 2023 | 0.0016176 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2023-06-14 11:17 | 2023-06-15 13:05 | 6 | 25:48 | P | TERMINACION SOTERRADA AVERIADA | 1 X 15 EN RISER REEMPLAZO 2 PISTOLAS EN EL T - 10 | C23061400120 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 1548 | 2023-06-14 | 9288 | keep | 0 | Jun | 2023 | 0.006326 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-06-14 11:18 | 2023-06-14 16:48 | 60 | 5:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA PRIMARIA | S23061400081 | New_Event | Cutout Failure | Include | Include | Equipment | 330 | 2023-06-14 | 19800 | keep | 0 | Jun | 2023 | 0.013486 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-06-14 11:18 | 2023-06-14 12:12 | 1 | 0:54 | P | ANIMAL | 1 X 25 EN C/L CRUCE POR AVE | B23061400240 | New_Event | Animals | Include | Include | Wildlife | 54 | 2023-06-14 | 54 | keep | 0 | Jun | 2023 | 3.6779e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-06-14 11:24 | 2023-06-14 16:50 | 150 | 5:26 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | A23061400050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 326 | 2023-06-14 | 48900 | keep | 0 | Jun | 2023 | 0.033306 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-06-14 11:25 | 2023-06-14 14:59 | 252 | 3:34 | P | DESGANCHE | 1 X 100 EN C/L 2 X 65 EN C/L DESGACHE | S23061400083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 214 | 2023-06-14 | 53928 | keep | 0 | Jun | 2023 | 0.03673 | 0.00017164 | Sustained | FALSE | FALSE | Not_TMED_Event | 252
VEGA BAJA | 2023-06-14 11:31 | 2023-06-14 14:02 | 1 | 2:31 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23061400094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2023-06-14 | 151 | keep | 0 | Jun | 2023 | 0.00010285 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-06-14 11:35 | 2023-06-14 11:59 | 1 | 0:24 | P | ANIMAL | 1 X 10 EN XMR Y 1 X 15 EN RISER CRUCE X RATON | R23061400067 | New_Event | Animals | Include | Include | Wildlife | 24 | 2023-06-14 | 24 | keep | 0 | Jun | 2023 | 1.6346e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-06-14 11:35 | 2023-06-14 13:15 | 20 | 1:40 | P | MAL TIEMPO/RAYOS | 1 X 30 EN RISER DESCARGAS ELECTRICAS | M23061400090 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 100 | 2023-06-14 | 2000 | keep | 0 | Jun | 2023 | 0.0013622 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-06-14 11:44 | 2023-06-14 15:00 | 4 | 3:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN CORTE DE LINEA | M23061400094 | New_Event | Cutout Failure | Include | Include | Equipment | 196 | 2023-06-14 | 784 | keep | 0 | Jun | 2023 | 0.00053398 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2023-06-14 11:50 | 2023-06-14 15:00 | 10 | 3:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 20 EN XMR SE REPARO SECUNDARIA | P23061400267 | New_Event | Secondary Wire Break | Include | Include | Equipment | 190 | 2023-06-14 | 1900 | keep | 0 | Jun | 2023 | 0.0012941 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2023-06-14 11:51 | 2023-06-14 17:47 | 60 | 5:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23061400055 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 356 | 2023-06-14 | 21360 | keep | 0 | Jun | 2023 | 0.014548 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2023-06-14 11:59 | 2023-06-14 14:54 | 100 | 2:55 | P | DESGANCHE | (1 X 30) (1 X 65) Y (1 X 80) EN CORTES DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23061400057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2023-06-14 | 17500 | keep | 0 | Jun | 2023 | 0.011919 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-06-14 12:03 | 2023-06-14 16:15 | 72 | 4:12 | P | DESGANCHE | 1 X 80 C/L DESGANCHE | S23061400093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 252 | 2023-06-14 | 18144 | keep | 0 | Jun | 2023 | 0.012358 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
SAN JUAN | 2023-06-14 12:06 | 2023-06-14 15:25 | 233 | 3:19 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23061400097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2023-06-14 | 46367 | keep | 0 | Jun | 2023 | 0.03158 | 0.0001587 | Sustained | FALSE | FALSE | Not_TMED_Event | 233
BAYAMON | 2023-06-14 12:11 | 2023-06-14 14:56 | 10 | 2:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23061400101 | New_Event | Secondary Wire Break | Include | Include | Equipment | 165 | 2023-06-14 | 1650 | keep | 0 | Jun | 2023 | 0.0011238 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-06-14 12:12 | 2023-06-14 13:57 | 80 | 1:45 | P | DESGANCHE | 1 X 80 EN C/L | R23061400073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2023-06-14 | 8400 | keep | 0 | Jun | 2023 | 0.0057212 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-06-14 12:23 | 2023-06-14 14:30 | 125 | 2:07 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA EVENTO TRANSFERIDO DE PONCE | P23061400286 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2023-06-14 | 15875 | keep | 0 | Jun | 2023 | 0.010812 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BARRANQUITAS | 2023-06-14 12:23 | 2023-06-14 13:52 | 574 | 1:29 | P | ANIMAL | 1 X 200 EN CONVERTIDOR CRUCE X AVE | C23061400133 | New_Event | Animals | Include | Include | Wildlife | 89 | 2023-06-14 | 51086 | keep | 0 | Jun | 2023 | 0.034794 | 0.00039095 | Sustained | FALSE | FALSE | Not_TMED_Event | 574
CAGUAS | 2023-06-14 12:43 | 2023-06-14 13:19 | 58 | 0:36 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | C23061400138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 36 | 2023-06-14 | 2088 | keep | 0 | Jun | 2023 | 0.0014221 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
PONCE | 2023-06-14 12:44 | 2023-06-14 14:50 | 50 | 2:06 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P23061400300 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2023-06-14 | 6300 | keep | 0 | Jun | 2023 | 0.0042909 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-06-14 12:46 | 2023-06-14 20:18 | 203 | 7:32 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE. | S23061400103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 452 | 2023-06-14 | 91756 | keep | 0 | Jun | 2023 | 0.062495 | 0.00013826 | Sustained | FALSE | FALSE | Not_TMED_Event | 203
GUAYAMA | 2023-06-14 12:49 | 2023-06-14 15:00 | 1 | 2:11 | P | DESGANCHE | 1 X 20 EN XMR DESGANCHE | P23061400305 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2023-06-14 | 131 | keep | 0 | Jun | 2023 | 8.9224e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-06-14 12:59 | 2023-06-14 16:17 | 41 | 3:18 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23061400109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2023-06-14 | 8118 | keep | 0 | Jun | 2023 | 0.0055291 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
CAGUAS | 2023-06-14 13:19 | 2023-06-14 13:20 | 1271 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | C23061400149 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-06-14 | 1271 | keep | 0 | Jun | 2023 | 0.00086567 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-06-14 13:20 | 2023-06-14 13:27 | 58 | 0:07 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | C23061400138 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 7 | 2023-06-14 | 406 | keep | 0 | Jun | 2023 | 0.00027652 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
SAN JUAN | 2023-06-14 13:25 | 2023-06-14 13:26 | 1032 | 0:01 | P | OTRAS CAUSAS | SE ENERGIZO PORTATIL #22 Y SE ABRIO N/O 1348-08 Y 1424-08 PARA ENERGIZAR ALIMENTADOR LLEVA 80% DE SU CARGA NOTA: INTERRUPCION NO VA POR VIA LIBRE | S23061400000 | New_Event | Other Causes | Include | Include | Other | 1 | 2023-06-14 | 1032 | keep | 0 | Jun | 2023 | 0.00070289 | 0.00070289 | Momentary | FALSE | FALSE | Not_TMED_Event | 1032
HUMACAO | 2023-06-14 13:25 | 2023-06-14 17:17 | 12 | 3:52 | P | SECUNDARIA/DESGANCHE | 1 X 50 EN XMR SE REPARO SECUNDARIA Y DESGANCHE SECUNDARIO | C23061400155 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 232 | 2023-06-14 | 2784 | keep | 0 | Jun | 2023 | 0.0018962 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-06-14 13:27 | 2023-06-14 13:28 | 1271 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | C23061400157 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-06-14 | 1271 | keep | 0 | Jun | 2023 | 0.00086567 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-06-14 13:28 | 2023-06-14 22:05 | 58 | 8:37 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | C23061400138 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 517 | 2023-06-14 | 29986 | keep | 0 | Jun | 2023 | 0.020423 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
FAJARDO | 2023-06-14 13:29 | 2023-06-14 15:03 | 56 | 1:34 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | R23061400088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2023-06-14 | 5264 | keep | 0 | Jun | 2023 | 0.0035853 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
MAYAGÃœEZ | 2023-06-14 13:33 | 2023-06-14 17:37 | 15 | 4:04 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA IGUANA CRUZO LINEAS | P23061400333 | New_Event | Animals | Include | Include | Wildlife | 244 | 2023-06-14 | 3660 | keep | 0 | Jun | 2023 | 0.0024928 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-06-14 13:42 | 2023-06-14 16:56 | 43 | 3:14 | P | ANIMAL | 1 X 100 EN C/L AVE | B23061400116 | New_Event | Animals | Include | Include | Wildlife | 194 | 2023-06-14 | 8342 | keep | 0 | Jun | 2023 | 0.0056817 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
SAN JUAN | 2023-06-14 13:45 | 2023-06-14 13:46 | 1251 | 0:01 | T | OTRAS CAUSAS | SE ENERGIZO PORTATIL #22 Y SE ABRIO N/O 1348-07 Y 1424-08 EN SU-3909 PARA ENERGIZAR ALIMENTADOR NOTA: INTERRUPCION NO VA POR VIA LIBRE | S23061400000 | New_Event | Other Causes | Include | Include | Other | 1 | 2023-06-14 | 1251 | keep | 0 | Jun | 2023 | 0.00085205 | 0.00085205 | Momentary | FALSE | FALSE | Not_TMED_Event | 1251
SAN JUAN | 2023-06-14 13:45 | 2023-06-14 13:46 | 278 | 0:01 | T | OTRAS CAUSAS | SE ENERGIZO PORTATIL #22 Y SE ABRIO N/O 1348-07 Y 1424-08 EN SU-3909 PARA ENERGIZAR ALIMENTADOR NOTA: INTERRUPCION NO VA POR VIA LIBRE | S23061400000 | New_Event | Other Causes | Include | Include | Other | 1 | 2023-06-14 | 278 | keep | 0 | Jun | 2023 | 0.00018934 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
UTUADO | 2023-06-14 13:56 | 2023-06-15 10:53 | 2 | 20:57 | P | DESGANCHE | 1 X 10 EN CORTE DE LINEA SE RETIRARON BAMBUS | P23061400351 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1257 | 2023-06-14 | 2514 | keep | 0 | Jun | 2023 | 0.0017123 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-06-14 14:25 | 2023-06-14 17:00 | 878 | 2:35 | T | CONDUCTOR ARRIADO O CRUZADO | SE LLEVO TIGUERO CON VARETA A SU SITIO Y SE CERRO POR SCADA | B23061400135 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 155 | 2023-06-14 | 136090 | keep | 0 | Jun | 2023 | 0.09269 | 0.000598 | Sustained | FALSE | FALSE | Not_TMED_Event | 878
SAN JUAN | 2023-06-14 15:08 | 2023-06-14 17:54 | 153 | 2:46 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | S23061400139 | New_Event | Primary Wire Break | Include | Include | Equipment | 166 | 2023-06-14 | 25398 | keep | 0 | Jun | 2023 | 0.017298 | 0.00010421 | Sustained | FALSE | FALSE | Not_TMED_Event | 153
CANOVANAS | 2023-06-14 15:11 | 2023-06-14 16:53 | 11 | 1:42 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE DE BAMBUA TOCANDO BUSHING PRIMARIO EVENTO TRANSFERIDO DE PONCE | P23061400395 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2023-06-14 | 1122 | keep | 0 | Jun | 2023 | 0.00076419 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CANOVANAS | 2023-06-14 15:13 | 2023-06-14 15:22 | 1 | 0:09 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R23061400099 | New_Event | Animals | Include | Include | Wildlife | 9 | 2023-06-14 | 9 | keep | 0 | Jun | 2023 | 6.1299e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-06-14 15:16 | 2023-06-14 17:28 | 12 | 2:12 | P | CAUSAS EXTERNAS | SE ABRIO XMR PARA REPARAR SECUNDARIA AFECTADA POR PERSONAL DE DESGANCHE | C23061400179 | New_Event | Damage From Public | Include | Include | Public | 132 | 2023-06-14 | 1584 | keep | 0 | Jun | 2023 | 0.0010789 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-06-14 15:20 | 2023-06-14 17:55 | 91 | 2:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | R23061400102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2023-06-14 | 14105 | keep | 0 | Jun | 2023 | 0.0096069 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
MAYAGÃœEZ | 2023-06-14 15:21 | 2023-06-14 19:35 | 100 | 4:14 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M23061400164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 254 | 2023-06-14 | 25400 | keep | 0 | Jun | 2023 | 0.0173 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-06-14 15:25 | 2023-06-14 15:54 | 6197 | 0:29 | T | ERROR HUMANO | DISPARO DE BKR A CAUSA DE PERSONAL DE CAMPO CERRANDO PUENTE DE LINEA A CAJA TOCO LA LINEA, SE VERIFICO PERSONAL FUERA DE LA LINEA Y SE CERRO POR CONTROL. EMPLEADO CON SUBSTATION ENTRY TARDO EN CONTESTAR LAS LLAMADAS. | C23061400194 | New_Event | Human Error | Include | Include | Other | 29 | 2023-06-14 | 179713 | keep | 0 | Jun | 2023 | 0.1224 | 0.0042207 | Sustained | FALSE | FALSE | Not_TMED_Event | 6197
VEGA BAJA | 2023-06-14 15:32 | 2023-06-14 20:34 | 40 | 5:02 | P | ARBOL SOBRE LINEA | (1 X 50) (1 X 40) Y (1 X 30) EN CORTES DE LINEA SE RETIRO ARBOL SOBRE LINEA | A23061400097 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 302 | 2023-06-14 | 12080 | keep | 0 | Jun | 2023 | 0.0082276 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-06-14 15:37 | 2023-06-14 17:45 | 15 | 2:08 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23061400206 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2023-06-14 | 1920 | keep | 0 | Jun | 2023 | 0.0013077 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-06-14 15:37 | 2023-06-14 16:52 | 8 | 1:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23061400161 | New_Event | Secondary Wire Break | Include | Include | Equipment | 75 | 2023-06-14 | 600 | keep | 0 | Jun | 2023 | 0.00040866 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-06-14 15:54 | 2023-06-14 16:15 | 10 | 0:21 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE DE LINEA A CAJA PRIMARIA | C23061300229 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 21 | 2023-06-14 | 210 | keep | 0 | Jun | 2023 | 0.00014303 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-06-14 16:01 | 2023-06-14 16:03 | 635 | 0:02 | T | ALIMENTADOR AMARRADO | SJ-230613-50 NORMALIZANDO LAS CARGAS DE LA PORTATIL, NO FASEA CON PALMER TC | R23061400125 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-06-14 | 1270 | keep | 0 | Jun | 2023 | 0.00086499 | 0.0004325 | Momentary | FALSE | FALSE | Not_TMED_Event | 635
CANOVANAS | 2023-06-14 16:01 | 2023-06-14 16:38 | 3766 | 0:37 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SJ-230613-50 NORMALIZANDO LAS CARGAS DE LA PORTATIL, NO FASEA CON PALMER TC, SE REPARO PLANCHELA AVERIADA EN MACHETE DE SALIDA DEL 2306-03 QUE AL CERRARLO SE PRENDIO | R23061400125 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 37 | 2023-06-14 | 139342 | keep | 0 | Jun | 2023 | 0.094905 | 0.002565 | Sustained | FALSE | FALSE | Not_TMED_Event | 3766
CANOVANAS | 2023-06-14 16:01 | 2023-06-14 16:04 | 1380 | 0:03 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SJ-230613-50 NORMALIZANDO LAS CARGAS DE LA PORTATIL, NO FASEA CON PALMER | R23061400125 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 3 | 2023-06-14 | 4140 | keep | 0 | Jun | 2023 | 0.0028197 | 0.00093991 | Momentary | FALSE | FALSE | Not_TMED_Event | 1380
BAYAMON | 2023-06-14 16:02 | 2023-06-14 19:29 | 82 | 3:27 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | B23061400168 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2023-06-14 | 16974 | keep | 0 | Jun | 2023 | 0.011561 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
CANOVANAS | 2023-06-14 16:07 | 2023-06-14 17:33 | 43 | 1:26 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE CAJA A LINEA | R23061400114 | New_Event | Primary Wire Break | Include | Include | Equipment | 86 | 2023-06-14 | 3698 | keep | 0 | Jun | 2023 | 0.0025187 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
CAGUAS | 2023-06-14 16:07 | 2023-06-14 19:17 | 85 | 3:10 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23061400259 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2023-06-14 | 16150 | keep | 0 | Jun | 2023 | 0.011 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
YAUCO | 2023-06-14 16:14 | 2023-06-14 16:15 | 1352 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE NO CAUSA | P23061400450 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-14 | 1352 | keep | 0 | Jun | 2023 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
SAN JUAN | 2023-06-14 16:24 | 2023-06-15 16:32 | 17 | 24:08 | P | CONDUCTOR ROTO O ABIERTO | 1 X 20 EN XMR SE CERRO PUENTE DE LINEA A CAJA. | S23061400155 | New_Event | Primary Wire Break | Include | Include | Equipment | 1448 | 2023-06-14 | 24616 | keep | 0 | Jun | 2023 | 0.016766 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
MAYAGÃœEZ | 2023-06-14 16:27 | 202
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