## SAIDI_SAIFI
FY2022 | Metric | Area | 2021-07-01 | 2021-08-01 | 2021-09-01 | 2021-10-01 | 2021-11-01 | 2021-12-01 | 2022-01-01 | 2022-02-01 | 2022-03-01 | 2022-04-01 | 2022-05-01 | 2022-06-01
| SAIDI (T&D) | System | 174.26 | 134.56 | 174.14 | 156.87 | 115.07 | 123.72 | 67.56 | 99.38 | 121.54 | 119.68 | 138.92 | 138.67
| SAIFI (T&D) | System | 0.64 | 0.61 | 0.72 | 0.84 | 0.57 | 0.62 | 0.48 | 0.5 | 0.59 | 0.61 | 0.68 | 0.66
| SAIDI (T&D) / YTD | System | 174.26 | 308.82 | 482.96 | 639.83 | 754.9 | 878.62 | 946.18 | 1045.56 | 1167.1 | 1286.78 | 1425.7 | 1564.37
| SAIFI (T&D) / YTD | System | 0.64 | 1.25 | 1.97 | 2.81 | 3.38 | 4 | 4.48 | 4.98 | 5.57 | 6.18 | 6.86 | 7.52
FY2023 | Metric | Area | 2022-07-01 | 2022-08-01 | 2022-09-01 | 2022-10-01 | 2022-11-01 | 2022-12-01 | 2023-01-01 | 2023-02-01 | 2023-03-01 | 2023-04-01 | 2023-05-01 | 2023-06-01
| SAIDI (T&D) | System | 137.35 | 162.77 | 86.61 | 68.45 | 94.97 | 76.4 | 63.93 | 57.26 | 66.33 | 126.52 | 130.51 | 146.9
| SAIFI (T&D) | System | 0.68 | 0.88 | 0.57 | 0.29 | 0.56 | 0.52 | 0.41 | 0.37 | 0.42 | 0.66 | 0.74 | 0.88
| SAIDI (T&D) / YTD | System | 137.35 | 300.12 | 386.73 | 455.18 | 550.15 | 626.55 | 690.48 | 747.74 | 814.07 | 940.59 | 1071.1 | 1218
| SAIFI (T&D) / YTD | System | 0.68 | 1.56 | 2.13 | 2.42 | 2.98 | 3.5 | 3.91 | 4.28 | 4.7 | 5.36 | 6.1 | 6.98
FY2024 | Metric | Area | 2023-07-01 | 2023-08-01 | 2023-09-01 | 2023-10-01 | 2023-11-01 | 2023-12-01 | 2024-01-01 | 2024-02-01 | 2024-03-01 | 2024-04-01 | 2024-05-01 | 2024-06-01
| SAIDI (T&D) | System | 166.62 | 160.52 | 104.28 | 113.83 | 84.96 | 106.26 | 63.68 | 101.9 | 92.56 | 123.37 | 158.83 | 155.08
| SAIFI (T&D) | System | 0.98 | 0.88 | 0.66 | 0.66 | 0.52 | 0.58 | 0.43 | 0.49 | 0.48 | 0.68 | 0.81 | 0.75
| SAIDI (T&D) / YTD | System | 166.62 | 327.14 | 431.42 | 545.25 | 630.21 | 736.47 | 800.15 | 902.05 | 994.61 | 1117.98 | 1276.81 | 1431.89
| SAIFI (T&D) / YTD | System | 0.98 | 1.86 | 2.52 | 3.18 | 3.7 | 4.28 | 4.71 | 5.2 | 5.68 | 6.36 | 7.17 | 7.92
FY2025 | Metric | Area | 2024-07-01 | 2024-08-01 | 2024-09-01 | 2024-10-01 | 2024-11-01 | 2024-12-01 | 2025-01-01 | 2025-02-01 | 2025-03-01 | 2025-04-01 | 2025-05-01 | 2025-06-01
| SAIDI (T&D) | System | 129.46 | 106.29 | 167.82 | 140.27 | 120 | 110.71 | 109.14 | 101.3 | 111.29
| SAIFI (T&D) | System | 0.67 | 0.56 | 0.86 | 0.77 | 0.55 | 0.59 | 0.52 | 0.56 | 0.53
| SAIDI (T&D) / YTD | System | 129.46 | 235.75 | 403.57 | 543.84 | 663.84 | 774.55 | 883.69 | 984.99 | 1096.28
| SAIFI (T&D) / YTD | System | 0.67 | 1.23 | 2.09 | 2.86 | 3.41 | 4 | 4.52 | 5.08 | 5.61

## FY2022
Distrito | Fecha_Recibida | Fecha_Corregida | Clientes | DuraciÃ³n | Tipo | CÃ³digo | Causas | Evento | Restoration_Type_4h | Code | Weather_Related_Cause | Relatad Outge Tab | Categorias | Duration_Minutes | Date | nCustxDuration | Exclusions | Earthquake | Month | Year | nCustxDuration_per_TotCustomers | Clientes_per_TotCustomers | Sustained_Momentary | Gen_Key | Line_Key | New_TMED_Event | Customers interrupted (CI)
CAGUAS | 2021-07-01 00:41 | 2021-07-01 17:56 | 106 | 017:15 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO ARBOL DE LA LINEA Y SE RETEZO LINEA PRIMARIA | C21070100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1035 | 2021-07-01 | 109710 | keep | 0 | Jul | 2021 | 0.074723 | 7.2196e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 106
CANOVANAS | 2021-07-01 01:21 | 2021-07-01 09:26 | 150 | 008:05 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | R21070100002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 485 | 2021-07-01 | 72750 | keep | 0 | Jul | 2021 | 0.04955 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-07-01 02:24 | 2021-07-01 11:48 | 30 | 009:24 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B21070100002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 564 | 2021-07-01 | 16920 | keep | 0 | Jul | 2021 | 0.011524 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-07-01 03:00 | 2021-07-01 11:20 | 250 | 008:20 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | PUENTE ABIERTO EN EL TRONCAL POR EMPALME AVERIADO EN RISER | B21070100003 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 500 | 2021-07-01 | 125000 | keep | 0 | Jul | 2021 | 0.085137 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
CAGUAS | 2021-07-01 03:06 | 2021-07-01 14:15 | 60 | 011:09 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C21070100006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 669 | 2021-07-01 | 40140 | keep | 0 | Jul | 2021 | 0.027339 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-07-01 03:32 | 2021-07-01 03:33 | 1984 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO SE PROBO CON RECIERRE EN OFF QUEDO EN SERVICIO LLEVA CARGA 1911-7 | S21070100004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-01 | 1984 | keep | 0 | Jul | 2021 | 0.0013513 | 0.0013513 | Momentary | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2021-07-01 03:32 | 2021-07-01 03:33 | 577 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO CON RECIERRE EN OFF QUEDO EN SERVICIO CARGA POR 1529-12 | S21070100004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-01 | 577 | keep | 0 | Jul | 2021 | 0.00039299 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
GUAYAMA | 2021-07-01 04:10 | 2021-07-01 10:38 | 150 | 006:28 | P | TRANSFORMADOR AVERIADO | PM-22 AVERIADO SE CERRO CIRCUITO DEL PM-21 AL PM-23 | P21070100001 | New_Event | Service Transformer Failure | Include | Include | Equipment | 388 | 2021-07-01 | 58200 | keep | 0 | Jul | 2021 | 0.03964 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2021-07-01 04:27 | 2021-07-01 06:08 | 31 | 001:41 | T | NO SE REPORTO CAUSA | CERRADO EN EL CAMPO POR PERSONAL DE SUBESTACIONES | B21070100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 101 | 2021-07-01 | 3131 | keep | 0 | Jul | 2021 | 0.0021325 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
PONCE | 2021-07-01 04:49 | 2021-07-01 17:50 | 150 | 013:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA GLOBO CRUZA FASE | P21070100019 | New_Event |  |  | Include | Wildlife | 781 | 2021-07-01 | 117150 | keep | 0 | Jul | 2021 | 0.07979 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-07-01 06:00 | 2021-07-01 20:20 | 50 | 014:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA PARTIDA | A21070100000 | New_Event | Wire Down | Include | Include | Equipment | 860 | 2021-07-01 | 43000 | keep | 0 | Jul | 2021 | 0.029287 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-07-01 06:01 | 2021-07-01 06:02 | 1478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDO EN SERVICIO | P21070100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-01 | 1478 | keep | 0 | Jul | 2021 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
SAN JUAN | 2021-07-01 06:14 | 2021-07-01 06:15 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21070100014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-01 | 4133 | keep | 0 | Jul | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
HUMACAO | 2021-07-01 06:24 | 2021-07-01 10:41 | 281 | 004:17 | P | DESGANCHE | 1 X 65, 1 X 50 Y 1 X 40 EN CORTES DE LINEA SE RETIRO RAMA DE LA LINEA | C21070100011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 257 | 2021-07-01 | 72217 | keep | 0 | Jul | 2021 | 0.049187 | 0.00019139 | Sustained | FALSE | TRUE | Not_TMED_Event | 281
VEGA BAJA | 2021-07-01 06:26 | 2021-07-01 06:27 | 3000 | 000:01 | T | DESGANCHE | RECERRO | B21070100011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-01 | 3000 | keep | 0 | Jul | 2021 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
VEGA BAJA | 2021-07-01 06:27 | 2021-07-01 09:00 | 60 | 002:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE DESGANCHO PALMAS | B21070100013 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 153 | 2021-07-01 | 9180 | keep | 0 | Jul | 2021 | 0.0062525 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
AGUADILLA | 2021-07-01 06:36 | 2021-07-01 06:37 | 1261 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21070100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-01 | 1261 | keep | 0 | Jul | 2021 | 0.00085886 | 0.00085886 | Momentary | FALSE | FALSE | Not_TMED_Event | 1261
BAYAMON | 2021-07-01 06:44 | 2021-07-01 06:45 | 5191 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR Y SE CERRO POR CONTROL | B21070100015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-01 | 5191 | keep | 0 | Jul | 2021 | 0.0035356 | 0.0035356 | Momentary | FALSE | FALSE | Not_TMED_Event | 5191
CANOVANAS | 2021-07-01 06:44 | 2021-07-01 17:57 | 40 | 011:13 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21070100007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 673 | 2021-07-01 | 26920 | keep | 0 | Jul | 2021 | 0.018335 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-01 06:50 | 2021-07-01 06:52 | 1983 | 000:02 | T | NO SE REPORTO CAUSA | INTERRUPTOR DISPARO Y SE CERRO POR CONTROL | B21070100016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-01 | 3966 | keep | 0 | Jul | 2021 | 0.0027012 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-07-01 06:50 | 2021-07-01 06:52 | 186 | 000:02 | T | NO SE REPORTO CAUSA | INTERRUPTOR DISPARO Y SE CERRO POR CONTROL | B21070100016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-01 | 372 | keep | 0 | Jul | 2021 | 0.00025337 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2021-07-01 07:23 | 2021-07-01 07:24 | 727 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 3500 | S21070100013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-01 | 727 | keep | 0 | Jul | 2021 | 0.00049516 | 0.00049516 | Momentary | FALSE | TRUE | Not_TMED_Event | 727
BAYAMON | 2021-07-01 07:23 | 2021-07-01 07:24 | 1420 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 3500 | S21070100013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-01 | 1420 | keep | 0 | Jul | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | TRUE | Not_TMED_Event | 1420
BAYAMON | 2021-07-01 07:23 | 2021-07-01 07:24 | 290 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 3500 | S21070100013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-01 | 290 | keep | 0 | Jul | 2021 | 0.00019752 | 0.00019752 | Momentary | FALSE | TRUE | Not_TMED_Event | 290
BAYAMON | 2021-07-01 07:23 | 2021-07-01 07:24 | 610 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 3500 | S21070100013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-01 | 610 | keep | 0 | Jul | 2021 | 0.00041547 | 0.00041547 | Momentary | FALSE | TRUE | Not_TMED_Event | 610
BAYAMON | 2021-07-01 07:23 | 2021-07-01 07:24 | 842 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 3500 | S21070100013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-01 | 842 | keep | 0 | Jul | 2021 | 0.00057348 | 0.00057348 | Momentary | FALSE | TRUE | Not_TMED_Event | 842
BAYAMON | 2021-07-01 07:23 | 2021-07-01 07:24 | 437 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 3500 | S21070100013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-01 | 437 | keep | 0 | Jul | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | TRUE | Not_TMED_Event | 437
BAYAMON | 2021-07-01 07:23 | 2021-07-01 07:24 | 643 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 3500 | S21070100013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-01 | 643 | keep | 0 | Jul | 2021 | 0.00043794 | 0.00043794 | Momentary | FALSE | TRUE | Not_TMED_Event | 643
BAYAMON | 2021-07-01 07:23 | 2021-07-01 07:24 | 1085 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 3500 | S21070100013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-01 | 1085 | keep | 0 | Jul | 2021 | 0.00073899 | 0.00073899 | Momentary | FALSE | TRUE | Not_TMED_Event | 1085
BAYAMON | 2021-07-01 07:23 | 2021-07-01 07:24 | 1310 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 3500 | S21070100013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-01 | 1310 | keep | 0 | Jul | 2021 | 0.00089224 | 0.00089224 | Momentary | FALSE | TRUE | Not_TMED_Event | 1310
BAYAMON | 2021-07-01 07:23 | 2021-07-01 07:24 | 411 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 3500 | S21070100013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-01 | 411 | keep | 0 | Jul | 2021 | 0.00027993 | 0.00027993 | Momentary | FALSE | TRUE | Not_TMED_Event | 411
BAYAMON | 2021-07-01 07:24 | 2021-07-01 12:50 | 20 | 005:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA | S21063000083 | New_Event | Cutout Failure | Include | Include | Equipment | 326 | 2021-07-01 | 6520 | keep | 0 | Jul | 2021 | 0.0044407 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-07-01 07:26 | 2021-07-01 11:16 | 30 | 003:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | R21070100009 | New_Event | Bad Weather | Include | Include | Weather | 230 | 2021-07-01 | 6900 | keep | 0 | Jul | 2021 | 0.0046996 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-07-01 07:43 | 2021-07-03 14:17 | 8 | 054:34 | P | SECUNDARIA/DESGANCHE | ABRIO TRANSFORMADOR PARA DESGANCHAR Y REPARAR SECUNDARIA | R21070100011 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 3274 | 2021-07-01 | 26192 | keep | 0 | Jul | 2021 | 0.017839 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-07-01 07:45 | 2021-07-01 11:10 | 1 | 003:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE 50 KVA X 50 KVA | A21070100005 | New_Event | Service Transformer Failure | Include | Include | Equipment | 205 | 2021-07-01 | 205 | keep | 0 | Jul | 2021 | 0.00013962 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-07-01 07:49 | 2021-07-01 09:40 | 6 | 001:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO TOMA DE CLIENTE | S21062900064 | New_Event | Secondary Wire Down | Include | Include | Equipment | 111 | 2021-07-01 | 666 | keep | 0 | Jul | 2021 | 0.00045361 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-07-01 07:50 | 2021-07-01 09:01 | 15 | 001:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REMPLAZARON CONECTORES | S21063000030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 71 | 2021-07-01 | 1065 | keep | 0 | Jul | 2021 | 0.00072537 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-07-01 07:50 | 2021-07-01 16:54 | 30 | 009:04 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21070100021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 544 | 2021-07-01 | 16320 | keep | 0 | Jul | 2021 | 0.011115 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-07-01 07:54 | 2021-07-01 10:35 | 300 | 002:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 80 EN CORTE DE LINEA Y 1 X 15 EN BANCO DE TRANSFORMADORES SE RETIRO NIDO DE LA LINEA | C21070100012 | New_Event |  |  | Include | Wildlife | 161 | 2021-07-01 | 48300 | keep | 0 | Jul | 2021 | 0.032897 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
ARECIBO | 2021-07-01 07:55 | 2021-07-01 07:56 | 2231 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21070100000 | New_Event |  |  | Include | Wildlife | 1 | 2021-07-01 | 2231 | keep | 0 | Jul | 2021 | 0.0015195 | 0.0015195 | Momentary | FALSE | FALSE | Not_TMED_Event | 2231
ARECIBO | 2021-07-01 07:56 | 2021-07-01 10:40 | 60 | 002:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | A21070100013 | 1st_after_momentary |  |  | Include | Wildlife | 164 | 2021-07-01 | 9840 | keep | 0 | Jul | 2021 | 0.006702 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
VEGA BAJA | 2021-07-01 07:59 | 2021-07-01 17:01 | 40 | 009:02 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REEMPLAZAR POSTE PARTIDO | B21070100022 | New_Event | Defective Pole | Include | Include | Equipment | 542 | 2021-07-01 | 21680 | keep | 0 | Jul | 2021 | 0.014766 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-07-01 08:05 | 2021-07-01 17:35 | 80 | 009:30 | P | LINEA DE TRANSMISION 38KV | SE ABRIÃ“ CORTE DE LINEA PARA TRABAJOS EN LINEAS DE TRANSMISIÃ“N 1500 Y 2000 | M21070100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 570 | 2021-07-01 | 45600 | keep | 0 | Jul | 2021 | 0.031058 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
AGUADILLA | 2021-07-01 08:05 | 2021-07-01 14:21 | 80 | 006:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO PUENTES PRIMARIOS | M21070100013 | New_Event | Wire Down | Include | Include | Equipment | 376 | 2021-07-01 | 30080 | keep | 0 | Jul | 2021 | 0.020487 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
VEGA BAJA | 2021-07-01 08:20 | 2021-07-01 09:15 | 10 | 000:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA DE TRANSFORMADOR | B21070100023 | New_Event | Cutout Failure | Include | Include | Equipment | 55 | 2021-07-01 | 550 | keep | 0 | Jul | 2021 | 0.0003746 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-07-01 08:25 | 2021-07-01 17:33 | 30 | 009:08 | P | SECUNDARIA/DESGANCHE | SE RETIRO BAMBUAS DE LA LINEA Y SE REPARO LINEA SECUNDARIA | C21070100015 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 548 | 2021-07-01 | 16440 | keep | 0 | Jul | 2021 | 0.011197 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-07-01 08:30 | 2021-07-01 16:34 | 12 | 008:04 | P | LINEA DE TRANSMISION 38KV | SE ABRIÃ“ CORTE DE LINEA PARA TRABAJOS EN LINEAS DE TRANSMISIÃ“N 1500 Y 2000 | M21070100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 484 | 2021-07-01 | 5808 | keep | 0 | Jul | 2021 | 0.0039558 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
BAYAMON | 2021-07-01 08:39 | 2021-07-01 16:30 | 60 | 007:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21070100025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 471 | 2021-07-01 | 28260 | keep | 0 | Jul | 2021 | 0.019248 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-07-01 08:45 | 2021-07-01 13:10 | 101 | 004:25 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO ARBOL DE LA LINEA | C21070100016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 265 | 2021-07-01 | 26765 | keep | 0 | Jul | 2021 | 0.01823 | 6.8791e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 101
ARECIBO | 2021-07-01 08:55 | 2021-07-01 09:14 | 8 | 000:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIO | A21070100010 | New_Event | Secondary Wire Down | Include | Include | Equipment | 19 | 2021-07-01 | 152 | keep | 0 | Jul | 2021 | 0.00010353 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-07-01 09:00 | 2021-07-01 17:15 | 300 | 008:15 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA Y 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070100020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 495 | 2021-07-01 | 148500 | keep | 0 | Jul | 2021 | 0.10114 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
UTUADO | 2021-07-01 09:04 | 2021-07-01 12:50 | 80 | 003:46 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21070100015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2021-07-01 | 18080 | keep | 0 | Jul | 2021 | 0.012314 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
AGUADILLA | 2021-07-01 09:10 | 2021-07-01 17:20 | 40 | 008:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M21070100000 | New_Event | Wire Down | Include | Include | Equipment | 490 | 2021-07-01 | 19600 | keep | 0 | Jul | 2021 | 0.013349 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-07-01 09:10 | 2021-07-01 09:13 | 2107 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA | A21070100016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-07-01 | 6321 | keep | 0 | Jul | 2021 | 0.0043052 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
VEGA BAJA | 2021-07-01 09:24 | 2021-07-01 13:22 | 10 | 003:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO TRANSFORMADOR Y SE CERRO PUENTE DE LINEA A CAJA | B21070100026 | New_Event | Wire Down | Include | Include | Equipment | 238 | 2021-07-01 | 2380 | keep | 0 | Jul | 2021 | 0.001621 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
YAUCO | 2021-07-01 09:40 | 2021-07-01 19:15 | 8 | 009:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN TRANSFORMADOR CAMION PARTE LINEA SECUNDARIA | P21070100008 | New_Event |  |  | Include | Wildlife | 575 | 2021-07-01 | 4600 | keep | 0 | Jul | 2021 | 0.003133 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
SAN JUAN | 2021-07-01 09:42 | 2021-07-02 10:47 | 15 | 025:05 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA X 50KVA | S21070100019 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1505 | 2021-07-01 | 22575 | keep | 0 | Jul | 2021 | 0.015376 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-07-01 09:45 | 2021-07-01 12:13 | 300 | 002:28 | P | ERROR HUMANO | 1 X 80 EN CORTE DE LINEA PERSONAL MUNICIPIO SALINAS CRUZAN FASE DURANTE DESGANCHE | P21070100009 | New_Event | Human Error | Include | Include | Other | 148 | 2021-07-01 | 44400 | keep | 0 | Jul | 2021 | 0.030241 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-07-01 09:52 | 2021-07-01 18:00 | 150 | 008:08 | P | DESGANCHE | SE ABRIÃ“ CORTE DE LINEA PARA REALIZAR DESGANCHE | M21070100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 488 | 2021-07-01 | 73200 | keep | 0 | Jul | 2021 | 0.049856 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-07-01 10:00 | 2021-07-01 11:51 | 11 | 001:51 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL QUEMADO Y REPARAR SECUNDARIA | C21070100025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2021-07-01 | 1221 | keep | 0 | Jul | 2021 | 0.00083162 | 7.492e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 11
ARECIBO | 2021-07-01 10:12 | 2021-07-01 10:33 | 6 | 000:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21063000202 | New_Event | Secondary Wire Down | Include | Include | Equipment | 21 | 2021-07-01 | 126 | keep | 0 | Jul | 2021 | 8.5818e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-07-01 10:16 | 2021-07-01 10:47 | 1 | 000:31 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S21070100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 31 | 2021-07-01 | 31 | keep | 0 | Jul | 2021 | 2.1114e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-07-01 10:21 | 2021-07-01 17:30 | 200 | 007:09 | P | DESGANCHE | SE ABRIÃ“ CORTE DE LINEA PARA REALIZAR DESGANCHE | M21070100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 429 | 2021-07-01 | 85800 | keep | 0 | Jul | 2021 | 0.058438 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-07-01 10:29 | 2021-07-01 11:08 | 1 | 000:39 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S21070100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 39 | 2021-07-01 | 39 | keep | 0 | Jul | 2021 | 2.6563e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-07-01 10:29 | 2021-07-01 11:40 | 50 | 001:11 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21070100027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2021-07-01 | 3550 | keep | 0 | Jul | 2021 | 0.0024179 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-07-01 10:38 | 2021-07-01 19:19 | 15 | 008:41 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO PM-22 AVERIADO 75KVA A 13.2 KV | P21070100013 | New_Event | Service Transformer Failure | Include | Include | Equipment | 521 | 2021-07-01 | 7815 | keep | 0 | Jul | 2021 | 0.0053228 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2021-07-01 10:45 | 2021-07-01 10:46 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21070100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-01 | 969 | keep | 0 | Jul | 2021 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | Not_TMED_Event | 969
ARECIBO | 2021-07-01 11:00 | 2021-07-01 11:30 | 4 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21070100003 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2021-07-01 | 120 | keep | 0 | Jul | 2021 | 8.1731e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-07-01 11:11 | 2021-07-02 09:08 | 95 | 021:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE FIJO CONDUCTOR AL AISLADOR | R21070100019 | New_Event | Wire Down | Include | Include | Equipment | 1317 | 2021-07-01 | 125115 | keep | 0 | Jul | 2021 | 0.085215 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
BAYAMON | 2021-07-01 11:20 | 2021-07-01 15:17 | 723 | 003:57 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE ABIERTO A LA SALIDA DEL ALIMENTADOR SE CERRO PUENTE ABIERTO INTERRUPTOR NO QUIZO CERRAR CDS LO VERIFICO SE ABRIO RISER #3 PATIO BTC Y SE CERRO INTERRUPTOR NUEVAMENTE ENTRO EN SERVICIO 1711-05 Y PARCIAL 1711-02 | B21070100003 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 237 | 2021-07-01 | 171351 | keep | 0 | Jul | 2021 | 0.11671 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2021-07-01 11:20 | 2021-07-01 15:17 | 1976 | 003:57 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE CERRO PUENTE A LA SALIDA 1711-02 CARGA POR EL 1711-02 | B21070100003 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 237 | 2021-07-01 | 468312 | keep | 0 | Jul | 2021 | 0.31897 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
AGUADILLA | 2021-07-01 11:24 | 2021-07-01 15:41 | 30 | 004:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO DESCARGAS ELECTRICAS | M21070100030 | New_Event | Bad Weather | Include | Include | Weather | 257 | 2021-07-01 | 7710 | keep | 0 | Jul | 2021 | 0.0052512 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-07-01 11:33 | 2021-07-02 17:10 | 8 | 029:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21070100031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1777 | 2021-07-01 | 14216 | keep | 0 | Jul | 2021 | 0.0096825 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-07-01 11:37 | 2021-07-01 11:38 | 2791 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 | A21070100033 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-01 | 2791 | keep | 0 | Jul | 2021 | 0.0019009 | 0.0019009 | Momentary | FALSE | TRUE | Not_TMED_Event | 2791
ARECIBO | 2021-07-01 11:37 | 2021-07-01 11:38 | 1464 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 | A21070100033 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-01 | 1464 | keep | 0 | Jul | 2021 | 0.00099712 | 0.00099712 | Momentary | FALSE | TRUE | Not_TMED_Event | 1464
ARECIBO | 2021-07-01 11:37 | 2021-07-01 11:38 | 759 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 | A21070100033 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-01 | 759 | keep | 0 | Jul | 2021 | 0.00051695 | 0.00051695 | Momentary | FALSE | TRUE | Not_TMED_Event | 759
ARECIBO | 2021-07-01 11:37 | 2021-07-01 11:38 | 1500 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 | A21070100033 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-01 | 1500 | keep | 0 | Jul | 2021 | 0.0010216 | 0.0010216 | Momentary | FALSE | TRUE | Not_TMED_Event | 1500
ARECIBO | 2021-07-01 11:37 | 2021-07-01 11:38 | 2132 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 | A21070100034 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-01 | 2132 | keep | 0 | Jul | 2021 | 0.0014521 | 0.0014521 | Momentary | FALSE | TRUE | Not_TMED_Event | 2132
ARECIBO | 2021-07-01 11:37 | 2021-07-01 11:38 | 2366 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 | A21070100034 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-01 | 2366 | keep | 0 | Jul | 2021 | 0.0016115 | 0.0016115 | Momentary | FALSE | TRUE | Not_TMED_Event | 2366
ARECIBO | 2021-07-01 11:37 | 2021-07-01 11:38 | 1976 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 | A21070100034 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-01 | 1976 | keep | 0 | Jul | 2021 | 0.0013458 | 0.0013458 | Momentary | FALSE | TRUE | Not_TMED_Event | 1976
ARECIBO | 2021-07-01 11:37 | 2021-07-01 11:38 | 3688 | 000:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 | A21070100034 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-01 | 3688 | keep | 0 | Jul | 2021 | 0.0025119 | 0.0025119 | Momentary | FALSE | TRUE | Not_TMED_Event | 3688
CANOVANAS | 2021-07-01 11:38 | 2021-07-01 12:21 | 50 | 000:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21070100020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 43 | 2021-07-01 | 2150 | keep | 0 | Jul | 2021 | 0.0014644 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-01 11:46 | 2021-07-02 11:55 | 130 | 024:09 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 80 EN SU - 14 CONTAMINACION | R21070100024 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1449 | 2021-07-01 | 188370 | keep | 0 | Jul | 2021 | 0.1283 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
GUAYAMA | 2021-07-01 11:48 | 2021-07-01 13:52 | 65 | 002:04 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | P21070100015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2021-07-01 | 8060 | keep | 0 | Jul | 2021 | 0.0054896 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
FAJARDO | 2021-07-01 11:49 | 2021-07-01 15:33 | 100 | 003:44 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR Y LEVANTO CONDUCTOR | R21070100022 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 224 | 2021-07-01 | 22400 | keep | 0 | Jul | 2021 | 0.015257 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-07-01 12:10 | 2021-07-01 15:22 | 200 | 003:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO A TRANSFORMADOR | A21070100028 | New_Event | Wire Down | Include | Include | Equipment | 192 | 2021-07-01 | 38400 | keep | 0 | Jul | 2021 | 0.026154 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2021-07-01 12:17 | 2021-07-01 12:18 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21070100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-01 | 3431 | keep | 0 | Jul | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2021-07-01 12:24 | 2021-07-01 13:50 | 30 | 001:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | A21070100036 | New_Event |  |  | Include | Wildlife | 86 | 2021-07-01 | 2580 | keep | 0 | Jul | 2021 | 0.0017572 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-07-01 12:30 | 2021-07-02 10:32 | 8 | 022:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTE SECUNDARIO QUEMADO | C21070100040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1322 | 2021-07-01 | 10576 | keep | 0 | Jul | 2021 | 0.0072033 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-07-01 12:31 | 2021-07-01 16:10 | 1116 | 003:39 | T | DESGANCHE | DISPARO INTERRUPTOR SE RETIRO RAMA DE LA LINEA Y SE INSTALO TIGUERO CERCA DE PALMA TRASPATIO CERRADO POR CONTROL | C21070100042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2021-07-01 | 244404 | keep | 0 | Jul | 2021 | 0.16646 | 0.0007601 | Sustained | FALSE | TRUE | Not_TMED_Event | 1116
UTUADO | 2021-07-01 12:40 | 2021-07-01 18:40 | 15 | 006:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21070100037 | New_Event | Bad Weather | Include | Include | Weather | 360 | 2021-07-01 | 5400 | keep | 0 | Jul | 2021 | 0.0036779 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CAGUAS | 2021-07-01 12:48 | 2021-07-02 15:56 | 220 | 027:08 | P | DESGANCHE | 1 X 65 Y 1 X 50 EN CORTES DE LINEA DESGANCHO Y REPARO BAJANTE LINEA A CAJA | C21070100044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1628 | 2021-07-01 | 358160 | keep | 0 | Jul | 2021 | 0.24394 | 0.00014984 | Sustained | FALSE | TRUE | Not_TMED_Event | 220
ARECIBO | 2021-07-01 12:48 | 2021-07-01 14:30 | 100 | 001:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO AVERIADO | A21070100038 | New_Event | Wire Down | Include | Include | Equipment | 102 | 2021-07-01 | 10200 | keep | 0 | Jul | 2021 | 0.0069472 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-07-01 12:49 | 2021-07-01 12:50 | 1212 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDO EN SERVICIO | P21070100017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-01 | 1212 | keep | 0 | Jul | 2021 | 0.00082549 | 0.00082549 | Momentary | FALSE | FALSE | Not_TMED_Event | 1212
MAYAGÃœEZ | 2021-07-01 12:51 | 2021-07-01 15:00 | 6 | 002:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIÃ“ CORTE DE LINEA PARA REPARAR BAJANTE DE TRANSFORMADOR | M21070100000 | New_Event | Wire Down | Include | Include | Equipment | 129 | 2021-07-01 | 774 | keep | 0 | Jul | 2021 | 0.00052717 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
ARECIBO | 2021-07-01 13:00 | 2021-07-01 20:43 | 20 | 007:43 | P | NO SE REPORTO CAUSA | 1 X 50 EN RIZER NO SE DETECTO LA CAUSA | A21070100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 463 | 2021-07-01 | 9260 | keep | 0 | Jul | 2021 | 0.0063069 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-07-01 13:11 | 2021-07-01 17:50 | 150 | 004:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21070100041 | New_Event | Bad Weather | Include | Include | Weather | 279 | 2021-07-01 | 41850 | keep | 0 | Jul | 2021 | 0.028504 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-07-01 13:14 | 2021-07-01 13:16 | 1218 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA | A21070100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-01 | 2436 | keep | 0 | Jul | 2021 | 0.0016591 | 0.00082957 | Momentary | FALSE | FALSE | Not_TMED_Event | 1218
BARRANQUITAS | 2021-07-01 13:15 | 2021-07-02 09:58 | 30 | 020:43 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA REMPLAZO AISLADOR | C21070100047 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1243 | 2021-07-01 | 37290 | keep | 0 | Jul | 2021 | 0.025398 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-07-01 13:20 | 2021-07-01 17:21 | 42 | 004:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE DESGANCHO Y SE DESPEGO BAJANTE PRIMARIO DE LA CRUCETA | C21070100048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2021-07-01 | 10122 | keep | 0 | Jul | 2021 | 0.006894 | 2.8606e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 42
BAYAMON | 2021-07-01 13:22 | 2021-07-02 10:10 | 8 | 020:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21070100036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1248 | 2021-07-01 | 9984 | keep | 0 | Jul | 2021 | 0.0068001 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-07-01 13:24 | 2021-07-01 13:25 | 1218 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA | A21070100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-01 | 1218 | keep | 0 | Jul | 2021 | 0.00082957 | 0.00082957 | Momentary | FALSE | FALSE | Not_TMED_Event | 1218
PONCE | 2021-07-01 13:26 | 2021-07-01 16:09 | 300 | 002:43 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA FUERTES VIENTOS | P21070100018 | New_Event | Bad Weather | Include | Include | Weather | 163 | 2021-07-01 | 48900 | keep | 0 | Jul | 2021 | 0.033306 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
SAN JUAN | 2021-07-01 13:42 | 2021-07-02 13:00 | 50 | 023:18 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21070100025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1398 | 2021-07-01 | 69900 | keep | 0 | Jul | 2021 | 0.047609 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-07-01 13:51 | 2021-07-01 21:34 | 90 | 007:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | A21070100045 | New_Event | Wire Down | Include | Include | Equipment | 463 | 2021-07-01 | 41670 | keep | 0 | Jul | 2021 | 0.028381 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
ARECIBO | 2021-07-01 13:51 | 2021-07-01 15:46 | 5 | 001:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO TRAMO DE SECUNDARIA PARTIDA | A21070100046 | New_Event | Secondary Wire Down | Include | Include | Equipment | 115 | 2021-07-01 | 575 | keep | 0 | Jul | 2021 | 0.00039163 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-07-01 13:54 | 2021-07-01 13:55 | 4664 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21070100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-01 | 4664 | keep | 0 | Jul | 2021 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
MAYAGÃœEZ | 2021-07-01 14:00 | 2021-07-01 15:30 | 50 | 001:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21070100000 | New_Event | Bad Weather | Include | Include | Weather | 90 | 2021-07-01 | 4500 | keep | 0 | Jul | 2021 | 0.0030649 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-07-01 14:06 | 2021-07-02 09:17 | 25 | 019:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN DOS TRANSFORMADORES LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21070100048 | New_Event | Bad Weather | Include | Include | Weather | 1151 | 2021-07-01 | 28775 | keep | 0 | Jul | 2021 | 0.019599 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-07-01 14:16 | 2021-07-01 19:25 | 1 | 005:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21062900060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 309 | 2021-07-01 | 309 | keep | 0 | Jul | 2021 | 0.00021046 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-07-01 14:21 | 2021-07-01 16:10 | 574 | 001:49 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21070100097 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 109 | 2021-07-01 | 62566 | keep | 0 | Jul | 2021 | 0.042613 | 0.00039095 | Sustained | FALSE | TRUE | Not_TMED_Event | 574
AGUADILLA | 2021-07-01 14:21 | 2021-07-01 16:10 | 2493 | 001:49 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21070100097 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 109 | 2021-07-01 | 271737 | keep | 0 | Jul | 2021 | 0.18508 | 0.001698 | Sustained | FALSE | TRUE | Not_TMED_Event | 2493
AGUADILLA | 2021-07-01 14:21 | 2021-07-01 16:10 | 1415 | 001:49 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21070100097 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 109 | 2021-07-01 | 154235 | keep | 0 | Jul | 2021 | 0.10505 | 0.00096375 | Sustained | FALSE | TRUE | Not_TMED_Event | 1415
AGUADILLA | 2021-07-01 14:21 | 2021-07-01 16:10 | 1428 | 001:49 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21070100097 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 109 | 2021-07-01 | 155652 | keep | 0 | Jul | 2021 | 0.10601 | 0.0009726 | Sustained | FALSE | TRUE | Not_TMED_Event | 1428
AGUADILLA | 2021-07-01 14:21 | 2021-07-01 16:10 | 1036 | 001:49 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21070100097 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 109 | 2021-07-01 | 112924 | keep | 0 | Jul | 2021 | 0.076912 | 0.00070561 | Sustained | FALSE | TRUE | Not_TMED_Event | 1036
AGUADILLA | 2021-07-01 14:21 | 2021-07-01 16:10 | 2366 | 001:49 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21070100099 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 109 | 2021-07-01 | 257894 | keep | 0 | Jul | 2021 | 0.17565 | 0.0016115 | Sustained | FALSE | TRUE | Not_TMED_Event | 2366
MAYAGÃœEZ | 2021-07-01 14:21 | 2021-07-01 16:10 | 1337 | 001:49 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21070100099 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 109 | 2021-07-01 | 145733 | keep | 0 | Jul | 2021 | 0.099258 | 0.00091062 | Sustained | FALSE | TRUE | Not_TMED_Event | 1337
AGUADILLA | 2021-07-01 14:21 | 2021-07-01 16:10 | 709 | 001:49 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21070100099 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 109 | 2021-07-01 | 77281 | keep | 0 | Jul | 2021 | 0.052636 | 0.0004829 | Sustained | FALSE | TRUE | Not_TMED_Event | 709
ARECIBO | 2021-07-01 14:26 | 2021-07-01 16:32 | 5 | 002:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE A TRANSFORMADOR WR5886179 | A21070100000 | New_Event | Wire Down | Include | Include | Equipment | 126 | 2021-07-01 | 630 | keep | 0 | Jul | 2021 | 0.00042909 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2021-07-01 14:27 | 2021-07-01 17:17 | 35 | 002:50 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE MASIVO DE ENREDADERAS ARROPANDO DOS TRANSFORMADORES LO CUAL ESTA CAUSANDO FLUCTUACIONES DE VOLTAJE E INTERRUPCIONES SEGUIDAS EN EL AREA | B21070100039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2021-07-01 | 5950 | keep | 0 | Jul | 2021 | 0.0040525 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-07-01 14:30 | 2021-07-01 18:55 | 70 | 004:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE LEVANTO CONDUCTOR | B21070100040 | New_Event | Wire Down | Include | Include | Equipment | 265 | 2021-07-01 | 18550 | keep | 0 | Jul | 2021 | 0.012634 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
AGUADILLA | 2021-07-01 14:50 | 2021-07-02 09:32 | 80 | 018:42 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070100082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1122 | 2021-07-01 | 89760 | keep | 0 | Jul | 2021 | 0.061135 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-07-01 14:51 | 2021-07-02 11:50 | 15 | 020:59 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 40 EN SU - 63-A CONTAMINACION | R21070100032 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1259 | 2021-07-01 | 18885 | keep | 0 | Jul | 2021 | 0.012862 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-07-01 14:56 | 2021-07-01 21:00 | 1268 | 006:04 | S | PROTECCION DEFECTUOSA | FUSIBLE 38 KV FUNDIDO INTERRUPTOR 6501-01 PASO LA AVERÃA A LA ALTA DEL TRANSFORMADOR SE PASO SU CARGA AL 6501-02 | M21070100100 | New_Event | Protection Miscoordination | Include | Include | Other | 364 | 2021-07-01 | 461552 | keep | 0 | Jul | 2021 | 0.31436 | 0.00086363 | Sustained | FALSE | FALSE | Not_TMED_Event | 1268
MAYAGÃœEZ | 2021-07-01 14:56 | 2021-07-01 20:07 | 2064 | 005:11 | S | PROTECCION DEFECTUOSA | FUSIBLE 38 KV FUNDIDO INTERRUPTOR 6501-01 PASO LA AVERÃA A LA ALTA DEL TRANSFORMADOR SE LE PASO LA CARGA DEL 6501-01 | M21070100100 | New_Event | Protection Miscoordination | Include | Include | Other | 311 | 2021-07-01 | 641904 | keep | 0 | Jul | 2021 | 0.4372 | 0.0014058 | Sustained | FALSE | FALSE | Not_TMED_Event | 2064
MAYAGÃœEZ | 2021-07-01 14:56 | 2021-07-01 19:06 | 3036 | 004:10 | S | PROTECCION DEFECTUOSA | FUSIBLE 38 KV FUNDIDO INTERRUPTOR 6501-01 PASO LA AVERÃA A LA ALTA DEL TRANSFORMADOR | M21070100100 | New_Event | Protection Miscoordination | Include | Include | Other | 250 | 2021-07-01 | 759000 | keep | 0 | Jul | 2021 | 0.51695 | 0.0020678 | Sustained | FALSE | FALSE | Not_TMED_Event | 3036
MAYAGÃœEZ | 2021-07-01 14:56 | 2021-07-01 19:06 | 2952 | 004:10 | S | PROTECCION DEFECTUOSA | FUSIBLE 38 KV FUNDIDO INTERRUPTOR 6501-01 PASO LA AVERÃA A LA ALTA DEL TRANSFORMADOR | M21070100100 | New_Event | Protection Miscoordination | Include | Include | Other | 250 | 2021-07-01 | 738000 | keep | 0 | Jul | 2021 | 0.50265 | 0.0020106 | Sustained | FALSE | FALSE | Not_TMED_Event | 2952
CANOVANAS | 2021-07-01 15:08 | 2021-07-01 15:27 | 4 | 000:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR MAL TIEMPO | R21070100033 | New_Event | Bad Weather | Include | Include | Weather | 19 | 2021-07-01 | 76 | keep | 0 | Jul | 2021 | 5.1763e-05 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-07-01 15:11 | 2021-07-01 15:12 | 863 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA | M21070100096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-01 | 863 | keep | 0 | Jul | 2021 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
BAYAMON | 2021-07-01 15:17 | 2021-07-01 15:29 | 600 | 000:12 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO PUENTES EN RISER AVERIADO Y SE CERRARON MACHETES DE AMARRE CONTRA EL 1716-03 PARA DAR SERVICIO TOTAL | B21070100046 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 12 | 2021-07-01 | 7200 | keep | 0 | Jul | 2021 | 0.0049039 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-01 15:27 | 2021-07-02 09:56 | 75 | 018:29 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 50 EN CORTES DE LINEA DIFERENTES | B21070100045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1109 | 2021-07-01 | 83175 | keep | 0 | Jul | 2021 | 0.05665 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-07-01 15:29 | 2021-07-01 15:38 | 723 | 000:09 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO 1711-02 CERRANDO RISER #3 PATIO BTC SE ABRIO NUEVAMENTE Y SE CERRO INTERRUPTOR | B21070100003 | Additional_clients | UG - Broken Splice / Terminal | Include | Include | Equipment | 9 | 2021-07-01 | 6507 | keep | 0 | Jul | 2021 | 0.0044319 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-01 15:29 | 2021-07-01 15:38 | 1976 | 000:09 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO 1711-02 CERRANDO RISER #3 PATIO BTC SE ABRIO NUEVAMENTE Y SE CERRO INTERRUPTOR | B21070100003 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 9 | 2021-07-01 | 17784 | keep | 0 | Jul | 2021 | 0.012113 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-07-01 15:30 | 2021-07-01 17:40 | 30 | 002:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA LINEA PRIMARIA ROTA SE ABRIÃ“ PUENTES PARA SECCIONALIZAR | M21070100000 | New_Event | Wire Down | Include | Include | Equipment | 130 | 2021-07-01 | 3900 | keep | 0 | Jul | 2021 | 0.0026563 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-07-01 15:38 | 2021-07-01 16:12 | 600 | 000:34 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO PUENTES EN RISER AVERIADO Y SE CERRARON MACHETES DE AMARRE CONTRA EL 1716-03 PARA DAR SERVICIO TOTAL | B21070100046 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 34 | 2021-07-01 | 20400 | keep | 0 | Jul | 2021 | 0.013894 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-07-01 15:42 | 2021-07-01 16:38 | 25 | 000:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R21070100000 | New_Event |  |  | Include | Wildlife | 56 | 2021-07-01 | 1400 | keep | 0 | Jul | 2021 | 0.00095353 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-07-01 15:56 | 2021-07-01 15:57 | 1307 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S21070100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-01 | 1307 | keep | 0 | Jul | 2021 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
BAYAMON | 2021-07-01 16:03 | 2021-07-01 16:04 | 4533 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVANDO LA CARGA DEL 1717-05 | B21070100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-01 | 4533 | keep | 0 | Jul | 2021 | 0.0030874 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
BAYAMON | 2021-07-01 16:03 | 2021-07-01 16:04 | 341 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR EL 1717-01 | B21070100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-01 | 341 | keep | 0 | Jul | 2021 | 0.00023225 | 0.00023225 | Momentary | FALSE | FALSE | Not_TMED_Event | 341
AGUADILLA | 2021-07-01 16:10 | 2021-07-01 19:17 | 14 | 003:07 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA | M21063000017 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 187 | 2021-07-01 | 2618 | keep | 0 | Jul | 2021 | 0.0017831 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-07-01 16:10 | 2021-07-02 11:30 | 80 | 019:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO PUENTES PRIMARIOS | M21070100013 | New_Event | Wire Down | Include | Include | Equipment | 1160 | 2021-07-01 | 92800 | keep | 0 | Jul | 2021 | 0.063206 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
AGUADILLA | 2021-07-01 16:10 | 2021-07-01 21:32 | 382 | 005:22 | S | NO SE REPORTO CAUSA | DISPARO DEL MLB 0010 AL ENTRAR EN SERVICIO LA LINEA 5600 | M21070100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 322 | 2021-07-01 | 123004 | keep | 0 | Jul | 2021 | 0.083777 | 0.00026018 | Sustained | FALSE | TRUE | Not_TMED_Event | 382
AGUADILLA | 2021-07-01 16:10 | 2021-07-01 21:32 | 39 | 005:22 | S | NO SE REPORTO CAUSA | DISPARO DEL MLB 0010 AL ENTRAR EN SERVICIO LA LINEA 5600 | M21070100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 322 | 2021-07-01 | 12558 | keep | 0 | Jul | 2021 | 0.0085532 | 2.6563e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 39
BAYAMON | 2021-07-01 16:12 | 2021-07-01 16:14 | 723 | 000:02 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO 1711-02 CERRANDO RISER #3 PATIO BTC SE ABRIO NUEVAMENTE Y SE CERRO INTERRUPTOR | B21070100003 | Additional_clients | UG - Broken Splice / Terminal | Include | Include | Equipment | 2 | 2021-07-01 | 1446 | keep | 0 | Jul | 2021 | 0.00098486 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-01 16:12 | 2021-07-01 16:14 | 1976 | 000:02 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO 1711-02 CERRANDO RISER #3 PATIO BTC SE ABRIO NUEVAMENTE Y SE CERRO INTERRUPTOR | B21070100003 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 2 | 2021-07-01 | 3952 | keep | 0 | Jul | 2021 | 0.0026917 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-01 16:14 | 2021-07-01 18:08 | 600 | 001:54 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO PUENTES EN RISER AVERIADO Y SE CERRARON MACHETES DE AMARRE CONTRA EL 1716-03 PARA DAR SERVICIO TOTAL | B21070100046 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 114 | 2021-07-01 | 68400 | keep | 0 | Jul | 2021 | 0.046587 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
MAYAGÃœEZ | 2021-07-01 16:34 | 2021-07-01 16:41 | 411 | 000:07 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DEL INTERRUPTOR RECIERRE EN OFF MAL TIEMPO | M21070100000 | New_Event | Bad Weather | Include | Include | Weather | 7 | 2021-07-01 | 2877 | keep | 0 | Jul | 2021 | 0.0019595 | 0.00027993 | Sustained | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2021-07-01 16:41 | 2021-07-01 18:10 | 12 | 001:29 | P | LINEA DE TRANSMISION 38KV | SE ABRIÃ“ CORTE DE LINEA PARA TRABAJOS EN LINEAS DE TRANSMISIÃ“N 1500 Y 2000 | M21070100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 89 | 2021-07-01 | 1068 | keep | 0 | Jul | 2021 | 0.00072741 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
HUMACAO | 2021-07-01 16:44 | 2021-07-01 17:30 | 7 | 000:46 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA DESGANCHE | C21070100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 46 | 2021-07-01 | 322 | keep | 0 | Jul | 2021 | 0.00021931 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
PONCE | 2021-07-01 16:48 | 2021-07-02 10:50 | 75 | 018:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE CORTO BAMBUS | P21070200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1082 | 2021-07-01 | 81150 | keep | 0 | Jul | 2021 | 0.055271 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
GUAYAMA | 2021-07-01 17:27 | 2021-07-02 11:55 | 150 | 018:28 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | P21070200003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1108 | 2021-07-01 | 166200 | keep | 0 | Jul | 2021 | 0.1132 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-07-01 17:39 | 2021-07-02 15:14 | 25 | 021:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO BAJANTE DE CORTE DE LINEA | A21070200007 | New_Event | Wire Down | Include | Include | Equipment | 1295 | 2021-07-01 | 32375 | keep | 0 | Jul | 2021 | 0.02205 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
AGUADILLA | 2021-07-01 17:40 | 2021-07-02 12:50 | 10 | 019:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE REALIZO DESGANCHE DE BAMBUAS | M21070200168 | Partial_restoration | Wire Down | Include | Include | Equipment | 1150 | 2021-07-01 | 11500 | keep | 0 | Jul | 2021 | 0.0078326 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-01 19:04 | 2021-07-01 19:05 | 810 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 9200 | M21070100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-01 | 810 | keep | 0 | Jul | 2021 | 0.00055169 | 0.00055169 | Momentary | FALSE | TRUE | Not_TMED_Event | 810
MAYAGÃœEZ | 2021-07-01 19:04 | 2021-07-01 19:05 | 1235 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 9200 | M21070100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-01 | 1235 | keep | 0 | Jul | 2021 | 0.00084115 | 0.00084115 | Momentary | FALSE | TRUE | Not_TMED_Event | 1235
MAYAGÃœEZ | 2021-07-01 19:04 | 2021-07-01 19:05 | 93 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 9200 | M21070100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-01 | 93 | keep | 0 | Jul | 2021 | 6.3342e-05 | 6.3342e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 93
MAYAGÃœEZ | 2021-07-01 19:04 | 2021-07-01 19:05 | 1825 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 9200 | M21070100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-01 | 1825 | keep | 0 | Jul | 2021 | 0.001243 | 0.001243 | Momentary | FALSE | TRUE | Not_TMED_Event | 1825
MAYAGÃœEZ | 2021-07-01 19:04 | 2021-07-01 19:05 | 3230 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 9200 | M21070100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-01 | 3230 | keep | 0 | Jul | 2021 | 0.0021999 | 0.0021999 | Momentary | FALSE | TRUE | Not_TMED_Event | 3230
SAN JUAN | 2021-07-01 19:10 | 2021-07-01 19:11 | 893 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21070100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-01 | 893 | keep | 0 | Jul | 2021 | 0.00060822 | 0.00060822 | Momentary | FALSE | FALSE | Not_TMED_Event | 893
PONCE | 2021-07-01 19:19 | 2021-07-02 15:20 | 22 | 020:01 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | P21070200010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1201 | 2021-07-01 | 26422 | keep | 0 | Jul | 2021 | 0.017996 | 1.4984e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 22
ARECIBO | 2021-07-01 20:30 | 2021-07-02 11:11 | 10 | 014:41 | P | CABLE SOTERRADO AVERIADO | AVERIA SOTERRADA DE PM-8 A PM-7 SE INSTALO PROVISIONAL AEREO DE LINEA PRIMARIA CERCANA A PM-7 | A21070200006 | New_Event | UG Cable Fault | Include | Include | Equipment | 881 | 2021-07-01 | 8810 | keep | 0 | Jul | 2021 | 0.0060005 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-01 22:20 | 2021-07-02 12:15 | 50 | 013:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21070200063 | New_Event | Bad Weather | Include | Include | Weather | 835 | 2021-07-01 | 41750 | keep | 0 | Jul | 2021 | 0.028436 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-01 23:05 | 2021-07-01 23:06 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21070100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-01 | 3941 | keep | 0 | Jul | 2021 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
MAYAGÃœEZ | 2021-07-01 23:40 | 2021-07-02 10:35 | 50 | 010:55 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070200069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 655 | 2021-07-01 | 32750 | keep | 0 | Jul | 2021 | 0.022306 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-07-02 03:41 | 2021-07-03 19:59 | 100 | 040:18 | P | DESGANCHE | 1 X 80 Y 2 X 30 EN DIFERENTES CORTES DE LINEA POR DESGANCHE | P21070200023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2418 | 2021-07-02 | 241800 | keep | 0 | Jul | 2021 | 0.16469 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-07-02 03:45 | 2021-07-02 03:46 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21040200033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-02 | 2113 | keep | 0 | Jul | 2021 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
MAYAGÃœEZ | 2021-07-02 06:00 | 2021-07-02 16:12 | 1 | 010:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21070200000 | New_Event | Bad Weather | Include | Include | Weather | 612 | 2021-07-02 | 612 | keep | 0 | Jul | 2021 | 0.00041683 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
AGUADILLA | 2021-07-02 06:19 | 2021-07-05 16:55 | 20 | 082:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA EN TRANSFORMADOR | M21070200207 | New_Event | Cutout Failure | Include | Include | Equipment | 4956 | 2021-07-02 | 99120 | keep | 0 | Jul | 2021 | 0.06751 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-07-02 06:41 | 2021-07-04 10:03 | 3 | 051:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIAS | R21070200015 | New_Event | Bad Weather | Include | Include | Weather | 3082 | 2021-07-02 | 9246 | keep | 0 | Jul | 2021 | 0.0062974 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2021-07-02 06:50 | 2021-07-02 06:51 | 1310 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO | B21070200000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-07-02 | 1310 | keep | 0 | Jul | 2021 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
VEGA BAJA | 2021-07-02 06:51 | 2021-07-02 15:59 | 50 | 009:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA 1 X 25 EN TRANSFORMADOR SE REMPLAZO AISLADOR | B21070300066 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 548 | 2021-07-02 | 27400 | keep | 0 | Jul | 2021 | 0.018662 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-02 07:00 | 2021-07-02 08:55 | 6 | 001:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21070200000 | New_Event | Bad Weather | Include | Include | Weather | 115 | 2021-07-02 | 690 | keep | 0 | Jul | 2021 | 0.00046996 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2021-07-02 07:00 | 2021-07-02 13:15 | 709 | 006:15 | T | DESGANCHE | SE RETIRO RAMAS DE ENTRE LAS LINEAS SE CERRO INTERRUPTOR | M21070200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 375 | 2021-07-02 | 265875 | keep | 0 | Jul | 2021 | 0.18109 | 0.0004829 | Sustained | FALSE | TRUE | Not_TMED_Event | 709
SAN JUAN | 2021-07-02 07:12 | 2021-07-02 07:13 | 601 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21070200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-02 | 601 | keep | 0 | Jul | 2021 | 0.00040934 | 0.00040934 | Momentary | FALSE | FALSE | Not_TMED_Event | 601
BAYAMON | 2021-07-02 07:28 | 2021-07-02 10:22 | 8 | 002:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR EN PEDESTAL | S21062800031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 174 | 2021-07-02 | 1392 | keep | 0 | Jul | 2021 | 0.00094808 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-07-02 08:12 | 2021-07-02 08:27 | 1 | 000:15 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO CAUSA | C21070200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2021-07-02 | 15 | keep | 0 | Jul | 2021 | 1.0216e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-07-02 08:45 | 2021-07-02 13:33 | 100 | 004:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DE AISLADOR Y SE REALIZO DESGANCHE | A21070200043 | New_Event | Wire Down | Include | Include | Equipment | 288 | 2021-07-02 | 28800 | keep | 0 | Jul | 2021 | 0.019616 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-02 08:57 | 2021-07-02 09:08 | 12 | 000:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN CORTE DE LINEA SE RETIRO CULEBRA DE LA LINEA | R21070200000 | New_Event |  |  | Include | Wildlife | 11 | 2021-07-02 | 132 | keep | 0 | Jul | 2021 | 8.9905e-05 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
PONCE | 2021-07-02 09:00 | 2021-07-04 12:29 | 100 | 051:29 | P | DESGANCHE | 2 X 200 EN CONVERTIDOR | P21070200023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3089 | 2021-07-02 | 308900 | keep | 0 | Jul | 2021 | 0.21039 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2021-07-02 09:07 | 2021-07-02 13:00 | 30 | 003:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | B21070200078 | New_Event | Wire Down | Include | Include | Equipment | 233 | 2021-07-02 | 6990 | keep | 0 | Jul | 2021 | 0.0047609 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-07-02 09:11 | 2021-07-02 09:35 | 10 | 000:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21070200058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 24 | 2021-07-02 | 240 | keep | 0 | Jul | 2021 | 0.00016346 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-02 09:19 | 2021-07-03 15:15 | 65 | 029:56 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070300041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1796 | 2021-07-02 | 116740 | keep | 0 | Jul | 2021 | 0.079511 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
AGUADILLA | 2021-07-02 09:19 | 2021-07-02 10:30 | 1337 | 001:11 | T | DESGANCHE | SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21070200147 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2021-07-02 | 94927 | keep | 0 | Jul | 2021 | 0.064654 | 0.00091062 | Sustained | FALSE | TRUE | Not_TMED_Event | 1337
FAJARDO | 2021-07-02 09:25 | 2021-07-02 09:26 | 3003 | 000:01 | T | DESGANCHE | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | R21070200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-02 | 3003 | keep | 0 | Jul | 2021 | 0.0020453 | 0.0020453 | Momentary | FALSE | FALSE | Not_TMED_Event | 3003
FAJARDO | 2021-07-02 09:26 | 2021-07-02 14:15 | 100 | 004:49 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21070200032 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 289 | 2021-07-02 | 28900 | keep | 0 | Jul | 2021 | 0.019684 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-07-02 09:30 | 2021-07-02 13:34 | 3 | 004:04 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO PUENTES PARA REMPLAZO DE AISLADOR PARTIDO | M21070200147 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 244 | 2021-07-02 | 732 | keep | 0 | Jul | 2021 | 0.00049856 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-07-02 09:38 | 2021-07-04 11:22 | 73 | 049:44 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | S21070200006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2984 | 2021-07-02 | 217832 | keep | 0 | Jul | 2021 | 0.14836 | 4.972e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 73
BAYAMON | 2021-07-02 09:38 | 2021-07-03 13:11 | 50 | 027:33 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER Y 1 X 65 EN RISER | B21070200017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1653 | 2021-07-02 | 82650 | keep | 0 | Jul | 2021 | 0.056293 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2021-07-02 09:38 | 2021-07-02 10:47 | 40 | 001:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | R21070200006 | New_Event | Cutout Failure | Include | Include | Equipment | 69 | 2021-07-02 | 2760 | keep | 0 | Jul | 2021 | 0.0018798 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-07-02 09:38 | 2021-07-02 11:30 | 72 | 001:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR SE REEMPLAZO DISCO ROTO Y REPARARON BAJANTE DE LINEA A CAJA | R21070200001 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 112 | 2021-07-02 | 8064 | keep | 0 | Jul | 2021 | 0.0054924 | 4.9039e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 72
CAGUAS | 2021-07-02 09:38 | 2021-07-02 18:25 | 30 | 008:47 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO CAUSA | C21070200015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 527 | 2021-07-02 | 15810 | keep | 0 | Jul | 2021 | 0.010768 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-07-02 09:38 | 2021-07-03 09:08 | 65 | 023:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | C21070200008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1410 | 2021-07-02 | 91650 | keep | 0 | Jul | 2021 | 0.062422 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
CAGUAS | 2021-07-02 09:38 | 2021-07-02 15:37 | 36 | 005:59 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C21070200010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 359 | 2021-07-02 | 12924 | keep | 0 | Jul | 2021 | 0.0088025 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
AGUADILLA | 2021-07-02 09:38 | 2021-07-02 17:30 | 200 | 007:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M21070200028 | New_Event | Wire Down | Include | Include | Equipment | 472 | 2021-07-02 | 94400 | keep | 0 | Jul | 2021 | 0.064295 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
VEGA BAJA | 2021-07-02 09:38 | 2021-07-02 19:25 | 8 | 009:47 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21070200012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 587 | 2021-07-02 | 4696 | keep | 0 | Jul | 2021 | 0.0031984 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-07-02 09:38 | 2021-07-02 17:40 | 25 | 008:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO Y SE CERRO CORTE DE LINEA | B21070200007 | New_Event | Wire Down | Include | Include | Equipment | 482 | 2021-07-02 | 12050 | keep | 0 | Jul | 2021 | 0.0082072 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-07-02 09:38 | 2021-07-02 16:36 | 50 | 006:58 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | B21070200011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 418 | 2021-07-02 | 20900 | keep | 0 | Jul | 2021 | 0.014235 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-02 09:41 | 2021-07-02 17:16 | 40 | 007:35 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21070200012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 455 | 2021-07-02 | 18200 | keep | 0 | Jul | 2021 | 0.012396 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-02 09:41 | 2021-07-02 20:50 | 200 | 011:09 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | B21070200038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 669 | 2021-07-02 | 133800 | keep | 0 | Jul | 2021 | 0.091131 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-07-02 09:41 | 2021-07-02 19:19 | 12 | 009:38 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVISIONAL AEREO PARA DAR SERVICIO AL T-2 DE UNO EXISTENTE | B21070200028 | New_Event | UG Cable Fault | Include | Include | Equipment | 578 | 2021-07-02 | 6936 | keep | 0 | Jul | 2021 | 0.0047241 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-07-02 09:41 | 2021-07-03 10:12 | 50 | 024:31 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070200064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1471 | 2021-07-02 | 73550 | keep | 0 | Jul | 2021 | 0.050095 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-07-02 09:41 | 2021-07-02 11:19 | 40 | 001:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21070200022 | New_Event | Bad Weather | Include | Include | Weather | 98 | 2021-07-02 | 3920 | keep | 0 | Jul | 2021 | 0.0026699 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-07-02 09:41 | 2021-07-02 16:13 | 40 | 006:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA REPARO BAJANTE LINEA A CAJA | C21070200021 | New_Event | Wire Down | Include | Include | Equipment | 392 | 2021-07-02 | 15680 | keep | 0 | Jul | 2021 | 0.01068 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-07-02 09:42 | 2021-07-02 14:25 | 40 | 004:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA RETEZO LINEAS | R21070200016 | New_Event | Wire Down | Include | Include | Equipment | 283 | 2021-07-02 | 11320 | keep | 0 | Jul | 2021 | 0.00771 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-02 09:42 | 2021-07-02 13:42 | 30 | 004:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA | B21070200045 | New_Event | Cutout Failure | Include | Include | Equipment | 240 | 2021-07-02 | 7200 | keep | 0 | Jul | 2021 | 0.0049039 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-07-02 09:42 | 2021-07-02 13:45 | 200 | 004:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21070200078 | New_Event | Bad Weather | Include | Include | Weather | 243 | 2021-07-02 | 48600 | keep | 0 | Jul | 2021 | 0.033101 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-07-02 09:42 | 2021-07-02 13:15 | 70 | 003:33 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070200081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2021-07-02 | 14910 | keep | 0 | Jul | 2021 | 0.010155 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
UTUADO | 2021-07-02 09:42 | 2021-07-02 18:55 | 80 | 009:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA LINEAS PRIMARIAS CRUZADAS | A21070200028 | New_Event | Wire Down | Include | Include | Equipment | 553 | 2021-07-02 | 44240 | keep | 0 | Jul | 2021 | 0.030132 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-07-02 09:42 | 2021-07-02 19:41 | 60 | 009:59 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21070200053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 599 | 2021-07-02 | 35940 | keep | 0 | Jul | 2021 | 0.024479 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-07-02 09:44 | 2021-07-02 12:51 | 12 | 003:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA | B21070200059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 187 | 2021-07-02 | 2244 | keep | 0 | Jul | 2021 | 0.0015284 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-07-02 09:44 | 2021-07-02 14:11 | 40 | 004:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C21070200047 | New_Event |  |  | Include | Wildlife | 267 | 2021-07-02 | 10680 | keep | 0 | Jul | 2021 | 0.0072741 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-07-02 09:44 | 2021-07-02 13:44 | 10 | 004:00 | P | SECUNDARIA/DESGANCHE | ABRIO TRANSFORMADOR PARA DESGANCHAR Y LEVANTAR SECUNDARIA | C21070200039 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 240 | 2021-07-02 | 2400 | keep | 0 | Jul | 2021 | 0.0016346 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-07-02 09:44 | 2021-07-02 17:07 | 96 | 007:23 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU - 7 NO CAUSA | C21070200053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 443 | 2021-07-02 | 42528 | keep | 0 | Jul | 2021 | 0.028966 | 6.5385e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 96
BARRANQUITAS | 2021-07-02 09:44 | 2021-07-02 11:53 | 65 | 002:09 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO CAUSA | C21070200054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 129 | 2021-07-02 | 8385 | keep | 0 | Jul | 2021 | 0.005711 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
PONCE | 2021-07-02 09:44 | 2021-07-02 13:02 | 50 | 003:18 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | P21070200029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2021-07-02 | 9900 | keep | 0 | Jul | 2021 | 0.0067428 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-02 09:44 | 2021-07-02 12:37 | 3 | 002:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21070200122 | New_Event | Bad Weather | Include | Include | Weather | 173 | 2021-07-02 | 519 | keep | 0 | Jul | 2021 | 0.00035349 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-07-02 09:44 | 2021-07-02 16:39 | 40 | 006:55 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21070200105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 415 | 2021-07-02 | 16600 | keep | 0 | Jul | 2021 | 0.011306 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-07-02 09:44 | 2021-07-04 15:40 | 100 | 053:56 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21070200030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3236 | 2021-07-02 | 323600 | keep | 0 | Jul | 2021 | 0.2204 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-07-02 09:44 | 2021-07-02 17:00 | 125 | 007:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21070200029 | New_Event | Bad Weather | Include | Include | Weather | 436 | 2021-07-02 | 54500 | keep | 0 | Jul | 2021 | 0.03712 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
BAYAMON | 2021-07-02 09:44 | 2021-07-02 17:24 | 45 | 007:40 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21070200063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 460 | 2021-07-02 | 20700 | keep | 0 | Jul | 2021 | 0.014099 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
MAYAGÃœEZ | 2021-07-02 09:52 | 2021-07-02 18:25 | 80 | 008:33 | P | LINEA DE TRANSMISION 38KV | SE ABRIO CORTE DE LINEA PARA TRABAJOS EN LINEA DE TRANSMISION 1500 Y 2000 | M21070200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 513 | 2021-07-02 | 41040 | keep | 0 | Jul | 2021 | 0.027952 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
UTUADO | 2021-07-02 09:52 | 2021-07-02 14:50 | 2 | 004:58 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA POR LO MISMO | A21070200051 | New_Event | Service Transformer Failure | Include | Include | Equipment | 298 | 2021-07-02 | 596 | keep | 0 | Jul | 2021 | 0.00040593 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2021-07-02 09:53 | 2021-07-02 10:56 | 2671 | 001:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR SE ABRIO MACHETES EN CARR 132 KM 9.2 SECTOR LOS RUBERTE DOS FASES PRIMARIAS PARTIDAS | P21070200036 | New_Event | Wire Down | Include | Include | Equipment | 63 | 2021-07-02 | 168273 | keep | 0 | Jul | 2021 | 0.11461 | 0.0018192 | Sustained | FALSE | FALSE | Not_TMED_Event | 2671
SAN JUAN | 2021-07-02 09:57 | 2021-07-02 09:58 | 3957 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21070200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-02 | 3957 | keep | 0 | Jul | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
HUMACAO | 2021-07-02 09:59 | 2021-07-02 13:28 | 8 | 003:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO BAJANTE DE CAJA A TRANSFORMADOR | C21070200061 | New_Event | Wire Down | Include | Include | Equipment | 209 | 2021-07-02 | 1672 | keep | 0 | Jul | 2021 | 0.0011388 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2021-07-02 10:00 | 2021-07-02 12:00 | 35 | 002:00 | P | DESCONECTIVO DEFECTUOSO | REMPLAZO DE MACHETE QUEMADO | P21070200065 | New_Event | Switch Failure | Include | Include | Equipment | 120 | 2021-07-02 | 4200 | keep | 0 | Jul | 2021 | 0.0028606 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2021-07-02 10:03 | 2021-07-02 15:40 | 35 | 005:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA Y SE REEMPLAZO CAJA PRIMARIA | S21070200039 | New_Event | Cutout Failure | Include | Include | Equipment | 337 | 2021-07-02 | 11795 | keep | 0 | Jul | 2021 | 0.0080335 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
PONCE | 2021-07-02 10:03 | 2021-07-02 18:35 | 18 | 008:32 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | P21070200039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 512 | 2021-07-02 | 9216 | keep | 0 | Jul | 2021 | 0.006277 | 1.226e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 18
BAYAMON | 2021-07-02 10:04 | 2021-07-02 11:14 | 30 | 001:10 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | S21070200040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2021-07-02 | 2100 | keep | 0 | Jul | 2021 | 0.0014303 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
HUMACAO | 2021-07-02 10:04 | 2021-07-02 11:50 | 15 | 001:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21070200000 | New_Event | Bad Weather | Include | Include | Weather | 106 | 2021-07-02 | 1590 | keep | 0 | Jul | 2021 | 0.0010829 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-07-02 10:05 | 2021-07-02 16:46 | 53 | 006:41 | P | CABLE SOTERRADO AVERIADO | SE ALAMBRO TRAMO T-14A A 150 | S21070200041 | New_Event | UG Cable Fault | Include | Include | Equipment | 401 | 2021-07-02 | 21253 | keep | 0 | Jul | 2021 | 0.014475 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
UTUADO | 2021-07-02 10:06 | 2021-07-03 20:00 | 150 | 033:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | A21070200131 | New_Event | Wire Down | Include | Include | Equipment | 2034 | 2021-07-02 | 305100 | keep | 0 | Jul | 2021 | 0.2078 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
UTUADO | 2021-07-02 10:06 | 2021-07-03 15:14 | 125 | 029:08 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21070200052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1748 | 2021-07-02 | 218500 | keep | 0 | Jul | 2021 | 0.14882 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
CAGUAS | 2021-07-02 10:10 | 2021-07-02 11:46 | 2 | 001:36 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER NO CAUSA | C21070200064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2021-07-02 | 192 | keep | 0 | Jul | 2021 | 0.00013077 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2021-07-02 10:17 | 2021-07-02 10:18 | 3 | 000:01 | T | DESGANCHE | DISPARO INTERRUPTOR Y SE CERRO POR CONTROL | B21070200080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-02 | 3 | keep | 0 | Jul | 2021 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-07-02 10:17 | 2021-07-02 10:18 | 61 | 000:01 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL | B21070200080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-02 | 61 | keep | 0 | Jul | 2021 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2021-07-02 10:22 | 2021-07-02 10:23 | 3 | 000:01 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL | B21070200080 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-02 | 3 | keep | 0 | Jul | 2021 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-07-02 10:22 | 2021-07-02 10:23 | 61 | 000:01 | T | DESGANCHE | DISPARO Y SE CERRO POR SCADA | B21070200080 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-02 | 61 | keep | 0 | Jul | 2021 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
SAN JUAN | 2021-07-02 10:24 | 2021-07-02 18:16 | 65 | 007:52 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21070200043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 472 | 2021-07-02 | 30680 | keep | 0 | Jul | 2021 | 0.020896 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
CAGUAS | 2021-07-02 10:24 | 2021-07-02 12:31 | 7 | 002:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR REPARO SECUNDARIA | C21070200067 | New_Event | Secondary Wire Down | Include | Include | Equipment | 127 | 2021-07-02 | 889 | keep | 0 | Jul | 2021 | 0.00060549 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-07-02 10:29 | 2021-07-02 11:11 | 3 | 000:42 | T | DESGANCHE | SE ABRIO AMARRE ENTRE 1707-02 Y 1707-03 | B21070200080 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 42 | 2021-07-02 | 126 | keep | 0 | Jul | 2021 | 8.5818e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-07-02 10:29 | 2021-07-02 12:50 | 61 | 002:21 | T | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETES DE AMARRE | B21070200080 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 141 | 2021-07-02 | 8601 | keep | 0 | Jul | 2021 | 0.0058581 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
UTUADO | 2021-07-02 10:32 | 2021-07-02 17:40 | 50 | 007:08 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21070200056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 428 | 2021-07-02 | 21400 | keep | 0 | Jul | 2021 | 0.014575 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-07-02 10:38 | 2021-07-02 18:30 | 125 | 007:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 50 EN CORTE DE LINEA SE REPARO LINEAS ZAFADAS DE AISLADORES | A21070200059 | New_Event | Wire Down | Include | Include | Equipment | 472 | 2021-07-02 | 59000 | keep | 0 | Jul | 2021 | 0.040185 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
BAYAMON | 2021-07-02 10:39 | 2021-07-02 17:09 | 1 | 006:30 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | B21070200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 390 | 2021-07-02 | 390 | keep | 0 | Jul | 2021 | 0.00026563 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-07-02 10:40 | 2021-07-04 15:40 | 100 | 052:60 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | M21070200303 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3180 | 2021-07-02 | 318000 | keep | 0 | Jul | 2021 | 0.21659 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
GUAYAMA | 2021-07-02 10:46 | 2021-07-02 13:02 | 80 | 002:16 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | P21070200061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2021-07-02 | 10880 | keep | 0 | Jul | 2021 | 0.0074103 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-07-02 10:50 | 2021-07-02 15:30 | 50 | 004:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21070200062 | New_Event | Bad Weather | Include | Include | Weather | 280 | 2021-07-02 | 14000 | keep | 0 | Jul | 2021 | 0.0095353 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-07-02 10:50 | 2021-07-02 20:25 | 200 | 009:35 | P | LINEA DE TRANSMISION | SE ABRIÃ“ CORTE DE LINEA PARA TRABAJOS EN LINEA 1900 | A21070200000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 575 | 2021-07-02 | 115000 | keep | 0 | Jul | 2021 | 0.078326 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
YAUCO | 2021-07-02 10:56 | 2021-07-02 20:00 | 1900 | 009:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DOS TRAMOS DE LINEA PRIMARIA EN EL PISO | P21070200019 | New_Event | Wire Down | Include | Include | Equipment | 544 | 2021-07-02 | 1033600 | keep | 0 | Jul | 2021 | 0.70398 | 0.0012941 | Sustained | FALSE | TRUE | Not_TMED_Event | 1900
ARECIBO | 2021-07-02 10:58 | 2021-07-02 14:53 | 15 | 003:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIÃ“ TRANSFORMADOR PARA REPARAR NEUTRAL SECUNDARIO | A21070200065 | New_Event | Secondary Wire Down | Include | Include | Equipment | 235 | 2021-07-02 | 3525 | keep | 0 | Jul | 2021 | 0.0024009 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-07-02 11:09 | 2021-07-02 14:02 | 25 | 002:53 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | P21070200064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2021-07-02 | 4325 | keep | 0 | Jul | 2021 | 0.0029457 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-07-02 11:23 | 2021-07-02 11:24 | 1408 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21070200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-02 | 1408 | keep | 0 | Jul | 2021 | 0.00095898 | 0.00095898 | Momentary | FALSE | FALSE | Not_TMED_Event | 1408
BAYAMON | 2021-07-02 11:23 | 2021-07-02 11:24 | 455 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21070200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-02 | 455 | keep | 0 | Jul | 2021 | 0.0003099 | 0.0003099 | Momentary | FALSE | FALSE | Not_TMED_Event | 455
SAN JUAN | 2021-07-02 11:27 | 2021-07-02 11:28 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21070200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-02 | 2203 | keep | 0 | Jul | 2021 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
PONCE | 2021-07-02 11:28 | 2021-07-02 11:29 | 778 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21070200072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-02 | 778 | keep | 0 | Jul | 2021 | 0.00052989 | 0.00052989 | Momentary | FALSE | FALSE | Not_TMED_Event | 778
ARECIBO | 2021-07-02 11:28 | 2021-07-02 17:11 | 15 | 005:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR 1 X 10 EN TRANSFORMADOR | A21070200071 | New_Event | Bad Weather | Include | Include | Weather | 343 | 2021-07-02 | 5145 | keep | 0 | Jul | 2021 | 0.0035042 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-07-02 11:38 | 2021-07-02 14:57 | 1 | 003:19 | P | DESGANCHE | 3 X 100 EN CORTE DE LINEA | S21070200052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2021-07-02 | 199 | keep | 0 | Jul | 2021 | 0.00013554 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-07-02 11:42 | 2021-07-02 11:43 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21070200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-02 | 2203 | keep | 0 | Jul | 2021 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
CAGUAS | 2021-07-02 11:42 | 2021-07-02 11:43 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21070200085 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-02 | 1565 | keep | 0 | Jul | 2021 | 0.0010659 | 0.0010659 | Momentary | FALSE | TRUE | Not_TMED_Event | 1565
CAGUAS | 2021-07-02 11:42 | 2021-07-02 11:43 | 976 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21070200085 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-02 | 976 | keep | 0 | Jul | 2021 | 0.00066475 | 0.00066475 | Momentary | FALSE | TRUE | Not_TMED_Event | 976
CAGUAS | 2021-07-02 11:42 | 2021-07-02 11:43 | 548 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21070200085 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-02 | 548 | keep | 0 | Jul | 2021 | 0.00037324 | 0.00037324 | Momentary | FALSE | TRUE | Not_TMED_Event | 548
CAGUAS | 2021-07-02 11:42 | 2021-07-02 11:43 | 315 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21070200087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-02 | 315 | keep | 0 | Jul | 2021 | 0.00021455 | 0.00021455 | Momentary | FALSE | TRUE | Not_TMED_Event | 315
CAGUAS | 2021-07-02 11:42 | 2021-07-02 11:43 | 870 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21070200087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-02 | 870 | keep | 0 | Jul | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | TRUE | Not_TMED_Event | 870
CAGUAS | 2021-07-02 11:42 | 2021-07-02 11:43 | 2906 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21070200088 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-02 | 2906 | keep | 0 | Jul | 2021 | 0.0019793 | 0.0019793 | Momentary | FALSE | TRUE | Not_TMED_Event | 2906
CAGUAS | 2021-07-02 11:42 | 2021-07-02 11:43 | 2343 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21070200088 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-02 | 2343 | keep | 0 | Jul | 2021 | 0.0015958 | 0.0015958 | Momentary | FALSE | TRUE | Not_TMED_Event | 2343
ARECIBO | 2021-07-02 11:45 | 2021-07-02 12:34 | 500 | 000:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CONVERTIDOR PARA SECCIONALIZAR LINEA PRIMARIA ROTA Y SE CERRO EL CONVERTIDOR | A21070200000 | New_Event | Wire Down | Include | Include | Equipment | 49 | 2021-07-02 | 24500 | keep | 0 | Jul | 2021 | 0.016687 | 0.00034055 | Sustained | FALSE | TRUE | Not_TMED_Event | 500
ARECIBO | 2021-07-02 11:45 | 2021-07-03 11:55 | 10 | 024:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21070200123 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1450 | 2021-07-02 | 14500 | keep | 0 | Jul | 2021 | 0.0098759 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-07-02 11:46 | 2021-07-05 13:46 | 12 | 073:60 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S21070200053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4440 | 2021-07-02 | 53280 | keep | 0 | Jul | 2021 | 0.036289 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2021-07-02 11:47 | 2021-07-02 15:11 | 57 | 003:24 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | P21070200074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2021-07-02 | 11628 | keep | 0 | Jul | 2021 | 0.0079198 | 3.8822e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 57
UTUADO | 2021-07-02 11:47 | 2021-07-03 09:42 | 50 | 021:55 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A21070100077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1315 | 2021-07-02 | 65750 | keep | 0 | Jul | 2021 | 0.044782 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-02 11:48 | 2021-07-03 10:33 | 10 | 022:45 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21070200091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1365 | 2021-07-02 | 13650 | keep | 0 | Jul | 2021 | 0.009297 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-07-02 11:55 | 2021-07-02 14:02 | 14 | 002:07 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 75KVA X 75KVA | C21070200089 | New_Event | Service Transformer Failure | Include | Include | Equipment | 127 | 2021-07-02 | 1778 | keep | 0 | Jul | 2021 | 0.001211 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2021-07-02 11:56 | 2021-07-03 07:38 | 30 | 019:42 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21070200056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1182 | 2021-07-02 | 35460 | keep | 0 | Jul | 2021 | 0.024152 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
HUMACAO | 2021-07-02 12:03 | 2021-07-02 17:09 | 100 | 005:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 50 EN CORTE DE LINEA REMPLAZO DISCO Y AISLADOR | C21070200090 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 306 | 2021-07-02 | 30600 | keep | 0 | Jul | 2021 | 0.020842 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-07-02 12:05 | 2021-07-02 12:07 | 1565 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21070200091 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-02 | 3130 | keep | 0 | Jul | 2021 | 0.0021318 | 0.0010659 | Momentary | FALSE | TRUE | Not_TMED_Event | 1565
CAGUAS | 2021-07-02 12:05 | 2021-07-02 12:07 | 976 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21070200091 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-02 | 1952 | keep | 0 | Jul | 2021 | 0.0013295 | 0.00066475 | Momentary | FALSE | TRUE | Not_TMED_Event | 976
CAGUAS | 2021-07-02 12:05 | 2021-07-02 12:07 | 548 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21070200091 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-02 | 1096 | keep | 0 | Jul | 2021 | 0.00074648 | 0.00037324 | Momentary | FALSE | TRUE | Not_TMED_Event | 548
CAGUAS | 2021-07-02 12:05 | 2021-07-02 12:07 | 315 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21070200092 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-02 | 630 | keep | 0 | Jul | 2021 | 0.00042909 | 0.00021455 | Momentary | FALSE | TRUE | Not_TMED_Event | 315
CAGUAS | 2021-07-02 12:05 | 2021-07-02 12:07 | 870 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21070200092 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-02 | 1740 | keep | 0 | Jul | 2021 | 0.0011851 | 0.00059255 | Momentary | FALSE | TRUE | Not_TMED_Event | 870
CAGUAS | 2021-07-02 12:05 | 2021-07-02 12:07 | 2906 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21070200093 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-02 | 5812 | keep | 0 | Jul | 2021 | 0.0039585 | 0.0019793 | Momentary | FALSE | TRUE | Not_TMED_Event | 2906
CAGUAS | 2021-07-02 12:05 | 2021-07-02 12:07 | 2343 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21070200093 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-02 | 4686 | keep | 0 | Jul | 2021 | 0.0031916 | 0.0015958 | Momentary | FALSE | TRUE | Not_TMED_Event | 2343
BARRANQUITAS | 2021-07-02 12:11 | 2021-07-02 17:00 | 30 | 004:49 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | C21070200094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 289 | 2021-07-02 | 8670 | keep | 0 | Jul | 2021 | 0.0059051 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-07-02 12:12 | 2021-07-03 12:13 | 80 | 024:01 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21070200094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1441 | 2021-07-02 | 115280 | keep | 0 | Jul | 2021 | 0.078517 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-07-02 12:13 | 2021-07-03 16:56 | 160 | 028:43 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGNCHE | B21070200083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1723 | 2021-07-02 | 275680 | keep | 0 | Jul | 2021 | 0.18776 | 0.00010898 | Sustained | FALSE | TRUE | Not_TMED_Event | 160
SAN JUAN | 2021-07-02 12:17 | 2021-07-02 12:21 | 870 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S21070200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-07-02 | 3480 | keep | 0 | Jul | 2021 | 0.0023702 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
ARECIBO | 2021-07-02 12:18 | 2021-07-02 13:23 | 1185 | 001:05 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE ABRIO EL AMARRE ENTRE EL 8002-03 Y 8002-04 Y SE CERRO EL INTERRUPTOR 8002-03 | A21070200000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 65 | 2021-07-02 | 77025 | keep | 0 | Jul | 2021 | 0.052461 | 0.0008071 | Sustained | FALSE | FALSE | Not_TMED_Event | 1185
ARECIBO | 2021-07-02 12:18 | 2021-07-02 15:53 | 63 | 003:35 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADORES ROTOS Y SE DEJO LA CARGA POR EL 8002-03 | A21070200000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 215 | 2021-07-02 | 13545 | keep | 0 | Jul | 2021 | 0.0092254 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
BAYAMON | 2021-07-02 12:23 | 2021-07-02 14:09 | 1 | 001:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21070200097 | New_Event | Secondary Wire Down | Include | Include | Equipment | 106 | 2021-07-02 | 106 | keep | 0 | Jul | 2021 | 7.2196e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-07-02 12:30 | 2021-07-02 19:30 | 18 | 007:00 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21070200088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 420 | 2021-07-02 | 7560 | keep | 0 | Jul | 2021 | 0.0051491 | 1.226e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 18
ARECIBO | 2021-07-02 12:30 | 2021-07-02 16:37 | 10 | 004:07 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21070200089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 247 | 2021-07-02 | 2470 | keep | 0 | Jul | 2021 | 0.0016823 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-07-02 12:34 | 2021-07-02 18:50 | 1 | 006:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA Y SE CERRO PUENTES PRIMARIOS | A21070200000 | Partial_restoration | Wire Down | Include | Include | Equipment | 376 | 2021-07-02 | 376 | keep | 0 | Jul | 2021 | 0.00025609 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-07-02 12:40 | 2021-07-03 17:50 | 40 | 029:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070200164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1750 | 2021-07-02 | 70000 | keep | 0 | Jul | 2021 | 0.047677 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-07-02 12:40 | 2021-07-02 12:41 | 2620 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21070200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-02 | 2620 | keep | 0 | Jul | 2021 | 0.0017845 | 0.0017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 2620
MAYAGÃœEZ | 2021-07-02 12:45 | 2021-07-02 16:40 | 60 | 003:55 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO | M21070200166 | New_Event | Defective Pole | Include | Include | Equipment | 235 | 2021-07-02 | 14100 | keep | 0 | Jul | 2021 | 0.0096034 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2021-07-02 12:45 | 2021-07-03 16:29 | 100 | 027:44 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | B21070200101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1664 | 2021-07-02 | 166400 | keep | 0 | Jul | 2021 | 0.11333 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-02 12:51 | 2021-07-05 12:37 | 20 | 071:46 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21070200072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4306 | 2021-07-02 | 86120 | keep | 0 | Jul | 2021 | 0.058656 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CANOVANAS | 2021-07-02 12:51 | 2021-07-02 18:40 | 30 | 005:49 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21070200035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 349 | 2021-07-02 | 10470 | keep | 0 | Jul | 2021 | 0.0071311 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-07-02 12:52 | 2021-07-02 16:30 | 2 | 003:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21070200169 | New_Event | Bad Weather | Include | Include | Weather | 218 | 2021-07-02 | 436 | keep | 0 | Jul | 2021 | 0.00029696 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
MAYAGÃœEZ | 2021-07-02 12:54 | 2021-07-02 16:40 | 125 | 003:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO EN LINEA PRIMARIA AVERIADA | M21070200048 | New_Event | Wire Down | Include | Include | Equipment | 226 | 2021-07-02 | 28250 | keep | 0 | Jul | 2021 | 0.019241 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
CAGUAS | 2021-07-02 12:55 | 2021-07-03 13:16 | 80 | 024:21 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C21070200101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1461 | 2021-07-02 | 116880 | keep | 0 | Jul | 2021 | 0.079606 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-07-02 12:56 | 2021-07-02 14:28 | 12 | 001:32 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21070200006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 92 | 2021-07-02 | 1104 | keep | 0 | Jul | 2021 | 0.00075193 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-07-02 13:08 | 2021-07-03 10:34 | 2 | 021:26 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21070200063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1286 | 2021-07-02 | 2572 | keep | 0 | Jul | 2021 | 0.0017518 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
BAYAMON | 2021-07-02 13:10 | 2021-07-02 14:23 | 3 | 001:13 | T | DESGANCHE | SE REALIZO DESGANCHE DE BAMBUAS Y SE CERRO POR SCADA | B21070200080 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 73 | 2021-07-02 | 219 | keep | 0 | Jul | 2021 | 0.00014916 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-02 13:10 | 2021-07-02 14:23 | 61 | 001:13 | T | DESGANCHE | SE REALIZO DESGANCHE DE BAMBUAS Y SE CERRO POR SCADA 1707-02 QUE LLEVA EL 1707-03 | B21070200080 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 73 | 2021-07-02 | 4453 | keep | 0 | Jul | 2021 | 0.0030329 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-02 13:11 | 2021-07-03 17:43 | 12 | 028:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA AVERIADA POSITEC | B21070200102 | New_Event | Cutout Failure | Include | Include | Equipment | 1712 | 2021-07-02 | 20544 | keep | 0 | Jul | 2021 | 0.013992 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-07-02 13:22 | 2021-07-02 14:00 | 60 | 000:38 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21070200036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 38 | 2021-07-02 | 2280 | keep | 0 | Jul | 2021 | 0.0015529 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-07-02 13:42 | 2021-07-02 14:05 | 1565 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21070200110 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-07-02 | 35995 | keep | 0 | Jul | 2021 | 0.024516 | 0.0010659 | Sustained | FALSE | TRUE | Not_TMED_Event | 1565
CAGUAS | 2021-07-02 13:42 | 2021-07-02 14:05 | 976 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21070200110 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-07-02 | 22448 | keep | 0 | Jul | 2021 | 0.015289 | 0.00066475 | Sustained | FALSE | TRUE | Not_TMED_Event | 976
CAGUAS | 2021-07-02 13:42 | 2021-07-02 14:05 | 548 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21070200110 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-07-02 | 12604 | keep | 0 | Jul | 2021 | 0.0085845 | 0.00037324 | Sustained | FALSE | TRUE | Not_TMED_Event | 548
CAGUAS | 2021-07-02 13:42 | 2021-07-02 14:05 | 315 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21070200116 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-07-02 | 7245 | keep | 0 | Jul | 2021 | 0.0049345 | 0.00021455 | Sustained | FALSE | TRUE | Not_TMED_Event | 315
CAGUAS | 2021-07-02 13:42 | 2021-07-02 14:05 | 870 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21070200116 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-07-02 | 20010 | keep | 0 | Jul | 2021 | 0.013629 | 0.00059255 | Sustained | FALSE | TRUE | Not_TMED_Event | 870
CAGUAS | 2021-07-02 13:42 | 2021-07-02 14:05 | 2906 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21070200118 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-07-02 | 66838 | keep | 0 | Jul | 2021 | 0.045523 | 0.0019793 | Sustained | FALSE | TRUE | Not_TMED_Event | 2906
CAGUAS | 2021-07-02 13:42 | 2021-07-02 14:05 | 2343 | 000:23 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21070200118 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2021-07-02 | 53889 | keep | 0 | Jul | 2021 | 0.036704 | 0.0015958 | Sustained | FALSE | TRUE | Not_TMED_Event | 2343
MAYAGÃœEZ | 2021-07-02 13:42 | 2021-07-02 13:49 | 5 | 000:07 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25 KVA X 25 KVA AVERIADO | M21070200178 | New_Event | Service Transformer Failure | Include | Include | Equipment | 7 | 2021-07-02 | 35 | keep | 0 | Jul | 2021 | 2.3838e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2021-07-02 13:47 | 2021-07-02 16:08 | 7 | 002:21 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R21070200037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 141 | 2021-07-02 | 987 | keep | 0 | Jul | 2021 | 0.00067224 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-07-02 13:48 | 2021-07-02 19:46 | 230 | 005:58 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO EN EL AREA | M21070200048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 358 | 2021-07-02 | 82340 | keep | 0 | Jul | 2021 | 0.056081 | 0.00015665 | Sustained | FALSE | TRUE | Not_TMED_Event | 230
BAYAMON | 2021-07-02 13:58 | 2021-07-02 14:00 | 723 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA NEUTRAL CRUZADO LLEVA 1711-05 | B21070200117 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2021-07-02 | 1446 | keep | 0 | Jul | 2021 | 0.00098486 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2021-07-02 13:58 | 2021-07-02 14:00 | 1976 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO 1711-02 SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA NEUTRAL CRUZADO LLEVA 1711-05 | B21070200117 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2021-07-02 | 3952 | keep | 0 | Jul | 2021 | 0.0026917 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
PONCE | 2021-07-02 14:00 | 2021-07-02 14:01 | 1212 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21070200094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-02 | 1212 | keep | 0 | Jul | 2021 | 0.00082549 | 0.00082549 | Momentary | FALSE | FALSE | Not_TMED_Event | 1212
CAGUAS | 2021-07-02 14:04 | 2021-07-02 18:36 | 50 | 004:32 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21070200133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 272 | 2021-07-02 | 13600 | keep | 0 | Jul | 2021 | 0.0092629 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-07-02 14:08 | 2021-07-03 10:27 | 10 | 020:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO DE XMR | P21070200095 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1219 | 2021-07-02 | 12190 | keep | 0 | Jul | 2021 | 0.0083026 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-07-02 14:15 | 2021-07-02 14:17 | 1617 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C21070200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-02 | 3234 | keep | 0 | Jul | 2021 | 0.0022027 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
BARRANQUITAS | 2021-07-02 14:16 | 2021-07-02 16:34 | 80 | 002:18 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | C21070200140 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 138 | 2021-07-02 | 11040 | keep | 0 | Jul | 2021 | 0.0075193 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BARRANQUITAS | 2021-07-02 14:17 | 2021-07-02 19:10 | 65 | 004:53 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C21070200143 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 293 | 2021-07-02 | 19045 | keep | 0 | Jul | 2021 | 0.012971 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BAYAMON | 2021-07-02 14:21 | 2021-07-02 16:00 | 1 | 001:39 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B21070200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2021-07-02 | 99 | keep | 0 | Jul | 2021 | 6.7428e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2021-07-02 14:27 | 2021-07-02 19:38 | 50 | 005:11 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C21070200145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 311 | 2021-07-02 | 15550 | keep | 0 | Jul | 2021 | 0.010591 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-07-02 14:28 | 2021-07-03 15:30 | 150 | 025:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M21070200189 | New_Event | Cutout Failure | Include | Include | Equipment | 1502 | 2021-07-02 | 225300 | keep | 0 | Jul | 2021 | 0.15345 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-07-02 14:29 | 2021-07-05 13:16 | 50 | 070:47 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO | S21070200074 | New_Event | Switch Failure | Include | Include | Equipment | 4247 | 2021-07-02 | 212350 | keep | 0 | Jul | 2021 | 0.14463 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-07-02 14:36 | 2021-07-02 14:37 | 1212 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21070200101 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-02 | 1212 | keep | 0 | Jul | 2021 | 0.00082549 | 0.00082549 | Momentary | FALSE | FALSE | Not_TMED_Event | 1212
SAN JUAN | 2021-07-02 14:38 | 2021-07-02 14:39 | 2391 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21070200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-02 | 2391 | keep | 0 | Jul | 2021 | 0.0016285 | 0.0016285 | Momentary | FALSE | FALSE | Not_TMED_Event | 2391
BAYAMON | 2021-07-02 14:38 | 2021-07-02 14:39 | 878 | 000:01 | T | ERROR HUMANO | SE ABRIO 1903-05 SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA NEUTRAL CRUZADO LLEVA 1714-05 SE ABRIO A PETICION DE SUPERVISOR PERO NO ERA EL CORRECTO | B21070200119 | New_Event | Human Error | Include | Include | Other | 1 | 2021-07-02 | 878 | keep | 0 | Jul | 2021 | 0.000598 | 0.000598 | Momentary | FALSE | FALSE | Not_TMED_Event | 878
BAYAMON | 2021-07-02 14:38 | 2021-07-02 14:39 | 1310 | 000:01 | T | ERROR HUMANO | SE ABRIO 1903-05 SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA NEUTRAL CRUZADO LLEVA 1714-05 SE ABRIO A PETICION DE SUPERVISOR PERO NO ERA EL CORRECTO | S21070200119 | New_Event | Human Error | Include | Include | Other | 1 | 2021-07-02 | 1310 | keep | 0 | Jul | 2021 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
ARECIBO | 2021-07-02 14:39 | 2021-07-02 19:11 | 80 | 004:32 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21070200113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 272 | 2021-07-02 | 21760 | keep | 0 | Jul | 2021 | 0.014821 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-07-02 14:40 | 2021-07-02 15:36 | 723 | 000:56 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1711-02 POR CONDUCTOR CRUZADO LLEVA 1711-05 | B21070200117 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 56 | 2021-07-02 | 40488 | keep | 0 | Jul | 2021 | 0.027576 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2021-07-02 14:40 | 2021-07-02 15:36 | 1976 | 000:56 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1711-02 POR CONDUCTOR CRUZADO LLEVA 1711-05 | B21070200117 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 56 | 2021-07-02 | 110656 | keep | 0 | Jul | 2021 | 0.075367 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2021-07-02 14:40 | 2021-07-02 15:36 | 1408 | 000:56 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR CONDUCTOR CRUZADO CARGA POR EL 1714-03 | B21070200104 | New_Event | Wire Down | Include | Include | Equipment | 56 | 2021-07-02 | 78848 | keep | 0 | Jul | 2021 | 0.053703 | 0.00095898 | Sustained | FALSE | FALSE | Not_TMED_Event | 1408
BAYAMON | 2021-07-02 14:40 | 2021-07-02 15:36 | 455 | 000:56 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR CONDUCTOR CRUZADO LLEVA 1714-02 | B21070200104 | New_Event | Wire Down | Include | Include | Equipment | 56 | 2021-07-02 | 25480 | keep | 0 | Jul | 2021 | 0.017354 | 0.0003099 | Sustained | FALSE | FALSE | Not_TMED_Event | 455
HUMACAO | 2021-07-02 14:41 | 2021-07-02 17:44 | 50 | 003:03 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21070200150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2021-07-02 | 9150 | keep | 0 | Jul | 2021 | 0.006232 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-07-02 14:44 | 2021-07-02 19:40 | 1 | 004:56 | P | NO SE REPORTO CAUSA | 1 X 10 EN BANCO DE TRANSFORMADORES | R21070200046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 296 | 2021-07-02 | 296 | keep | 0 | Jul | 2021 | 0.0002016 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-07-02 14:47 | 2021-07-03 10:41 | 75 | 019:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE RETEZO LINEA MONOFASICA | C21070200152 | New_Event | Wire Down | Include | Include | Equipment | 1194 | 2021-07-02 | 89550 | keep | 0 | Jul | 2021 | 0.060992 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
ARECIBO | 2021-07-02 14:51 | 2021-07-02 15:43 | 437 | 000:52 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIÃ“ INTERRUPTOR POR SEGURIDAD PARA REMPLAZAR AISLADORES EN EL 8002-04 AUTORIZO EL ING EDWIN COSME | A21070200000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 52 | 2021-07-02 | 22724 | keep | 0 | Jul | 2021 | 0.015477 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2021-07-02 14:59 | 2021-07-02 15:00 | 4431 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21070200118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-02 | 4431 | keep | 0 | Jul | 2021 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
YAUCO | 2021-07-02 15:00 | 2021-07-02 18:40 | 261 | 003:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO DE CAJA PRIMARIA QUEMADA | P21070200131 | New_Event | Cutout Failure | Include | Include | Equipment | 220 | 2021-07-02 | 57420 | keep | 0 | Jul | 2021 | 0.039109 | 0.00017777 | Sustained | FALSE | FALSE | Not_TMED_Event | 261
ARECIBO | 2021-07-02 15:02 | 2021-07-02 15:03 | 2620 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA | A21070200000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-02 | 2620 | keep | 0 | Jul | 2021 | 0.0017845 | 0.0017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 2620
ARECIBO | 2021-07-02 15:03 | 2021-07-02 18:20 | 50 | 003:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21070200120 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 197 | 2021-07-02 | 9850 | keep | 0 | Jul | 2021 | 0.0067088 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-07-02 15:06 | 2021-07-02 20:06 | 40 | 005:00 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21070200049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 300 | 2021-07-02 | 12000 | keep | 0 | Jul | 2021 | 0.0081731 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-07-02 15:23 | 2021-07-02 16:44 | 80 | 001:21 | P | ESTRUCTURA AVERIADA | SE ABRIO PUENTES PARA SECCIONALIZAR POSTE PARTIDO | C21070200162 | New_Event | Defective Pole | Include | Include | Equipment | 81 | 2021-07-02 | 6480 | keep | 0 | Jul | 2021 | 0.0044135 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2021-07-02 15:26 | 2021-07-03 13:51 | 50 | 022:25 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21070200113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1345 | 2021-07-02 | 67250 | keep | 0 | Jul | 2021 | 0.045804 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-07-02 15:29 | 2021-07-03 17:35 | 60 | 026:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | P21070200110 | New_Event | Bad Weather | Include | Include | Weather | 1566 | 2021-07-02 | 93960 | keep | 0 | Jul | 2021 | 0.063996 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-07-02 15:36 | 2021-07-02 19:09 | 100 | 003:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE LEVANTO NEUTRAL PRIMARIO PARTIDO | C21070200169 | New_Event | Wire Down | Include | Include | Equipment | 213 | 2021-07-02 | 21300 | keep | 0 | Jul | 2021 | 0.014507 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-02 15:40 | 2021-07-02 15:41 | 726 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21070200000 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2021-07-02 | 726 | keep | 0 | Jul | 2021 | 0.00049448 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-07-02 15:40 | 2021-07-02 17:37 | 80 | 001:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 Y 1 X 50 EN CORTES DE LINEA MAL TIEMPO | R21070200050 | New_Event | Bad Weather | Include | Include | Weather | 117 | 2021-07-02 | 9360 | keep | 0 | Jul | 2021 | 0.0063751 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-07-02 15:41 | 2021-07-02 16:57 | 35 | 001:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA Y SE REEMPLAZO CAJA | S21070200039 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 76 | 2021-07-02 | 2660 | keep | 0 | Jul | 2021 | 0.0018117 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-07-02 15:41 | 2021-07-02 15:42 | 723 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA NEUTRAL CRUZADO LLEVA 1711-05 | B21070200136 | Partial_restoration | Wire Down | Include | Include | Equipment | 1 | 2021-07-02 | 723 | keep | 0 | Jul | 2021 | 0.00049243 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-02 15:41 | 2021-07-02 15:42 | 1976 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO 1711-02 SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA NEUTRAL CRUZADO LLEVA 1711-05 | B21070200117 | Partial_restoration | Wire Down | Include | Include | Equipment | 1 | 2021-07-02 | 1976 | keep | 0 | Jul | 2021 | 0.0013458 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-02 15:46 | 2021-07-03 10:43 | 6 | 018:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21070200137 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1137 | 2021-07-02 | 6822 | keep | 0 | Jul | 2021 | 0.0046464 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-07-02 15:47 | 2021-07-02 18:51 | 50 | 003:04 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21070200138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 184 | 2021-07-02 | 9200 | keep | 0 | Jul | 2021 | 0.0062661 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-02 15:48 | 2021-07-02 15:57 | 20 | 000:09 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | R21070200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2021-07-02 | 180 | keep | 0 | Jul | 2021 | 0.0001226 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-07-02 15:48 | 2021-07-03 13:38 | 100 | 021:50 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21070200051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1310 | 2021-07-02 | 131000 | keep | 0 | Jul | 2021 | 0.089224 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-07-02 15:49 | 2021-07-03 09:10 | 175 | 017:21 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | C21070200175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1041 | 2021-07-02 | 182175 | keep | 0 | Jul | 2021 | 0.12408 | 0.00011919 | Sustained | FALSE | TRUE | Not_TMED_Event | 175
PONCE | 2021-07-02 16:05 | 2021-07-03 09:00 | 100 | 016:55 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA POR DESGANCHE | P21070200121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1015 | 2021-07-02 | 101500 | keep | 0 | Jul | 2021 | 0.069131 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-07-02 16:28 | 2021-07-03 16:00 | 80 | 023:32 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M21070200232 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1412 | 2021-07-02 | 112960 | keep | 0 | Jul | 2021 | 0.076937 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-07-02 16:38 | 2021-07-03 12:36 | 60 | 019:58 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C21070200192 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1198 | 2021-07-02 | 71880 | keep | 0 | Jul | 2021 | 0.048957 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
YAUCO | 2021-07-02 16:38 | 2021-07-03 12:18 | 100 | 019:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA POR CAJA PRIMARIA QUEMADA | P21070200127 | New_Event | Cutout Failure | Include | Include | Equipment | 1180 | 2021-07-02 | 118000 | keep | 0 | Jul | 2021 | 0.080369 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-07-02 16:44 | 2021-07-02 19:02 | 20 | 002:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A21070200133 | New_Event | Wire Down | Include | Include | Equipment | 138 | 2021-07-02 | 2760 | keep | 0 | Jul | 2021 | 0.0018798 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2021-07-02 16:48 | 2021-07-03 10:15 | 13 | 017:27 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C21070200196 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1047 | 2021-07-02 | 13611 | keep | 0 | Jul | 2021 | 0.0092704 | 8.8542e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 13
ARECIBO | 2021-07-02 16:59 | 2021-07-04 19:00 | 30 | 050:01 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | A21070200135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3001 | 2021-07-02 | 90030 | keep | 0 | Jul | 2021 | 0.061319 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-07-02 17:00 | 2021-07-03 21:06 | 50 | 028:06 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | S21070200104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1686 | 2021-07-02 | 84300 | keep | 0 | Jul | 2021 | 0.057416 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-02 17:21 | 2021-07-03 09:55 | 60 | 016:34 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER | B21070200152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 994 | 2021-07-02 | 59640 | keep | 0 | Jul | 2021 | 0.040621 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2021-07-02 17:23 | 2021-07-02 17:39 | 10 | 000:16 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | R21070200058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 16 | 2021-07-02 | 160 | keep | 0 | Jul | 2021 | 0.00010898 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
VEGA BAJA | 2021-07-02 17:23 | 2021-07-03 14:34 | 36 | 021:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PARARRAYO Y DISCO | B21070200153 | New_Event | Cutout Failure | Include | Include | Equipment | 1271 | 2021-07-02 | 45756 | keep | 0 | Jul | 2021 | 0.031164 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
BAYAMON | 2021-07-02 17:43 | 2021-07-02 20:56 | 3 | 003:13 | T | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO POR SCADA 1707-02 QUE LLEVA 1707-03 | B21070200000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 193 | 2021-07-02 | 579 | keep | 0 | Jul | 2021 | 0.00039435 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-02 17:43 | 2021-07-02 20:56 | 61 | 003:13 | T | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO POR SCADA 1707-02 QUE LLEVA 1707-03 | B21070200000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 193 | 2021-07-02 | 11773 | keep | 0 | Jul | 2021 | 0.0080185 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-02 17:55 | 2021-07-03 11:03 | 50 | 017:08 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21070200157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1028 | 2021-07-02 | 51400 | keep | 0 | Jul | 2021 | 0.035008 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-02 18:06 | 2021-07-03 09:43 | 100 | 015:37 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070200249 | New_Event | Vegetation Contact | Include | Include | Vegetation | 937 | 2021-07-02 | 93700 | keep | 0 | Jul | 2021 | 0.063819 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-07-02 18:25 | 2021-07-03 10:04 | 30 | 015:39 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA CAMION CRUZO LINEAS | A21070100077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 939 | 2021-07-02 | 28170 | keep | 0 | Jul | 2021 | 0.019186 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
HUMACAO | 2021-07-02 18:28 | 2021-07-02 23:33 | 22 | 005:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA CRUCE POR GLOBO | C21070200208 | New_Event |  |  | Include | Wildlife | 305 | 2021-07-02 | 6710 | keep | 0 | Jul | 2021 | 0.0045702 | 1.4984e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 22
CAGUAS | 2021-07-02 18:39 | 2021-07-02 21:50 | 150 | 003:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA LEVANTO CONDUCTOR | C21070200000 | New_Event | Wire Down | Include | Include | Equipment | 191 | 2021-07-02 | 28650 | keep | 0 | Jul | 2021 | 0.019513 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-07-02 19:00 | 2021-07-03 14:25 | 8 | 019:25 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21070200160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1165 | 2021-07-02 | 9320 | keep | 0 | Jul | 2021 | 0.0063478 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-07-02 19:42 | 2021-07-02 20:29 | 50 | 000:47 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21070200061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 47 | 2021-07-02 | 2350 | keep | 0 | Jul | 2021 | 0.0016006 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-07-02 19:43 | 2021-07-03 18:33 | 80 | 022:50 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA POR DESGANCHE | P21070200143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1370 | 2021-07-02 | 109600 | keep | 0 | Jul | 2021 | 0.074648 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BARRANQUITAS | 2021-07-02 19:57 | 2021-07-03 09:40 | 55 | 013:43 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO AISLADOR ROTO | C21070200212 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 823 | 2021-07-02 | 45265 | keep | 0 | Jul | 2021 | 0.03083 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
MAYAGÃœEZ | 2021-07-02 20:00 | 2021-07-03 12:50 | 70 | 016:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M21070200259 | New_Event | Cutout Failure | Include | Include | Equipment | 1010 | 2021-07-02 | 70700 | keep | 0 | Jul | 2021 | 0.048153 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2021-07-02 20:00 | 2021-07-03 09:19 | 60 | 013:19 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21070200166 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 799 | 2021-07-02 | 47940 | keep | 0 | Jul | 2021 | 0.032652 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
PONCE | 2021-07-02 20:04 | 2021-07-02 20:05 | 1863 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P21070200157 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-02 | 1863 | keep | 0 | Jul | 2021 | 0.0012689 | 0.0012689 | Momentary | FALSE | TRUE | Not_TMED_Event | 1863
PONCE | 2021-07-02 20:04 | 2021-07-02 20:05 | 708 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0500 | P21070200157 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-02 | 708 | keep | 0 | Jul | 2021 | 0.00048222 | 0.00048222 | Momentary | FALSE | TRUE | Not_TMED_Event | 708
YAUCO | 2021-07-02 20:04 | 2021-07-02 20:05 | 502 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P21070200156 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-02 | 502 | keep | 0 | Jul | 2021 | 0.00034191 | 0.00034191 | Momentary | FALSE | TRUE | Not_TMED_Event | 502
YAUCO | 2021-07-02 20:04 | 2021-07-02 20:05 | 2747 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P21070200156 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-02 | 2747 | keep | 0 | Jul | 2021 | 0.001871 | 0.001871 | Momentary | FALSE | TRUE | Not_TMED_Event | 2747
YAUCO | 2021-07-02 20:04 | 2021-07-02 20:05 | 1587 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P21070200156 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-02 | 1587 | keep | 0 | Jul | 2021 | 0.0010809 | 0.0010809 | Momentary | FALSE | TRUE | Not_TMED_Event | 1587
YAUCO | 2021-07-02 20:04 | 2021-07-02 20:05 | 2671 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P21070200156 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-02 | 2671 | keep | 0 | Jul | 2021 | 0.0018192 | 0.0018192 | Momentary | FALSE | TRUE | Not_TMED_Event | 2671
MAYAGÃœEZ | 2021-07-02 20:37 | 2021-07-03 03:04 | 300 | 006:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21070200262 | New_Event | Bad Weather | Include | Include | Weather | 387 | 2021-07-02 | 116100 | keep | 0 | Jul | 2021 | 0.079075 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
CAGUAS | 2021-07-02 20:39 | 2021-07-03 15:19 | 150 | 018:40 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO | C21070200245 | New_Event | Bad Weather | Include | Include | Weather | 1120 | 2021-07-02 | 168000 | keep | 0 | Jul | 2021 | 0.11442 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
PONCE | 2021-07-02 20:40 | 2021-07-02 20:41 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210702000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-02 | 3744 | keep | 0 | Jul | 2021 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2021-07-02 20:41 | 2021-07-06 12:15 | 10 | 087:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 FUSE DE 10 AMP EN XMR AVE CRUZO LINEAS | P21070200073 | New_Event |  |  | Include | Wildlife | 5254 | 2021-07-02 | 52540 | keep | 0 | Jul | 2021 | 0.035785 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-07-02 20:46 | 2021-07-03 09:56 | 145 | 013:10 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO | C21070200254 | New_Event | Bad Weather | Include | Include | Weather | 790 | 2021-07-02 | 114550 | keep | 0 | Jul | 2021 | 0.078019 | 9.8759e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 145
CAGUAS | 2021-07-02 20:54 | 2021-07-05 10:34 | 10 | 061:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA EN VARIOS PUNTOS | C21062600067 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 3700 | 2021-07-02 | 37000 | keep | 0 | Jul | 2021 | 0.025201 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-07-02 20:55 | 2021-07-03 10:35 | 208 | 013:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21070200230 | New_Event | Bad Weather | Include | Include | Weather | 820 | 2021-07-02 | 170560 | keep | 0 | Jul | 2021 | 0.11617 | 0.00014167 | Sustained | FALSE | TRUE | Not_TMED_Event | 208
ARECIBO | 2021-07-02 20:55 | 2021-07-03 11:00 | 20 | 014:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIÃ“ TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21070200161 | New_Event | Secondary Wire Down | Include | Include | Equipment | 845 | 2021-07-02 | 16900 | keep | 0 | Jul | 2021 | 0.011511 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
YAUCO | 2021-07-02 20:56 | 2021-07-04 13:00 | 79 | 040:04 | P | DESGANCHE | 1 X 100 Y 1 X 50 EN DISTINTOS CORTES DE LINEA POR DESGANCHE | P21071200154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2404 | 2021-07-02 | 189916 | keep | 0 | Jul | 2021 | 0.12935 | 5.3807e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 79
HUMACAO | 2021-07-02 20:57 | 2021-07-03 09:42 | 7 | 012:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZO DE BARRA EN PEDESTAL | C21070200263 | New_Event | Secondary Wire Down | Include | Include | Equipment | 765 | 2021-07-02 | 5355 | keep | 0 | Jul | 2021 | 0.0036473 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-07-02 21:08 | 2021-07-03 18:40 | 50 | 021:32 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | M21070200273 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1292 | 2021-07-02 | 64600 | keep | 0 | Jul | 2021 | 0.043999 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-02 21:21 | 2021-07-03 11:31 | 80 | 014:10 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070200275 | New_Event | Vegetation Contact | Include | Include | Vegetation | 850 | 2021-07-02 | 68000 | keep | 0 | Jul | 2021 | 0.046314 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-07-02 21:22 | 2021-07-03 08:15 | 80 | 010:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21070200165 | New_Event | Bad Weather | Include | Include | Weather | 653 | 2021-07-02 | 52240 | keep | 0 | Jul | 2021 | 0.03558 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-07-02 21:26 | 2021-07-04 10:43 | 69 | 037:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21070200266 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2237 | 2021-07-02 | 154353 | keep | 0 | Jul | 2021 | 0.10513 | 4.6996e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 69
MAYAGÃœEZ | 2021-07-02 21:35 | 2021-07-03 14:20 | 65 | 016:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21070200282 | New_Event | Bad Weather | Include | Include | Weather | 1005 | 2021-07-02 | 65325 | keep | 0 | Jul | 2021 | 0.044493 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
MAYAGÃœEZ | 2021-07-02 21:57 | 2021-07-03 20:20 | 200 | 022:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 Y 2 X 140 SE REPARO ALAMBRE PARTIDO | M21070200291 | New_Event | Wire Down | Include | Include | Equipment | 1343 | 2021-07-02 | 268600 | keep | 0 | Jul | 2021 | 0.18294 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-07-02 22:05 | 2021-07-03 09:54 | 80 | 011:49 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21070200199 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 709 | 2021-07-02 | 56720 | keep | 0 | Jul | 2021 | 0.038632 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CANOVANAS | 2021-07-02 22:11 | 2021-07-03 13:02 | 30 | 014:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | R21070200086 | New_Event | Bad Weather | Include | Include | Weather | 891 | 2021-07-02 | 26730 | keep | 0 | Jul | 2021 | 0.018206 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
VEGA BAJA | 2021-07-02 22:12 | 2021-07-03 09:25 | 60 | 011:13 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B21070200201 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 673 | 2021-07-02 | 40380 | keep | 0 | Jul | 2021 | 0.027503 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-07-02 22:46 | 2021-07-02 22:47 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR SCADA | C21070200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-02 | 870 | keep | 0 | Jul | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CANOVANAS | 2021-07-02 22:51 | 2021-07-03 07:42 | 539 | 008:51 | T | OTRAS CAUSAS | SE TRANSFIRIO LA CARGA AL 2302-03 POR AVERIA EN EL TRANSFORMADOR 2305 DISPARO POR TEMPERATURA ABANICOS NO ESTABAN FUNCIONANDO | R21070200104 | New_Event | Other Causes | Include | Include | Other | 531 | 2021-07-02 | 286209 | keep | 0 | Jul | 2021 | 0.19494 | 0.00036711 | Sustained | FALSE | FALSE | Not_TMED_Event | 539
CANOVANAS | 2021-07-02 22:51 | 2021-07-03 07:42 | 3012 | 008:51 | T | OTRAS CAUSAS | SE TRANSFIRIO LA CARGA AL 2005-10 POR AVERIA EN EL TRANSFORMADOR 2305 DISPARO POR TEMPERATURA ABANICOS NO ESTABAN FUNCIONANDO | R21070300020 | New_Event | Other Causes | Include | Include | Other | 531 | 2021-07-02 | 1599372 | keep | 0 | Jul | 2021 | 1.0893 | 0.0020515 | Sustained | FALSE | FALSE | Not_TMED_Event | 3012
CANOVANAS | 2021-07-02 22:51 | 2021-07-03 09:26 | 2106 | 010:35 | T | OTRAS CAUSAS | SE TRANSFIRIO PARTE DE LA CARGA AL 2005-10 POR AVERIA EN EL TRANSFORMADOR 2305 DISPARO POR TEMPERATURA ABANICOS NO ESTABAN FUNCIONANDO | R21070300019 | New_Event | Other Causes | Include | Include | Other | 635 | 2021-07-02 | 1337310 | keep | 0 | Jul | 2021 | 0.91084 | 0.0014344 | Sustained | FALSE | FALSE | Not_TMED_Event | 2106
CANOVANAS | 2021-07-02 22:51 | 2021-07-03 07:42 | 635 | 008:51 | T | OTRAS CAUSAS | SE TRANSFIRIO LA CARGA AL 2302-03 POR AVERIA EN EL TRANSFORMADOR 2305 DISPARO POR TEMPERATURA ABANICOS NO ESTABAN FUNCIONANDO | R21070200104 | New_Event | Other Causes | Include | Include | Other | 531 | 2021-07-02 | 337185 | keep | 0 | Jul | 2021 | 0.22966 | 0.0004325 | Sustained | FALSE | FALSE | Not_TMED_Event | 635
BARRANQUITAS | 2021-07-02 23:08 | 2021-07-03 14:29 | 70 | 015:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21070200272 | New_Event | Bad Weather | Include | Include | Weather | 921 | 2021-07-02 | 64470 | keep | 0 | Jul | 2021 | 0.04391 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
HUMACAO | 2021-07-02 23:33 | 2021-07-02 23:34 | 3896 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21070200273 | Additional_clients |  |  | Include | Wildlife | 1 | 2021-07-02 | 3896 | keep | 0 | Jul | 2021 | 0.0026535 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-07-02 23:34 | 2021-07-03 12:32 | 22 | 012:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA CRUCE POR GLOBO | C21070200208 | 1st_after_momentary |  |  | Include | Wildlife | 778 | 2021-07-02 | 17116 | keep | 0 | Jul | 2021 | 0.011658 | 1.4984e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 22
YAUCO | 2021-07-02 23:40 | 2021-07-04 14:04 | 100 | 038:24 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P21070200168 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2304 | 2021-07-02 | 230400 | keep | 0 | Jul | 2021 | 0.15692 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-07-02 23:57 | 2021-07-03 13:51 | 50 | 013:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21070200172 | New_Event | Vegetation Contact | Include | Include | Vegetation | 834 | 2021-07-02 | 41700 | keep | 0 | Jul | 2021 | 0.028402 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-07-03 00:09 | 2021-07-03 09:50 | 70 | 009:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21070300001 | New_Event | Bad Weather | Include | Include | Weather | 581 | 2021-07-03 | 40670 | keep | 0 | Jul | 2021 | 0.0277 | 4.7677e-05 | Sustained | FALSE | TRUE | TMED_Event | 70
ARECIBO | 2021-07-03 00:26 | 2021-07-03 11:04 | 100 | 010:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | A21070300001 | New_Event | Bad Weather | Include | Include | Weather | 638 | 2021-07-03 | 63800 | keep | 0 | Jul | 2021 | 0.043454 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
YAUCO | 2021-07-03 01:02 | 2021-07-03 01:03 | 591 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210703000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 591 | keep | 0 | Jul | 2021 | 0.00040253 | 0.00040253 | Momentary | FALSE | FALSE | TMED_Event | 591
YAUCO | 2021-07-03 01:03 | 2021-07-03 20:36 | 591 | 019:33 | S | DESCONECTIVO DEFECTUOSO | SE REMPLAZO BASE DE PORTAFUSIBLE DE 38 KV EN LA ALTA DEL TRANSFORMADOR | P21070300051 | New_Event | Switch Failure | Include | Include | Equipment | 1173 | 2021-07-03 | 693243 | keep | 0 | Jul | 2021 | 0.47216 | 0.00040253 | Sustained | FALSE | FALSE | TMED_Event | 591
MAYAGÃœEZ | 2021-07-03 01:14 | 2021-07-03 16:10 | 100 | 014:56 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070300009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 896 | 2021-07-03 | 89600 | keep | 0 | Jul | 2021 | 0.061026 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
BAYAMON | 2021-07-03 01:20 | 2021-07-03 01:21 | 1210 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 1210 | keep | 0 | Jul | 2021 | 0.00082413 | 0.00082413 | Momentary | FALSE | FALSE | TMED_Event | 1210
HUMACAO | 2021-07-03 01:27 | 2021-07-03 12:00 | 135 | 010:33 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C21070300005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 633 | 2021-07-03 | 85455 | keep | 0 | Jul | 2021 | 0.058203 | 9.1948e-05 | Sustained | FALSE | TRUE | TMED_Event | 135
MAYAGÃœEZ | 2021-07-03 01:49 | 2021-07-03 17:10 | 75 | 015:21 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070300012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 921 | 2021-07-03 | 69075 | keep | 0 | Jul | 2021 | 0.047047 | 5.1082e-05 | Sustained | FALSE | TRUE | TMED_Event | 75
MAYAGÃœEZ | 2021-07-03 02:00 | 2021-07-03 18:45 | 50 | 016:45 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | M21070300015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1005 | 2021-07-03 | 50250 | keep | 0 | Jul | 2021 | 0.034225 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
MAYAGÃœEZ | 2021-07-03 02:13 | 2021-07-03 17:40 | 100 | 015:27 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070300019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 927 | 2021-07-03 | 92700 | keep | 0 | Jul | 2021 | 0.063138 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
CAGUAS | 2021-07-03 02:40 | 2021-07-04 09:06 | 300 | 030:26 | P | DESGANCHE | 2 X 80 Y 1 X 65 EN CORTE DE LINEA | C21070300007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1826 | 2021-07-03 | 547800 | keep | 0 | Jul | 2021 | 0.3731 | 0.00020433 | Sustained | FALSE | TRUE | TMED_Event | 300
MAYAGÃœEZ | 2021-07-03 03:04 | 2021-07-03 11:22 | 3147 | 008:18 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 498 | 2021-07-03 | 1567206 | keep | 0 | Jul | 2021 | 1.0674 | 0.0021434 | Sustained | FALSE | TRUE | TMED_Event | 3147
MAYAGÃœEZ | 2021-07-03 03:04 | 2021-07-03 11:22 | 4304 | 008:18 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 498 | 2021-07-03 | 2143392 | keep | 0 | Jul | 2021 | 1.4599 | 0.0029314 | Sustained | FALSE | TRUE | TMED_Event | 4304
PONCE | 2021-07-03 03:30 | 2021-07-03 03:31 | 969 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210703000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 969 | keep | 0 | Jul | 2021 | 0.00065998 | 0.00065998 | Momentary | FALSE | FALSE | TMED_Event | 969
BARRANQUITAS | 2021-07-03 03:35 | 2021-07-03 09:40 | 50 | 006:05 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZARON DISCOS ROTOS | C21070300159 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 365 | 2021-07-03 | 18250 | keep | 0 | Jul | 2021 | 0.01243 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
CAGUAS | 2021-07-03 03:42 | 2021-07-03 03:43 | 2907 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C21070300018 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-03 | 2907 | keep | 0 | Jul | 2021 | 0.0019799 | 0.0019799 | Momentary | FALSE | FALSE | TMED_Event | 2907
CAGUAS | 2021-07-03 03:43 | 2021-07-03 21:29 | 60 | 017:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTO CONDUCTOR NO FUNDIO | C21070300021 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1066 | 2021-07-03 | 63960 | keep | 0 | Jul | 2021 | 0.043563 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
PONCE | 2021-07-03 03:59 | 2021-07-05 09:58 | 50 | 053:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA DEL PISO | P21040300020 | New_Event | Wire Down | Include | Include | Equipment | 3239 | 2021-07-03 | 161950 | keep | 0 | Jul | 2021 | 0.1103 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
ARECIBO | 2021-07-03 03:59 | 2021-07-03 07:09 | 1644 | 003:10 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR RECIERRE EN OFF NO SE REPORTO CAUSA NO HAY CONTROL POR SCADA | A21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 190 | 2021-07-03 | 312360 | keep | 0 | Jul | 2021 | 0.21275 | 0.0011197 | Sustained | FALSE | FALSE | TMED_Event | 1644
CAGUAS | 2021-07-03 04:07 | 2021-07-03 04:08 | 1709 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 1709 | keep | 0 | Jul | 2021 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | TMED_Event | 1709
MAYAGÃœEZ | 2021-07-03 05:58 | 2021-07-04 12:50 | 100 | 030:52 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070300239 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1852 | 2021-07-03 | 185200 | keep | 0 | Jul | 2021 | 0.12614 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
MAYAGÃœEZ | 2021-07-03 06:11 | 2021-07-05 08:02 | 6 | 049:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21070300095 | New_Event | Bad Weather | Include | Include | Weather | 2991 | 2021-07-03 | 17946 | keep | 0 | Jul | 2021 | 0.012223 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
PONCE | 2021-07-03 06:25 | 2021-07-03 16:00 | 75 | 009:35 | S | ANIMAL U OBJETO EXTRAÃ‘O | AVE CRUZO FASE DE LA BARRA DE LA SUBESTACION/ SE RETIRO AVE/ SE REMPLAZARON 3 PARARRAYOS Y 3 CAJA PORTA FUSIBLES DE 20A EN MEDICION REMOTA Y SE REMONTO LOCKOUT | P210703000XX | New_Event |  |  | Include | Wildlife | 575 | 2021-07-03 | 43125 | keep | 0 | Jul | 2021 | 0.029372 | 5.1082e-05 | Sustained | FALSE | FALSE | TMED_Event | 75
PONCE | 2021-07-03 06:25 | 2021-07-03 11:35 | 449 | 005:10 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE SUBESTACION. SE TRANSFIRIO LA CARGA DEL 4402-02 AL 4603-01 EN LO REMPLAZABAN LOS 3 PARARRAYOS PARA DEJAR MENOS CLIENTES SIN SERVICIO | P210703000XX | New_Event |  |  | Include | Wildlife | 310 | 2021-07-03 | 139190 | keep | 0 | Jul | 2021 | 0.094802 | 0.00030581 | Sustained | FALSE | FALSE | TMED_Event | 449
MAYAGÃœEZ | 2021-07-03 06:26 | 2021-07-03 06:27 | 810 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 810 | keep | 0 | Jul | 2021 | 0.00055169 | 0.00055169 | Momentary | FALSE | TRUE | TMED_Event | 810
MAYAGÃœEZ | 2021-07-03 06:26 | 2021-07-03 06:27 | 1235 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 1235 | keep | 0 | Jul | 2021 | 0.00084115 | 0.00084115 | Momentary | FALSE | TRUE | TMED_Event | 1235
MAYAGÃœEZ | 2021-07-03 06:26 | 2021-07-03 06:27 | 93 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 93 | keep | 0 | Jul | 2021 | 6.3342e-05 | 6.3342e-05 | Momentary | FALSE | TRUE | TMED_Event | 93
MAYAGÃœEZ | 2021-07-03 06:26 | 2021-07-03 06:27 | 1825 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 1825 | keep | 0 | Jul | 2021 | 0.001243 | 0.001243 | Momentary | FALSE | TRUE | TMED_Event | 1825
MAYAGÃœEZ | 2021-07-03 06:26 | 2021-07-03 06:27 | 3230 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE DE LINEA 5600 | M21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 3230 | keep | 0 | Jul | 2021 | 0.0021999 | 0.0021999 | Momentary | FALSE | TRUE | TMED_Event | 3230
CANOVANAS | 2021-07-03 06:45 | 2021-07-03 06:46 | 7621 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | R21070300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-03 | 7621 | keep | 0 | Jul | 2021 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | TMED_Event | 7621
CANOVANAS | 2021-07-03 06:46 | 2021-07-03 15:41 | 80 | 008:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | R21070300049 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 535 | 2021-07-03 | 42800 | keep | 0 | Jul | 2021 | 0.029151 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
MAYAGÃœEZ | 2021-07-03 06:47 | 2021-07-03 07:52 | 810 | 001:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21070300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 65 | 2021-07-03 | 52650 | keep | 0 | Jul | 2021 | 0.03586 | 0.00055169 | Sustained | FALSE | TRUE | TMED_Event | 810
MAYAGÃœEZ | 2021-07-03 06:47 | 2021-07-03 07:52 | 1235 | 001:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21070300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 65 | 2021-07-03 | 80275 | keep | 0 | Jul | 2021 | 0.054675 | 0.00084115 | Sustained | FALSE | TRUE | TMED_Event | 1235
MAYAGÃœEZ | 2021-07-03 06:47 | 2021-07-03 07:52 | 93 | 001:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21070300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 65 | 2021-07-03 | 6045 | keep | 0 | Jul | 2021 | 0.0041172 | 6.3342e-05 | Sustained | FALSE | TRUE | TMED_Event | 93
MAYAGÃœEZ | 2021-07-03 06:47 | 2021-07-03 07:52 | 1825 | 001:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21070300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 65 | 2021-07-03 | 118625 | keep | 0 | Jul | 2021 | 0.080795 | 0.001243 | Sustained | FALSE | TRUE | TMED_Event | 1825
MAYAGÃœEZ | 2021-07-03 06:47 | 2021-07-03 07:52 | 3230 | 001:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 65 | 2021-07-03 | 209950 | keep | 0 | Jul | 2021 | 0.143 | 0.0021999 | Sustained | FALSE | TRUE | TMED_Event | 3230
MAYAGÃœEZ | 2021-07-03 06:57 | 2021-07-03 06:58 | 1142 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA | M21070300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-03 | 1142 | keep | 0 | Jul | 2021 | 0.00077781 | 0.00077781 | Momentary | FALSE | FALSE | TMED_Event | 1142
MAYAGÃœEZ | 2021-07-03 06:58 | 2021-07-04 17:45 | 40 | 034:47 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070300496 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2087 | 2021-07-03 | 83480 | keep | 0 | Jul | 2021 | 0.056858 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
MAYAGÃœEZ | 2021-07-03 07:11 | 2021-07-03 07:12 | 1417 | 000:01 | T | DESGANCHE | DISPARO DEL INTERRUPTOR RECIERRE EN OFF NO SE REPORTO CAUSA | M21070300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-03 | 1417 | keep | 0 | Jul | 2021 | 0.00096511 | 0.00096511 | Momentary | FALSE | FALSE | TMED_Event | 1417
MAYAGÃœEZ | 2021-07-03 07:39 | 2021-07-03 07:40 | 1417 | 000:01 | T | DESGANCHE | DISPARO DEL INTERRUPTOR RECIERRE EN OFF NO SE REPORTO CAUSA | M21070300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-03 | 1417 | keep | 0 | Jul | 2021 | 0.00096511 | 0.00096511 | Momentary | FALSE | FALSE | TMED_Event | 1417
MAYAGÃœEZ | 2021-07-03 07:40 | 2021-07-03 10:08 | 80 | 002:28 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 148 | 2021-07-03 | 11840 | keep | 0 | Jul | 2021 | 0.0080642 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
ARECIBO | 2021-07-03 07:43 | 2021-07-05 18:27 | 20 | 058:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A21070300023 | New_Event | Wire Down | Include | Include | Equipment | 3524 | 2021-07-03 | 70480 | keep | 0 | Jul | 2021 | 0.048004 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
SAN JUAN | 2021-07-03 07:45 | 2021-07-03 07:46 | 3718 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTROR SE CERRO POR SCADA | S21070300000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-03 | 3718 | keep | 0 | Jul | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | TMED_Event | 3718
SAN JUAN | 2021-07-03 07:46 | 2021-07-05 14:14 | 100 | 054:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO PRIMARIA | S21070300107 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 3268 | 2021-07-03 | 326800 | keep | 0 | Jul | 2021 | 0.22258 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
MAYAGÃœEZ | 2021-07-03 07:53 | 2021-07-03 10:47 | 50 | 002:54 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21070300140 | New_Event | Bad Weather | Include | Include | Weather | 174 | 2021-07-03 | 8700 | keep | 0 | Jul | 2021 | 0.0059255 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
SAN JUAN | 2021-07-03 08:20 | 2021-07-03 09:32 | 150 | 001:12 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | R21070300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2021-07-03 | 10800 | keep | 0 | Jul | 2021 | 0.0073558 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
MAYAGÃœEZ | 2021-07-03 08:39 | 2021-07-03 17:45 | 30 | 009:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | M21070300182 | New_Event | Wire Down | Include | Include | Equipment | 546 | 2021-07-03 | 16380 | keep | 0 | Jul | 2021 | 0.011156 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
CAGUAS | 2021-07-03 08:43 | 2021-07-03 13:54 | 12 | 005:11 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIO CAJA DE TRANSFORMADOR PARA REMPLAZAR POSTE SECUNDARIO | C21070200251 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 311 | 2021-07-03 | 3732 | keep | 0 | Jul | 2021 | 0.0025418 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
ARECIBO | 2021-07-03 08:56 | 2021-07-03 12:10 | 1210 | 003:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A21070300035 | New_Event | Cutout Failure | Include | Include | Equipment | 194 | 2021-07-03 | 234740 | keep | 0 | Jul | 2021 | 0.15988 | 0.00082413 | Sustained | FALSE | FALSE | TMED_Event | 1210
BAYAMON | 2021-07-03 08:57 | 2021-07-03 08:58 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVANDO LA CARGA DEL 1909-09 | S21070300009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 222 | keep | 0 | Jul | 2021 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | TMED_Event | 222
BAYAMON | 2021-07-03 08:57 | 2021-07-03 08:58 | 4456 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO CARGA POR EL 1907-03 | S21070030009 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-03 | 4456 | keep | 0 | Jul | 2021 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | TMED_Event | 4456
SAN JUAN | 2021-07-03 08:58 | 2021-07-03 09:00 | 9 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-03 | 18 | keep | 0 | Jul | 2021 | 1.226e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | TMED_Event | 9
MAYAGÃœEZ | 2021-07-03 08:58 | 2021-07-05 11:02 | 40 | 050:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21070300222 | New_Event | Bad Weather | Include | Include | Weather | 3004 | 2021-07-03 | 120160 | keep | 0 | Jul | 2021 | 0.08184 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
PONCE | 2021-07-03 09:00 | 2021-07-05 15:45 | 8 | 054:45 | P | SECUNDARIA/ESTRUCTURA AVERIADA | POSTE SECUNDARIO PARTIDO | P21070300111 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 3285 | 2021-07-03 | 26280 | keep | 0 | Jul | 2021 | 0.017899 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
MAYAGÃœEZ | 2021-07-03 09:00 | 2021-07-03 15:50 | 12 | 006:50 | P | LINEA DE TRANSMISION 38KV | SE ABRIO CORTE DE LINEA PARA TRABAJOS EN LINEAS 1500 Y 2000 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 410 | 2021-07-03 | 4920 | keep | 0 | Jul | 2021 | 0.003351 | 8.1731e-06 | Sustained | FALSE | TRUE | TMED_Event | 12
PONCE | 2021-07-03 09:01 | 2021-07-03 15:31 | 1 | 006:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA POR CAJA PRIMARIA AVERIADA | P21070300043 | New_Event | Cutout Failure | Include | Include | Equipment | 390 | 2021-07-03 | 390 | keep | 0 | Jul | 2021 | 0.00026563 | 6.811e-07 | Sustained | FALSE | TRUE | TMED_Event | 1
MAYAGÃœEZ | 2021-07-03 09:03 | 2021-07-03 10:08 | 50 | 001:05 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 65 | 2021-07-03 | 3250 | keep | 0 | Jul | 2021 | 0.0022136 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
BAYAMON | 2021-07-03 09:07 | 2021-07-03 09:09 | 1 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SEVERIFICO CON PERSNONAL DE AAA SUP. PACHECO Y SE CERRO POR SCADA | B21070300013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-03 | 2 | keep | 0 | Jul | 2021 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2021-07-03 09:08 | 2021-07-03 12:36 | 255 | 003:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6600 | S21070300028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 208 | 2021-07-03 | 53040 | keep | 0 | Jul | 2021 | 0.036125 | 0.00017368 | Sustained | FALSE | TRUE | TMED_Event | 255
SAN JUAN | 2021-07-03 09:08 | 2021-07-03 12:36 | 928 | 003:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6600 | S21070300028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 208 | 2021-07-03 | 193024 | keep | 0 | Jul | 2021 | 0.13147 | 0.00063206 | Sustained | FALSE | TRUE | TMED_Event | 928
SAN JUAN | 2021-07-03 09:08 | 2021-07-03 12:36 | 200 | 003:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6600 | S21070300028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 208 | 2021-07-03 | 41600 | keep | 0 | Jul | 2021 | 0.028334 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
SAN JUAN | 2021-07-03 09:08 | 2021-07-03 12:36 | 185 | 003:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6600 | S21070300028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 208 | 2021-07-03 | 38480 | keep | 0 | Jul | 2021 | 0.026209 | 0.000126 | Sustained | FALSE | TRUE | TMED_Event | 185
SAN JUAN | 2021-07-03 09:08 | 2021-07-03 12:36 | 73 | 003:28 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6600 | S21070300028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 208 | 2021-07-03 | 15184 | keep | 0 | Jul | 2021 | 0.010342 | 4.972e-05 | Sustained | FALSE | TRUE | TMED_Event | 73
CAGUAS | 2021-07-03 09:16 | 2021-07-03 09:17 | 598 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3800 DE CAYEY TC A JAJOME | C21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 598 | keep | 0 | Jul | 2021 | 0.0004073 | 0.0004073 | Momentary | FALSE | TRUE | TMED_Event | 598
CAGUAS | 2021-07-03 09:16 | 2021-07-03 09:17 | 2486 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3800 DE CAYEY TC A JAJOME | C21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 2486 | keep | 0 | Jul | 2021 | 0.0016932 | 0.0016932 | Momentary | FALSE | TRUE | TMED_Event | 2486
CAGUAS | 2021-07-03 09:16 | 2021-07-03 09:17 | 1403 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3800 DE CAYEY TC A JAJOME | C21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 1403 | keep | 0 | Jul | 2021 | 0.00095558 | 0.00095558 | Momentary | FALSE | TRUE | TMED_Event | 1403
CAGUAS | 2021-07-03 09:16 | 2021-07-03 09:17 | 1001 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3800 DE CAYEY TC A JAJOME | C21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 1001 | keep | 0 | Jul | 2021 | 0.00068178 | 0.00068178 | Momentary | FALSE | TRUE | TMED_Event | 1001
VEGA BAJA | 2021-07-03 09:19 | 2021-07-03 09:20 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21070300014 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 1310 | keep | 0 | Jul | 2021 | 0.00089224 | 0 | Momentary | FALSE | FALSE | TMED_Event | 0
MAYAGÃœEZ | 2021-07-03 09:22 | 2021-07-03 13:22 | 974 | 004:00 | T | DESGANCHE | DISPARO DEL INTERRUPTOR SE REALIZO DESGANCHE Y SE CERRO EL INTERRUPTOR | M21070300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2021-07-03 | 233760 | keep | 0 | Jul | 2021 | 0.15921 | 0.00066339 | Sustained | FALSE | FALSE | TMED_Event | 974
SAN JUAN | 2021-07-03 09:24 | 2021-07-04 18:00 | 40 | 032:36 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE Y CRUCETA PARTIDOS | S21070300040 | New_Event | Defective Pole | Include | Include | Equipment | 1956 | 2021-07-03 | 78240 | keep | 0 | Jul | 2021 | 0.053289 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
CANOVANAS | 2021-07-03 09:26 | 2021-07-03 18:50 | 1423 | 009:24 | P | OTRAS CAUSAS | DISPARO DEL TRANSFORMADOR 2305 SE CERRARON LOS MACHETESY SE NORMALIZO LA CARGA | R21070300019 | Partial_restoration | Other Causes | Include | Include | Other | 564 | 2021-07-03 | 802572 | keep | 0 | Jul | 2021 | 0.54663 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
CANOVANAS | 2021-07-03 09:26 | 2021-07-03 12:27 | 50 | 003:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21070300024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2021-07-03 | 9050 | keep | 0 | Jul | 2021 | 0.0061639 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
HUMACAO | 2021-07-03 09:26 | 2021-07-03 16:47 | 250 | 007:21 | P | CABLE SOTERRADO AVERIADO | 2 X 80 Y 1 X 100 EN CORTE DE LINEAS SE CAMBIO FASE EN SU-2 A FASE B POR AVERIA EN RISER @ SU-1 | C21070300025 | New_Event | UG Cable Fault | Include | Include | Equipment | 441 | 2021-07-03 | 110250 | keep | 0 | Jul | 2021 | 0.075091 | 0.00017027 | Sustained | FALSE | TRUE | TMED_Event | 250
CAGUAS | 2021-07-03 09:26 | 2021-07-04 11:02 | 200 | 025:36 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C21070300030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1536 | 2021-07-03 | 307200 | keep | 0 | Jul | 2021 | 0.20923 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
CAGUAS | 2021-07-03 09:26 | 2021-07-03 14:31 | 40 | 005:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN RISER MAL TIEMPO | C21070300023 | New_Event | Bad Weather | Include | Include | Weather | 305 | 2021-07-03 | 12200 | keep | 0 | Jul | 2021 | 0.0083094 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
MAYAGÃœEZ | 2021-07-03 09:26 | 2021-07-05 10:45 | 30 | 049:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21070300086 | New_Event | Bad Weather | Include | Include | Weather | 2959 | 2021-07-03 | 88770 | keep | 0 | Jul | 2021 | 0.060461 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
FAJARDO | 2021-07-03 09:27 | 2021-07-03 13:34 | 40 | 004:07 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21070300040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 247 | 2021-07-03 | 9880 | keep | 0 | Jul | 2021 | 0.0067292 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
FAJARDO | 2021-07-03 09:27 | 2021-07-03 17:40 | 50 | 008:13 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21070300035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 493 | 2021-07-03 | 24650 | keep | 0 | Jul | 2021 | 0.016789 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
CAGUAS | 2021-07-03 09:27 | 2021-07-03 12:06 | 20 | 002:39 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADORES MAL TIEMPO | C21070300037 | New_Event | Bad Weather | Include | Include | Weather | 159 | 2021-07-03 | 3180 | keep | 0 | Jul | 2021 | 0.0021659 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
MAYAGÃœEZ | 2021-07-03 09:27 | 2021-07-03 18:45 | 80 | 009:18 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M21070300183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 558 | 2021-07-03 | 44640 | keep | 0 | Jul | 2021 | 0.030404 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
UTUADO | 2021-07-03 09:27 | 2021-07-03 16:30 | 100 | 007:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | A21070300026 | New_Event | Wire Down | Include | Include | Equipment | 423 | 2021-07-03 | 42300 | keep | 0 | Jul | 2021 | 0.02881 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
HUMACAO | 2021-07-03 09:28 | 2021-07-03 09:29 | 4161 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR | C21070300048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-03 | 4161 | keep | 0 | Jul | 2021 | 0.002834 | 0.002834 | Momentary | FALSE | FALSE | TMED_Event | 4161
HUMACAO | 2021-07-03 09:29 | 2021-07-03 13:31 | 158 | 004:02 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA BAMBUA TOCANDO LA LINEA | C21070300079 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 242 | 2021-07-03 | 38236 | keep | 0 | Jul | 2021 | 0.026042 | 0.00010761 | Sustained | FALSE | TRUE | TMED_Event | 158
SAN JUAN | 2021-07-03 09:30 | 2021-07-03 09:31 | 3957 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 3957 | keep | 0 | Jul | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | TMED_Event | 3957
CAGUAS | 2021-07-03 09:39 | 2021-07-03 19:41 | 80 | 010:02 | P | DESGANCHE | SE DESGANCHO Y CERRO CORTE DE LINEA | C21070300126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 602 | 2021-07-03 | 48160 | keep | 0 | Jul | 2021 | 0.032802 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
BARRANQUITAS | 2021-07-03 09:40 | 2021-07-03 09:41 | 2635 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO DE LA LINEA 6500 DE BARRANQUITAS A TORO NEGRO | C21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 2635 | keep | 0 | Jul | 2021 | 0.0017947 | 0.0017947 | Momentary | FALSE | TRUE | TMED_Event | 2635
BARRANQUITAS | 2021-07-03 09:40 | 2021-07-03 09:41 | 2280 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO DE LA LINEA 6500 DE BARRANQUITAS A TORO NEGRO | C21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 2280 | keep | 0 | Jul | 2021 | 0.0015529 | 0.0015529 | Momentary | FALSE | TRUE | TMED_Event | 2280
BARRANQUITAS | 2021-07-03 09:40 | 2021-07-03 09:41 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO DE LA LINEA 6500 DE BARRANQUITAS A TORO NEGRO | C21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 1617 | keep | 0 | Jul | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | TRUE | TMED_Event | 1617
UTUADO | 2021-07-03 09:41 | 2021-07-03 10:12 | 15 | 000:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21070200019 | New_Event | Wire Down | Include | Include | Equipment | 31 | 2021-07-03 | 465 | keep | 0 | Jul | 2021 | 0.00031671 | 1.0216e-05 | Sustained | FALSE | TRUE | TMED_Event | 15
BARRANQUITAS | 2021-07-03 09:41 | 2021-07-03 09:44 | 50 | 000:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZARON DISCOS ROTOS | C21070300159 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 3 | 2021-07-03 | 150 | keep | 0 | Jul | 2021 | 0.00010216 | 0 | Momentary | FALSE | TRUE | TMED_Event | 0
HUMACAO | 2021-07-03 09:43 | 2021-07-03 10:52 | 12 | 001:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21070200078 | New_Event | Secondary Wire Down | Include | Include | Equipment | 69 | 2021-07-03 | 828 | keep | 0 | Jul | 2021 | 0.00056395 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
BARRANQUITAS | 2021-07-03 09:44 | 2021-07-03 09:56 | 2635 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 6500 DE BARRANQUITAS A TORO NEGRO | C21070300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-07-03 | 31620 | keep | 0 | Jul | 2021 | 0.021536 | 0.0017947 | Sustained | FALSE | TRUE | TMED_Event | 2635
BARRANQUITAS | 2021-07-03 09:44 | 2021-07-03 09:56 | 2280 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 6500 DE BARRANQUITAS A TORO NEGRO | C21070300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-07-03 | 27360 | keep | 0 | Jul | 2021 | 0.018635 | 0.0015529 | Sustained | FALSE | TRUE | TMED_Event | 2280
BARRANQUITAS | 2021-07-03 09:44 | 2021-07-03 09:56 | 1617 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 6500 DE BARRANQUITAS A TORO NEGRO | C21070300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-07-03 | 19404 | keep | 0 | Jul | 2021 | 0.013216 | 0.0011013 | Sustained | FALSE | TRUE | TMED_Event | 1617
BAYAMON | 2021-07-03 09:47 | 2021-07-03 09:48 | 1533 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 1533 | keep | 0 | Jul | 2021 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | TMED_Event | 1533
AGUADILLA | 2021-07-03 09:47 | 2021-07-03 09:48 | 390 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA | M21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 390 | keep | 0 | Jul | 2021 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | TMED_Event | 390
SAN JUAN | 2021-07-03 09:48 | 2021-07-03 09:49 | 1448 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 1448 | keep | 0 | Jul | 2021 | 0.00098623 | 0.00098623 | Momentary | FALSE | FALSE | TMED_Event | 1448
SAN JUAN | 2021-07-03 09:50 | 2021-07-03 09:53 | 908 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S21060300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-07-03 | 2724 | keep | 0 | Jul | 2021 | 0.0018553 | 0.00061843 | Momentary | FALSE | FALSE | TMED_Event | 908
PONCE | 2021-07-03 09:50 | 2021-07-03 09:51 | 23 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210703000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 23 | keep | 0 | Jul | 2021 | 1.5665e-05 | 1.5665e-05 | Momentary | FALSE | FALSE | TMED_Event | 23
MAYAGÃœEZ | 2021-07-03 09:52 | 2021-07-03 13:43 | 1287 | 003:51 | T | DESGANCHE | DISPARO DEL INTERRUPTOR SE REALIZO DESGANCHE | M21070300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 231 | 2021-07-03 | 297297 | keep | 0 | Jul | 2021 | 0.20249 | 0.00087657 | Sustained | FALSE | FALSE | TMED_Event | 1287
SAN JUAN | 2021-07-03 09:55 | 2021-07-03 12:27 | 1066 | 002:32 | T | DESGANCHE | SE DISPARO INTERRUPTOR SE REALIZO DESGANCHE Y SE CERRO POR SCADA | S21070300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2021-07-03 | 162032 | keep | 0 | Jul | 2021 | 0.11036 | 0.00072605 | Sustained | FALSE | FALSE | TMED_Event | 1066
PONCE | 2021-07-03 09:56 | 2021-07-03 09:57 | 2689 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210703000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 2689 | keep | 0 | Jul | 2021 | 0.0018315 | 0.0018315 | Momentary | FALSE | FALSE | TMED_Event | 2689
PONCE | 2021-07-03 09:56 | 2021-07-03 09:57 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210703000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 1746 | keep | 0 | Jul | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | TMED_Event | 1746
BARRANQUITAS | 2021-07-03 09:56 | 2021-07-05 14:59 | 50 | 053:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZARON DISCOS ROTOS | C21070300159 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 3183 | 2021-07-03 | 159150 | keep | 0 | Jul | 2021 | 0.1084 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
BARRANQUITAS | 2021-07-03 09:56 | 2021-07-06 20:56 | 55 | 082:60 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO AISLADOR ROTO | C21070200212 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 4980 | 2021-07-03 | 273900 | keep | 0 | Jul | 2021 | 0.18655 | 3.746e-05 | Sustained | FALSE | TRUE | TMED_Event | 55
PONCE | 2021-07-03 09:57 | 2021-07-03 09:58 | 2689 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210703000XX | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 2689 | keep | 0 | Jul | 2021 | 0.0018315 | 0.0018315 | Momentary | FALSE | FALSE | TMED_Event | 2689
PONCE | 2021-07-03 09:57 | 2021-07-03 09:58 | 18 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210703000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 18 | keep | 0 | Jul | 2021 | 1.226e-05 | 1.226e-05 | Momentary | FALSE | FALSE | TMED_Event | 18
PONCE | 2021-07-03 09:58 | 2021-07-03 13:39 | 2163 | 003:41 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 18000 | P21070300053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 221 | 2021-07-03 | 478023 | keep | 0 | Jul | 2021 | 0.32558 | 0.0014732 | Sustained | FALSE | TRUE | TMED_Event | 2163
PONCE | 2021-07-03 09:58 | 2021-07-03 13:39 | 1340 | 003:41 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 18000 | P21070300053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 221 | 2021-07-03 | 296140 | keep | 0 | Jul | 2021 | 0.2017 | 0.00091267 | Sustained | FALSE | TRUE | TMED_Event | 1340
PONCE | 2021-07-03 09:58 | 2021-07-03 13:39 | 2039 | 003:41 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 18000 | P21070300053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 221 | 2021-07-03 | 450619 | keep | 0 | Jul | 2021 | 0.30691 | 0.0013888 | Sustained | FALSE | TRUE | TMED_Event | 2039
PONCE | 2021-07-03 09:58 | 2021-07-03 13:39 | 485 | 003:41 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 18000 | P210703000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 221 | 2021-07-03 | 107185 | keep | 0 | Jul | 2021 | 0.073003 | 0.00033033 | Sustained | FALSE | TRUE | TMED_Event | 485
PONCE | 2021-07-03 09:58 | 2021-07-03 13:39 | 732 | 003:41 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 18000 | P210703000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 221 | 2021-07-03 | 161772 | keep | 0 | Jul | 2021 | 0.11018 | 0.00049856 | Sustained | FALSE | TRUE | TMED_Event | 732
PONCE | 2021-07-03 09:59 | 2021-07-03 10:00 | 2379 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210703000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 2379 | keep | 0 | Jul | 2021 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | TMED_Event | 2379
GUAYAMA | 2021-07-03 10:00 | 2021-07-03 11:48 | 50 | 001:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA RELACIONADO AL MAL TIEMPO | P210703000XX | New_Event | Bad Weather | Include | Include | Weather | 108 | 2021-07-03 | 5400 | keep | 0 | Jul | 2021 | 0.0036779 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
SAN JUAN | 2021-07-03 10:06 | 2021-07-03 10:07 | 1825 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S21070300029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 1825 | keep | 0 | Jul | 2021 | 0.001243 | 0.001243 | Momentary | FALSE | TRUE | TMED_Event | 1825
SAN JUAN | 2021-07-03 10:06 | 2021-07-03 10:07 | 47 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S21070300029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 47 | keep | 0 | Jul | 2021 | 3.2011e-05 | 3.2011e-05 | Momentary | FALSE | TRUE | TMED_Event | 47
SAN JUAN | 2021-07-03 10:06 | 2021-07-03 10:07 | 315 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S21070300029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 315 | keep | 0 | Jul | 2021 | 0.00021455 | 0.00021455 | Momentary | FALSE | TRUE | TMED_Event | 315
SAN JUAN | 2021-07-03 10:06 | 2021-07-03 10:07 | 2 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S21070300029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 2 | keep | 0 | Jul | 2021 | 1.3622e-06 | 1.3622e-06 | Momentary | FALSE | TRUE | TMED_Event | 2
SAN JUAN | 2021-07-03 10:06 | 2021-07-03 10:07 | 2391 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S21070300029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 2391 | keep | 0 | Jul | 2021 | 0.0016285 | 0.0016285 | Momentary | FALSE | TRUE | TMED_Event | 2391
PONCE | 2021-07-03 10:11 | 2021-07-03 11:57 | 752 | 001:46 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO INTERRUPTOR MAL TIEMPO | P210703000XX | New_Event | Bad Weather | Include | Include | Weather | 106 | 2021-07-03 | 79712 | keep | 0 | Jul | 2021 | 0.054291 | 0.00051218 | Sustained | FALSE | FALSE | TMED_Event | 752
MAYAGÃœEZ | 2021-07-03 10:12 | 2021-07-03 10:13 | 281 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 281 | keep | 0 | Jul | 2021 | 0.00019139 | 0.00019139 | Momentary | FALSE | TRUE | TMED_Event | 281
MAYAGÃœEZ | 2021-07-03 10:12 | 2021-07-03 10:13 | 1252 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 1252 | keep | 0 | Jul | 2021 | 0.00085273 | 0.00085273 | Momentary | FALSE | TRUE | TMED_Event | 1252
MAYAGÃœEZ | 2021-07-03 10:12 | 2021-07-03 10:13 | 595 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 595 | keep | 0 | Jul | 2021 | 0.00040525 | 0.00040525 | Momentary | FALSE | TRUE | TMED_Event | 595
MAYAGÃœEZ | 2021-07-03 10:12 | 2021-07-03 10:13 | 51 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 51 | keep | 0 | Jul | 2021 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | TRUE | TMED_Event | 51
MAYAGÃœEZ | 2021-07-03 10:12 | 2021-07-03 10:13 | 721 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 721 | keep | 0 | Jul | 2021 | 0.00049107 | 0.00049107 | Momentary | FALSE | TRUE | TMED_Event | 721
UTUADO | 2021-07-03 10:12 | 2021-07-03 10:13 | 3316 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4700 | A21070300044 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 3316 | keep | 0 | Jul | 2021 | 0.0022585 | 0.0022585 | Momentary | FALSE | TRUE | TMED_Event | 3316
UTUADO | 2021-07-03 10:12 | 2021-07-03 10:13 | 1241 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4700 | A21070300044 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 1241 | keep | 0 | Jul | 2021 | 0.00084524 | 0.00084524 | Momentary | FALSE | TRUE | TMED_Event | 1241
UTUADO | 2021-07-03 10:12 | 2021-07-03 10:13 | 650 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4700 | A21070300044 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 650 | keep | 0 | Jul | 2021 | 0.00044271 | 0.00044271 | Momentary | FALSE | TRUE | TMED_Event | 650
UTUADO | 2021-07-03 10:12 | 2021-07-03 10:13 | 1382 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4700 | A21070300045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 1382 | keep | 0 | Jul | 2021 | 0.00094127 | 0.00094127 | Momentary | FALSE | TRUE | TMED_Event | 1382
UTUADO | 2021-07-03 10:12 | 2021-07-03 10:13 | 654 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4700 | A21070300045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 654 | keep | 0 | Jul | 2021 | 0.00044544 | 0.00044544 | Momentary | FALSE | TRUE | TMED_Event | 654
CAGUAS | 2021-07-03 10:13 | 2021-07-03 10:14 | 2276 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAS A MONACILLOS | C21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 2276 | keep | 0 | Jul | 2021 | 0.0015502 | 0.0015502 | Momentary | FALSE | TRUE | TMED_Event | 2276
CAGUAS | 2021-07-03 10:13 | 2021-07-03 10:14 | 777 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAS A MONACILLOS | C21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 777 | keep | 0 | Jul | 2021 | 0.00052921 | 0.00052921 | Momentary | FALSE | TRUE | TMED_Event | 777
CAGUAS | 2021-07-03 10:13 | 2021-07-03 10:14 | 12 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAS A MONACILLOS | C21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 12 | keep | 0 | Jul | 2021 | 8.1731e-06 | 8.1731e-06 | Momentary | FALSE | TRUE | TMED_Event | 12
CAGUAS | 2021-07-03 10:13 | 2021-07-03 10:14 | 1290 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAS A MONACILLOS | C21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 1290 | keep | 0 | Jul | 2021 | 0.00087861 | 0.00087861 | Momentary | FALSE | TRUE | TMED_Event | 1290
MAYAGÃœEZ | 2021-07-03 10:13 | 2021-07-03 12:15 | 50 | 002:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070200064 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 122 | 2021-07-03 | 6100 | keep | 0 | Jul | 2021 | 0.0041547 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
UTUADO | 2021-07-03 10:13 | 2021-07-03 15:45 | 15 | 005:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21070200019 | New_Event | Wire Down | Include | Include | Equipment | 332 | 2021-07-03 | 4980 | keep | 0 | Jul | 2021 | 0.0033919 | 1.0216e-05 | Sustained | FALSE | TRUE | TMED_Event | 15
UTUADO | 2021-07-03 10:19 | 2021-07-03 11:47 | 1527 | 001:28 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO INTERRUPTOR SE PATRULLO MAL TIEMPO EN EL AREA SE CERRO INTERRUPTOR | A21070300000 | New_Event | Bad Weather | Include | Include | Weather | 88 | 2021-07-03 | 134376 | keep | 0 | Jul | 2021 | 0.091523 | 0.00104 | Sustained | FALSE | FALSE | TMED_Event | 1527
BARRANQUITAS | 2021-07-03 10:19 | 2021-07-03 15:27 | 1246 | 005:08 | T | AISLADOR ROTO, PARTIDO O SAFADO | DESPEGO AISLADOR PARTIDO CON LA VERETA | C21070300000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 308 | 2021-07-03 | 383768 | keep | 0 | Jul | 2021 | 0.26138 | 0.00084864 | Sustained | FALSE | FALSE | TMED_Event | 1246
MAYAGÃœEZ | 2021-07-03 10:20 | 2021-07-03 10:21 | 1017 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR MAL TIEMPO | M21070300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-03 | 1017 | keep | 0 | Jul | 2021 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | TMED_Event | 1017
MAYAGÃœEZ | 2021-07-03 10:27 | 2021-07-03 18:05 | 93 | 007:38 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DEL INTERRUPTOR MAL TIEMPO | M21070300000 | New_Event | Bad Weather | Include | Include | Weather | 458 | 2021-07-03 | 42594 | keep | 0 | Jul | 2021 | 0.029011 | 6.3342e-05 | Sustained | FALSE | FALSE | TMED_Event | 93
MAYAGÃœEZ | 2021-07-03 10:27 | 2021-07-03 10:28 | 3230 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 3230 | keep | 0 | Jul | 2021 | 0.0021999 | 0.0021999 | Momentary | FALSE | FALSE | TMED_Event | 3230
MAYAGÃœEZ | 2021-07-03 10:30 | 2021-07-03 21:51 | 1252 | 011:21 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR RTU DOWN CERRADO MANUAL ELECTRICO | M21070300120 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 681 | 2021-07-03 | 852612 | keep | 0 | Jul | 2021 | 0.58071 | 0.00085273 | Sustained | FALSE | FALSE | TMED_Event | 1252
ARECIBO | 2021-07-03 10:32 | 2021-07-03 10:33 | 5042 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR DESCARGAS ELECTRICAS | A21070300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-03 | 5042 | keep | 0 | Jul | 2021 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | TMED_Event | 5042
ARECIBO | 2021-07-03 10:33 | 2021-07-03 10:34 | 2266 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR DESCARGAS ELECTRICAS | A21070300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-03 | 2266 | keep | 0 | Jul | 2021 | 0.0015434 | 0.0015434 | Momentary | FALSE | FALSE | TMED_Event | 2266
ARECIBO | 2021-07-03 10:35 | 2021-07-03 10:36 | 1 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR DESCARGAS ELECTRICAS | A21070300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-03 | 1 | keep | 0 | Jul | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | TMED_Event | 1
ARECIBO | 2021-07-03 10:35 | 2021-07-03 10:36 | 2266 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR DESCARGAS ELECTRICAS | A21070300000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2021-07-03 | 2266 | keep | 0 | Jul | 2021 | 0.0015434 | 0.0015434 | Momentary | FALSE | FALSE | TMED_Event | 2266
ARECIBO | 2021-07-03 10:35 | 2021-07-03 10:36 | 1644 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR DESCARGAS ELECTRICAS | A21070300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-03 | 1644 | keep | 0 | Jul | 2021 | 0.0011197 | 0.0011197 | Momentary | FALSE | FALSE | TMED_Event | 1644
ARECIBO | 2021-07-03 10:35 | 2021-07-03 10:36 | 1883 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR DESCARGAS ELECTRICAS | A21070300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-03 | 1883 | keep | 0 | Jul | 2021 | 0.0012825 | 0.0012825 | Momentary | FALSE | FALSE | TMED_Event | 1883
ARECIBO | 2021-07-03 10:36 | 2021-07-03 10:37 | 5042 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR DESCARGAS ELECTRICAS | A21070300000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-03 | 5042 | keep | 0 | Jul | 2021 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | TMED_Event | 5042
ARECIBO | 2021-07-03 10:37 | 2021-07-03 19:20 | 80 | 008:43 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHE | A21070300080 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 523 | 2021-07-03 | 41840 | keep | 0 | Jul | 2021 | 0.028497 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
AGUADILLA | 2021-07-03 10:40 | 2021-07-03 10:41 | 3041 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR MAL TIEMPO | M21070300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-03 | 3041 | keep | 0 | Jul | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | TMED_Event | 3041
AGUADILLA | 2021-07-03 10:40 | 2021-07-03 10:41 | 1261 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR MAL TIEMPO | M21070300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-03 | 1261 | keep | 0 | Jul | 2021 | 0.00085886 | 0.00085886 | Momentary | FALSE | FALSE | TMED_Event | 1261
AGUADILLA | 2021-07-03 10:40 | 2021-07-03 10:41 | 574 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 574 | keep | 0 | Jul | 2021 | 0.00039095 | 0.00039095 | Momentary | FALSE | TRUE | TMED_Event | 574
AGUADILLA | 2021-07-03 10:40 | 2021-07-03 10:41 | 2493 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 2493 | keep | 0 | Jul | 2021 | 0.001698 | 0.001698 | Momentary | FALSE | TRUE | TMED_Event | 2493
AGUADILLA | 2021-07-03 10:40 | 2021-07-03 10:41 | 1415 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 1415 | keep | 0 | Jul | 2021 | 0.00096375 | 0.00096375 | Momentary | FALSE | TRUE | TMED_Event | 1415
AGUADILLA | 2021-07-03 10:40 | 2021-07-03 10:41 | 1428 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 1428 | keep | 0 | Jul | 2021 | 0.0009726 | 0.0009726 | Momentary | FALSE | TRUE | TMED_Event | 1428
AGUADILLA | 2021-07-03 10:40 | 2021-07-03 10:41 | 1036 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 1036 | keep | 0 | Jul | 2021 | 0.00070561 | 0.00070561 | Momentary | FALSE | TRUE | TMED_Event | 1036
AGUADILLA | 2021-07-03 10:40 | 2021-07-03 10:41 | 382 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 382 | keep | 0 | Jul | 2021 | 0.00026018 | 0.00026018 | Momentary | FALSE | TRUE | TMED_Event | 382
AGUADILLA | 2021-07-03 10:40 | 2021-07-03 10:41 | 39 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 39 | keep | 0 | Jul | 2021 | 2.6563e-05 | 2.6563e-05 | Momentary | FALSE | TRUE | TMED_Event | 39
AGUADILLA | 2021-07-03 10:40 | 2021-07-03 10:41 | 2366 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 2366 | keep | 0 | Jul | 2021 | 0.0016115 | 0.0016115 | Momentary | FALSE | TRUE | TMED_Event | 2366
MAYAGÃœEZ | 2021-07-03 10:40 | 2021-07-03 10:41 | 1337 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 1337 | keep | 0 | Jul | 2021 | 0.00091062 | 0.00091062 | Momentary | FALSE | TRUE | TMED_Event | 1337
AGUADILLA | 2021-07-03 10:40 | 2021-07-03 10:41 | 709 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 709 | keep | 0 | Jul | 2021 | 0.0004829 | 0.0004829 | Momentary | FALSE | TRUE | TMED_Event | 709
BAYAMON | 2021-07-03 10:40 | 2021-07-03 10:41 | 1 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21070300022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 1 | keep | 0 | Jul | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | TMED_Event | 1
BARRANQUITAS | 2021-07-03 10:40 | 2021-07-03 10:41 | 2280 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CARGA POR EL 9902-03 CERRADO POR CONTROL | C21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 2280 | keep | 0 | Jul | 2021 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | TMED_Event | 2280
BARRANQUITAS | 2021-07-03 10:40 | 2021-07-03 10:41 | 1617 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL LLEVANDO LA CARGA DEL 9902-02 | C21070300000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-03 | 1617 | keep | 0 | Jul | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | TMED_Event | 1617
ARECIBO | 2021-07-03 10:43 | 2021-07-03 15:31 | 207 | 004:48 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL INTERRUPTOR SE REPARO LINEA PRIMARIA ROTA Y AISLADORES | A21070300000 | New_Event | Wire Down | Include | Include | Equipment | 288 | 2021-07-03 | 59616 | keep | 0 | Jul | 2021 | 0.040604 | 0.00014099 | Sustained | FALSE | TRUE | TMED_Event | 207
BARRANQUITAS | 2021-07-03 10:43 | 2021-07-03 10:51 | 2280 | 000:08 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CARGA POR EL 9902-03 CERRADO POR CONTROL | C21070300000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 8 | 2021-07-03 | 18240 | keep | 0 | Jul | 2021 | 0.012423 | 0.0015529 | Sustained | FALSE | FALSE | TMED_Event | 2280
BARRANQUITAS | 2021-07-03 10:43 | 2021-07-03 10:51 | 1617 | 000:08 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL LLEVANDO LA CARGA DEL 9902-02 | C21070300000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 8 | 2021-07-03 | 12936 | keep | 0 | Jul | 2021 | 0.0088107 | 0.0011013 | Sustained | FALSE | FALSE | TMED_Event | 1617
AGUADILLA | 2021-07-03 10:44 | 2021-07-03 10:45 | 3041 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR MAL TIEMPO | M21070300000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2021-07-03 | 3041 | keep | 0 | Jul | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | TMED_Event | 3041
AGUADILLA | 2021-07-03 10:46 | 2021-07-03 10:47 | 1057 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR MAL TIEMPO | M21070300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-03 | 1057 | keep | 0 | Jul | 2021 | 0.00071992 | 0.00071992 | Momentary | FALSE | FALSE | TMED_Event | 1057
MAYAGÃœEZ | 2021-07-03 10:47 | 2021-07-03 10:48 | 108 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR MAL TIEMPO | M21070300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-03 | 108 | keep | 0 | Jul | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | TMED_Event | 108
MAYAGÃœEZ | 2021-07-03 10:48 | 2021-07-03 10:50 | 50 | 000:02 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21070300140 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 2 | 2021-07-03 | 100 | keep | 0 | Jul | 2021 | 6.811e-05 | 3.4055e-05 | Momentary | FALSE | TRUE | TMED_Event | 50
BAYAMON | 2021-07-03 10:49 | 2021-07-03 10:50 | 878 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1903-05 Y SE CERRO POR SCADA LLEVA 1714-05 | B21070300046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 878 | keep | 0 | Jul | 2021 | 0.000598 | 0.000598 | Momentary | FALSE | FALSE | TMED_Event | 878
BAYAMON | 2021-07-03 10:49 | 2021-07-03 10:50 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1903-05 Y SE CERRO POR SCADA LLEVA 1714-05 | S21070300046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 1310 | keep | 0 | Jul | 2021 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | TMED_Event | 1310
PONCE | 2021-07-03 10:49 | 2021-07-03 17:21 | 65 | 006:32 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA POR DESGANCHE | P21070300059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 392 | 2021-07-03 | 25480 | keep | 0 | Jul | 2021 | 0.017354 | 4.4271e-05 | Sustained | FALSE | TRUE | TMED_Event | 65
MAYAGÃœEZ | 2021-07-03 10:50 | 2021-07-03 10:51 | 108 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR MAL TIEMPO | M21070300000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2021-07-03 | 108 | keep | 0 | Jul | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | TMED_Event | 108
BAYAMON | 2021-07-03 10:50 | 2021-07-03 10:51 | 3070 | 000:01 | T | DESGANCHE | RECIERRE | B21070300023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-03 | 3070 | keep | 0 | Jul | 2021 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | TMED_Event | 3070
MAYAGÃœEZ | 2021-07-03 10:51 | 2021-07-03 10:52 | 108 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR MAL TIEMPO | M21070300000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2021-07-03 | 108 | keep | 0 | Jul | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | TMED_Event | 108
ARECIBO | 2021-07-03 10:51 | 2021-07-03 10:52 | 274 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR DESCARGAS ELECTRICAS | A21070300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-03 | 274 | keep | 0 | Jul | 2021 | 0.00018662 | 0.00018662 | Momentary | FALSE | FALSE | TMED_Event | 274
ARECIBO | 2021-07-03 10:51 | 2021-07-03 10:52 | 1227 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR DESCARGAS ELECTRICAS | A21070300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-03 | 1227 | keep | 0 | Jul | 2021 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | TMED_Event | 1227
BAYAMON | 2021-07-03 10:51 | 2021-07-04 02:13 | 30 | 015:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | B21070300123 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 922 | 2021-07-03 | 27660 | keep | 0 | Jul | 2021 | 0.018839 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
BARRANQUITAS | 2021-07-03 10:51 | 2021-07-04 11:10 | 100 | 024:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE RETIRO POSTE DE COMUNICACION SOBRE LINEAS | C21070300074 | Partial_restoration | Wire Down | Include | Include | Equipment | 1459 | 2021-07-03 | 145900 | keep | 0 | Jul | 2021 | 0.099372 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
MAYAGÃœEZ | 2021-07-03 10:52 | 2021-07-03 16:45 | 50 | 005:53 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21070300140 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 353 | 2021-07-03 | 17650 | keep | 0 | Jul | 2021 | 0.012021 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
ARECIBO | 2021-07-03 10:52 | 2021-07-03 16:26 | 30 | 005:34 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | A21070300149 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 334 | 2021-07-03 | 10020 | keep | 0 | Jul | 2021 | 0.0068246 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
UTUADO | 2021-07-03 10:53 | 2021-07-03 16:45 | 50 | 005:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | A21070300050 | New_Event | Bad Weather | Include | Include | Weather | 352 | 2021-07-03 | 17600 | keep | 0 | Jul | 2021 | 0.011987 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
SAN JUAN | 2021-07-03 10:54 | 2021-07-06 09:54 | 1 | 070:60 | P | NO SE REPORTO CAUSA | 1 RBA DE 80 AMP EN EL SU - 13 | R21070300048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4260 | 2021-07-03 | 4260 | keep | 0 | Jul | 2021 | 0.0029015 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
MAYAGÃœEZ | 2021-07-03 10:55 | 2021-07-04 10:40 | 40 | 023:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070300269 | New_Event | Bad Weather | Include | Include | Weather | 1425 | 2021-07-03 | 57000 | keep | 0 | Jul | 2021 | 0.038822 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
CAGUAS | 2021-07-03 10:56 | 2021-07-03 13:57 | 90 | 003:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C21070300050 | New_Event | Bad Weather | Include | Include | Weather | 181 | 2021-07-03 | 16290 | keep | 0 | Jul | 2021 | 0.011095 | 6.1299e-05 | Sustained | FALSE | TRUE | TMED_Event | 90
BAYAMON | 2021-07-03 10:58 | 2021-07-03 11:29 | 12 | 000:31 | P | TRANSFORMADOR AVERIADO | SE REPARO BARRAS DE TRANSFORMADOR | B21070200016 | New_Event | Service Transformer Failure | Include | Include | Equipment | 31 | 2021-07-03 | 372 | keep | 0 | Jul | 2021 | 0.00025337 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
PONCE | 2021-07-03 10:59 | 2021-07-03 16:36 | 65 | 005:37 | P | DESGANCHE | 1 X 65 EN RISER POR DESGANCHE | P21070300063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 337 | 2021-07-03 | 21905 | keep | 0 | Jul | 2021 | 0.014919 | 4.4271e-05 | Sustained | FALSE | FALSE | TMED_Event | 65
AGUADILLA | 2021-07-03 11:00 | 2021-07-03 11:55 | 1827 | 000:55 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DEL INTERRUPTOR RECIERRE EN OFF MAL TIEMPO SE VERIFICO PERSONAL FUERA DE LAS LINEAS | M21070300000 | New_Event | Bad Weather | Include | Include | Weather | 55 | 2021-07-03 | 100485 | keep | 0 | Jul | 2021 | 0.06844 | 0.0012444 | Sustained | FALSE | TRUE | TMED_Event | 1827
MAYAGÃœEZ | 2021-07-03 11:01 | 2021-07-03 16:13 | 1666 | 005:12 | T | BREAKER DEFECTUOSO O NO OPERA | DISPARO DEL INTERRUPTOR NO SE PUEDE CERRAR POR SCADA SE CERRO EN LA SUBESTACION | M21070300000 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 312 | 2021-07-03 | 519792 | keep | 0 | Jul | 2021 | 0.35403 | 0.0011347 | Sustained | FALSE | FALSE | TMED_Event | 1666
SAN JUAN | 2021-07-03 11:02 | 2021-07-03 11:03 | 137 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 137 | keep | 0 | Jul | 2021 | 9.331e-05 | 9.331e-05 | Momentary | FALSE | FALSE | TMED_Event | 137
ARECIBO | 2021-07-03 11:05 | 2021-07-03 14:35 | 2266 | 003:30 | T | DESGANCHE | DISPARO DEL INTERRUPTOR ARBOL SOBRE LAS LINEAS | A21070300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2021-07-03 | 475860 | keep | 0 | Jul | 2021 | 0.32411 | 0.0015434 | Sustained | FALSE | TRUE | TMED_Event | 2266
BAYAMON | 2021-07-03 11:07 | 2021-07-04 09:37 | 20 | 022:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21070300027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1350 | 2021-07-03 | 27000 | keep | 0 | Jul | 2021 | 0.01839 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
CAGUAS | 2021-07-03 11:10 | 2021-07-03 16:31 | 40 | 005:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21070300058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 321 | 2021-07-03 | 12840 | keep | 0 | Jul | 2021 | 0.0087453 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
UTUADO | 2021-07-03 11:11 | 2021-07-05 12:29 | 50 | 049:18 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21070300069 | New_Event | Bad Weather | Include | Include | Weather | 2958 | 2021-07-03 | 147900 | keep | 0 | Jul | 2021 | 0.10073 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
BAYAMON | 2021-07-03 11:11 | 2021-07-03 14:18 | 1 | 003:07 | T | NO SE REPORTO CAUSA | SE PATRULLO NO SE VIO CONDICION Y SE CERRO POR SCADA | B21070300000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 187 | 2021-07-03 | 187 | keep | 0 | Jul | 2021 | 0.00012736 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2021-07-03 11:13 | 2021-07-03 11:41 | 343 | 000:28 | T | NO SE REPORTO CAUSA | SE ABRIO INTERRUPTOR PARA PERSONAL TRABAJAR EN TOMA CLIENTE | S21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 28 | 2021-07-03 | 9604 | keep | 0 | Jul | 2021 | 0.0065412 | 0.00023362 | Sustained | FALSE | FALSE | TMED_Event | 343
MAYAGÃœEZ | 2021-07-03 11:13 | 2021-07-03 11:20 | 372 | 000:07 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DEL INTERRUPTOR MAL TIEMPO SU CARGA POR EL 6802-03 (SPARE) | M21070300000 | New_Event | Bad Weather | Include | Include | Weather | 7 | 2021-07-03 | 2604 | keep | 0 | Jul | 2021 | 0.0017736 | 0.00025337 | Sustained | FALSE | FALSE | TMED_Event | 372
MAYAGÃœEZ | 2021-07-03 11:13 | 2021-07-03 12:15 | 1268 | 001:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 62 | 2021-07-03 | 78616 | keep | 0 | Jul | 2021 | 0.053545 | 0.00086363 | Sustained | FALSE | TRUE | TMED_Event | 1268
MAYAGÃœEZ | 2021-07-03 11:13 | 2021-07-03 12:15 | 2064 | 001:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 62 | 2021-07-03 | 127968 | keep | 0 | Jul | 2021 | 0.087158 | 0.0014058 | Sustained | FALSE | TRUE | TMED_Event | 2064
MAYAGÃœEZ | 2021-07-03 11:13 | 2021-07-03 12:15 | 3036 | 001:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 62 | 2021-07-03 | 188232 | keep | 0 | Jul | 2021 | 0.1282 | 0.0020678 | Sustained | FALSE | TRUE | TMED_Event | 3036
MAYAGÃœEZ | 2021-07-03 11:13 | 2021-07-03 12:15 | 2952 | 001:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | M21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 62 | 2021-07-03 | 183024 | keep | 0 | Jul | 2021 | 0.12466 | 0.0020106 | Sustained | FALSE | TRUE | TMED_Event | 2952
MAYAGÃœEZ | 2021-07-03 11:13 | 2021-07-03 11:17 | 3458 | 000:04 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DEL INTERRUPTOR RECIERRE EN OFF MAL TIEMPO | M21070300000 | New_Event | Bad Weather | Include | Include | Weather | 4 | 2021-07-03 | 13832 | keep | 0 | Jul | 2021 | 0.0094209 | 0.0023552 | Momentary | FALSE | FALSE | TMED_Event | 3458
MAYAGÃœEZ | 2021-07-03 11:13 | 2021-07-03 11:17 | 3458 | 000:04 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DEL INTERRUPTOR RECIERRE EN OFF MAL TIEMPO | M21070300000 | New_Event | Bad Weather | Include | Include | Weather | 4 | 2021-07-03 | 13832 | keep | 0 | Jul | 2021 | 0.0094209 | 0.0023552 | Momentary | FALSE | FALSE | TMED_Event | 3458
ARECIBO | 2021-07-03 11:14 | 2021-07-03 15:00 | 30 | 003:46 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A21070300074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2021-07-03 | 6780 | keep | 0 | Jul | 2021 | 0.0046178 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
YAUCO | 2021-07-03 11:16 | 2021-07-05 13:31 | 50 | 050:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA. SE LEVANTO LINEA PRIMARIA DEL PISO | P21070500014 | New_Event | Wire Down | Include | Include | Equipment | 3015 | 2021-07-03 | 150750 | keep | 0 | Jul | 2021 | 0.10268 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
MAYAGÃœEZ | 2021-07-03 11:16 | 2021-07-04 12:00 | 80 | 024:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | M21070300269 | New_Event | Bad Weather | Include | Include | Weather | 1484 | 2021-07-03 | 118720 | keep | 0 | Jul | 2021 | 0.08086 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
YAUCO | 2021-07-03 11:17 | 2021-07-04 16:29 | 100 | 029:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 Y 1 X 65 EN DISTINTOS CORTES DE LINEA POR MAL TIEMPO | P21070300069 | New_Event | Bad Weather | Include | Include | Weather | 1752 | 2021-07-03 | 175200 | keep | 0 | Jul | 2021 | 0.11933 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
AGUADILLA | 2021-07-03 11:18 | 2021-07-03 11:19 | 574 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21070300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 574 | keep | 0 | Jul | 2021 | 0.00039095 | 0.00039095 | Momentary | FALSE | TRUE | TMED_Event | 574
AGUADILLA | 2021-07-03 11:18 | 2021-07-03 11:19 | 2493 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21070300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 2493 | keep | 0 | Jul | 2021 | 0.001698 | 0.001698 | Momentary | FALSE | TRUE | TMED_Event | 2493
AGUADILLA | 2021-07-03 11:18 | 2021-07-03 11:19 | 1415 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21070300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 1415 | keep | 0 | Jul | 2021 | 0.00096375 | 0.00096375 | Momentary | FALSE | TRUE | TMED_Event | 1415
AGUADILLA | 2021-07-03 11:18 | 2021-07-03 11:19 | 1428 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21070300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 1428 | keep | 0 | Jul | 2021 | 0.0009726 | 0.0009726 | Momentary | FALSE | TRUE | TMED_Event | 1428
AGUADILLA | 2021-07-03 11:18 | 2021-07-03 11:19 | 1036 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21070300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 1036 | keep | 0 | Jul | 2021 | 0.00070561 | 0.00070561 | Momentary | FALSE | TRUE | TMED_Event | 1036
AGUADILLA | 2021-07-03 11:18 | 2021-07-03 11:19 | 2366 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21070300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 2366 | keep | 0 | Jul | 2021 | 0.0016115 | 0.0016115 | Momentary | FALSE | TRUE | TMED_Event | 2366
MAYAGÃœEZ | 2021-07-03 11:18 | 2021-07-03 11:19 | 1337 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21070300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 1337 | keep | 0 | Jul | 2021 | 0.00091062 | 0.00091062 | Momentary | FALSE | TRUE | TMED_Event | 1337
AGUADILLA | 2021-07-03 11:18 | 2021-07-03 11:19 | 709 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M21070300000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 709 | keep | 0 | Jul | 2021 | 0.0004829 | 0.0004829 | Momentary | FALSE | TRUE | TMED_Event | 709
MAYAGÃœEZ | 2021-07-03 11:22 | 2021-07-03 13:24 | 300 | 002:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21070200262 | New_Event | Bad Weather | Include | Include | Weather | 122 | 2021-07-03 | 36600 | keep | 0 | Jul | 2021 | 0.024928 | 0.00020433 | Sustained | FALSE | TRUE | TMED_Event | 300
GUAYAMA | 2021-07-03 11:27 | 2021-07-03 18:30 | 15 | 007:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO CAJA DE TRANSFORMADOR | P21070300071 | New_Event | Wire Down | Include | Include | Equipment | 423 | 2021-07-03 | 6345 | keep | 0 | Jul | 2021 | 0.0043216 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
CAGUAS | 2021-07-03 11:32 | 2021-07-03 18:27 | 150 | 006:55 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA | C21070300079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 415 | 2021-07-03 | 62250 | keep | 0 | Jul | 2021 | 0.042398 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
PONCE | 2021-07-03 11:32 | 2021-07-03 17:18 | 50 | 005:46 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P21070300073 | New_Event | Bad Weather | Include | Include | Weather | 346 | 2021-07-03 | 17300 | keep | 0 | Jul | 2021 | 0.011783 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
MAYAGÃœEZ | 2021-07-03 11:34 | 2021-07-03 13:30 | 100 | 001:56 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070300000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 116 | 2021-07-03 | 11600 | keep | 0 | Jul | 2021 | 0.0079007 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
MAYAGÃœEZ | 2021-07-03 11:37 | 2021-07-05 19:40 | 50 | 056:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | M21070300327 | New_Event | Bad Weather | Include | Include | Weather | 3363 | 2021-07-03 | 168150 | keep | 0 | Jul | 2021 | 0.11453 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
AGUADILLA | 2021-07-03 11:39 | 2021-07-05 07:38 | 60 | 043:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M21070300328 | New_Event | Wire Down | Include | Include | Equipment | 2639 | 2021-07-03 | 158340 | keep | 0 | Jul | 2021 | 0.10784 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
ARECIBO | 2021-07-03 11:39 | 2021-07-03 14:50 | 200 | 003:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 200 EN CORTE DE LINEA SE SECCIONALIZO LINEA ROTA | A21070300092 | New_Event | Wire Down | Include | Include | Equipment | 191 | 2021-07-03 | 38200 | keep | 0 | Jul | 2021 | 0.026018 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
SAN JUAN | 2021-07-03 11:43 | 2021-07-03 11:46 | 172 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-07-03 | 516 | keep | 0 | Jul | 2021 | 0.00035145 | 0.00011715 | Momentary | FALSE | FALSE | TMED_Event | 172
BAYAMON | 2021-07-03 11:44 | 2021-07-03 11:45 | 320 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21070300029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 320 | keep | 0 | Jul | 2021 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | TMED_Event | 320
PONCE | 2021-07-03 11:45 | 2021-07-03 11:46 | 2379 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P210703000XX | New_Event |  |  | Include | Wildlife | 1 | 2021-07-03 | 2379 | keep | 0 | Jul | 2021 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | TMED_Event | 2379
MAYAGÃœEZ | 2021-07-03 11:45 | 2021-07-03 13:04 | 250 | 001:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21070300000 | New_Event | Bad Weather | Include | Include | Weather | 79 | 2021-07-03 | 19750 | keep | 0 | Jul | 2021 | 0.013452 | 0.00017027 | Sustained | FALSE | TRUE | TMED_Event | 250
BAYAMON | 2021-07-03 11:45 | 2021-07-03 11:46 | 2861 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21070300030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 2861 | keep | 0 | Jul | 2021 | 0.0019486 | 0.0019486 | Momentary | FALSE | FALSE | TMED_Event | 2861
PONCE | 2021-07-03 11:46 | 2021-07-03 15:18 | 100 | 003:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA CAUSADO POR POSTE DE TELEFONICA PARTIDO | P21070300072 | 1st_after_momentary |  |  | Include | Wildlife | 212 | 2021-07-03 | 21200 | keep | 0 | Jul | 2021 | 0.014439 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
SAN JUAN | 2021-07-03 11:48 | 2021-07-03 11:50 | 172 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S21070300000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-03 | 344 | keep | 0 | Jul | 2021 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | TMED_Event | 172
PONCE | 2021-07-03 11:58 | 2021-07-03 13:25 | 100 | 001:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 Y 1 X 40 EN DIFERENTES CL POR AVE CRUZAR FASE | P21070300083 | New_Event |  |  | Include | Wildlife | 87 | 2021-07-03 | 8700 | keep | 0 | Jul | 2021 | 0.0059255 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
SAN JUAN | 2021-07-03 12:02 | 2021-07-03 18:00 | 80 | 005:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA CERRAR PUENTE PRIMARIO TRAS PATIO | S21070300053 | New_Event | Wire Down | Include | Include | Equipment | 358 | 2021-07-03 | 28640 | keep | 0 | Jul | 2021 | 0.019507 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
SAN JUAN | 2021-07-03 12:05 | 2021-07-03 14:06 | 225 | 002:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA. SE REPORTA AVERIA POR DESGANCHE | S21070300011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2021-07-03 | 27225 | keep | 0 | Jul | 2021 | 0.018543 | 0.00015325 | Sustained | FALSE | FALSE | TMED_Event | 225
VEGA BAJA | 2021-07-03 12:07 | 2021-07-03 20:58 | 40 | 008:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA | B21070300033 | New_Event | Cutout Failure | Include | Include | Equipment | 531 | 2021-07-03 | 21240 | keep | 0 | Jul | 2021 | 0.014466 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
MAYAGÃœEZ | 2021-07-03 12:17 | 2021-07-03 12:18 | 871 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR MAL TIEMPO | M21070300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-03 | 871 | keep | 0 | Jul | 2021 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | TMED_Event | 871
HUMACAO | 2021-07-03 12:23 | 2021-07-03 17:43 | 7 | 005:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21070300076 | New_Event | Secondary Wire Down | Include | Include | Equipment | 320 | 2021-07-03 | 2240 | keep | 0 | Jul | 2021 | 0.0015257 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
UTUADO | 2021-07-03 12:23 | 2021-07-04 14:45 | 100 | 026:22 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A21070300134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1582 | 2021-07-03 | 158200 | keep | 0 | Jul | 2021 | 0.10775 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
BAYAMON | 2021-07-03 12:27 | 2021-07-04 16:17 | 36 | 027:50 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21070200098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1670 | 2021-07-03 | 60120 | keep | 0 | Jul | 2021 | 0.040947 | 2.4519e-05 | Sustained | FALSE | TRUE | TMED_Event | 36
PONCE | 2021-07-03 12:31 | 2021-07-04 13:56 | 80 | 025:25 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21070300096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1525 | 2021-07-03 | 122000 | keep | 0 | Jul | 2021 | 0.083094 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
PONCE | 2021-07-03 12:38 | 2021-07-03 14:41 | 1650 | 002:03 | T | DESGANCHE | SE SACO RAMA SOBRE LINEA | P21070300098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2021-07-03 | 202950 | keep | 0 | Jul | 2021 | 0.13823 | 0.0011238 | Sustained | FALSE | TRUE | TMED_Event | 1650
BAYAMON | 2021-07-03 12:39 | 2021-07-05 14:50 | 50 | 050:11 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21070300064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3011 | 2021-07-03 | 150550 | keep | 0 | Jul | 2021 | 0.10254 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
PONCE | 2021-07-03 12:44 | 2021-07-03 18:56 | 100 | 006:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA POR CONECTOR PRIMARIO QUEMADO | P21070300100 | New_Event | Wire Down | Include | Include | Equipment | 372 | 2021-07-03 | 37200 | keep | 0 | Jul | 2021 | 0.025337 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
UTUADO | 2021-07-03 12:44 | 2021-07-04 12:00 | 80 | 023:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARARON LINEAS PRIMARIAS PARTIDAS | A21070300148 | New_Event | Wire Down | Include | Include | Equipment | 1396 | 2021-07-03 | 111680 | keep | 0 | Jul | 2021 | 0.076065 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
MAYAGÃœEZ | 2021-07-03 12:49 | 2021-07-04 15:15 | 50 | 026:26 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | M21070300391 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1586 | 2021-07-03 | 79300 | keep | 0 | Jul | 2021 | 0.054011 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
CAGUAS | 2021-07-03 12:56 | 2021-07-03 17:09 | 80 | 004:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA REPARO CONDUCTOR ROTO | C21070300085 | New_Event | Wire Down | Include | Include | Equipment | 253 | 2021-07-03 | 20240 | keep | 0 | Jul | 2021 | 0.013785 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
PONCE | 2021-07-03 12:57 | 2021-07-05 08:30 | 106 | 043:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN RISER POR MAL TIEMPO | P21070300105 | New_Event | Bad Weather | Include | Include | Weather | 2613 | 2021-07-03 | 276978 | keep | 0 | Jul | 2021 | 0.18865 | 7.2196e-05 | Sustained | FALSE | FALSE | TMED_Event | 106
BAYAMON | 2021-07-03 12:59 | 2021-07-03 14:54 | 2735 | 001:55 | T | DESGANCHE | SE SECCIONALIZO Y SE CERRO POR SCADA | B21070300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2021-07-03 | 314525 | keep | 0 | Jul | 2021 | 0.21422 | 0.0018628 | Sustained | FALSE | FALSE | TMED_Event | 2735
UTUADO | 2021-07-03 13:01 | 2021-07-07 18:34 | 150 | 101:33 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A21070300163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 6093 | 2021-07-03 | 913950 | keep | 0 | Jul | 2021 | 0.62249 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
MAYAGÃœEZ | 2021-07-03 13:03 | 2021-07-04 14:30 | 50 | 025:27 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | M21070300407 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1527 | 2021-07-03 | 76350 | keep | 0 | Jul | 2021 | 0.052002 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
CANOVANAS | 2021-07-03 13:04 | 2021-07-04 15:59 | 120 | 026:55 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | R21070300068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1615 | 2021-07-03 | 193800 | keep | 0 | Jul | 2021 | 0.132 | 8.1731e-05 | Sustained | FALSE | TRUE | TMED_Event | 120
BAYAMON | 2021-07-03 13:10 | 2021-07-03 16:15 | 150 | 003:05 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | S21070200074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2021-07-03 | 27750 | keep | 0 | Jul | 2021 | 0.0189 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
PONCE | 2021-07-03 13:11 | 2021-07-04 17:09 | 125 | 027:58 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA POR MAL TIEMPO | P21070300108 | New_Event | Bad Weather | Include | Include | Weather | 1678 | 2021-07-03 | 209750 | keep | 0 | Jul | 2021 | 0.14286 | 8.5137e-05 | Sustained | FALSE | TRUE | TMED_Event | 125
PONCE | 2021-07-03 13:14 | 2021-07-05 14:15 | 167 | 049:01 | T | DESGANCHE | ALIMENTADOR FUERA DE SERVICIO BAMBUAS SOBRE LINEA | P21070300109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2941 | 2021-07-03 | 491147 | keep | 0 | Jul | 2021 | 0.33452 | 0.00011374 | Sustained | FALSE | TRUE | TMED_Event | 167
BARRANQUITAS | 2021-07-03 13:15 | 2021-07-04 19:30 | 30 | 030:15 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA SE PATRULLO | C21070300095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1815 | 2021-07-03 | 54450 | keep | 0 | Jul | 2021 | 0.037086 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
MAYAGÃœEZ | 2021-07-03 13:15 | 2021-07-03 13:16 | 871 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR MAL TIEMPO | M21070300000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2021-07-03 | 871 | keep | 0 | Jul | 2021 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | TMED_Event | 871
YAUCO | 2021-07-03 13:21 | 2021-07-04 15:18 | 70 | 025:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P21070300114 | New_Event | Bad Weather | Include | Include | Weather | 1557 | 2021-07-03 | 108990 | keep | 0 | Jul | 2021 | 0.074233 | 4.7677e-05 | Sustained | FALSE | TRUE | TMED_Event | 70
PONCE | 2021-07-03 13:25 | 2021-07-03 13:26 | 1979 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE DE PORTATIL | P210704000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 1979 | keep | 0 | Jul | 2021 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | TMED_Event | 1979
PONCE | 2021-07-03 13:25 | 2021-07-03 13:26 | 5069 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE DE PORTATIL | P210704000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 5069 | keep | 0 | Jul | 2021 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | TMED_Event | 5069
PONCE | 2021-07-03 13:25 | 2021-07-03 13:26 | 5063 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE DE PORTATIL | P210704000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 5063 | keep | 0 | Jul | 2021 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | TMED_Event | 5063
PONCE | 2021-07-03 13:26 | 2021-07-03 19:50 | 100 | 006:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 Y 1 X 40 EN DIFERENTES CL POR AVE CRUZAR FASE | P21070300083 | Partial_restoration |  |  | Include | Wildlife | 384 | 2021-07-03 | 38400 | keep | 0 | Jul | 2021 | 0.026154 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
GUAYAMA | 2021-07-03 13:29 | 2021-07-03 18:33 | 40 | 005:04 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA POR DESGANCHE | P21070300118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 304 | 2021-07-03 | 12160 | keep | 0 | Jul | 2021 | 0.0082821 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
PONCE | 2021-07-03 13:29 | 2021-07-06 16:35 | 12 | 075:06 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR | P21070300117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 4506 | 2021-07-03 | 54072 | keep | 0 | Jul | 2021 | 0.036828 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
ARECIBO | 2021-07-03 13:36 | 2021-07-03 15:00 | 30 | 001:24 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A21070300191 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2021-07-03 | 2520 | keep | 0 | Jul | 2021 | 0.0017164 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
BAYAMON | 2021-07-03 13:37 | 2021-07-03 13:38 | 2858 | 000:01 | T | DESGANCHE | RECERRO | B21070300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-03 | 2858 | keep | 0 | Jul | 2021 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | TMED_Event | 2858
BAYAMON | 2021-07-03 13:38 | 2021-07-04 13:47 | 40 | 024:09 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | B21070300117 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1449 | 2021-07-03 | 57960 | keep | 0 | Jul | 2021 | 0.039476 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
CAGUAS | 2021-07-03 13:39 | 2021-07-03 16:28 | 150 | 002:49 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO | C21070300107 | New_Event | Bad Weather | Include | Include | Weather | 169 | 2021-07-03 | 25350 | keep | 0 | Jul | 2021 | 0.017266 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
ARECIBO | 2021-07-03 13:39 | 2021-07-03 17:50 | 80 | 004:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | A21070300198 | New_Event | Bad Weather | Include | Include | Weather | 251 | 2021-07-03 | 20080 | keep | 0 | Jul | 2021 | 0.013676 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
MAYAGÃœEZ | 2021-07-03 13:45 | 2021-07-04 19:17 | 50 | 029:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21070300453 | New_Event | Bad Weather | Include | Include | Weather | 1772 | 2021-07-03 | 88600 | keep | 0 | Jul | 2021 | 0.060345 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
PONCE | 2021-07-03 13:46 | 2021-07-04 19:51 | 150 | 030:05 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P21070300128 | New_Event | Bad Weather | Include | Include | Weather | 1805 | 2021-07-03 | 270750 | keep | 0 | Jul | 2021 | 0.18441 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
PONCE | 2021-07-03 13:52 | 2021-07-04 09:00 | 65 | 019:08 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | P21070300130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1148 | 2021-07-03 | 74620 | keep | 0 | Jul | 2021 | 0.050823 | 4.4271e-05 | Sustained | FALSE | TRUE | TMED_Event | 65
ARECIBO | 2021-07-03 13:57 | 2021-07-04 18:05 | 80 | 028:08 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A21070300216 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1688 | 2021-07-03 | 135040 | keep | 0 | Jul | 2021 | 0.091975 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
HUMACAO | 2021-07-03 14:04 | 2021-07-04 15:03 | 20 | 024:59 | P | CABLE SOTERRADO AVERIADO | SE TRANSPOSICIONO FASE EN EL SU-3 AVERIA EN RISER @ SU-1 | C21070300113 | New_Event | UG Cable Fault | Include | Include | Equipment | 1499 | 2021-07-03 | 29980 | keep | 0 | Jul | 2021 | 0.020419 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
HUMACAO | 2021-07-03 14:06 | 2021-07-03 18:53 | 20 | 004:47 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO CAUSA | C21070300115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 287 | 2021-07-03 | 5740 | keep | 0 | Jul | 2021 | 0.0039095 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
MAYAGÃœEZ | 2021-07-03 14:14 | 2021-07-05 16:38 | 60 | 050:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21070300481 | New_Event | Bad Weather | Include | Include | Weather | 3024 | 2021-07-03 | 181440 | keep | 0 | Jul | 2021 | 0.12358 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
ARECIBO | 2021-07-03 14:15 | 2021-07-03 17:58 | 150 | 003:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | A21070300231 | New_Event | Wire Down | Include | Include | Equipment | 223 | 2021-07-03 | 33450 | keep | 0 | Jul | 2021 | 0.022783 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
SAN JUAN | 2021-07-03 14:17 | 2021-07-03 14:18 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 4133 | keep | 0 | Jul | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | TMED_Event | 4133
SAN JUAN | 2021-07-03 14:17 | 2021-07-03 14:18 | 1615 | 000:01 | T | SECUNDARIA/DESGANCHE | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21070300000 | Additional_clients | Secondary Vegetation | Include | Include | Vegetation | 1 | 2021-07-03 | 1615 | keep | 0 | Jul | 2021 | 0.0011 | 0 | Momentary | FALSE | FALSE | TMED_Event | 0
SAN JUAN | 2021-07-03 14:18 | 2021-07-03 16:18 | 8 | 002:00 | P | SECUNDARIA/DESGANCHE | ABRIO TRANSFORMADOR PARA DESGANCHAR Y REPARAR SECUNDARIA | R21070100011 | 1st_after_momentary | Secondary Vegetation | Include | Include | Vegetation | 120 | 2021-07-03 | 960 | keep | 0 | Jul | 2021 | 0.00065385 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
UTUADO | 2021-07-03 14:18 | 2021-07-05 12:00 | 12 | 045:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21070300235 | New_Event | Bad Weather | Include | Include | Weather | 2742 | 2021-07-03 | 32904 | keep | 0 | Jul | 2021 | 0.022411 | 8.1731e-06 | Sustained | FALSE | TRUE | TMED_Event | 12
ARECIBO | 2021-07-03 14:20 | 2021-07-05 12:47 | 100 | 046:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21070300239 | New_Event | Wire Down | Include | Include | Equipment | 2787 | 2021-07-03 | 278700 | keep | 0 | Jul | 2021 | 0.18982 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
SAN JUAN | 2021-07-03 14:23 | 2021-07-04 14:08 | 99 | 023:45 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21070300082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1425 | 2021-07-03 | 141075 | keep | 0 | Jul | 2021 | 0.096086 | 6.7428e-05 | Sustained | FALSE | TRUE | TMED_Event | 99
SAN JUAN | 2021-07-03 14:24 | 2021-07-04 11:04 | 80 | 020:40 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21070300118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1240 | 2021-07-03 | 99200 | keep | 0 | Jul | 2021 | 0.067565 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
MAYAGÃœEZ | 2021-07-03 14:24 | 2021-07-03 15:45 | 70 | 001:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21070300000 | New_Event | Wire Down | Include | Include | Equipment | 81 | 2021-07-03 | 5670 | keep | 0 | Jul | 2021 | 0.0038618 | 4.7677e-05 | Sustained | FALSE | TRUE | TMED_Event | 70
BAYAMON | 2021-07-03 14:28 | 2021-07-03 16:30 | 1085 | 002:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA SE TUVO QUE REALIZAR PODA | S21070300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2021-07-03 | 132370 | keep | 0 | Jul | 2021 | 0.090157 | 0.00073899 | Sustained | FALSE | FALSE | TMED_Event | 1085
CAGUAS | 2021-07-03 14:32 | 2021-07-06 20:46 | 10 | 078:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE DESGANCHO Y SE LEVANTO CONDUCTOR PRIMARIO | C21070300124 | New_Event | Wire Down | Include | Include | Equipment | 4694 | 2021-07-03 | 46940 | keep | 0 | Jul | 2021 | 0.031971 | 6.811e-06 | Sustained | FALSE | TRUE | TMED_Event | 10
ARECIBO | 2021-07-03 14:33 | 2021-07-04 14:15 | 300 | 023:42 | P | ESTRUCTURA AVERIADA | 1 X 100 EN CORTE DE LINEA SE ELIMINO TENSOR HACIENDO CONTACTO CON FASES | A21070300250 | New_Event | Defective Pole | Include | Include | Equipment | 1422 | 2021-07-03 | 426600 | keep | 0 | Jul | 2021 | 0.29056 | 0.00020433 | Sustained | FALSE | TRUE | TMED_Event | 300
MAYAGÃœEZ | 2021-07-03 14:33 | 2021-07-04 18:00 | 15 | 027:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA LINEA PRIMARIA ROTA SE ABRIO PUENTES | M21070300496 | New_Event | Wire Down | Include | Include | Equipment | 1647 | 2021-07-03 | 24705 | keep | 0 | Jul | 2021 | 0.016826 | 1.0216e-05 | Sustained | FALSE | TRUE | TMED_Event | 15
MAYAGÃœEZ | 2021-07-03 14:33 | 2021-07-05 18:00 | 3 | 051:27 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO Y SE RELOCALIZO TRANSFORMADOR | M21070300496 | New_Event | Defective Pole | Include | Include | Equipment | 3087 | 2021-07-03 | 9261 | keep | 0 | Jul | 2021 | 0.0063076 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
BAYAMON | 2021-07-03 14:35 | 2021-07-03 16:34 | 1715 | 001:59 | T | DESGANCHE | SE SECCIONALIZO Y SE CERRO POR SCADA | B21070300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2021-07-03 | 204085 | keep | 0 | Jul | 2021 | 0.139 | 0.0011681 | Sustained | FALSE | FALSE | TMED_Event | 1715
BAYAMON | 2021-07-03 14:39 | 2021-07-04 10:26 | 20 | 019:47 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE REPARO TOMA | B21070300071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1187 | 2021-07-03 | 23740 | keep | 0 | Jul | 2021 | 0.016169 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
CAGUAS | 2021-07-03 14:41 | 2021-07-03 14:42 | 1307 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C21070300000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-03 | 1307 | keep | 0 | Jul | 2021 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | TMED_Event | 1307
UTUADO | 2021-07-03 14:41 | 2021-07-04 15:25 | 40 | 024:44 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21070300255 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1484 | 2021-07-03 | 59360 | keep | 0 | Jul | 2021 | 0.04043 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
CAGUAS | 2021-07-03 14:42 | 2021-07-03 15:15 | 900 | 000:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR | C21070300000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 33 | 2021-07-03 | 29700 | keep | 0 | Jul | 2021 | 0.020229 | 0.00061299 | Sustained | FALSE | FALSE | TMED_Event | 900
YAUCO | 2021-07-03 14:50 | 2021-07-05 17:10 | 53 | 050:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | P21070400060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3020 | 2021-07-03 | 160060 | keep | 0 | Jul | 2021 | 0.10902 | 3.6098e-05 | Sustained | FALSE | TRUE | TMED_Event | 53
ARECIBO | 2021-07-03 14:50 | 2021-07-03 18:15 | 80 | 003:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21070300260 | New_Event | Wire Down | Include | Include | Equipment | 205 | 2021-07-03 | 16400 | keep | 0 | Jul | 2021 | 0.01117 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
UTUADO | 2021-07-03 14:54 | 2021-07-03 17:48 | 60 | 002:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | A21070300262 | New_Event | Bad Weather | Include | Include | Weather | 174 | 2021-07-03 | 10440 | keep | 0 | Jul | 2021 | 0.0071106 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
VEGA BAJA | 2021-07-03 14:54 | 2021-07-03 20:57 | 60 | 006:03 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21070300079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 363 | 2021-07-03 | 21780 | keep | 0 | Jul | 2021 | 0.014834 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
BAYAMON | 2021-07-03 14:54 | 2021-07-03 17:23 | 2000 | 002:29 | P | DESGANCHE | SE DESGANCHARON BAMBUAS Y SE CERRO MACHETES | B21070300000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 149 | 2021-07-03 | 298000 | keep | 0 | Jul | 2021 | 0.20297 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
CAGUAS | 2021-07-03 14:55 | 2021-07-04 11:51 | 100 | 020:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21070300013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1256 | 2021-07-03 | 125600 | keep | 0 | Jul | 2021 | 0.085546 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
MAYAGÃœEZ | 2021-07-03 14:56 | 2021-07-03 14:57 | 1268 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR MAL TIEMPO | M21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 1268 | keep | 0 | Jul | 2021 | 0.00086363 | 0.00086363 | Momentary | FALSE | FALSE | TMED_Event | 1268
ARECIBO | 2021-07-03 14:57 | 2021-07-03 19:30 | 10 | 004:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | A21070200115 | New_Event | Bad Weather | Include | Include | Weather | 273 | 2021-07-03 | 2730 | keep | 0 | Jul | 2021 | 0.0018594 | 6.811e-06 | Sustained | FALSE | TRUE | TMED_Event | 10
MAYAGÃœEZ | 2021-07-03 15:01 | 2021-07-04 18:40 | 50 | 027:39 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070300524 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1659 | 2021-07-03 | 82950 | keep | 0 | Jul | 2021 | 0.056497 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
BAYAMON | 2021-07-03 15:02 | 2021-07-03 22:23 | 312 | 007:21 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIERON MACHETES DETRAS DE CRUZ ROJA, SE ABRIO PUENTE POCO MAS ADELANTE DE UNA FASE POR CABLE EN EL SUELO | S21070300000 | New_Event | Wire Down | Include | Include | Equipment | 441 | 2021-07-03 | 137592 | keep | 0 | Jul | 2021 | 0.093713 | 0.0002125 | Sustained | FALSE | FALSE | TMED_Event | 312
SAN JUAN | 2021-07-03 15:09 | 2021-07-04 11:27 | 130 | 020:18 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21070300095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1218 | 2021-07-03 | 158340 | keep | 0 | Jul | 2021 | 0.10784 | 8.8542e-05 | Sustained | FALSE | TRUE | TMED_Event | 130
MAYAGÃœEZ | 2021-07-03 15:12 | 2021-07-03 15:15 | 1337 | 000:03 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DEL INTERRUPTOR MAL TIEMPO VIENTOS FUERTES | M21070300000 | New_Event | Bad Weather | Include | Include | Weather | 3 | 2021-07-03 | 4011 | keep | 0 | Jul | 2021 | 0.0027319 | 0.00091062 | Momentary | FALSE | FALSE | TMED_Event | 1337
CAGUAS | 2021-07-03 15:15 | 2021-07-03 17:12 | 1307 | 001:57 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO | C21070300162 | Additional_clients | Wire Down | Include | Include | Equipment | 117 | 2021-07-03 | 152919 | keep | 0 | Jul | 2021 | 0.10415 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
AGUADILLA | 2021-07-03 15:15 | 2021-07-04 15:30 | 100 | 024:15 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA DESGANCHE | M21070400011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1455 | 2021-07-03 | 145500 | keep | 0 | Jul | 2021 | 0.099099 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
BAYAMON | 2021-07-03 15:17 | 2021-07-03 16:20 | 7 | 001:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO POSTE PARTIDO IMPACTADO Y SE CERRO TRANSFORMADOR | B21070300000 | New_Event |  |  | Include | Wildlife | 63 | 2021-07-03 | 441 | keep | 0 | Jul | 2021 | 0.00030036 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
ARECIBO | 2021-07-03 15:20 | 2021-07-03 16:40 | 20 | 001:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21070300270 | New_Event | Bad Weather | Include | Include | Weather | 80 | 2021-07-03 | 1600 | keep | 0 | Jul | 2021 | 0.0010898 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
MAYAGÃœEZ | 2021-07-03 15:28 | 2021-07-05 10:05 | 150 | 042:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21070300538 | New_Event | Bad Weather | Include | Include | Weather | 2557 | 2021-07-03 | 383550 | keep | 0 | Jul | 2021 | 0.26123 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
ARECIBO | 2021-07-03 15:28 | 2021-07-04 10:20 | 40 | 018:52 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | A21070300407 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1132 | 2021-07-03 | 45280 | keep | 0 | Jul | 2021 | 0.03084 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
BAYAMON | 2021-07-03 15:29 | 2021-07-05 10:17 | 50 | 042:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA SE REPARO PUENTE LINEA A CAJA | S21070300155 | New_Event | Cutout Failure | Include | Include | Equipment | 2568 | 2021-07-03 | 128400 | keep | 0 | Jul | 2021 | 0.087453 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
BARRANQUITAS | 2021-07-03 15:29 | 2021-07-03 18:53 | 1246 | 003:24 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE REEMPLAZO AISLADOR | C21070300000 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 204 | 2021-07-03 | 254184 | keep | 0 | Jul | 2021 | 0.17312 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
CAGUAS | 2021-07-03 15:33 | 2021-07-03 15:34 | 2608 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 2608 | keep | 0 | Jul | 2021 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | TMED_Event | 2608
MAYAGÃœEZ | 2021-07-03 15:35 | 2021-07-06 12:51 | 2 | 069:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA AVERIADA | M21070300542 | New_Event | Cutout Failure | Include | Include | Equipment | 4156 | 2021-07-03 | 8312 | keep | 0 | Jul | 2021 | 0.0056613 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
PONCE | 2021-07-03 15:37 | 2021-07-04 21:26 | 97 | 029:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CONVERTIDOR Y 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P21070300165 | New_Event | Bad Weather | Include | Include | Weather | 1789 | 2021-07-03 | 173533 | keep | 0 | Jul | 2021 | 0.11819 | 6.6066e-05 | Sustained | FALSE | TRUE | TMED_Event | 97
PONCE | 2021-07-03 15:39 | 2021-07-04 08:15 | 18 | 016:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR, AVE CRUZO FASE. | P21070300166 | New_Event |  |  | Include | Wildlife | 996 | 2021-07-03 | 17928 | keep | 0 | Jul | 2021 | 0.012211 | 1.226e-05 | Sustained | FALSE | FALSE | TMED_Event | 18
BAYAMON | 2021-07-03 15:41 | 2021-07-04 15:17 | 120 | 023:36 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21070300096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1416 | 2021-07-03 | 169920 | keep | 0 | Jul | 2021 | 0.11573 | 8.1731e-05 | Sustained | FALSE | TRUE | TMED_Event | 120
UTUADO | 2021-07-03 15:48 | 2021-07-04 12:20 | 50 | 020:32 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REEMPLAZARON AISLADORES PRIMARIOS PARTIDOS | A21070300281 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1232 | 2021-07-03 | 61600 | keep | 0 | Jul | 2021 | 0.041955 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
ARECIBO | 2021-07-03 15:51 | 2021-07-03 17:45 | 20 | 001:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21070300283 | New_Event | Bad Weather | Include | Include | Weather | 114 | 2021-07-03 | 2280 | keep | 0 | Jul | 2021 | 0.0015529 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
BAYAMON | 2021-07-03 15:56 | 2021-07-05 07:40 | 50 | 039:44 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21070300161 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2384 | 2021-07-03 | 119200 | keep | 0 | Jul | 2021 | 0.081187 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
CANOVANAS | 2021-07-03 15:56 | 2021-07-04 15:20 | 3 | 023:24 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR SE INSPECCIONO | R21070300106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1404 | 2021-07-03 | 4212 | keep | 0 | Jul | 2021 | 0.0028688 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
ARECIBO | 2021-07-03 16:00 | 2021-07-03 17:17 | 274 | 001:17 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA ROTA EN EL 8001-03 CUYA CARGA ESTA POR EL 8001-02 SE ABRIO EL AMARRE ENTRE AMBOS | A21070300000 | New_Event | Wire Down | Include | Include | Equipment | 77 | 2021-07-03 | 21098 | keep | 0 | Jul | 2021 | 0.01437 | 0.00018662 | Sustained | FALSE | TRUE | TMED_Event | 274
ARECIBO | 2021-07-03 16:00 | 2021-07-03 19:32 | 185 | 003:32 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA ROTA EN TRONCAL | A21070300000 | New_Event | Wire Down | Include | Include | Equipment | 212 | 2021-07-03 | 39220 | keep | 0 | Jul | 2021 | 0.026713 | 0.000126 | Sustained | FALSE | TRUE | TMED_Event | 185
PONCE | 2021-07-03 16:00 | 2021-07-04 16:54 | 80 | 024:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 Y 1 X 30 EN DISTINTOS CORTES DE LINEA, SE REEMPLAZO CAJA PRIMARIA QUEMADA | P210704000XX | New_Event | Cutout Failure | Include | Include | Equipment | 1494 | 2021-07-03 | 119520 | keep | 0 | Jul | 2021 | 0.081405 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
ARECIBO | 2021-07-03 16:08 | 2021-07-03 20:20 | 60 | 004:12 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO | A21070300293 | New_Event | Bad Weather | Include | Include | Weather | 252 | 2021-07-03 | 15120 | keep | 0 | Jul | 2021 | 0.010298 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
BAYAMON | 2021-07-03 16:16 | 2021-07-03 18:32 | 100 | 002:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | S21070300075 | New_Event | Cutout Failure | Include | Include | Equipment | 136 | 2021-07-03 | 13600 | keep | 0 | Jul | 2021 | 0.0092629 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
ARECIBO | 2021-07-03 16:16 | 2021-07-03 19:10 | 40 | 002:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | A21070300301 | New_Event | Bad Weather | Include | Include | Weather | 174 | 2021-07-03 | 6960 | keep | 0 | Jul | 2021 | 0.0047404 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
SAN JUAN | 2021-07-03 16:25 | 2021-07-06 07:51 | 35 | 063:26 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21070300164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3806 | 2021-07-03 | 133210 | keep | 0 | Jul | 2021 | 0.090729 | 2.3838e-05 | Sustained | FALSE | TRUE | TMED_Event | 35
BAYAMON | 2021-07-03 16:26 | 2021-07-03 18:06 | 80 | 001:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO TRASPATIO Y SE CERRO MACHETES | B21070200155 | New_Event | Wire Down | Include | Include | Equipment | 100 | 2021-07-03 | 8000 | keep | 0 | Jul | 2021 | 0.0054488 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
ARECIBO | 2021-07-03 16:26 | 2021-07-03 16:27 | 1227 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR MAL TIEMPO | A21070300000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-03 | 1227 | keep | 0 | Jul | 2021 | 0.0008357 | 0 | Momentary | FALSE | FALSE | TMED_Event | 0
ARECIBO | 2021-07-03 16:27 | 2021-07-03 19:30 | 30 | 003:03 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | A21070300149 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 183 | 2021-07-03 | 5490 | keep | 0 | Jul | 2021 | 0.0037392 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
MAYAGÃœEZ | 2021-07-03 16:28 | 2021-07-03 18:20 | 150 | 001:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M21070300000 | New_Event | Wire Down | Include | Include | Equipment | 112 | 2021-07-03 | 16800 | keep | 0 | Jul | 2021 | 0.011442 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
UTUADO | 2021-07-03 16:30 | 2021-07-05 20:15 | 30 | 051:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y SE RETIRO RAMAS SOBRE LAS LINEAS | A21070300318 | New_Event | Wire Down | Include | Include | Equipment | 3105 | 2021-07-03 | 93150 | keep | 0 | Jul | 2021 | 0.063444 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
YAUCO | 2021-07-03 16:32 | 2021-07-07 20:50 | 100 | 100:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA DEL SUELO | P21070300178 | New_Event | Wire Down | Include | Include | Equipment | 6018 | 2021-07-03 | 601800 | keep | 0 | Jul | 2021 | 0.40988 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
BAYAMON | 2021-07-03 16:34 | 2021-07-03 16:45 | 1300 | 000:11 | P | DESGANCHE | SE DESGANCHO EN MACHETES Y SE CERRO MACHETES | B21070300000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 11 | 2021-07-03 | 14300 | keep | 0 | Jul | 2021 | 0.0097397 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
CANOVANAS | 2021-07-03 16:37 | 2021-07-04 10:59 | 36 | 018:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA CRUCE CON CULEBRA | R21070300112 | New_Event |  |  | Include | Wildlife | 1102 | 2021-07-03 | 39672 | keep | 0 | Jul | 2021 | 0.02702 | 2.4519e-05 | Sustained | FALSE | TRUE | TMED_Event | 36
ARECIBO | 2021-07-03 16:37 | 2021-07-03 20:20 | 65 | 003:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | A21070300324 | New_Event | Vegetation Contact | Include | Include | Vegetation | 223 | 2021-07-03 | 14495 | keep | 0 | Jul | 2021 | 0.0098725 | 4.4271e-05 | Sustained | FALSE | TRUE | TMED_Event | 65
MAYAGÃœEZ | 2021-07-03 16:40 | 2021-07-03 16:41 | 871 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR MAL TIEMPO | M21070300000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2021-07-03 | 871 | keep | 0 | Jul | 2021 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | TMED_Event | 871
ARECIBO | 2021-07-03 16:49 | 2021-07-03 20:22 | 2266 | 003:33 | T | DESGANCHE | SE ABRIO INTERRUPTOR AUTORIZADO POR ING FENEQUE PARA REALIZAR DESGANCHE Y ENDEREZAR POSTE CONCRETO | A21070300000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 213 | 2021-07-03 | 482658 | keep | 0 | Jul | 2021 | 0.32874 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
BAYAMON | 2021-07-03 16:50 | 2021-07-04 08:21 | 20 | 015:31 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21070300112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 931 | 2021-07-03 | 18620 | keep | 0 | Jul | 2021 | 0.012682 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
HUMACAO | 2021-07-03 17:09 | 2021-07-03 20:36 | 150 | 003:27 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO | C21070300000 | New_Event | Bad Weather | Include | Include | Weather | 207 | 2021-07-03 | 31050 | keep | 0 | Jul | 2021 | 0.021148 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
CAGUAS | 2021-07-03 17:12 | 2021-07-03 21:29 | 900 | 004:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR | C21070300000 | Partial_restoration | Wire Down | Include | Include | Equipment | 257 | 2021-07-03 | 231300 | keep | 0 | Jul | 2021 | 0.15754 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
BAYAMON | 2021-07-03 17:24 | 2021-07-03 18:05 | 60 | 000:41 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 41 | 2021-07-03 | 2460 | keep | 0 | Jul | 2021 | 0.0016755 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
ARECIBO | 2021-07-03 17:27 | 2021-07-04 12:29 | 60 | 019:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | A21070300347 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1142 | 2021-07-03 | 68520 | keep | 0 | Jul | 2021 | 0.046669 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
PONCE | 2021-07-03 17:36 | 2021-07-03 22:00 | 147 | 004:24 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | P21070300018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 264 | 2021-07-03 | 38808 | keep | 0 | Jul | 2021 | 0.026432 | 0.00010012 | Sustained | FALSE | TRUE | TMED_Event | 147
MAYAGÃœEZ | 2021-07-03 17:37 | 2021-07-05 10:00 | 80 | 040:23 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070300606 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2423 | 2021-07-03 | 193840 | keep | 0 | Jul | 2021 | 0.13202 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
MAYAGÃœEZ | 2021-07-03 17:53 | 2021-07-05 14:45 | 300 | 044:52 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA DESGANCHE | M21070300612 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2692 | 2021-07-03 | 807600 | keep | 0 | Jul | 2021 | 0.55005 | 0.00020433 | Sustained | FALSE | TRUE | TMED_Event | 300
BAYAMON | 2021-07-03 17:55 | 2021-07-04 12:14 | 25 | 018:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO TRASPATIO CARGA POR 1903 05 | B21070300118 | New_Event | Wire Down | Include | Include | Equipment | 1099 | 2021-07-03 | 27475 | keep | 0 | Jul | 2021 | 0.018713 | 1.7027e-05 | Sustained | FALSE | TRUE | TMED_Event | 25
BAYAMON | 2021-07-03 17:55 | 2021-07-04 15:08 | 23 | 021:13 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO | B21070300118 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1273 | 2021-07-03 | 29279 | keep | 0 | Jul | 2021 | 0.019942 | 1.5665e-05 | Sustained | FALSE | TRUE | TMED_Event | 23
AGUADILLA | 2021-07-03 17:59 | 2021-07-04 20:00 | 100 | 026:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21070300615 | New_Event | Bad Weather | Include | Include | Weather | 1561 | 2021-07-03 | 156100 | keep | 0 | Jul | 2021 | 0.10632 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
SAN JUAN | 2021-07-03 18:00 | 2021-07-03 20:50 | 1271 | 002:50 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21070300000 | Additional_clients | Wire Down | Include | Include | Equipment | 170 | 2021-07-03 | 216070 | keep | 0 | Jul | 2021 | 0.14716 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
AGUADILLA | 2021-07-03 18:00 | 2021-07-05 11:20 | 80 | 041:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21070300000 | New_Event | Bad Weather | Include | Include | Weather | 2480 | 2021-07-03 | 198400 | keep | 0 | Jul | 2021 | 0.13513 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
PONCE | 2021-07-03 18:10 | 2021-07-04 17:30 | 120 | 023:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR MAL TIEMPO | P21070300187 | New_Event | Bad Weather | Include | Include | Weather | 1400 | 2021-07-03 | 168000 | keep | 0 | Jul | 2021 | 0.11442 | 8.1731e-05 | Sustained | FALSE | TRUE | TMED_Event | 120
BAYAMON | 2021-07-03 18:13 | 2021-07-04 16:30 | 36 | 022:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUAS | B21070300120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1337 | 2021-07-03 | 48132 | keep | 0 | Jul | 2021 | 0.032782 | 2.4519e-05 | Sustained | FALSE | TRUE | TMED_Event | 36
CANOVANAS | 2021-07-03 18:14 | 2021-07-03 19:36 | 2708 | 001:22 | S | NO SE REPORTO CAUSA | DISPARO DEL TRANSFORMADOR 2305 | R21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2021-07-03 | 222056 | keep | 0 | Jul | 2021 | 0.15124 | 0.0018444 | Sustained | FALSE | FALSE | TMED_Event | 2708
CANOVANAS | 2021-07-03 18:14 | 2021-07-03 19:36 | 2524 | 001:22 | S | NO SE REPORTO CAUSA | DISPARO DEL TRANSFORMADOR 2305 | R21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2021-07-03 | 206968 | keep | 0 | Jul | 2021 | 0.14096 | 0.0017191 | Sustained | FALSE | FALSE | TMED_Event | 2524
CANOVANAS | 2021-07-03 18:14 | 2021-07-03 19:36 | 1648 | 001:22 | S | NO SE REPORTO CAUSA | DISPARO DEL TRANSFORMADOR 2305 | R21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2021-07-03 | 135136 | keep | 0 | Jul | 2021 | 0.092041 | 0.0011224 | Sustained | FALSE | FALSE | TMED_Event | 1648
BAYAMON | 2021-07-03 18:17 | 2021-07-04 11:58 | 12 | 017:41 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REMPLAZARON BARRAS SECUNDARIAS EN PEDESTAL | B21070300122 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 1061 | 2021-07-03 | 12732 | keep | 0 | Jul | 2021 | 0.0086717 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
MAYAGÃœEZ | 2021-07-03 18:31 | 2021-07-03 18:32 | 863 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 863 | keep | 0 | Jul | 2021 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | TMED_Event | 863
MAYAGÃœEZ | 2021-07-03 18:44 | 2021-07-03 20:20 | 80 | 001:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO | M21070300000 | New_Event | Wire Down | Include | Include | Equipment | 96 | 2021-07-03 | 7680 | keep | 0 | Jul | 2021 | 0.0052308 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
AGUADILLA | 2021-07-03 19:02 | 2021-07-04 12:30 | 100 | 017:28 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | M21070300624 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1048 | 2021-07-03 | 104800 | keep | 0 | Jul | 2021 | 0.071379 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
BAYAMON | 2021-07-03 19:05 | 2021-07-04 02:13 | 20 | 007:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA Y SE REALIZO DESGANCHE | B21070300161 | New_Event | Cutout Failure | Include | Include | Equipment | 428 | 2021-07-03 | 8560 | keep | 0 | Jul | 2021 | 0.0058302 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
BARRANQUITAS | 2021-07-03 19:12 | 2021-07-04 19:16 | 6 | 024:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO HACIA CAJA PRIMARIA | C21070300195 | New_Event | Wire Down | Include | Include | Equipment | 1444 | 2021-07-03 | 8664 | keep | 0 | Jul | 2021 | 0.005901 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
CAGUAS | 2021-07-03 19:17 | 2021-07-04 01:47 | 10 | 006:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO HACIA CAJA | C21070300197 | New_Event | Wire Down | Include | Include | Equipment | 390 | 2021-07-03 | 3900 | keep | 0 | Jul | 2021 | 0.0026563 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
CANOVANAS | 2021-07-03 19:25 | 2021-07-03 19:26 | 7621 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 7621 | keep | 0 | Jul | 2021 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | TMED_Event | 7621
ARECIBO | 2021-07-03 19:35 | 2021-07-04 19:10 | 100 | 023:35 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A21070300076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1415 | 2021-07-03 | 141500 | keep | 0 | Jul | 2021 | 0.096375 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
FAJARDO | 2021-07-03 19:40 | 2021-07-03 19:43 | 1571 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 4713 | keep | 0 | Jul | 2021 | 0.00321 | 0.00107 | Momentary | FALSE | TRUE | TMED_Event | 1571
FAJARDO | 2021-07-03 19:40 | 2021-07-03 19:43 | 2041 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 6123 | keep | 0 | Jul | 2021 | 0.0041703 | 0.0013901 | Momentary | FALSE | TRUE | TMED_Event | 2041
FAJARDO | 2021-07-03 19:40 | 2021-07-03 19:43 | 625 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 1875 | keep | 0 | Jul | 2021 | 0.0012771 | 0.00042568 | Momentary | FALSE | TRUE | TMED_Event | 625
FAJARDO | 2021-07-03 19:40 | 2021-07-03 19:43 | 1463 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 4389 | keep | 0 | Jul | 2021 | 0.0029893 | 0.00099644 | Momentary | FALSE | TRUE | TMED_Event | 1463
FAJARDO | 2021-07-03 19:40 | 2021-07-03 19:43 | 1394 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 4182 | keep | 0 | Jul | 2021 | 0.0028483 | 0.00094945 | Momentary | FALSE | TRUE | TMED_Event | 1394
FAJARDO | 2021-07-03 19:40 | 2021-07-03 19:43 | 412 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 1236 | keep | 0 | Jul | 2021 | 0.00084183 | 0.00028061 | Momentary | FALSE | TRUE | TMED_Event | 412
FAJARDO | 2021-07-03 19:40 | 2021-07-03 19:43 | 2286 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 6858 | keep | 0 | Jul | 2021 | 0.004671 | 0.001557 | Momentary | FALSE | TRUE | TMED_Event | 2286
FAJARDO | 2021-07-03 19:40 | 2021-07-03 19:43 | 693 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 2079 | keep | 0 | Jul | 2021 | 0.001416 | 0.000472 | Momentary | FALSE | TRUE | TMED_Event | 693
FAJARDO | 2021-07-03 19:40 | 2021-07-03 19:43 | 4098 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 12294 | keep | 0 | Jul | 2021 | 0.0083734 | 0.0027911 | Momentary | FALSE | TRUE | TMED_Event | 4098
FAJARDO | 2021-07-03 19:40 | 2021-07-03 19:43 | 956 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 2868 | keep | 0 | Jul | 2021 | 0.0019534 | 0.00065113 | Momentary | FALSE | TRUE | TMED_Event | 956
FAJARDO | 2021-07-03 19:40 | 2021-07-03 19:43 | 2343 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 7029 | keep | 0 | Jul | 2021 | 0.0047874 | 0.0015958 | Momentary | FALSE | TRUE | TMED_Event | 2343
FAJARDO | 2021-07-03 19:40 | 2021-07-03 19:43 | 1830 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 5490 | keep | 0 | Jul | 2021 | 0.0037392 | 0.0012464 | Momentary | FALSE | TRUE | TMED_Event | 1830
FAJARDO | 2021-07-03 19:40 | 2021-07-03 19:43 | 710 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 2130 | keep | 0 | Jul | 2021 | 0.0014507 | 0.00048358 | Momentary | FALSE | TRUE | TMED_Event | 710
FAJARDO | 2021-07-03 19:40 | 2021-07-03 19:43 | 969 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 2907 | keep | 0 | Jul | 2021 | 0.0019799 | 0.00065998 | Momentary | FALSE | TRUE | TMED_Event | 969
CANOVANAS | 2021-07-03 19:40 | 2021-07-03 19:43 | 2708 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 8124 | keep | 0 | Jul | 2021 | 0.0055332 | 0.0018444 | Momentary | FALSE | TRUE | TMED_Event | 2708
CANOVANAS | 2021-07-03 19:40 | 2021-07-03 19:43 | 2524 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 7572 | keep | 0 | Jul | 2021 | 0.0051573 | 0.0017191 | Momentary | FALSE | TRUE | TMED_Event | 2524
CANOVANAS | 2021-07-03 19:40 | 2021-07-03 19:43 | 1648 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 4944 | keep | 0 | Jul | 2021 | 0.0033673 | 0.0011224 | Momentary | FALSE | TRUE | TMED_Event | 1648
CANOVANAS | 2021-07-03 19:40 | 2021-07-03 20:34 | 3838 | 000:54 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 54 | 2021-07-03 | 207252 | keep | 0 | Jul | 2021 | 0.14116 | 0.002614 | Sustained | FALSE | TRUE | TMED_Event | 3838
CANOVANAS | 2021-07-03 19:40 | 2021-07-03 20:34 | 817 | 000:54 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 54 | 2021-07-03 | 44118 | keep | 0 | Jul | 2021 | 0.030049 | 0.00055645 | Sustained | FALSE | TRUE | TMED_Event | 817
CANOVANAS | 2021-07-03 19:40 | 2021-07-03 20:34 | 1124 | 000:54 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 54 | 2021-07-03 | 60696 | keep | 0 | Jul | 2021 | 0.04134 | 0.00076555 | Sustained | FALSE | TRUE | TMED_Event | 1124
CANOVANAS | 2021-07-03 19:40 | 2021-07-03 19:43 | 2039 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 6117 | keep | 0 | Jul | 2021 | 0.0041663 | 0.0013888 | Momentary | FALSE | TRUE | TMED_Event | 2039
CANOVANAS | 2021-07-03 19:40 | 2021-07-03 19:43 | 4188 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 12564 | keep | 0 | Jul | 2021 | 0.0085573 | 0.0028524 | Momentary | FALSE | TRUE | TMED_Event | 4188
CANOVANAS | 2021-07-03 19:40 | 2021-07-03 19:43 | 4085 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 12255 | keep | 0 | Jul | 2021 | 0.0083468 | 0.0027823 | Momentary | FALSE | TRUE | TMED_Event | 4085
CANOVANAS | 2021-07-03 19:40 | 2021-07-03 19:43 | 3464 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 10392 | keep | 0 | Jul | 2021 | 0.0070779 | 0.0023593 | Momentary | FALSE | TRUE | TMED_Event | 3464
CANOVANAS | 2021-07-03 19:40 | 2021-07-03 19:43 | 7621 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 22863 | keep | 0 | Jul | 2021 | 0.015572 | 0.0051906 | Momentary | FALSE | TRUE | TMED_Event | 7621
CANOVANAS | 2021-07-03 19:40 | 2021-07-03 19:43 | 3699 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 11097 | keep | 0 | Jul | 2021 | 0.0075581 | 0.0025194 | Momentary | FALSE | TRUE | TMED_Event | 3699
CANOVANAS | 2021-07-03 19:40 | 2021-07-03 19:43 | 2675 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 8025 | keep | 0 | Jul | 2021 | 0.0054658 | 0.0018219 | Momentary | FALSE | TRUE | TMED_Event | 2675
FAJARDO | 2021-07-03 19:40 | 2021-07-03 19:43 | 1839 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 5517 | keep | 0 | Jul | 2021 | 0.0037576 | 0.0012525 | Momentary | FALSE | TRUE | TMED_Event | 1839
FAJARDO | 2021-07-03 19:40 | 2021-07-03 19:43 | 1778 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 5334 | keep | 0 | Jul | 2021 | 0.003633 | 0.001211 | Momentary | FALSE | TRUE | TMED_Event | 1778
FAJARDO | 2021-07-03 19:40 | 2021-07-03 19:43 | 1376 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 4128 | keep | 0 | Jul | 2021 | 0.0028116 | 0.00093719 | Momentary | FALSE | TRUE | TMED_Event | 1376
FAJARDO | 2021-07-03 19:40 | 2021-07-03 19:43 | 293 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 879 | keep | 0 | Jul | 2021 | 0.00059868 | 0.00019956 | Momentary | FALSE | TRUE | TMED_Event | 293
FAJARDO | 2021-07-03 19:40 | 2021-07-03 19:43 | 1215 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 3645 | keep | 0 | Jul | 2021 | 0.0024826 | 0.00082753 | Momentary | FALSE | TRUE | TMED_Event | 1215
MAYAGÃœEZ | 2021-07-03 19:43 | 2021-07-04 14:30 | 200 | 018:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | M21070300634 | New_Event | Bad Weather | Include | Include | Weather | 1127 | 2021-07-03 | 225400 | keep | 0 | Jul | 2021 | 0.15352 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
HUMACAO | 2021-07-03 19:49 | 2021-07-04 11:05 | 170 | 015:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 25 Y 1 X 15 EN CORTE DE LINEA Y TRANSFORMADOR CRUCE CON CABLE TELEFONICO | C21070300205 | New_Event | Wire Down | Include | Include | Equipment | 916 | 2021-07-03 | 155720 | keep | 0 | Jul | 2021 | 0.10606 | 0.00011579 | Sustained | FALSE | TRUE | TMED_Event | 170
SAN JUAN | 2021-07-03 20:15 | 2021-07-03 20:27 | 1862 | 000:12 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-07-03 | 22344 | keep | 0 | Jul | 2021 | 0.015218 | 0.0012682 | Sustained | FALSE | TRUE | TMED_Event | 1862
SAN JUAN | 2021-07-03 20:15 | 2021-07-03 20:27 | 1613 | 000:12 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-07-03 | 19356 | keep | 0 | Jul | 2021 | 0.013183 | 0.0010986 | Sustained | FALSE | TRUE | TMED_Event | 1613
SAN JUAN | 2021-07-03 20:15 | 2021-07-03 20:27 | 1448 | 000:12 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-07-03 | 17376 | keep | 0 | Jul | 2021 | 0.011835 | 0.00098623 | Sustained | FALSE | TRUE | TMED_Event | 1448
FAJARDO | 2021-07-03 20:15 | 2021-07-03 20:28 | 1902 | 000:13 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 13 | 2021-07-03 | 24726 | keep | 0 | Jul | 2021 | 0.016841 | 0.0012954 | Sustained | FALSE | TRUE | TMED_Event | 1902
FAJARDO | 2021-07-03 20:15 | 2021-07-03 20:28 | 970 | 000:13 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 13 | 2021-07-03 | 12610 | keep | 0 | Jul | 2021 | 0.0085886 | 0.00066066 | Sustained | FALSE | TRUE | TMED_Event | 970
FAJARDO | 2021-07-03 20:15 | 2021-07-03 20:28 | 3003 | 000:13 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 13 | 2021-07-03 | 39039 | keep | 0 | Jul | 2021 | 0.026589 | 0.0020453 | Sustained | FALSE | TRUE | TMED_Event | 3003
FAJARDO | 2021-07-03 20:15 | 2021-07-03 20:21 | 1394 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-07-03 | 8364 | keep | 0 | Jul | 2021 | 0.0056967 | 0.00094945 | Sustained | FALSE | TRUE | TMED_Event | 1394
FAJARDO | 2021-07-03 20:15 | 2021-07-03 20:21 | 412 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-07-03 | 2472 | keep | 0 | Jul | 2021 | 0.0016837 | 0.00028061 | Sustained | FALSE | TRUE | TMED_Event | 412
FAJARDO | 2021-07-03 20:15 | 2021-07-03 20:21 | 424 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-07-03 | 2544 | keep | 0 | Jul | 2021 | 0.0017327 | 0.00028878 | Sustained | FALSE | TRUE | TMED_Event | 424
FAJARDO | 2021-07-03 20:15 | 2021-07-03 20:21 | 240 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-07-03 | 1440 | keep | 0 | Jul | 2021 | 0.00098078 | 0.00016346 | Sustained | FALSE | TRUE | TMED_Event | 240
FAJARDO | 2021-07-03 20:15 | 2021-07-03 20:21 | 2722 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-07-03 | 16332 | keep | 0 | Jul | 2021 | 0.011124 | 0.0018539 | Sustained | FALSE | TRUE | TMED_Event | 2722
FAJARDO | 2021-07-03 20:15 | 2021-07-03 20:21 | 1234 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-07-03 | 7404 | keep | 0 | Jul | 2021 | 0.0050428 | 0.00084047 | Sustained | FALSE | TRUE | TMED_Event | 1234
FAJARDO | 2021-07-03 20:15 | 2021-07-03 20:21 | 76 | 000:06 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-07-03 | 456 | keep | 0 | Jul | 2021 | 0.00031058 | 5.1763e-05 | Sustained | FALSE | TRUE | TMED_Event | 76
FAJARDO | 2021-07-03 20:15 | 2021-07-03 20:18 | 2286 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 6858 | keep | 0 | Jul | 2021 | 0.004671 | 0.001557 | Momentary | FALSE | TRUE | TMED_Event | 2286
FAJARDO | 2021-07-03 20:15 | 2021-07-03 20:18 | 693 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 2079 | keep | 0 | Jul | 2021 | 0.001416 | 0.000472 | Momentary | FALSE | TRUE | TMED_Event | 693
FAJARDO | 2021-07-03 20:15 | 2021-07-03 20:18 | 4098 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 12294 | keep | 0 | Jul | 2021 | 0.0083734 | 0.0027911 | Momentary | FALSE | TRUE | TMED_Event | 4098
FAJARDO | 2021-07-03 20:15 | 2021-07-03 20:18 | 956 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 2868 | keep | 0 | Jul | 2021 | 0.0019534 | 0.00065113 | Momentary | FALSE | TRUE | TMED_Event | 956
FAJARDO | 2021-07-03 20:15 | 2021-07-03 20:28 | 2343 | 000:13 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 13 | 2021-07-03 | 30459 | keep | 0 | Jul | 2021 | 0.020745 | 0.0015958 | Sustained | FALSE | TRUE | TMED_Event | 2343
FAJARDO | 2021-07-03 20:15 | 2021-07-03 20:28 | 1830 | 000:13 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 13 | 2021-07-03 | 23790 | keep | 0 | Jul | 2021 | 0.016203 | 0.0012464 | Sustained | FALSE | TRUE | TMED_Event | 1830
FAJARDO | 2021-07-03 20:15 | 2021-07-03 20:28 | 710 | 000:13 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 13 | 2021-07-03 | 9230 | keep | 0 | Jul | 2021 | 0.0062865 | 0.00048358 | Sustained | FALSE | TRUE | TMED_Event | 710
FAJARDO | 2021-07-03 20:15 | 2021-07-03 20:28 | 969 | 000:13 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 13 | 2021-07-03 | 12597 | keep | 0 | Jul | 2021 | 0.0085798 | 0.00065998 | Sustained | FALSE | TRUE | TMED_Event | 969
CANOVANAS | 2021-07-03 20:15 | 2021-07-03 20:29 | 2708 | 000:14 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 14 | 2021-07-03 | 37912 | keep | 0 | Jul | 2021 | 0.025822 | 0.0018444 | Sustained | FALSE | TRUE | TMED_Event | 2708
CANOVANAS | 2021-07-03 20:15 | 2021-07-03 20:29 | 2524 | 000:14 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 14 | 2021-07-03 | 35336 | keep | 0 | Jul | 2021 | 0.024067 | 0.0017191 | Sustained | FALSE | TRUE | TMED_Event | 2524
CANOVANAS | 2021-07-03 20:15 | 2021-07-03 20:29 | 1648 | 000:14 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 14 | 2021-07-03 | 23072 | keep | 0 | Jul | 2021 | 0.015714 | 0.0011224 | Sustained | FALSE | TRUE | TMED_Event | 1648
CANOVANAS | 2021-07-03 20:15 | 2021-07-03 20:27 | 539 | 000:12 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-07-03 | 6468 | keep | 0 | Jul | 2021 | 0.0044053 | 0.00036711 | Sustained | FALSE | TRUE | TMED_Event | 539
CANOVANAS | 2021-07-03 20:15 | 2021-07-03 20:27 | 3012 | 000:12 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-07-03 | 36144 | keep | 0 | Jul | 2021 | 0.024618 | 0.0020515 | Sustained | FALSE | TRUE | TMED_Event | 3012
CANOVANAS | 2021-07-03 20:15 | 2021-07-03 20:27 | 2106 | 000:12 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-07-03 | 25272 | keep | 0 | Jul | 2021 | 0.017213 | 0.0014344 | Sustained | FALSE | TRUE | TMED_Event | 2106
CANOVANAS | 2021-07-03 20:15 | 2021-07-03 20:27 | 635 | 000:12 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-07-03 | 7620 | keep | 0 | Jul | 2021 | 0.0051899 | 0.0004325 | Sustained | FALSE | TRUE | TMED_Event | 635
CANOVANAS | 2021-07-03 20:15 | 2021-07-03 20:29 | 2039 | 000:14 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 14 | 2021-07-03 | 28546 | keep | 0 | Jul | 2021 | 0.019443 | 0.0013888 | Sustained | FALSE | TRUE | TMED_Event | 2039
CANOVANAS | 2021-07-03 20:15 | 2021-07-03 20:29 | 4188 | 000:14 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 14 | 2021-07-03 | 58632 | keep | 0 | Jul | 2021 | 0.039934 | 0.0028524 | Sustained | FALSE | TRUE | TMED_Event | 4188
CANOVANAS | 2021-07-03 20:15 | 2021-07-03 20:29 | 4085 | 000:14 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 14 | 2021-07-03 | 57190 | keep | 0 | Jul | 2021 | 0.038952 | 0.0027823 | Sustained | FALSE | TRUE | TMED_Event | 4085
CANOVANAS | 2021-07-03 20:15 | 2021-07-03 20:29 | 3464 | 000:14 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 14 | 2021-07-03 | 48496 | keep | 0 | Jul | 2021 | 0.03303 | 0.0023593 | Sustained | FALSE | TRUE | TMED_Event | 3464
CANOVANAS | 2021-07-03 20:15 | 2021-07-03 20:29 | 7621 | 000:14 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 14 | 2021-07-03 | 106694 | keep | 0 | Jul | 2021 | 0.072669 | 0.0051906 | Sustained | FALSE | TRUE | TMED_Event | 7621
CANOVANAS | 2021-07-03 20:15 | 2021-07-03 20:29 | 3699 | 000:14 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 14 | 2021-07-03 | 51786 | keep | 0 | Jul | 2021 | 0.035271 | 0.0025194 | Sustained | FALSE | TRUE | TMED_Event | 3699
CANOVANAS | 2021-07-03 20:15 | 2021-07-03 20:29 | 2675 | 000:14 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 14 | 2021-07-03 | 37450 | keep | 0 | Jul | 2021 | 0.025507 | 0.0018219 | Sustained | FALSE | TRUE | TMED_Event | 2675
FAJARDO | 2021-07-03 20:15 | 2021-07-03 20:18 | 1839 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 5517 | keep | 0 | Jul | 2021 | 0.0037576 | 0.0012525 | Momentary | FALSE | TRUE | TMED_Event | 1839
FAJARDO | 2021-07-03 20:15 | 2021-07-03 20:18 | 1778 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 5334 | keep | 0 | Jul | 2021 | 0.003633 | 0.001211 | Momentary | FALSE | TRUE | TMED_Event | 1778
FAJARDO | 2021-07-03 20:15 | 2021-07-03 20:18 | 1376 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 4128 | keep | 0 | Jul | 2021 | 0.0028116 | 0.00093719 | Momentary | FALSE | TRUE | TMED_Event | 1376
FAJARDO | 2021-07-03 20:15 | 2021-07-03 20:18 | 293 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 879 | keep | 0 | Jul | 2021 | 0.00059868 | 0.00019956 | Momentary | FALSE | TRUE | TMED_Event | 293
FAJARDO | 2021-07-03 20:15 | 2021-07-03 20:18 | 1215 | 000:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 3645 | keep | 0 | Jul | 2021 | 0.0024826 | 0.00082753 | Momentary | FALSE | TRUE | TMED_Event | 1215
ARECIBO | 2021-07-03 20:22 | 2021-07-06 16:40 | 100 | 068:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE REALIZO DESGANCHE | A21063000144 | New_Event | Wire Down | Include | Include | Equipment | 4098 | 2021-07-03 | 409800 | keep | 0 | Jul | 2021 | 0.27911 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
MAYAGÃœEZ | 2021-07-03 20:28 | 2021-07-03 20:29 | 863 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR MAL TIEMPO | M21070300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-03 | 863 | keep | 0 | Jul | 2021 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | TMED_Event | 863
ARECIBO | 2021-07-03 20:30 | 2021-07-04 17:30 | 80 | 021:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO | A21070300126 | New_Event | Wire Down | Include | Include | Equipment | 1260 | 2021-07-03 | 100800 | keep | 0 | Jul | 2021 | 0.068654 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
YAUCO | 2021-07-03 20:40 | 2021-07-04 18:23 | 160 | 021:43 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA POR MAL TIEMPO | P21070300039 | New_Event | Bad Weather | Include | Include | Weather | 1303 | 2021-07-03 | 208480 | keep | 0 | Jul | 2021 | 0.14199 | 0.00010898 | Sustained | FALSE | TRUE | TMED_Event | 160
SAN JUAN | 2021-07-03 20:50 | 2021-07-04 12:35 | 80 | 015:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA CERRAR PUENTE PRIMARIO TRAS PATIO | S21070300053 | Partial_restoration | Wire Down | Include | Include | Equipment | 945 | 2021-07-03 | 75600 | keep | 0 | Jul | 2021 | 0.051491 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
CANOVANAS | 2021-07-03 20:56 | 2021-07-03 21:01 | 2039 | 000:05 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-07-03 | 10195 | keep | 0 | Jul | 2021 | 0.0069438 | 0 | Momentary | FALSE | TRUE | TMED_Event | 0
CANOVANAS | 2021-07-03 20:56 | 2021-07-03 21:01 | 4188 | 000:05 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-07-03 | 20940 | keep | 0 | Jul | 2021 | 0.014262 | 0 | Momentary | FALSE | TRUE | TMED_Event | 0
CANOVANAS | 2021-07-03 20:56 | 2021-07-03 21:01 | 4085 | 000:05 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-07-03 | 20425 | keep | 0 | Jul | 2021 | 0.013911 | 0 | Momentary | FALSE | TRUE | TMED_Event | 0
CANOVANAS | 2021-07-03 20:56 | 2021-07-03 21:03 | 3464 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-07-03 | 24248 | keep | 0 | Jul | 2021 | 0.016515 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
CANOVANAS | 2021-07-03 20:56 | 2021-07-03 21:03 | 7621 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-07-03 | 53347 | keep | 0 | Jul | 2021 | 0.036334 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
CANOVANAS | 2021-07-03 20:56 | 2021-07-03 21:03 | 3699 | 000:07 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-07-03 | 25893 | keep | 0 | Jul | 2021 | 0.017636 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
CANOVANAS | 2021-07-03 20:56 | 2021-07-03 20:58 | 2675 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36800 | R21070300000 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-03 | 5350 | keep | 0 | Jul | 2021 | 0.0036439 | 0 | Momentary | FALSE | TRUE | TMED_Event | 0
SAN JUAN | 2021-07-03 20:59 | 2021-07-03 21:14 | 1271 | 000:15 | T | DESGANCHE | SE ABRIO EL ALIMENTADOR POR ARBOL SOBRE LA LINEA | R21070300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 15 | 2021-07-03 | 19065 | keep | 0 | Jul | 2021 | 0.012985 | 0.00086567 | Sustained | FALSE | TRUE | TMED_Event | 1271
ARECIBO | 2021-07-03 21:00 | 2021-07-04 15:30 | 80 | 018:30 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A21070300172 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1110 | 2021-07-03 | 88800 | keep | 0 | Jul | 2021 | 0.060481 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
ARECIBO | 2021-07-03 21:05 | 2021-07-05 12:25 | 9 | 039:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA Y SE REPARO PUENTES PRIMARIOS | A21070300399 | New_Event | Wire Down | Include | Include | Equipment | 2360 | 2021-07-03 | 21240 | keep | 0 | Jul | 2021 | 0.014466 | 6.1299e-06 | Sustained | FALSE | TRUE | TMED_Event | 9
MAYAGÃœEZ | 2021-07-03 21:37 | 2021-07-03 21:38 | 108 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR MAL TIEMPO | M21070300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-03 | 108 | keep | 0 | Jul | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | TMED_Event | 108
ARECIBO | 2021-07-03 21:37 | 2021-07-04 16:35 | 6 | 018:58 | P | DESGANCHE | 1 X 8 EN TRANSFORMADOR SE RETIRO ENREDADERA | A21070300403 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1138 | 2021-07-03 | 6828 | keep | 0 | Jul | 2021 | 0.0046505 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
FAJARDO | 2021-07-03 21:47 | 2021-07-03 21:49 | 1571 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-03 | 3142 | keep | 0 | Jul | 2021 | 0.00214 | 0.00107 | Momentary | FALSE | TRUE | TMED_Event | 1571
FAJARDO | 2021-07-03 21:47 | 2021-07-03 21:49 | 2041 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-03 | 4082 | keep | 0 | Jul | 2021 | 0.0027802 | 0.0013901 | Momentary | FALSE | TRUE | TMED_Event | 2041
FAJARDO | 2021-07-03 21:47 | 2021-07-03 21:49 | 625 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-03 | 1250 | keep | 0 | Jul | 2021 | 0.00085137 | 0.00042568 | Momentary | FALSE | TRUE | TMED_Event | 625
FAJARDO | 2021-07-03 21:47 | 2021-07-03 21:49 | 1463 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-03 | 2926 | keep | 0 | Jul | 2021 | 0.0019929 | 0.00099644 | Momentary | FALSE | TRUE | TMED_Event | 1463
FAJARDO | 2021-07-03 21:47 | 2021-07-03 21:51 | 1902 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-03 | 7608 | keep | 0 | Jul | 2021 | 0.0051818 | 0.0012954 | Momentary | FALSE | TRUE | TMED_Event | 1902
FAJARDO | 2021-07-03 21:47 | 2021-07-03 21:51 | 970 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-03 | 3880 | keep | 0 | Jul | 2021 | 0.0026427 | 0.00066066 | Momentary | FALSE | TRUE | TMED_Event | 970
FAJARDO | 2021-07-03 21:47 | 2021-07-03 21:51 | 3003 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-03 | 12012 | keep | 0 | Jul | 2021 | 0.0081813 | 0.0020453 | Momentary | FALSE | TRUE | TMED_Event | 3003
FAJARDO | 2021-07-03 21:47 | 2021-07-03 21:48 | 1394 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 1394 | keep | 0 | Jul | 2021 | 0.00094945 | 0.00094945 | Momentary | FALSE | TRUE | TMED_Event | 1394
FAJARDO | 2021-07-03 21:47 | 2021-07-03 21:48 | 412 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 412 | keep | 0 | Jul | 2021 | 0.00028061 | 0.00028061 | Momentary | FALSE | TRUE | TMED_Event | 412
FAJARDO | 2021-07-03 21:47 | 2021-07-03 21:51 | 2343 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-03 | 9372 | keep | 0 | Jul | 2021 | 0.0063832 | 0.0015958 | Momentary | FALSE | TRUE | TMED_Event | 2343
FAJARDO | 2021-07-03 21:47 | 2021-07-03 21:51 | 1830 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-03 | 7320 | keep | 0 | Jul | 2021 | 0.0049856 | 0.0012464 | Momentary | FALSE | TRUE | TMED_Event | 1830
FAJARDO | 2021-07-03 21:47 | 2021-07-03 21:51 | 710 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-03 | 2840 | keep | 0 | Jul | 2021 | 0.0019343 | 0.00048358 | Momentary | FALSE | TRUE | TMED_Event | 710
FAJARDO | 2021-07-03 21:47 | 2021-07-03 21:51 | 969 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-03 | 3876 | keep | 0 | Jul | 2021 | 0.0026399 | 0.00065998 | Momentary | FALSE | TRUE | TMED_Event | 969
CANOVANAS | 2021-07-03 21:47 | 2021-07-03 21:48 | 1894 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 1894 | keep | 0 | Jul | 2021 | 0.00129 | 0.00129 | Momentary | FALSE | TRUE | TMED_Event | 1894
CANOVANAS | 2021-07-03 21:47 | 2021-07-03 21:48 | 4154 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 4154 | keep | 0 | Jul | 2021 | 0.0028293 | 0.0028293 | Momentary | FALSE | TRUE | TMED_Event | 4154
CANOVANAS | 2021-07-03 21:47 | 2021-07-03 21:48 | 424 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-03 | 424 | keep | 0 | Jul | 2021 | 0.00028878 | 0.00028878 | Momentary | FALSE | TRUE | TMED_Event | 424
CANOVANAS | 2021-07-03 21:47 | 2021-07-03 21:50 | 3838 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 11514 | keep | 0 | Jul | 2021 | 0.0078421 | 0.002614 | Momentary | FALSE | TRUE | TMED_Event | 3838
CANOVANAS | 2021-07-03 21:47 | 2021-07-03 21:50 | 817 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 2451 | keep | 0 | Jul | 2021 | 0.0016694 | 0.00055645 | Momentary | FALSE | TRUE | TMED_Event | 817
CANOVANAS | 2021-07-03 21:47 | 2021-07-03 21:50 | 1124 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R21070300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 3372 | keep | 0 | Jul | 2021 | 0.0022967 | 0.00076555 | Momentary | FALSE | TRUE | TMED_Event | 1124
HUMACAO | 2021-07-03 22:16 | 2021-07-03 22:17 | 109 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE INTELLIRUPTER 2603-7A | C21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 109 | keep | 0 | Jul | 2021 | 7.4239e-05 | 7.4239e-05 | Momentary | FALSE | FALSE | TMED_Event | 109
ARECIBO | 2021-07-03 22:22 | 2021-07-04 17:05 | 60 | 018:43 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21070300415 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1123 | 2021-07-03 | 67380 | keep | 0 | Jul | 2021 | 0.045892 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
BAYAMON | 2021-07-03 22:23 | 2021-07-03 22:30 | 150 | 000:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIERON MACHETES DETRAS DE CRUZ ROJA, SE ABRIO PUENTE POCO MAS ADELANTE DE UNA FASE POR CABLE EN EL SUELO Y SE CERRO MACHETES N/O CONTRA EL 1531-02 | S21070300000 | Partial_restoration | Wire Down | Include | Include | Equipment | 7 | 2021-07-03 | 1050 | keep | 0 | Jul | 2021 | 0.00071515 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
CAGUAS | 2021-07-03 22:31 | 2021-07-04 15:35 | 90 | 017:04 | P | DESGANCHE | 1 X 50 Y 1 X 30 EN CORTES DE LINEA | C21070300227 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1024 | 2021-07-03 | 92160 | keep | 0 | Jul | 2021 | 0.06277 | 6.1299e-05 | Sustained | FALSE | TRUE | TMED_Event | 90
ARECIBO | 2021-07-03 22:50 | 2021-07-04 12:03 | 50 | 013:13 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | A21070300419 | New_Event | Vegetation Contact | Include | Include | Vegetation | 793 | 2021-07-03 | 39650 | keep | 0 | Jul | 2021 | 0.027005 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
FAJARDO | 2021-07-03 23:00 | 2021-07-03 23:04 | 1902 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARARON LINEA 3100 PARA SECCIONALIZAR PUENTE ABIERTO EN ACB 3157A | R21070300202 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-03 | 7608 | keep | 0 | Jul | 2021 | 0.0051818 | 0.0012954 | Momentary | FALSE | TRUE | TMED_Event | 1902
FAJARDO | 2021-07-03 23:00 | 2021-07-03 23:04 | 970 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARARON LINEA 3100 PARA SECCIONALIZAR PUENTE ABIERTO EN ACB 3157A | R21070300202 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-03 | 3880 | keep | 0 | Jul | 2021 | 0.0026427 | 0.00066066 | Momentary | FALSE | TRUE | TMED_Event | 970
FAJARDO | 2021-07-03 23:00 | 2021-07-03 23:04 | 3003 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARARON LINEA 3100 PARA SECCIONALIZAR PUENTE ABIERTO EN ACB 3157A | R21070300202 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-03 | 12012 | keep | 0 | Jul | 2021 | 0.0081813 | 0.0020453 | Momentary | FALSE | TRUE | TMED_Event | 3003
FAJARDO | 2021-07-03 23:00 | 2021-07-03 23:03 | 2343 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARARON LINEA 3100 PARA SECCIONALIZAR PUENTE ABIERTO EN ACB 3157A | R21070300201 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 7029 | keep | 0 | Jul | 2021 | 0.0047874 | 0.0015958 | Momentary | FALSE | TRUE | TMED_Event | 2343
FAJARDO | 2021-07-03 23:00 | 2021-07-03 23:03 | 1830 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARARON LINEA 3100 PARA SECCIONALIZAR PUENTE ABIERTO EN ACB 3157A | R21070300201 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 5490 | keep | 0 | Jul | 2021 | 0.0037392 | 0.0012464 | Momentary | FALSE | TRUE | TMED_Event | 1830
FAJARDO | 2021-07-03 23:00 | 2021-07-03 23:03 | 710 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARARON LINEA 3100 PARA SECCIONALIZAR PUENTE ABIERTO EN ACB 3157A | R21070300201 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 2130 | keep | 0 | Jul | 2021 | 0.0014507 | 0.00048358 | Momentary | FALSE | TRUE | TMED_Event | 710
FAJARDO | 2021-07-03 23:00 | 2021-07-03 23:03 | 969 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARARON LINEA 3100 PARA SECCIONALIZAR PUENTE ABIERTO EN ACB 3157A | R21070300201 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-03 | 2907 | keep | 0 | Jul | 2021 | 0.0019799 | 0.00065998 | Momentary | FALSE | TRUE | TMED_Event | 969
CAGUAS | 2021-07-03 23:17 | 2021-07-03 23:18 | 2900 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO RR/OFF | C21070300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-03 | 2900 | keep | 0 | Jul | 2021 | 0.0019752 | 0.0019752 | Momentary | FALSE | FALSE | TMED_Event | 2900
ARECIBO | 2021-07-03 23:21 | 2021-07-04 10:40 | 60 | 011:19 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | A21070300429 | New_Event | Vegetation Contact | Include | Include | Vegetation | 679 | 2021-07-03 | 40740 | keep | 0 | Jul | 2021 | 0.027748 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
SAN JUAN | 2021-07-03 23:24 | 2021-07-06 09:59 | 12 | 058:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO TRAMO SECUNDARIO Y VARIAS TOMAS | S21070300196 | New_Event | Secondary Wire Down | Include | Include | Equipment | 3515 | 2021-07-03 | 42180 | keep | 0 | Jul | 2021 | 0.028729 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
ARECIBO | 2021-07-04 00:05 | 2021-07-04 14:45 | 50 | 014:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A21070400001 | New_Event | Wire Down | Include | Include | Equipment | 880 | 2021-07-04 | 44000 | keep | 0 | Jul | 2021 | 0.029968 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-04 00:14 | 2021-07-04 10:00 | 100 | 009:46 | P | DESGANCHE | 1 X 50 Y 1 X 30 EN CORTES DE LINEA | C21070400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 586 | 2021-07-04 | 58600 | keep | 0 | Jul | 2021 | 0.039912 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-07-04 00:37 | 2021-07-04 16:28 | 90 | 015:51 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZARON DISCOS ROTOS | C21070400003 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 951 | 2021-07-04 | 85590 | keep | 0 | Jul | 2021 | 0.058295 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
CANOVANAS | 2021-07-04 01:35 | 2021-07-04 14:49 | 19 | 013:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | R21070400003 | New_Event | Cutout Failure | Include | Include | Equipment | 794 | 2021-07-04 | 15086 | keep | 0 | Jul | 2021 | 0.010275 | 1.2941e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 19
CAGUAS | 2021-07-04 01:47 | 2021-07-04 01:48 | 1702 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C21070400000 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2021-07-04 | 1702 | keep | 0 | Jul | 2021 | 0.0011592 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-07-04 01:48 | 2021-07-04 01:52 | 10 | 000:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO HACIA CAJA | C21070300197 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 4 | 2021-07-04 | 40 | keep | 0 | Jul | 2021 | 2.7244e-05 | 6.811e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-07-04 01:49 | 2021-07-04 01:50 | 638 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE LLUVIA | C21070400000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-04 | 638 | keep | 0 | Jul | 2021 | 0.00043454 | 0.00043454 | Momentary | FALSE | FALSE | Not_TMED_Event | 638
CAGUAS | 2021-07-04 01:50 | 2021-07-04 11:26 | 100 | 009:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIAS | C21070400018 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 576 | 2021-07-04 | 57600 | keep | 0 | Jul | 2021 | 0.039231 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-07-04 01:52 | 2021-07-04 01:53 | 1702 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C21070400000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-07-04 | 1702 | keep | 0 | Jul | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2021-07-04 01:53 | 2021-07-04 16:06 | 10 | 014:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO HACIA CAJA | C21070300197 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 853 | 2021-07-04 | 8530 | keep | 0 | Jul | 2021 | 0.0058097 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-04 02:13 | 2021-07-04 02:14 | 3070 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO | B21070400000 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2021-07-04 | 3070 | keep | 0 | Jul | 2021 | 0.002091 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-04 02:14 | 2021-07-04 10:43 | 20 | 008:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA Y SE REALIZO DESGANCHE | B21070300161 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 509 | 2021-07-04 | 10180 | keep | 0 | Jul | 2021 | 0.0069336 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-07-04 02:14 | 2021-07-04 10:37 | 30 | 008:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA | B21070300123 | New_Event | Cutout Failure | Include | Include | Equipment | 503 | 2021-07-04 | 15090 | keep | 0 | Jul | 2021 | 0.010278 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-07-04 02:30 | 2021-07-04 15:00 | 60 | 012:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 1 X 50 EN CORTE DE LINEA RAYOS | B21070400004 | New_Event | Bad Weather | Include | Include | Weather | 750 | 2021-07-04 | 45000 | keep | 0 | Jul | 2021 | 0.030649 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-07-04 02:47 | 2021-07-05 12:50 | 80 | 034:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21070400014 | New_Event | Bad Weather | Include | Include | Weather | 2043 | 2021-07-04 | 163440 | keep | 0 | Jul | 2021 | 0.11132 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-07-04 02:48 | 2021-07-04 16:05 | 80 | 013:17 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A21070400009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 797 | 2021-07-04 | 63760 | keep | 0 | Jul | 2021 | 0.043427 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-07-04 02:49 | 2021-07-05 09:08 | 88 | 030:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA. SE FIJO BAJANTE PRIMARIA A CAJA EN CORTE DE LINEA | P21070400005 | New_Event | Wire Down | Include | Include | Equipment | 1819 | 2021-07-04 | 160072 | keep | 0 | Jul | 2021 | 0.10902 | 5.9936e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 88
MAYAGÃœEZ | 2021-07-04 02:53 | 2021-07-05 08:59 | 80 | 030:06 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21070400016 | New_Event | Bad Weather | Include | Include | Weather | 1806 | 2021-07-04 | 144480 | keep | 0 | Jul | 2021 | 0.098405 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-07-04 04:52 | 2021-07-04 10:26 | 55 | 005:34 | P | DESGANCHE | 1 X 50 EN CONVERTIDOR | P21070400006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 334 | 2021-07-04 | 18370 | keep | 0 | Jul | 2021 | 0.012512 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
HUMACAO | 2021-07-04 05:05 | 2021-07-04 13:58 | 70 | 008:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE DESCRUZARON CONDUCTORES | C21070400022 | New_Event | Wire Down | Include | Include | Equipment | 533 | 2021-07-04 | 37310 | keep | 0 | Jul | 2021 | 0.025412 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
CAGUAS | 2021-07-04 05:17 | 2021-07-04 16:12 | 100 | 010:55 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21070400023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 655 | 2021-07-04 | 65500 | keep | 0 | Jul | 2021 | 0.044612 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-07-04 05:31 | 2021-07-04 12:04 | 100 | 006:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN RISER CRUCE CON REPTIL | C21070400024 | New_Event |  |  | Include | Wildlife | 393 | 2021-07-04 | 39300 | keep | 0 | Jul | 2021 | 0.026767 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-07-04 05:31 | 2021-07-04 12:04 | 23 | 006:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN RISER CRUCE CON REPTIL | C21070400024 | New_Event |  |  | Include | Wildlife | 393 | 2021-07-04 | 9039 | keep | 0 | Jul | 2021 | 0.0061564 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BAYAMON | 2021-07-04 06:00 | 2021-07-04 09:07 | 40 | 003:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S21070400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2021-07-04 | 7480 | keep | 0 | Jul | 2021 | 0.0050946 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
YAUCO | 2021-07-04 06:00 | 2021-07-04 10:57 | 50 | 004:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | P210704000XX | New_Event | Vegetation Contact | Include | Include | Vegetation | 297 | 2021-07-04 | 14850 | keep | 0 | Jul | 2021 | 0.010114 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-04 06:00 | 2021-07-04 09:34 | 411 | 003:34 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR RTU FUERA DE SERVICIO SE CERRO MANUAL ELECTRICO | M21070400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 214 | 2021-07-04 | 87954 | keep | 0 | Jul | 2021 | 0.059905 | 0.00027993 | Sustained | FALSE | FALSE | Not_TMED_Event | 411
ARECIBO | 2021-07-04 06:10 | 2021-07-04 16:10 | 70 | 010:00 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | A21070400017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 600 | 2021-07-04 | 42000 | keep | 0 | Jul | 2021 | 0.028606 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-07-04 06:19 | 2021-07-05 15:50 | 80 | 033:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21070400025 | New_Event | Bad Weather | Include | Include | Weather | 2011 | 2021-07-04 | 160880 | keep | 0 | Jul | 2021 | 0.10957 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
GUAYAMA | 2021-07-04 06:20 | 2021-07-04 10:24 | 65 | 004:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE DESPEGO PUENTE PRIMARIO DE POSTE | P21070400008 | New_Event | Wire Down | Include | Include | Equipment | 244 | 2021-07-04 | 15860 | keep | 0 | Jul | 2021 | 0.010802 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
ARECIBO | 2021-07-04 06:29 | 2021-07-04 18:00 | 300 | 011:31 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A21070400020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 691 | 2021-07-04 | 207300 | keep | 0 | Jul | 2021 | 0.14119 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
YAUCO | 2021-07-04 06:31 | 2021-07-04 06:32 | 3973 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21070400029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-04 | 3973 | keep | 0 | Jul | 2021 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
CAGUAS | 2021-07-04 06:35 | 2021-07-04 13:32 | 80 | 006:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIAS | C21070400028 | New_Event | Bad Weather | Include | Include | Weather | 417 | 2021-07-04 | 33360 | keep | 0 | Jul | 2021 | 0.022721 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
YAUCO | 2021-07-04 06:41 | 2021-07-04 06:42 | 2484 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21070400029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-04 | 2484 | keep | 0 | Jul | 2021 | 0.0016918 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
MAYAGÃœEZ | 2021-07-04 06:42 | 2021-07-07 19:30 | 100 | 084:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | M21070400044 | New_Event | Wire Down | Include | Include | Equipment | 5088 | 2021-07-04 | 508800 | keep | 0 | Jul | 2021 | 0.34654 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-04 06:43 | 2021-07-04 12:21 | 80 | 005:38 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | S21070400023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 338 | 2021-07-04 | 27040 | keep | 0 | Jul | 2021 | 0.018417 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-07-04 06:48 | 2021-07-04 11:30 | 200 | 004:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21070300105 | New_Event | Bad Weather | Include | Include | Weather | 282 | 2021-07-04 | 56400 | keep | 0 | Jul | 2021 | 0.038414 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CANOVANAS | 2021-07-04 06:52 | 2021-07-05 12:46 | 50 | 029:54 | P | DESGANCHE | 1 X 10 Y 1 X 20 EN TRANSFORMADORES | R21070400020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1794 | 2021-07-04 | 89700 | keep | 0 | Jul | 2021 | 0.061094 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-07-04 07:08 | 2021-07-04 07:09 | 5668 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO SE CERRO POR CONTROL | R21070400000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-04 | 5668 | keep | 0 | Jul | 2021 | 0.0038604 | 0.0038604 | Momentary | FALSE | FALSE | Not_TMED_Event | 5668
SAN JUAN | 2021-07-04 07:09 | 2021-07-04 15:30 | 30 | 008:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO RISER ZAFADO DE CAJAS | R21070400030 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 501 | 2021-07-04 | 15030 | keep | 0 | Jul | 2021 | 0.010237 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-07-04 07:17 | 2021-07-05 13:10 | 40 | 029:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21070400062 | New_Event | Bad Weather | Include | Include | Weather | 1793 | 2021-07-04 | 71720 | keep | 0 | Jul | 2021 | 0.048848 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-07-04 07:27 | 2021-07-04 17:56 | 115 | 010:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | P21070400032 | New_Event | Bad Weather | Include | Include | Weather | 629 | 2021-07-04 | 72335 | keep | 0 | Jul | 2021 | 0.049267 | 7.8326e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 115
CAGUAS | 2021-07-04 07:30 | 2021-07-04 11:54 | 100 | 004:24 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21070400042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 264 | 2021-07-04 | 26400 | keep | 0 | Jul | 2021 | 0.017981 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-07-04 07:35 | 2021-07-05 16:00 | 50 | 032:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO | M21070400065 | New_Event | Wire Down | Include | Include | Equipment | 1945 | 2021-07-04 | 97250 | keep | 0 | Jul | 2021 | 0.066237 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-07-04 07:43 | 2021-07-04 09:18 | 100 | 001:35 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21070400024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2021-07-04 | 9500 | keep | 0 | Jul | 2021 | 0.0064704 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-07-04 07:43 | 2021-07-04 14:04 | 1 | 006:21 | P | PARARRAYOS DEFECTUOSO | 1 X 25 EN BANCO DE TRANSFORMADORES SE REEMPLAZO PARARRAYOS | C21070400045 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 381 | 2021-07-04 | 381 | keep | 0 | Jul | 2021 | 0.0002595 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-07-04 07:56 | 2021-07-05 09:00 | 25 | 025:04 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21070400079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1504 | 2021-07-04 | 37600 | keep | 0 | Jul | 2021 | 0.025609 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-07-04 07:59 | 2021-07-04 08:02 | 36 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON RECIERRE EN OFF SE PROBO POR CONTROL QUEDO EN SERVICIO CARGA POR EL 1620-04 | S21070400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-07-04 | 108 | keep | 0 | Jul | 2021 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-07-04 07:59 | 2021-07-04 08:02 | 172 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON RECIERRE EN OFF SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA CARGA 1620-01 SE VERIFICO CON COD CAGUAS | S21070400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-07-04 | 516 | keep | 0 | Jul | 2021 | 0.00035145 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
MAYAGÃœEZ | 2021-07-04 08:19 | 2021-07-04 13:15 | 55 | 004:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE SECCIONALIZO LINEA PRIMARIA | M21070400074 | New_Event | Wire Down | Include | Include | Equipment | 296 | 2021-07-04 | 16280 | keep | 0 | Jul | 2021 | 0.011088 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
CANOVANAS | 2021-07-04 08:21 | 2021-07-04 17:55 | 100 | 009:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 Y 1 X 80 EN CORTE DE LINEA Y TRANSFORMADOR LLUVIAS | R21070400027 | New_Event | Bad Weather | Include | Include | Weather | 574 | 2021-07-04 | 57400 | keep | 0 | Jul | 2021 | 0.039095 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
GUAYAMA | 2021-07-04 08:23 | 2021-07-04 12:30 | 65 | 004:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | P21070400034 | New_Event |  |  | Include | Wildlife | 247 | 2021-07-04 | 16055 | keep | 0 | Jul | 2021 | 0.010935 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BARRANQUITAS | 2021-07-04 08:25 | 2021-07-04 20:32 | 50 | 012:07 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA SE PATRULLO | C21070400054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 727 | 2021-07-04 | 36350 | keep | 0 | Jul | 2021 | 0.024758 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-04 08:42 | 2021-07-05 17:10 | 3 | 032:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE HACIA TRANSFORMADOR | R21070400068 | New_Event | Wire Down | Include | Include | Equipment | 1948 | 2021-07-04 | 5844 | keep | 0 | Jul | 2021 | 0.0039803 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2021-07-04 08:45 | 2021-07-04 10:19 | 60 | 001:34 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070400088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2021-07-04 | 5640 | keep | 0 | Jul | 2021 | 0.0038414 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-07-04 08:52 | 2021-07-04 09:37 | 6 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA PARTIDA | C21070400000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2021-07-04 | 270 | keep | 0 | Jul | 2021 | 0.0001839 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
BAYAMON | 2021-07-04 09:07 | 2021-07-04 12:30 | 80 | 003:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO | S21070400178 | New_Event | Wire Down | Include | Include | Equipment | 203 | 2021-07-04 | 16240 | keep | 0 | Jul | 2021 | 0.011061 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2021-07-04 09:28 | 2021-07-07 17:00 | 40 | 079:32 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA DESGANCHE | A21070700145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 4772 | 2021-07-04 | 190880 | keep | 0 | Jul | 2021 | 0.13001 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-04 09:49 | 2021-07-04 16:05 | 200 | 006:16 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO ARBOL | B21070400020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 376 | 2021-07-04 | 75200 | keep | 0 | Jul | 2021 | 0.051218 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-07-04 10:05 | 2021-07-05 08:59 | 100 | 022:54 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070400112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1374 | 2021-07-04 | 137400 | keep | 0 | Jul | 2021 | 0.093583 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-07-04 10:15 | 2021-07-05 16:50 | 30 | 030:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21070400118 | New_Event | Bad Weather | Include | Include | Weather | 1835 | 2021-07-04 | 55050 | keep | 0 | Jul | 2021 | 0.037494 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BARRANQUITAS | 2021-07-04 10:18 | 2021-07-04 10:19 | 2565 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C21070400000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-04 | 2565 | keep | 0 | Jul | 2021 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2021-07-04 10:19 | 2021-07-04 10:35 | 500 | 000:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR DEL SUELO | C21070400000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 16 | 2021-07-04 | 8000 | keep | 0 | Jul | 2021 | 0.0054488 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
PONCE | 2021-07-04 10:23 | 2021-07-04 10:24 | 1979 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE DE PORTATIL 10 | P210704000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-04 | 1979 | keep | 0 | Jul | 2021 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2021-07-04 10:23 | 2021-07-04 10:24 | 5069 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE DE PORTATIL 10 | P210704000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-04 | 5069 | keep | 0 | Jul | 2021 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2021-07-04 10:23 | 2021-07-04 10:24 | 5063 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE DE PORTATIL 10 | P210704000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-04 | 5063 | keep | 0 | Jul | 2021 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
AGUADILLA | 2021-07-04 10:23 | 2021-07-05 13:40 | 40 | 027:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21070400127 | New_Event | Bad Weather | Include | Include | Weather | 1637 | 2021-07-04 | 65480 | keep | 0 | Jul | 2021 | 0.044598 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
YAUCO | 2021-07-04 10:29 | 2021-07-04 10:30 | 3973 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210704000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-04 | 3973 | keep | 0 | Jul | 2021 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2021-07-04 10:29 | 2021-07-04 10:30 | 2484 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210704000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-04 | 2484 | keep | 0 | Jul | 2021 | 0.0016918 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
BARRANQUITAS | 2021-07-04 10:35 | 2021-07-04 11:45 | 2565 | 001:10 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR CONDUCTOR EN EL SUELO | C21070400000 | Additional_clients | Wire Down | Include | Include | Equipment | 70 | 2021-07-04 | 179550 | keep | 0 | Jul | 2021 | 0.12229 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-04 10:40 | 2021-07-04 10:41 | 271 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21070400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-04 | 271 | keep | 0 | Jul | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
ARECIBO | 2021-07-04 10:40 | 2021-07-04 11:40 | 50 | 001:00 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | A21070300046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2021-07-04 | 3000 | keep | 0 | Jul | 2021 | 0.0020433 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-07-04 10:42 | 2021-07-05 11:11 | 44 | 024:29 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P21070400046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1469 | 2021-07-04 | 64636 | keep | 0 | Jul | 2021 | 0.044023 | 2.9968e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 44
MAYAGÃœEZ | 2021-07-04 10:48 | 2021-07-04 12:00 | 30 | 001:12 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M21070400136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2021-07-04 | 2160 | keep | 0 | Jul | 2021 | 0.0014712 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
YAUCO | 2021-07-04 10:55 | 2021-07-04 17:00 | 70 | 006:05 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA POR DESGANCHE | P21070400048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 365 | 2021-07-04 | 25550 | keep | 0 | Jul | 2021 | 0.017402 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
AGUADILLA | 2021-07-04 11:11 | 2021-07-04 11:12 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 7011-02 | M21070400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-04 | 1827 | keep | 0 | Jul | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2021-07-04 11:11 | 2021-07-04 11:12 | 1047 | 000:01 | T | NO SE REPORTO CAUSA | CARGA POR 7011-01 | M21070400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-04 | 1047 | keep | 0 | Jul | 2021 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
BAYAMON | 2021-07-04 11:13 | 2021-07-05 11:29 | 15 | 024:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE REPARO BAJANTE SECUNDARIO | B21070400024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1456 | 2021-07-04 | 21840 | keep | 0 | Jul | 2021 | 0.014875 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2021-07-04 11:20 | 2021-07-05 21:14 | 300 | 033:54 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA SE PATRULLO | C21070400107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2034 | 2021-07-04 | 610200 | keep | 0 | Jul | 2021 | 0.4156 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
SAN JUAN | 2021-07-04 11:24 | 2021-07-07 12:42 | 50 | 073:18 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA, 1 X 50 EN CORTE DE LINEA Y 1 X 65 EN CORTE DE LINEA | S21070400046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4398 | 2021-07-04 | 219900 | keep | 0 | Jul | 2021 | 0.14977 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-07-04 11:33 | 2021-07-05 16:59 | 202 | 029:26 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DOS ALAMBRES EN EL PISO | P21070400053 | New_Event | Wire Down | Include | Include | Equipment | 1766 | 2021-07-04 | 356732 | keep | 0 | Jul | 2021 | 0.24297 | 0.00013758 | Sustained | FALSE | FALSE | Not_TMED_Event | 202
CAGUAS | 2021-07-04 11:43 | 2021-07-04 16:47 | 100 | 005:04 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTE DE LINEA | C21070400092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 304 | 2021-07-04 | 30400 | keep | 0 | Jul | 2021 | 0.020705 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BARRANQUITAS | 2021-07-04 11:45 | 2021-07-04 15:39 | 500 | 003:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR DEL SUELO | C21070400000 | Partial_restoration | Wire Down | Include | Include | Equipment | 234 | 2021-07-04 | 117000 | keep | 0 | Jul | 2021 | 0.079688 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-07-04 12:00 | 2021-07-07 11:06 | 6 | 071:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21070400093 | New_Event | Secondary Wire Down | Include | Include | Equipment | 4266 | 2021-07-04 | 25596 | keep | 0 | Jul | 2021 | 0.017433 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-07-04 12:22 | 2021-07-04 12:23 | 1307 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C21070400000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-04 | 1307 | keep | 0 | Jul | 2021 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
CAGUAS | 2021-07-04 12:23 | 2021-07-05 10:34 | 4 | 022:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO BAJANTE | C21070400142 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1331 | 2021-07-04 | 5324 | keep | 0 | Jul | 2021 | 0.0036262 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-07-04 12:32 | 2021-07-05 09:20 | 20 | 020:48 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21070400183 | New_Event | Bad Weather | Include | Include | Weather | 1248 | 2021-07-04 | 24960 | keep | 0 | Jul | 2021 | 0.017 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-07-04 12:33 | 2021-07-05 10:31 | 63 | 021:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | C21070400100 | New_Event |  |  | Include | Wildlife | 1318 | 2021-07-04 | 83034 | keep | 0 | Jul | 2021 | 0.056554 | 4.2909e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 63
SAN JUAN | 2021-07-04 12:35 | 2021-07-04 13:08 | 1271 | 000:33 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO SALIDA INTERRUPTOR COORDINADO CON COD CAROLINA | S21070400055 | New_Event | Switch Failure | Include | Include | Equipment | 33 | 2021-07-04 | 41943 | keep | 0 | Jul | 2021 | 0.028567 | 0.00086567 | Sustained | FALSE | FALSE | Not_TMED_Event | 1271
FAJARDO | 2021-07-04 12:37 | 2021-07-05 10:23 | 70 | 021:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE CON RATAS | R21070400040 | New_Event |  |  | Include | Wildlife | 1306 | 2021-07-04 | 91420 | keep | 0 | Jul | 2021 | 0.062266 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
UTUADO | 2021-07-04 12:37 | 2021-07-06 13:42 | 60 | 049:05 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | A21070400088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2945 | 2021-07-04 | 176700 | keep | 0 | Jul | 2021 | 0.12035 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-07-04 12:38 | 2021-07-05 13:44 | 56 | 025:06 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEAS | C21070400103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1506 | 2021-07-04 | 84336 | keep | 0 | Jul | 2021 | 0.057441 | 3.8141e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 56
UTUADO | 2021-07-04 12:40 | 2021-07-04 14:00 | 50 | 001:20 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21070400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2021-07-04 | 4000 | keep | 0 | Jul | 2021 | 0.0027244 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-07-04 12:47 | 2021-07-05 14:20 | 12 | 025:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A21070400094 | New_Event | Bad Weather | Include | Include | Weather | 1533 | 2021-07-04 | 18396 | keep | 0 | Jul | 2021 | 0.012529 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-07-04 12:55 | 2021-07-04 17:50 | 80 | 004:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21070400189 | New_Event | Bad Weather | Include | Include | Weather | 295 | 2021-07-04 | 23600 | keep | 0 | Jul | 2021 | 0.016074 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
AGUADILLA | 2021-07-04 12:56 | 2021-07-05 18:30 | 50 | 029:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | M21070400191 | New_Event | Bad Weather | Include | Include | Weather | 1774 | 2021-07-04 | 88700 | keep | 0 | Jul | 2021 | 0.060413 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
YAUCO | 2021-07-04 12:59 | 2021-07-06 19:15 | 15 | 054:16 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21070400062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3256 | 2021-07-04 | 48840 | keep | 0 | Jul | 2021 | 0.033265 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-07-04 13:03 | 2021-07-04 15:27 | 2713 | 002:24 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO LINEA PRIMARIA AVERIADA | M21070400193 | New_Event | Wire Down | Include | Include | Equipment | 144 | 2021-07-04 | 390672 | keep | 0 | Jul | 2021 | 0.26608 | 0.0018478 | Sustained | FALSE | TRUE | Not_TMED_Event | 2713
UTUADO | 2021-07-04 13:13 | 2021-07-04 19:25 | 500 | 006:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO | A21070400098 | New_Event | Wire Down | Include | Include | Equipment | 372 | 2021-07-04 | 186000 | keep | 0 | Jul | 2021 | 0.12668 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CANOVANAS | 2021-07-04 13:22 | 2021-07-05 13:27 | 90 | 024:05 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21070400043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1445 | 2021-07-04 | 130050 | keep | 0 | Jul | 2021 | 0.088576 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
CAGUAS | 2021-07-04 13:23 | 2021-07-04 17:17 | 4 | 003:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO HACIA CAJA PRIMARIA | C21070400112 | New_Event | Wire Down | Include | Include | Equipment | 234 | 2021-07-04 | 936 | keep | 0 | Jul | 2021 | 0.00063751 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2021-07-04 13:26 | 2021-07-04 15:10 | 200 | 001:44 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 200 EN CORTE DE LINEA POR MAL TIEMPO | P21070400041 | New_Event | Bad Weather | Include | Include | Weather | 104 | 2021-07-04 | 20800 | keep | 0 | Jul | 2021 | 0.014167 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
PONCE | 2021-07-04 13:26 | 2021-07-04 15:52 | 66 | 002:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | P21070300104 | New_Event | Bad Weather | Include | Include | Weather | 146 | 2021-07-04 | 9636 | keep | 0 | Jul | 2021 | 0.006563 | 4.4952e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 66
MAYAGÃœEZ | 2021-07-04 13:26 | 2021-07-05 20:15 | 10 | 030:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | M21070400202 | New_Event | Bad Weather | Include | Include | Weather | 1849 | 2021-07-04 | 18490 | keep | 0 | Jul | 2021 | 0.012593 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-04 13:29 | 2021-07-04 13:47 | 353 | 000:18 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO RECERRO SE PROBO POR CONTROL SE QUEDO EN SERVICIO | S21070400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 18 | 2021-07-04 | 6354 | keep | 0 | Jul | 2021 | 0.0043277 | 0.00024043 | Sustained | FALSE | FALSE | Not_TMED_Event | 353
CANOVANAS | 2021-07-04 13:29 | 2021-07-05 09:26 | 1 | 019:57 | P | DESGANCHE | 2 X 10 EN BANCO DE TRANSFORMADOR | R21070400044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1197 | 2021-07-04 | 1197 | keep | 0 | Jul | 2021 | 0.00081527 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-07-04 13:29 | 2021-07-07 19:30 | 80 | 078:01 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | A21070400100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 4681 | 2021-07-04 | 374480 | keep | 0 | Jul | 2021 | 0.25506 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
UTUADO | 2021-07-04 13:29 | 2021-07-04 16:45 | 100 | 003:16 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO RAMA | A21070400100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2021-07-04 | 19600 | keep | 0 | Jul | 2021 | 0.013349 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-04 13:40 | 2021-07-04 17:55 | 25 | 004:15 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21070400031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 255 | 2021-07-04 | 6375 | keep | 0 | Jul | 2021 | 0.004342 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-07-04 13:44 | 2021-07-05 09:49 | 40 | 020:05 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | S21070400058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1205 | 2021-07-04 | 48200 | keep | 0 | Jul | 2021 | 0.032829 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-04 13:50 | 2021-07-04 13:51 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21070400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-04 | 2605 | keep | 0 | Jul | 2021 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
PONCE | 2021-07-04 14:17 | 2021-07-06 20:54 | 50 | 054:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS Y SE CERRO PUENTE PRIMARIO | P21070400068 | New_Event | Wire Down | Include | Include | Equipment | 3277 | 2021-07-04 | 163850 | keep | 0 | Jul | 2021 | 0.1116 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-07-04 14:17 | 2021-07-05 18:55 | 80 | 028:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS ROTAS | A21070400125 | New_Event | Wire Down | Include | Include | Equipment | 1718 | 2021-07-04 | 137440 | keep | 0 | Jul | 2021 | 0.09361 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-07-04 14:18 | 2021-07-04 15:36 | 6 | 001:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIAS | C21070400000 | New_Event | Bad Weather | Include | Include | Weather | 78 | 2021-07-04 | 468 | keep | 0 | Jul | 2021 | 0.00031875 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
VEGA BAJA | 2021-07-04 14:28 | 2021-07-04 17:59 | 50 | 003:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA SE SECCIONALIZO POSTE IMPACTADO | B21070400036 | New_Event |  |  | Include | Wildlife | 211 | 2021-07-04 | 10550 | keep | 0 | Jul | 2021 | 0.0071856 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-04 14:33 | 2021-07-05 09:38 | 50 | 019:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21070400230 | New_Event | Bad Weather | Include | Include | Weather | 1145 | 2021-07-04 | 57250 | keep | 0 | Jul | 2021 | 0.038993 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-04 14:34 | 2021-07-04 17:10 | 40 | 002:36 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21070400117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2021-07-04 | 6240 | keep | 0 | Jul | 2021 | 0.00425 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-07-04 14:42 | 2021-07-05 12:20 | 100 | 021:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | A21070400116 | New_Event | Wire Down | Include | Include | Equipment | 1298 | 2021-07-04 | 129800 | keep | 0 | Jul | 2021 | 0.088406 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-07-04 14:50 | 2021-07-05 09:14 | 1 | 018:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | C21070400118 | New_Event | Cutout Failure | Include | Include | Equipment | 1104 | 2021-07-04 | 1104 | keep | 0 | Jul | 2021 | 0.00075193 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-07-04 14:50 | 2021-07-05 17:40 | 70 | 026:50 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | M21070400235 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1610 | 2021-07-04 | 112700 | keep | 0 | Jul | 2021 | 0.076759 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
AGUADILLA | 2021-07-04 14:54 | 2021-07-05 19:31 | 50 | 028:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | M21070400240 | New_Event | Bad Weather | Include | Include | Weather | 1717 | 2021-07-04 | 85850 | keep | 0 | Jul | 2021 | 0.058472 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-04 14:57 | 2021-07-04 16:42 | 1 | 001:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR CRUCE CON AVE | C21070400119 | New_Event |  |  | Include | Wildlife | 105 | 2021-07-04 | 105 | keep | 0 | Jul | 2021 | 7.1515e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-07-04 15:01 | 2021-07-05 17:00 | 40 | 025:59 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21070400121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1559 | 2021-07-04 | 62360 | keep | 0 | Jul | 2021 | 0.042473 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-07-04 15:16 | 2021-07-04 15:18 | 2658 | 000:02 | T | DESGANCHE | RECIERRE INTERRUPTOR | M21070400000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-07-04 | 5316 | keep | 0 | Jul | 2021 | 0.0036207 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-04 15:18 | 2021-07-04 15:45 | 50 | 000:27 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | M21070300391 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 27 | 2021-07-04 | 1350 | keep | 0 | Jul | 2021 | 0.00091948 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-04 15:27 | 2021-07-04 17:00 | 10 | 001:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE CERRO CORTE DE LINEA | M21070400196 | Partial_restoration | Wire Down | Include | Include | Equipment | 93 | 2021-07-04 | 930 | keep | 0 | Jul | 2021 | 0.00063342 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-07-04 15:57 | 2021-07-05 09:20 | 50 | 017:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21070400124 | New_Event | Bad Weather | Include | Include | Weather | 1043 | 2021-07-04 | 52150 | keep | 0 | Jul | 2021 | 0.035519 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-04 16:00 | 2021-07-05 16:50 | 50 | 024:50 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | S21070400047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1490 | 2021-07-04 | 74500 | keep | 0 | Jul | 2021 | 0.050742 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-04 16:08 | 2021-07-06 10:48 | 2 | 042:40 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21070400254 | New_Event | Bad Weather | Include | Include | Weather | 2560 | 2021-07-04 | 5120 | keep | 0 | Jul | 2021 | 0.0034872 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
UTUADO | 2021-07-04 16:13 | 2021-07-05 16:50 | 20 | 024:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21070500108 | New_Event | Bad Weather | Include | Include | Weather | 1477 | 2021-07-04 | 29540 | keep | 0 | Jul | 2021 | 0.02012 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
HUMACAO | 2021-07-04 16:19 | 2021-07-04 21:46 | 1 | 005:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | C21070400023 | New_Event | Cutout Failure | Include | Include | Equipment | 327 | 2021-07-04 | 327 | keep | 0 | Jul | 2021 | 0.00022272 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-07-04 16:22 | 2021-07-04 18:57 | 90 | 002:35 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO | C21070400124 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 155 | 2021-07-04 | 13950 | keep | 0 | Jul | 2021 | 0.0095013 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
CANOVANAS | 2021-07-04 16:34 | 2021-07-05 08:19 | 10 | 015:45 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | R21070400052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 945 | 2021-07-04 | 9450 | keep | 0 | Jul | 2021 | 0.0064364 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
SAN JUAN | 2021-07-04 16:46 | 2021-07-07 08:55 | 50 | 064:09 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN CORTE DE LINEA SE REEMPLAZO AISLADOR | S21070400068 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 3849 | 2021-07-04 | 192450 | keep | 0 | Jul | 2021 | 0.13108 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-04 17:09 | 2021-07-04 17:10 | 2000 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE | R21070400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-04 | 2000 | keep | 0 | Jul | 2021 | 0.0013622 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
MAYAGÃœEZ | 2021-07-04 17:12 | 2021-07-04 17:16 | 1142 | 000:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR LINEA PRIMARIA ROTA | M21070400000 | New_Event | Wire Down | Include | Include | Equipment | 4 | 2021-07-04 | 4568 | keep | 0 | Jul | 2021 | 0.0031112 | 0.00077781 | Momentary | FALSE | TRUE | Not_TMED_Event | 1142
MAYAGÃœEZ | 2021-07-04 17:16 | 2021-07-04 19:07 | 500 | 001:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA SE CERRO PUENTES | M21070400280 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 111 | 2021-07-04 | 55500 | keep | 0 | Jul | 2021 | 0.037801 | 0.00034055 | Sustained | FALSE | TRUE | Not_TMED_Event | 500
CAGUAS | 2021-07-04 17:25 | 2021-07-05 10:07 | 6 | 016:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE HACIA CAJA Y SE REEMPLAZO CAJA | C21070400134 | New_Event | Wire Down | Include | Include | Equipment | 1002 | 2021-07-04 | 6012 | keep | 0 | Jul | 2021 | 0.0040947 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2021-07-04 17:29 | 2021-07-05 11:20 | 30 | 017:51 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21070400057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1071 | 2021-07-04 | 32130 | keep | 0 | Jul | 2021 | 0.021884 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
VEGA BAJA | 2021-07-04 17:36 | 2021-07-04 20:21 | 60 | 002:45 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21070400049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 165 | 2021-07-04 | 9900 | keep | 0 | Jul | 2021 | 0.0067428 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-07-04 17:44 | 2021-07-04 17:45 | 2842 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C21070040000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-04 | 2842 | keep | 0 | Jul | 2021 | 0.0019357 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
MAYAGÃœEZ | 2021-07-04 17:45 | 2021-07-05 18:15 | 40 | 024:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21070400294 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1470 | 2021-07-04 | 58800 | keep | 0 | Jul | 2021 | 0.040048 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-07-04 17:50 | 2021-07-05 21:41 | 30 | 027:51 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C21070400137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1671 | 2021-07-04 | 50130 | keep | 0 | Jul | 2021 | 0.034143 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-07-04 17:56 | 2021-07-05 18:30 | 100 | 024:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | M21070400298 | New_Event | Bad Weather | Include | Include | Weather | 1474 | 2021-07-04 | 147400 | keep | 0 | Jul | 2021 | 0.10039 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-07-04 17:59 | 2021-07-05 12:15 | 100 | 018:16 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070400301 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1096 | 2021-07-04 | 109600 | keep | 0 | Jul | 2021 | 0.074648 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-07-04 17:59 | 2021-07-05 19:25 | 36 | 025:26 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE AVERIADO | B21070400036 | New_Event | Defective Pole | Include | Include | Equipment | 1526 | 2021-07-04 | 54936 | keep | 0 | Jul | 2021 | 0.037417 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CANOVANAS | 2021-07-04 18:07 | 2021-07-04 18:08 | 2106 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21070400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-04 | 2106 | keep | 0 | Jul | 2021 | 0.0014344 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
BAYAMON | 2021-07-04 18:08 | 2021-07-04 18:09 | 6136 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21070400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-04 | 6136 | keep | 0 | Jul | 2021 | 0.0041792 | 0.0041792 | Momentary | FALSE | FALSE | Not_TMED_Event | 6136
MAYAGÃœEZ | 2021-07-04 18:08 | 2021-07-05 17:55 | 50 | 023:47 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | M21070400305 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1427 | 2021-07-04 | 71350 | keep | 0 | Jul | 2021 | 0.048596 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-07-04 18:13 | 2021-07-05 09:25 | 50 | 015:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21070400149 | New_Event | Bad Weather | Include | Include | Weather | 912 | 2021-07-04 | 45600 | keep | 0 | Jul | 2021 | 0.031058 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-04 18:20 | 2021-07-04 18:21 | 5668 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21070400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-04 | 5668 | keep | 0 | Jul | 2021 | 0.0038604 | 0.0038604 | Momentary | FALSE | FALSE | Not_TMED_Event | 5668
ARECIBO | 2021-07-04 18:25 | 2021-07-05 17:45 | 70 | 023:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21070400151 | New_Event | Bad Weather | Include | Include | Weather | 1400 | 2021-07-04 | 98000 | keep | 0 | Jul | 2021 | 0.066747 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
SAN JUAN | 2021-07-04 18:33 | 2021-07-05 11:46 | 15 | 017:13 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR | S21070400073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1033 | 2021-07-04 | 15495 | keep | 0 | Jul | 2021 | 0.010554 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-07-04 18:38 | 2021-07-05 09:04 | 25 | 014:26 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21070400057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 866 | 2021-07-04 | 21650 | keep | 0 | Jul | 2021 | 0.014746 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
FAJARDO | 2021-07-04 18:39 | 2021-07-04 21:05 | 100 | 002:26 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R21070400064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2021-07-04 | 14600 | keep | 0 | Jul | 2021 | 0.009944 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-04 18:45 | 2021-07-05 10:30 | 40 | 015:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA | S21070400074 | New_Event | Cutout Failure | Include | Include | Equipment | 945 | 2021-07-04 | 37800 | keep | 0 | Jul | 2021 | 0.025745 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-07-04 18:51 | 2021-07-05 11:12 | 100 | 016:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21070400317 | New_Event | Bad Weather | Include | Include | Weather | 981 | 2021-07-04 | 98100 | keep | 0 | Jul | 2021 | 0.066815 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-04 18:56 | 2021-07-05 12:48 | 12 | 017:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO Y LEVANTO DOS TRAMOS DE LINEA SECUNDARIA | S21070400076 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1072 | 2021-07-04 | 12864 | keep | 0 | Jul | 2021 | 0.0087616 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
CAGUAS | 2021-07-04 19:54 | 2021-07-06 14:50 | 6 | 042:56 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | C21070400144 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 2576 | 2021-07-04 | 15456 | keep | 0 | Jul | 2021 | 0.010527 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-07-04 19:57 | 2021-07-05 11:00 | 60 | 015:03 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21070400078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 903 | 2021-07-04 | 54180 | keep | 0 | Jul | 2021 | 0.036902 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
AGUADILLA | 2021-07-04 20:00 | 2021-07-04 20:10 | 709 | 000:10 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR RECIERRE EN OFF NO SE REPORTO CAUSA | M21070400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2021-07-04 | 7090 | keep | 0 | Jul | 2021 | 0.004829 | 0.0004829 | Sustained | FALSE | FALSE | Not_TMED_Event | 709
BARRANQUITAS | 2021-07-04 20:09 | 2021-07-04 20:10 | 2362 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C21070400000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-04 | 2362 | keep | 0 | Jul | 2021 | 0.0016087 | 0.0016087 | Momentary | FALSE | FALSE | Not_TMED_Event | 2362
AGUADILLA | 2021-07-04 20:10 | 2021-07-05 11:25 | 100 | 015:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21070400345 | New_Event | Bad Weather | Include | Include | Weather | 915 | 2021-07-04 | 91500 | keep | 0 | Jul | 2021 | 0.06232 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BARRANQUITAS | 2021-07-04 20:10 | 2021-07-05 13:00 | 500 | 016:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | C21070400157 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1010 | 2021-07-04 | 505000 | keep | 0 | Jul | 2021 | 0.34395 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
MAYAGÃœEZ | 2021-07-04 20:40 | 2021-07-05 14:00 | 100 | 017:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | M21070400338 | New_Event | Bad Weather | Include | Include | Weather | 1040 | 2021-07-04 | 104000 | keep | 0 | Jul | 2021 | 0.070834 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
YAUCO | 2021-07-04 20:52 | 2021-07-06 10:09 | 15 | 037:17 | P | NO SE REPORTO CAUSA | SE CERRO CORTE DE LINEA. NO SE REPORTO AVERIA | P21070400089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2237 | 2021-07-04 | 33555 | keep | 0 | Jul | 2021 | 0.022854 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-07-04 20:59 | 2021-07-05 14:15 | 12 | 017:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE REPARO CONECTOR BAJANTE SECUNDARIO | S21070400083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1036 | 2021-07-04 | 12432 | keep | 0 | Jul | 2021 | 0.0084674 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-07-04 21:02 | 2021-07-05 15:00 | 80 | 017:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21070400340 | New_Event | Bad Weather | Include | Include | Weather | 1078 | 2021-07-04 | 86240 | keep | 0 | Jul | 2021 | 0.058738 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
AGUADILLA | 2021-07-04 21:20 | 2021-07-05 10:15 | 200 | 012:55 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M21070400342 | New_Event | Vegetation Contact | Include | Include | Vegetation | 775 | 2021-07-04 | 155000 | keep | 0 | Jul | 2021 | 0.10557 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
HUMACAO | 2021-07-04 21:46 | 2021-07-04 21:47 | 3701 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21070400159 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2021-07-04 | 3701 | keep | 0 | Jul | 2021 | 0.0025207 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-07-04 21:47 | 2021-07-04 21:58 | 1 | 000:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | C21070400023 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 11 | 2021-07-04 | 11 | keep | 0 | Jul | 2021 | 7.492e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-07-04 21:51 | 2021-07-04 21:52 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21070400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-04 | 2354 | keep | 0 | Jul | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
BAYAMON | 2021-07-04 21:58 | 2021-07-05 08:59 | 60 | 011:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN CORTE DE LINEA SEREMPLAZO CAJA | B21070400065 | New_Event | Cutout Failure | Include | Include | Equipment | 661 | 2021-07-04 | 39660 | keep | 0 | Jul | 2021 | 0.027012 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-07-04 21:58 | 2021-07-04 21:59 | 3701 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21070400000 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2021-07-04 | 3701 | keep | 0 | Jul | 2021 | 0.0025207 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-07-04 21:59 | 2021-07-05 19:20 | 1 | 021:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRMARIA | C21070400023 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1281 | 2021-07-04 | 1281 | keep | 0 | Jul | 2021 | 0.00087248 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-07-04 22:03 | 2021-07-04 22:04 | 1606 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21070400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-04 | 1606 | keep | 0 | Jul | 2021 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
MAYAGÃœEZ | 2021-07-04 22:09 | 2021-07-05 15:00 | 400 | 016:51 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA DESGANCHE | M21070400350 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1011 | 2021-07-04 | 404400 | keep | 0 | Jul | 2021 | 0.27543 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
MAYAGÃœEZ | 2021-07-04 22:09 | 2021-07-05 08:59 | 500 | 010:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ABIERTO EN TRONCAL DEL ALIMENTADOR SE ABRIO INTERRUPTOR PARA REPARAR LA CONDICION | M21070400351 | New_Event | Wire Down | Include | Include | Equipment | 650 | 2021-07-04 | 325000 | keep | 0 | Jul | 2021 | 0.22136 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
HUMACAO | 2021-07-04 22:11 | 2021-07-05 00:40 | 2354 | 002:29 | T | NO SE REPORTO CAUSA | INTERRUPTOR SECCIONALIZADO. SE ABRIERON MACHETES EN SALIDA DEL PB-1 Y PB-2 | C21070400167 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 149 | 2021-07-04 | 350746 | keep | 0 | Jul | 2021 | 0.23889 | 0.0016033 | Sustained | FALSE | FALSE | Not_TMED_Event | 2354
MAYAGÃœEZ | 2021-07-04 23:03 | 2021-07-05 08:41 | 80 | 009:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21070400361 | New_Event | Bad Weather | Include | Include | Weather | 578 | 2021-07-04 | 46240 | keep | 0 | Jul | 2021 | 0.031494 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-07-04 23:52 | 2021-07-05 10:23 | 70 | 010:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 Y 1 X 5 EN CORTE DE LINEA Y TRANSFORMADOR CRUCE CON RATA | R21070400082 | New_Event |  |  | Include | Wildlife | 631 | 2021-07-04 | 44170 | keep | 0 | Jul | 2021 | 0.030084 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
HUMACAO | 2021-07-05 00:40 | 2021-07-05 01:17 | 1200 | 000:37 | P | NO SE REPORTO CAUSA | SE CERRARON MACHETES EN SALIDA DEL PB-1 Y PB-2 SE PATRULLO Y SECCIONALIZO POR TRAMOS | C21070400167 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 37 | 2021-07-05 | 44400 | keep | 0 | Jul | 2021 | 0.030241 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-07-05 02:39 | 2021-07-05 02:40 | 4085 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21070500006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 4085 | keep | 0 | Jul | 2021 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
SAN JUAN | 2021-07-05 03:15 | 2021-07-06 16:25 | 60 | 037:10 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21070600004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2230 | 2021-07-05 | 133800 | keep | 0 | Jul | 2021 | 0.091131 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-07-05 03:15 | 2021-07-05 18:27 | 150 | 015:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 Y 1 X 30 EN CORTES DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21070500004 | New_Event | Bad Weather | Include | Include | Weather | 912 | 2021-07-05 | 136800 | keep | 0 | Jul | 2021 | 0.093174 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
HUMACAO | 2021-07-05 03:24 | 2021-07-05 17:18 | 200 | 013:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIAS | C21070500017 | New_Event | Bad Weather | Include | Include | Weather | 834 | 2021-07-05 | 166800 | keep | 0 | Jul | 2021 | 0.11361 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BARRANQUITAS | 2021-07-05 04:00 | 2021-07-05 04:01 | 2280 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO RR/OFF 9902-03 CARGA POR EL 9902-03 | C21070500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 2280 | keep | 0 | Jul | 2021 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2021-07-05 04:00 | 2021-07-05 04:01 | 1617 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO RR/OFF 9902-03 LLEVANDO LA CARGA DEL 9902-02 | C21070500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 1617 | keep | 0 | Jul | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
HUMACAO | 2021-07-05 04:11 | 2021-07-05 16:02 | 200 | 011:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE SE SECCIONALIZO CONDUCTOR DEL SUELO | C21070500020 | New_Event | Wire Down | Include | Include | Equipment | 711 | 2021-07-05 | 142200 | keep | 0 | Jul | 2021 | 0.096852 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2021-07-05 04:43 | 2021-07-05 04:45 | 2888 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | A21070500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-05 | 5776 | keep | 0 | Jul | 2021 | 0.003934 | 0.001967 | Momentary | FALSE | FALSE | Not_TMED_Event | 2888
FAJARDO | 2021-07-05 05:00 | 2021-07-05 06:34 | 3003 | 001:34 | T | NO SE REPORTO CAUSA | DISPARO SE RESETEARON BANDERASY SE CERRO INTERRUPTOR | R21070500008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 94 | 2021-07-05 | 282282 | keep | 0 | Jul | 2021 | 0.19226 | 0.0020453 | Sustained | FALSE | FALSE | Not_TMED_Event | 3003
VEGA BAJA | 2021-07-05 05:00 | 2021-07-05 05:02 | 31 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21070500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-05 | 62 | keep | 0 | Jul | 2021 | 4.2228e-05 | 2.1114e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 31
SAN JUAN | 2021-07-05 05:22 | 2021-07-05 05:23 | 4291 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CARGA POR EL 1303-02 | S21070500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 4291 | keep | 0 | Jul | 2021 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
SAN JUAN | 2021-07-05 05:22 | 2021-07-05 05:23 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVANDO LA CARGA DEL 1204-02 Y 60% DEL 1346-05 | S21070500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 2435 | keep | 0 | Jul | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2021-07-05 05:22 | 2021-07-05 05:23 | 575 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1303-02 LLEVANDO 60% DEL 1346-05 | S21070500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 575 | keep | 0 | Jul | 2021 | 0.00039163 | 0.00039163 | Momentary | FALSE | FALSE | Not_TMED_Event | 575
SAN JUAN | 2021-07-05 05:23 | 2021-07-07 18:59 | 25 | 061:36 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | S21070500044 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 3696 | 2021-07-05 | 92400 | keep | 0 | Jul | 2021 | 0.062933 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2021-07-05 05:31 | 2021-07-05 10:06 | 60 | 004:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR Y 1 X 65 EN CORTE DE LINEA, AVE CRUZO FASE. | P21070500002 | New_Event |  |  | Include | Wildlife | 275 | 2021-07-05 | 16500 | keep | 0 | Jul | 2021 | 0.011238 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-07-05 06:00 | 2021-07-05 16:00 | 15 | 010:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21070500000 | New_Event | Bad Weather | Include | Include | Weather | 600 | 2021-07-05 | 9000 | keep | 0 | Jul | 2021 | 0.0061299 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-07-05 06:00 | 2021-07-05 14:00 | 15 | 008:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO | M21070400000 | New_Event | Wire Down | Include | Include | Equipment | 480 | 2021-07-05 | 7200 | keep | 0 | Jul | 2021 | 0.0049039 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-07-05 06:20 | 2021-07-05 12:20 | 150 | 006:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21070500045 | New_Event | Bad Weather | Include | Include | Weather | 360 | 2021-07-05 | 54000 | keep | 0 | Jul | 2021 | 0.036779 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-07-05 06:31 | 2021-07-05 16:54 | 20 | 010:23 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R21070500013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 623 | 2021-07-05 | 12460 | keep | 0 | Jul | 2021 | 0.0084864 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
HUMACAO | 2021-07-05 06:38 | 2021-07-05 06:39 | 2450 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO SE CERRO POR CONTROL | C21070500025 | New_Event |  |  | Include | Wildlife | 1 | 2021-07-05 | 2450 | keep | 0 | Jul | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2021-07-05 06:39 | 2021-07-05 11:17 | 200 | 004:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE CON ANIMAL | C21070500172 | 1st_after_momentary |  |  | Include | Wildlife | 278 | 2021-07-05 | 55600 | keep | 0 | Jul | 2021 | 0.037869 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
GUAYAMA | 2021-07-05 06:47 | 2021-07-05 09:21 | 18 | 002:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR. SE REPARO LINEA SECUNDARIA. | P21040500004 | New_Event | Secondary Wire Down | Include | Include | Equipment | 154 | 2021-07-05 | 2772 | keep | 0 | Jul | 2021 | 0.001888 | 1.226e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 18
SAN JUAN | 2021-07-05 06:58 | 2021-07-05 20:00 | 12 | 013:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA DE TRANSFORMADOR | S21070500001 | New_Event | Cutout Failure | Include | Include | Equipment | 782 | 2021-07-05 | 9384 | keep | 0 | Jul | 2021 | 0.0063914 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-07-05 07:07 | 2021-07-05 17:53 | 1 | 010:46 | P | NO SE REPORTO CAUSA | 1 X 10 EN BANCO DE TRANSFORMADORES | R21070500014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 646 | 2021-07-05 | 646 | keep | 0 | Jul | 2021 | 0.00043999 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-07-05 07:07 | 2021-07-05 18:28 | 100 | 011:21 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL HACIA EL T-38 | C21070500034 | New_Event | UG Cable Fault | Include | Include | Equipment | 681 | 2021-07-05 | 68100 | keep | 0 | Jul | 2021 | 0.046383 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-07-05 07:13 | 2021-07-05 20:51 | 7 | 013:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN CORTE DE LINEA LLUVIAS | C21070500036 | New_Event | Bad Weather | Include | Include | Weather | 818 | 2021-07-05 | 5726 | keep | 0 | Jul | 2021 | 0.0039 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
CAGUAS | 2021-07-05 07:18 | 2021-07-05 13:24 | 79 | 006:06 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21070500039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 366 | 2021-07-05 | 28914 | keep | 0 | Jul | 2021 | 0.019693 | 5.3807e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 79
BAYAMON | 2021-07-05 07:25 | 2021-07-05 13:00 | 1 | 005:35 | P | NO SE REPORTO CAUSA | 2 X 40 EN CORTE DE LINEA | B21070500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 335 | 2021-07-05 | 335 | keep | 0 | Jul | 2021 | 0.00022817 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-07-05 07:33 | 2021-07-05 07:34 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A02107050000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 3431 | keep | 0 | Jul | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2021-07-05 07:42 | 2021-07-05 10:40 | 80 | 002:58 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21070500019 | New_Event | Bad Weather | Include | Include | Weather | 178 | 2021-07-05 | 14240 | keep | 0 | Jul | 2021 | 0.0096988 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-07-05 08:11 | 2021-07-05 11:41 | 75 | 003:30 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEASE RETIRO RAMAS SOBRE LAS LINEAS | A21070500026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2021-07-05 | 15750 | keep | 0 | Jul | 2021 | 0.010727 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
UTUADO | 2021-07-05 08:17 | 2021-07-06 13:49 | 50 | 029:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | A21070500032 | New_Event | Bad Weather | Include | Include | Weather | 1772 | 2021-07-05 | 88600 | keep | 0 | Jul | 2021 | 0.060345 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-07-05 08:19 | 2021-07-06 14:25 | 50 | 030:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADORES | M21070500045 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1806 | 2021-07-05 | 90300 | keep | 0 | Jul | 2021 | 0.061503 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-05 08:21 | 2021-07-05 15:30 | 80 | 007:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S21070500008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 429 | 2021-07-05 | 34320 | keep | 0 | Jul | 2021 | 0.023375 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
UTUADO | 2021-07-05 08:21 | 2021-07-05 19:00 | 150 | 010:39 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21070500034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 639 | 2021-07-05 | 95850 | keep | 0 | Jul | 2021 | 0.065283 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-07-05 08:27 | 2021-07-05 08:28 | 73 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21070500011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 73 | keep | 0 | Jul | 2021 | 4.972e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
MAYAGÃœEZ | 2021-07-05 08:30 | 2021-07-05 09:40 | 6 | 001:10 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070500053 | New_Event | Bad Weather | Include | Include | Weather | 70 | 2021-07-05 | 420 | keep | 0 | Jul | 2021 | 0.00028606 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
SAN JUAN | 2021-07-05 08:42 | 2021-07-05 17:10 | 4 | 008:28 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA SE PATRULLO | R21070500016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 508 | 2021-07-05 | 2032 | keep | 0 | Jul | 2021 | 0.001384 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
BAYAMON | 2021-07-05 08:42 | 2021-07-06 12:53 | 20 | 028:11 | P | DESGANCHE | 1 X 40 CORTE DE LINEA | B21070500009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1691 | 2021-07-05 | 33820 | keep | 0 | Jul | 2021 | 0.023035 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-07-05 08:43 | 2021-07-05 10:54 | 40 | 002:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21070500060 | New_Event | Bad Weather | Include | Include | Weather | 131 | 2021-07-05 | 5240 | keep | 0 | Jul | 2021 | 0.0035689 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-07-05 08:43 | 2021-07-05 18:27 | 100 | 009:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21070500048 | New_Event | Bad Weather | Include | Include | Weather | 584 | 2021-07-05 | 58400 | keep | 0 | Jul | 2021 | 0.039776 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-07-05 08:50 | 2021-07-08 18:00 | 65 | 081:10 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO DE 50 KVA X 50 KVA A 2400 | M21070500070 | New_Event | Service Transformer Failure | Include | Include | Equipment | 4870 | 2021-07-05 | 316550 | keep | 0 | Jul | 2021 | 0.2156 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
UTUADO | 2021-07-05 08:54 | 2021-07-05 16:05 | 100 | 007:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A21070500053 | New_Event | Cutout Failure | Include | Include | Equipment | 431 | 2021-07-05 | 43100 | keep | 0 | Jul | 2021 | 0.029355 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-05 08:56 | 2021-07-05 16:29 | 50 | 007:33 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21070500016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 453 | 2021-07-05 | 22650 | keep | 0 | Jul | 2021 | 0.015427 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-07-05 08:58 | 2021-07-07 15:45 | 15 | 054:47 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21070500056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3287 | 2021-07-05 | 49305 | keep | 0 | Jul | 2021 | 0.033581 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-07-05 08:59 | 2021-07-05 10:38 | 25 | 001:39 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21070500010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2021-07-05 | 2475 | keep | 0 | Jul | 2021 | 0.0016857 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
PONCE | 2021-07-05 08:59 | 2021-07-06 09:28 | 10 | 024:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTE DE LINEA ANIMAL CRUZO FACES | P21070500012 | New_Event |  |  | Include | Wildlife | 1469 | 2021-07-05 | 14690 | keep | 0 | Jul | 2021 | 0.010005 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-05 08:59 | 2021-07-06 17:55 | 80 | 032:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M21070500073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1976 | 2021-07-05 | 158080 | keep | 0 | Jul | 2021 | 0.10767 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-07-05 08:59 | 2021-07-05 09:16 | 1584 | 000:17 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO ABIERTO EN TRONCAL DEL ALIMENTADOR SE CERRO INTERRUPTOR | M21070400351 | Additional_clients | Wire Down | Include | Include | Equipment | 17 | 2021-07-05 | 26928 | keep | 0 | Jul | 2021 | 0.018341 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-07-05 09:01 | 2021-07-05 16:42 | 122 | 007:41 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | P21070500013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 461 | 2021-07-05 | 56242 | keep | 0 | Jul | 2021 | 0.038306 | 8.3094e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 122
CAGUAS | 2021-07-05 09:04 | 2021-07-07 12:48 | 6 | 051:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21070500057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 3104 | 2021-07-05 | 18624 | keep | 0 | Jul | 2021 | 0.012685 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2021-07-05 09:10 | 2021-07-05 18:23 | 24 | 009:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA QUEMADA | C21070500059 | New_Event | Cutout Failure | Include | Include | Equipment | 553 | 2021-07-05 | 13272 | keep | 0 | Jul | 2021 | 0.0090395 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
MAYAGÃœEZ | 2021-07-05 09:16 | 2021-07-05 10:45 | 100 | 001:29 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070400112 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 89 | 2021-07-05 | 8900 | keep | 0 | Jul | 2021 | 0.0060617 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-05 09:16 | 2021-07-05 12:38 | 80 | 003:22 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21070400016 | Partial_restoration | Bad Weather | Include | Include | Weather | 202 | 2021-07-05 | 16160 | keep | 0 | Jul | 2021 | 0.011007 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-07-05 09:26 | 2021-07-08 09:08 | 8 | 071:42 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REPARO Y RETESO SECUNDARIA Y UNA TOMA DE SERVICIO | S21070500022 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 4302 | 2021-07-05 | 34416 | keep | 0 | Jul | 2021 | 0.023441 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-07-05 09:35 | 2021-07-05 18:50 | 40 | 009:15 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | M21070500102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 555 | 2021-07-05 | 22200 | keep | 0 | Jul | 2021 | 0.01512 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-07-05 09:38 | 2021-07-05 17:10 | 100 | 007:32 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21070500064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 452 | 2021-07-05 | 45200 | keep | 0 | Jul | 2021 | 0.030786 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-07-05 09:46 | 2021-07-05 15:34 | 8 | 005:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LA LINEA SECUNDARIA | C21070500067 | New_Event | Secondary Wire Down | Include | Include | Equipment | 348 | 2021-07-05 | 2784 | keep | 0 | Jul | 2021 | 0.0018962 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-07-05 10:10 | 2021-07-05 21:00 | 60 | 010:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | M21070500115 | New_Event | Wire Down | Include | Include | Equipment | 650 | 2021-07-05 | 39000 | keep | 0 | Jul | 2021 | 0.026563 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-07-05 10:13 | 2021-07-05 14:35 | 20 | 004:22 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25KVA X 25KVA | C21070500073 | New_Event | Service Transformer Failure | Include | Include | Equipment | 262 | 2021-07-05 | 5240 | keep | 0 | Jul | 2021 | 0.0035689 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-07-05 10:19 | 2021-07-06 17:35 | 50 | 031:16 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M21070500122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1876 | 2021-07-05 | 93800 | keep | 0 | Jul | 2021 | 0.063887 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-05 10:33 | 2021-07-05 13:20 | 20 | 002:47 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B21070500016 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 167 | 2021-07-05 | 3340 | keep | 0 | Jul | 2021 | 0.0022749 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-07-05 10:34 | 2021-07-05 14:04 | 4 | 003:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A21070500084 | New_Event | Bad Weather | Include | Include | Weather | 210 | 2021-07-05 | 840 | keep | 0 | Jul | 2021 | 0.00057212 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-07-05 10:36 | 2021-07-08 12:08 | 1 | 073:32 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRAYOS SE CERRO PUENTE DE LINEA A CAJA Y SE CERRO GABINETE | S21070500034 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 4412 | 2021-07-05 | 4412 | keep | 0 | Jul | 2021 | 0.003005 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-07-05 10:37 | 2021-07-06 20:07 | 169 | 033:30 | P | ESTRUCTURA AVERIADA | 2 X 50 EN CORTES DE LINEA SE REEMPLAZO POSTE PARTIDO | R21070500024 | New_Event | Defective Pole | Include | Include | Equipment | 2010 | 2021-07-05 | 339690 | keep | 0 | Jul | 2021 | 0.23136 | 0.00011511 | Sustained | FALSE | TRUE | Not_TMED_Event | 169
ARECIBO | 2021-07-05 10:40 | 2021-07-05 11:59 | 8 | 001:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A21070500000 | New_Event | Wire Down | Include | Include | Equipment | 79 | 2021-07-05 | 632 | keep | 0 | Jul | 2021 | 0.00043045 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-07-05 11:08 | 2021-07-05 14:20 | 80 | 003:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21070500142 | New_Event | Bad Weather | Include | Include | Weather | 192 | 2021-07-05 | 15360 | keep | 0 | Jul | 2021 | 0.010462 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-07-05 11:17 | 2021-07-05 11:28 | 2450 | 000:11 | S | LINEA DE TRANSMISION 38KV | TRABAJOS EN LA LINEA 12600 | C21070500159 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2021-07-05 | 26950 | keep | 0 | Jul | 2021 | 0.018356 | 0.0016687 | Sustained | FALSE | TRUE | Not_TMED_Event | 2450
HUMACAO | 2021-07-05 11:17 | 2021-07-05 11:28 | 640 | 000:11 | S | LINEA DE TRANSMISION 38KV | TRABAJOS EN LA LINEA 12600 | C21070500159 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2021-07-05 | 7040 | keep | 0 | Jul | 2021 | 0.0047949 | 0.0004359 | Sustained | FALSE | TRUE | Not_TMED_Event | 640
BAYAMON | 2021-07-05 11:26 | 2021-07-05 11:27 | 1533 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO LLEVANDO LA CARGA DEL 1709-05 | S21070500043 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-07-05 | 1533 | keep | 0 | Jul | 2021 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
BAYAMON | 2021-07-05 11:26 | 2021-07-05 11:27 | 2364 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO CARGA POR EL 1709-03 | S21070500043 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-07-05 | 2364 | keep | 0 | Jul | 2021 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
BAYAMON | 2021-07-05 11:27 | 2021-07-05 13:15 | 100 | 001:48 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 200 EN CORTE DE LINEA SE REMPLAZO AISLADOR | S21070500043 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 108 | 2021-07-05 | 10800 | keep | 0 | Jul | 2021 | 0.0073558 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-07-05 11:28 | 2021-07-05 17:19 | 200 | 005:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE CON ANIMAL | C21070500172 | New_Event |  |  | Include | Wildlife | 351 | 2021-07-05 | 70200 | keep | 0 | Jul | 2021 | 0.047813 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-07-05 11:29 | 2021-07-05 14:27 | 200 | 002:58 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C21070500118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2021-07-05 | 35600 | keep | 0 | Jul | 2021 | 0.024247 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-07-05 11:32 | 2021-07-05 11:34 | 1715 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21070500022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-05 | 3430 | keep | 0 | Jul | 2021 | 0.0023362 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
HUMACAO | 2021-07-05 11:42 | 2021-07-05 16:57 | 200 | 005:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA BAJANTE CRUZADO | C21070500123 | New_Event | Wire Down | Include | Include | Equipment | 315 | 2021-07-05 | 63000 | keep | 0 | Jul | 2021 | 0.042909 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CANOVANAS | 2021-07-05 12:17 | 2021-07-05 15:18 | 3 | 003:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN CORTE DE LINEA CRUCE CON AVE | R21070500029 | New_Event |  |  | Include | Wildlife | 181 | 2021-07-05 | 543 | keep | 0 | Jul | 2021 | 0.00036983 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
SAN JUAN | 2021-07-05 12:19 | 2021-07-05 12:20 | 790 | 000:01 | T | DESGANCHE | RECIERRE | S21070500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-05 | 790 | keep | 0 | Jul | 2021 | 0.00053807 | 0.00053807 | Momentary | FALSE | FALSE | Not_TMED_Event | 790
SAN JUAN | 2021-07-05 12:20 | 2021-07-05 19:19 | 150 | 006:59 | P | DESGANCHE | 3 X 100 EN CORTE DE LINEA SE HIZO DESGANCHE Y PORTAFUSIBLE | S21070500058 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 419 | 2021-07-05 | 62850 | keep | 0 | Jul | 2021 | 0.042807 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-07-05 12:26 | 2021-07-05 12:53 | 30 | 000:27 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21070400051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 27 | 2021-07-05 | 810 | keep | 0 | Jul | 2021 | 0.00055169 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-07-05 12:26 | 2021-07-06 08:50 | 25 | 020:24 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21070500055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1224 | 2021-07-05 | 30600 | keep | 0 | Jul | 2021 | 0.020842 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CAGUAS | 2021-07-05 12:28 | 2021-07-05 20:48 | 3 | 008:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE SAFADO A TRANSFORMADOR | C21070500135 | New_Event | Wire Down | Include | Include | Equipment | 500 | 2021-07-05 | 1500 | keep | 0 | Jul | 2021 | 0.0010216 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2021-07-05 12:29 | 2021-07-05 12:30 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21070500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 1827 | keep | 0 | Jul | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
SAN JUAN | 2021-07-05 12:39 | 2021-07-05 12:40 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1206-03 | S21070500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 10211 | keep | 0 | Jul | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-07-05 12:39 | 2021-07-05 12:40 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 1204-05 | S21070500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 4133 | keep | 0 | Jul | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-07-05 12:41 | 2021-07-05 12:42 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1206-03 | S21070500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 10211 | keep | 0 | Jul | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-07-05 12:41 | 2021-07-05 12:42 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 1204-05 | S21070500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 4133 | keep | 0 | Jul | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
CAGUAS | 2021-07-05 12:41 | 2021-07-05 12:42 | 1702 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21070500000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-07-05 | 1702 | keep | 0 | Jul | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2021-07-05 12:42 | 2021-07-05 14:41 | 95 | 001:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA REEMPLAZO CAJA QUEMADA | C21070500170 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 119 | 2021-07-05 | 11305 | keep | 0 | Jul | 2021 | 0.0076998 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
CAGUAS | 2021-07-05 12:53 | 2021-07-05 14:00 | 3 | 001:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARO SECUNDARIA | C21070400105 | New_Event | Secondary Wire Down | Include | Include | Equipment | 67 | 2021-07-05 | 201 | keep | 0 | Jul | 2021 | 0.0001369 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2021-07-05 12:59 | 2021-07-05 22:15 | 50 | 009:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO ENREDADERA | A21070500105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 556 | 2021-07-05 | 27800 | keep | 0 | Jul | 2021 | 0.018934 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-05 13:03 | 2021-07-05 13:05 | 837 | 000:02 | T | OTRAS CAUSAS | SE CERRO POR SCADA CARGA POR EL 1401-07 | S21070500000 | New_Event | Other Causes | Include | Include | Other | 2 | 2021-07-05 | 1674 | keep | 0 | Jul | 2021 | 0.0011402 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2021-07-05 13:03 | 2021-07-05 13:05 | 908 | 000:02 | T | OTRAS CAUSAS | SE CERRO POR SCADA LLEVA 1401-06 | S21070500000 | New_Event | Other Causes | Include | Include | Other | 2 | 2021-07-05 | 1816 | keep | 0 | Jul | 2021 | 0.0012369 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
SAN JUAN | 2021-07-05 13:05 | 2021-07-06 00:13 | 75 | 011:08 | P | OTRAS CAUSAS | 2 X 65 EN CORTE DE LINEA PROBO MALO HACIA PARQUE Y SE DEJO FUERA PROA | S21070500194 | 1st_after_momentary | Other Causes | Include | Include | Other | 668 | 2021-07-05 | 50100 | keep | 0 | Jul | 2021 | 0.034123 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
ARECIBO | 2021-07-05 13:17 | 2021-07-05 21:34 | 15 | 008:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A21070500107 | New_Event | Bad Weather | Include | Include | Weather | 497 | 2021-07-05 | 7455 | keep | 0 | Jul | 2021 | 0.0050776 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-07-05 13:19 | 2021-07-05 13:20 | 4622 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21070500026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 4622 | keep | 0 | Jul | 2021 | 0.003148 | 0.003148 | Momentary | FALSE | FALSE | Not_TMED_Event | 4622
BAYAMON | 2021-07-05 13:20 | 2021-07-05 14:44 | 60 | 001:24 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | B21070500028 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 84 | 2021-07-05 | 5040 | keep | 0 | Jul | 2021 | 0.0034327 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-07-05 13:20 | 2021-07-05 18:29 | 8 | 005:09 | P | DESGANCHE | SE REALIZO DESGANCHE CRITICO Y SE REPARO BAJANTE ZAFADO HACIA TRANSFORMADOR | C21070500146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 309 | 2021-07-05 | 2472 | keep | 0 | Jul | 2021 | 0.0016837 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2021-07-05 13:21 | 2021-07-06 10:09 | 18 | 020:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA AVERIADA | M21070500200 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1248 | 2021-07-05 | 22464 | keep | 0 | Jul | 2021 | 0.0153 | 1.226e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 18
SAN JUAN | 2021-07-05 13:22 | 2021-07-05 20:47 | 80 | 007:25 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21070400056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 445 | 2021-07-05 | 35600 | keep | 0 | Jul | 2021 | 0.024247 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-07-05 13:30 | 2021-07-05 20:44 | 34 | 007:14 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25KVA X 25KVA QUEMADO | C21070500149 | New_Event | Service Transformer Failure | Include | Include | Equipment | 434 | 2021-07-05 | 14756 | keep | 0 | Jul | 2021 | 0.01005 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
BAYAMON | 2021-07-05 13:43 | 2021-07-05 15:39 | 26 | 001:56 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21070500001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2021-07-05 | 3016 | keep | 0 | Jul | 2021 | 0.0020542 | 1.7708e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 26
ARECIBO | 2021-07-05 13:44 | 2021-07-05 18:45 | 100 | 005:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21070500112 | New_Event | Bad Weather | Include | Include | Weather | 301 | 2021-07-05 | 30100 | keep | 0 | Jul | 2021 | 0.020501 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-07-05 13:45 | 2021-07-07 10:51 | 10 | 045:06 | P | TRANSFORMADOR AVERIADO | CAMBIO DE TRANSFORMADOR DE 25KVA X 25 KVA POR ESCAPE DE ACEITE | M21070500208 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2706 | 2021-07-05 | 27060 | keep | 0 | Jul | 2021 | 0.01843 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-05 13:51 | 2021-07-05 13:53 | 1983 | 000:02 | T | DESGANCHE | INTERRUPTOR DISPARO Y SE CERRO POR CONTROL | B21070500032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-07-05 | 3966 | keep | 0 | Jul | 2021 | 0.0027012 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-07-05 13:51 | 2021-07-05 13:53 | 186 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR Y SE CERRO POR CONTROL | B21070500032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-05 | 372 | keep | 0 | Jul | 2021 | 0.00025337 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2021-07-05 13:53 | 2021-07-06 11:34 | 8 | 021:41 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR | B21070500052 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1301 | 2021-07-05 | 10408 | keep | 0 | Jul | 2021 | 0.0070888 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2021-07-05 13:59 | 2021-07-05 14:00 | 1182 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210705000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 1182 | keep | 0 | Jul | 2021 | 0.00080505 | 0.00080505 | Momentary | FALSE | FALSE | Not_TMED_Event | 1182
ARECIBO | 2021-07-05 14:17 | 2021-07-06 10:00 | 50 | 019:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | A21070500125 | New_Event | Bad Weather | Include | Include | Weather | 1183 | 2021-07-05 | 59150 | keep | 0 | Jul | 2021 | 0.040287 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BARRANQUITAS | 2021-07-05 14:19 | 2021-07-05 14:57 | 200 | 000:38 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA LLUVIAS | C21070500157 | New_Event | Bad Weather | Include | Include | Weather | 38 | 2021-07-05 | 7600 | keep | 0 | Jul | 2021 | 0.0051763 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
VEGA BAJA | 2021-07-05 14:28 | 2021-07-05 20:45 | 30 | 006:17 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21070500012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 377 | 2021-07-05 | 11310 | keep | 0 | Jul | 2021 | 0.0077032 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
GUAYAMA | 2021-07-05 14:29 | 2021-07-05 16:54 | 12 | 002:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR EXCAVANDO EN AVERIA SECUNDARIA | P21070500037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 145 | 2021-07-05 | 1740 | keep | 0 | Jul | 2021 | 0.0011851 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-07-05 14:35 | 2021-07-06 13:30 | 10 | 022:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 10 EN TRANSFORMADOR REMPLAZO 2 CAJAS QUEMADAS Y LOS BAJANTES PRIMARIOS | C21070500159 | New_Event | Cutout Failure | Include | Include | Equipment | 1375 | 2021-07-05 | 13750 | keep | 0 | Jul | 2021 | 0.0093651 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-07-05 14:41 | 2021-07-05 14:42 | 1702 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21070400000 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2021-07-05 | 1702 | keep | 0 | Jul | 2021 | 0.0011592 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-07-05 14:42 | 2021-07-05 14:47 | 95 | 000:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA REEMPLAZO CAJA QUEMADA | C21070500170 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 5 | 2021-07-05 | 475 | keep | 0 | Jul | 2021 | 0.00032352 | 6.4704e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 95
BAYAMON | 2021-07-05 14:44 | 2021-07-05 14:45 | 4622 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21070500000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 4622 | keep | 0 | Jul | 2021 | 0.003148 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-05 14:45 | 2021-07-05 17:58 | 60 | 003:13 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | B21070500028 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 193 | 2021-07-05 | 11580 | keep | 0 | Jul | 2021 | 0.0078871 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-07-05 14:47 | 2021-07-05 14:48 | 1702 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21070400000 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2021-07-05 | 1702 | keep | 0 | Jul | 2021 | 0.0011592 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-07-05 14:48 | 2021-07-05 14:52 | 95 | 000:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA REEMPLAZO CAJA QUEMADA | C21070500170 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 4 | 2021-07-05 | 380 | keep | 0 | Jul | 2021 | 0.00025882 | 6.4704e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 95
CAGUAS | 2021-07-05 14:52 | 2021-07-05 14:53 | 1702 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21070400000 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1 | 2021-07-05 | 1702 | keep | 0 | Jul | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2021-07-05 14:53 | 2021-07-05 15:04 | 95 | 000:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA REEMPLAZO CAJA QUEMADA | C21070500170 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 11 | 2021-07-05 | 1045 | keep | 0 | Jul | 2021 | 0.00071174 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
BAYAMON | 2021-07-05 15:03 | 2021-07-06 10:11 | 20 | 019:08 | P | DESGANCHE | 1 X 40 CORTE DE LINEA | B21070500039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1148 | 2021-07-05 | 22960 | keep | 0 | Jul | 2021 | 0.015638 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-07-05 15:04 | 2021-07-05 20:42 | 1825 | 005:38 | S | LINEA DE TRANSMISION 115KV | SE RETIRA CARGA SUB 1343 PARA CERRAR PUENTE PRIMARIO LINEA 3000 | S21070500182 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 338 | 2021-07-05 | 616850 | keep | 0 | Jul | 2021 | 0.42013 | 0.001243 | Sustained | FALSE | TRUE | Not_TMED_Event | 1825
SAN JUAN | 2021-07-05 15:04 | 2021-07-05 20:42 | 47 | 005:38 | S | LINEA DE TRANSMISION 115KV | SE RETIRA CARGA SUB 1343 PARA CERRAR PUENTE PRIMARIO LINEA 3000 | S21070500182 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 338 | 2021-07-05 | 15886 | keep | 0 | Jul | 2021 | 0.01082 | 3.2011e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 47
SAN JUAN | 2021-07-05 15:04 | 2021-07-05 20:42 | 315 | 005:38 | S | LINEA DE TRANSMISION 115KV | SE RETIRA CARGA SUB 1343 PARA CERRAR PUENTE PRIMARIO LINEA 3000 | S21070500182 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 338 | 2021-07-05 | 106470 | keep | 0 | Jul | 2021 | 0.072516 | 0.00021455 | Sustained | FALSE | TRUE | Not_TMED_Event | 315
SAN JUAN | 2021-07-05 15:04 | 2021-07-05 20:42 | 2 | 005:38 | S | LINEA DE TRANSMISION 115KV | SE RETIRA CARGA SUB 1343 PARA CERRAR PUENTE PRIMARIO LINEA 3000 | S21070500182 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 338 | 2021-07-05 | 676 | keep | 0 | Jul | 2021 | 0.00046042 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
SAN JUAN | 2021-07-05 15:04 | 2021-07-05 20:42 | 2391 | 005:38 | S | LINEA DE TRANSMISION 115KV | SE RETIRA CARGA SUB 1343 PARA CERRAR PUENTE PRIMARIO LINEA 3000 | S21070500182 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 338 | 2021-07-05 | 808158 | keep | 0 | Jul | 2021 | 0.55043 | 0.0016285 | Sustained | FALSE | TRUE | Not_TMED_Event | 2391
CAGUAS | 2021-07-05 15:04 | 2021-07-05 15:05 | 1702 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21070400000 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2021-07-05 | 1702 | keep | 0 | Jul | 2021 | 0.0011592 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-07-05 15:05 | 2021-07-05 22:20 | 95 | 007:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA REEMPLAZO CAJA QUEMADA | C21070500170 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 435 | 2021-07-05 | 41325 | keep | 0 | Jul | 2021 | 0.028146 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
CANOVANAS | 2021-07-05 15:09 | 2021-07-05 16:40 | 30 | 001:31 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R21070500035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2021-07-05 | 2730 | keep | 0 | Jul | 2021 | 0.0018594 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
VEGA BAJA | 2021-07-05 15:12 | 2021-07-05 19:28 | 50 | 004:16 | P | TRANSFORMADOR AVERIADO | SE REMPLAZARON 2 TRANSFORMADORES AVERIADOS DE 100KVA POR 2 DE IGUAL CAPACIDAD | B21070400023 | New_Event | Service Transformer Failure | Include | Include | Equipment | 256 | 2021-07-05 | 12800 | keep | 0 | Jul | 2021 | 0.008718 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-07-05 15:18 | 2021-07-05 18:50 | 569 | 003:32 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21070500242 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 212 | 2021-07-05 | 120628 | keep | 0 | Jul | 2021 | 0.082159 | 0.00038754 | Sustained | FALSE | TRUE | Not_TMED_Event | 569
AGUADILLA | 2021-07-05 15:18 | 2021-07-05 18:50 | 1245 | 003:32 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21070500242 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 212 | 2021-07-05 | 263940 | keep | 0 | Jul | 2021 | 0.17977 | 0.00084796 | Sustained | FALSE | TRUE | Not_TMED_Event | 1245
AGUADILLA | 2021-07-05 15:18 | 2021-07-05 18:50 | 1155 | 003:32 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21070500242 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 212 | 2021-07-05 | 244860 | keep | 0 | Jul | 2021 | 0.16677 | 0.00078667 | Sustained | FALSE | TRUE | Not_TMED_Event | 1155
AGUADILLA | 2021-07-05 15:18 | 2021-07-05 18:50 | 867 | 003:32 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21070500244 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 212 | 2021-07-05 | 183804 | keep | 0 | Jul | 2021 | 0.12519 | 0.00059051 | Sustained | FALSE | TRUE | Not_TMED_Event | 867
AGUADILLA | 2021-07-05 15:18 | 2021-07-05 18:50 | 257 | 003:32 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21070500244 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 212 | 2021-07-05 | 54484 | keep | 0 | Jul | 2021 | 0.037109 | 0.00017504 | Sustained | FALSE | TRUE | Not_TMED_Event | 257
AGUADILLA | 2021-07-05 15:18 | 2021-07-05 18:50 | 1336 | 003:32 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21070500244 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 212 | 2021-07-05 | 283232 | keep | 0 | Jul | 2021 | 0.19291 | 0.00090994 | Sustained | FALSE | TRUE | Not_TMED_Event | 1336
AGUADILLA | 2021-07-05 15:18 | 2021-07-05 18:50 | 3315 | 003:32 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21070500245 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 212 | 2021-07-05 | 702780 | keep | 0 | Jul | 2021 | 0.47866 | 0.0022578 | Sustained | FALSE | TRUE | Not_TMED_Event | 3315
AGUADILLA | 2021-07-05 15:18 | 2021-07-05 18:50 | 1718 | 003:32 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21070500245 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 212 | 2021-07-05 | 364216 | keep | 0 | Jul | 2021 | 0.24807 | 0.0011701 | Sustained | FALSE | TRUE | Not_TMED_Event | 1718
ARECIBO | 2021-07-05 15:34 | 2021-07-05 17:45 | 15 | 002:11 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A21070500142 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 131 | 2021-07-05 | 1965 | keep | 0 | Jul | 2021 | 0.0013384 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
UTUADO | 2021-07-05 15:40 | 2021-07-06 15:15 | 25 | 023:35 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | A21070500144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1415 | 2021-07-05 | 35375 | keep | 0 | Jul | 2021 | 0.024094 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-07-05 15:44 | 2021-07-05 15:45 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21070500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 3431 | keep | 0 | Jul | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2021-07-05 15:47 | 2021-07-05 15:48 | 2201 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21070500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 2201 | keep | 0 | Jul | 2021 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2021-07-05 15:51 | 2021-07-05 15:52 | 2201 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21070500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 2201 | keep | 0 | Jul | 2021 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
HUMACAO | 2021-07-05 15:52 | 2021-07-05 18:12 | 60 | 002:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIAS | C21070500180 | New_Event | Bad Weather | Include | Include | Weather | 140 | 2021-07-05 | 8400 | keep | 0 | Jul | 2021 | 0.0057212 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-07-05 15:56 | 2021-07-05 15:57 | 2201 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21070500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 2201 | keep | 0 | Jul | 2021 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2021-07-05 15:58 | 2021-07-05 15:59 | 2201 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21070500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 2201 | keep | 0 | Jul | 2021 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
HUMACAO | 2021-07-05 16:02 | 2021-07-07 16:49 | 23 | 048:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA SE LEVANTO CONDUCTOR DEL SUELO | C21070600033 | New_Event | Wire Down | Include | Include | Equipment | 2927 | 2021-07-05 | 67321 | keep | 0 | Jul | 2021 | 0.045852 | 1.5665e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 23
ARECIBO | 2021-07-05 16:02 | 2021-07-05 16:03 | 2201 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21070500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 2201 | keep | 0 | Jul | 2021 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
AGUADILLA | 2021-07-05 16:07 | 2021-07-05 21:00 | 100 | 004:53 | P | PARARRAYOS DEFECTUOSO | 2 X 80 EN CORTE DE LINEA PARARRAYO | M21070500266 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 293 | 2021-07-05 | 29300 | keep | 0 | Jul | 2021 | 0.019956 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-07-05 16:07 | 2021-07-05 16:08 | 2201 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21070500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 2201 | keep | 0 | Jul | 2021 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2021-07-05 16:12 | 2021-07-05 16:13 | 2201 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21070500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 2201 | keep | 0 | Jul | 2021 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
CANOVANAS | 2021-07-05 16:13 | 2021-07-05 18:22 | 12 | 002:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | R21070500045 | New_Event | Cutout Failure | Include | Include | Equipment | 129 | 2021-07-05 | 1548 | keep | 0 | Jul | 2021 | 0.0010543 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
SAN JUAN | 2021-07-05 16:25 | 2021-07-05 17:45 | 15 | 001:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR CONECTORES SECUNDARIOS | S21070200038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 80 | 2021-07-05 | 1200 | keep | 0 | Jul | 2021 | 0.00081731 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-07-05 16:36 | 2021-07-06 15:49 | 99 | 023:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE CON AVE | R21070500046 | New_Event |  |  | Include | Wildlife | 1393 | 2021-07-05 | 137907 | keep | 0 | Jul | 2021 | 0.093928 | 6.7428e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 99
BAYAMON | 2021-07-05 16:51 | 2021-07-05 19:42 | 30 | 002:51 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21070400064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2021-07-05 | 5130 | keep | 0 | Jul | 2021 | 0.003494 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
HUMACAO | 2021-07-05 16:57 | 2021-07-05 17:19 | 2450 | 000:22 | S | LINEA DE TRANSMISION 38KV | OPERACIONES EN LA LINEA 12600 | C21070500034 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2021-07-05 | 53900 | keep | 0 | Jul | 2021 | 0.036711 | 0.0016687 | Sustained | FALSE | TRUE | Not_TMED_Event | 2450
HUMACAO | 2021-07-05 16:57 | 2021-07-05 17:19 | 640 | 000:22 | S | LINEA DE TRANSMISION 38KV | OPERACIONES EN LA LINEA 12600 | C21070500034 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2021-07-05 | 14080 | keep | 0 | Jul | 2021 | 0.0095898 | 0.0004359 | Sustained | FALSE | TRUE | Not_TMED_Event | 640
BAYAMON | 2021-07-05 17:03 | 2021-07-06 09:17 | 27 | 016:14 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21070500050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 974 | 2021-07-05 | 26298 | keep | 0 | Jul | 2021 | 0.017911 | 1.839e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 27
HUMACAO | 2021-07-05 17:19 | 2021-07-05 19:20 | 200 | 002:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA BAJANTE CRUZADO | C21070500123 | Partial_restoration | Wire Down | Include | Include | Equipment | 121 | 2021-07-05 | 24200 | keep | 0 | Jul | 2021 | 0.016483 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-05 17:20 | 2021-07-05 18:15 | 50 | 000:55 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21070500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2021-07-05 | 2750 | keep | 0 | Jul | 2021 | 0.001873 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-05 17:35 | 2021-07-05 17:36 | 271 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21070500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 271 | keep | 0 | Jul | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
MAYAGÃœEZ | 2021-07-05 17:45 | 2021-07-05 17:47 | 3458 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON RECIERRE EN OFF CERRADO POR SCADA | M21070500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-05 | 6916 | keep | 0 | Jul | 2021 | 0.0047105 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
MAYAGÃœEZ | 2021-07-05 18:27 | 2021-07-05 18:48 | 6285 | 000:21 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR A PETICION DE ING FENEQUE PARA RETIRAR BAMBUA SOBRE LINEA 2500 | M21070500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2021-07-05 | 131985 | keep | 0 | Jul | 2021 | 0.089894 | 0.0042807 | Sustained | FALSE | TRUE | Not_TMED_Event | 6285
CAGUAS | 2021-07-05 18:28 | 2021-07-05 18:33 | 1606 | 000:05 | T | CABLE SOTERRADO AVERIADO | DISPARO SE VERIFICO PERSONAL FUERA | C21070500000 | New_Event | UG Cable Fault | Include | Include | Equipment | 5 | 2021-07-05 | 8030 | keep | 0 | Jul | 2021 | 0.0054692 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
CAGUAS | 2021-07-05 18:33 | 2021-07-05 18:55 | 100 | 000:22 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL HACIA EL T-38 | C21070500034 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 22 | 2021-07-05 | 2200 | keep | 0 | Jul | 2021 | 0.0014984 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-07-05 18:44 | 2021-07-05 19:20 | 3 | 000:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A21070500000 | New_Event | Wire Down | Include | Include | Equipment | 36 | 2021-07-05 | 108 | keep | 0 | Jul | 2021 | 7.3558e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-07-05 18:44 | 2021-07-06 12:07 | 25 | 017:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA | M21070500325 | New_Event | Wire Down | Include | Include | Equipment | 1043 | 2021-07-05 | 26075 | keep | 0 | Jul | 2021 | 0.01776 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-07-05 18:48 | 2021-07-05 19:40 | 100 | 000:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21070500048 | New_Event | Bad Weather | Include | Include | Weather | 52 | 2021-07-05 | 5200 | keep | 0 | Jul | 2021 | 0.0035417 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-07-05 18:48 | 2021-07-06 15:45 | 150 | 020:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 Y 1 X 30 EN CORTES DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21070500004 | New_Event | Bad Weather | Include | Include | Weather | 1257 | 2021-07-05 | 188550 | keep | 0 | Jul | 2021 | 0.12842 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-07-05 18:48 | 2021-07-05 20:00 | 80 | 001:12 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21070500189 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2021-07-05 | 5760 | keep | 0 | Jul | 2021 | 0.0039231 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
AGUADILLA | 2021-07-05 18:50 | 2021-07-05 22:10 | 80 | 003:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA | M21070500215 | New_Event | Wire Down | Include | Include | Equipment | 200 | 2021-07-05 | 16000 | keep | 0 | Jul | 2021 | 0.010898 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CANOVANAS | 2021-07-05 18:55 | 2021-07-06 11:49 | 5 | 016:54 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE | R21070500051 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1014 | 2021-07-05 | 5070 | keep | 0 | Jul | 2021 | 0.0034532 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-07-05 18:55 | 2021-07-05 19:36 | 1606 | 000:41 | T | CABLE SOTERRADO AVERIADO | DISPARO SE VERIFICO PERSONAL FUERA | C21070500000 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 41 | 2021-07-05 | 65846 | keep | 0 | Jul | 2021 | 0.044847 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-05 19:06 | 2021-07-06 14:51 | 20 | 019:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA SE CERRO PUENTE Y SE REMPLAZO PARARRAYOS | S21070300177 | New_Event | Cutout Failure | Include | Include | Equipment | 1185 | 2021-07-05 | 23700 | keep | 0 | Jul | 2021 | 0.016142 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-07-05 19:28 | 2021-07-05 19:30 | 3701 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C21070500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-05 | 7402 | keep | 0 | Jul | 2021 | 0.0050415 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
CAGUAS | 2021-07-05 19:36 | 2021-07-06 21:42 | 100 | 026:06 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL HACIA EL T-38 | C21070500034 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1566 | 2021-07-05 | 156600 | keep | 0 | Jul | 2021 | 0.10666 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-07-05 19:43 | 2021-07-05 19:44 | 3701 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C21070500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 3701 | keep | 0 | Jul | 2021 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
CAGUAS | 2021-07-05 19:46 | 2021-07-05 20:39 | 2276 | 000:53 | S | LINEA DE TRANSMISION 38KV | OPERACIONES EN LA LINEA 3000 | C21070500222 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 53 | 2021-07-05 | 120628 | keep | 0 | Jul | 2021 | 0.082159 | 0.0015502 | Sustained | FALSE | TRUE | Not_TMED_Event | 2276
CAGUAS | 2021-07-05 19:46 | 2021-07-05 20:39 | 777 | 000:53 | S | LINEA DE TRANSMISION 38KV | OPERACIONES EN LA LINEA 3000 | C21070500222 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 53 | 2021-07-05 | 41181 | keep | 0 | Jul | 2021 | 0.028048 | 0.00052921 | Sustained | FALSE | TRUE | Not_TMED_Event | 777
CAGUAS | 2021-07-05 19:46 | 2021-07-05 20:39 | 12 | 000:53 | S | LINEA DE TRANSMISION 38KV | OPERACIONES EN LA LINEA 3000 | C21070500222 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 53 | 2021-07-05 | 636 | keep | 0 | Jul | 2021 | 0.00043318 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
CAGUAS | 2021-07-05 19:46 | 2021-07-05 20:39 | 1290 | 000:53 | S | LINEA DE TRANSMISION 38KV | OPERACIONES EN LA LINEA 3000 | C21070500222 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 53 | 2021-07-05 | 68370 | keep | 0 | Jul | 2021 | 0.046566 | 0.00087861 | Sustained | FALSE | TRUE | Not_TMED_Event | 1290
MAYAGÃœEZ | 2021-07-05 19:47 | 2021-07-06 17:40 | 25 | 021:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M21070500350 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1313 | 2021-07-05 | 32825 | keep | 0 | Jul | 2021 | 0.022357 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
HUMACAO | 2021-07-05 20:02 | 2021-07-05 20:04 | 3701 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C21070500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-05 | 7402 | keep | 0 | Jul | 2021 | 0.0050415 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
SAN JUAN | 2021-07-05 20:34 | 2021-07-05 20:35 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21070500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 3046 | keep | 0 | Jul | 2021 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
CAGUAS | 2021-07-05 20:34 | 2021-07-05 20:36 | 853 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C21070500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-05 | 1706 | keep | 0 | Jul | 2021 | 0.0011619 | 0.00058097 | Momentary | FALSE | FALSE | Not_TMED_Event | 853
VEGA BAJA | 2021-07-05 20:59 | 2021-07-06 11:16 | 15 | 014:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 CORTE DE LINEA Y SE LLEVO BAJANTE A LA CAJA | B21070500061 | New_Event | Wire Down | Include | Include | Equipment | 857 | 2021-07-05 | 12855 | keep | 0 | Jul | 2021 | 0.0087555 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CAGUAS | 2021-07-05 21:00 | 2021-07-05 21:01 | 1742 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21070500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 1742 | keep | 0 | Jul | 2021 | 0.0011865 | 0.0011865 | Momentary | FALSE | FALSE | Not_TMED_Event | 1742
HUMACAO | 2021-07-05 21:04 | 2021-07-05 22:13 | 3701 | 001:09 | T | NO SE REPORTO CAUSA | SE PATRULLO NO SE ENCONTRO CAUSA DE AVERIA | C21070500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 69 | 2021-07-05 | 255369 | keep | 0 | Jul | 2021 | 0.17393 | 0.0025207 | Sustained | FALSE | FALSE | Not_TMED_Event | 3701
SAN JUAN | 2021-07-05 21:29 | 2021-07-05 21:31 | 2391 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO | S21070500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-05 | 4782 | keep | 0 | Jul | 2021 | 0.003257 | 0.0016285 | Momentary | FALSE | FALSE | Not_TMED_Event | 2391
MAYAGÃœEZ | 2021-07-05 21:31 | 2021-07-05 21:32 | 281 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21070500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-05 | 281 | keep | 0 | Jul | 2021 | 0.00019139 | 0.00019139 | Momentary | FALSE | TRUE | Not_TMED_Event | 281
MAYAGÃœEZ | 2021-07-05 21:31 | 2021-07-05 21:32 | 1252 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21070500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-05 | 1252 | keep | 0 | Jul | 2021 | 0.00085273 | 0.00085273 | Momentary | FALSE | TRUE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2021-07-05 21:31 | 2021-07-05 21:32 | 595 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21070500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-05 | 595 | keep | 0 | Jul | 2021 | 0.00040525 | 0.00040525 | Momentary | FALSE | TRUE | Not_TMED_Event | 595
MAYAGÃœEZ | 2021-07-05 21:31 | 2021-07-05 21:32 | 51 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21070500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-05 | 51 | keep | 0 | Jul | 2021 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 51
MAYAGÃœEZ | 2021-07-05 21:31 | 2021-07-05 21:32 | 721 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21070500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-05 | 721 | keep | 0 | Jul | 2021 | 0.00049107 | 0.00049107 | Momentary | FALSE | TRUE | Not_TMED_Event | 721
UTUADO | 2021-07-05 21:31 | 2021-07-05 21:32 | 1382 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DELINEA 8100 | A21070500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-05 | 1382 | keep | 0 | Jul | 2021 | 0.00094127 | 0.00094127 | Momentary | FALSE | TRUE | Not_TMED_Event | 1382
UTUADO | 2021-07-05 21:31 | 2021-07-05 21:32 | 654 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DELINEA 8100 | A21070500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-05 | 654 | keep | 0 | Jul | 2021 | 0.00044544 | 0.00044544 | Momentary | FALSE | TRUE | Not_TMED_Event | 654
MAYAGÃœEZ | 2021-07-05 21:33 | 2021-07-06 21:17 | 200 | 023:44 | P | DESGANCHE | 1 X 100, 1 X 80, 1 X 65, 1 X 50 Y 1 X 30 EN DISTINTOS CORTES DE LINEA SE REALIZO DESGANCHE MASIVO | M21070500357 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1424 | 2021-07-05 | 284800 | keep | 0 | Jul | 2021 | 0.19398 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-07-05 21:33 | 2021-07-06 10:52 | 50 | 013:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA | A21070500215 | New_Event | Bad Weather | Include | Include | Weather | 799 | 2021-07-05 | 39950 | keep | 0 | Jul | 2021 | 0.02721 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-07-05 22:23 | 2021-07-05 23:03 | 3701 | 000:40 | T | NO SE REPORTO CAUSA | SE PATRULLO Y SECCIONALIZO INTERRUPTOR POR TRAMO NO SE ENCONTRO CAUSA DE AVERIA | C21070500000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 40 | 2021-07-05 | 148040 | keep | 0 | Jul | 2021 | 0.10083 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-05 22:43 | 2021-07-06 16:25 | 80 | 017:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE RETEZO LINEAS PRIMARIAS | M21070500361 | New_Event | Wire Down | Include | Include | Equipment | 1062 | 2021-07-05 | 84960 | keep | 0 | Jul | 2021 | 0.057866 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-07-05 23:39 | 2021-07-09 09:19 | 20 | 081:40 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21070500204 | New_Event | Vegetation Contact | Include | Include | Vegetation | 4900 | 2021-07-05 | 98000 | keep | 0 | Jul | 2021 | 0.066747 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CANOVANAS | 2021-07-05 23:56 | 2021-07-05 23:57 | 4188 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21070500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-05 | 4188 | keep | 0 | Jul | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
ARECIBO | 2021-07-06 00:11 | 2021-07-06 09:48 | 15 | 009:37 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA REPUSO PARARRAYO | A21070600001 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 577 | 2021-07-06 | 8655 | keep | 0 | Jul | 2021 | 0.0058949 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CANOVANAS | 2021-07-06 01:03 | 2021-07-06 01:04 | 4188 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21070600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-06 | 4188 | keep | 0 | Jul | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
HUMACAO | 2021-07-06 01:41 | 2021-07-06 01:45 | 676 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV LAS PIEDRAS | C21070600010 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2021-07-06 | 2704 | keep | 0 | Jul | 2021 | 0.0018417 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
HUMACAO | 2021-07-06 01:41 | 2021-07-06 01:45 | 2873 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV LAS PIEDRAS | C21070600010 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2021-07-06 | 11492 | keep | 0 | Jul | 2021 | 0.0078271 | 0.0019568 | Momentary | FALSE | FALSE | Not_TMED_Event | 2873
HUMACAO | 2021-07-06 01:41 | 2021-07-06 01:45 | 3902 | 000:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV LAS PIEDRAS | C21070600010 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2021-07-06 | 15608 | keep | 0 | Jul | 2021 | 0.010631 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
HUMACAO | 2021-07-06 01:49 | 2021-07-06 01:52 | 676 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV LAS PIEDRAS | C21070600010 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-07-06 | 2028 | keep | 0 | Jul | 2021 | 0.0013813 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
HUMACAO | 2021-07-06 01:49 | 2021-07-06 01:52 | 2873 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV LAS PIEDRAS | C21070600010 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-07-06 | 8619 | keep | 0 | Jul | 2021 | 0.0058704 | 0.0019568 | Momentary | FALSE | FALSE | Not_TMED_Event | 2873
HUMACAO | 2021-07-06 01:49 | 2021-07-06 01:52 | 3902 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV LAS PIEDRAS | C21070600010 | 1st_after_momentary | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-07-06 | 11706 | keep | 0 | Jul | 2021 | 0.0079729 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
MAYAGÃœEZ | 2021-07-06 01:58 | 2021-07-06 14:35 | 200 | 012:37 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M21070600003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 757 | 2021-07-06 | 151400 | keep | 0 | Jul | 2021 | 0.10312 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-07-06 02:49 | 2021-07-06 02:50 | 6136 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR EL 1709-01 | S21070600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-06 | 6136 | keep | 0 | Jul | 2021 | 0.0041792 | 0.0041792 | Momentary | FALSE | FALSE | Not_TMED_Event | 6136
BAYAMON | 2021-07-06 03:40 | 2021-07-06 16:06 | 12 | 012:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | B21070600001 | New_Event | Cutout Failure | Include | Include | Equipment | 746 | 2021-07-06 | 8952 | keep | 0 | Jul | 2021 | 0.0060972 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-07-06 03:55 | 2021-07-07 08:41 | 7 | 028:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21070600005 | New_Event | Bad Weather | Include | Include | Weather | 1726 | 2021-07-06 | 12082 | keep | 0 | Jul | 2021 | 0.008229 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2021-07-06 04:00 | 2021-07-06 12:00 | 80 | 008:00 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R21070600005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 480 | 2021-07-06 | 38400 | keep | 0 | Jul | 2021 | 0.026154 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-07-06 04:11 | 2021-07-06 04:12 | 1271 | 000:01 | T | DESGANCHE | RECIERRE | C21070600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-06 | 1271 | keep | 0 | Jul | 2021 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
CAGUAS | 2021-07-06 04:12 | 2021-07-07 09:55 | 25 | 029:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21070600019 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1783 | 2021-07-06 | 44575 | keep | 0 | Jul | 2021 | 0.03036 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-07-06 04:25 | 2021-07-06 11:50 | 8 | 007:25 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21070600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 445 | 2021-07-06 | 3560 | keep | 0 | Jul | 2021 | 0.0024247 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-07-06 04:45 | 2021-07-06 15:12 | 50 | 010:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | B21070600003 | New_Event | Cutout Failure | Include | Include | Equipment | 627 | 2021-07-06 | 31350 | keep | 0 | Jul | 2021 | 0.021352 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-06 04:51 | 2021-07-09 09:44 | 1 | 076:53 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | S21070600009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4613 | 2021-07-06 | 4613 | keep | 0 | Jul | 2021 | 0.0031419 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-07-06 05:04 | 2021-07-06 05:05 | 1569 | 000:01 | T | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | RECIERRE | C21070600000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1 | 2021-07-06 | 1569 | keep | 0 | Jul | 2021 | 0.0010686 | 0.0010686 | Momentary | FALSE | FALSE | Not_TMED_Event | 1569
CAGUAS | 2021-07-06 05:05 | 2021-07-07 11:03 | 6 | 029:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR REPARO SECUNDARIA | C21070600083 | 1st_after_momentary | Secondary Wire Down | Include | Include | Equipment | 1798 | 2021-07-06 | 10788 | keep | 0 | Jul | 2021 | 0.0073477 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-07-06 05:16 | 2021-07-06 14:54 | 1 | 009:38 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO AISLADOR ROTO | C21070600009 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 578 | 2021-07-06 | 578 | keep | 0 | Jul | 2021 | 0.00039367 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-07-06 05:29 | 2021-07-06 05:30 | 1827 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C21070600000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-06 | 1827 | keep | 0 | Jul | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
HUMACAO | 2021-07-06 05:30 | 2021-07-06 07:35 | 827 | 002:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTO CONDUCTOR Y CERRO MACHETES | C21070600011 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 125 | 2021-07-06 | 103375 | keep | 0 | Jul | 2021 | 0.070408 | 0.00056327 | Sustained | FALSE | FALSE | Not_TMED_Event | 827
BAYAMON | 2021-07-06 05:45 | 2021-07-06 11:35 | 75 | 005:50 | P | DESGANCHE | 2 X 65 CORTE DE LINEA Y 1 X 40 EN OTRO CORTE DE LINEA | B21070600006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 350 | 2021-07-06 | 26250 | keep | 0 | Jul | 2021 | 0.017879 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-07-06 06:00 | 2021-07-06 18:12 | 1 | 012:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN RISER SE REEMPLAZO CAJA PRIMARIA | S21070600000 | New_Event | Cutout Failure | Include | Include | Equipment | 732 | 2021-07-06 | 732 | keep | 0 | Jul | 2021 | 0.00049856 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-07-06 06:00 | 2021-07-06 10:00 | 15 | 004:00 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 20 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21070600000 | New_Event | Bad Weather | Include | Include | Weather | 240 | 2021-07-06 | 3600 | keep | 0 | Jul | 2021 | 0.0024519 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-07-06 06:00 | 2021-07-06 12:56 | 25 | 006:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21070600000 | New_Event | Bad Weather | Include | Include | Weather | 416 | 2021-07-06 | 10400 | keep | 0 | Jul | 2021 | 0.0070834 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-07-06 06:00 | 2021-07-06 18:30 | 100 | 012:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21070600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 750 | 2021-07-06 | 75000 | keep | 0 | Jul | 2021 | 0.051082 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-07-06 06:01 | 2021-07-06 10:07 | 8 | 004:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPAZAR BAJANTE SECUNDARIO | C21070600014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 246 | 2021-07-06 | 1968 | keep | 0 | Jul | 2021 | 0.0013404 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-07-06 06:11 | 2021-07-06 09:00 | 50 | 002:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21070500010 | New_Event | Bad Weather | Include | Include | Weather | 169 | 2021-07-06 | 8450 | keep | 0 | Jul | 2021 | 0.0057553 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-06 06:19 | 2021-07-06 15:23 | 105 | 009:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 Y 1 X 30 EN CORTES DE LINEA SE REMPLAZO BAJATE PRIMARIO DE LINEA A CAJA | C21070600038 | New_Event | Wire Down | Include | Include | Equipment | 544 | 2021-07-06 | 57120 | keep | 0 | Jul | 2021 | 0.038904 | 7.1515e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 105
FAJARDO | 2021-07-06 06:38 | 2021-07-06 10:29 | 50 | 003:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21070600010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 231 | 2021-07-06 | 11550 | keep | 0 | Jul | 2021 | 0.0078667 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-06 06:44 | 2021-07-06 06:45 | 2448 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21070600000 | New_Event |  |  | Include | Wildlife | 1 | 2021-07-06 | 2448 | keep | 0 | Jul | 2021 | 0.0016673 | 0.0016673 | Momentary | FALSE | FALSE | Not_TMED_Event | 2448
CAGUAS | 2021-07-06 06:45 | 2021-07-06 10:36 | 5 | 003:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | C21070600017 | 1st_after_momentary |  |  | Include | Wildlife | 231 | 2021-07-06 | 1155 | keep | 0 | Jul | 2021 | 0.00078667 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-07-06 06:56 | 2021-07-06 06:57 | 5062 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21070600011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-06 | 5062 | keep | 0 | Jul | 2021 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
SAN JUAN | 2021-07-06 07:05 | 2021-07-06 18:30 | 300 | 011:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | S21070600019 | New_Event | Wire Down | Include | Include | Equipment | 685 | 2021-07-06 | 205500 | keep | 0 | Jul | 2021 | 0.13997 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
ARECIBO | 2021-07-06 07:07 | 2021-07-06 09:42 | 12 | 002:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 25 EN CORTE DE LINEA REPARO LINEA PARTIDA | A21070600011 | New_Event | Wire Down | Include | Include | Equipment | 155 | 2021-07-06 | 1860 | keep | 0 | Jul | 2021 | 0.0012668 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
UTUADO | 2021-07-06 07:07 | 2021-07-08 10:43 | 50 | 051:36 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | A21070600111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3096 | 2021-07-06 | 154800 | keep | 0 | Jul | 2021 | 0.10543 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-06 07:08 | 2021-07-07 17:10 | 50 | 034:02 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | C21070600049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2042 | 2021-07-06 | 102100 | keep | 0 | Jul | 2021 | 0.06954 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-06 07:12 | 2021-07-06 11:05 | 113 | 003:53 | P | NO SE REPORTO CAUSA | 1 X 100 EN LA SALIDA DEL CONVERTIDOR NO CAUSA | C21070600022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 233 | 2021-07-06 | 26329 | keep | 0 | Jul | 2021 | 0.017933 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
VEGA BAJA | 2021-07-06 07:13 | 2021-07-06 07:14 | 1100 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE | B21070600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-06 | 1100 | keep | 0 | Jul | 2021 | 0.0007492 | 0.0007492 | Momentary | FALSE | FALSE | Not_TMED_Event | 1100
VEGA BAJA | 2021-07-06 07:24 | 2021-07-06 15:01 | 30 | 007:37 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | B21070600011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 457 | 2021-07-06 | 13710 | keep | 0 | Jul | 2021 | 0.0093378 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2021-07-06 07:31 | 2021-07-06 15:34 | 5 | 008:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 10 EN CORTE DE LINEA SE REPARO BAJANTE ZAFADO HACIA TRANSFORMADOR | R21070600013 | New_Event | Wire Down | Include | Include | Equipment | 483 | 2021-07-06 | 2415 | keep | 0 | Jul | 2021 | 0.0016448 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
BAYAMON | 2021-07-06 07:35 | 2021-07-06 07:36 | 112 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21070600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-06 | 112 | keep | 0 | Jul | 2021 | 7.6283e-05 | 7.6283e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 112
HUMACAO | 2021-07-06 07:35 | 2021-07-06 08:15 | 1827 | 000:40 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR CONDUCTOR VIVO EN EL SUELO | C21070600011 | Additional_clients | Wire Down | Include | Include | Equipment | 40 | 2021-07-06 | 73080 | keep | 0 | Jul | 2021 | 0.049774 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-06 07:36 | 2021-07-08 09:20 | 100 | 049:44 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S21070600033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2984 | 2021-07-06 | 298400 | keep | 0 | Jul | 2021 | 0.20324 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-06 07:38 | 2021-07-06 15:20 | 80 | 007:42 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21070600013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 462 | 2021-07-06 | 36960 | keep | 0 | Jul | 2021 | 0.025173 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-07-06 07:39 | 2021-07-06 09:31 | 1 | 001:52 | P | DESGANCHE | 1 X 50 EN RISER Y 1 X 65 EN CORTE DE LINEA | C21070600027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2021-07-06 | 112 | keep | 0 | Jul | 2021 | 7.6283e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CANOVANAS | 2021-07-06 07:49 | 2021-07-06 20:06 | 70 | 012:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20, 1 X 30, 1 X 40 Y 1 X 50 EN CORTES DE LINEAS SE DESPEGO PUENTE A POSTE DE METAL | R21070600017 | New_Event | Wire Down | Include | Include | Equipment | 737 | 2021-07-06 | 51590 | keep | 0 | Jul | 2021 | 0.035138 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
CANOVANAS | 2021-07-06 07:49 | 2021-07-06 11:56 | 80 | 004:07 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTE DE LINEA | R21070600017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 247 | 2021-07-06 | 19760 | keep | 0 | Jul | 2021 | 0.013458 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-07-06 07:56 | 2021-07-06 16:20 | 22 | 008:24 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR UNO DE 100KVA | S21070600028 | New_Event | Service Transformer Failure | Include | Include | Equipment | 504 | 2021-07-06 | 11088 | keep | 0 | Jul | 2021 | 0.007552 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
BARRANQUITAS | 2021-07-06 08:08 | 2021-07-06 19:42 | 4 | 011:34 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA X 25 KVA | C21070600036 | New_Event | Service Transformer Failure | Include | Include | Equipment | 694 | 2021-07-06 | 2776 | keep | 0 | Jul | 2021 | 0.0018907 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-07-06 08:11 | 2021-07-06 15:15 | 90 | 007:04 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | A21070600022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 424 | 2021-07-06 | 38160 | keep | 0 | Jul | 2021 | 0.025991 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
HUMACAO | 2021-07-06 08:15 | 2021-07-06 13:18 | 827 | 005:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTO CONDUCTOR Y CERRO MACHETES | C21070600011 | Partial_restoration | Wire Down | Include | Include | Equipment | 303 | 2021-07-06 | 250581 | keep | 0 | Jul | 2021 | 0.17067 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-06 08:19 | 2021-07-06 08:56 | 2391 | 000:37 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR Y SE CERRO PUENTE PRIMARIO ABIERTO | S21070600000 | New_Event | Wire Down | Include | Include | Equipment | 37 | 2021-07-06 | 88467 | keep | 0 | Jul | 2021 | 0.060254 | 0.0016285 | Sustained | FALSE | FALSE | Not_TMED_Event | 2391
UTUADO | 2021-07-06 08:19 | 2021-07-07 15:55 | 60 | 031:36 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | A21070600024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1896 | 2021-07-06 | 113760 | keep | 0 | Jul | 2021 | 0.077481 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
VEGA BAJA | 2021-07-06 08:26 | 2021-07-06 12:29 | 12 | 004:03 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REPARO SECUNDARIA | B21070600017 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 243 | 2021-07-06 | 2916 | keep | 0 | Jul | 2021 | 0.0019861 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2021-07-06 08:29 | 2021-07-06 15:46 | 1 | 007:17 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA X 37.5 KVA | C21070600042 | New_Event | Service Transformer Failure | Include | Include | Equipment | 437 | 2021-07-06 | 437 | keep | 0 | Jul | 2021 | 0.00029764 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-07-06 09:06 | 2021-07-06 14:41 | 90 | 005:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN SU - 15 CRUCE CON RATA | R21070600032 | New_Event |  |  | Include | Wildlife | 335 | 2021-07-06 | 30150 | keep | 0 | Jul | 2021 | 0.020535 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2021-07-06 09:06 | 2021-07-06 17:21 | 1 | 008:15 | P | OTRAS CAUSAS | 1 X 10 EN BANCO DE TRANSFORMADORES PROBLEMA DEL CLIENTE | R21070600132 | New_Event | Other Causes | Include | Include | Other | 495 | 2021-07-06 | 495 | keep | 0 | Jul | 2021 | 0.00033714 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-07-06 09:14 | 2021-07-07 09:10 | 40 | 023:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | S21070600048 | New_Event | Cutout Failure | Include | Include | Equipment | 1436 | 2021-07-06 | 57440 | keep | 0 | Jul | 2021 | 0.039122 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-07-06 09:19 | 2021-07-06 17:00 | 20 | 007:41 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | A21070600050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 461 | 2021-07-06 | 9220 | keep | 0 | Jul | 2021 | 0.0062797 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-07-06 09:25 | 2021-07-07 13:38 | 50 | 028:13 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | M21070600055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1693 | 2021-07-06 | 84650 | keep | 0 | Jul | 2021 | 0.057655 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-06 09:25 | 2021-07-07 12:32 | 60 | 027:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA REPARO LINEA PARTIDA | M21070600054 | New_Event | Wire Down | Include | Include | Equipment | 1627 | 2021-07-06 | 97620 | keep | 0 | Jul | 2021 | 0.066489 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-07-06 09:38 | 2021-07-06 15:20 | 100 | 005:42 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21070600038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 342 | 2021-07-06 | 34200 | keep | 0 | Jul | 2021 | 0.023293 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-07-06 09:50 | 2021-07-06 10:43 | 15 | 000:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA REMPLAZO CAJA PRIMARIA | M21070500012 | New_Event | Cutout Failure | Include | Include | Equipment | 53 | 2021-07-06 | 795 | keep | 0 | Jul | 2021 | 0.00054147 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CAGUAS | 2021-07-06 09:51 | 2021-07-06 14:53 | 1 | 005:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 15 EN BANCO DE TRANSFORMADORES CRUCE POR AVE | C21070600060 | New_Event |  |  | Include | Wildlife | 302 | 2021-07-06 | 302 | keep | 0 | Jul | 2021 | 0.00020569 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-07-06 09:54 | 2021-07-06 10:00 | 437 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO SE VERIFICO PERSONAL FUERA | R21070600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2021-07-06 | 2622 | keep | 0 | Jul | 2021 | 0.0017858 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
MAYAGÃœEZ | 2021-07-06 09:54 | 2021-07-06 18:00 | 5 | 008:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO Y SE CERRO PUENTES | M21070600053 | New_Event | Wire Down | Include | Include | Equipment | 486 | 2021-07-06 | 2430 | keep | 0 | Jul | 2021 | 0.0016551 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-07-06 09:56 | 2021-07-09 11:21 | 12 | 073:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | R21070600050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 4405 | 2021-07-06 | 52860 | keep | 0 | Jul | 2021 | 0.036003 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-07-06 09:57 | 2021-07-07 10:30 | 70 | 024:33 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | B21070600122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1473 | 2021-07-06 | 103110 | keep | 0 | Jul | 2021 | 0.070228 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
SAN JUAN | 2021-07-06 10:00 | 2021-07-06 11:37 | 1 | 001:37 | P | NO SE REPORTO CAUSA | 1 RBA DE 80 AMP EN EL SU - 13 | R21070300048 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 97 | 2021-07-06 | 97 | keep | 0 | Jul | 2021 | 6.6066e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-06 10:10 | 2021-07-07 10:52 | 4 | 024:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE CAJA A TRANSFORMADOR | S21070600057 | New_Event | Wire Down | Include | Include | Equipment | 1482 | 2021-07-06 | 5928 | keep | 0 | Jul | 2021 | 0.0040375 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2021-07-06 10:11 | 2021-07-09 14:30 | 15 | 076:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA | P21070600010 | New_Event | Wire Down | Include | Include | Equipment | 4579 | 2021-07-06 | 68685 | keep | 0 | Jul | 2021 | 0.046781 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
ARECIBO | 2021-07-06 10:13 | 2021-07-06 17:25 | 10 | 007:12 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | A21070600064 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 432 | 2021-07-06 | 4320 | keep | 0 | Jul | 2021 | 0.0029423 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-06 10:15 | 2021-07-06 12:57 | 60 | 002:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | B21070500074 | New_Event | Cutout Failure | Include | Include | Equipment | 162 | 2021-07-06 | 9720 | keep | 0 | Jul | 2021 | 0.0066202 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
PONCE | 2021-07-06 10:21 | 2021-07-06 10:22 | 80 | 000:01 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA PARARRAYO DESFECTUOSO | P21070600001 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-07-06 | 80 | keep | 0 | Jul | 2021 | 5.4488e-05 | 5.4488e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-07-06 10:27 | 2021-07-08 09:29 | 10 | 047:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA | S21070600062 | New_Event | Cutout Failure | Include | Include | Equipment | 2822 | 2021-07-06 | 28220 | keep | 0 | Jul | 2021 | 0.019221 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-07-06 10:28 | 2021-07-06 14:57 | 60 | 004:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO | M21070600000 | New_Event | Wire Down | Include | Include | Equipment | 269 | 2021-07-06 | 16140 | keep | 0 | Jul | 2021 | 0.010993 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2021-07-06 10:30 | 2021-07-06 19:34 | 1 | 009:04 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO ENREDADERA | C21070600067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 544 | 2021-07-06 | 544 | keep | 0 | Jul | 2021 | 0.00037052 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-07-06 10:32 | 2021-07-07 18:10 | 100 | 031:38 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21070600069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1898 | 2021-07-06 | 189800 | keep | 0 | Jul | 2021 | 0.12927 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-07-06 10:52 | 2021-07-07 10:31 | 10 | 023:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR | M21070600087 | New_Event | Bad Weather | Include | Include | Weather | 1419 | 2021-07-06 | 14190 | keep | 0 | Jul | 2021 | 0.0096647 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-07-06 10:54 | 2021-07-06 15:20 | 50 | 004:26 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | A21070600075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2021-07-06 | 13300 | keep | 0 | Jul | 2021 | 0.0090586 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-06 10:55 | 2021-07-06 12:20 | 5668 | 001:25 | T | DESGANCHE | DISPARO SE SECCIONALIZO | R21070600055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2021-07-06 | 481780 | keep | 0 | Jul | 2021 | 0.32814 | 0.0038604 | Sustained | FALSE | FALSE | Not_TMED_Event | 5668
UTUADO | 2021-07-06 11:00 | 2021-07-07 18:30 | 50 | 031:30 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21070500059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1890 | 2021-07-06 | 94500 | keep | 0 | Jul | 2021 | 0.064364 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BARRANQUITAS | 2021-07-06 11:04 | 2021-07-07 12:02 | 30 | 024:58 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO CAUSA | C21070600076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1498 | 2021-07-06 | 44940 | keep | 0 | Jul | 2021 | 0.030608 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-07-06 11:29 | 2021-07-06 13:52 | 25 | 002:23 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR | S21070600070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2021-07-06 | 3575 | keep | 0 | Jul | 2021 | 0.0024349 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-07-06 11:37 | 2021-07-06 19:38 | 35 | 008:01 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | S21070600043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 481 | 2021-07-06 | 16835 | keep | 0 | Jul | 2021 | 0.011466 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
UTUADO | 2021-07-06 11:47 | 2021-07-07 14:45 | 125 | 026:58 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A21070600089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1618 | 2021-07-06 | 202250 | keep | 0 | Jul | 2021 | 0.13775 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
UTUADO | 2021-07-06 11:47 | 2021-07-07 19:55 | 150 | 032:08 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A21070600090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1928 | 2021-07-06 | 289200 | keep | 0 | Jul | 2021 | 0.19697 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-07-06 11:51 | 2021-07-06 16:30 | 15 | 004:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO | M21070600000 | New_Event | Wire Down | Include | Include | Equipment | 279 | 2021-07-06 | 4185 | keep | 0 | Jul | 2021 | 0.0028504 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-07-06 11:58 | 2021-07-06 17:00 | 12 | 005:02 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR LA MISMA CAPACIDAD | A21070600092 | New_Event | Service Transformer Failure | Include | Include | Equipment | 302 | 2021-07-06 | 3624 | keep | 0 | Jul | 2021 | 0.0024683 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2021-07-06 12:00 | 2021-07-06 15:35 | 20 | 003:35 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | A21070600093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2021-07-06 | 4300 | keep | 0 | Jul | 2021 | 0.0029287 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-07-06 12:20 | 2021-07-06 12:24 | 800 | 000:04 | P | DESGANCHE | SE RETIRO ARBOL SOBRE LINEAS | R21070600055 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 4 | 2021-07-06 | 3200 | keep | 0 | Jul | 2021 | 0.0021795 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
CANOVANAS | 2021-07-06 12:22 | 2021-07-06 13:21 | 10 | 000:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE DE LINEA A CAJA | R21070600089 | New_Event | Wire Down | Include | Include | Equipment | 59 | 2021-07-06 | 590 | keep | 0 | Jul | 2021 | 0.00040185 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
SAN JUAN | 2021-07-06 12:24 | 2021-07-06 12:26 | 5668 | 000:02 | T | DESGANCHE | PERSONAL REALIZANDO OPERACIONES | R21070600055 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-07-06 | 11336 | keep | 0 | Jul | 2021 | 0.0077209 | 0.0038604 | Momentary | FALSE | FALSE | Not_TMED_Event | 5668
SAN JUAN | 2021-07-06 12:26 | 2021-07-06 16:11 | 800 | 003:45 | P | DESGANCHE | SE RETIRO ARBOL SOBRE LINEAS | R21070600055 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 225 | 2021-07-06 | 180000 | keep | 0 | Jul | 2021 | 0.1226 | 0.00054488 | Sustained | FALSE | TRUE | Not_TMED_Event | 800
SAN JUAN | 2021-07-06 12:54 | 2021-07-06 14:48 | 1 | 001:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO EN PROVISIONAL | S21070600083 | New_Event | Wire Down | Include | Include | Equipment | 114 | 2021-07-06 | 114 | keep | 0 | Jul | 2021 | 7.7645e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-07-06 13:04 | 2021-07-06 16:00 | 44 | 002:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | C21070600085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2021-07-06 | 7744 | keep | 0 | Jul | 2021 | 0.0052744 | 2.9968e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 44
PONCE | 2021-07-06 13:09 | 2021-07-06 13:10 | 1093 | 000:01 | T | DESGANCHE | RECIERRE | P210706000XX | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-06 | 1093 | keep | 0 | Jul | 2021 | 0.00074444 | 0.00074444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1093
MAYAGÃœEZ | 2021-07-06 13:09 | 2021-07-06 15:20 | 80 | 002:11 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M21070600120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2021-07-06 | 10480 | keep | 0 | Jul | 2021 | 0.0071379 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-07-06 13:10 | 2021-07-06 15:22 | 100 | 002:12 | P | DESGANCHE | 3 X 80 EN CORTE DE LINEA POR DESGANCHE | P21070600019 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 132 | 2021-07-06 | 13200 | keep | 0 | Jul | 2021 | 0.0089905 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-07-06 13:12 | 2021-07-08 11:22 | 30 | 046:10 | P | DESGANCHE | 1 X 30 EN CONVERTIDOR | A21070600099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2770 | 2021-07-06 | 83100 | keep | 0 | Jul | 2021 | 0.056599 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2021-07-06 13:16 | 2021-07-08 14:15 | 28 | 048:59 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE Y SE REPARO BAJANTE EN TRANSFORMADOR | A21070600018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2939 | 2021-07-06 | 82292 | keep | 0 | Jul | 2021 | 0.056049 | 1.9071e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 28
VEGA BAJA | 2021-07-06 13:19 | 2021-07-06 21:18 | 100 | 007:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA Y DESGANCHE | B21070600039 | New_Event | Cutout Failure | Include | Include | Equipment | 479 | 2021-07-06 | 47900 | keep | 0 | Jul | 2021 | 0.032624 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-07-06 13:19 | 2021-07-06 21:18 | 80 | 007:59 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 80 EN CORTE DE LINEA | B21070600059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 479 | 2021-07-06 | 38320 | keep | 0 | Jul | 2021 | 0.0261 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-07-06 13:25 | 2021-07-06 18:25 | 300 | 005:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO | M21070600000 | New_Event | Wire Down | Include | Include | Equipment | 300 | 2021-07-06 | 90000 | keep | 0 | Jul | 2021 | 0.061299 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
UTUADO | 2021-07-06 13:31 | 2021-07-07 12:27 | 125 | 022:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO PUENTE ABIERTO | A21070600104 | New_Event | Wire Down | Include | Include | Equipment | 1376 | 2021-07-06 | 172000 | keep | 0 | Jul | 2021 | 0.11715 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
VEGA BAJA | 2021-07-06 13:35 | 2021-07-07 13:36 | 20 | 024:01 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | B21070600024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1441 | 2021-07-06 | 28820 | keep | 0 | Jul | 2021 | 0.019629 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
FAJARDO | 2021-07-06 13:43 | 2021-07-06 15:02 | 60 | 001:19 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN RISER AVERIA DEL T2 AL T4 PENDIENTE PROVISIONAL | R21070600124 | New_Event | UG Cable Fault | Include | Include | Equipment | 79 | 2021-07-06 | 4740 | keep | 0 | Jul | 2021 | 0.0032284 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2021-07-06 13:50 | 2021-07-06 14:03 | 12 | 000:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | B21070600010 | New_Event | Secondary Wire Down | Include | Include | Equipment | 13 | 2021-07-06 | 156 | keep | 0 | Jul | 2021 | 0.00010625 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2021-07-06 14:00 | 2021-07-06 15:43 | 5 | 001:43 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21070600071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 103 | 2021-07-06 | 515 | keep | 0 | Jul | 2021 | 0.00035076 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
VEGA BAJA | 2021-07-06 14:05 | 2021-07-06 15:43 | 60 | 001:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 Y 1 X 65 EN CORTE DE LINEA SE RETIRO GLOBO CRUZANDO FASE | B21070600032 | New_Event |  |  | Include | Wildlife | 98 | 2021-07-06 | 5880 | keep | 0 | Jul | 2021 | 0.0040048 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-07-06 14:10 | 2021-07-06 16:17 | 12 | 002:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZO DE 100 PIES DE SEUCUNDARIA Y 25 PIES DE TOMA | C21070600092 | New_Event | Secondary Wire Down | Include | Include | Equipment | 127 | 2021-07-06 | 1524 | keep | 0 | Jul | 2021 | 0.001038 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2021-07-06 14:21 | 2021-07-07 09:03 | 15 | 018:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO CONECTOR DE BAJANTE PRIMARIO A CAJA DE TRANSFORMADOR. | P21070600072 | New_Event | Wire Down | Include | Include | Equipment | 1122 | 2021-07-06 | 16830 | keep | 0 | Jul | 2021 | 0.011463 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-07-06 14:22 | 2021-07-06 18:20 | 100 | 003:58 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M21070600133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2021-07-06 | 23800 | keep | 0 | Jul | 2021 | 0.01621 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-07-06 14:30 | 2021-07-06 14:31 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21070600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-06 | 3041 | keep | 0 | Jul | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
MAYAGÃœEZ | 2021-07-06 14:31 | 2021-07-06 16:55 | 40 | 002:24 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M21070600136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2021-07-06 | 5760 | keep | 0 | Jul | 2021 | 0.0039231 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-07-06 14:32 | 2021-07-06 14:33 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21070600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-06 | 312 | keep | 0 | Jul | 2021 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
UTUADO | 2021-07-06 14:38 | 2021-07-07 13:25 | 30 | 022:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A21070600129 | New_Event | Wire Down | Include | Include | Equipment | 1367 | 2021-07-06 | 41010 | keep | 0 | Jul | 2021 | 0.027932 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
FAJARDO | 2021-07-06 14:46 | 2021-07-06 14:47 | 1902 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21070600129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-06 | 1902 | keep | 0 | Jul | 2021 | 0.0012954 | 0.0012954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1902
MAYAGÃœEZ | 2021-07-06 14:51 | 2021-07-06 16:59 | 1818 | 002:08 | T | DESGANCHE | SE RETIRO BAMBUAS CAIDAS SOBRE EL TRONCAL DEL ALIMENTADOR Y SE CERRO EL INTERRUPTOR. | M21070600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2021-07-06 | 232704 | keep | 0 | Jul | 2021 | 0.15849 | 0.0012382 | Sustained | FALSE | FALSE | Not_TMED_Event | 1818
BAYAMON | 2021-07-06 14:53 | 2021-07-06 16:28 | 8 | 001:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE REPARO SECUNDARIA | S21070500013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 95 | 2021-07-06 | 760 | keep | 0 | Jul | 2021 | 0.00051763 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2021-07-06 14:57 | 2021-07-06 15:45 | 569 | 000:48 | T | DESGANCHE | SE RETIRO BAMBUA SOBRE LINEA | M21070600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 48 | 2021-07-06 | 27312 | keep | 0 | Jul | 2021 | 0.018602 | 0.00038754 | Sustained | FALSE | TRUE | Not_TMED_Event | 569
HUMACAO | 2021-07-06 15:00 | 2021-07-06 16:05 | 10 | 001:05 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO CORTE DE LINEA PARA REEMPLAZAR DISCO ROTO SOBRE CRUCETA | C21070600097 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 65 | 2021-07-06 | 650 | keep | 0 | Jul | 2021 | 0.00044271 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
FAJARDO | 2021-07-06 15:02 | 2021-07-07 17:59 | 15 | 026:57 | P | CABLE SOTERRADO AVERIADO | 1 X 25 EN AEREO PROVISIONAL SE CONSTRUYO AEREO HACIA T-3 | R21070600143 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1617 | 2021-07-06 | 24255 | keep | 0 | Jul | 2021 | 0.01652 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-07-06 15:04 | 2021-07-07 13:00 | 40 | 021:56 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | A21070600156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1316 | 2021-07-06 | 52640 | keep | 0 | Jul | 2021 | 0.035853 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-06 15:29 | 2021-07-06 18:14 | 60 | 002:45 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | B21070600073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2021-07-06 | 9900 | keep | 0 | Jul | 2021 | 0.0067428 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-07-06 15:34 | 2021-07-07 11:14 | 40 | 019:40 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21070600101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1180 | 2021-07-06 | 47200 | keep | 0 | Jul | 2021 | 0.032148 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-06 15:38 | 2021-07-06 15:42 | 1399 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | B21070600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-06 | 5596 | keep | 0 | Jul | 2021 | 0.0038114 | 0.00095285 | Momentary | FALSE | TRUE | Not_TMED_Event | 1399
BAYAMON | 2021-07-06 15:38 | 2021-07-06 15:42 | 302 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | B21070600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-06 | 1208 | keep | 0 | Jul | 2021 | 0.00082276 | 0.00020569 | Momentary | FALSE | TRUE | Not_TMED_Event | 302
BAYAMON | 2021-07-06 15:38 | 2021-07-06 15:42 | 1048 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 | B21070600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-06 | 4192 | keep | 0 | Jul | 2021 | 0.0028552 | 0.00071379 | Momentary | FALSE | TRUE | Not_TMED_Event | 1048
BAYAMON | 2021-07-06 15:38 | 2021-07-06 15:42 | 573 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 LLEVANDO LA CARGA DEL 1704-05 | B21070600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-06 | 2292 | keep | 0 | Jul | 2021 | 0.0015611 | 0.00039027 | Momentary | FALSE | TRUE | Not_TMED_Event | 573
BAYAMON | 2021-07-06 15:38 | 2021-07-06 15:42 | 1313 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 CARGA POR EL 1704-04 | B21070600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-06 | 5252 | keep | 0 | Jul | 2021 | 0.0035771 | 0.00089428 | Momentary | FALSE | TRUE | Not_TMED_Event | 1313
BAYAMON | 2021-07-06 15:38 | 2021-07-06 15:42 | 1715 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO L-1000 | B21070600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-06 | 6860 | keep | 0 | Jul | 2021 | 0.0046723 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2021-07-06 15:38 | 2021-07-06 15:42 | 1498 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO L-1000 | B21070600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-06 | 5992 | keep | 0 | Jul | 2021 | 0.0040811 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2021-07-06 15:38 | 2021-07-06 15:42 | 1221 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO L-1000 | B21070600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-06 | 4884 | keep | 0 | Jul | 2021 | 0.0033265 | 0.00083162 | Momentary | FALSE | FALSE | Not_TMED_Event | 1221
BAYAMON | 2021-07-06 15:38 | 2021-07-06 15:42 | 1100 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO L-1000 | B21070600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-06 | 4400 | keep | 0 | Jul | 2021 | 0.0029968 | 0.0007492 | Momentary | FALSE | FALSE | Not_TMED_Event | 1100
BAYAMON | 2021-07-06 15:38 | 2021-07-06 15:39 | 4431 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21070600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-06 | 4431 | keep | 0 | Jul | 2021 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
BAYAMON | 2021-07-06 15:40 | 2021-07-07 08:56 | 50 | 017:16 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | B21070600074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1036 | 2021-07-06 | 51800 | keep | 0 | Jul | 2021 | 0.035281 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-07-06 15:41 | 2021-07-06 17:17 | 50 | 001:36 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21070600138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2021-07-06 | 4800 | keep | 0 | Jul | 2021 | 0.0032693 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-07-06 15:42 | 2021-07-06 17:30 | 15 | 001:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | P21070600028 | New_Event | Wire Down | Include | Include | Equipment | 108 | 2021-07-06 | 1620 | keep | 0 | Jul | 2021 | 0.0011034 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-07-06 15:45 | 2021-07-06 19:50 | 569 | 004:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21070600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 245 | 2021-07-06 | 139405 | keep | 0 | Jul | 2021 | 0.094948 | 0.00038754 | Sustained | FALSE | TRUE | Not_TMED_Event | 569
AGUADILLA | 2021-07-06 15:45 | 2021-07-06 19:50 | 1245 | 004:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21070600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 245 | 2021-07-06 | 305025 | keep | 0 | Jul | 2021 | 0.20775 | 0.00084796 | Sustained | FALSE | TRUE | Not_TMED_Event | 1245
AGUADILLA | 2021-07-06 15:45 | 2021-07-06 19:50 | 1155 | 004:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21070600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 245 | 2021-07-06 | 282975 | keep | 0 | Jul | 2021 | 0.19273 | 0.00078667 | Sustained | FALSE | TRUE | Not_TMED_Event | 1155
AGUADILLA | 2021-07-06 15:45 | 2021-07-06 19:50 | 867 | 004:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21070600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 245 | 2021-07-06 | 212415 | keep | 0 | Jul | 2021 | 0.14467 | 0.00059051 | Sustained | FALSE | TRUE | Not_TMED_Event | 867
AGUADILLA | 2021-07-06 15:45 | 2021-07-06 19:50 | 257 | 004:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21070600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 245 | 2021-07-06 | 62965 | keep | 0 | Jul | 2021 | 0.042885 | 0.00017504 | Sustained | FALSE | TRUE | Not_TMED_Event | 257
AGUADILLA | 2021-07-06 15:45 | 2021-07-06 19:50 | 1336 | 004:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21070600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 245 | 2021-07-06 | 327320 | keep | 0 | Jul | 2021 | 0.22294 | 0.00090994 | Sustained | FALSE | TRUE | Not_TMED_Event | 1336
AGUADILLA | 2021-07-06 15:45 | 2021-07-06 19:50 | 3315 | 004:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21070600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 245 | 2021-07-06 | 812175 | keep | 0 | Jul | 2021 | 0.55317 | 0.0022578 | Sustained | FALSE | TRUE | Not_TMED_Event | 3315
AGUADILLA | 2021-07-06 15:45 | 2021-07-06 19:50 | 1718 | 004:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21070600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 245 | 2021-07-06 | 420910 | keep | 0 | Jul | 2021 | 0.28668 | 0.0011701 | Sustained | FALSE | TRUE | Not_TMED_Event | 1718
MAYAGÃœEZ | 2021-07-06 15:45 | 2021-07-06 15:46 | 6285 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M21070600000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-06 | 6285 | keep | 0 | Jul | 2021 | 0.0042807 | 0.0042807 | Momentary | FALSE | FALSE | Not_TMED_Event | 6285
MAYAGÃœEZ | 2021-07-06 15:46 | 2021-07-06 16:02 | 150 | 000:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 Y 1 X 30 EN CORTES DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21070500004 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 16 | 2021-07-06 | 2400 | keep | 0 | Jul | 2021 | 0.0016346 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-07-06 15:50 | 2021-07-07 10:59 | 50 | 019:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN RISER Y SE FIJO PUENTE EN EL RISER | B21070600078 | New_Event | Wire Down | Include | Include | Equipment | 1149 | 2021-07-06 | 57450 | keep | 0 | Jul | 2021 | 0.039129 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-07-06 15:55 | 2021-07-07 11:45 | 70 | 019:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21070600201 | New_Event | Bad Weather | Include | Include | Weather | 1190 | 2021-07-06 | 83300 | keep | 0 | Jul | 2021 | 0.056735 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
ARECIBO | 2021-07-06 15:55 | 2021-07-06 15:56 | 2620 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21070600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-06 | 2620 | keep | 0 | Jul | 2021 | 0.0017845 | 0.0017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 2620
BAYAMON | 2021-07-06 16:00 | 2021-07-07 10:27 | 100 | 018:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO DE LINEA A CAJA | S21070600085 | New_Event | Wire Down | Include | Include | Equipment | 1107 | 2021-07-06 | 110700 | keep | 0 | Jul | 2021 | 0.075397 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-06 16:01 | 2021-07-06 16:03 | 3798 | 000:02 | T | NO SE REPORTO CAUSA | RECERRO | B21070600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-06 | 7596 | keep | 0 | Jul | 2021 | 0.0051736 | 0.0025868 | Momentary | FALSE | FALSE | Not_TMED_Event | 3798
MAYAGÃœEZ | 2021-07-06 16:02 | 2021-07-06 16:03 | 6285 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M21070600000 | Additional_clients | Bad Weather | Include | Include | Weather | 1 | 2021-07-06 | 6285 | keep | 0 | Jul | 2021 | 0.0042807 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-06 16:03 | 2021-07-06 18:39 | 150 | 002:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 Y 1 X 30 EN CORTES DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21070500004 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 156 | 2021-07-06 | 23400 | keep | 0 | Jul | 2021 | 0.015938 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-07-06 16:19 | 2021-07-07 17:40 | 125 | 025:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | M21070600244 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1521 | 2021-07-06 | 190125 | keep | 0 | Jul | 2021 | 0.12949 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
MAYAGÃœEZ | 2021-07-06 16:19 | 2021-07-07 09:58 | 120 | 017:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA | M21070600244 | New_Event | Bad Weather | Include | Include | Weather | 1059 | 2021-07-06 | 127080 | keep | 0 | Jul | 2021 | 0.086554 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
UTUADO | 2021-07-06 16:20 | 2021-07-07 17:45 | 25 | 025:25 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A21070600148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1525 | 2021-07-06 | 38125 | keep | 0 | Jul | 2021 | 0.025967 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
PONCE | 2021-07-06 16:26 | 2021-07-06 21:16 | 1212 | 004:50 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE CRUZADO PEGADO A ESTRUCTURA | P21070600031 | New_Event | Wire Down | Include | Include | Equipment | 290 | 2021-07-06 | 351480 | keep | 0 | Jul | 2021 | 0.23939 | 0.00082549 | Sustained | FALSE | FALSE | Not_TMED_Event | 1212
HUMACAO | 2021-07-06 16:33 | 2021-07-07 08:41 | 40 | 016:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21070600116 | New_Event | Bad Weather | Include | Include | Weather | 968 | 2021-07-06 | 38720 | keep | 0 | Jul | 2021 | 0.026372 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-07-06 16:33 | 2021-07-06 19:20 | 20 | 002:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO EN CORTE DE LINEA | M21070600000 | New_Event | Wire Down | Include | Include | Equipment | 167 | 2021-07-06 | 3340 | keep | 0 | Jul | 2021 | 0.0022749 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-07-06 16:38 | 2021-07-06 18:39 | 150 | 002:01 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M21070600265 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2021-07-06 | 18150 | keep | 0 | Jul | 2021 | 0.012362 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-07-06 16:49 | 2021-07-07 09:36 | 10 | 016:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | B21070600086 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1007 | 2021-07-06 | 10070 | keep | 0 | Jul | 2021 | 0.0068586 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-06 16:52 | 2021-07-06 16:53 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21070600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-06 | 393 | keep | 0 | Jul | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
UTUADO | 2021-07-06 17:15 | 2021-07-07 15:30 | 60 | 022:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO | A21070500174 | New_Event | Wire Down | Include | Include | Equipment | 1335 | 2021-07-06 | 80100 | keep | 0 | Jul | 2021 | 0.054556 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-07-06 17:47 | 2021-07-07 17:56 | 300 | 024:09 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA DESGANCHE | M21070600324 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1449 | 2021-07-06 | 434700 | keep | 0 | Jul | 2021 | 0.29607 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-07-06 18:00 | 2021-07-06 18:20 | 5 | 000:20 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M21070600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 20 | 2021-07-06 | 100 | keep | 0 | Jul | 2021 | 6.811e-05 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-07-06 18:30 | 2021-07-07 14:30 | 200 | 020:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | M21070600345 | New_Event | Cutout Failure | Include | Include | Equipment | 1200 | 2021-07-06 | 240000 | keep | 0 | Jul | 2021 | 0.16346 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-07-06 18:32 | 2021-07-06 19:05 | 25 | 000:33 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | M21070600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 33 | 2021-07-06 | 825 | keep | 0 | Jul | 2021 | 0.0005619 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-07-06 18:39 | 2021-07-06 18:52 | 6285 | 000:13 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR PARA RETIRAR BAMBUA EN LINEA 2500 AUTORIZADO POR ING FENEQUE | M21070600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 13 | 2021-07-06 | 81705 | keep | 0 | Jul | 2021 | 0.055649 | 0.0042807 | Sustained | FALSE | TRUE | Not_TMED_Event | 6285
MAYAGÃœEZ | 2021-07-06 18:52 | 2021-07-07 19:24 | 150 | 024:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 Y 1 X 30 EN CORTES DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21070500004 | Partial_restoration | Bad Weather | Include | Include | Weather | 1472 | 2021-07-06 | 220800 | keep | 0 | Jul | 2021 | 0.15039 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-07-06 18:53 | 2021-07-06 18:54 | 271 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21070600110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-06 | 271 | keep | 0 | Jul | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
YAUCO | 2021-07-06 18:55 | 2021-07-10 16:50 | 13 | 093:55 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA A 4.16KV POR UNO DE IGUAL CAPACIDAD. | P21070600046 | New_Event | Service Transformer Failure | Include | Include | Equipment | 5635 | 2021-07-06 | 73255 | keep | 0 | Jul | 2021 | 0.049894 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2021-07-06 19:09 | 2021-07-06 19:10 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21070600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-06 | 312 | keep | 0 | Jul | 2021 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
YAUCO | 2021-07-06 19:14 | 2021-07-06 19:15 | 2747 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210706000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-06 | 2747 | keep | 0 | Jul | 2021 | 0.001871 | 0.001871 | Momentary | FALSE | FALSE | Not_TMED_Event | 2747
BAYAMON | 2021-07-06 19:30 | 2021-07-06 19:31 | 1180 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21070600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-06 | 1180 | keep | 0 | Jul | 2021 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
MAYAGÃœEZ | 2021-07-06 19:42 | 2021-07-07 12:12 | 50 | 016:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | M21070600386 | New_Event | Vegetation Contact | Include | Include | Vegetation | 990 | 2021-07-06 | 49500 | keep | 0 | Jul | 2021 | 0.033714 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-06 20:09 | 2021-07-07 12:00 | 40 | 015:51 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | M21070600395 | New_Event | Vegetation Contact | Include | Include | Vegetation | 951 | 2021-07-06 | 38040 | keep | 0 | Jul | 2021 | 0.025909 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-07-06 20:39 | 2021-07-06 20:40 | 4085 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21070600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-06 | 4085 | keep | 0 | Jul | 2021 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
MAYAGÃœEZ | 2021-07-06 21:17 | 2021-07-06 21:18 | 1185 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21070600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-06 | 1185 | keep | 0 | Jul | 2021 | 0.0008071 | 0.0008071 | Momentary | FALSE | FALSE | Not_TMED_Event | 1185
MAYAGÃœEZ | 2021-07-06 21:18 | 2021-07-07 14:59 | 200 | 017:41 | P | DESGANCHE | 1 X 100, 1 X 80, 1 X 65, 1 X 50 Y 1 X 30 EN DISTINTOS CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | M21070500357 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1061 | 2021-07-06 | 212200 | keep | 0 | Jul | 2021 | 0.14453 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
HUMACAO | 2021-07-06 21:34 | 2021-07-06 21:35 | 3701 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR | C21070600000 | New_Event |  |  | Include | Wildlife | 1 | 2021-07-06 | 3701 | keep | 0 | Jul | 2021 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
HUMACAO | 2021-07-06 21:35 | 2021-07-06 21:42 | 100 | 000:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE CON AVE | C21070700158 | 1st_after_momentary |  |  | Include | Wildlife | 7 | 2021-07-06 | 700 | keep | 0 | Jul | 2021 | 0.00047677 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-07-06 21:42 | 2021-07-06 21:43 | 3701 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR | C21070600156 | Additional_clients |  |  | Include | Wildlife | 1 | 2021-07-06 | 3701 | keep | 0 | Jul | 2021 | 0.0025207 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-07-06 21:43 | 2021-07-06 22:03 | 100 | 000:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE CON AVE | C21070700158 | 1st_after_momentary |  |  | Include | Wildlife | 20 | 2021-07-06 | 2000 | keep | 0 | Jul | 2021 | 0.0013622 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-07-06 22:03 | 2021-07-06 22:04 | 3701 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR | C21070600157 | Additional_clients |  |  | Include | Wildlife | 1 | 2021-07-06 | 3701 | keep | 0 | Jul | 2021 | 0.0025207 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-07-06 22:04 | 2021-07-07 18:00 | 100 | 019:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE CON AVE | C21070700158 | 1st_after_momentary |  |  | Include | Wildlife | 1196 | 2021-07-06 | 119600 | keep | 0 | Jul | 2021 | 0.081459 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-07-06 22:05 | 2021-07-07 09:51 | 10 | 011:46 | P | TRANSFORMADOR AVERIADO | REMPLAZO BUSHING SECUNDARIO EN TRANSFORMADOR | R21070600144 | New_Event | Service Transformer Failure | Include | Include | Equipment | 706 | 2021-07-06 | 7060 | keep | 0 | Jul | 2021 | 0.0048085 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-07-06 23:05 | 2021-07-07 08:35 | 200 | 009:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | A21070600212 | New_Event | Cutout Failure | Include | Include | Equipment | 570 | 2021-07-06 | 114000 | keep | 0 | Jul | 2021 | 0.077645 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-07-07 00:28 | 2021-07-07 20:09 | 12 | 019:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 30 EN TRANSFORMADOR Y SE REPARO SECUNDARIA | S21070700003 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1181 | 2021-07-07 | 14172 | keep | 0 | Jul | 2021 | 0.0096525 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2021-07-07 00:49 | 2021-07-07 16:38 | 40 | 015:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | B21070700001 | New_Event | Cutout Failure | Include | Include | Equipment | 949 | 2021-07-07 | 37960 | keep | 0 | Jul | 2021 | 0.025854 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-07-07 02:31 | 2021-07-07 14:38 | 130 | 012:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | C21070700032 | New_Event | Cutout Failure | Include | Include | Equipment | 727 | 2021-07-07 | 94510 | keep | 0 | Jul | 2021 | 0.06437 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
BAYAMON | 2021-07-07 02:34 | 2021-07-07 02:35 | 142 | 000:01 | T | NO SE REPORTO CAUSA | INTERRUPTOR DISPARO Y SE CERRO POR CONTROL | S21070700031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-07 | 142 | keep | 0 | Jul | 2021 | 9.6716e-05 | 9.6716e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 142
CAGUAS | 2021-07-07 04:50 | 2021-07-07 18:33 | 150 | 013:43 | P | DESGANCHE | 2 X 140 EN CORTE DE LINEA | C21070700035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 823 | 2021-07-07 | 123450 | keep | 0 | Jul | 2021 | 0.084081 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-07-07 04:51 | 2021-07-07 12:21 | 70 | 007:30 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZARON SEIS AISLADORES Y DOS CAJAS PRIMARIAS | B21070700018 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 450 | 2021-07-07 | 31500 | keep | 0 | Jul | 2021 | 0.021455 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2021-07-07 04:52 | 2021-07-08 19:34 | 7 | 038:42 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHO | C21070700036 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 2322 | 2021-07-07 | 16254 | keep | 0 | Jul | 2021 | 0.011071 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2021-07-07 05:13 | 2021-07-07 12:31 | 8 | 007:18 | P | NO SE REPORTO CAUSA | 1 X 15 EN RISER | B21070700019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 438 | 2021-07-07 | 3504 | keep | 0 | Jul | 2021 | 0.0023866 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-07-07 06:00 | 2021-07-07 17:34 | 100 | 011:34 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE | M21070700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 694 | 2021-07-07 | 69400 | keep | 0 | Jul | 2021 | 0.047268 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-07-07 06:00 | 2021-07-07 16:50 | 25 | 010:50 | P | DESGANCHE | 1 X 40 EN CORTE DE LIMNEA DESGANCHE | A21070700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 650 | 2021-07-07 | 16250 | keep | 0 | Jul | 2021 | 0.011068 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2021-07-07 06:03 | 2021-07-07 10:20 | 50 | 004:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | C21070700038 | New_Event | Bad Weather | Include | Include | Weather | 257 | 2021-07-07 | 12850 | keep | 0 | Jul | 2021 | 0.0087521 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-07-07 06:13 | 2021-07-07 20:09 | 100 | 013:56 | P | DESGANCHE | 1 X 25 EN CONVERTIDOR SE RETIRO RAMA | A21070700014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 836 | 2021-07-07 | 83600 | keep | 0 | Jul | 2021 | 0.05694 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2021-07-07 06:14 | 2021-07-07 18:26 | 35 | 012:12 | P | AISLADOR ROTO, PARTIDO O SAFADO | 3 X 40 EN CORTES DE LINEA DESGANCHARON REEMPLAZARON RIGIDOS Y RETEZARON LINEA | R21070700008 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 732 | 2021-07-07 | 25620 | keep | 0 | Jul | 2021 | 0.01745 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
UTUADO | 2021-07-07 06:23 | 2021-07-08 19:00 | 20 | 036:37 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21070700015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2197 | 2021-07-07 | 43940 | keep | 0 | Jul | 2021 | 0.029927 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-07-07 06:25 | 2021-07-07 18:28 | 125 | 012:03 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P21070700014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 723 | 2021-07-07 | 90375 | keep | 0 | Jul | 2021 | 0.061554 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
BAYAMON | 2021-07-07 06:32 | 2021-07-08 20:14 | 10 | 037:42 | P | CABLE SOTERRADO AVERIADO | SE PREPARO PROVISIONAL AEREO PARA ENERGIZAR EL PM 10 | B21070700022 | New_Event | UG Cable Fault | Include | Include | Equipment | 2262 | 2021-07-07 | 22620 | keep | 0 | Jul | 2021 | 0.015406 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-07 06:32 | 2021-07-07 10:34 | 20 | 004:02 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | B21070600022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 242 | 2021-07-07 | 4840 | keep | 0 | Jul | 2021 | 0.0032965 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-07-07 06:46 | 2021-07-07 18:10 | 40 | 011:24 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21070700023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 684 | 2021-07-07 | 27360 | keep | 0 | Jul | 2021 | 0.018635 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-07-07 07:05 | 2021-07-07 18:02 | 500 | 010:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M21070700032 | New_Event | Wire Down | Include | Include | Equipment | 657 | 2021-07-07 | 328500 | keep | 0 | Jul | 2021 | 0.22374 | 0.00034055 | Sustained | FALSE | TRUE | Not_TMED_Event | 500
SAN JUAN | 2021-07-07 07:11 | 2021-07-07 08:23 | 80 | 001:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | R21070700009 | New_Event |  |  | Include | Wildlife | 72 | 2021-07-07 | 5760 | keep | 0 | Jul | 2021 | 0.0039231 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-07-07 07:12 | 2021-07-07 11:24 | 30 | 004:12 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21070700035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 252 | 2021-07-07 | 7560 | keep | 0 | Jul | 2021 | 0.0051491 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-07-07 07:15 | 2021-07-07 11:37 | 15 | 004:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | R21070700010 | New_Event |  |  | Include | Wildlife | 262 | 2021-07-07 | 3930 | keep | 0 | Jul | 2021 | 0.0026767 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-07-07 07:17 | 2021-07-07 14:23 | 1382 | 007:06 | T | NO SE REPORTO CAUSA | ALIMENTADOR ESTABA FUERA DE SERVICIO NO HAY RTU EN LA SUBESTACION | B21070700029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 426 | 2021-07-07 | 588732 | keep | 0 | Jul | 2021 | 0.40098 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2021-07-07 07:19 | 2021-07-07 07:21 | 2435 | 000:02 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1909-08 | S21070700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-07 | 4870 | keep | 0 | Jul | 2021 | 0.0033169 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-07-07 07:19 | 2021-07-07 07:21 | 2956 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVANDO LA CARGA DEL 1907-5 | S21070700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-07 | 5912 | keep | 0 | Jul | 2021 | 0.0040266 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
CAGUAS | 2021-07-07 07:19 | 2021-07-08 11:20 | 25 | 028:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21070700051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1681 | 2021-07-07 | 42025 | keep | 0 | Jul | 2021 | 0.028623 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-07-07 07:34 | 2021-07-07 11:14 | 20 | 003:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21070600104 | New_Event | Bad Weather | Include | Include | Weather | 220 | 2021-07-07 | 4400 | keep | 0 | Jul | 2021 | 0.0029968 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
AGUADILLA | 2021-07-07 07:51 | 2021-07-09 16:58 | 60 | 057:07 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO ENCONTRARON CAUSA | M21070700043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3427 | 2021-07-07 | 205620 | keep | 0 | Jul | 2021 | 0.14005 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-07-07 07:53 | 2021-07-09 12:33 | 40 | 052:40 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21070700055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3160 | 2021-07-07 | 126400 | keep | 0 | Jul | 2021 | 0.08609 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-07 07:54 | 2021-07-07 07:57 | 573 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL LLEVANDO LA CARGA DEL 1704-05 | B21070700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-07-07 | 1719 | keep | 0 | Jul | 2021 | 0.0011708 | 0.00039027 | Momentary | FALSE | FALSE | Not_TMED_Event | 573
BAYAMON | 2021-07-07 07:54 | 2021-07-07 07:55 | 1313 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL CARGA POR EL 1704-04 | B21070700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-07 | 1313 | keep | 0 | Jul | 2021 | 0.00089428 | 0.00089428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1313
ARECIBO | 2021-07-07 08:00 | 2021-07-07 18:10 | 25 | 010:10 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A21070700019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 610 | 2021-07-07 | 15250 | keep | 0 | Jul | 2021 | 0.010387 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-07-07 08:15 | 2021-07-07 16:05 | 40 | 007:50 | P | NO SE REPORTO CAUSA | 2 X 40 EN SU-1 Y 2 X 25 EN RISER | S21070700042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 470 | 2021-07-07 | 18800 | keep | 0 | Jul | 2021 | 0.012805 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-07-07 08:17 | 2021-07-08 16:39 | 50 | 032:22 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21070700036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1942 | 2021-07-07 | 97100 | keep | 0 | Jul | 2021 | 0.066134 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-07 08:23 | 2021-07-08 14:54 | 7 | 030:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE CON AVE | R21070700018 | Partial_restoration |  |  | Include | Wildlife | 1831 | 2021-07-07 | 12817 | keep | 0 | Jul | 2021 | 0.0087296 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2021-07-07 08:24 | 2021-07-07 12:05 | 2747 | 003:41 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR DE EMERGENCIA POR LINEA EN EL PISO EN EL TRONCAL DEL ALIMENTADOR | P21070700054 | New_Event | Wire Down | Include | Include | Equipment | 221 | 2021-07-07 | 607087 | keep | 0 | Jul | 2021 | 0.41348 | 0.001871 | Sustained | FALSE | TRUE | Not_TMED_Event | 2747
CAGUAS | 2021-07-07 08:25 | 2021-07-07 08:26 | 1702 | 000:01 | T | DESGANCHE | RECIERRE | C21070700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-07 | 1702 | keep | 0 | Jul | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2021-07-07 08:26 | 2021-07-07 12:19 | 40 | 003:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21070700065 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 233 | 2021-07-07 | 9320 | keep | 0 | Jul | 2021 | 0.0063478 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-07-07 08:26 | 2021-07-07 12:20 | 20 | 003:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | A21070700025 | New_Event | Bad Weather | Include | Include | Weather | 234 | 2021-07-07 | 4680 | keep | 0 | Jul | 2021 | 0.0031875 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
UTUADO | 2021-07-07 08:48 | 2021-07-08 16:28 | 3 | 031:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR LA MISMA CAPACIDAD | A21070700027 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1900 | 2021-07-07 | 5700 | keep | 0 | Jul | 2021 | 0.0038822 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2021-07-07 09:07 | 2021-07-07 09:42 | 40 | 000:35 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN SU - 7 SE SECCIONALIZO AVERIA ENTRE EL T - 33 Y T - 34 NO HAY CLIENTES FUERA | C21070700064 | New_Event | UG Cable Fault | Include | Include | Equipment | 35 | 2021-07-07 | 1400 | keep | 0 | Jul | 2021 | 0.00095353 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2021-07-07 09:07 | 2021-07-07 10:00 | 100 | 000:53 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA POR CARGA | P21070700030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 53 | 2021-07-07 | 5300 | keep | 0 | Jul | 2021 | 0.0036098 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-07-07 09:15 | 2021-07-07 19:47 | 30 | 010:32 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PRIMARIO PARTIDO Y SE CERRO PUENTE PRIMARIO | P21070700011 | New_Event | Defective Pole | Include | Include | Equipment | 632 | 2021-07-07 | 18960 | keep | 0 | Jul | 2021 | 0.012914 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-07-07 09:19 | 2021-07-07 15:30 | 90 | 006:11 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | M21070600051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 371 | 2021-07-07 | 33390 | keep | 0 | Jul | 2021 | 0.022742 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
MAYAGÃœEZ | 2021-07-07 09:20 | 2021-07-07 11:43 | 300 | 002:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE PRIMARIO ABIERTO | M21070700000 | New_Event | Wire Down | Include | Include | Equipment | 143 | 2021-07-07 | 42900 | keep | 0 | Jul | 2021 | 0.029219 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-07-07 09:38 | 2021-07-09 11:51 | 8 | 050:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO | M21070700092 | New_Event | Wire Down | Include | Include | Equipment | 3013 | 2021-07-07 | 24104 | keep | 0 | Jul | 2021 | 0.016417 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-07-07 09:42 | 2021-07-07 09:43 | 1606 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE | C21070700000 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1 | 2021-07-07 | 1606 | keep | 0 | Jul | 2021 | 0.0010938 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-07-07 09:43 | 2021-07-07 11:29 | 40 | 001:46 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN SU - 7 SE SECCIONALIZO AVERIA ENTRE EL T - 33 Y T - 34 NO HAY CLIENTES FUERA | C21070700064 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 106 | 2021-07-07 | 4240 | keep | 0 | Jul | 2021 | 0.0028878 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-07-07 09:44 | 2021-07-08 10:43 | 1 | 024:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR Y SE REMPLAZO CAJA PRIMARIA | S21070700070 | New_Event | Cutout Failure | Include | Include | Equipment | 1499 | 2021-07-07 | 1499 | keep | 0 | Jul | 2021 | 0.001021 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-07-07 09:58 | 2021-07-07 15:22 | 8 | 005:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21070600024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 324 | 2021-07-07 | 2592 | keep | 0 | Jul | 2021 | 0.0017654 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2021-07-07 10:00 | 2021-07-07 15:30 | 65 | 005:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P210707000XX | New_Event | Vegetation Contact | Include | Include | Vegetation | 330 | 2021-07-07 | 21450 | keep | 0 | Jul | 2021 | 0.014609 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
ARECIBO | 2021-07-07 10:07 | 2021-07-07 12:27 | 15 | 002:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO THREE WIRE ZAFADO | A21070700043 | New_Event | Wire Down | Include | Include | Equipment | 140 | 2021-07-07 | 2100 | keep | 0 | Jul | 2021 | 0.0014303 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
PONCE | 2021-07-07 10:10 | 2021-07-07 18:00 | 60 | 007:50 | P | ESTRUCTURA AVERIADA | SE ABRE CORTE DE LINEA PARA REEMPLAZAR POSTE PRIMARIO | P210707000XX | New_Event | Defective Pole | Include | Include | Equipment | 470 | 2021-07-07 | 28200 | keep | 0 | Jul | 2021 | 0.019207 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
AGUADILLA | 2021-07-07 10:30 | 2021-07-07 15:12 | 12 | 004:42 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO CON MONTURA DE TRANSFORMADORES | M21070700000 | New_Event | Defective Pole | Include | Include | Equipment | 282 | 2021-07-07 | 3384 | keep | 0 | Jul | 2021 | 0.0023048 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-07-07 10:34 | 2021-07-07 18:46 | 9 | 008:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE CON CULEBRA | C21070700080 | New_Event |  |  | Include | Wildlife | 492 | 2021-07-07 | 4428 | keep | 0 | Jul | 2021 | 0.0030159 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BARRANQUITAS | 2021-07-07 10:52 | 2021-07-08 15:19 | 53 | 028:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA | C21070700082 | New_Event | Wire Down | Include | Include | Equipment | 1707 | 2021-07-07 | 90471 | keep | 0 | Jul | 2021 | 0.061619 | 3.6098e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 53
ARECIBO | 2021-07-07 10:53 | 2021-07-09 11:33 | 15 | 048:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SOTERRADO | A21070700177 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2920 | 2021-07-07 | 43800 | keep | 0 | Jul | 2021 | 0.029832 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-07-07 11:13 | 2021-07-07 11:31 | 20 | 000:18 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA WR - 5889814 | R21070700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 18 | 2021-07-07 | 360 | keep | 0 | Jul | 2021 | 0.00024519 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
AGUADILLA | 2021-07-07 11:28 | 2021-07-07 16:04 | 6 | 004:36 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA REALIZAR DESGANCHE Y REPARAR LINEA SECUNDARIA | M21070600093 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 276 | 2021-07-07 | 1656 | keep | 0 | Jul | 2021 | 0.0011279 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
CAGUAS | 2021-07-07 11:34 | 2021-07-07 16:57 | 106 | 005:23 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C21070700091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 323 | 2021-07-07 | 34238 | keep | 0 | Jul | 2021 | 0.023319 | 7.2196e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 106
UTUADO | 2021-07-07 11:38 | 2021-07-09 16:25 | 6 | 052:47 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZO POSTE SECUNDARIO PARTIDO | A21070700052 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 3167 | 2021-07-07 | 19002 | keep | 0 | Jul | 2021 | 0.012942 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-07-07 11:41 | 2021-07-07 13:20 | 1105 | 001:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21070700086 | New_Event | Bad Weather | Include | Include | Weather | 99 | 2021-07-07 | 109395 | keep | 0 | Jul | 2021 | 0.074508 | 0.00075261 | Sustained | FALSE | TRUE | Not_TMED_Event | 1105
HUMACAO | 2021-07-07 11:42 | 2021-07-08 14:20 | 6 | 026:38 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHO | C21070700093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1598 | 2021-07-07 | 9588 | keep | 0 | Jul | 2021 | 0.0065303 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-07-07 11:43 | 2021-07-07 21:30 | 100 | 009:47 | P | PARARRAYOS DEFECTUOSO | 1 X 65 Y 1 X 50 EN CORTES DE LINEA SE REEMPLAZO PARARRAYO | C21070700094 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 587 | 2021-07-07 | 58700 | keep | 0 | Jul | 2021 | 0.03998 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-07-07 11:43 | 2021-07-07 14:12 | 1252 | 002:29 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE PRIMARIO ABIERTO | M21070700000 | New_Event | Wire Down | Include | Include | Equipment | 149 | 2021-07-07 | 186548 | keep | 0 | Jul | 2021 | 0.12706 | 0.00085273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1252
BAYAMON | 2021-07-07 11:51 | 2021-07-08 14:20 | 10 | 026:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA Y BAJANTE DE TRANSFORMADOR | S21070700061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1589 | 2021-07-07 | 15890 | keep | 0 | Jul | 2021 | 0.010823 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2021-07-07 11:52 | 2021-07-07 14:12 | 1252 | 002:20 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR PARA CERRAR PUENTE PRIMARIO | P21070700020 | New_Event | Wire Down | Include | Include | Equipment | 140 | 2021-07-07 | 175280 | keep | 0 | Jul | 2021 | 0.11938 | 0.00085273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1252
CANOVANAS | 2021-07-07 11:54 | 2021-07-07 11:55 | 635 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21070700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-07 | 635 | keep | 0 | Jul | 2021 | 0.0004325 | 0.0004325 | Momentary | FALSE | FALSE | Not_TMED_Event | 635
GUAYAMA | 2021-07-07 12:00 | 2021-07-07 17:54 | 50 | 005:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P210707000XX | New_Event | Vegetation Contact | Include | Include | Vegetation | 354 | 2021-07-07 | 17700 | keep | 0 | Jul | 2021 | 0.012055 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-07-07 12:10 | 2021-07-07 15:03 | 15 | 002:53 | P | ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE POSTE | B21070700000 | New_Event | Defective Pole | Include | Include | Equipment | 173 | 2021-07-07 | 2595 | keep | 0 | Jul | 2021 | 0.0017674 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-07-07 12:25 | 2021-07-08 10:04 | 8 | 021:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO BAJANTE DE CAJA A TRANSFORMADOR NO FUNDIO | C21070700099 | New_Event | Wire Down | Include | Include | Equipment | 1299 | 2021-07-07 | 10392 | keep | 0 | Jul | 2021 | 0.0070779 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-07-07 12:36 | 2021-07-08 18:45 | 100 | 030:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21070700137 | New_Event | Wire Down | Include | Include | Equipment | 1809 | 2021-07-07 | 180900 | keep | 0 | Jul | 2021 | 0.12321 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-07-07 12:38 | 2021-07-08 10:16 | 25 | 021:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE RETIRO GLOBO ENREDADO EN LINEA PRIMARIA | M21070700132 | New_Event |  |  | Include | Wildlife | 1298 | 2021-07-07 | 32450 | keep | 0 | Jul | 2021 | 0.022102 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-07-07 12:49 | 2021-07-07 14:53 | 12 | 002:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA Y PORTAFUSIBLE | S21070700049 | New_Event | Cutout Failure | Include | Include | Equipment | 124 | 2021-07-07 | 1488 | keep | 0 | Jul | 2021 | 0.0010135 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-07-07 13:15 | 2021-07-07 17:05 | 15 | 003:50 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | M21070700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 230 | 2021-07-07 | 3450 | keep | 0 | Jul | 2021 | 0.0023498 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-07-07 13:30 | 2021-07-07 15:36 | 40 | 002:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21070700000 | New_Event | Bad Weather | Include | Include | Weather | 126 | 2021-07-07 | 5040 | keep | 0 | Jul | 2021 | 0.0034327 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-07-07 13:46 | 2021-07-07 17:45 | 25 | 003:59 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A21070700072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2021-07-07 | 5975 | keep | 0 | Jul | 2021 | 0.0040695 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-07-07 13:53 | 2021-07-08 13:12 | 1 | 023:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA | A21070700075 | New_Event | Bad Weather | Include | Include | Weather | 1399 | 2021-07-07 | 1399 | keep | 0 | Jul | 2021 | 0.00095285 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-07-07 13:55 | 2021-07-08 15:30 | 100 | 025:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070700162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1535 | 2021-07-07 | 153500 | keep | 0 | Jul | 2021 | 0.10455 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
GUAYAMA | 2021-07-07 14:00 | 2021-07-07 17:50 | 50 | 003:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | P21070700058 | New_Event | Cutout Failure | Include | Include | Equipment | 230 | 2021-07-07 | 11500 | keep | 0 | Jul | 2021 | 0.0078326 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-07 14:08 | 2021-07-07 17:08 | 75 | 003:00 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S21070700069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2021-07-07 | 13500 | keep | 0 | Jul | 2021 | 0.0091948 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-07-07 14:14 | 2021-07-08 13:44 | 8 | 023:30 | P | TRANSFORMADOR AVERIADO | 1 X 15 EN TRANSFORMADOR SE REMPLAZO TRANSFORMADOR DE 37.5KVA X 37.5KVA | S21070500070 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1410 | 2021-07-07 | 11280 | keep | 0 | Jul | 2021 | 0.0076828 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-07-07 14:18 | 2021-07-08 10:23 | 100 | 020:05 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21070700177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1205 | 2021-07-07 | 120500 | keep | 0 | Jul | 2021 | 0.082072 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-07-07 14:30 | 2021-07-08 17:30 | 1 | 027:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA Y 1 X 10 EN TRANSFORMADOR | P21070700057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1620 | 2021-07-07 | 1620 | keep | 0 | Jul | 2021 | 0.0011034 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-07-07 14:30 | 2021-07-07 14:31 | 2620 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE INTERRUPTOR | A21070700000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-07 | 2620 | keep | 0 | Jul | 2021 | 0.0017845 | 0.0017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 2620
SAN JUAN | 2021-07-07 14:45 | 2021-07-07 16:24 | 150 | 001:39 | P | NO SE REPORTO CAUSA | 2 X 200 EN CORTE DE LINEA | S21070700073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2021-07-07 | 14850 | keep | 0 | Jul | 2021 | 0.010114 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
VEGA BAJA | 2021-07-07 14:52 | 2021-07-07 15:52 | 10 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21070700084 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2021-07-07 | 600 | keep | 0 | Jul | 2021 | 0.00040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-07-07 14:52 | 2021-07-07 18:43 | 79 | 003:51 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA SE PATRULLO | C21070700118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 231 | 2021-07-07 | 18249 | keep | 0 | Jul | 2021 | 0.012429 | 5.3807e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 79
CAGUAS | 2021-07-07 14:53 | 2021-07-08 15:09 | 40 | 024:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA DESPEGO PUENTE DE NEUTRAL | C21070700119 | New_Event | Wire Down | Include | Include | Equipment | 1456 | 2021-07-07 | 58240 | keep | 0 | Jul | 2021 | 0.039667 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-07-07 15:07 | 2021-07-08 08:47 | 50 | 017:40 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA ELIMINO PARARRAYO | C21070700124 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1060 | 2021-07-07 | 53000 | keep | 0 | Jul | 2021 | 0.036098 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-07 15:12 | 2021-07-07 19:00 | 100 | 003:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE DESGANCHO Y SE LEVANTO LINEA | S21070700080 | New_Event | Wire Down | Include | Include | Equipment | 228 | 2021-07-07 | 22800 | keep | 0 | Jul | 2021 | 0.015529 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-07-07 15:14 | 2021-07-07 15:15 | 2620 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE INTERRUPTOR | A21070700000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-07-07 | 2620 | keep | 0 | Jul | 2021 | 0.0017845 | 0.0017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 2620
ARECIBO | 2021-07-07 15:20 | 2021-07-07 15:21 | 2620 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE INTERRUPTOR | A21070700000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-07-07 | 2620 | keep | 0 | Jul | 2021 | 0.0017845 | 0.0017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 2620
SAN JUAN | 2021-07-07 15:21 | 2021-07-11 14:49 | 12 | 095:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | S21070700082 | New_Event | Secondary Wire Down | Include | Include | Equipment | 5728 | 2021-07-07 | 68736 | keep | 0 | Jul | 2021 | 0.046816 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
CANOVANAS | 2021-07-07 15:21 | 2021-07-07 18:34 | 12 | 003:13 | P | DESGANCHE | 1 X 40 Y 1 X 15 EN CORTES DE LINEA SE REALIZO DESGANCHE | R21070700024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2021-07-07 | 2316 | keep | 0 | Jul | 2021 | 0.0015774 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
HUMACAO | 2021-07-07 15:35 | 2021-07-08 13:27 | 1 | 021:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN CORTE DE LINEA CONDUCTORES ARRIADOS | C21070700136 | New_Event | Wire Down | Include | Include | Equipment | 1312 | 2021-07-07 | 1312 | keep | 0 | Jul | 2021 | 0.0008936 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-07-07 15:38 | 2021-07-07 19:39 | 50 | 004:01 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | S21070700085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2021-07-07 | 12050 | keep | 0 | Jul | 2021 | 0.0082072 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-07-07 15:40 | 2021-07-07 17:30 | 2620 | 001:50 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE REMPLAZARON AISLADORES | A21070700000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 110 | 2021-07-07 | 288200 | keep | 0 | Jul | 2021 | 0.19629 | 0.0017845 | Sustained | FALSE | TRUE | Not_TMED_Event | 2620
PONCE | 2021-07-07 15:42 | 2021-07-07 19:44 | 100 | 004:02 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P21070700066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2021-07-07 | 24200 | keep | 0 | Jul | 2021 | 0.016483 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-07-07 15:53 | 2021-07-08 13:28 | 200 | 021:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO | A21070700107 | New_Event | Wire Down | Include | Include | Equipment | 1295 | 2021-07-07 | 259000 | keep | 0 | Jul | 2021 | 0.1764 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
UTUADO | 2021-07-07 15:56 | 2021-07-07 17:05 | 50 | 001:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | A21070700111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 69 | 2021-07-07 | 3450 | keep | 0 | Jul | 2021 | 0.0023498 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-07 16:00 | 2021-07-08 11:17 | 10 | 019:17 | P | NO SE REPORTO CAUSA | 1 X 15 EN CORTE DE LINEA | B21070700088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1157 | 2021-07-07 | 11570 | keep | 0 | Jul | 2021 | 0.0078803 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
UTUADO | 2021-07-07 16:14 | 2021-07-07 18:20 | 150 | 002:06 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA POR DESGANCHE | A21070700126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2021-07-07 | 18900 | keep | 0 | Jul | 2021 | 0.012873 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-07-07 16:16 | 2021-07-08 12:09 | 40 | 019:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | B21070700091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1193 | 2021-07-07 | 47720 | keep | 0 | Jul | 2021 | 0.032502 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-07-07 16:20 | 2021-07-07 19:50 | 10 | 003:30 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21070600052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 210 | 2021-07-07 | 2100 | keep | 0 | Jul | 2021 | 0.0014303 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-07 16:24 | 2021-07-07 16:25 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | M21070700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-07 | 1192 | keep | 0 | Jul | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
BARRANQUITAS | 2021-07-07 16:30 | 2021-07-07 18:04 | 133 | 001:34 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21070700145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2021-07-07 | 12502 | keep | 0 | Jul | 2021 | 0.0085151 | 9.0586e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 133
MAYAGÃœEZ | 2021-07-07 16:31 | 2021-07-07 16:32 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | M21070700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-07 | 393 | keep | 0 | Jul | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2021-07-07 17:01 | 2021-07-08 15:30 | 20 | 022:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | M21070700241 | New_Event | Cutout Failure | Include | Include | Equipment | 1349 | 2021-07-07 | 26980 | keep | 0 | Jul | 2021 | 0.018376 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-07-07 17:02 | 2021-07-08 09:33 | 2 | 016:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA Y SE CERRO CORTE DE LINEA | A21070700156 | New_Event | Wire Down | Include | Include | Equipment | 991 | 2021-07-07 | 1982 | keep | 0 | Jul | 2021 | 0.0013499 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
YAUCO | 2021-07-07 17:03 | 2021-07-07 19:28 | 45 | 002:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P21070700068 | New_Event | Bad Weather | Include | Include | Weather | 145 | 2021-07-07 | 6525 | keep | 0 | Jul | 2021 | 0.0044441 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
UTUADO | 2021-07-07 17:15 | 2021-07-08 18:45 | 40 | 025:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE DESPEGO PUENTE PRIMARIO CRUZANDO CON TENZOR DE LINEA DE TRANSMISION | A21070700163 | New_Event |  |  | Include | Wildlife | 1530 | 2021-07-07 | 61200 | keep | 0 | Jul | 2021 | 0.041683 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-07-07 17:30 | 2021-07-07 19:02 | 150 | 001:32 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA REQUIERE DESGANCHE | M21070700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2021-07-07 | 13800 | keep | 0 | Jul | 2021 | 0.0093991 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-07-07 17:47 | 2021-07-10 18:48 | 16 | 073:01 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL DE EXISTENTE A T-55 | B21070700098 | New_Event | UG Cable Fault | Include | Include | Equipment | 4381 | 2021-07-07 | 70096 | keep | 0 | Jul | 2021 | 0.047742 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2021-07-07 17:56 | 2021-07-08 19:07 | 12 | 025:11 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO Y TRANSFORMADOR AVERIADO DE 15 KVA X 15 KVA | C21070700166 | New_Event | Defective Pole | Include | Include | Equipment | 1511 | 2021-07-07 | 18132 | keep | 0 | Jul | 2021 | 0.01235 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2021-07-07 18:37 | 2021-07-08 19:30 | 100 | 024:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO ALAMBRE PRIMARIO | P21070700070 | New_Event | Wire Down | Include | Include | Equipment | 1493 | 2021-07-07 | 149300 | keep | 0 | Jul | 2021 | 0.10169 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-07-07 18:51 | 2021-07-09 11:06 | 86 | 040:15 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C21070700177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2415 | 2021-07-07 | 207690 | keep | 0 | Jul | 2021 | 0.14146 | 5.8574e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 86
CAGUAS | 2021-07-07 18:53 | 2021-07-07 18:54 | 1843 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21070700178 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-07 | 1843 | keep | 0 | Jul | 2021 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
SAN JUAN | 2021-07-07 19:15 | 2021-07-07 20:57 | 100 | 001:42 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21070700097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 102 | 2021-07-07 | 10200 | keep | 0 | Jul | 2021 | 0.0069472 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-07-07 19:28 | 2021-07-08 12:33 | 6 | 017:05 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO CAUSA | C21070700183 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1025 | 2021-07-07 | 6150 | keep | 0 | Jul | 2021 | 0.0041887 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2021-07-07 19:30 | 2021-07-07 20:25 | 30 | 000:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A21070700186 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2021-07-07 | 1650 | keep | 0 | Jul | 2021 | 0.0011238 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
AGUADILLA | 2021-07-07 19:37 | 2021-07-08 13:30 | 50 | 017:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070700280 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1073 | 2021-07-07 | 53650 | keep | 0 | Jul | 2021 | 0.036541 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-07-07 19:44 | 2021-07-08 12:13 | 30 | 016:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21070700185 | New_Event | Bad Weather | Include | Include | Weather | 989 | 2021-07-07 | 29670 | keep | 0 | Jul | 2021 | 0.020208 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
YAUCO | 2021-07-07 19:48 | 2021-07-08 10:45 | 10 | 014:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO NEUTRAL EN XMR | P21080700075 | New_Event | Wire Down | Include | Include | Equipment | 897 | 2021-07-07 | 8970 | keep | 0 | Jul | 2021 | 0.0061094 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-07 19:51 | 2021-07-08 12:18 | 100 | 016:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | B21070700104 | New_Event | Wire Down | Include | Include | Equipment | 987 | 2021-07-07 | 98700 | keep | 0 | Jul | 2021 | 0.067224 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-07 19:55 | 2021-07-08 10:31 | 40 | 014:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | B21070700105 | New_Event | Cutout Failure | Include | Include | Equipment | 876 | 2021-07-07 | 35040 | keep | 0 | Jul | 2021 | 0.023866 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-07-07 20:16 | 2021-07-08 08:00 | 30 | 011:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA CRUZADA | M21070700292 | New_Event | Wire Down | Include | Include | Equipment | 704 | 2021-07-07 | 21120 | keep | 0 | Jul | 2021 | 0.014385 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-07-07 20:33 | 2021-07-08 10:58 | 100 | 014:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA 1 X 25 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | B21070700109 | New_Event | Cutout Failure | Include | Include | Equipment | 865 | 2021-07-07 | 86500 | keep | 0 | Jul | 2021 | 0.058915 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-07 20:35 | 2021-07-09 11:13 | 30 | 038:38 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 50KVA X 50KVA | S21070700101 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2318 | 2021-07-07 | 69540 | keep | 0 | Jul | 2021 | 0.047363 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-07-07 20:49 | 2021-07-08 13:43 | 15 | 016:54 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO ENCONTRARON CAUSA | A21070700188 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1014 | 2021-07-07 | 15210 | keep | 0 | Jul | 2021 | 0.010359 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-07-07 21:07 | 2021-07-09 17:39 | 60 | 044:32 | P | CABLE SOTERRADO AVERIADO | 1 X 25 Y 1 X 20 EN CORTES DE LINEA SE CONSTRUYO PROVISIONAL AEREO | C21070700193 | New_Event | UG Cable Fault | Include | Include | Equipment | 2672 | 2021-07-07 | 160320 | keep | 0 | Jul | 2021 | 0.10919 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-07-07 21:35 | 2021-07-08 08:59 | 40 | 011:24 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21070700197 | New_Event | Vegetation Contact | Include | Include | Vegetation | 684 | 2021-07-07 | 27360 | keep | 0 | Jul | 2021 | 0.018635 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-07-07 21:36 | 2021-07-08 17:30 | 100 | 019:54 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070700306 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1194 | 2021-07-07 | 119400 | keep | 0 | Jul | 2021 | 0.081323 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-07 21:41 | 2021-07-08 14:44 | 200 | 017:03 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | B21070700119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1023 | 2021-07-07 | 204600 | keep | 0 | Jul | 2021 | 0.13935 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
UTUADO | 2021-07-07 21:58 | 2021-07-09 15:10 | 150 | 041:12 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21070700197 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2472 | 2021-07-07 | 370800 | keep | 0 | Jul | 2021 | 0.25255 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-07-07 22:04 | 2021-07-08 10:07 | 150 | 012:03 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO | C21070700203 | New_Event | Bad Weather | Include | Include | Weather | 723 | 2021-07-07 | 108450 | keep | 0 | Jul | 2021 | 0.073865 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-07-07 22:43 | 2021-07-08 15:10 | 40 | 016:27 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21070700122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 987 | 2021-07-07 | 39480 | keep | 0 | Jul | 2021 | 0.02689 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
GUAYAMA | 2021-07-07 23:50 | 2021-07-07 23:51 | 4132 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE ALIMENTADOR | P21070700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-07 | 4132 | keep | 0 | Jul | 2021 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
BARRANQUITAS | 2021-07-08 02:30 | 2021-07-08 13:03 | 50 | 010:33 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C21070800003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 633 | 2021-07-08 | 31650 | keep | 0 | Jul | 2021 | 0.021557 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-08 03:14 | 2021-07-08 03:17 | 600 | 000:03 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR SE CERRO POR SCADA | S21070800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-07-08 | 1800 | keep | 0 | Jul | 2021 | 0.001226 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
BAYAMON | 2021-07-08 03:14 | 2021-07-08 03:17 | 1802 | 000:03 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR SE CERRO POR SCADA | S21070800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-07-08 | 5406 | keep | 0 | Jul | 2021 | 0.003682 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
CAGUAS | 2021-07-08 03:41 | 2021-07-08 15:55 | 100 | 012:14 | P | DESGANCHE | 1 X 40 Y 1 X 65 EN CORTES DE LINEA | C21070800005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 734 | 2021-07-08 | 73400 | keep | 0 | Jul | 2021 | 0.049992 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-07-08 04:27 | 2021-07-08 04:28 | 1894 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | R21070800004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-08 | 1894 | keep | 0 | Jul | 2021 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
BAYAMON | 2021-07-08 04:46 | 2021-07-08 04:47 | 2466 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | S21070800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-08 | 2466 | keep | 0 | Jul | 2021 | 0.0016796 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
BAYAMON | 2021-07-08 04:47 | 2021-07-08 16:32 | 75 | 011:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE CAJA A RISER | S21070800001 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 705 | 2021-07-08 | 52875 | keep | 0 | Jul | 2021 | 0.036013 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
PONCE | 2021-07-08 05:09 | 2021-07-08 05:10 | 2379 | 000:01 | T | DESGANCHE | RECIERRE NO SE SABE LA CAUSA | P21070800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-08 | 2379 | keep | 0 | Jul | 2021 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
YAUCO | 2021-07-08 05:29 | 2021-07-08 05:30 | 3973 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 5602-02 | P21080600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-08 | 3973 | keep | 0 | Jul | 2021 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
MAYAGÃœEZ | 2021-07-08 05:30 | 2021-07-08 12:40 | 500 | 007:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | M21070800006 | New_Event | Wire Down | Include | Include | Equipment | 430 | 2021-07-08 | 215000 | keep | 0 | Jul | 2021 | 0.14644 | 0.00034055 | Sustained | FALSE | TRUE | Not_TMED_Event | 500
FAJARDO | 2021-07-08 05:32 | 2021-07-09 12:12 | 60 | 030:40 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO AISLADOR PARTIDO | R21070800089 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1840 | 2021-07-08 | 110400 | keep | 0 | Jul | 2021 | 0.075193 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
FAJARDO | 2021-07-08 05:34 | 2021-07-08 15:31 | 200 | 009:57 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R21070800005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 597 | 2021-07-08 | 119400 | keep | 0 | Jul | 2021 | 0.081323 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-07-08 05:37 | 2021-07-08 05:39 | 2888 | 000:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR | A21070800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-07-08 | 5776 | keep | 0 | Jul | 2021 | 0.003934 | 0.001967 | Momentary | FALSE | FALSE | Not_TMED_Event | 2888
VEGA BAJA | 2021-07-08 05:43 | 2021-07-08 08:34 | 40 | 002:51 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA SE REALIZO PRUEBA A TRANSFORMADOR | B21070800002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 171 | 2021-07-08 | 6840 | keep | 0 | Jul | 2021 | 0.0046587 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-07-08 06:12 | 2021-07-08 06:13 | 1922 | 000:01 | T | ERROR HUMANO | RECIERRE | C21070800007 | New_Event | Human Error | Include | Include | Other | 1 | 2021-07-08 | 1922 | keep | 0 | Jul | 2021 | 0.0013091 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
UTUADO | 2021-07-08 06:12 | 2021-07-08 16:25 | 30 | 010:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 Y 1 X 40 EN CONVERTIDOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21070800009 | New_Event | Bad Weather | Include | Include | Weather | 613 | 2021-07-08 | 18390 | keep | 0 | Jul | 2021 | 0.012525 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-07-08 06:13 | 2021-07-08 18:00 | 80 | 011:47 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070800007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 707 | 2021-07-08 | 56560 | keep | 0 | Jul | 2021 | 0.038523 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-07-08 06:19 | 2021-07-08 06:20 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1909-08 | S21070800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-08 | 2435 | keep | 0 | Jul | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-07-08 06:19 | 2021-07-08 06:20 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVANDO LA CARGA DEL 1907-5 | S21070800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-08 | 2956 | keep | 0 | Jul | 2021 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
CAGUAS | 2021-07-08 06:24 | 2021-07-08 11:37 | 6 | 005:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR REPTIL | C21070800009 | New_Event |  |  | Include | Wildlife | 313 | 2021-07-08 | 1878 | keep | 0 | Jul | 2021 | 0.0012791 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-07-08 06:45 | 2021-07-08 09:44 | 90 | 002:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21070800011 | New_Event | Bad Weather | Include | Include | Weather | 179 | 2021-07-08 | 16110 | keep | 0 | Jul | 2021 | 0.010972 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
FAJARDO | 2021-07-08 06:52 | 2021-07-08 08:25 | 1234 | 001:33 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO LLEVANDO LA CARGA DEL 2305-02 SE ABRIO N/O CONTRA EL 2305-02 Y SE CERRO INTERRUPTOR 2005-10 | R21070800000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 93 | 2021-07-08 | 114762 | keep | 0 | Jul | 2021 | 0.078164 | 0.00084047 | Sustained | FALSE | FALSE | Not_TMED_Event | 1234
CANOVANAS | 2021-07-08 06:52 | 2021-07-08 09:18 | 3012 | 002:26 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO EL ALIMENTADOR CARGA POR EL 2005-10 | R21070800000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 146 | 2021-07-08 | 439752 | keep | 0 | Jul | 2021 | 0.29951 | 0.0020515 | Sustained | FALSE | FALSE | Not_TMED_Event | 3012
FAJARDO | 2021-07-08 06:53 | 2021-07-08 06:58 | 1902 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21070800016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-07-08 | 9510 | keep | 0 | Jul | 2021 | 0.0064772 | 0.0012954 | Momentary | FALSE | TRUE | Not_TMED_Event | 1902
FAJARDO | 2021-07-08 06:53 | 2021-07-08 06:58 | 970 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21070800016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-07-08 | 4850 | keep | 0 | Jul | 2021 | 0.0033033 | 0.00066066 | Momentary | FALSE | TRUE | Not_TMED_Event | 970
FAJARDO | 2021-07-08 06:53 | 2021-07-08 06:58 | 3003 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21070800016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-07-08 | 15015 | keep | 0 | Jul | 2021 | 0.010227 | 0.0020453 | Momentary | FALSE | TRUE | Not_TMED_Event | 3003
FAJARDO | 2021-07-08 06:53 | 2021-07-08 06:58 | 2343 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21070800031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-07-08 | 11715 | keep | 0 | Jul | 2021 | 0.007979 | 0.0015958 | Momentary | FALSE | TRUE | Not_TMED_Event | 2343
FAJARDO | 2021-07-08 06:53 | 2021-07-08 06:58 | 1830 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21070800031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-07-08 | 9150 | keep | 0 | Jul | 2021 | 0.006232 | 0.0012464 | Momentary | FALSE | TRUE | Not_TMED_Event | 1830
FAJARDO | 2021-07-08 06:53 | 2021-07-08 06:58 | 710 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21070800031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-07-08 | 3550 | keep | 0 | Jul | 2021 | 0.0024179 | 0.00048358 | Momentary | FALSE | TRUE | Not_TMED_Event | 710
FAJARDO | 2021-07-08 06:53 | 2021-07-08 06:58 | 969 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21070800031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-07-08 | 4845 | keep | 0 | Jul | 2021 | 0.0032999 | 0.00065998 | Momentary | FALSE | TRUE | Not_TMED_Event | 969
GUAYAMA | 2021-07-08 07:00 | 2021-07-08 11:10 | 50 | 004:10 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA DESGANCHE | P2107080000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 250 | 2021-07-08 | 12500 | keep | 0 | Jul | 2021 | 0.0085137 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-08 07:00 | 2021-07-08 17:40 | 1 | 010:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M21070800000 | New_Event | Wire Down | Include | Include | Equipment | 640 | 2021-07-08 | 640 | keep | 0 | Jul | 2021 | 0.0004359 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-07-08 07:04 | 2021-07-08 15:25 | 50 | 008:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21070800012 | New_Event | Bad Weather | Include | Include | Weather | 501 | 2021-07-08 | 25050 | keep | 0 | Jul | 2021 | 0.017061 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-07-08 07:06 | 2021-07-08 08:35 | 900 | 001:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 80 EN CORTE DE LINEA IMPACTO DE AUTO | A21070800015 | New_Event |  |  | Include | Wildlife | 89 | 2021-07-08 | 80100 | keep | 0 | Jul | 2021 | 0.054556 | 0.00061299 | Sustained | FALSE | TRUE | Not_TMED_Event | 900
ARECIBO | 2021-07-08 07:08 | 2021-07-08 12:06 | 700 | 004:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE | A21070800016 | New_Event | Wire Down | Include | Include | Equipment | 298 | 2021-07-08 | 208600 | keep | 0 | Jul | 2021 | 0.14208 | 0.00047677 | Sustained | FALSE | FALSE | Not_TMED_Event | 700
CANOVANAS | 2021-07-08 07:12 | 2021-07-08 10:21 | 1 | 003:09 | P | NO SE REPORTO CAUSA | 1 SMU 20 DE 20 AMP EN TRANSCLOSURE | R21070800014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 189 | 2021-07-08 | 189 | keep | 0 | Jul | 2021 | 0.00012873 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-07-08 07:13 | 2021-07-11 09:49 | 58 | 074:36 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | B21070800012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 4476 | 2021-07-08 | 259608 | keep | 0 | Jul | 2021 | 0.17682 | 3.9504e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 58
CANOVANAS | 2021-07-08 07:18 | 2021-07-08 08:24 | 10 | 001:06 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR | R21070800019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2021-07-08 | 660 | keep | 0 | Jul | 2021 | 0.00044952 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-07-08 07:21 | 2021-07-08 17:15 | 65 | 009:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 Y 1 X 50 EN CORTES DE LINEA CRUCE POR AVE | C21070800014 | New_Event |  |  | Include | Wildlife | 594 | 2021-07-08 | 38610 | keep | 0 | Jul | 2021 | 0.026297 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
MAYAGÃœEZ | 2021-07-08 07:35 | 2021-07-08 16:45 | 30 | 009:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE CORTE DE LINEA | M21070800025 | New_Event | Wire Down | Include | Include | Equipment | 550 | 2021-07-08 | 16500 | keep | 0 | Jul | 2021 | 0.011238 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BARRANQUITAS | 2021-07-08 07:43 | 2021-07-08 13:06 | 40 | 005:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO BAJANTE DE LINEA A CAJA | C21070800015 | New_Event | Wire Down | Include | Include | Equipment | 323 | 2021-07-08 | 12920 | keep | 0 | Jul | 2021 | 0.0087998 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-08 07:52 | 2021-07-08 09:35 | 40 | 001:43 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S21070700036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 103 | 2021-07-08 | 4120 | keep | 0 | Jul | 2021 | 0.0028061 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-07-08 08:04 | 2021-07-08 16:41 | 15 | 008:37 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR LA MISMA CAPACIDAD | A21070800023 | New_Event | Service Transformer Failure | Include | Include | Equipment | 517 | 2021-07-08 | 7755 | keep | 0 | Jul | 2021 | 0.0052819 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-07-08 08:08 | 2021-07-08 13:30 | 300 | 005:22 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070800029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 322 | 2021-07-08 | 96600 | keep | 0 | Jul | 2021 | 0.065794 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
GUAYAMA | 2021-07-08 08:10 | 2021-07-08 09:56 | 45 | 001:46 | P | DESGANCHE | 1 X 50 CORTE DE LINEA DESGANCHE | P21060800007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2021-07-08 | 4770 | keep | 0 | Jul | 2021 | 0.0032488 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
MAYAGÃœEZ | 2021-07-08 08:21 | 2021-07-08 16:00 | 100 | 007:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | M21070800040 | New_Event |  |  | Include | Wildlife | 459 | 2021-07-08 | 45900 | keep | 0 | Jul | 2021 | 0.031262 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-08 08:32 | 2021-07-08 18:43 | 5 | 010:11 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21070800007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 611 | 2021-07-08 | 3055 | keep | 0 | Jul | 2021 | 0.0020807 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
AGUADILLA | 2021-07-08 08:33 | 2021-07-08 15:04 | 100 | 006:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA | M21070700061 | New_Event | Wire Down | Include | Include | Equipment | 391 | 2021-07-08 | 39100 | keep | 0 | Jul | 2021 | 0.026631 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-07-08 08:38 | 2021-07-08 15:20 | 2 | 006:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | M21070600032 | New_Event | Cutout Failure | Include | Include | Equipment | 402 | 2021-07-08 | 804 | keep | 0 | Jul | 2021 | 0.0005476 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2021-07-08 08:50 | 2021-07-08 14:11 | 75 | 005:21 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21070800030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 321 | 2021-07-08 | 24075 | keep | 0 | Jul | 2021 | 0.016397 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
ARECIBO | 2021-07-08 08:52 | 2021-07-08 12:35 | 12 | 003:43 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50KVA X 50 KVA | A21070800000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 223 | 2021-07-08 | 2676 | keep | 0 | Jul | 2021 | 0.0018226 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-07-08 08:56 | 2021-07-08 12:10 | 100 | 003:14 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | S21070800010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2021-07-08 | 19400 | keep | 0 | Jul | 2021 | 0.013213 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-07-08 09:00 | 2021-07-08 15:50 | 200 | 006:50 | P | ESTRUCTURA AVERIADA | SE ABRE CORTE DE LINEA PARA CAMBIAR POSTE PRIMARIO PARTIDO Y SE CERRO CORTE DE LINEA | P21070800011 | New_Event | Defective Pole | Include | Include | Equipment | 410 | 2021-07-08 | 82000 | keep | 0 | Jul | 2021 | 0.05585 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-07-08 09:04 | 2021-07-09 09:28 | 80 | 024:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN COIRTE DE LINEA MAL TIEMPO | M21070800051 | New_Event | Bad Weather | Include | Include | Weather | 1464 | 2021-07-08 | 117120 | keep | 0 | Jul | 2021 | 0.07977 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
UTUADO | 2021-07-08 09:09 | 2021-07-08 14:15 | 80 | 005:06 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A21070800029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 306 | 2021-07-08 | 24480 | keep | 0 | Jul | 2021 | 0.016673 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BARRANQUITAS | 2021-07-08 09:10 | 2021-07-08 14:38 | 30 | 005:28 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21070800033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 328 | 2021-07-08 | 9840 | keep | 0 | Jul | 2021 | 0.006702 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-07-08 09:11 | 2021-07-10 09:25 | 10 | 048:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | C21070800034 | New_Event | Bad Weather | Include | Include | Weather | 2894 | 2021-07-08 | 28940 | keep | 0 | Jul | 2021 | 0.019711 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CANOVANAS | 2021-07-08 09:18 | 2021-07-08 14:00 | 2000 | 004:42 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADORES Y CERRO MACHETES | R21070800000 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 282 | 2021-07-08 | 564000 | keep | 0 | Jul | 2021 | 0.38414 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-07-08 09:38 | 2021-07-08 17:34 | 10 | 007:56 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA X 37.5KVA | B21070800027 | New_Event | Service Transformer Failure | Include | Include | Equipment | 476 | 2021-07-08 | 4760 | keep | 0 | Jul | 2021 | 0.003242 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-07-08 09:48 | 2021-07-08 14:11 | 200 | 004:23 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | C21070800040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2021-07-08 | 52600 | keep | 0 | Jul | 2021 | 0.035826 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-07-08 09:50 | 2021-07-10 09:35 | 20 | 047:45 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | B21070800030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2865 | 2021-07-08 | 57300 | keep | 0 | Jul | 2021 | 0.039027 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-07-08 10:02 | 2021-07-08 12:18 | 10 | 002:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO THREE WIRE ZAFADO EN TRANSFORMADOR | M21070700067 | New_Event | Wire Down | Include | Include | Equipment | 136 | 2021-07-08 | 1360 | keep | 0 | Jul | 2021 | 0.00092629 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-07-08 10:04 | 2021-07-08 20:01 | 40 | 009:57 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C21070800044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 597 | 2021-07-08 | 23880 | keep | 0 | Jul | 2021 | 0.016265 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-07-08 10:09 | 2021-07-08 14:33 | 8 | 004:24 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR DERRAMANDO ACEITE DE 37.5 KVA X 50 KVA | C21070800046 | New_Event | Service Transformer Failure | Include | Include | Equipment | 264 | 2021-07-08 | 2112 | keep | 0 | Jul | 2021 | 0.0014385 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-07-08 10:09 | 2021-07-08 11:33 | 20 | 001:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | A21070800018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 84 | 2021-07-08 | 1680 | keep | 0 | Jul | 2021 | 0.0011442 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-07-08 10:21 | 2021-07-08 12:54 | 250 | 002:33 | P | NO SE REPORTO CAUSA | 1 X 80 EN LA ENTRADA DEL CONVERTIDOR | R21070800070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 153 | 2021-07-08 | 38250 | keep | 0 | Jul | 2021 | 0.026052 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
YAUCO | 2021-07-08 10:21 | 2021-07-09 14:05 | 20 | 027:44 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA POR FUERTES VIENTOS Y DESGANCHE | P21070800013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1664 | 2021-07-08 | 33280 | keep | 0 | Jul | 2021 | 0.022667 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
UTUADO | 2021-07-08 10:39 | 2021-07-09 21:10 | 10 | 034:31 | P | ESTRUCTURA AVERIADA | REMPLAZO POSTE PRIMARIO CON TRANSFORMADOR SE CERRO CORTE DE LINEA | A21070800038 | New_Event | Defective Pole | Include | Include | Equipment | 2071 | 2021-07-08 | 20710 | keep | 0 | Jul | 2021 | 0.014105 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-07-08 10:54 | 2021-07-08 10:55 | 1342 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21070800050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-08 | 1342 | keep | 0 | Jul | 2021 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
CAGUAS | 2021-07-08 10:55 | 2021-07-09 14:30 | 40 | 027:35 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C21070800053 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1655 | 2021-07-08 | 66200 | keep | 0 | Jul | 2021 | 0.045089 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-07-08 11:06 | 2021-07-08 14:30 | 705 | 003:24 | S | DESGANCHE | SE RETIRO BAMBUAS CAIDAS SOBRE LAS LINEAS Y SE CERRO EL INTERRUPTOR PORTATIL QUE ESTA LLEVANDO LA CARGA DE LA SUBESTACION | A21070800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2021-07-08 | 143820 | keep | 0 | Jul | 2021 | 0.097955 | 0.00048017 | Sustained | FALSE | TRUE | Not_TMED_Event | 705
UTUADO | 2021-07-08 11:06 | 2021-07-08 14:30 | 1521 | 003:24 | S | DESGANCHE | SE RETIRO BAMBUAS CAIDAS SOBRE LAS LINEAS Y SE CERRO EL INTERRUPTOR PORTATIL QUE ESTA LLEVANDO LA CARGA DE LA SUBESTACION | A21070800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2021-07-08 | 310284 | keep | 0 | Jul | 2021 | 0.21133 | 0.0010359 | Sustained | FALSE | TRUE | Not_TMED_Event | 1521
UTUADO | 2021-07-08 11:06 | 2021-07-08 14:30 | 882 | 003:24 | S | DESGANCHE | SE RETIRO BAMBUAS CAIDAS SOBRE LAS LINEAS Y SE CERRO EL INTERRUPTOR PORTATIL QUE ESTA LLEVANDO LA CARGA DE LA SUBESTACION | A21070800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2021-07-08 | 179928 | keep | 0 | Jul | 2021 | 0.12255 | 0.00060073 | Sustained | FALSE | TRUE | Not_TMED_Event | 882
ARECIBO | 2021-07-08 11:15 | 2021-07-08 17:00 | 29 | 005:45 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR POSTE PRIMARIO | A21070800000 | New_Event | Defective Pole | Include | Include | Equipment | 345 | 2021-07-08 | 10005 | keep | 0 | Jul | 2021 | 0.0068144 | 1.9752e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 29
ARECIBO | 2021-07-08 11:15 | 2021-07-08 13:00 | 5 | 001:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA ROTA POR CAMION | A21070800000 | New_Event |  |  | Include | Wildlife | 105 | 2021-07-08 | 525 | keep | 0 | Jul | 2021 | 0.00035758 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
UTUADO | 2021-07-08 11:30 | 2021-07-08 18:15 | 20 | 006:45 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21070800052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 405 | 2021-07-08 | 8100 | keep | 0 | Jul | 2021 | 0.0055169 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-07-08 11:39 | 2021-07-10 12:34 | 1 | 048:55 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA REMPLAZO PARARRAYO | C21070800054 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 2935 | 2021-07-08 | 2935 | keep | 0 | Jul | 2021 | 0.001999 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-07-08 11:40 | 2021-07-08 22:00 | 50 | 010:20 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO SE CERRO CORTE DE LINEA | M21070800000 | New_Event | Defective Pole | Include | Include | Equipment | 620 | 2021-07-08 | 31000 | keep | 0 | Jul | 2021 | 0.021114 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-07-08 11:48 | 2021-07-08 14:18 | 100 | 002:30 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | P21070800018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2021-07-08 | 15000 | keep | 0 | Jul | 2021 | 0.010216 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-07-08 11:53 | 2021-07-08 16:22 | 30 | 004:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | M21070800087 | New_Event |  |  | Include | Wildlife | 269 | 2021-07-08 | 8070 | keep | 0 | Jul | 2021 | 0.0054964 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-07-08 11:57 | 2021-07-08 15:23 | 50 | 003:26 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21070800062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2021-07-08 | 10300 | keep | 0 | Jul | 2021 | 0.0070153 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-07-08 11:58 | 2021-07-08 16:00 | 50 | 004:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y 1 X 20 EN TRANSFORMADOR POR DESGANCHE | P21070800019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2021-07-08 | 12100 | keep | 0 | Jul | 2021 | 0.0082413 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-08 12:17 | 2021-07-08 12:18 | 32 | 000:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S21070800003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-08 | 32 | keep | 0 | Jul | 2021 | 2.1795e-05 | 2.1795e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 32
ARECIBO | 2021-07-08 12:18 | 2021-07-08 21:06 | 75 | 008:48 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 40 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DE AISLADORES | A21070800064 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 528 | 2021-07-08 | 39600 | keep | 0 | Jul | 2021 | 0.026971 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-07-08 12:22 | 2021-07-10 20:17 | 1 | 055:55 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR 25KVA | B21070800046 | New_Event | Service Transformer Failure | Include | Include | Equipment | 3355 | 2021-07-08 | 3355 | keep | 0 | Jul | 2021 | 0.0022851 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-07-08 12:31 | 2021-07-08 13:23 | 250 | 000:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 50 EN CORTE DE LINEA | A21070700070 | New_Event | Wire Down | Include | Include | Equipment | 52 | 2021-07-08 | 13000 | keep | 0 | Jul | 2021 | 0.0088542 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
ARECIBO | 2021-07-08 12:41 | 2021-07-08 16:00 | 10 | 003:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTES SECUNDARIOS EN TRANSFORMADOR | A21070800069 | New_Event | Secondary Wire Down | Include | Include | Equipment | 199 | 2021-07-08 | 1990 | keep | 0 | Jul | 2021 | 0.0013554 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-07-08 13:01 | 2021-07-08 13:02 | 2302 | 000:01 | T | DESGANCHE | RECIERRE | C21070800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-08 | 2302 | keep | 0 | Jul | 2021 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
CAGUAS | 2021-07-08 13:02 | 2021-07-09 18:17 | 500 | 029:15 | P | DESGANCHE | SE DESGANCHO LEVANTO CONDUCTOR Y CERRO MACHETES | C21070800062 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1755 | 2021-07-08 | 877500 | keep | 0 | Jul | 2021 | 0.59766 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
PONCE | 2021-07-08 13:08 | 2021-07-08 21:00 | 100 | 007:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO DE MACHETE | P21070800021 | New_Event | Wire Down | Include | Include | Equipment | 472 | 2021-07-08 | 47200 | keep | 0 | Jul | 2021 | 0.032148 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2021-07-08 13:08 | 2021-07-09 12:52 | 1 | 023:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA POR CONTACTO DE AVE | P21070800020 | New_Event |  |  | Include | Wildlife | 1424 | 2021-07-08 | 1424 | keep | 0 | Jul | 2021 | 0.00096988 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-07-08 13:10 | 2021-07-08 18:40 | 300 | 005:30 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070800108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 330 | 2021-07-08 | 99000 | keep | 0 | Jul | 2021 | 0.067428 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
CAGUAS | 2021-07-08 13:12 | 2021-07-11 18:03 | 16 | 076:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR REEMPLAZO CAJA TRANSFORMADOR | C21070800064 | New_Event | Cutout Failure | Include | Include | Equipment | 4611 | 2021-07-08 | 73776 | keep | 0 | Jul | 2021 | 0.050248 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
AGUADILLA | 2021-07-08 13:13 | 2021-07-08 20:11 | 12 | 006:58 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO 50 KVA X 50 KVA | M21070800109 | New_Event | Service Transformer Failure | Include | Include | Equipment | 418 | 2021-07-08 | 5016 | keep | 0 | Jul | 2021 | 0.0034164 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-07-08 13:30 | 2021-07-08 19:09 | 14 | 005:39 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR LA MISMA CAPACIDAD | A21070800000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 339 | 2021-07-08 | 4746 | keep | 0 | Jul | 2021 | 0.0032325 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2021-07-08 13:31 | 2021-07-09 17:29 | 30 | 027:58 | P | NO SE REPORTO CAUSA | 1 X 25 EN PROVISIONAL AEREO | B21070800057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1678 | 2021-07-08 | 50340 | keep | 0 | Jul | 2021 | 0.034286 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2021-07-08 13:54 | 2021-07-10 12:01 | 100 | 046:07 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | C21070800072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2767 | 2021-07-08 | 276700 | keep | 0 | Jul | 2021 | 0.18846 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-08 13:58 | 2021-07-08 13:59 | 222 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO TRES VECES LLEVANDO LA CARGA DEL 1909-09 | S21070800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-08 | 222 | keep | 0 | Jul | 2021 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2021-07-08 13:58 | 2021-07-08 13:59 | 4456 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO CARGA POR EL 1907-03 | S21070800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-08 | 4456 | keep | 0 | Jul | 2021 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
BAYAMON | 2021-07-08 13:59 | 2021-07-08 16:46 | 75 | 002:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO LLEVANDO LA CARGA DEL 1909-09 | S21070800068 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 167 | 2021-07-08 | 12525 | keep | 0 | Jul | 2021 | 0.0085307 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2021-07-08 14:10 | 2021-07-08 16:26 | 80 | 002:16 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21070800077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2021-07-08 | 10880 | keep | 0 | Jul | 2021 | 0.0074103 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
UTUADO | 2021-07-08 14:11 | 2021-07-09 15:35 | 100 | 025:24 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21070800087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1524 | 2021-07-08 | 152400 | keep | 0 | Jul | 2021 | 0.1038 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-07-08 14:12 | 2021-07-09 13:35 | 40 | 023:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21070800088 | New_Event | Bad Weather | Include | Include | Weather | 1403 | 2021-07-08 | 56120 | keep | 0 | Jul | 2021 | 0.038223 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-07-08 14:13 | 2021-07-10 15:41 | 5 | 049:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21070800089 | New_Event | Bad Weather | Include | Include | Weather | 2968 | 2021-07-08 | 14840 | keep | 0 | Jul | 2021 | 0.010107 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-07-08 14:20 | 2021-07-08 16:20 | 514 | 002:00 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7500 SE PATRULLO SE ENCONTRO PUENTE ABIERTO 7515B Y 7517 | S21070800030 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2021-07-08 | 61680 | keep | 0 | Jul | 2021 | 0.04201 | 0.00035008 | Sustained | FALSE | TRUE | Not_TMED_Event | 514
BAYAMON | 2021-07-08 14:20 | 2021-07-08 16:20 | 681 | 002:00 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7500 SE PATRULLO SE ENCONTRO PUENTE ABIERTO 7515B Y 7517 | S21070800030 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2021-07-08 | 81720 | keep | 0 | Jul | 2021 | 0.055659 | 0.00046383 | Sustained | FALSE | TRUE | Not_TMED_Event | 681
BAYAMON | 2021-07-08 14:20 | 2021-07-08 16:20 | 752 | 002:00 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7500 SE PATRULLO SE ENCONTRO PUENTE ABIERTO 7515B Y 7517 | S21070800030 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2021-07-08 | 90240 | keep | 0 | Jul | 2021 | 0.061462 | 0.00051218 | Sustained | FALSE | TRUE | Not_TMED_Event | 752
BAYAMON | 2021-07-08 14:20 | 2021-07-08 16:20 | 68 | 002:00 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7500 SE PATRULLO SE ENCONTRO PUENTE ABIERTO 7515B Y 7517 | S21070800030 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2021-07-08 | 8160 | keep | 0 | Jul | 2021 | 0.0055577 | 4.6314e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 68
PONCE | 2021-07-08 14:31 | 2021-07-08 18:00 | 100 | 003:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA QUEMADA DE CORTE DE LINEA | P21070800029 | New_Event | Cutout Failure | Include | Include | Equipment | 209 | 2021-07-08 | 20900 | keep | 0 | Jul | 2021 | 0.014235 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-07-08 14:33 | 2021-07-08 21:48 | 150 | 007:15 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070800128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 435 | 2021-07-08 | 65250 | keep | 0 | Jul | 2021 | 0.044441 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
FAJARDO | 2021-07-08 14:38 | 2021-07-08 16:48 | 100 | 002:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 Y 1 X 40 EN CORTES DE LINEA CRUCE CON AVE | R21070800084 | New_Event |  |  | Include | Wildlife | 130 | 2021-07-08 | 13000 | keep | 0 | Jul | 2021 | 0.0088542 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
YAUCO | 2021-07-08 14:40 | 2021-07-09 15:30 | 50 | 024:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA QUEMADA | P21070800030 | New_Event | Cutout Failure | Include | Include | Equipment | 1490 | 2021-07-08 | 74500 | keep | 0 | Jul | 2021 | 0.050742 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-08 15:00 | 2021-07-08 19:11 | 300 | 004:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 200 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21070700194 | New_Event | Wire Down | Include | Include | Equipment | 251 | 2021-07-08 | 75300 | keep | 0 | Jul | 2021 | 0.051286 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
SAN JUAN | 2021-07-08 15:01 | 2021-07-08 17:20 | 162 | 002:19 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S21070800037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 139 | 2021-07-08 | 22518 | keep | 0 | Jul | 2021 | 0.015337 | 0.00011034 | Sustained | FALSE | TRUE | Not_TMED_Event | 162
ARECIBO | 2021-07-08 15:17 | 2021-07-08 17:42 | 180 | 002:25 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO ENCONTRARON CAUSA | A21070800092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2021-07-08 | 26100 | keep | 0 | Jul | 2021 | 0.017777 | 0.0001226 | Sustained | FALSE | TRUE | Not_TMED_Event | 180
HUMACAO | 2021-07-08 15:23 | 2021-07-09 09:33 | 40 | 018:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO BAJANTE DE LINEA A CAJA | C21070800093 | New_Event | Wire Down | Include | Include | Equipment | 1090 | 2021-07-08 | 43600 | keep | 0 | Jul | 2021 | 0.029696 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-07-08 15:27 | 2021-07-08 16:54 | 100 | 001:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21070800096 | New_Event | Bad Weather | Include | Include | Weather | 87 | 2021-07-08 | 8700 | keep | 0 | Jul | 2021 | 0.0059255 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-07-08 15:40 | 2021-07-08 19:23 | 300 | 003:43 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 40 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DE AISLADORES | A21070800000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 223 | 2021-07-08 | 66900 | keep | 0 | Jul | 2021 | 0.045565 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
PONCE | 2021-07-08 15:47 | 2021-07-10 08:20 | 25 | 040:33 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | P21070900041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2433 | 2021-07-08 | 60825 | keep | 0 | Jul | 2021 | 0.041428 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-07-08 15:50 | 2021-07-08 15:55 | 948 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO CON RECIERRE EN OFF CARGA POR EL 1120-10 SE CERRO POR SCADA | S21070800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-07-08 | 4740 | keep | 0 | Jul | 2021 | 0.0032284 | 0.00064568 | Momentary | FALSE | FALSE | Not_TMED_Event | 948
BAYAMON | 2021-07-08 15:50 | 2021-07-08 15:55 | 1 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO CON RECIERRE EN OFF LLEVA LA CARGA DEL 1014-18 SE CERRO POR SCADA | S21070800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-07-08 | 5 | keep | 0 | Jul | 2021 | 3.4055e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-07-08 15:51 | 2021-07-08 16:42 | 5 | 000:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21070800101 | New_Event | Secondary Wire Down | Include | Include | Equipment | 51 | 2021-07-08 | 255 | keep | 0 | Jul | 2021 | 0.00017368 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-07-08 16:09 | 2021-07-08 20:55 | 150 | 004:46 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA DESGANCHO Y LEVANTO CONDUCTOR | C21070800104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 286 | 2021-07-08 | 42900 | keep | 0 | Jul | 2021 | 0.029219 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-07-08 16:14 | 2021-07-08 19:32 | 311 | 003:18 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21070800060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2021-07-08 | 61578 | keep | 0 | Jul | 2021 | 0.04194 | 0.00021182 | Sustained | FALSE | TRUE | Not_TMED_Event | 311
HUMACAO | 2021-07-08 16:23 | 2021-07-09 11:14 | 4 | 018:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21070800106 | New_Event | Bad Weather | Include | Include | Weather | 1131 | 2021-07-08 | 4524 | keep | 0 | Jul | 2021 | 0.0030813 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2021-07-08 16:32 | 2021-07-08 18:30 | 80 | 001:58 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070800158 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2021-07-08 | 9440 | keep | 0 | Jul | 2021 | 0.0064295 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-07-08 16:33 | 2021-07-10 10:39 | 7 | 042:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO CORTE DE LINEA PARA REMPLAZAR BUSHING SECUNDARIO | C21070800109 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2526 | 2021-07-08 | 17682 | keep | 0 | Jul | 2021 | 0.012043 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
BAYAMON | 2021-07-08 16:41 | 2021-07-08 16:43 | 514 | 000:02 | S | LINEA DE TRANSMISION 38KV | SE ABRE LINEA 7500 PARA PODER CERRAR EL 7517 DE BPPR | S21070800030 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-08 | 1028 | keep | 0 | Jul | 2021 | 0.00070017 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-07-08 16:41 | 2021-07-08 16:43 | 681 | 000:02 | S | LINEA DE TRANSMISION 38KV | SE ABRE LINEA 7500 PARA PODER CERRAR EL 7517 DE BPPR | S21070800030 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-08 | 1362 | keep | 0 | Jul | 2021 | 0.00092765 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-07-08 16:41 | 2021-07-08 16:43 | 752 | 000:02 | S | LINEA DE TRANSMISION 38KV | SE ABRE LINEA 7500 PARA PODER CERRAR EL 7517 DE BPPR | S21070800030 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-08 | 1504 | keep | 0 | Jul | 2021 | 0.0010244 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-07-08 16:41 | 2021-07-08 16:43 | 68 | 000:02 | S | LINEA DE TRANSMISION 38KV | SE ABRE LINEA 7500 PARA PODER CERRAR EL 7517 DE BPPR | S21070800030 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-08 | 136 | keep | 0 | Jul | 2021 | 9.2629e-05 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-07-08 16:46 | 2021-07-08 17:46 | 222 | 001:00 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE PRIMARIO LLEVANDO LA CARGA DEL 1909-09 | S21070800068 | Additional_clients | Wire Down | Include | Include | Equipment | 60 | 2021-07-08 | 13320 | keep | 0 | Jul | 2021 | 0.0090722 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-08 16:46 | 2021-07-08 17:46 | 4456 | 001:00 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE PRIMARIO CARGA POR EL 1907-03 | S21070800068 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 60 | 2021-07-08 | 267360 | keep | 0 | Jul | 2021 | 0.1821 | 0.003035 | Sustained | FALSE | FALSE | Not_TMED_Event | 4456
GUAYAMA | 2021-07-08 16:48 | 2021-07-09 07:50 | 12 | 015:02 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | P21070800049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 902 | 2021-07-08 | 10824 | keep | 0 | Jul | 2021 | 0.0073722 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-07-08 16:52 | 2021-07-08 17:30 | 10 | 000:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21070800028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 38 | 2021-07-08 | 380 | keep | 0 | Jul | 2021 | 0.00025882 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-08 16:59 | 2021-07-08 19:45 | 5 | 002:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M21070800160 | New_Event | Wire Down | Include | Include | Equipment | 166 | 2021-07-08 | 830 | keep | 0 | Jul | 2021 | 0.00056531 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-07-08 17:01 | 2021-07-09 16:50 | 20 | 023:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA | P21070800054 | New_Event | Wire Down | Include | Include | Equipment | 1429 | 2021-07-08 | 28580 | keep | 0 | Jul | 2021 | 0.019466 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-07-08 17:02 | 2021-07-08 21:17 | 400 | 004:15 | P | DESGANCHE | 2 X 80 Y 1 X 50 EN CORTES DE LINEA SE REALIZO DESGANCHE MASIVO | A21070800108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 255 | 2021-07-08 | 102000 | keep | 0 | Jul | 2021 | 0.069472 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
BAYAMON | 2021-07-08 17:16 | 2021-07-08 17:17 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1909-08 | S21070800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-08 | 2435 | keep | 0 | Jul | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-07-08 17:16 | 2021-07-08 17:17 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVANDO LA CARGA DEL 1907-5 | S21070800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-08 | 2956 | keep | 0 | Jul | 2021 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
SAN JUAN | 2021-07-08 17:27 | 2021-07-08 17:30 | 2203 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO CON RECIERRE EN OFF SE PROBO POR CONTROL QUEDO EN SERVICIO | S21070800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-07-08 | 6609 | keep | 0 | Jul | 2021 | 0.0045014 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
GUAYAMA | 2021-07-08 17:27 | 2021-07-09 07:50 | 12 | 014:23 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | P21070800056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 863 | 2021-07-08 | 10356 | keep | 0 | Jul | 2021 | 0.0070534 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-07-08 17:49 | 2021-07-08 19:20 | 200 | 001:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR LINEA ARREADA | M21070800176 | New_Event | Wire Down | Include | Include | Equipment | 91 | 2021-07-08 | 18200 | keep | 0 | Jul | 2021 | 0.012396 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
AGUADILLA | 2021-07-08 17:50 | 2021-07-08 20:15 | 543 | 002:25 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RETIRO LINEA VACANTE PARTIDA SE CERRO INTERRUPTOR | M21070800165 | New_Event | Wire Down | Include | Include | Equipment | 145 | 2021-07-08 | 78735 | keep | 0 | Jul | 2021 | 0.053626 | 0.00036983 | Sustained | FALSE | TRUE | Not_TMED_Event | 543
BAYAMON | 2021-07-08 17:54 | 2021-07-08 17:56 | 320 | 000:02 | T | NO SE REPORTO CAUSA | INTERRUPTOR DISPARO Y SE CERRO POR CONTROL | B21070800069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-08 | 640 | keep | 0 | Jul | 2021 | 0.0004359 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
PONCE | 2021-07-08 18:30 | 2021-07-09 19:40 | 15 | 025:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE RERPARO SECUNDARIA | P21070800052 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1510 | 2021-07-08 | 22650 | keep | 0 | Jul | 2021 | 0.015427 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-07-08 19:03 | 2021-07-09 16:15 | 80 | 021:12 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21070800115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1272 | 2021-07-08 | 101760 | keep | 0 | Jul | 2021 | 0.069308 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CANOVANAS | 2021-07-08 19:06 | 2021-07-08 22:04 | 4 | 002:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA CONTACTO ELECTRICO | R21070800093 | New_Event |  |  | Include | Wildlife | 178 | 2021-07-08 | 712 | keep | 0 | Jul | 2021 | 0.00048494 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
BAYAMON | 2021-07-08 19:34 | 2021-07-08 19:35 | 3511 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21070800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-08 | 3511 | keep | 0 | Jul | 2021 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
CAGUAS | 2021-07-08 19:45 | 2021-07-10 15:19 | 10 | 043:34 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR AVERIADO DE 15KVA | C21070800128 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2614 | 2021-07-08 | 26140 | keep | 0 | Jul | 2021 | 0.017804 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-07-08 19:46 | 2021-07-09 09:30 | 100 | 013:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C21070800130 | New_Event |  |  | Include | Wildlife | 824 | 2021-07-08 | 82400 | keep | 0 | Jul | 2021 | 0.056122 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-07-08 20:04 | 2021-07-09 09:30 | 15 | 013:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | M21070800192 | New_Event | Cutout Failure | Include | Include | Equipment | 806 | 2021-07-08 | 12090 | keep | 0 | Jul | 2021 | 0.0082344 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-07-08 20:15 | 2021-07-08 22:30 | 25 | 002:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE REPARO LINEAS SECUNDARIAS ROTAS | M21070800000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 135 | 2021-07-08 | 3375 | keep | 0 | Jul | 2021 | 0.0022987 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
UTUADO | 2021-07-08 20:18 | 2021-07-09 17:54 | 20 | 021:36 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBÃšES SOBRE LAS LINEAS | A21070800118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1296 | 2021-07-08 | 25920 | keep | 0 | Jul | 2021 | 0.017654 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-07-08 20:35 | 2021-07-09 09:15 | 75 | 012:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 80 1 X 25 EN CORTE DE LINEA | P21070900065 | New_Event |  |  | Include | Wildlife | 760 | 2021-07-08 | 57000 | keep | 0 | Jul | 2021 | 0.038822 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
PONCE | 2021-07-08 20:35 | 2021-07-09 09:15 | 250 | 012:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA POR CONTACTO DE AVE | P21070800075 | New_Event |  |  | Include | Wildlife | 760 | 2021-07-08 | 190000 | keep | 0 | Jul | 2021 | 0.12941 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
MAYAGÃœEZ | 2021-07-08 20:52 | 2021-07-08 20:53 | 1266 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21070800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-08 | 1266 | keep | 0 | Jul | 2021 | 0.00086227 | 0.00086227 | Momentary | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2021-07-08 21:04 | 2021-07-09 10:15 | 60 | 013:11 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | M21070800200 | New_Event | Vegetation Contact | Include | Include | Vegetation | 791 | 2021-07-08 | 47460 | keep | 0 | Jul | 2021 | 0.032325 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-07-08 21:12 | 2021-07-09 10:00 | 75 | 012:48 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070800204 | New_Event | Vegetation Contact | Include | Include | Vegetation | 768 | 2021-07-08 | 57600 | keep | 0 | Jul | 2021 | 0.039231 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-07-08 21:17 | 2021-07-09 09:28 | 150 | 012:11 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA Y 1 X 100 EN CORTE DE LINEA | S21070800098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 731 | 2021-07-08 | 109650 | keep | 0 | Jul | 2021 | 0.074682 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
HUMACAO | 2021-07-08 21:27 | 2021-07-09 12:54 | 20 | 015:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21070800149 | New_Event | Bad Weather | Include | Include | Weather | 927 | 2021-07-08 | 18540 | keep | 0 | Jul | 2021 | 0.012628 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-07-08 21:33 | 2021-07-09 17:30 | 75 | 019:57 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21070800070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1197 | 2021-07-08 | 89775 | keep | 0 | Jul | 2021 | 0.061145 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
PONCE | 2021-07-08 21:35 | 2021-07-09 12:30 | 196 | 014:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | P21070800073 | New_Event | Wire Down | Include | Include | Equipment | 895 | 2021-07-08 | 175420 | keep | 0 | Jul | 2021 | 0.11948 | 0.00013349 | Sustained | FALSE | FALSE | Not_TMED_Event | 196
MAYAGÃœEZ | 2021-07-08 21:46 | 2021-07-08 21:47 | 1266 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21070800000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-08 | 1266 | keep | 0 | Jul | 2021 | 0.00086227 | 0.00086227 | Momentary | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2021-07-08 21:48 | 2021-07-08 21:49 | 637 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M21070800000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-08 | 637 | keep | 0 | Jul | 2021 | 0.00043386 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-08 21:49 | 2021-07-09 13:35 | 150 | 015:46 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070800128 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 946 | 2021-07-08 | 141900 | keep | 0 | Jul | 2021 | 0.096647 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
AGUADILLA | 2021-07-08 21:50 | 2021-07-09 12:04 | 300 | 014:14 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | M21070800210 | New_Event | Vegetation Contact | Include | Include | Vegetation | 854 | 2021-07-08 | 256200 | keep | 0 | Jul | 2021 | 0.1745 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-07-08 22:02 | 2021-07-08 22:03 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21070800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-08 | 393 | keep | 0 | Jul | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
ARECIBO | 2021-07-08 23:33 | 2021-07-08 23:34 | 1628 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21070800000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-07-08 | 1628 | keep | 0 | Jul | 2021 | 0.0011088 | 0.0011088 | Momentary | FALSE | FALSE | Not_TMED_Event | 1628
ARECIBO | 2021-07-08 23:37 | 2021-07-08 23:38 | 1628 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21070800000 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-07-08 | 1628 | keep | 0 | Jul | 2021 | 0.0011088 | 0.0011088 | Momentary | FALSE | FALSE | Not_TMED_Event | 1628
UTUADO | 2021-07-09 01:22 | 2021-07-09 01:23 | 650 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA | A21070900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-09 | 650 | keep | 0 | Jul | 2021 | 0.00044271 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
SAN JUAN | 2021-07-09 02:47 | 2021-07-09 02:50 | 135 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR Y SE CERRO POR CONTROL | S21070900000 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2021-07-09 | 405 | keep | 0 | Jul | 2021 | 0.00027584 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2021-07-09 02:50 | 2021-07-09 15:12 | 1 | 012:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | S21070900010 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 742 | 2021-07-09 | 742 | keep | 0 | Jul | 2021 | 0.00050537 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-07-09 03:50 | 2021-07-09 16:39 | 15 | 012:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CONECTO PUENTE DE LINEA A CAJA | S21070900005 | New_Event | Wire Down | Include | Include | Equipment | 769 | 2021-07-09 | 11535 | keep | 0 | Jul | 2021 | 0.0078564 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CANOVANAS | 2021-07-09 03:53 | 2021-07-09 03:54 | 4188 | 000:01 | T | SECUNDARIA/ESTRUCTURA AVERIADA | RECERRO INTERRUPTOR | R21070900000 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 1 | 2021-07-09 | 4188 | keep | 0 | Jul | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2021-07-09 03:54 | 2021-07-09 17:04 | 25 | 013:10 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR POSTE SECUNDARIO ROTO | R21070900013 | 1st_after_momentary | Secondary Defective Pole | Include | Include | Equipment | 790 | 2021-07-09 | 19750 | keep | 0 | Jul | 2021 | 0.013452 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2021-07-09 04:18 | 2021-07-09 04:19 | 1827 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO INTERRUPTOR | C21070900005 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-09 | 1827 | keep | 0 | Jul | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
HUMACAO | 2021-07-09 04:19 | 2021-07-10 13:01 | 10 | 032:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21070900250 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1962 | 2021-07-09 | 19620 | keep | 0 | Jul | 2021 | 0.013363 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-07-09 04:19 | 2021-07-09 15:23 | 40 | 011:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21070900062 | New_Event | Bad Weather | Include | Include | Weather | 664 | 2021-07-09 | 26560 | keep | 0 | Jul | 2021 | 0.01809 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-09 05:12 | 2021-07-09 14:43 | 60 | 009:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA | B21070900001 | New_Event | Wire Down | Include | Include | Equipment | 571 | 2021-07-09 | 34260 | keep | 0 | Jul | 2021 | 0.023334 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-07-09 05:39 | 2021-07-09 18:20 | 30 | 012:41 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21070900097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 761 | 2021-07-09 | 22830 | keep | 0 | Jul | 2021 | 0.015549 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-07-09 05:41 | 2021-07-09 14:16 | 40 | 008:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21070900002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 515 | 2021-07-09 | 20600 | keep | 0 | Jul | 2021 | 0.014031 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
AGUADILLA | 2021-07-09 06:00 | 2021-07-09 13:18 | 6 | 007:18 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | M21070900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 438 | 2021-07-09 | 2628 | keep | 0 | Jul | 2021 | 0.0017899 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
BAYAMON | 2021-07-09 06:06 | 2021-07-09 08:09 | 150 | 002:03 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA | B21070900004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 123 | 2021-07-09 | 18450 | keep | 0 | Jul | 2021 | 0.012566 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
PONCE | 2021-07-09 06:32 | 2021-07-09 06:33 | 2379 | 000:01 | T | DESGANCHE | RECIERRE | P21070900014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-09 | 2379 | keep | 0 | Jul | 2021 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
PONCE | 2021-07-09 06:33 | 2021-07-09 16:40 | 500 | 010:07 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P21070900015 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 607 | 2021-07-09 | 303500 | keep | 0 | Jul | 2021 | 0.20671 | 0.00034055 | Sustained | FALSE | TRUE | Not_TMED_Event | 500
BAYAMON | 2021-07-09 06:35 | 2021-07-09 11:25 | 50 | 004:50 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE RETIRO AISLADOR VACANTE ENERGIZADO | B21070900004 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 290 | 2021-07-09 | 14500 | keep | 0 | Jul | 2021 | 0.0098759 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-09 07:10 | 2021-07-09 07:11 | 320 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO | B21070900000 | New_Event |  |  | Include | Wildlife | 1 | 2021-07-09 | 320 | keep | 0 | Jul | 2021 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
SAN JUAN | 2021-07-09 07:11 | 2021-07-09 18:03 | 30 | 010:52 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU-10 | S21070900017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 652 | 2021-07-09 | 19560 | keep | 0 | Jul | 2021 | 0.013322 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-07-09 07:11 | 2021-07-09 17:51 | 16 | 010:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA AVE CRUZADA | B21070900007 | 1st_after_momentary |  |  | Include | Wildlife | 640 | 2021-07-09 | 10240 | keep | 0 | Jul | 2021 | 0.0069744 | 1.0898e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 16
SAN JUAN | 2021-07-09 07:14 | 2021-07-09 13:06 | 30 | 005:52 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21070900019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 352 | 2021-07-09 | 10560 | keep | 0 | Jul | 2021 | 0.0071924 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-07-09 07:26 | 2021-07-09 07:27 | 2617 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21070900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-09 | 2617 | keep | 0 | Jul | 2021 | 0.0017824 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
SAN JUAN | 2021-07-09 07:26 | 2021-07-09 08:48 | 1 | 001:22 | P | OTRAS CAUSAS | SE HIZO DERIVACION AL CT WR - 5890756 | R21070900000 | New_Event | Other Causes | Include | Include | Other | 82 | 2021-07-09 | 82 | keep | 0 | Jul | 2021 | 5.585e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-07-09 07:30 | 2021-07-09 17:15 | 100 | 009:45 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE MASIVO | M21070900004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 585 | 2021-07-09 | 58500 | keep | 0 | Jul | 2021 | 0.039844 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-07-09 07:48 | 2021-07-09 11:29 | 40 | 003:41 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR | R21070900002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2021-07-09 | 8840 | keep | 0 | Jul | 2021 | 0.0060209 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-07-09 08:30 | 2021-07-09 14:45 | 20 | 006:15 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21070900003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 375 | 2021-07-09 | 7500 | keep | 0 | Jul | 2021 | 0.0051082 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-07-09 08:45 | 2021-07-09 17:10 | 25 | 008:25 | P | LINEA DE TRANSMISION 38KV | TRABAJOS DE REPARACION EN LINEA 2000 | M21070900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 505 | 2021-07-09 | 12625 | keep | 0 | Jul | 2021 | 0.0085988 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
VEGA BAJA | 2021-07-09 08:49 | 2021-07-09 13:25 | 12 | 004:36 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO 37.5KVA X 37.5 KVA | B21070900017 | New_Event | Service Transformer Failure | Include | Include | Equipment | 276 | 2021-07-09 | 3312 | keep | 0 | Jul | 2021 | 0.0022558 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-07-09 08:55 | 2021-07-09 10:50 | 40 | 001:55 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE DETECTO LA CAUSA | A21070900008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2021-07-09 | 4600 | keep | 0 | Jul | 2021 | 0.003133 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-07-09 08:57 | 2021-07-09 11:29 | 1 | 002:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZARON 3 CAJAS AVERIADAS | B21070900019 | New_Event | Cutout Failure | Include | Include | Equipment | 152 | 2021-07-09 | 152 | keep | 0 | Jul | 2021 | 0.00010353 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-07-09 09:02 | 2021-07-09 14:30 | 40 | 005:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21070900025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 328 | 2021-07-09 | 13120 | keep | 0 | Jul | 2021 | 0.008936 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-09 09:10 | 2021-07-10 14:40 | 38 | 029:30 | P | NO SE REPORTO CAUSA | 2 X 20 EN CORTE DE LINEA | B21070900021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1770 | 2021-07-09 | 67260 | keep | 0 | Jul | 2021 | 0.04581 | 2.5882e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 38
ARECIBO | 2021-07-09 09:10 | 2021-07-09 20:50 | 60 | 011:40 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A21070900012 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 700 | 2021-07-09 | 42000 | keep | 0 | Jul | 2021 | 0.028606 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
YAUCO | 2021-07-09 09:14 | 2021-07-11 17:13 | 10 | 055:59 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA POR DESGANCHE | P21070900027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3359 | 2021-07-09 | 33590 | keep | 0 | Jul | 2021 | 0.022878 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BAYAMON | 2021-07-09 09:19 | 2021-07-09 09:20 | 1860 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21070900000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-09 | 1860 | keep | 0 | Jul | 2021 | 0.0012668 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-09 09:20 | 2021-07-09 11:06 | 20 | 001:46 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21070500204 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 106 | 2021-07-09 | 2120 | keep | 0 | Jul | 2021 | 0.0014439 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-07-09 09:24 | 2021-07-09 16:08 | 1 | 006:44 | P | NO SE REPORTO CAUSA | 1 X 45 EN CORTE DE LINEA | S21070900045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 404 | 2021-07-09 | 404 | keep | 0 | Jul | 2021 | 0.00027516 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-07-09 09:27 | 2021-07-09 15:06 | 20 | 005:39 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO | B21070800028 | New_Event | Defective Pole | Include | Include | Equipment | 339 | 2021-07-09 | 6780 | keep | 0 | Jul | 2021 | 0.0046178 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-07-09 09:34 | 2021-07-09 13:45 | 75 | 004:11 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21070900031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2021-07-09 | 18825 | keep | 0 | Jul | 2021 | 0.012822 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
UTUADO | 2021-07-09 09:39 | 2021-07-10 09:18 | 2 | 023:39 | P | DESGANCHE | 1 X 30 EN CORTE DE LNEA | A21070900014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1419 | 2021-07-09 | 2838 | keep | 0 | Jul | 2021 | 0.0019329 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2021-07-09 09:46 | 2021-07-09 09:47 | 181 | 000:01 | T | DESGANCHE | RECIERRE | C21070900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-09 | 181 | keep | 0 | Jul | 2021 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
HUMACAO | 2021-07-09 09:47 | 2021-07-09 16:53 | 20 | 007:06 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHO Y REMPLAZO PARARRAYO | C21070900039 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 426 | 2021-07-09 | 8520 | keep | 0 | Jul | 2021 | 0.0058029 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
HUMACAO | 2021-07-09 09:48 | 2021-07-09 11:22 | 1 | 001:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO WR5889201 | C21070900000 | New_Event | Bad Weather | Include | Include | Weather | 94 | 2021-07-09 | 94 | keep | 0 | Jul | 2021 | 6.4023e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-07-09 10:03 | 2021-07-09 16:18 | 80 | 006:15 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21070900037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 375 | 2021-07-09 | 30000 | keep | 0 | Jul | 2021 | 0.020433 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
GUAYAMA | 2021-07-09 10:14 | 2021-07-09 10:15 | 2100 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P210709000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-09 | 2100 | keep | 0 | Jul | 2021 | 0.0014303 | 0.0014303 | Momentary | FALSE | TRUE | Not_TMED_Event | 2100
GUAYAMA | 2021-07-09 10:14 | 2021-07-09 10:15 | 922 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P210709000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-09 | 922 | keep | 0 | Jul | 2021 | 0.00062797 | 0.00062797 | Momentary | FALSE | TRUE | Not_TMED_Event | 922
GUAYAMA | 2021-07-09 10:14 | 2021-07-09 10:15 | 1676 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P210709000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-09 | 1676 | keep | 0 | Jul | 2021 | 0.0011415 | 0.0011415 | Momentary | FALSE | TRUE | Not_TMED_Event | 1676
GUAYAMA | 2021-07-09 10:14 | 2021-07-09 10:15 | 2844 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P210709000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-09 | 2844 | keep | 0 | Jul | 2021 | 0.001937 | 0.001937 | Momentary | FALSE | TRUE | Not_TMED_Event | 2844
GUAYAMA | 2021-07-09 10:14 | 2021-07-09 10:15 | 2775 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P210709000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-09 | 2775 | keep | 0 | Jul | 2021 | 0.00189 | 0.00189 | Momentary | FALSE | TRUE | Not_TMED_Event | 2775
GUAYAMA | 2021-07-09 10:14 | 2021-07-09 10:15 | 1457 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P210709000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-09 | 1457 | keep | 0 | Jul | 2021 | 0.00099236 | 0.00099236 | Momentary | FALSE | TRUE | Not_TMED_Event | 1457
GUAYAMA | 2021-07-09 10:14 | 2021-07-09 10:15 | 1086 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P210709000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-09 | 1086 | keep | 0 | Jul | 2021 | 0.00073967 | 0.00073967 | Momentary | FALSE | TRUE | Not_TMED_Event | 1086
GUAYAMA | 2021-07-09 10:14 | 2021-07-09 10:15 | 1464 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P210709000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-09 | 1464 | keep | 0 | Jul | 2021 | 0.00099712 | 0.00099712 | Momentary | FALSE | TRUE | Not_TMED_Event | 1464
GUAYAMA | 2021-07-09 10:14 | 2021-07-09 10:15 | 1833 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P210709000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-09 | 1833 | keep | 0 | Jul | 2021 | 0.0012484 | 0.0012484 | Momentary | FALSE | TRUE | Not_TMED_Event | 1833
GUAYAMA | 2021-07-09 10:14 | 2021-07-09 10:15 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P210709000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-09 | 1565 | keep | 0 | Jul | 2021 | 0.0010659 | 0.0010659 | Momentary | FALSE | TRUE | Not_TMED_Event | 1565
GUAYAMA | 2021-07-09 10:14 | 2021-07-09 10:15 | 977 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 3700 | P210709000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-09 | 977 | keep | 0 | Jul | 2021 | 0.00066543 | 0.00066543 | Momentary | FALSE | TRUE | Not_TMED_Event | 977
GUAYAMA | 2021-07-09 10:15 | 2021-07-09 14:20 | 10 | 004:05 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR, NO SE ENCONTRO CAUSA | P21070900031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 245 | 2021-07-09 | 2450 | keep | 0 | Jul | 2021 | 0.0016687 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-09 10:22 | 2021-07-10 08:33 | 1 | 022:11 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S21070900062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1331 | 2021-07-09 | 1331 | keep | 0 | Jul | 2021 | 0.00090654 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-07-09 10:43 | 2021-07-09 15:40 | 50 | 004:57 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21070900020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 297 | 2021-07-09 | 14850 | keep | 0 | Jul | 2021 | 0.010114 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-09 10:51 | 2021-07-09 10:52 | 353 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S21070900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-09 | 353 | keep | 0 | Jul | 2021 | 0.00024043 | 0.00024043 | Momentary | FALSE | FALSE | Not_TMED_Event | 353
SAN JUAN | 2021-07-09 10:53 | 2021-07-09 12:20 | 844 | 001:27 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21070900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2021-07-09 | 73428 | keep | 0 | Jul | 2021 | 0.050011 | 0.00057484 | Sustained | FALSE | FALSE | Not_TMED_Event | 844
AGUADILLA | 2021-07-09 10:56 | 2021-07-10 14:20 | 75 | 027:24 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070900040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1644 | 2021-07-09 | 123300 | keep | 0 | Jul | 2021 | 0.083979 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
CAGUAS | 2021-07-09 10:57 | 2021-07-09 11:27 | 200 | 000:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA PERSONAL DESGANCHANDO | C21070900009 | New_Event |  |  | Include | Wildlife | 30 | 2021-07-09 | 6000 | keep | 0 | Jul | 2021 | 0.0040866 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
PONCE | 2021-07-09 11:00 | 2021-07-09 12:40 | 20 | 001:40 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR AVERIADO DE 37.5KVA A 2.4KV POR 37.5 KVA | P21070900044 | New_Event | Service Transformer Failure | Include | Include | Equipment | 100 | 2021-07-09 | 2000 | keep | 0 | Jul | 2021 | 0.0013622 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-07-09 11:05 | 2021-07-09 15:04 | 90 | 003:59 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA Y 1 X 80 CORTE DE LINEA | S21070900079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2021-07-09 | 21510 | keep | 0 | Jul | 2021 | 0.01465 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
BAYAMON | 2021-07-09 11:08 | 2021-07-09 11:09 | 1984 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21070900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-09 | 1984 | keep | 0 | Jul | 2021 | 0.0013513 | 0.0013513 | Momentary | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2021-07-09 11:09 | 2021-07-09 11:10 | 5809 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21070900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-09 | 5809 | keep | 0 | Jul | 2021 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
BARRANQUITAS | 2021-07-09 11:09 | 2021-07-09 15:28 | 12 | 004:19 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA X 37.5 KVA | C21070900073 | New_Event | Service Transformer Failure | Include | Include | Equipment | 259 | 2021-07-09 | 3108 | keep | 0 | Jul | 2021 | 0.0021168 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-07-09 11:10 | 2021-07-09 19:30 | 4 | 008:20 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO Y UN TRANSFORMADOR AVERIADO DE 50KVA POR LA MISMA CAPACIDAD | M21070900000 | New_Event | Defective Pole | Include | Include | Equipment | 500 | 2021-07-09 | 2000 | keep | 0 | Jul | 2021 | 0.0013622 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-07-09 11:11 | 2021-07-09 13:47 | 80 | 002:36 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO | S21070900000 | New_Event | Switch Failure | Include | Include | Equipment | 156 | 2021-07-09 | 12480 | keep | 0 | Jul | 2021 | 0.0085001 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-07-09 11:12 | 2021-07-09 13:23 | 10 | 002:11 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21070900051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 131 | 2021-07-09 | 1310 | keep | 0 | Jul | 2021 | 0.00089224 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-07-09 11:18 | 2021-07-09 19:00 | 11 | 007:42 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR | R21070900006 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 462 | 2021-07-09 | 5082 | keep | 0 | Jul | 2021 | 0.0034613 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CANOVANAS | 2021-07-09 11:20 | 2021-07-09 12:40 | 1 | 001:20 | P | DESGANCHE | 1 X 30 Y 1 X 40 EN CORTES DE LINEA | R21070900007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2021-07-09 | 80 | keep | 0 | Jul | 2021 | 5.4488e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-07-09 11:25 | 2021-07-09 13:34 | 6 | 002:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21070900028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 129 | 2021-07-09 | 774 | keep | 0 | Jul | 2021 | 0.00052717 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2021-07-09 11:26 | 2021-07-09 13:50 | 200 | 002:24 | P | DESGANCHE | 1 X 140 Y 2 X 100 EN DIFERENTES CORTES DE LINEA POR DESGANCHE | P21070900042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2021-07-09 | 28800 | keep | 0 | Jul | 2021 | 0.019616 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-07-09 11:32 | 2021-07-09 11:45 | 5 | 000:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA ROTA | A21070900024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 13 | 2021-07-09 | 65 | keep | 0 | Jul | 2021 | 4.4271e-05 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
CAGUAS | 2021-07-09 11:33 | 2021-07-09 18:34 | 25 | 007:01 | P | PARARRAYOS DEFECTUOSO | 1 X 25 EN CORTE DE LINEA ELIMINO PARARRAYO | C21070900057 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 421 | 2021-07-09 | 10525 | keep | 0 | Jul | 2021 | 0.0071685 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-07-09 11:34 | 2021-07-09 16:02 | 36 | 004:28 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21070900053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2021-07-09 | 9648 | keep | 0 | Jul | 2021 | 0.0065712 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
UTUADO | 2021-07-09 11:35 | 2021-07-09 14:55 | 12 | 003:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR LINEA PRIMARIA ARRIADA | A21070900000 | New_Event | Wire Down | Include | Include | Equipment | 200 | 2021-07-09 | 2400 | keep | 0 | Jul | 2021 | 0.0016346 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-07-09 11:47 | 2021-07-09 14:46 | 40 | 002:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO BAJANTE EN CORTE DE LINEA | M21070900000 | New_Event | Wire Down | Include | Include | Equipment | 179 | 2021-07-09 | 7160 | keep | 0 | Jul | 2021 | 0.0048766 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-07-09 11:53 | 2021-07-09 11:58 | 776 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO Y SE VERIFICO PERSONAL FUERA | B21070900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-07-09 | 3880 | keep | 0 | Jul | 2021 | 0.0026427 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
BARRANQUITAS | 2021-07-09 11:53 | 2021-07-09 16:28 | 100 | 004:35 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | C21070900061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2021-07-09 | 27500 | keep | 0 | Jul | 2021 | 0.01873 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-07-09 11:57 | 2021-07-09 11:58 | 1628 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO INTERRUPTOR PARA RETIRAR PELIGRO LINEA PRIMARIA CRUZADA SOBRE ESTRUCTURA | A21070800129 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-07-09 | 1628 | keep | 0 | Jul | 2021 | 0.0011088 | 0.0011088 | Momentary | FALSE | TRUE | Not_TMED_Event | 1628
ARECIBO | 2021-07-09 11:58 | 2021-07-09 13:40 | 500 | 001:42 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADORES ROTOS SE CERRO MACHETES | A21070800129 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 102 | 2021-07-09 | 51000 | keep | 0 | Jul | 2021 | 0.034736 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
VEGA BAJA | 2021-07-09 11:58 | 2021-07-09 14:58 | 60 | 003:00 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21070900000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 180 | 2021-07-09 | 10800 | keep | 0 | Jul | 2021 | 0.0073558 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-09 12:00 | 2021-07-09 16:54 | 1 | 004:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | M21070900000 | New_Event | Wire Down | Include | Include | Equipment | 294 | 2021-07-09 | 294 | keep | 0 | Jul | 2021 | 0.00020024 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-07-09 12:01 | 2021-07-09 12:02 | 4431 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21070900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-09 | 4431 | keep | 0 | Jul | 2021 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
BAYAMON | 2021-07-09 12:02 | 2021-07-09 18:35 | 7 | 006:33 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21070800045 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 393 | 2021-07-09 | 2751 | keep | 0 | Jul | 2021 | 0.0018737 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-07-09 12:06 | 2021-07-10 08:18 | 55 | 020:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ZAFADO EN RISER | S21070900143 | New_Event | Wire Down | Include | Include | Equipment | 1212 | 2021-07-09 | 66660 | keep | 0 | Jul | 2021 | 0.045402 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
SAN JUAN | 2021-07-09 12:08 | 2021-07-09 13:53 | 4 | 001:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | R21070700019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 105 | 2021-07-09 | 420 | keep | 0 | Jul | 2021 | 0.00028606 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
FAJARDO | 2021-07-09 12:09 | 2021-07-09 18:17 | 1 | 006:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO TOMA SECUNDARIA | R21070900012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 368 | 2021-07-09 | 368 | keep | 0 | Jul | 2021 | 0.00025064 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-07-09 12:13 | 2021-07-09 13:51 | 810 | 001:38 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21070900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 98 | 2021-07-09 | 79380 | keep | 0 | Jul | 2021 | 0.054065 | 0.00055169 | Sustained | FALSE | TRUE | Not_TMED_Event | 810
MAYAGÃœEZ | 2021-07-09 12:13 | 2021-07-09 13:51 | 1235 | 001:38 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21070900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 98 | 2021-07-09 | 121030 | keep | 0 | Jul | 2021 | 0.082433 | 0.00084115 | Sustained | FALSE | TRUE | Not_TMED_Event | 1235
MAYAGÃœEZ | 2021-07-09 12:13 | 2021-07-09 13:51 | 93 | 001:38 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21070900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 98 | 2021-07-09 | 9114 | keep | 0 | Jul | 2021 | 0.0062075 | 6.3342e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 93
MAYAGÃœEZ | 2021-07-09 12:13 | 2021-07-09 13:51 | 1825 | 001:38 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21070900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 98 | 2021-07-09 | 178850 | keep | 0 | Jul | 2021 | 0.12181 | 0.001243 | Sustained | FALSE | TRUE | Not_TMED_Event | 1825
MAYAGÃœEZ | 2021-07-09 12:13 | 2021-07-09 13:51 | 3230 | 001:38 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21070900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 98 | 2021-07-09 | 316540 | keep | 0 | Jul | 2021 | 0.21559 | 0.0021999 | Sustained | FALSE | TRUE | Not_TMED_Event | 3230
ARECIBO | 2021-07-09 12:15 | 2021-07-09 15:16 | 3 | 003:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21070900029 | New_Event | Bad Weather | Include | Include | Weather | 181 | 2021-07-09 | 543 | keep | 0 | Jul | 2021 | 0.00036983 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-07-09 12:25 | 2021-07-09 12:26 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21070900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-09 | 1310 | keep | 0 | Jul | 2021 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
CAGUAS | 2021-07-09 12:27 | 2021-07-09 18:19 | 200 | 005:52 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA DESGANCHO Y LEVANTO CONDUCTOR | C21070900089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 352 | 2021-07-09 | 70400 | keep | 0 | Jul | 2021 | 0.047949 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-07-09 12:27 | 2021-07-09 20:30 | 300 | 008:03 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA | C21070900070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 483 | 2021-07-09 | 144900 | keep | 0 | Jul | 2021 | 0.098691 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-07-09 12:34 | 2021-07-10 11:24 | 80 | 022:50 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21070900230 | New_Event | Bad Weather | Include | Include | Weather | 1370 | 2021-07-09 | 109600 | keep | 0 | Jul | 2021 | 0.074648 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
UTUADO | 2021-07-09 12:38 | 2021-07-09 19:34 | 934 | 006:56 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DEL INTERRUPTOR RTU FUERA DE SERVICIO MAL TIEMPO DESCARGAS ELECTRICAS SE CERRO MANUAL ELECTRICO | A21070900034 | New_Event | Bad Weather | Include | Include | Weather | 416 | 2021-07-09 | 388544 | keep | 0 | Jul | 2021 | 0.26464 | 0.00063614 | Sustained | FALSE | FALSE | Not_TMED_Event | 934
BAYAMON | 2021-07-09 12:43 | 2021-07-10 20:17 | 27 | 031:34 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21070900113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1894 | 2021-07-09 | 51138 | keep | 0 | Jul | 2021 | 0.03483 | 1.839e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 27
BAYAMON | 2021-07-09 12:50 | 2021-07-10 11:04 | 30 | 022:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO TRASPATIO | B21070900071 | New_Event | Wire Down | Include | Include | Equipment | 1334 | 2021-07-09 | 40020 | keep | 0 | Jul | 2021 | 0.027257 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2021-07-09 12:51 | 2021-07-09 12:52 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210709000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-09 | 2113 | keep | 0 | Jul | 2021 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
BAYAMON | 2021-07-09 12:52 | 2021-07-09 12:53 | 1085 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21070900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-09 | 1085 | keep | 0 | Jul | 2021 | 0.00073899 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
PONCE | 2021-07-09 12:56 | 2021-07-09 19:00 | 412 | 006:04 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21070900052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 364 | 2021-07-09 | 149968 | keep | 0 | Jul | 2021 | 0.10214 | 0.00028061 | Sustained | FALSE | TRUE | Not_TMED_Event | 412
BAYAMON | 2021-07-09 13:01 | 2021-07-09 13:02 | 437 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21070900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-09 | 437 | keep | 0 | Jul | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
CAGUAS | 2021-07-09 13:04 | 2021-07-09 16:38 | 1 | 003:34 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA Y 2 X 15 EN BANCO DE TRANSFORMADORES | C21070900083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 214 | 2021-07-09 | 214 | keep | 0 | Jul | 2021 | 0.00014575 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-07-09 13:04 | 2021-07-09 17:21 | 89 | 004:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21070900078 | New_Event | Bad Weather | Include | Include | Weather | 257 | 2021-07-09 | 22873 | keep | 0 | Jul | 2021 | 0.015579 | 6.0617e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 89
SAN JUAN | 2021-07-09 13:06 | 2021-07-09 13:07 | 1799 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21070900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-09 | 1799 | keep | 0 | Jul | 2021 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
UTUADO | 2021-07-09 13:11 | 2021-07-09 18:50 | 60 | 005:39 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBÃšES SOBRE LAS LINEAS | A21070900044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 339 | 2021-07-09 | 20340 | keep | 0 | Jul | 2021 | 0.013853 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-07-09 13:12 | 2021-07-09 20:47 | 1590 | 007:35 | S | TRANSFORMADOR AVERIADO | TRANSFORMADOR DEL SERVICE STATION Y RISER DE LA MEDICION REMOTA AVERIADOS | C21070900122 | New_Event | Service Transformer Failure | Include | Include | Equipment | 455 | 2021-07-09 | 723450 | keep | 0 | Jul | 2021 | 0.49274 | 0.0010829 | Sustained | FALSE | FALSE | Not_TMED_Event | 1590
CAGUAS | 2021-07-09 13:12 | 2021-07-09 20:47 | 1 | 007:35 | S | TRANSFORMADOR AVERIADO | TRANSFORMADOR DEL SERVICE STATION Y RISER DE LA MEDICION REMOTA AVERIADOS | C21070900122 | New_Event | Service Transformer Failure | Include | Include | Equipment | 455 | 2021-07-09 | 455 | keep | 0 | Jul | 2021 | 0.0003099 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-07-09 13:12 | 2021-07-09 20:47 | 1510 | 007:35 | S | TRANSFORMADOR AVERIADO | TRANSFORMADOR DEL SERVICE STATION Y RISER DE LA MEDICION REMOTA AVERIADOS | C21070900122 | New_Event | Service Transformer Failure | Include | Include | Equipment | 455 | 2021-07-09 | 687050 | keep | 0 | Jul | 2021 | 0.46795 | 0.0010285 | Sustained | FALSE | FALSE | Not_TMED_Event | 1510
CAGUAS | 2021-07-09 13:12 | 2021-07-09 20:47 | 166 | 007:35 | S | TRANSFORMADOR AVERIADO | TRANSFORMADOR DEL SERVICE STATION Y RISER DE LA MEDICION REMOTA AVERIADOS | C21070900122 | New_Event | Service Transformer Failure | Include | Include | Equipment | 455 | 2021-07-09 | 75530 | keep | 0 | Jul | 2021 | 0.051443 | 0.00011306 | Sustained | FALSE | FALSE | Not_TMED_Event | 166
UTUADO | 2021-07-09 13:12 | 2021-07-10 12:50 | 200 | 023:38 | P | DESGANCHE | 1 X 100 Y 1 X 40 EN CORTE DE LINEA | A21070900046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1418 | 2021-07-09 | 283600 | keep | 0 | Jul | 2021 | 0.19316 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
AGUADILLA | 2021-07-09 13:15 | 2021-07-09 16:00 | 200 | 002:45 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE MASIVO | M21070900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2021-07-09 | 33000 | keep | 0 | Jul | 2021 | 0.022476 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
UTUADO | 2021-07-09 13:17 | 2021-07-09 16:23 | 40 | 003:06 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21070900047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2021-07-09 | 7440 | keep | 0 | Jul | 2021 | 0.0050674 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-07-09 13:21 | 2021-07-10 17:52 | 95 | 028:31 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | R21070900018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1711 | 2021-07-09 | 162545 | keep | 0 | Jul | 2021 | 0.11071 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
FAJARDO | 2021-07-09 13:22 | 2021-07-09 16:49 | 41 | 003:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE HACIA CAJA PRIMARIA | R21070900019 | New_Event | Wire Down | Include | Include | Equipment | 207 | 2021-07-09 | 8487 | keep | 0 | Jul | 2021 | 0.0057805 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
CAGUAS | 2021-07-09 13:24 | 2021-07-09 16:11 | 40 | 002:47 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21070900095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2021-07-09 | 6680 | keep | 0 | Jul | 2021 | 0.0045497 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
FAJARDO | 2021-07-09 13:36 | 2021-07-09 15:53 | 95 | 002:17 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA REEMPLAZO PARARRAYO | R21070900020 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 137 | 2021-07-09 | 13015 | keep | 0 | Jul | 2021 | 0.0088645 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
HUMACAO | 2021-07-09 13:36 | 2021-07-09 14:26 | 40 | 000:50 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21070900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 50 | 2021-07-09 | 2000 | keep | 0 | Jul | 2021 | 0.0013622 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-07-09 13:38 | 2021-07-09 16:25 | 50 | 002:47 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21070900053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2021-07-09 | 8350 | keep | 0 | Jul | 2021 | 0.0056871 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-09 13:43 | 2021-07-09 13:45 | 3957 | 000:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21070900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-07-09 | 7914 | keep | 0 | Jul | 2021 | 0.0053902 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
MAYAGÃœEZ | 2021-07-09 13:43 | 2021-07-09 14:00 | 107 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21070900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2021-07-09 | 1819 | keep | 0 | Jul | 2021 | 0.0012389 | 7.2877e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 107
MAYAGÃœEZ | 2021-07-09 13:43 | 2021-07-09 14:00 | 1666 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21070900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2021-07-09 | 28322 | keep | 0 | Jul | 2021 | 0.01929 | 0.0011347 | Sustained | FALSE | TRUE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2021-07-09 13:43 | 2021-07-09 14:00 | 4387 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21070900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2021-07-09 | 74579 | keep | 0 | Jul | 2021 | 0.050795 | 0.002988 | Sustained | FALSE | TRUE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2021-07-09 13:43 | 2021-07-09 14:00 | 3147 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21070900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2021-07-09 | 53499 | keep | 0 | Jul | 2021 | 0.036438 | 0.0021434 | Sustained | FALSE | TRUE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2021-07-09 13:43 | 2021-07-09 14:00 | 4304 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M21070900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2021-07-09 | 73168 | keep | 0 | Jul | 2021 | 0.049834 | 0.0029314 | Sustained | FALSE | TRUE | Not_TMED_Event | 4304
BAYAMON | 2021-07-09 13:45 | 2021-07-09 17:01 | 200 | 003:16 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | S21070900195 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 196 | 2021-07-09 | 39200 | keep | 0 | Jul | 2021 | 0.026699 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-07-09 13:47 | 2021-07-09 15:10 | 2435 | 001:23 | T | DESCONECTIVO DEFECTUOSO | SE DISPARO INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1909-08 | S21070900000 | New_Event | Switch Failure | Include | Include | Equipment | 83 | 2021-07-09 | 202105 | keep | 0 | Jul | 2021 | 0.13765 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-07-09 13:47 | 2021-07-09 15:10 | 2956 | 001:23 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA REMPLAZAR MACHETE QUEMADO SE CERRO POR SCADA | S21070900000 | Additional_clients | Switch Failure | Include | Include | Equipment | 83 | 2021-07-09 | 245348 | keep | 0 | Jul | 2021 | 0.16711 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-07-09 13:56 | 2021-07-09 17:10 | 120 | 003:14 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DEL LINEA MAL TIEMPO | R21070900024 | New_Event | Bad Weather | Include | Include | Weather | 194 | 2021-07-09 | 23280 | keep | 0 | Jul | 2021 | 0.015856 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
UTUADO | 2021-07-09 13:57 | 2021-07-10 08:10 | 120 | 018:13 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | A21070900056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1093 | 2021-07-09 | 131160 | keep | 0 | Jul | 2021 | 0.089332 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
MAYAGÃœEZ | 2021-07-09 13:58 | 2021-07-09 18:30 | 15 | 004:32 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | M21070900109 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 272 | 2021-07-09 | 4080 | keep | 0 | Jul | 2021 | 0.0027789 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-07-09 14:00 | 2021-07-09 14:50 | 75 | 000:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21070900120 | New_Event | Bad Weather | Include | Include | Weather | 50 | 2021-07-09 | 3750 | keep | 0 | Jul | 2021 | 0.0025541 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-07-09 14:02 | 2021-07-11 07:47 | 150 | 041:45 | P | NO SE REPORTO CAUSA | 1 X 40 Y 1 X 50 EN CORTE LINEA | B21070900102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2505 | 2021-07-09 | 375750 | keep | 0 | Jul | 2021 | 0.25592 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-07-09 14:13 | 2021-07-09 14:14 | 2092 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | C21070900000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2021-07-09 | 2092 | keep | 0 | Jul | 2021 | 0.0014249 | 0.0014249 | Momentary | FALSE | FALSE | Not_TMED_Event | 2092
SAN JUAN | 2021-07-09 14:15 | 2021-07-09 16:00 | 8 | 001:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA CRUZADA WR - 5891392 | R21070900000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 105 | 2021-07-09 | 840 | keep | 0 | Jul | 2021 | 0.00057212 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-07-09 14:18 | 2021-07-10 14:43 | 150 | 024:25 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21070900125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1465 | 2021-07-09 | 219750 | keep | 0 | Jul | 2021 | 0.14967 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
AGUADILLA | 2021-07-09 14:20 | 2021-07-09 16:41 | 50 | 002:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA Y PUENTE PRIMARIO ABIERTO | M21070900000 | New_Event | Wire Down | Include | Include | Equipment | 141 | 2021-07-09 | 7050 | keep | 0 | Jul | 2021 | 0.0048017 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-07-09 14:27 | 2021-07-09 16:13 | 50 | 001:46 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO CAUSA | C21070900126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2021-07-09 | 5300 | keep | 0 | Jul | 2021 | 0.0036098 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-09 14:27 | 2021-07-09 16:32 | 4 | 002:05 | P | TRANSFORMADOR AVERIADO | SE CAMBIO LA CONECCION DE LA MONTURA DE TRANSFORMADOR DE DELTA A DELTA ABIERTA POR TENER UN TRANSFORMADOR AVERIADO EN MONTURA | M21070900128 | New_Event | Service Transformer Failure | Include | Include | Equipment | 125 | 2021-07-09 | 500 | keep | 0 | Jul | 2021 | 0.00034055 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-07-09 14:35 | 2021-07-09 14:36 | 810 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M21070900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-09 | 810 | keep | 0 | Jul | 2021 | 0.00055169 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-09 14:35 | 2021-07-09 14:36 | 1235 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M21070900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-09 | 1235 | keep | 0 | Jul | 2021 | 0.00084115 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-09 14:35 | 2021-07-09 14:36 | 93 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M21070900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-09 | 93 | keep | 0 | Jul | 2021 | 6.3342e-05 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-09 14:35 | 2021-07-09 14:36 | 1825 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M21070900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-09 | 1825 | keep | 0 | Jul | 2021 | 0.001243 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-09 14:35 | 2021-07-09 14:36 | 3230 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M21070900000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-09 | 3230 | keep | 0 | Jul | 2021 | 0.0021999 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-07-09 14:57 | 2021-07-09 20:30 | 40 | 005:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21070900069 | New_Event | Wire Down | Include | Include | Equipment | 333 | 2021-07-09 | 13320 | keep | 0 | Jul | 2021 | 0.0090722 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-09 14:57 | 2021-07-10 15:51 | 60 | 024:54 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21070900090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1494 | 2021-07-09 | 89640 | keep | 0 | Jul | 2021 | 0.061053 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-07-09 14:59 | 2021-07-09 16:43 | 40 | 001:44 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO CAUSA | C21070900140 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2021-07-09 | 4160 | keep | 0 | Jul | 2021 | 0.0028334 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-07-09 15:00 | 2021-07-09 16:05 | 60 | 001:05 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21070900075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 65 | 2021-07-09 | 3900 | keep | 0 | Jul | 2021 | 0.0026563 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-07-09 15:02 | 2021-07-09 17:40 | 10 | 002:38 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | A21070900070 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 158 | 2021-07-09 | 1580 | keep | 0 | Jul | 2021 | 0.0010761 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-09 15:03 | 2021-07-10 11:50 | 200 | 020:47 | P | CABLE SOTERRADO AVERIADO | 1 X 100 EN CORTE DE LINEA SE CONSTRUYO AEREO PROVISIONAL AL T-1 | B21070900091 | New_Event | UG Cable Fault | Include | Include | Equipment | 1247 | 2021-07-09 | 249400 | keep | 0 | Jul | 2021 | 0.16987 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
HUMACAO | 2021-07-09 15:15 | 2021-07-09 16:54 | 50 | 001:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21070900147 | New_Event | Bad Weather | Include | Include | Weather | 99 | 2021-07-09 | 4950 | keep | 0 | Jul | 2021 | 0.0033714 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-09 15:17 | 2021-07-09 18:06 | 60 | 002:49 | P | DESGANCHE | 1 X 60 EN CORTE DE LINEA | S21070900194 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2021-07-09 | 10140 | keep | 0 | Jul | 2021 | 0.0069063 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-07-09 15:22 | 2021-07-10 16:43 | 170 | 025:21 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | R21070900028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1521 | 2021-07-09 | 258570 | keep | 0 | Jul | 2021 | 0.17611 | 0.00011579 | Sustained | FALSE | TRUE | Not_TMED_Event | 170
BAYAMON | 2021-07-09 15:33 | 2021-07-09 15:35 | 90 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S21070900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-09 | 180 | keep | 0 | Jul | 2021 | 0.0001226 | 6.1299e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 90
BARRANQUITAS | 2021-07-09 15:37 | 2021-07-09 15:38 | 1604 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | C21070900000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-09 | 1604 | keep | 0 | Jul | 2021 | 0.0010925 | 0.0010925 | Momentary | FALSE | FALSE | Not_TMED_Event | 1604
BARRANQUITAS | 2021-07-09 15:38 | 2021-07-09 15:41 | 2362 | 000:03 | T | DESGANCHE | DISPARO RR EN OFF | C21070900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-07-09 | 7086 | keep | 0 | Jul | 2021 | 0.0048262 | 0.0016087 | Momentary | FALSE | FALSE | Not_TMED_Event | 2362
BARRANQUITAS | 2021-07-09 15:40 | 2021-07-09 15:41 | 1604 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | C21070900000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1 | 2021-07-09 | 1604 | keep | 0 | Jul | 2021 | 0.0010925 | 0.0010925 | Momentary | FALSE | FALSE | Not_TMED_Event | 1604
BARRANQUITAS | 2021-07-09 15:41 | 2021-07-09 18:48 | 150 | 003:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO | C21070900183 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 187 | 2021-07-09 | 28050 | keep | 0 | Jul | 2021 | 0.019105 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BARRANQUITAS | 2021-07-09 15:41 | 2021-07-10 11:33 | 40 | 019:52 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21070900055 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1192 | 2021-07-09 | 47680 | keep | 0 | Jul | 2021 | 0.032475 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-07-09 15:41 | 2021-07-10 11:08 | 40 | 019:27 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21070900240 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1167 | 2021-07-09 | 46680 | keep | 0 | Jul | 2021 | 0.031794 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-07-09 15:48 | 2021-07-09 15:49 | 2450 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO NO RECERRO | C21070900000 | New_Event |  |  | Include | Wildlife | 1 | 2021-07-09 | 2450 | keep | 0 | Jul | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2021-07-09 15:49 | 2021-07-09 17:51 | 50 | 002:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C21070900179 | 1st_after_momentary |  |  | Include | Wildlife | 122 | 2021-07-09 | 6100 | keep | 0 | Jul | 2021 | 0.0041547 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-07-09 16:00 | 2021-07-10 01:05 | 40 | 009:05 | P | LINEA DE TRANSMISION 38KV | SE ABRIÃ“ CORTE DE LINEA PARA REPARAR LINEA 2700 | M21070900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 545 | 2021-07-09 | 21800 | keep | 0 | Jul | 2021 | 0.014848 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-07-09 16:08 | 2021-07-09 18:25 | 870 | 002:17 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO Y SE CERRO POR SCADA | S21070900000 | New_Event | Wire Down | Include | Include | Equipment | 137 | 2021-07-09 | 119190 | keep | 0 | Jul | 2021 | 0.08118 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2021-07-09 16:17 | 2021-07-11 04:23 | 15 | 036:06 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21070900096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2166 | 2021-07-09 | 32490 | keep | 0 | Jul | 2021 | 0.022129 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CAGUAS | 2021-07-09 16:22 | 2021-07-09 22:36 | 4390 | 006:14 | S | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE Y UN FUSIBLE DE 38 KV | C21070900280 | New_Event | Switch Failure | Include | Include | Equipment | 374 | 2021-07-09 | 1641860 | keep | 0 | Jul | 2021 | 1.1183 | 0.00299 | Sustained | FALSE | FALSE | Not_TMED_Event | 4390
CAGUAS | 2021-07-09 16:22 | 2021-07-09 22:36 | 2092 | 006:14 | S | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE Y UN FUSIBLE DE 38 KV | C21070900280 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 374 | 2021-07-09 | 782408 | keep | 0 | Jul | 2021 | 0.53289 | 0.0014249 | Sustained | FALSE | FALSE | Not_TMED_Event | 2092
CAGUAS | 2021-07-09 16:22 | 2021-07-09 22:36 | 540 | 006:14 | S | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE Y UN FUSIBLE DE 38 KV | C21070900280 | New_Event | Switch Failure | Include | Include | Equipment | 374 | 2021-07-09 | 201960 | keep | 0 | Jul | 2021 | 0.13755 | 0.00036779 | Sustained | FALSE | FALSE | Not_TMED_Event | 540
UTUADO | 2021-07-09 16:25 | 2021-07-10 13:00 | 40 | 020:35 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | A21070900080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1235 | 2021-07-09 | 49400 | keep | 0 | Jul | 2021 | 0.033646 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-07-09 16:55 | 2021-07-09 18:00 | 4 | 001:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE TRANSFORMADOR PARA ELIMINAR ALAMBRE PRIMARIO FUERA DE SERVICIO | P21070900071 | New_Event | Wire Down | Include | Include | Equipment | 65 | 2021-07-09 | 260 | keep | 0 | Jul | 2021 | 0.00017708 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
FAJARDO | 2021-07-09 16:56 | 2021-07-09 19:47 | 15 | 002:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE LINEA A CAJA TRANSFORMADOR | R21070900033 | New_Event | Wire Down | Include | Include | Equipment | 171 | 2021-07-09 | 2565 | keep | 0 | Jul | 2021 | 0.001747 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-07-09 17:00 | 2021-07-09 20:51 | 36 | 003:51 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21070900105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 231 | 2021-07-09 | 8316 | keep | 0 | Jul | 2021 | 0.005664 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
BAYAMON | 2021-07-09 17:00 | 2021-07-09 17:01 | 3597 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21070900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-09 | 3597 | keep | 0 | Jul | 2021 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2021-07-09 17:03 | 2021-07-09 17:04 | 3597 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21070900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-09 | 3597 | keep | 0 | Jul | 2021 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
MAYAGÃœEZ | 2021-07-09 17:05 | 2021-07-09 19:00 | 150 | 001:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | M21070900000 | New_Event | Cutout Failure | Include | Include | Equipment | 115 | 2021-07-09 | 17250 | keep | 0 | Jul | 2021 | 0.011749 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-07-09 17:15 | 2021-07-10 13:52 | 60 | 020:37 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21070900106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1237 | 2021-07-09 | 74220 | keep | 0 | Jul | 2021 | 0.050551 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CANOVANAS | 2021-07-09 17:21 | 2021-07-10 08:07 | 30 | 014:46 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA REMPLAZO AISLADOR | R21070900035 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 886 | 2021-07-09 | 26580 | keep | 0 | Jul | 2021 | 0.018104 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-07-09 17:23 | 2021-07-10 10:50 | 10 | 017:27 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21070900182 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1047 | 2021-07-09 | 10470 | keep | 0 | Jul | 2021 | 0.0071311 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-07-09 17:33 | 2021-07-09 19:40 | 40 | 002:07 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21070900090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2021-07-09 | 5080 | keep | 0 | Jul | 2021 | 0.00346 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-07-09 17:39 | 2021-07-09 19:46 | 1 | 002:07 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21070900220 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 127 | 2021-07-09 | 127 | keep | 0 | Jul | 2021 | 8.6499e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-07-09 17:41 | 2021-07-09 17:42 | 1266 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21070900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-09 | 1266 | keep | 0 | Jul | 2021 | 0.00086227 | 0.00086227 | Momentary | FALSE | FALSE | Not_TMED_Event | 1266
YAUCO | 2021-07-09 17:47 | 2021-07-09 18:37 | 50 | 000:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 100 EN CORTE DE LINEA POR BOMBA DE HELIO QUE CRUZO FASE | P21070900078 | New_Event |  |  | Include | Wildlife | 50 | 2021-07-09 | 2500 | keep | 0 | Jul | 2021 | 0.0017027 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-09 17:52 | 2021-07-09 18:41 | 50 | 000:49 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21070900060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 49 | 2021-07-09 | 2450 | keep | 0 | Jul | 2021 | 0.0016687 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-09 18:08 | 2021-07-09 18:09 | 4664 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21070900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-09 | 4664 | keep | 0 | Jul | 2021 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
SAN JUAN | 2021-07-09 18:25 | 2021-07-09 19:07 | 1 | 000:42 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S21070900045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 42 | 2021-07-09 | 42 | keep | 0 | Jul | 2021 | 2.8606e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-07-09 18:45 | 2021-07-09 21:36 | 8 | 002:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21070900117 | New_Event | Secondary Wire Down | Include | Include | Equipment | 171 | 2021-07-09 | 1368 | keep | 0 | Jul | 2021 | 0.00093174 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-07-09 18:47 | 2021-07-09 18:48 | 2873 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C21070900000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-09 | 2873 | keep | 0 | Jul | 2021 | 0.0019568 | 0.0019568 | Momentary | FALSE | FALSE | Not_TMED_Event | 2873
HUMACAO | 2021-07-09 18:48 | 2021-07-10 14:39 | 400 | 019:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR ROTO Y CERRO MACHETES | C21071000005 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1191 | 2021-07-09 | 476400 | keep | 0 | Jul | 2021 | 0.32447 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
HUMACAO | 2021-07-09 18:56 | 2021-07-10 09:31 | 40 | 014:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21070900248 | New_Event | Vegetation Contact | Include | Include | Vegetation | 875 | 2021-07-09 | 35000 | keep | 0 | Jul | 2021 | 0.023838 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-09 19:19 | 2021-07-10 18:09 | 16 | 022:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA | S21070900225 | New_Event | Cutout Failure | Include | Include | Equipment | 1370 | 2021-07-09 | 21920 | keep | 0 | Jul | 2021 | 0.01493 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2021-07-09 19:44 | 2021-07-10 04:38 | 40 | 008:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21070900119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 534 | 2021-07-09 | 21360 | keep | 0 | Jul | 2021 | 0.014548 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-07-09 19:46 | 2021-07-09 19:47 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CARGA POR EL 1206-03 | S21070900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-09 | 10211 | keep | 0 | Jul | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-07-09 19:46 | 2021-07-09 19:47 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVANDO LA CARGA DEL 1204-05 | S21070900000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-09 | 4133 | keep | 0 | Jul | 2021 | 0.002815 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-09 19:49 | 2021-07-09 21:17 | 10211 | 001:28 | T | NO SE REPORTO CAUSA | DISPARO CARGA POR EL 1206-03 | S21070900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 88 | 2021-07-09 | 898568 | keep | 0 | Jul | 2021 | 0.61201 | 0.0069547 | Sustained | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-07-09 19:49 | 2021-07-09 21:17 | 4133 | 001:28 | T | NO SE REPORTO CAUSA | SE ABRIO AMARRE Y SE CERRO POR SCADA LLEVANDO LA CARGA DEL 1204-05 | S21070900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 88 | 2021-07-09 | 363704 | keep | 0 | Jul | 2021 | 0.24772 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
BAYAMON | 2021-07-09 19:49 | 2021-07-10 11:21 | 40 | 015:32 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA Y SE RETEZO LINEA | S21070900227 | New_Event | Vegetation Contact | Include | Include | Vegetation | 932 | 2021-07-09 | 37280 | keep | 0 | Jul | 2021 | 0.025391 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-07-09 20:18 | 2021-07-10 15:20 | 250 | 019:02 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21070900211 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1142 | 2021-07-09 | 285500 | keep | 0 | Jul | 2021 | 0.19445 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
BAYAMON | 2021-07-09 20:20 | 2021-07-09 20:22 | 1715 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21070900118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-09 | 3430 | keep | 0 | Jul | 2021 | 0.0023362 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
HUMACAO | 2021-07-09 21:05 | 2021-07-10 09:21 | 8 | 012:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BARRAS DE PEDESTAL | C21070900274 | New_Event | Secondary Wire Down | Include | Include | Equipment | 736 | 2021-07-09 | 5888 | keep | 0 | Jul | 2021 | 0.0040103 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-07-09 21:17 | 2021-07-09 21:29 | 100 | 000:12 | P | NO SE REPORTO CAUSA | SE PATRULLO NO SE ENCONTRO CONDICION Y SE CERRARON MACHETES PREVIAMENTE ABIERTOS | S21070900000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 12 | 2021-07-09 | 1200 | keep | 0 | Jul | 2021 | 0.00081731 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-07-09 21:24 | 2021-07-10 18:25 | 50 | 021:01 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21070900277 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1261 | 2021-07-09 | 63050 | keep | 0 | Jul | 2021 | 0.042943 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-09 21:25 | 2021-07-10 18:26 | 90 | 021:01 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21070900278 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1261 | 2021-07-09 | 113490 | keep | 0 | Jul | 2021 | 0.077298 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
CANOVANAS | 2021-07-09 21:28 | 2021-07-10 11:35 | 100 | 014:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN RISER Y 1 X 8 EN TRANSFORMADOR REMPLAZO AISLADOR | R21070900041 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 847 | 2021-07-09 | 84700 | keep | 0 | Jul | 2021 | 0.057689 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-07-09 21:36 | 2021-07-09 21:38 | 172 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S21070900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-09 | 344 | keep | 0 | Jul | 2021 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2021-07-09 21:40 | 2021-07-09 22:12 | 3718 | 000:32 | T | DESGANCHE | DISPARO DE INTERRUPTOR PROBO MALO SE SECCIONALIZO PARA TRABAJAR Y SE CERRO POR SCADA | S21070900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 32 | 2021-07-09 | 118976 | keep | 0 | Jul | 2021 | 0.081034 | 0.0025323 | Sustained | FALSE | FALSE | Not_TMED_Event | 3718
HUMACAO | 2021-07-09 21:47 | 2021-07-10 16:18 | 215 | 018:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN SALIDA DEL CONVERTIDOR Y 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21070900282 | New_Event | Bad Weather | Include | Include | Weather | 1111 | 2021-07-09 | 238865 | keep | 0 | Jul | 2021 | 0.16269 | 0.00014644 | Sustained | FALSE | TRUE | Not_TMED_Event | 215
ARECIBO | 2021-07-09 21:48 | 2021-07-09 21:49 | 4607 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21070900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-09 | 4607 | keep | 0 | Jul | 2021 | 0.0031378 | 0.0031378 | Momentary | FALSE | FALSE | Not_TMED_Event | 4607
SAN JUAN | 2021-07-09 22:01 | 2021-07-10 14:00 | 55 | 015:59 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | S21070900262 | New_Event | Vegetation Contact | Include | Include | Vegetation | 959 | 2021-07-09 | 52745 | keep | 0 | Jul | 2021 | 0.035924 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
SAN JUAN | 2021-07-09 22:09 | 2021-07-09 22:12 | 255 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6600 | S21070900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-09 | 765 | keep | 0 | Jul | 2021 | 0.00052104 | 0.00017368 | Momentary | FALSE | TRUE | Not_TMED_Event | 255
SAN JUAN | 2021-07-09 22:09 | 2021-07-09 22:12 | 928 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6600 | S21070900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-09 | 2784 | keep | 0 | Jul | 2021 | 0.0018962 | 0.00063206 | Momentary | FALSE | TRUE | Not_TMED_Event | 928
SAN JUAN | 2021-07-09 22:09 | 2021-07-09 22:12 | 200 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6600 | S21070900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-09 | 600 | keep | 0 | Jul | 2021 | 0.00040866 | 0.00013622 | Momentary | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-07-09 22:09 | 2021-07-09 22:12 | 185 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6600 | S21070900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-09 | 555 | keep | 0 | Jul | 2021 | 0.00037801 | 0.000126 | Momentary | FALSE | TRUE | Not_TMED_Event | 185
SAN JUAN | 2021-07-09 22:09 | 2021-07-09 22:12 | 73 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6600 | S21070900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-09 | 219 | keep | 0 | Jul | 2021 | 0.00014916 | 4.972e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 73
SAN JUAN | 2021-07-09 22:12 | 2021-07-09 23:23 | 1500 | 001:11 | P | DESGANCHE | SE DISPARA INTERRUPTOR PARA REALIZAR OPERACIONES ABRIR MACHETES Y SE CERRO POR SCADA | S21070900000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 71 | 2021-07-09 | 106500 | keep | 0 | Jul | 2021 | 0.072537 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-07-09 22:17 | 2021-07-10 15:45 | 60 | 017:28 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21070900111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1048 | 2021-07-09 | 62880 | keep | 0 | Jul | 2021 | 0.042827 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-07-09 22:22 | 2021-07-10 10:20 | 200 | 011:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 200 Y 2 X 30 EN CORTE DE LINEA | A21070900112 | New_Event | Cutout Failure | Include | Include | Equipment | 718 | 2021-07-09 | 143600 | keep | 0 | Jul | 2021 | 0.097805 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-07-09 22:31 | 2021-07-10 10:45 | 50 | 012:14 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21070900123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 734 | 2021-07-09 | 36700 | keep | 0 | Jul | 2021 | 0.024996 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-07-09 22:37 | 2021-07-10 21:25 | 70 | 022:48 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | R21070900052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1368 | 2021-07-09 | 95760 | keep | 0 | Jul | 2021 | 0.065222 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-07-09 22:40 | 2021-07-10 18:29 | 75 | 019:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA SE CERRO CORTE DE LINEA | M21070900217 | New_Event | Wire Down | Include | Include | Equipment | 1189 | 2021-07-09 | 89175 | keep | 0 | Jul | 2021 | 0.060737 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
UTUADO | 2021-07-09 23:00 | 2021-07-10 14:29 | 32 | 015:29 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21070900115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 929 | 2021-07-09 | 29728 | keep | 0 | Jul | 2021 | 0.020248 | 2.1795e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 32
SAN JUAN | 2021-07-09 23:07 | 2021-07-10 14:00 | 100 | 014:53 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | S21070900298 | New_Event | Vegetation Contact | Include | Include | Vegetation | 893 | 2021-07-09 | 89300 | keep | 0 | Jul | 2021 | 0.060822 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-07-09 23:07 | 2021-07-10 12:15 | 1825 | 013:08 | T | LINEA DE TRANSMISION 38KV | SE RETIRO OVERHEAD SOBRE EL TRONCAL DEL ALIMENTADOR | M21070900225 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 788 | 2021-07-09 | 1438100 | keep | 0 | Jul | 2021 | 0.97948 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2021-07-09 23:23 | 2021-07-09 23:24 | 3718 | 000:01 | T | DESGANCHE | SE SECCIONALIZO Y SE CERRO POR SCADA | S21070900000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-09 | 3718 | keep | 0 | Jul | 2021 | 0.0025323 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-09 23:24 | 2021-07-09 23:51 | 1500 | 000:27 | P | DESGANCHE | SE DISPARA INTERRUPTOR PARA REALIZAR OPERACIONES ABRIR MACHETES Y SE CERRO POR SCADA | S21070900000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 27 | 2021-07-09 | 40500 | keep | 0 | Jul | 2021 | 0.027584 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2021-07-09 23:51 | 2021-07-09 23:52 | 3718 | 000:01 | T | DESGANCHE | HACIENDO OPERACIONES DISPARO INTERRUPTOR SE SECCCIONALIZO Y SE CERRO POR SCADA | S21070900000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-09 | 3718 | keep | 0 | Jul | 2021 | 0.0025323 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-09 23:52 | 2021-07-10 00:36 | 1000 | 000:44 | P | DESGANCHE | SE SECCIONALIZO PARA DESGANCHAR Y SE CERRO MACHETES EN CARR 849 | S21070900000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 44 | 2021-07-09 | 44000 | keep | 0 | Jul | 2021 | 0.029968 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
FAJARDO | 2021-07-09 23:55 | 2021-07-10 05:32 | 1234 | 005:37 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 3 VECES SE DEJO FUERA SE PATRULLO NO SE ENCONTRO CAUSA CERRADO POR CONTROL LLEVANDO LA CARGA DEL 2305-02 | R21071000001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 337 | 2021-07-09 | 415858 | keep | 0 | Jul | 2021 | 0.28324 | 0.00084047 | Sustained | FALSE | FALSE | Not_TMED_Event | 1234
FAJARDO | 2021-07-09 23:55 | 2021-07-10 05:32 | 3012 | 005:37 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 3 VECES SE DEJO FUERA SE PATRULLO NO SE ENCONTRO CAUSA CERRADO POR CONTROL CARGA POR EL 2005-10 | R21071000001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 337 | 2021-07-09 | 1015044 | keep | 0 | Jul | 2021 | 0.69134 | 0.0020515 | Sustained | FALSE | FALSE | Not_TMED_Event | 3012
CANOVANAS | 2021-07-10 00:14 | 2021-07-10 00:17 | 2106 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR CERRADO POR CONTROL | R21071000010 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2021-07-10 | 6318 | keep | 0 | Jul | 2021 | 0.0043032 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
CANOVANAS | 2021-07-10 00:17 | 2021-07-10 16:22 | 100 | 016:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA Y REEMPLAZO CAJA PRIMARIA QUEMADA | R21071000034 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 965 | 2021-07-10 | 96500 | keep | 0 | Jul | 2021 | 0.065726 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-07-10 00:24 | 2021-07-10 12:40 | 22 | 012:16 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A21071000002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 736 | 2021-07-10 | 16192 | keep | 0 | Jul | 2021 | 0.011028 | 1.4984e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 22
SAN JUAN | 2021-07-10 00:36 | 2021-07-10 02:37 | 500 | 002:01 | P | DESGANCHE | SE CERRO MACHETES | S21071000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2021-07-10 | 60500 | keep | 0 | Jul | 2021 | 0.041206 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2021-07-10 00:54 | 2021-07-10 00:55 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1206-03 Y SE CERRO POR SCADA LLEVA 1204-05 | S21071000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-10 | 10211 | keep | 0 | Jul | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-07-10 00:54 | 2021-07-10 00:55 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1206-03 Y SE CERRO POR SCADA LLEVA 1204-05 | S21071000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-10 | 4133 | keep | 0 | Jul | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
CAGUAS | 2021-07-10 00:57 | 2021-07-10 07:14 | 90 | 006:17 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21071000003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 377 | 2021-07-10 | 33930 | keep | 0 | Jul | 2021 | 0.02311 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
PONCE | 2021-07-10 01:09 | 2021-07-10 08:49 | 3744 | 007:40 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ENCONTRO AISLADOR ROTO | P21071000015 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 460 | 2021-07-10 | 1722240 | keep | 0 | Jul | 2021 | 1.173 | 0.00255 | Sustained | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2021-07-10 01:36 | 2021-07-10 12:30 | 34 | 010:54 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | P21071000019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 654 | 2021-07-10 | 22236 | keep | 0 | Jul | 2021 | 0.015145 | 2.3157e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 34
FAJARDO | 2021-07-10 01:57 | 2021-07-11 09:32 | 4 | 031:35 | P | DESGANCHE | 1 X 10 EN CORTE DE LINEA | R21071000031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1895 | 2021-07-10 | 7580 | keep | 0 | Jul | 2021 | 0.0051627 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
SAN JUAN | 2021-07-10 02:06 | 2021-07-10 02:07 | 5290 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21071000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-10 | 5290 | keep | 0 | Jul | 2021 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
CAGUAS | 2021-07-10 02:10 | 2021-07-10 10:56 | 40 | 008:46 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR | C21071000004 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 526 | 2021-07-10 | 21040 | keep | 0 | Jul | 2021 | 0.01433 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-10 04:07 | 2021-07-10 04:16 | 1310 | 000:09 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2021-07-10 | 11790 | keep | 0 | Jul | 2021 | 0.0080301 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2021-07-10 04:07 | 2021-07-10 04:10 | 353 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-07-10 | 1059 | keep | 0 | Jul | 2021 | 0.00072128 | 0.00024043 | Momentary | FALSE | FALSE | Not_TMED_Event | 353
SAN JUAN | 2021-07-10 04:16 | 2021-07-10 04:17 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR Y SE CERRO POR SCADA | S21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-10 | 870 | keep | 0 | Jul | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CAGUAS | 2021-07-10 04:19 | 2021-07-10 11:12 | 40 | 006:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA REMPLAZO PORTAFUSIBLE | C21071000009 | New_Event | Cutout Failure | Include | Include | Equipment | 413 | 2021-07-10 | 16520 | keep | 0 | Jul | 2021 | 0.011252 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-07-10 04:23 | 2021-07-10 10:45 | 1 | 006:22 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHO REMPLAZO CAJA Y DISCO | C21071000010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 382 | 2021-07-10 | 382 | keep | 0 | Jul | 2021 | 0.00026018 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-07-10 04:29 | 2021-07-10 04:30 | 1362 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21071000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-10 | 1362 | keep | 0 | Jul | 2021 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
ARECIBO | 2021-07-10 05:29 | 2021-07-10 10:50 | 100 | 005:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA | A21071000016 | New_Event | Cutout Failure | Include | Include | Equipment | 321 | 2021-07-10 | 32100 | keep | 0 | Jul | 2021 | 0.021863 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
FAJARDO | 2021-07-10 05:32 | 2021-07-10 08:34 | 247 | 003:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y CERRO PUENTE | R21071000088 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 182 | 2021-07-10 | 44954 | keep | 0 | Jul | 2021 | 0.030618 | 0.00016823 | Sustained | FALSE | FALSE | Not_TMED_Event | 247
CANOVANAS | 2021-07-10 06:17 | 2021-07-10 13:21 | 50 | 007:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | R21071000054 | New_Event |  |  | Include | Wildlife | 424 | 2021-07-10 | 21200 | keep | 0 | Jul | 2021 | 0.014439 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-10 06:32 | 2021-07-10 15:00 | 20 | 008:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21071000012 | New_Event | Wire Down | Include | Include | Equipment | 508 | 2021-07-10 | 10160 | keep | 0 | Jul | 2021 | 0.0069199 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-07-10 06:39 | 2021-07-13 18:08 | 100 | 083:29 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE EXPERT | M21071000252 | New_Event | Vegetation Contact | Include | Include | Vegetation | 5009 | 2021-07-10 | 500900 | keep | 0 | Jul | 2021 | 0.34116 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-10 06:46 | 2021-07-10 14:18 | 95 | 007:32 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R21071000057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 452 | 2021-07-10 | 42940 | keep | 0 | Jul | 2021 | 0.029246 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
AGUADILLA | 2021-07-10 06:52 | 2021-07-10 14:50 | 100 | 007:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21071000020 | New_Event | Bad Weather | Include | Include | Weather | 478 | 2021-07-10 | 47800 | keep | 0 | Jul | 2021 | 0.032556 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-07-10 06:52 | 2021-07-10 12:30 | 50 | 005:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A21071000051 | New_Event | Cutout Failure | Include | Include | Equipment | 338 | 2021-07-10 | 16900 | keep | 0 | Jul | 2021 | 0.011511 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-10 07:00 | 2021-07-10 13:55 | 10 | 006:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21071000000 | New_Event | Bad Weather | Include | Include | Weather | 415 | 2021-07-10 | 4150 | keep | 0 | Jul | 2021 | 0.0028265 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-07-10 07:07 | 2021-07-10 08:06 | 80 | 000:59 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | A21071000021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 59 | 2021-07-10 | 4720 | keep | 0 | Jul | 2021 | 0.0032148 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-07-10 07:29 | 2021-07-10 16:18 | 15 | 008:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21071000029 | New_Event | Bad Weather | Include | Include | Weather | 529 | 2021-07-10 | 7935 | keep | 0 | Jul | 2021 | 0.0054045 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-07-10 07:31 | 2021-07-10 13:01 | 1 | 005:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO BAJANTE DE LINEA A CAJA | C21071000030 | New_Event | Wire Down | Include | Include | Equipment | 330 | 2021-07-10 | 330 | keep | 0 | Jul | 2021 | 0.00022476 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-07-10 07:32 | 2021-07-11 19:20 | 90 | 035:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN SU - 3 CRUCE POR IGUANA | R21071000069 | New_Event |  |  | Include | Wildlife | 2148 | 2021-07-10 | 193320 | keep | 0 | Jul | 2021 | 0.13167 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2021-07-10 07:34 | 2021-07-10 07:35 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21071000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-10 | 3718 | keep | 0 | Jul | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
BAYAMON | 2021-07-10 07:35 | 2021-07-10 07:36 | 1983 | 000:01 | T | CABLE SOTERRADO AVERIADO | DISPARO 1801-02 LLEVANDO LA CARGA DEL 1711-04 | B21071000000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2021-07-10 | 1983 | keep | 0 | Jul | 2021 | 0.0013506 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-07-10 07:35 | 2021-07-10 07:36 | 186 | 000:01 | T | CABLE SOTERRADO AVERIADO | DISPARO 1801-02 LLEVANDO LA CARGA DEL 1711-04 Y SE CERRO POR SCADA | B21071000000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2021-07-10 | 186 | keep | 0 | Jul | 2021 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2021-07-10 07:36 | 2021-07-10 14:43 | 27 | 007:07 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL AEREO DE T15 AL T-16 | B21070800057 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 427 | 2021-07-10 | 11529 | keep | 0 | Jul | 2021 | 0.0078523 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
GUAYAMA | 2021-07-10 07:45 | 2021-07-10 18:40 | 12 | 010:55 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 50KVA A 13KV POR UNO DE IGUAL CAPACIDAD. | P21071000068 | New_Event | Service Transformer Failure | Include | Include | Equipment | 655 | 2021-07-10 | 7860 | keep | 0 | Jul | 2021 | 0.0053534 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-07-10 07:56 | 2021-07-10 09:50 | 40 | 001:54 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21071000073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2021-07-10 | 4560 | keep | 0 | Jul | 2021 | 0.0031058 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-07-10 08:09 | 2021-07-10 18:47 | 20 | 010:38 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU-1 | S21071000034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 638 | 2021-07-10 | 12760 | keep | 0 | Jul | 2021 | 0.0086908 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-07-10 08:09 | 2021-07-10 15:45 | 100 | 007:36 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBÃšES SOBRE LAS LINEAS | M21071000026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 456 | 2021-07-10 | 45600 | keep | 0 | Jul | 2021 | 0.031058 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-10 08:14 | 2021-07-10 15:41 | 27 | 007:27 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21071000010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 447 | 2021-07-10 | 12069 | keep | 0 | Jul | 2021 | 0.0082201 | 1.839e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 27
MAYAGÃœEZ | 2021-07-10 08:18 | 2021-07-10 13:04 | 30 | 004:46 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21071000031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 286 | 2021-07-10 | 8580 | keep | 0 | Jul | 2021 | 0.0058438 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BARRANQUITAS | 2021-07-10 08:19 | 2021-07-10 13:07 | 60 | 004:48 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21071000041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2021-07-10 | 17280 | keep | 0 | Jul | 2021 | 0.011769 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-07-10 08:22 | 2021-07-10 12:39 | 65 | 004:17 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO CAUSA | C21071000040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 257 | 2021-07-10 | 16705 | keep | 0 | Jul | 2021 | 0.011378 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BAYAMON | 2021-07-10 08:25 | 2021-07-10 12:57 | 12 | 004:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | B21071000012 | New_Event | Wire Down | Include | Include | Equipment | 272 | 2021-07-10 | 3264 | keep | 0 | Jul | 2021 | 0.0022231 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2021-07-10 08:34 | 2021-07-10 10:00 | 1234 | 001:26 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO EL ALIMENTADOR | R21071000088 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 86 | 2021-07-10 | 106124 | keep | 0 | Jul | 2021 | 0.072281 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-10 08:39 | 2021-07-10 10:01 | 40 | 001:22 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21070900223 | New_Event | Vegetation Contact | Include | Include | Vegetation | 82 | 2021-07-10 | 3280 | keep | 0 | Jul | 2021 | 0.002234 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-07-10 08:45 | 2021-07-10 09:18 | 14 | 000:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | P21070900018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 33 | 2021-07-10 | 462 | keep | 0 | Jul | 2021 | 0.00031467 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2021-07-10 08:53 | 2021-07-10 14:54 | 52 | 006:01 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21071000037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 361 | 2021-07-10 | 18772 | keep | 0 | Jul | 2021 | 0.012786 | 3.5417e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 52
HUMACAO | 2021-07-10 09:21 | 2021-07-10 09:22 | 2354 | 000:01 | T | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | RECIERRE | C21071000000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1 | 2021-07-10 | 2354 | keep | 0 | Jul | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
HUMACAO | 2021-07-10 09:22 | 2021-07-10 12:48 | 8 | 003:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BARRAS DE PEDESTAL | C21070900274 | 1st_after_momentary | Secondary Wire Down | Include | Include | Equipment | 206 | 2021-07-10 | 1648 | keep | 0 | Jul | 2021 | 0.0011224 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-07-10 09:24 | 2021-07-10 12:11 | 30 | 002:47 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21071000032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 167 | 2021-07-10 | 5010 | keep | 0 | Jul | 2021 | 0.0034123 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-07-10 09:26 | 2021-07-12 17:22 | 12 | 055:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO BAJANTE SECUNDARIO DE TRANSFORMADOR | B21071000034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 3356 | 2021-07-10 | 40272 | keep | 0 | Jul | 2021 | 0.027429 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-07-10 09:31 | 2021-07-10 11:15 | 10 | 001:44 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR DESGANCHE | R21071000118 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 104 | 2021-07-10 | 1040 | keep | 0 | Jul | 2021 | 0.00070834 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-10 09:35 | 2021-07-10 09:36 | 90 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21071000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-10 | 90 | keep | 0 | Jul | 2021 | 6.1299e-05 | 6.1299e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2021-07-10 09:35 | 2021-07-10 09:36 | 1105 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1100-05 LLEVA LA CARGA DE 1109-01 Y 1109-04 SE CERRO INTERRUPTOR LOCAL POR PERSONAL DE CONSERVACION | S21071000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-10 | 1105 | keep | 0 | Jul | 2021 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
SAN JUAN | 2021-07-10 09:35 | 2021-07-10 09:36 | 351 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1100-05 LLEVA LA CARGA DE 1109-01 Y 1109-04 SE CERRO INTERRUPTOR LOCAL POR PERSONAL DE CONSERVACION | S21071000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-10 | 351 | keep | 0 | Jul | 2021 | 0.00023906 | 0.00023906 | Momentary | FALSE | FALSE | Not_TMED_Event | 351
CAGUAS | 2021-07-10 09:36 | 2021-07-10 14:21 | 2 | 004:45 | P | LINEA DE TRANSMISION 115KV | SE ABRIO CORTE DE LINEA PARA REEMPLAZAR AISLACION EN LINEA 51000 LINEA TRANSMISION 230KV | C21071000000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 285 | 2021-07-10 | 570 | keep | 0 | Jul | 2021 | 0.00038822 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
ARECIBO | 2021-07-10 09:47 | 2021-07-10 12:02 | 125 | 002:15 | P | SOBRECARGA | 1 X 200 EN CORTE DE LINEA POR CARGA | A21071000052 | New_Event | Trip Due To Overload | Include | Include | Other | 135 | 2021-07-10 | 16875 | keep | 0 | Jul | 2021 | 0.011493 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
BARRANQUITAS | 2021-07-10 09:47 | 2021-07-10 15:30 | 30 | 005:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA QUEMADA | C21071000055 | New_Event | Cutout Failure | Include | Include | Equipment | 343 | 2021-07-10 | 10290 | keep | 0 | Jul | 2021 | 0.0070085 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
AGUADILLA | 2021-07-10 09:56 | 2021-07-10 14:30 | 100 | 004:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21070900029 | New_Event | Bad Weather | Include | Include | Weather | 274 | 2021-07-10 | 27400 | keep | 0 | Jul | 2021 | 0.018662 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
FAJARDO | 2021-07-10 10:00 | 2021-07-10 12:15 | 247 | 002:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y CERRO PUENTE | R21071000088 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 135 | 2021-07-10 | 33345 | keep | 0 | Jul | 2021 | 0.022711 | 0.00016823 | Sustained | FALSE | FALSE | Not_TMED_Event | 247
ARECIBO | 2021-07-10 10:01 | 2021-07-10 16:36 | 1 | 006:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21071000055 | New_Event | Bad Weather | Include | Include | Weather | 395 | 2021-07-10 | 395 | keep | 0 | Jul | 2021 | 0.00026903 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
YAUCO | 2021-07-10 10:03 | 2021-07-11 14:53 | 10 | 028:50 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR POR DESGANCHE SECUNDARIO | P21071000104 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1730 | 2021-07-10 | 17300 | keep | 0 | Jul | 2021 | 0.011783 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-10 10:09 | 2021-07-12 10:30 | 60 | 048:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO EN CORTE DE LINEA | M21071000065 | New_Event | Wire Down | Include | Include | Equipment | 2901 | 2021-07-10 | 174060 | keep | 0 | Jul | 2021 | 0.11855 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-07-10 10:15 | 2021-07-10 18:00 | 75 | 007:45 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBÃšES SOBRE LAS LINEAS | M21071000067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 465 | 2021-07-10 | 34875 | keep | 0 | Jul | 2021 | 0.023753 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
CANOVANAS | 2021-07-10 10:18 | 2021-07-10 14:51 | 50 | 004:33 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA RETIRAR POSTE ROTO VACANTE SOBRE LINEAS | R21071000135 | New_Event | Defective Pole | Include | Include | Equipment | 273 | 2021-07-10 | 13650 | keep | 0 | Jul | 2021 | 0.009297 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-07-10 10:38 | 2021-07-11 12:45 | 47 | 026:07 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | P21071100035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1567 | 2021-07-10 | 73649 | keep | 0 | Jul | 2021 | 0.050162 | 3.2011e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 47
CAGUAS | 2021-07-10 10:59 | 2021-07-10 12:26 | 100 | 001:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 Y 1 X 65 EN CORTES DE LINEA CRUCE POR GLOBOS | C21071000078 | New_Event |  |  | Include | Wildlife | 87 | 2021-07-10 | 8700 | keep | 0 | Jul | 2021 | 0.0059255 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-10 11:04 | 2021-07-10 11:49 | 2391 | 000:45 | T | DESGANCHE | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21071000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 45 | 2021-07-10 | 107595 | keep | 0 | Jul | 2021 | 0.073282 | 0.0016285 | Sustained | FALSE | FALSE | Not_TMED_Event | 2391
BAYAMON | 2021-07-10 11:04 | 2021-07-10 11:38 | 125 | 000:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIERON MACHETES Y SE CERRO PUENTE ABIERTO TRASPATIO | B21070900071 | New_Event | Wire Down | Include | Include | Equipment | 34 | 2021-07-10 | 4250 | keep | 0 | Jul | 2021 | 0.0028947 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2021-07-10 11:04 | 2021-07-10 11:05 | 67 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1705-05 LLEVANDO 1705-04 | B21071000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-10 | 67 | keep | 0 | Jul | 2021 | 4.5633e-05 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2021-07-10 11:05 | 2021-07-10 11:06 | 637 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVANDO LA CARGA DEL 1705-04 | B21071000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-10 | 637 | keep | 0 | Jul | 2021 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
PONCE | 2021-07-10 11:17 | 2021-07-10 13:10 | 175 | 001:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA | P21071000116 | New_Event | Wire Down | Include | Include | Equipment | 113 | 2021-07-10 | 19775 | keep | 0 | Jul | 2021 | 0.013469 | 0.00011919 | Sustained | FALSE | TRUE | Not_TMED_Event | 175
YAUCO | 2021-07-10 11:19 | 2021-07-11 10:40 | 133 | 023:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA REEMPLAZO CAJA | P21071000118 | New_Event | Cutout Failure | Include | Include | Equipment | 1401 | 2021-07-10 | 186333 | keep | 0 | Jul | 2021 | 0.12691 | 9.0586e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 133
PONCE | 2021-07-10 11:20 | 2021-07-10 11:22 | 3744 | 000:02 | T | NO SE REPORTO CAUSA | SE DISPARA ALIMENTADOR AL CERRAR MACHETES EN SU | P21071000107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-10 | 7488 | keep | 0 | Jul | 2021 | 0.0051 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
YAUCO | 2021-07-10 11:28 | 2021-07-11 09:15 | 87 | 021:47 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA ARBOL SOBRE LA LINEA | P21071000120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1307 | 2021-07-10 | 113709 | keep | 0 | Jul | 2021 | 0.077447 | 5.9255e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 87
SAN JUAN | 2021-07-10 11:43 | 2021-07-10 20:20 | 110 | 008:37 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU - 4 Y 1 X 50 EN SU - 3 | R21071000145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 517 | 2021-07-10 | 56870 | keep | 0 | Jul | 2021 | 0.038734 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
BARRANQUITAS | 2021-07-10 11:44 | 2021-07-10 16:20 | 11 | 004:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN TRANSFORMADOR SE RETIRO TENSOR SOBRE BUSHING DEL TRANSFORMADOR | C21071000088 | New_Event | Wire Down | Include | Include | Equipment | 276 | 2021-07-10 | 3036 | keep | 0 | Jul | 2021 | 0.0020678 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2021-07-10 11:45 | 2021-07-11 13:14 | 99 | 025:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21071000089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1529 | 2021-07-10 | 151371 | keep | 0 | Jul | 2021 | 0.1031 | 6.7428e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 99
BAYAMON | 2021-07-10 11:48 | 2021-07-10 11:49 | 1715 | 000:01 | T | SECUNDARIA/DESGANCHE | DISPARO Y SE CERRO POR CONTROL | B21071000000 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1 | 2021-07-10 | 1715 | keep | 0 | Jul | 2021 | 0.0011681 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
ARECIBO | 2021-07-10 11:48 | 2021-07-10 14:30 | 400 | 002:42 | P | ESTRUCTURA AVERIADA | 2 X 100 EN CORTE DE LINEA SE SECCIONALIZO POSTE PRIMARIO PARTIDO | A21071000065 | New_Event | Defective Pole | Include | Include | Equipment | 162 | 2021-07-10 | 64800 | keep | 0 | Jul | 2021 | 0.044135 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
BAYAMON | 2021-07-10 11:49 | 2021-07-10 15:30 | 60 | 003:41 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | B21071000058 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 221 | 2021-07-10 | 13260 | keep | 0 | Jul | 2021 | 0.0090313 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-07-10 11:49 | 2021-07-10 14:50 | 8 | 003:01 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR SE REALIZO DESGANCHE | B21070800007 | 1st_after_momentary | Secondary Vegetation | Include | Include | Vegetation | 181 | 2021-07-10 | 1448 | keep | 0 | Jul | 2021 | 0.00098623 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2021-07-10 11:50 | 2021-07-10 16:25 | 25 | 004:35 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21071000066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2021-07-10 | 6875 | keep | 0 | Jul | 2021 | 0.0046825 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
PONCE | 2021-07-10 12:00 | 2021-07-10 15:34 | 50 | 003:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN RISER, AVE CRUZO FASE | P210710000XX | New_Event |  |  | Include | Wildlife | 214 | 2021-07-10 | 10700 | keep | 0 | Jul | 2021 | 0.0072877 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-07-10 12:02 | 2021-07-10 18:29 | 27 | 006:27 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21071000077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 387 | 2021-07-10 | 10449 | keep | 0 | Jul | 2021 | 0.0071168 | 1.839e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 27
BAYAMON | 2021-07-10 12:05 | 2021-07-10 17:17 | 16 | 005:12 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | B21071000078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 312 | 2021-07-10 | 4992 | keep | 0 | Jul | 2021 | 0.0034 | 1.0898e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 16
PONCE | 2021-07-10 12:09 | 2021-07-10 14:30 | 500 | 002:21 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO AISLAOR Y SE CERRARON MACHETES | P21071000137 | New_Event | Switch Failure | Include | Include | Equipment | 141 | 2021-07-10 | 70500 | keep | 0 | Jul | 2021 | 0.048017 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2021-07-10 12:17 | 2021-07-10 12:18 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21071000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-10 | 3718 | keep | 0 | Jul | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
HUMACAO | 2021-07-10 12:27 | 2021-07-10 17:19 | 80 | 004:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA REEMPLAZO AISLADOR ROTO | C21071000094 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 292 | 2021-07-10 | 23360 | keep | 0 | Jul | 2021 | 0.01591 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-07-10 12:39 | 2021-07-10 15:15 | 90 | 002:36 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA REEMPLAZO AISLADOR SAFADO | C21071000098 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 156 | 2021-07-10 | 14040 | keep | 0 | Jul | 2021 | 0.0095626 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
SAN JUAN | 2021-07-10 12:43 | 2021-07-10 15:10 | 837 | 002:27 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE REEMPLAZO MACHETE EN RISER DE SALIDA Y SE CERRO POR SCADA CARGA POR EL 1401-07 | S21071000082 | New_Event | Switch Failure | Include | Include | Equipment | 147 | 2021-07-10 | 123039 | keep | 0 | Jul | 2021 | 0.083801 | 0.00057008 | Sustained | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2021-07-10 12:43 | 2021-07-10 15:10 | 908 | 002:27 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE REEMPLAZO MACHETE EN RISER DE SALIDA Y SE CERRO POR SCADA LLEVANDO LA CARGA DEL 1401-06 | S21071000082 | New_Event | Switch Failure | Include | Include | Equipment | 147 | 2021-07-10 | 133476 | keep | 0 | Jul | 2021 | 0.09091 | 0.00061843 | Sustained | FALSE | FALSE | Not_TMED_Event | 908
YAUCO | 2021-07-10 12:45 | 2021-07-11 11:37 | 128 | 022:52 | P | OTRAS CAUSAS | SE ENCONTRO CAJA PRIMARIA EN CORTE DE LINEA ABIERTA | P21071000131 | New_Event | Other Causes | Include | Include | Other | 1372 | 2021-07-10 | 175616 | keep | 0 | Jul | 2021 | 0.11961 | 8.718e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 128
PONCE | 2021-07-10 12:47 | 2021-07-10 12:54 | 2379 | 000:07 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE DISPARO ALIMENTADOR AL CERRAR RISER | P21071000136 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 7 | 2021-07-10 | 16653 | keep | 0 | Jul | 2021 | 0.011342 | 0.0016203 | Sustained | FALSE | FALSE | Not_TMED_Event | 2379
BAYAMON | 2021-07-10 12:55 | 2021-07-10 12:56 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21071000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-10 | 2605 | keep | 0 | Jul | 2021 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
AGUADILLA | 2021-07-10 13:27 | 2021-07-10 15:26 | 574 | 001:59 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21071000198 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 119 | 2021-07-10 | 68306 | keep | 0 | Jul | 2021 | 0.046523 | 0.00039095 | Sustained | FALSE | TRUE | Not_TMED_Event | 574
AGUADILLA | 2021-07-10 13:27 | 2021-07-10 15:26 | 2493 | 001:59 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21071000198 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 119 | 2021-07-10 | 296667 | keep | 0 | Jul | 2021 | 0.20206 | 0.001698 | Sustained | FALSE | TRUE | Not_TMED_Event | 2493
AGUADILLA | 2021-07-10 13:27 | 2021-07-10 15:26 | 1415 | 001:59 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21071000198 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 119 | 2021-07-10 | 168385 | keep | 0 | Jul | 2021 | 0.11469 | 0.00096375 | Sustained | FALSE | TRUE | Not_TMED_Event | 1415
AGUADILLA | 2021-07-10 13:27 | 2021-07-10 15:26 | 1428 | 001:59 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21071000198 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 119 | 2021-07-10 | 169932 | keep | 0 | Jul | 2021 | 0.11574 | 0.0009726 | Sustained | FALSE | TRUE | Not_TMED_Event | 1428
AGUADILLA | 2021-07-10 13:27 | 2021-07-10 15:26 | 1036 | 001:59 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21071000198 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 119 | 2021-07-10 | 123284 | keep | 0 | Jul | 2021 | 0.083968 | 0.00070561 | Sustained | FALSE | TRUE | Not_TMED_Event | 1036
AGUADILLA | 2021-07-10 13:27 | 2021-07-10 15:26 | 382 | 001:59 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21071000199 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 119 | 2021-07-10 | 45458 | keep | 0 | Jul | 2021 | 0.030961 | 0.00026018 | Sustained | FALSE | TRUE | Not_TMED_Event | 382
AGUADILLA | 2021-07-10 13:27 | 2021-07-10 15:26 | 39 | 001:59 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21071000199 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 119 | 2021-07-10 | 4641 | keep | 0 | Jul | 2021 | 0.003161 | 2.6563e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 39
AGUADILLA | 2021-07-10 13:27 | 2021-07-10 15:26 | 2366 | 001:59 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21071000201 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 119 | 2021-07-10 | 281554 | keep | 0 | Jul | 2021 | 0.19177 | 0.0016115 | Sustained | FALSE | TRUE | Not_TMED_Event | 2366
MAYAGÃœEZ | 2021-07-10 13:27 | 2021-07-10 15:26 | 1337 | 001:59 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21071000201 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 119 | 2021-07-10 | 159103 | keep | 0 | Jul | 2021 | 0.10836 | 0.00091062 | Sustained | FALSE | TRUE | Not_TMED_Event | 1337
AGUADILLA | 2021-07-10 13:27 | 2021-07-10 15:26 | 709 | 001:59 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21071000201 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 119 | 2021-07-10 | 84371 | keep | 0 | Jul | 2021 | 0.057465 | 0.0004829 | Sustained | FALSE | TRUE | Not_TMED_Event | 709
AGUADILLA | 2021-07-10 13:28 | 2021-07-10 13:29 | 3041 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR POR DESCARGAS ELECTRICAS | M21071000026 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-10 | 3041 | keep | 0 | Jul | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2021-07-10 13:29 | 2021-07-10 16:18 | 70 | 002:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21071000119 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 169 | 2021-07-10 | 11830 | keep | 0 | Jul | 2021 | 0.0080574 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
ARECIBO | 2021-07-10 13:30 | 2021-07-10 19:28 | 10 | 005:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA AVERIADA EN TRANSFORMADOR | A21071000095 | New_Event | Cutout Failure | Include | Include | Equipment | 358 | 2021-07-10 | 3580 | keep | 0 | Jul | 2021 | 0.0024383 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-07-10 13:57 | 2021-07-11 17:30 | 1 | 027:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21071000154 | New_Event | Bad Weather | Include | Include | Weather | 1653 | 2021-07-10 | 1653 | keep | 0 | Jul | 2021 | 0.0011259 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-07-10 13:59 | 2021-07-13 16:40 | 1 | 074:41 | P | NO SE REPORTO CAUSA | 1 X 25 EN SU | B21071000093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4481 | 2021-07-10 | 4481 | keep | 0 | Jul | 2021 | 0.003052 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-07-10 14:05 | 2021-07-11 10:22 | 3 | 020:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LA LINEA SECUNDARIA | C21071000111 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1217 | 2021-07-10 | 3651 | keep | 0 | Jul | 2021 | 0.0024867 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
CAGUAS | 2021-07-10 14:06 | 2021-07-10 15:34 | 5 | 001:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR REEMPLAZO SECUNDARIA AVERIADA | C21071000112 | New_Event | Secondary Wire Down | Include | Include | Equipment | 88 | 2021-07-10 | 440 | keep | 0 | Jul | 2021 | 0.00029968 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2021-07-10 14:21 | 2021-07-10 23:02 | 50 | 008:41 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21071000178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 521 | 2021-07-10 | 26050 | keep | 0 | Jul | 2021 | 0.017743 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-07-10 14:29 | 2021-07-10 21:12 | 100 | 006:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO BAJANTE DE CORTE DE LINEA | M21071000139 | New_Event | Wire Down | Include | Include | Equipment | 403 | 2021-07-10 | 40300 | keep | 0 | Jul | 2021 | 0.027448 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-07-10 14:30 | 2021-07-10 15:40 | 29 | 001:10 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR AL REALIZAR PRUEBAS A SOTERRADO | P210710000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 70 | 2021-07-10 | 2030 | keep | 0 | Jul | 2021 | 0.0013826 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
ARECIBO | 2021-07-10 14:30 | 2021-07-10 18:00 | 20 | 003:30 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO SE CERRO PUENTES | A21071000065 | Partial_restoration | Defective Pole | Include | Include | Equipment | 210 | 2021-07-10 | 4200 | keep | 0 | Jul | 2021 | 0.0028606 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-07-10 14:37 | 2021-07-10 17:17 | 60 | 002:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 Y 1 X 25 EN CORTES DE LINEAS REEMPLAZO CAJA QUEMADA | R21071000159 | New_Event | Cutout Failure | Include | Include | Equipment | 160 | 2021-07-10 | 9600 | keep | 0 | Jul | 2021 | 0.0065385 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-07-10 14:44 | 2021-07-10 17:11 | 5 | 002:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | A21071000082 | New_Event | Wire Down | Include | Include | Equipment | 147 | 2021-07-10 | 735 | keep | 0 | Jul | 2021 | 0.00050061 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-07-10 14:53 | 2021-07-10 17:31 | 25 | 002:38 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA Y 2 X 10 EN TRANSFORMADOR | B21071000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2021-07-10 | 3950 | keep | 0 | Jul | 2021 | 0.0026903 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-07-10 14:59 | 2021-07-10 17:37 | 1 | 002:38 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | A21071000083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2021-07-10 | 158 | keep | 0 | Jul | 2021 | 0.00010761 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
UTUADO | 2021-07-10 15:02 | 2021-07-11 13:51 | 25 | 022:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A21071000084 | New_Event | Wire Down | Include | Include | Equipment | 1369 | 2021-07-10 | 34225 | keep | 0 | Jul | 2021 | 0.02331 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-07-10 15:17 | 2021-07-10 17:19 | 120 | 002:02 | P | NO SE REPORTO CAUSA | 1 X 100 Y 2 X 65 EN CORTES DE LINEA | B21070900055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2021-07-10 | 14640 | keep | 0 | Jul | 2021 | 0.0099712 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
CAGUAS | 2021-07-10 15:19 | 2021-07-11 04:59 | 65 | 013:40 | P | TRANSFORMADOR AVERIADO | SE ABRIO CORTE DE LINEA PARA REEMPLAZAR TRANSFORMADOR AVERIADO DE 15KVA X 15KVA | C21070800128 | New_Event | Service Transformer Failure | Include | Include | Equipment | 820 | 2021-07-10 | 53300 | keep | 0 | Jul | 2021 | 0.036302 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
YAUCO | 2021-07-10 15:23 | 2021-07-10 15:24 | 3973 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210710000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-10 | 3973 | keep | 0 | Jul | 2021 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2021-07-10 15:23 | 2021-07-10 15:24 | 2484 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210710000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-10 | 2484 | keep | 0 | Jul | 2021 | 0.0016918 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
BAYAMON | 2021-07-10 15:24 | 2021-07-10 17:10 | 50 | 001:46 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21071000049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2021-07-10 | 5300 | keep | 0 | Jul | 2021 | 0.0036098 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-07-10 15:26 | 2021-07-16 18:36 | 2 | 147:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21071000201 | New_Event | Bad Weather | Include | Include | Weather | 8830 | 2021-07-10 | 17660 | keep | 0 | Jul | 2021 | 0.012028 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
MAYAGÃœEZ | 2021-07-10 15:26 | 2021-07-10 16:10 | 1337 | 000:44 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO INTERRUPTOR PROBLEMA COMUNICACION NO CAMBIA STATUS A OPEN SE CERRO MANUAL ELECTRICO MAL TIEMPO DESCARGAS ELECTRICAS EN EL AREA | M21071000000 | New_Event | Bad Weather | Include | Include | Weather | 44 | 2021-07-10 | 58828 | keep | 0 | Jul | 2021 | 0.040067 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
PONCE | 2021-07-10 15:40 | 2021-07-10 15:41 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR AL REALIZAR PRUEBAS A SOTERRADO | P210710000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-10 | 3744 | keep | 0 | Jul | 2021 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2021-07-10 15:40 | 2021-07-10 15:41 | 3114 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR AL REALIZAR PRUEBAS A SOTERRADO | P210710000XX | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-10 | 3114 | keep | 0 | Jul | 2021 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
PONCE | 2021-07-10 15:41 | 2021-07-10 16:29 | 29 | 000:48 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO RISER DE SALIDA | P210710000XX | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 48 | 2021-07-10 | 1392 | keep | 0 | Jul | 2021 | 0.00094808 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
BAYAMON | 2021-07-10 15:43 | 2021-07-10 17:19 | 1 | 001:36 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | B21071000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2021-07-10 | 96 | keep | 0 | Jul | 2021 | 6.5385e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2021-07-10 15:49 | 2021-07-10 17:16 | 11 | 001:27 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C21071000126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2021-07-10 | 957 | keep | 0 | Jul | 2021 | 0.00065181 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2021-07-10 15:50 | 2021-07-12 15:10 | 11 | 047:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R21071000039 | New_Event |  |  | Include | Wildlife | 2840 | 2021-07-10 | 31240 | keep | 0 | Jul | 2021 | 0.021277 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2021-07-10 15:55 | 2021-07-12 13:27 | 80 | 045:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA Y SE RETESO LINEA PRIMARIA | S21071000108 | New_Event | Wire Down | Include | Include | Equipment | 2732 | 2021-07-10 | 218560 | keep | 0 | Jul | 2021 | 0.14886 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CANOVANAS | 2021-07-10 16:22 | 2021-07-10 18:53 | 95 | 002:31 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA Y PIN POLE TOP | R21071000166 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 151 | 2021-07-10 | 14345 | keep | 0 | Jul | 2021 | 0.0097703 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
ARECIBO | 2021-07-10 16:29 | 2021-07-10 16:30 | 1066 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21071000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-10 | 1066 | keep | 0 | Jul | 2021 | 0.00072605 | 0.00072605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1066
HUMACAO | 2021-07-10 17:32 | 2021-07-11 11:10 | 70 | 017:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 Y 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C21071000132 | New_Event |  |  | Include | Wildlife | 1058 | 2021-07-10 | 74060 | keep | 0 | Jul | 2021 | 0.050442 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
CAGUAS | 2021-07-10 17:46 | 2021-07-11 10:09 | 120 | 016:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 Y 2 X 50 EN CORTE DE LINEA LLUVIAS | C21071000135 | New_Event | Bad Weather | Include | Include | Weather | 983 | 2021-07-10 | 117960 | keep | 0 | Jul | 2021 | 0.080342 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
MAYAGÃœEZ | 2021-07-10 17:55 | 2021-07-11 11:10 | 200 | 017:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | M21071000232 | New_Event | Cutout Failure | Include | Include | Equipment | 1035 | 2021-07-10 | 207000 | keep | 0 | Jul | 2021 | 0.14099 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
HUMACAO | 2021-07-10 18:08 | 2021-07-10 18:09 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21071000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-10 | 1827 | keep | 0 | Jul | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
SAN JUAN | 2021-07-10 18:24 | 2021-07-11 13:26 | 23 | 019:02 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R21071000177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1142 | 2021-07-10 | 26266 | keep | 0 | Jul | 2021 | 0.01789 | 1.5665e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 23
BAYAMON | 2021-07-10 18:29 | 2021-07-11 11:50 | 50 | 017:21 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21071000120 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1041 | 2021-07-10 | 52050 | keep | 0 | Jul | 2021 | 0.035451 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-07-10 18:35 | 2021-07-11 17:35 | 40 | 023:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA DE CORTE DE LINEA | A21071000099 | New_Event | Cutout Failure | Include | Include | Equipment | 1380 | 2021-07-10 | 55200 | keep | 0 | Jul | 2021 | 0.037596 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-10 18:42 | 2021-07-10 20:28 | 1715 | 001:46 | T | BREAKER DEFECTUOSO O NO OPERA | DISPARO DE INTERRUPTOR SE TRANSFIRIO LA CARGA AL 1708-03 POR INTERRUPTOR 1708-02 AVERIADO | B21071000000 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 106 | 2021-07-10 | 181790 | keep | 0 | Jul | 2021 | 0.12382 | 0.0011681 | Sustained | FALSE | FALSE | Not_TMED_Event | 1715
ARECIBO | 2021-07-10 18:45 | 2021-07-11 09:15 | 12 | 014:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21071000096 | New_Event | Bad Weather | Include | Include | Weather | 870 | 2021-07-10 | 10440 | keep | 0 | Jul | 2021 | 0.0071106 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2021-07-10 18:58 | 2021-07-10 23:25 | 10 | 004:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIAS | R21071000179 | New_Event | Bad Weather | Include | Include | Weather | 267 | 2021-07-10 | 2670 | keep | 0 | Jul | 2021 | 0.0018185 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-07-10 19:11 | 2021-07-10 20:01 | 20 | 000:50 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA REQUIERE DESGANCHE | A21071000098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 50 | 2021-07-10 | 1000 | keep | 0 | Jul | 2021 | 0.0006811 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-07-10 19:17 | 2021-07-11 13:50 | 100 | 18:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | M21071000238 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1113 | 2021-07-10 | 111300 | keep | 0 | Jul | 2021 | 0.075806 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-07-10 19:23 | 2021-07-11 08:57 | 80 | 013:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIUAS | C21071000140 | New_Event | Bad Weather | Include | Include | Weather | 814 | 2021-07-10 | 65120 | keep | 0 | Jul | 2021 | 0.044353 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-07-10 19:28 | 2021-07-12 17:00 | 6 | 045:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | M21071000240 | New_Event | Bad Weather | Include | Include | Weather | 2732 | 2021-07-10 | 16392 | keep | 0 | Jul | 2021 | 0.011165 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-07-10 19:35 | 2021-07-11 08:40 | 15 | 013:05 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B21070800072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 785 | 2021-07-10 | 11775 | keep | 0 | Jul | 2021 | 0.0080199 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-07-10 19:48 | 2021-07-10 20:00 | 458 | 000:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV MIRADOR | A21071000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 12 | 2021-07-10 | 5496 | keep | 0 | Jul | 2021 | 0.0037433 | 0.00031194 | Sustained | FALSE | FALSE | Not_TMED_Event | 458
ARECIBO | 2021-07-10 19:48 | 2021-07-10 20:00 | 437 | 000:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV MIRADOR | A21071000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 12 | 2021-07-10 | 5244 | keep | 0 | Jul | 2021 | 0.0035717 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
ARECIBO | 2021-07-10 19:48 | 2021-07-10 20:00 | 1185 | 000:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV MIRADOR | A21071000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 12 | 2021-07-10 | 14220 | keep | 0 | Jul | 2021 | 0.0096852 | 0.0008071 | Sustained | FALSE | FALSE | Not_TMED_Event | 1185
ARECIBO | 2021-07-10 19:48 | 2021-07-10 20:00 | 63 | 000:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV MIRADOR | A21071000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 12 | 2021-07-10 | 756 | keep | 0 | Jul | 2021 | 0.00051491 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
ARECIBO | 2021-07-10 19:48 | 2021-07-10 20:00 | 232 | 000:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV MIRADOR | A21071000000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 12 | 2021-07-10 | 2784 | keep | 0 | Jul | 2021 | 0.0018962 | 0.00015801 | Sustained | FALSE | FALSE | Not_TMED_Event | 232
ARECIBO | 2021-07-10 19:48 | 2021-07-10 22:31 | 2694 | 002:43 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE 38KV MIRADOR | A21071000143 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 163 | 2021-07-10 | 439122 | keep | 0 | Jul | 2021 | 0.29908 | 0.0018349 | Sustained | FALSE | FALSE | Not_TMED_Event | 2694
ARECIBO | 2021-07-10 19:48 | 2021-07-10 22:31 | 2228 | 002:43 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE 38KV MIRADOR CARGA DEL 8007-03 A TRAVÃ‰S DEL 8007-04 | A21071000143 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 163 | 2021-07-10 | 363164 | keep | 0 | Jul | 2021 | 0.24735 | 0.0015175 | Sustained | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2021-07-10 19:48 | 2021-07-10 22:31 | 438 | 002:43 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE 38KV MIRADOR EL 8007-04 LLEVA LA CARGA DEL 8007-03 | A21071000143 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 163 | 2021-07-10 | 71394 | keep | 0 | Jul | 2021 | 0.048626 | 0.00029832 | Sustained | FALSE | FALSE | Not_TMED_Event | 438
ARECIBO | 2021-07-10 19:48 | 2021-07-10 21:15 | 2201 | 001:27 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE 38KV MIRADOR | A21071000144 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 87 | 2021-07-10 | 191487 | keep | 0 | Jul | 2021 | 0.13042 | 0.0014991 | Sustained | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2021-07-10 19:48 | 2021-07-10 21:15 | 1986 | 001:27 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO LA BARRA DE 38KV MIRADOR | A21071000144 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 87 | 2021-07-10 | 172782 | keep | 0 | Jul | 2021 | 0.11768 | 0.0013527 | Sustained | FALSE | FALSE | Not_TMED_Event | 1986
ARECIBO | 2021-07-10 19:48 | 2021-07-10 21:15 | 199 | 001:27 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE 38KV MIRADOR | A21071000144 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 87 | 2021-07-10 | 17313 | keep | 0 | Jul | 2021 | 0.011792 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2021-07-10 19:48 | 2021-07-10 21:15 | 24 | 001:27 | S | DISPARO DE BARRA DE TRANSMISION | SE ENERGIZO LA BARRA DE 38KV MIRADOR | A21071000144 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 87 | 2021-07-10 | 2088 | keep | 0 | Jul | 2021 | 0.0014221 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2021-07-10 20:26 | 2021-07-10 20:28 | 1498 | 000:02 | T | BREAKER DEFECTUOSO O NO OPERA | SE ABRIO INTERRUPTOR PARA QUE PERSONAL CERRARA MACHETE DE AMARRE CONTRA 1708-02 | B21071000000 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 2 | 2021-07-10 | 2996 | keep | 0 | Jul | 2021 | 0.0020406 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
MAYAGÃœEZ | 2021-07-10 21:37 | 2021-07-11 10:29 | 150 | 012:52 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | M21071000252 | New_Event | Vegetation Contact | Include | Include | Vegetation | 772 | 2021-07-10 | 115800 | keep | 0 | Jul | 2021 | 0.078871 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
HUMACAO | 2021-07-10 22:16 | 2021-07-11 09:54 | 90 | 011:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | C21071000145 | New_Event | Wire Down | Include | Include | Equipment | 698 | 2021-07-10 | 62820 | keep | 0 | Jul | 2021 | 0.042786 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
ARECIBO | 2021-07-10 23:09 | 2021-07-11 16:20 | 30 | 017:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A21071100001 | New_Event | Wire Down | Include | Include | Equipment | 1031 | 2021-07-10 | 30930 | keep | 0 | Jul | 2021 | 0.021066 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
FAJARDO | 2021-07-10 23:25 | 2021-07-10 23:26 | 1234 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO INTERRUPTOR | R21071000183 | Additional_clients | Bad Weather | Include | Include | Weather | 1 | 2021-07-10 | 1234 | keep | 0 | Jul | 2021 | 0.00084047 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2021-07-10 23:26 | 2021-07-11 07:49 | 10 | 008:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIAS | R21071000179 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 503 | 2021-07-10 | 5030 | keep | 0 | Jul | 2021 | 0.0034259 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BAYAMON | 2021-07-10 23:57 | 2021-07-11 07:07 | 90 | 007:10 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1100-05 LLEVA LA CARGA DE 1109-01 Y 1109-04 SE CERRO INTERRUPTOR LOCAL POR PERSONAL DE CONSERVACION | S21071000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 430 | 2021-07-10 | 38700 | keep | 0 | Jul | 2021 | 0.026358 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2021-07-10 23:57 | 2021-07-11 07:07 | 1105 | 007:10 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1100-05 LLEVA LA CARGA DE 1109-01 Y 1109-04 SE CERRO INTERRUPTOR LOCAL POR PERSONAL DE CONSERVACION | S21071000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 430 | 2021-07-10 | 475150 | keep | 0 | Jul | 2021 | 0.32362 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
SAN JUAN | 2021-07-10 23:57 | 2021-07-11 07:07 | 351 | 007:10 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1100-05 LLEVA LA CARGA DE 1109-01 Y 1109-04 SE CERRO INTERRUPTOR LOCAL POR PERSONAL DE CONSERVACION | S21071000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 430 | 2021-07-10 | 150930 | keep | 0 | Jul | 2021 | 0.1028 | 0.00023906 | Sustained | FALSE | FALSE | Not_TMED_Event | 351
CANOVANAS | 2021-07-10 23:59 | 2021-07-11 12:14 | 7 | 012:15 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 10 EN PROVISIONAL AEREO SE REEMPLAZO TERMINACION | R21071000186 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 735 | 2021-07-10 | 5145 | keep | 0 | Jul | 2021 | 0.0035042 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2021-07-11 00:04 | 2021-07-11 14:06 | 60 | 014:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21071100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 842 | 2021-07-11 | 50520 | keep | 0 | Jul | 2021 | 0.034409 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-07-11 00:46 | 2021-07-11 00:47 | 450 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 450 | keep | 0 | Jul | 2021 | 0.00030649 | 0.00030649 | Momentary | FALSE | FALSE | Not_TMED_Event | 450
AGUADILLA | 2021-07-11 00:56 | 2021-07-11 00:57 | 1428 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21071100000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-11 | 1428 | keep | 0 | Jul | 2021 | 0.0009726 | 0.0009726 | Momentary | FALSE | FALSE | Not_TMED_Event | 1428
AGUADILLA | 2021-07-11 00:57 | 2021-07-11 19:23 | 150 | 018:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO PUENTES PRIMARIOS | M21071100002 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1106 | 2021-07-11 | 165900 | keep | 0 | Jul | 2021 | 0.11299 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-07-11 03:26 | 2021-07-11 03:27 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 108 | keep | 0 | Jul | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
MAYAGÃœEZ | 2021-07-11 03:48 | 2021-07-11 03:49 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21071100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 108 | keep | 0 | Jul | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
CANOVANAS | 2021-07-11 03:51 | 2021-07-11 03:52 | 1894 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | R21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 1894 | keep | 0 | Jul | 2021 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
AGUADILLA | 2021-07-11 04:00 | 2021-07-11 04:01 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 1192 | keep | 0 | Jul | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
BAYAMON | 2021-07-11 04:19 | 2021-07-11 04:20 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 2605 | keep | 0 | Jul | 2021 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
SAN JUAN | 2021-07-11 04:22 | 2021-07-11 04:23 | 3957 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 3957 | keep | 0 | Jul | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
BAYAMON | 2021-07-11 04:23 | 2021-07-11 04:24 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 3941 | keep | 0 | Jul | 2021 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
BAYAMON | 2021-07-11 04:24 | 2021-07-12 13:33 | 15 | 033:09 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21070900096 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1989 | 2021-07-11 | 29835 | keep | 0 | Jul | 2021 | 0.02032 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-07-11 04:37 | 2021-07-11 09:00 | 249 | 004:23 | P | DESGANCHE | 1 X 65 Y 1 X 30 EN CORTE DE LINEA | B21071100010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2021-07-11 | 65487 | keep | 0 | Jul | 2021 | 0.044603 | 0.00016959 | Sustained | FALSE | TRUE | Not_TMED_Event | 249
BAYAMON | 2021-07-11 04:38 | 2021-07-11 04:39 | 1514 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9100 | B21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 1514 | keep | 0 | Jul | 2021 | 0.0010312 | 0.0010312 | Momentary | FALSE | TRUE | Not_TMED_Event | 1514
BAYAMON | 2021-07-11 04:38 | 2021-07-11 04:39 | 1105 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9100 | B21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 1105 | keep | 0 | Jul | 2021 | 0.00075261 | 0.00075261 | Momentary | FALSE | TRUE | Not_TMED_Event | 1105
BAYAMON | 2021-07-11 04:38 | 2021-07-11 04:39 | 4176 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9100 | B21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 4176 | keep | 0 | Jul | 2021 | 0.0028443 | 0.0028443 | Momentary | FALSE | TRUE | Not_TMED_Event | 4176
BAYAMON | 2021-07-11 04:38 | 2021-07-11 04:39 | 252 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9100 | B21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 252 | keep | 0 | Jul | 2021 | 0.00017164 | 0.00017164 | Momentary | FALSE | TRUE | Not_TMED_Event | 252
BAYAMON | 2021-07-11 04:38 | 2021-07-11 04:39 | 2147 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9100 | B21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 2147 | keep | 0 | Jul | 2021 | 0.0014623 | 0.0014623 | Momentary | FALSE | TRUE | Not_TMED_Event | 2147
BAYAMON | 2021-07-11 04:38 | 2021-07-11 04:39 | 2858 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9100 | B21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 2858 | keep | 0 | Jul | 2021 | 0.0019466 | 0.0019466 | Momentary | FALSE | TRUE | Not_TMED_Event | 2858
BAYAMON | 2021-07-11 04:39 | 2021-07-11 16:21 | 40 | 011:42 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21070900119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 702 | 2021-07-11 | 28080 | keep | 0 | Jul | 2021 | 0.019125 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-11 04:39 | 2021-07-11 04:45 | 2234 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2021-07-11 | 13404 | keep | 0 | Jul | 2021 | 0.0091294 | 0.0015216 | Sustained | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2021-07-11 04:48 | 2021-07-11 04:51 | 2234 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21071100000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-07-11 | 6702 | keep | 0 | Jul | 2021 | 0.0045647 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-11 04:57 | 2021-07-11 04:58 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21071100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 108 | keep | 0 | Jul | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
ARECIBO | 2021-07-11 05:00 | 2021-07-11 08:10 | 100 | 003:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A21071100003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2021-07-11 | 19000 | keep | 0 | Jul | 2021 | 0.012941 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-07-11 05:05 | 2021-07-11 05:06 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21071100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 108 | keep | 0 | Jul | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
BAYAMON | 2021-07-11 05:07 | 2021-07-11 05:10 | 2234 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21071100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-07-11 | 6702 | keep | 0 | Jul | 2021 | 0.0045647 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
MAYAGÃœEZ | 2021-07-11 05:30 | 2021-07-11 05:31 | 107 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA | M21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 107 | keep | 0 | Jul | 2021 | 7.2877e-05 | 7.2877e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 107
PONCE | 2021-07-11 05:34 | 2021-07-11 05:35 | 449 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210711000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 449 | keep | 0 | Jul | 2021 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
YAUCO | 2021-07-11 05:38 | 2021-07-11 10:25 | 16 | 004:47 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | P21071100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 287 | 2021-07-11 | 4592 | keep | 0 | Jul | 2021 | 0.0031276 | 1.0898e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 16
PONCE | 2021-07-11 05:53 | 2021-07-11 08:25 | 30 | 002:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AUTO IMPACTO POSTE | P21071100002 | New_Event |  |  | Include | Wildlife | 152 | 2021-07-11 | 4560 | keep | 0 | Jul | 2021 | 0.0031058 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-07-11 05:55 | 2021-07-11 05:56 | 514 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7500 | S21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 514 | keep | 0 | Jul | 2021 | 0.00035008 | 0.00035008 | Momentary | FALSE | TRUE | Not_TMED_Event | 514
BAYAMON | 2021-07-11 05:55 | 2021-07-11 05:56 | 681 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7500 | S21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 681 | keep | 0 | Jul | 2021 | 0.00046383 | 0.00046383 | Momentary | FALSE | TRUE | Not_TMED_Event | 681
BAYAMON | 2021-07-11 05:55 | 2021-07-11 05:56 | 752 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7500 | S21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 752 | keep | 0 | Jul | 2021 | 0.00051218 | 0.00051218 | Momentary | FALSE | TRUE | Not_TMED_Event | 752
BAYAMON | 2021-07-11 05:55 | 2021-07-11 05:56 | 68 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7500 | S21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 68 | keep | 0 | Jul | 2021 | 4.6314e-05 | 4.6314e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 68
VEGA BAJA | 2021-07-11 06:00 | 2021-07-11 17:00 | 30 | 011:00 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA Y 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21071100008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 660 | 2021-07-11 | 19800 | keep | 0 | Jul | 2021 | 0.013486 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-07-11 06:07 | 2021-07-11 08:14 | 250 | 002:07 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTES DE LINEA LLUVIAS | R21071100007 | New_Event | Bad Weather | Include | Include | Weather | 127 | 2021-07-11 | 31750 | keep | 0 | Jul | 2021 | 0.021625 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
BAYAMON | 2021-07-11 06:20 | 2021-07-11 06:21 | 1588 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1711-3 | B21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 1588 | keep | 0 | Jul | 2021 | 0.0010816 | 0.0010816 | Momentary | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2021-07-11 06:20 | 2021-07-11 06:21 | 13 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR 1711-01 | B21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 13 | keep | 0 | Jul | 2021 | 8.8542e-06 | 8.8542e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2021-07-11 07:02 | 2021-07-11 07:03 | 3597 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 3597 | keep | 0 | Jul | 2021 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2021-07-11 07:15 | 2021-07-11 07:16 | 700 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF 90% POR 1716-03 | B21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 700 | keep | 0 | Jul | 2021 | 0.00047677 | 0.00047677 | Momentary | FALSE | FALSE | Not_TMED_Event | 700
BAYAMON | 2021-07-11 07:15 | 2021-07-11 07:16 | 1812 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA 90% DEL 1711-2 | B21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 1812 | keep | 0 | Jul | 2021 | 0.0012341 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
SAN JUAN | 2021-07-11 07:24 | 2021-07-12 16:29 | 55 | 033:05 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21071100010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1985 | 2021-07-11 | 109175 | keep | 0 | Jul | 2021 | 0.074359 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
MAYAGÃœEZ | 2021-07-11 07:32 | 2021-07-12 11:35 | 25 | 028:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASES | M21071100006 | New_Event |  |  | Include | Wildlife | 1683 | 2021-07-11 | 42075 | keep | 0 | Jul | 2021 | 0.028657 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-07-11 07:47 | 2021-07-11 07:48 | 6136 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 6136 | keep | 0 | Jul | 2021 | 0.0041792 | 0.0041792 | Momentary | FALSE | FALSE | Not_TMED_Event | 6136
BAYAMON | 2021-07-11 07:48 | 2021-07-11 11:10 | 150 | 003:22 | P | NO SE REPORTO CAUSA | 1 X 40 Y 1 X 50 EN CORTE LINEA | B21070900102 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 202 | 2021-07-11 | 30300 | keep | 0 | Jul | 2021 | 0.020637 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
GUAYAMA | 2021-07-11 07:54 | 2021-07-11 14:03 | 50 | 006:09 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | P21071100013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 369 | 2021-07-11 | 18450 | keep | 0 | Jul | 2021 | 0.012566 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-11 07:55 | 2021-07-12 13:49 | 300 | 029:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN SU-3 Y 1 X 140 EN CORTE DE LINEA CRUCE POR IGUANA | C21071100020 | New_Event |  |  | Include | Wildlife | 1794 | 2021-07-11 | 538200 | keep | 0 | Jul | 2021 | 0.36657 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
PONCE | 2021-07-11 07:55 | 2021-07-11 08:30 | 6 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REMPLAZO DE TOMA | P21071000142 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2021-07-11 | 210 | keep | 0 | Jul | 2021 | 0.00014303 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-07-11 08:00 | 2021-07-11 14:11 | 30 | 006:11 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO PUENTE PRIMARIO | P210711000XX | New_Event | Vegetation Contact | Include | Include | Vegetation | 371 | 2021-07-11 | 11130 | keep | 0 | Jul | 2021 | 0.0075806 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-07-11 08:12 | 2021-07-11 12:23 | 17 | 004:11 | P | NO SE REPORTO CAUSA | 2 X 15 EN CORTE DE LINEA | B21071100009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 251 | 2021-07-11 | 4267 | keep | 0 | Jul | 2021 | 0.0029062 | 1.1579e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 17
VEGA BAJA | 2021-07-11 08:12 | 2021-07-11 11:30 | 15 | 003:18 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REPARO LINEA Y SE REMPLAZO AISLADOR | B21071100010 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 198 | 2021-07-11 | 2970 | keep | 0 | Jul | 2021 | 0.0020229 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
HUMACAO | 2021-07-11 08:13 | 2021-07-12 10:50 | 60 | 026:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIAS | C21071100085 | New_Event | Bad Weather | Include | Include | Weather | 1597 | 2021-07-11 | 95820 | keep | 0 | Jul | 2021 | 0.065263 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-07-11 08:25 | 2021-07-12 14:30 | 65 | 030:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | M21071100019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1805 | 2021-07-11 | 117325 | keep | 0 | Jul | 2021 | 0.07991 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
PONCE | 2021-07-11 08:30 | 2021-07-11 10:45 | 60 | 002:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA AVERIADA | P210711000XX | New_Event | Cutout Failure | Include | Include | Equipment | 135 | 2021-07-11 | 8100 | keep | 0 | Jul | 2021 | 0.0055169 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-07-11 08:32 | 2021-07-11 10:18 | 40 | 001:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21071000043 | New_Event | Bad Weather | Include | Include | Weather | 106 | 2021-07-11 | 4240 | keep | 0 | Jul | 2021 | 0.0028878 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-07-11 08:36 | 2021-07-11 16:43 | 130 | 008:07 | P | NO SE REPORTO CAUSA | 1 X 80 Y 1 X 65 EN CORTES DE LINEAS | R21071100023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 487 | 2021-07-11 | 63310 | keep | 0 | Jul | 2021 | 0.04312 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
MAYAGÃœEZ | 2021-07-11 08:42 | 2021-07-12 12:50 | 50 | 028:08 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO BAMBUAS | M21071100020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1688 | 2021-07-11 | 84400 | keep | 0 | Jul | 2021 | 0.057484 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-07-11 08:55 | 2021-07-11 12:07 | 300 | 003:12 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | P21071100017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2021-07-11 | 57600 | keep | 0 | Jul | 2021 | 0.039231 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
BAYAMON | 2021-07-11 09:15 | 2021-07-11 14:03 | 100 | 004:48 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S21071100049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2021-07-11 | 28800 | keep | 0 | Jul | 2021 | 0.019616 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-07-11 09:15 | 2021-07-12 13:51 | 1 | 028:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN BANCO DE TRANSFORMADOR CRUCE CON RATA | R21071200015 | New_Event |  |  | Include | Wildlife | 1716 | 2021-07-11 | 1716 | keep | 0 | Jul | 2021 | 0.0011688 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-07-11 09:25 | 2021-07-11 09:26 | 4085 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 4085 | keep | 0 | Jul | 2021 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2021-07-11 09:25 | 2021-07-11 09:26 | 3699 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 3699 | keep | 0 | Jul | 2021 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
BAYAMON | 2021-07-11 09:26 | 2021-07-11 15:00 | 85 | 005:34 | P | DESGANCHE | 1 X 140 DE RISER @ SU-1 SE RETIRO RAMA | B21071000033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 334 | 2021-07-11 | 28390 | keep | 0 | Jul | 2021 | 0.019336 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
MAYAGÃœEZ | 2021-07-11 09:40 | 2021-07-11 09:41 | 1253 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 1253 | keep | 0 | Jul | 2021 | 0.00085341 | 0.00085341 | Momentary | FALSE | TRUE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2021-07-11 09:40 | 2021-07-11 09:41 | 1266 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 1266 | keep | 0 | Jul | 2021 | 0.00086227 | 0.00086227 | Momentary | FALSE | TRUE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2021-07-11 09:40 | 2021-07-11 09:41 | 411 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 411 | keep | 0 | Jul | 2021 | 0.00027993 | 0.00027993 | Momentary | FALSE | TRUE | Not_TMED_Event | 411
MAYAGÃœEZ | 2021-07-11 09:40 | 2021-07-11 09:41 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 1617 | keep | 0 | Jul | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | TRUE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-07-11 09:40 | 2021-07-11 09:41 | 1017 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 1017 | keep | 0 | Jul | 2021 | 0.00069267 | 0.00069267 | Momentary | FALSE | TRUE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-07-11 09:40 | 2021-07-11 09:41 | 828 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 828 | keep | 0 | Jul | 2021 | 0.00056395 | 0.00056395 | Momentary | FALSE | TRUE | Not_TMED_Event | 828
MAYAGÃœEZ | 2021-07-11 09:40 | 2021-07-11 09:41 | 863 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 863 | keep | 0 | Jul | 2021 | 0.00058779 | 0.00058779 | Momentary | FALSE | TRUE | Not_TMED_Event | 863
MAYAGÃœEZ | 2021-07-11 09:40 | 2021-07-11 09:41 | 309 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 309 | keep | 0 | Jul | 2021 | 0.00021046 | 0.00021046 | Momentary | FALSE | TRUE | Not_TMED_Event | 309
MAYAGÃœEZ | 2021-07-11 09:40 | 2021-07-11 09:41 | 176 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 176 | keep | 0 | Jul | 2021 | 0.00011987 | 0.00011987 | Momentary | FALSE | TRUE | Not_TMED_Event | 176
MAYAGÃœEZ | 2021-07-11 09:40 | 2021-07-11 09:41 | 108 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 108 | keep | 0 | Jul | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 108
MAYAGÃœEZ | 2021-07-11 09:40 | 2021-07-11 09:41 | 974 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 974 | keep | 0 | Jul | 2021 | 0.00066339 | 0.00066339 | Momentary | FALSE | TRUE | Not_TMED_Event | 974
HUMACAO | 2021-07-11 09:56 | 2021-07-11 11:10 | 7 | 001:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN CORTE DE LINEA LLUVIAS | C21071100000 | New_Event | Bad Weather | Include | Include | Weather | 74 | 2021-07-11 | 518 | keep | 0 | Jul | 2021 | 0.00035281 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
VEGA BAJA | 2021-07-11 09:56 | 2021-07-11 09:57 | 2610 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 2610 | keep | 0 | Jul | 2021 | 0.0017777 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
CAGUAS | 2021-07-11 10:10 | 2021-07-11 13:28 | 99 | 003:18 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21071100030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2021-07-11 | 19602 | keep | 0 | Jul | 2021 | 0.013351 | 6.7428e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 99
AGUADILLA | 2021-07-11 10:10 | 2021-07-11 11:05 | 1337 | 000:55 | T | TRANSFORMADOR AVERIADO | DISPARO DE INTERRUPTOR AL HACER PRUEBA A TRANSFORMADOR QUEMADO | M21071100000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 55 | 2021-07-11 | 73535 | keep | 0 | Jul | 2021 | 0.050084 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
MAYAGÃœEZ | 2021-07-11 10:12 | 2021-07-12 16:30 | 50 | 030:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M21071100030 | New_Event | Cutout Failure | Include | Include | Equipment | 1818 | 2021-07-11 | 90900 | keep | 0 | Jul | 2021 | 0.061912 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-11 10:17 | 2021-07-12 10:09 | 9 | 023:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | R21071100027 | New_Event |  |  | Include | Wildlife | 1432 | 2021-07-11 | 12888 | keep | 0 | Jul | 2021 | 0.008778 | 6.1299e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 9
UTUADO | 2021-07-11 10:30 | 2021-07-11 15:40 | 6 | 005:10 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO RAMA | A21071100011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 310 | 2021-07-11 | 1860 | keep | 0 | Jul | 2021 | 0.0012668 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-07-11 10:31 | 2021-07-12 19:12 | 1 | 032:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARARON 3 PUENTES PRIMARIOS DE LINEA A CAJA EN CORTE DE LINEA | B21071100034 | New_Event | Wire Down | Include | Include | Equipment | 1961 | 2021-07-11 | 1961 | keep | 0 | Jul | 2021 | 0.0013356 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-07-11 10:31 | 2021-07-12 19:12 | 25 | 032:41 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21071100034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1961 | 2021-07-11 | 49025 | keep | 0 | Jul | 2021 | 0.033391 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-07-11 10:46 | 2021-07-11 10:48 | 870 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL CON RECIERRE EN OFF Y QUEDO EN SERVICIO | S21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-11 | 1740 | keep | 0 | Jul | 2021 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
PONCE | 2021-07-11 10:49 | 2021-07-11 11:26 | 562 | 000:37 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17900 | P21071100039 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 37 | 2021-07-11 | 20794 | keep | 0 | Jul | 2021 | 0.014163 | 0.00038278 | Sustained | FALSE | TRUE | Not_TMED_Event | 562
PONCE | 2021-07-11 10:49 | 2021-07-11 11:26 | 688 | 000:37 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17900 | P21071100039 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 37 | 2021-07-11 | 25456 | keep | 0 | Jul | 2021 | 0.017338 | 0.00046859 | Sustained | FALSE | TRUE | Not_TMED_Event | 688
PONCE | 2021-07-11 10:49 | 2021-07-11 11:26 | 658 | 000:37 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17900 | P21071100039 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 37 | 2021-07-11 | 24346 | keep | 0 | Jul | 2021 | 0.016582 | 0.00044816 | Sustained | FALSE | TRUE | Not_TMED_Event | 658
PONCE | 2021-07-11 10:49 | 2021-07-11 11:26 | 4009 | 000:37 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17900 | P21071100039 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 37 | 2021-07-11 | 148333 | keep | 0 | Jul | 2021 | 0.10103 | 0.0027305 | Sustained | FALSE | TRUE | Not_TMED_Event | 4009
BAYAMON | 2021-07-11 11:12 | 2021-07-11 17:49 | 1 | 006:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 40 EN BANCO DE TRANSFORMADORES SE REMPLAZO 2 CAJAS PRIMARIAS Y SE REPARO BAJANTE PRIMARIO LINEA A CAJA | S21071100057 | New_Event | Cutout Failure | Include | Include | Equipment | 397 | 2021-07-11 | 397 | keep | 0 | Jul | 2021 | 0.00027039 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-07-11 11:12 | 2021-07-11 12:40 | 1 | 001:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN BANCO DE TRANSFORMADOR MAL TIEMPO | C21071100000 | New_Event | Bad Weather | Include | Include | Weather | 88 | 2021-07-11 | 88 | keep | 0 | Jul | 2021 | 5.9936e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-07-11 11:14 | 2021-07-11 12:40 | 25 | 001:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO Y SE REALIZO DESGANCHE | S21070900087 | New_Event | Wire Down | Include | Include | Equipment | 86 | 2021-07-11 | 2150 | keep | 0 | Jul | 2021 | 0.0014644 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-07-11 11:24 | 2021-07-11 11:25 | 842 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21071100000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-11 | 842 | keep | 0 | Jul | 2021 | 0.00057348 | 0.00057348 | Momentary | FALSE | FALSE | Not_TMED_Event | 842
BAYAMON | 2021-07-11 11:25 | 2021-07-11 12:57 | 175 | 001:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO | S21071100000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 92 | 2021-07-11 | 16100 | keep | 0 | Jul | 2021 | 0.010966 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
ARECIBO | 2021-07-11 11:25 | 2021-07-12 11:05 | 12 | 023:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | A21071100014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1420 | 2021-07-11 | 17040 | keep | 0 | Jul | 2021 | 0.011606 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-07-11 11:33 | 2021-07-11 14:30 | 2 | 002:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21071100065 | New_Event | Bad Weather | Include | Include | Weather | 177 | 2021-07-11 | 354 | keep | 0 | Jul | 2021 | 0.00024111 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
YAUCO | 2021-07-11 11:39 | 2021-07-11 19:15 | 591 | 007:36 | S | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE SUBESTACION POR MAL TIEMPO. SE REEMPLAZO UN FUSIBLE DE ALTA | P21071100066 | New_Event | Bad Weather | Include | Include | Weather | 456 | 2021-07-11 | 269496 | keep | 0 | Jul | 2021 | 0.18355 | 0.00040253 | Sustained | FALSE | FALSE | Not_TMED_Event | 591
BAYAMON | 2021-07-11 11:46 | 2021-07-11 11:48 | 2234 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO | B21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-11 | 4468 | keep | 0 | Jul | 2021 | 0.0030431 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2021-07-11 11:49 | 2021-07-11 16:31 | 80 | 004:42 | P | CABLE SOTERRADO AVERIADO | 1 X 80 EN RISER @ T-1. AVERIA NUEVA DE T-7 2 T-8 Y AVERIA VIEJA DE T-8 @ RISER. T-8 FUERA DE SERVICIO SE CREO EVENTO B21071100084 | B21071100038 | New_Event | UG Cable Fault | Include | Include | Equipment | 282 | 2021-07-11 | 22560 | keep | 0 | Jul | 2021 | 0.015366 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-07-11 11:57 | 2021-07-11 16:29 | 35 | 004:32 | P | DESGANCHE | 1 X 50 EN RISER Y 2 X 15 EN MONTURA ANTENA SE REALIZO DESGANCHE | B21071100039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 272 | 2021-07-11 | 9520 | keep | 0 | Jul | 2021 | 0.006484 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2021-07-11 11:57 | 2021-07-11 14:32 | 80 | 002:35 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA POR DESGANCHE | P21071100048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2021-07-11 | 12400 | keep | 0 | Jul | 2021 | 0.0084456 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-07-11 12:03 | 2021-07-11 15:12 | 300 | 003:09 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 100 EN CORTE DE LINEA REEMPLAZARON AISLADOR ROTO | C21071100039 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 189 | 2021-07-11 | 56700 | keep | 0 | Jul | 2021 | 0.038618 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-07-11 12:08 | 2021-07-11 12:09 | 1266 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR POR DESCARGAS ELECTRICAS | M | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-11 | 1266 | keep | 0 | Jul | 2021 | 0.00086227 | 0.00086227 | Momentary | FALSE | FALSE | Not_TMED_Event | 1266
SAN JUAN | 2021-07-11 12:21 | 2021-07-11 13:46 | 55 | 001:25 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 75KVA POR IGUAL CAPACIDAD | S21071000069 | New_Event | Service Transformer Failure | Include | Include | Equipment | 85 | 2021-07-11 | 4675 | keep | 0 | Jul | 2021 | 0.0031841 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
HUMACAO | 2021-07-11 12:25 | 2021-07-11 16:30 | 80 | 004:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO BAJANTE ABIERTO HACIA TRANSFORMADOR | C21071100041 | New_Event | Wire Down | Include | Include | Equipment | 245 | 2021-07-11 | 19600 | keep | 0 | Jul | 2021 | 0.013349 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-07-11 12:40 | 2021-07-11 12:41 | 5630 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | C21071100000 | Additional_clients | Bad Weather | Include | Include | Weather | 1 | 2021-07-11 | 5630 | keep | 0 | Jul | 2021 | 0.0038346 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-07-11 12:41 | 2021-07-11 14:12 | 1 | 001:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN BANCO DE TRANSFORMADOR MAL TIEMPO | C21071100000 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 91 | 2021-07-11 | 91 | keep | 0 | Jul | 2021 | 6.198e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-07-11 12:57 | 2021-07-11 13:17 | 842 | 000:20 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR CODUCTOR PUENTE ABIERTO | S21071100000 | Additional_clients | Wire Down | Include | Include | Equipment | 20 | 2021-07-11 | 16840 | keep | 0 | Jul | 2021 | 0.01147 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-07-11 13:03 | 2021-07-11 17:20 | 30 | 004:17 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A21071100016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 257 | 2021-07-11 | 7710 | keep | 0 | Jul | 2021 | 0.0052512 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-07-11 13:04 | 2021-07-11 17:33 | 1337 | 004:29 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO NEUTRAL PRIMARIO PARTIDO SE CORRIGIO CONDICION DE LINEAS CRUZADAS Y SE CERRO INTERRUPTOR | M21071100064 | New_Event | Wire Down | Include | Include | Equipment | 269 | 2021-07-11 | 359653 | keep | 0 | Jul | 2021 | 0.24496 | 0.00091062 | Sustained | FALSE | TRUE | Not_TMED_Event | 1337
BARRANQUITAS | 2021-07-11 13:10 | 2021-07-11 15:20 | 60 | 002:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE HACIA CAJA PRIMARIA | C21071100045 | New_Event | Wire Down | Include | Include | Equipment | 130 | 2021-07-11 | 7800 | keep | 0 | Jul | 2021 | 0.0053125 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-07-11 13:11 | 2021-07-11 15:29 | 12 | 002:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO DE LINEA A CAJA EN TRANSFORMADOR | S21071100062 | New_Event | Wire Down | Include | Include | Equipment | 138 | 2021-07-11 | 1656 | keep | 0 | Jul | 2021 | 0.0011279 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
BAYAMON | 2021-07-11 13:14 | 2021-07-11 17:45 | 50 | 004:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA AVERIADA | B21071100049 | New_Event | Cutout Failure | Include | Include | Equipment | 271 | 2021-07-11 | 13550 | keep | 0 | Jul | 2021 | 0.0092288 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-11 13:17 | 2021-07-11 13:59 | 175 | 000:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO | S21071100000 | Partial_restoration | Wire Down | Include | Include | Equipment | 42 | 2021-07-11 | 7350 | keep | 0 | Jul | 2021 | 0.0050061 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-11 13:22 | 2021-07-12 17:05 | 80 | 027:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | M21071100080 | New_Event | Bad Weather | Include | Include | Weather | 1663 | 2021-07-11 | 133040 | keep | 0 | Jul | 2021 | 0.090613 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-07-11 13:23 | 2021-07-12 21:00 | 2 | 031:37 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 15 KVA X UNO DE 25 KVA | A21071100018 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1897 | 2021-07-11 | 3794 | keep | 0 | Jul | 2021 | 0.0025841 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2021-07-11 13:26 | 2021-07-11 17:31 | 150 | 004:05 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P21071100057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2021-07-11 | 36750 | keep | 0 | Jul | 2021 | 0.02503 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-07-11 13:44 | 2021-07-11 15:40 | 35 | 001:56 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21071100068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2021-07-11 | 4060 | keep | 0 | Jul | 2021 | 0.0027652 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
SAN JUAN | 2021-07-11 13:50 | 2021-07-11 18:35 | 40 | 004:45 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | S21071100070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 285 | 2021-07-11 | 11400 | keep | 0 | Jul | 2021 | 0.0077645 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-07-11 13:52 | 2021-07-11 16:15 | 1843 | 002:23 | T | DESGANCHE | SE RETIRO BAMBUAS SOBRE LINEAS | C21071100074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2021-07-11 | 263549 | keep | 0 | Jul | 2021 | 0.1795 | 0.0012553 | Sustained | FALSE | TRUE | Not_TMED_Event | 1843
CAGUAS | 2021-07-11 13:57 | 2021-07-11 15:45 | 3 | 001:48 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C21071100052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 108 | 2021-07-11 | 324 | keep | 0 | Jul | 2021 | 0.00022067 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-07-11 13:59 | 2021-07-11 14:07 | 842 | 000:08 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA REPARAR PUENTE PRIMARIO A LA SALIDA DE ALIMENTADOR | S21071100000 | Additional_clients | Wire Down | Include | Include | Equipment | 8 | 2021-07-11 | 6736 | keep | 0 | Jul | 2021 | 0.0045879 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-07-11 14:05 | 2021-07-11 16:11 | 80 | 002:06 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21071100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2021-07-11 | 10080 | keep | 0 | Jul | 2021 | 0.0068654 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
AGUADILLA | 2021-07-11 14:21 | 2021-07-11 19:23 | 50 | 005:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21071100092 | New_Event | Bad Weather | Include | Include | Weather | 302 | 2021-07-11 | 15100 | keep | 0 | Jul | 2021 | 0.010285 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-11 14:32 | 2021-07-11 18:30 | 15 | 003:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA AVE CRUZO LINEAS | M21071100094 | New_Event |  |  | Include | Wildlife | 238 | 2021-07-11 | 3570 | keep | 0 | Jul | 2021 | 0.0024315 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
SAN JUAN | 2021-07-11 14:40 | 2021-07-11 15:40 | 12 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BARRA EN PEDESTAL AVERIADA | R21071100020 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2021-07-11 | 720 | keep | 0 | Jul | 2021 | 0.00049039 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-07-11 14:46 | 2021-07-11 17:14 | 10 | 002:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE TRANSFORMADOR | S21071100075 | New_Event | Wire Down | Include | Include | Equipment | 148 | 2021-07-11 | 1480 | keep | 0 | Jul | 2021 | 0.001008 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
SAN JUAN | 2021-07-11 14:55 | 2021-07-11 17:10 | 16 | 002:15 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO PM PARA REEMPLAZAR BARRA EN PEDESTAL WR - 5883170 | R21071100000 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 135 | 2021-07-11 | 2160 | keep | 0 | Jul | 2021 | 0.0014712 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
HUMACAO | 2021-07-11 15:12 | 2021-07-11 15:17 | 4161 | 000:05 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO RR/OFF | C21071100000 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 5 | 2021-07-11 | 20805 | keep | 0 | Jul | 2021 | 0.01417 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-07-11 15:17 | 2021-07-11 15:50 | 300 | 000:33 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 100 EN CORTE DE LINEA REEMPLAZARON AISLADOR ROTO | C21071100039 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 33 | 2021-07-11 | 9900 | keep | 0 | Jul | 2021 | 0.0067428 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-11 15:46 | 2021-07-11 16:39 | 100 | 000:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21071100116 | New_Event | Bad Weather | Include | Include | Weather | 53 | 2021-07-11 | 5300 | keep | 0 | Jul | 2021 | 0.0036098 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-11 15:54 | 2021-07-11 15:55 | 3798 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO Y SE CERRO POR SCADA | B21071100000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-07-11 | 3798 | keep | 0 | Jul | 2021 | 0.0025868 | 0.0025868 | Momentary | FALSE | FALSE | Not_TMED_Event | 3798
BAYAMON | 2021-07-11 15:55 | 2021-07-12 13:18 | 35 | 021:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN CORTE DE LINEA SE REMPLAZARON 2 CAJAS PRIMARIAS | B21071100080 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1283 | 2021-07-11 | 44905 | keep | 0 | Jul | 2021 | 0.030585 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
SAN JUAN | 2021-07-11 15:58 | 2021-07-11 18:35 | 25 | 002:37 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | S21071100084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2021-07-11 | 3925 | keep | 0 | Jul | 2021 | 0.0026733 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
VEGA BAJA | 2021-07-11 16:09 | 2021-07-11 19:55 | 30 | 003:46 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21071100077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2021-07-11 | 6780 | keep | 0 | Jul | 2021 | 0.0046178 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-07-11 16:16 | 2021-07-12 15:29 | 20 | 023:13 | P | HERRAJE ROTO O PODRIDO | 2 X 50 EN CORTE DE LINEA SE REMPLAZO CRUCETA PARTIDA | B21071100079 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 1393 | 2021-07-11 | 27860 | keep | 0 | Jul | 2021 | 0.018975 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
UTUADO | 2021-07-11 16:17 | 2021-07-12 10:30 | 30 | 018:13 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | A21071100023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1093 | 2021-07-11 | 32790 | keep | 0 | Jul | 2021 | 0.022333 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-07-11 16:41 | 2021-07-12 17:49 | 30 | 025:08 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | A21071100025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1508 | 2021-07-11 | 45240 | keep | 0 | Jul | 2021 | 0.030813 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-07-11 16:46 | 2021-07-11 23:56 | 25 | 007:10 | P | ESTRUCTURA AVERIADA | 1 X 30 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO | B21071100082 | New_Event | Defective Pole | Include | Include | Equipment | 430 | 2021-07-11 | 10750 | keep | 0 | Jul | 2021 | 0.0073218 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-07-11 16:47 | 2021-07-12 11:15 | 10 | 018:28 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S21071100088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1108 | 2021-07-11 | 11080 | keep | 0 | Jul | 2021 | 0.0075465 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2021-07-11 17:00 | 2021-07-12 19:19 | 15 | 026:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | P21071100069 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1579 | 2021-07-11 | 23685 | keep | 0 | Jul | 2021 | 0.016132 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-07-11 17:04 | 2021-07-11 17:05 | 1444 | 000:01 | T | NO SE REPORTO CAUSA | CARGA POR 6014-03 | M21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 1444 | keep | 0 | Jul | 2021 | 0.0009835 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2021-07-11 17:04 | 2021-07-11 17:05 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 6014-01 | M21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 871 | keep | 0 | Jul | 2021 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2021-07-11 17:09 | 2021-07-11 17:10 | 1444 | 000:01 | T | NO SE REPORTO CAUSA | CARGA POR 6014-03 | M21071100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 1444 | keep | 0 | Jul | 2021 | 0.0009835 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2021-07-11 17:09 | 2021-07-11 17:10 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 6014-01 | M21071100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 871 | keep | 0 | Jul | 2021 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2021-07-11 17:12 | 2021-07-11 20:10 | 1444 | 002:58 | S | PROTECCION DEFECTUOSA | INTERRUPTOR 6014-03 DISPARO Y SE LLEVO EL 0050 EZEQUIEL MEDINA VERIFICO EL TRANSFORMADOR Y EL INTERRUPTOR Y ESTAN EN BUENAS CONDICIONES SE ENERGIZO TRANSFORMADOR Y SE CERRO EL INTERRUPTOR 6014-02 | M21071100000 | New_Event | Protection Miscoordination | Include | Include | Other | 178 | 2021-07-11 | 257032 | keep | 0 | Jul | 2021 | 0.17506 | 0.0009835 | Sustained | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2021-07-11 17:12 | 2021-07-11 20:10 | 3630 | 002:58 | S | PROTECCION DEFECTUOSA | INTERRUPTOR 6014-03 DISPARO Y SE LLEVO EL 0050 EZEQUIEL MEDINA VERIFICO EL TRANSFORMADOR Y EL INTERRUPTOR Y ESTAN EN BUENAS CONDICIONES SE ENERGIZO TRANSFORMADOR Y SE CERRO EL INTERRUPTOR 6014-02 | M21071100000 | New_Event | Protection Miscoordination | Include | Include | Other | 178 | 2021-07-11 | 646140 | keep | 0 | Jul | 2021 | 0.44008 | 0.0024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2021-07-11 17:12 | 2021-07-11 20:10 | 871 | 002:58 | S | PROTECCION DEFECTUOSA | INTERRUPTOR 6014-03 DISPARO Y SE LLEVO EL 0050 EZEQUIEL MEDINA VERIFICO EL TRANSFORMADOR Y EL INTERRUPTOR Y ESTAN EN BUENAS CONDICIONES SE ENERGIZO TRANSFORMADOR Y SE CERRO EL INTERRUPTOR 6014-02 | M21071100000 | New_Event | Protection Miscoordination | Include | Include | Other | 178 | 2021-07-11 | 155038 | keep | 0 | Jul | 2021 | 0.1056 | 0.00059323 | Sustained | FALSE | FALSE | Not_TMED_Event | 871
BAYAMON | 2021-07-11 17:14 | 2021-07-12 14:14 | 12 | 021:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO NEUTRAL SECUNDARIO | B21071100088 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1260 | 2021-07-11 | 15120 | keep | 0 | Jul | 2021 | 0.010298 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-07-11 17:35 | 2021-07-11 17:38 | 1251 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DISPARO INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1424-08 | S21071100000 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2021-07-11 | 3753 | keep | 0 | Jul | 2021 | 0.0025562 | 0.00085205 | Momentary | FALSE | FALSE | Not_TMED_Event | 1251
SAN JUAN | 2021-07-11 17:35 | 2021-07-11 17:38 | 278 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DISPARO INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1424-08 | S21071100000 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2021-07-11 | 834 | keep | 0 | Jul | 2021 | 0.00056803 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2021-07-11 17:35 | 2021-07-11 17:38 | 9 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DISPARO INTERRUPTOR SE CERRO POR SCADA LLEVA CARGA DEL 1348-06 1348-07 | S21071100000 | New_Event | Wire Down | Include | Include | Equipment | 3 | 2021-07-11 | 27 | keep | 0 | Jul | 2021 | 1.839e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2021-07-11 17:38 | 2021-07-12 09:08 | 85 | 015:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 200 EN CORTE DE LINEA Y 2 X 80 EN CORTE DE LINEA PRINCIPAL Y RAMAL SE CERRO PUENTE EN LA CAJA | S21071100104 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 930 | 2021-07-11 | 79050 | keep | 0 | Jul | 2021 | 0.053841 | 5.7893e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 85
UTUADO | 2021-07-11 17:39 | 2021-07-12 11:30 | 6 | 017:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21071100026 | New_Event | Bad Weather | Include | Include | Weather | 1071 | 2021-07-11 | 6426 | keep | 0 | Jul | 2021 | 0.0043767 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-07-11 18:34 | 2021-07-11 18:35 | 1342 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 1342 | keep | 0 | Jul | 2021 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
MAYAGÃœEZ | 2021-07-11 18:49 | 2021-07-12 11:45 | 75 | 016:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DE AISLADOR | M21071100213 | New_Event | Wire Down | Include | Include | Equipment | 1016 | 2021-07-11 | 76200 | keep | 0 | Jul | 2021 | 0.051899 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-07-11 19:32 | 2021-07-11 19:33 | 5252 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 5252 | keep | 0 | Jul | 2021 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
SAN JUAN | 2021-07-11 19:36 | 2021-07-11 19:37 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LA CARGA ESTA POR EL 1206-03 | S21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 10211 | keep | 0 | Jul | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-07-11 19:36 | 2021-07-11 19:37 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA CARGA DEL 1204-05 | S21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 4133 | keep | 0 | Jul | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
MAYAGÃœEZ | 2021-07-11 19:52 | 2021-07-12 21:10 | 65 | 025:18 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21071100247 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1518 | 2021-07-11 | 98670 | keep | 0 | Jul | 2021 | 0.067204 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
SAN JUAN | 2021-07-11 20:06 | 2021-07-12 09:43 | 35 | 013:37 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21071100105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 817 | 2021-07-11 | 28595 | keep | 0 | Jul | 2021 | 0.019476 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-07-11 20:18 | 2021-07-12 12:50 | 75 | 016:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE DESENREDARON LINEA LINEAS | M21071100261 | New_Event | Wire Down | Include | Include | Equipment | 992 | 2021-07-11 | 74400 | keep | 0 | Jul | 2021 | 0.050674 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BARRANQUITAS | 2021-07-11 20:28 | 2021-07-12 12:55 | 40 | 016:27 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21071200086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 987 | 2021-07-11 | 39480 | keep | 0 | Jul | 2021 | 0.02689 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-07-11 20:55 | 2021-07-11 21:22 | 1444 | 000:27 | S | PROTECCION DEFECTUOSA | SE SECCIONLIZO ALIMENTADOR 6014-03 POR RAFAEL FONT Y CUANDO SE CERRO INTERRUPTRO SE FUE A LOCKOUT LA SUBESTACION SE REMONTO EL LOCKOUT Y SE ENERGIZO LA SUBESTACION NUEVAMENTE AUTORIZADO POR EZEQUIEL MEDINA | M21071100000 | Partial_restoration | Protection Miscoordination | Include | Include | Other | 27 | 2021-07-11 | 38988 | keep | 0 | Jul | 2021 | 0.026555 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-11 20:55 | 2021-07-11 21:22 | 3630 | 000:27 | S | PROTECCION DEFECTUOSA | SE SECCIONLIZO ALIMENTADOR 6014-03 POR RAFAEL FONT Y CUANDO SE CERRO INTERRUPTRO SE FUE A LOCKOUT LA SUBESTACION SE REMONTO EL LOCKOUT Y SE ENERGIZO LA SUBESTACION NUEVAMENTE AUTORIZADO POR EZEQUIEL MEDINA | M21071100000 | Partial_restoration | Protection Miscoordination | Include | Include | Other | 27 | 2021-07-11 | 98010 | keep | 0 | Jul | 2021 | 0.066754 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-11 20:55 | 2021-07-11 21:22 | 871 | 000:27 | S | PROTECCION DEFECTUOSA | SE SECCIONLIZO ALIMENTADOR 6014-03 POR RAFAEL FONT Y CUANDO SE CERRO INTERRUPTRO SE FUE A LOCKOUT LA SUBESTACION SE REMONTO EL LOCKOUT Y SE ENERGIZO LA SUBESTACION NUEVAMENTE AUTORIZADO POR EZEQUIEL MEDINA | M21071100000 | Partial_restoration | Protection Miscoordination | Include | Include | Other | 27 | 2021-07-11 | 23517 | keep | 0 | Jul | 2021 | 0.016017 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-07-11 21:05 | 2021-07-11 21:06 | 2523 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 2523 | keep | 0 | Jul | 2021 | 0.0017184 | 0.0017184 | Momentary | FALSE | TRUE | Not_TMED_Event | 2523
ARECIBO | 2021-07-11 21:05 | 2021-07-11 21:06 | 1607 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 1607 | keep | 0 | Jul | 2021 | 0.0010945 | 0.0010945 | Momentary | FALSE | TRUE | Not_TMED_Event | 1607
ARECIBO | 2021-07-11 21:05 | 2021-07-11 21:06 | 1722 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 1722 | keep | 0 | Jul | 2021 | 0.0011728 | 0.0011728 | Momentary | FALSE | TRUE | Not_TMED_Event | 1722
ARECIBO | 2021-07-11 21:05 | 2021-07-11 21:06 | 619 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 619 | keep | 0 | Jul | 2021 | 0.0004216 | 0.0004216 | Momentary | FALSE | TRUE | Not_TMED_Event | 619
ARECIBO | 2021-07-11 21:05 | 2021-07-11 21:06 | 243 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 243 | keep | 0 | Jul | 2021 | 0.00016551 | 0.00016551 | Momentary | FALSE | TRUE | Not_TMED_Event | 243
ARECIBO | 2021-07-11 21:05 | 2021-07-11 21:06 | 2703 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 2703 | keep | 0 | Jul | 2021 | 0.001841 | 0.001841 | Momentary | FALSE | TRUE | Not_TMED_Event | 2703
ARECIBO | 2021-07-11 21:05 | 2021-07-11 21:06 | 3157 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 3157 | keep | 0 | Jul | 2021 | 0.0021502 | 0.0021502 | Momentary | FALSE | TRUE | Not_TMED_Event | 3157
ARECIBO | 2021-07-11 21:05 | 2021-07-11 21:06 | 35 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 35 | keep | 0 | Jul | 2021 | 2.3838e-05 | 2.3838e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-07-11 21:05 | 2021-07-11 21:06 | 2916 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A21071100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-11 | 2916 | keep | 0 | Jul | 2021 | 0.0019861 | 0.0019861 | Momentary | FALSE | TRUE | Not_TMED_Event | 2916
SAN JUAN | 2021-07-11 21:06 | 2021-07-12 11:59 | 20 | 014:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN CAJA PRIMARIA SE REEMPLAZO | R21071100044 | New_Event | Cutout Failure | Include | Include | Equipment | 893 | 2021-07-11 | 17860 | keep | 0 | Jul | 2021 | 0.012164 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-07-11 21:57 | 2021-07-11 21:58 | 1976 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 1976 | keep | 0 | Jul | 2021 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
HUMACAO | 2021-07-11 22:21 | 2021-07-12 02:44 | 5630 | 004:23 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO SE REMPLAZO AISLADOR Y SE CERRO INTERRUPTOR | C21071100105 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 263 | 2021-07-11 | 1480690 | keep | 0 | Jul | 2021 | 1.0085 | 0.0038346 | Sustained | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2021-07-11 22:21 | 2021-07-11 22:23 | 2126 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-11 | 4252 | keep | 0 | Jul | 2021 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
MAYAGÃœEZ | 2021-07-11 22:24 | 2021-07-11 22:25 | 6285 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21071100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-11 | 6285 | keep | 0 | Jul | 2021 | 0.0042807 | 0.0042807 | Momentary | FALSE | FALSE | Not_TMED_Event | 6285
VEGA BAJA | 2021-07-11 22:26 | 2021-07-12 13:00 | 15 | 014:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE LEVANTO CONDUCTOR COMPAÃ‘IA LORD | B21071100100 | New_Event | Wire Down | Include | Include | Equipment | 874 | 2021-07-11 | 13110 | keep | 0 | Jul | 2021 | 0.0089292 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
ARECIBO | 2021-07-11 23:06 | 2021-07-12 09:45 | 10 | 010:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21071100046 | New_Event | Bad Weather | Include | Include | Weather | 639 | 2021-07-11 | 6390 | keep | 0 | Jul | 2021 | 0.0043522 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-07-11 23:48 | 2021-07-12 09:30 | 30 | 009:42 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | A21071100048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 582 | 2021-07-11 | 17460 | keep | 0 | Jul | 2021 | 0.011892 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-07-12 00:39 | 2021-07-12 00:40 | 2708 | 000:01 | T | TRANSFORMADOR AVERIADO | RECIERRE | R21071200000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1 | 2021-07-12 | 2708 | keep | 0 | Jul | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2021-07-12 00:40 | 2021-07-12 11:17 | 30 | 010:37 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DERRAMANDO DE 50KVA X 50KVA | R21071200016 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 637 | 2021-07-12 | 19110 | keep | 0 | Jul | 2021 | 0.013016 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2021-07-12 00:52 | 2021-07-12 13:50 | 20 | 012:58 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R21071200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 778 | 2021-07-12 | 15560 | keep | 0 | Jul | 2021 | 0.010598 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-07-12 01:33 | 2021-07-12 01:34 | 2302 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21071200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-12 | 2302 | keep | 0 | Jul | 2021 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
UTUADO | 2021-07-12 01:36 | 2021-07-12 14:27 | 40 | 012:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | A21071200002 | New_Event | Cutout Failure | Include | Include | Equipment | 771 | 2021-07-12 | 30840 | keep | 0 | Jul | 2021 | 0.021005 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-07-12 01:38 | 2021-07-12 21:15 | 1 | 019:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR ROTO Y CERRO CORTE DE LINEA | C21071200008 | New_Event | Wire Down | Include | Include | Equipment | 1177 | 2021-07-12 | 1177 | keep | 0 | Jul | 2021 | 0.00080165 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
UTUADO | 2021-07-12 01:46 | 2021-07-12 12:08 | 25 | 010:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21071200003 | New_Event | Bad Weather | Include | Include | Weather | 622 | 2021-07-12 | 15550 | keep | 0 | Jul | 2021 | 0.010591 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-07-12 01:49 | 2021-07-12 15:35 | 50 | 013:46 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA Y 1 X 65 EN CORTE DE LINEA | B21071200003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 826 | 2021-07-12 | 41300 | keep | 0 | Jul | 2021 | 0.028129 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-07-12 02:44 | 2021-07-12 19:40 | 12 | 016:56 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR 50KVA X 50KVA | C21071200043 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1016 | 2021-07-12 | 12192 | keep | 0 | Jul | 2021 | 0.0083039 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-07-12 03:57 | 2021-07-12 18:45 | 1444 | 014:48 | S | PROTECCION DEFECTUOSA | SE CORRIGIERON PARAMETROS DE PROTECCION EN MAIN BREAKER | M21071200009 | New_Event | Protection Miscoordination | Include | Include | Other | 888 | 2021-07-12 | 1282272 | keep | 0 | Jul | 2021 | 0.87335 | 0.0009835 | Sustained | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2021-07-12 03:57 | 2021-07-12 18:45 | 3630 | 014:48 | S | PROTECCION DEFECTUOSA | SE CORRIGIERON PARAMETROS DE PROTECCION EN MAIN BREAKER | M21071200009 | New_Event | Protection Miscoordination | Include | Include | Other | 888 | 2021-07-12 | 3223440 | keep | 0 | Jul | 2021 | 2.1955 | 0.0024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2021-07-12 03:57 | 2021-07-12 17:34 | 871 | 013:37 | S | PROTECCION DEFECTUOSA | SE CORRIGIERON PARAMETROS DE PROTECCION EN MAIN BREAKER SE SECCIONALIZO ALIMENTADOR Y SE PASO LA CARGA AL 6012-05 | M21071200009 | New_Event | Protection Miscoordination | Include | Include | Other | 817 | 2021-07-12 | 711607 | keep | 0 | Jul | 2021 | 0.48467 | 0.00059323 | Sustained | FALSE | FALSE | Not_TMED_Event | 871
SAN JUAN | 2021-07-12 04:06 | 2021-07-12 04:07 | 10211 | 000:01 | T | DESGANCHE | DISPARO CARGA POR EL 1206-03 | S21071200291 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-12 | 10211 | keep | 0 | Jul | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-07-12 04:06 | 2021-07-12 04:07 | 4133 | 000:01 | T | DESGANCHE | RECIERRE LLEVA CARGA DEL 1204-05 | S21071200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-12 | 4133 | keep | 0 | Jul | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-07-12 04:07 | 2021-07-12 09:51 | 40 | 005:44 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA Y SE REPORTA AVERIA POR DESGANCHE | S21071100050 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 344 | 2021-07-12 | 13760 | keep | 0 | Jul | 2021 | 0.0093719 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-07-12 05:17 | 2021-07-12 10:48 | 528 | 005:31 | S | PROTECCION DEFECTUOSA | LINEA PRIMARIA PARTIDA EN ALIMENTADOR 6012-05 INTERRUPTOR NO VIO AVERIA SE LLEVO LA ALTA DEL TRANSFORMADOR SE DEJO INTERRUPTOR ABIERTO Y SE ENERGIZO TRANSFORMADOR | M21071200019 | New_Event | Protection Miscoordination | Include | Include | Other | 331 | 2021-07-12 | 174768 | keep | 0 | Jul | 2021 | 0.11903 | 0.00035962 | Sustained | FALSE | TRUE | Not_TMED_Event | 528
MAYAGÃœEZ | 2021-07-12 05:17 | 2021-07-12 10:48 | 4664 | 005:31 | S | PROTECCION DEFECTUOSA | LINEA PRIMARIA PARTIDA EN ALIMENTADOR 6012-05 INTERRUPTOR NO VIO AVERIA SE LLEVO LA ALTA DEL TRANSFORMADOR SE DEJO INTERRUPTOR ABIERTO Y SE ENERGIZO TRANSFORMADOR | M21071200019 | New_Event | Protection Miscoordination | Include | Include | Other | 331 | 2021-07-12 | 1543784 | keep | 0 | Jul | 2021 | 1.0515 | 0.0031766 | Sustained | FALSE | TRUE | Not_TMED_Event | 4664
MAYAGÃœEZ | 2021-07-12 05:17 | 2021-07-12 10:48 | 2067 | 005:31 | S | PROTECCION DEFECTUOSA | LINEA PRIMARIA PARTIDA EN ALIMENTADOR 6012-05 INTERRUPTOR NO VIO AVERIA SE LLEVO LA ALTA DEL TRANSFORMADOR SE DEJO INTERRUPTOR ABIERTO Y SE ENERGIZO TRANSFORMADOR | M21071200019 | New_Event | Protection Miscoordination | Include | Include | Other | 331 | 2021-07-12 | 684177 | keep | 0 | Jul | 2021 | 0.46599 | 0.0014078 | Sustained | FALSE | TRUE | Not_TMED_Event | 2067
MAYAGÃœEZ | 2021-07-12 05:17 | 2021-07-12 10:48 | 1352 | 005:31 | S | PROTECCION DEFECTUOSA | LINEA PRIMARIA PARTIDA EN ALIMENTADOR 6012-05 INTERRUPTOR NO VIO AVERIA SE LLEVO LA ALTA DEL TRANSFORMADOR SE DEJO INTERRUPTOR ABIERTO Y SE ENERGIZO TRANSFORMADOR | M21071200019 | New_Event | Protection Miscoordination | Include | Include | Other | 331 | 2021-07-12 | 447512 | keep | 0 | Jul | 2021 | 0.3048 | 0.00092084 | Sustained | FALSE | TRUE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2021-07-12 06:00 | 2021-07-12 13:50 | 15 | 007:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA LINEAS CRUZADAS | M21071200000 | New_Event | Wire Down | Include | Include | Equipment | 470 | 2021-07-12 | 7050 | keep | 0 | Jul | 2021 | 0.0048017 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-07-12 06:00 | 2021-07-12 19:53 | 150 | 013:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | M21071200000 | New_Event | Bad Weather | Include | Include | Weather | 833 | 2021-07-12 | 124950 | keep | 0 | Jul | 2021 | 0.085103 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-07-12 06:00 | 2021-07-12 11:30 | 6 | 005:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | M21071200000 | New_Event | Bad Weather | Include | Include | Weather | 330 | 2021-07-12 | 1980 | keep | 0 | Jul | 2021 | 0.0013486 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-07-12 06:00 | 2021-07-12 11:00 | 1 | 005:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN TRANSFORMADOR | A21071200000 | New_Event | Cutout Failure | Include | Include | Equipment | 300 | 2021-07-12 | 300 | keep | 0 | Jul | 2021 | 0.00020433 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-07-12 06:02 | 2021-07-12 15:33 | 45 | 009:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO CAJA PRIMARIA AVERIADA NO FUNDIO FUSIBLE | C21071200010 | New_Event | Cutout Failure | Include | Include | Equipment | 571 | 2021-07-12 | 25695 | keep | 0 | Jul | 2021 | 0.017501 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2021-07-12 06:20 | 2021-07-12 09:26 | 540 | 003:06 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO | C21071200000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 186 | 2021-07-12 | 100440 | keep | 0 | Jul | 2021 | 0.068409 | 0.00036779 | Sustained | FALSE | FALSE | Not_TMED_Event | 540
BARRANQUITAS | 2021-07-12 06:20 | 2021-07-12 18:20 | 65 | 012:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE RETEZO LINEA ARRIADA | C21071200011 | New_Event | Wire Down | Include | Include | Equipment | 720 | 2021-07-12 | 46800 | keep | 0 | Jul | 2021 | 0.031875 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
VEGA BAJA | 2021-07-12 06:52 | 2021-07-12 11:52 | 80 | 005:00 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA DESGANCHE MASIVO | B21071200012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 300 | 2021-07-12 | 24000 | keep | 0 | Jul | 2021 | 0.016346 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
VEGA BAJA | 2021-07-12 07:00 | 2021-07-12 09:20 | 40 | 002:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO EN CORTE DE LINEA | B21071200017 | New_Event | Wire Down | Include | Include | Equipment | 140 | 2021-07-12 | 5600 | keep | 0 | Jul | 2021 | 0.0038141 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-12 07:06 | 2021-07-12 16:13 | 20 | 009:07 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21071200013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 547 | 2021-07-12 | 10940 | keep | 0 | Jul | 2021 | 0.0074512 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
YAUCO | 2021-07-12 07:16 | 2021-07-12 12:10 | 5 | 004:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA | P21071200001 | New_Event | Bad Weather | Include | Include | Weather | 294 | 2021-07-12 | 1470 | keep | 0 | Jul | 2021 | 0.0010012 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-07-12 07:22 | 2021-07-12 19:06 | 100 | 011:44 | P | LINEA DE TRANSMISION 38KV | SE ABRIO CORTE DE LINEA PARA TRABAJAR EN LINEA 1500 Y 2000 | M12071200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 704 | 2021-07-12 | 70400 | keep | 0 | Jul | 2021 | 0.047949 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-07-12 07:40 | 2021-07-12 19:05 | 150 | 011:25 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE | M21071200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 685 | 2021-07-12 | 102750 | keep | 0 | Jul | 2021 | 0.069983 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-07-12 07:45 | 2021-07-12 14:40 | 30 | 006:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21071200009 | New_Event | Bad Weather | Include | Include | Weather | 415 | 2021-07-12 | 12450 | keep | 0 | Jul | 2021 | 0.0084796 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-07-12 07:47 | 2021-07-12 15:29 | 100 | 007:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | C21071200018 | New_Event | Wire Down | Include | Include | Equipment | 462 | 2021-07-12 | 46200 | keep | 0 | Jul | 2021 | 0.031467 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2021-07-12 07:53 | 2021-07-23 11:27 | 1 | 267:34 | P | CABLE SOTERRADO AVERIADO | 1 X 30 EN RISER SE REMPLAZO CABLE SOTERRADO AVERIADO | B21071200020 | New_Event | UG Cable Fault | Include | Include | Equipment | 16054 | 2021-07-12 | 16054 | keep | 0 | Jul | 2021 | 0.010934 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2021-07-12 08:02 | 2021-07-12 10:52 | 60 | 002:50 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21071200023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2021-07-12 | 10200 | keep | 0 | Jul | 2021 | 0.0069472 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-07-12 08:08 | 2021-07-12 11:08 | 10 | 003:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA AVERIADA Y SE CERRO BAJANTE DE TRANSFORMADOR | S21071200012 | New_Event | Cutout Failure | Include | Include | Equipment | 180 | 2021-07-12 | 1800 | keep | 0 | Jul | 2021 | 0.001226 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-07-12 08:30 | 2021-07-12 08:31 | 4035 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | P21071200005 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-07-12 | 4035 | keep | 0 | Jul | 2021 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
PONCE | 2021-07-12 08:31 | 2021-07-12 12:35 | 267 | 004:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE DE LINEA REMPLAZO CAJA | P21071200008 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 244 | 2021-07-12 | 65148 | keep | 0 | Jul | 2021 | 0.044372 | 0.00018185 | Sustained | FALSE | TRUE | Not_TMED_Event | 267
BAYAMON | 2021-07-12 08:32 | 2021-07-13 10:35 | 10 | 026:03 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA REALIZAR DESGANCHE ENREDADERA Y CERRAR BAJANTE SECUNDARIO | S21071200019 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1563 | 2021-07-12 | 15630 | keep | 0 | Jul | 2021 | 0.010646 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2021-07-12 08:50 | 2021-07-12 10:00 | 50 | 001:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | P21071200010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2021-07-12 | 3500 | keep | 0 | Jul | 2021 | 0.0023838 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-07-12 08:50 | 2021-07-12 09:34 | 10 | 000:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE CERRO BAJANTE SECUNDARIO | B21071200030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 44 | 2021-07-12 | 440 | keep | 0 | Jul | 2021 | 0.00029968 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-07-12 08:59 | 2021-07-12 10:36 | 20 | 001:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO HACIA TRANSFORMADOR | C21071200038 | New_Event | Wire Down | Include | Include | Equipment | 97 | 2021-07-12 | 1940 | keep | 0 | Jul | 2021 | 0.0013213 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2021-07-12 09:14 | 2021-07-13 16:47 | 30 | 031:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE | A21071200002 | New_Event | Wire Down | Include | Include | Equipment | 1893 | 2021-07-12 | 56790 | keep | 0 | Jul | 2021 | 0.038679 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-07-12 09:26 | 2021-07-12 11:38 | 540 | 002:12 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO PIN POLE TOP Y SE RETORNO CONDUCTOR ZAFADO AL PIN | C21071200000 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 132 | 2021-07-12 | 71280 | keep | 0 | Jul | 2021 | 0.048548 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-12 09:35 | 2021-07-12 10:40 | 200 | 001:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA | M21071200000 | New_Event | Cutout Failure | Include | Include | Equipment | 65 | 2021-07-12 | 13000 | keep | 0 | Jul | 2021 | 0.0088542 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-07-12 09:38 | 2021-07-12 14:37 | 1 | 004:59 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS | B21071200043 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 299 | 2021-07-12 | 299 | keep | 0 | Jul | 2021 | 0.00020365 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-07-12 09:40 | 2021-07-12 17:56 | 25 | 008:16 | P | HERRAJE ROTO O PODRIDO | SE ABRE MACHETE PARA REMPLAZAR CRUCETA Y CAJA PRIMARIA | S21071200029 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 496 | 2021-07-12 | 12400 | keep | 0 | Jul | 2021 | 0.0084456 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-07-12 09:49 | 2021-07-12 11:50 | 60 | 002:01 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO BAMBUA | M21071200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2021-07-12 | 7260 | keep | 0 | Jul | 2021 | 0.0049448 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-07-12 10:03 | 2021-07-12 13:16 | 99 | 003:13 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21071200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2021-07-12 | 19107 | keep | 0 | Jul | 2021 | 0.013014 | 6.7428e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 99
CAGUAS | 2021-07-12 10:13 | 2021-07-12 13:50 | 100 | 003:37 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21071200044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2021-07-12 | 21700 | keep | 0 | Jul | 2021 | 0.01478 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-12 10:18 | 2021-07-12 14:51 | 95 | 004:33 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21071200020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 273 | 2021-07-12 | 25935 | keep | 0 | Jul | 2021 | 0.017664 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
BAYAMON | 2021-07-12 10:22 | 2021-07-12 15:58 | 20 | 005:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 50 EN CORTE DE LINEA SE ENDEREZO POSTE Y SE REMPLAZO AISLACION POR IMPACTO DE VEHICULO | B21071200065 | New_Event |  |  | Include | Wildlife | 336 | 2021-07-12 | 6720 | keep | 0 | Jul | 2021 | 0.004577 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-07-12 10:24 | 2021-07-12 14:30 | 40 | 004:06 | P | ESTRUCTURA AVERIADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO POSTE PRIMARIO | M12071200000 | New_Event | Defective Pole | Include | Include | Equipment | 246 | 2021-07-12 | 9840 | keep | 0 | Jul | 2021 | 0.006702 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
YAUCO | 2021-07-12 10:40 | 2021-07-13 09:31 | 35 | 022:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | P21071200018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1371 | 2021-07-12 | 47985 | keep | 0 | Jul | 2021 | 0.032682 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-07-12 10:47 | 2021-07-14 12:45 | 200 | 049:58 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | A21071400029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2998 | 2021-07-12 | 599600 | keep | 0 | Jul | 2021 | 0.40838 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-07-12 10:48 | 2021-07-12 14:34 | 1352 | 003:46 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA Y SE PASO LA CARGA AL 6012-01 | M21071200019 | New_Event | Wire Down | Include | Include | Equipment | 226 | 2021-07-12 | 305552 | keep | 0 | Jul | 2021 | 0.20811 | 0.00092084 | Sustained | FALSE | TRUE | Not_TMED_Event | 1352
CAGUAS | 2021-07-12 10:57 | 2021-07-12 15:06 | 95 | 004:09 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTES DE LINEAS | C21071200052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 249 | 2021-07-12 | 23655 | keep | 0 | Jul | 2021 | 0.016111 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
BAYAMON | 2021-07-12 11:08 | 2021-07-12 20:56 | 35 | 009:48 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21071200088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 588 | 2021-07-12 | 20580 | keep | 0 | Jul | 2021 | 0.014017 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
CAGUAS | 2021-07-12 11:08 | 2021-07-12 17:29 | 10 | 006:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA ABIERTA | C21071200056 | New_Event | Secondary Wire Down | Include | Include | Equipment | 381 | 2021-07-12 | 3810 | keep | 0 | Jul | 2021 | 0.002595 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-12 11:11 | 2021-07-12 15:25 | 2658 | 004:14 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEAS PRIMARIAS AVERIADAS | M21071200238 | New_Event | Wire Down | Include | Include | Equipment | 254 | 2021-07-12 | 675132 | keep | 0 | Jul | 2021 | 0.45983 | 0.0018104 | Sustained | FALSE | TRUE | Not_TMED_Event | 2658
BAYAMON | 2021-07-12 11:45 | 2021-07-12 16:27 | 1 | 004:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA Y PARARRAYO SE REALIZO DESGANCHE | B21071200099 | New_Event | Cutout Failure | Include | Include | Equipment | 282 | 2021-07-12 | 282 | keep | 0 | Jul | 2021 | 0.00019207 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-07-12 11:55 | 2021-07-12 11:56 | 10211 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO CARGA POR EL 1206-03 | S21071200291 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-12 | 10211 | keep | 0 | Jul | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-07-12 11:55 | 2021-07-12 11:56 | 4133 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR Y SE CEERO POR SCADA LLEVA CARGA DEL 1204-05 | S21071200000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-12 | 4133 | keep | 0 | Jul | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
YAUCO | 2021-07-12 12:00 | 2021-07-12 15:41 | 60 | 003:41 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | P210712000XX | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2021-07-12 | 13260 | keep | 0 | Jul | 2021 | 0.0090313 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-07-12 12:00 | 2021-07-12 13:16 | 50 | 001:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA CRUZADA | A21071200000 | New_Event | Wire Down | Include | Include | Equipment | 76 | 2021-07-12 | 3800 | keep | 0 | Jul | 2021 | 0.0025882 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-07-12 12:02 | 2021-07-12 16:52 | 1 | 004:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21071200064 | New_Event | Bad Weather | Include | Include | Weather | 290 | 2021-07-12 | 290 | keep | 0 | Jul | 2021 | 0.00019752 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-07-12 12:02 | 2021-07-12 17:55 | 100 | 005:53 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA Y 2 X 15 EN TRANSFORMADOR | C21071200065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 353 | 2021-07-12 | 35300 | keep | 0 | Jul | 2021 | 0.024043 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-07-12 12:04 | 2021-07-12 18:00 | 2 | 005:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO | A21071200039 | New_Event | Wire Down | Include | Include | Equipment | 356 | 2021-07-12 | 712 | keep | 0 | Jul | 2021 | 0.00048494 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2021-07-12 12:12 | 2021-07-12 14:00 | 30 | 001:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21071200041 | New_Event | Bad Weather | Include | Include | Weather | 108 | 2021-07-12 | 3240 | keep | 0 | Jul | 2021 | 0.0022067 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-07-12 12:16 | 2021-07-12 16:13 | 50 | 003:57 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21070900156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 237 | 2021-07-12 | 11850 | keep | 0 | Jul | 2021 | 0.008071 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-12 12:39 | 2021-07-15 11:15 | 8 | 070:36 | P | SECUNDARIA/DESGANCHE | SE LEVANTO SECUNDARIA DEL SUELO SE REALIZO DESGANCHE Y SE RELOCALIZARON DOS (2) TOMAS DE SERVICIO TRASPATIO | S21071200063 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 4236 | 2021-07-12 | 33888 | keep | 0 | Jul | 2021 | 0.023081 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-07-12 12:39 | 2021-07-12 14:04 | 65 | 001:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21071200069 | New_Event | Bad Weather | Include | Include | Weather | 85 | 2021-07-12 | 5525 | keep | 0 | Jul | 2021 | 0.0037631 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
SAN JUAN | 2021-07-12 12:47 | 2021-07-12 12:48 | 10211 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO CARGA POR EL 1206-03 | S21071200291 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-07-12 | 10211 | keep | 0 | Jul | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-07-12 12:47 | 2021-07-12 12:48 | 4133 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR LLEVA CARGA DEL 1204-05 | S21071200000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-07-12 | 4133 | keep | 0 | Jul | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-07-12 12:47 | 2021-07-12 13:27 | 1 | 000:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA Y SE RETESO LINEA | S21071200066 | New_Event | Wire Down | Include | Include | Equipment | 40 | 2021-07-12 | 40 | keep | 0 | Jul | 2021 | 2.7244e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BARRANQUITAS | 2021-07-12 13:04 | 2021-07-12 16:06 | 60 | 003:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21071200073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2021-07-12 | 10920 | keep | 0 | Jul | 2021 | 0.0074376 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-07-12 13:09 | 2021-07-13 11:27 | 72 | 022:18 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21071200078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1338 | 2021-07-12 | 96336 | keep | 0 | Jul | 2021 | 0.065614 | 4.9039e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 72
BAYAMON | 2021-07-12 13:19 | 2021-07-12 19:35 | 45 | 006:16 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21071200074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 376 | 2021-07-12 | 16920 | keep | 0 | Jul | 2021 | 0.011524 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
SAN JUAN | 2021-07-12 13:20 | 2021-07-12 13:21 | 10211 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO CARGA POR EL 1206-03 | S21071200291 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-07-12 | 10211 | keep | 0 | Jul | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-07-12 13:20 | 2021-07-12 13:21 | 4133 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR LLEVA CARGA DEL 1204-05 | S21071200000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-07-12 | 4133 | keep | 0 | Jul | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
AGUADILLA | 2021-07-12 13:20 | 2021-07-12 14:40 | 1261 | 001:20 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR AUTORIZADO POR ING FENEQUE PARA REPARAR LINEA 5600 | M21071200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2021-07-12 | 100880 | keep | 0 | Jul | 2021 | 0.068709 | 0.00085886 | Sustained | FALSE | TRUE | Not_TMED_Event | 1261
MAYAGÃœEZ | 2021-07-12 13:23 | 2021-07-12 18:25 | 300 | 005:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO SE ABRIO MACHETES PARA CERRARLO | M21071200366 | New_Event | Wire Down | Include | Include | Equipment | 302 | 2021-07-12 | 90600 | keep | 0 | Jul | 2021 | 0.061707 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BARRANQUITAS | 2021-07-12 13:24 | 2021-07-12 16:18 | 1 | 002:54 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | C21071200085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2021-07-12 | 174 | keep | 0 | Jul | 2021 | 0.00011851 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2021-07-12 14:00 | 2021-07-12 15:10 | 10 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P210712000XX | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2021-07-12 | 700 | keep | 0 | Jul | 2021 | 0.00047677 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
UTUADO | 2021-07-12 14:12 | 2021-07-13 14:00 | 30 | 023:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | A21071200049 | New_Event | Wire Down | Include | Include | Equipment | 1428 | 2021-07-12 | 42840 | keep | 0 | Jul | 2021 | 0.029178 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-07-12 14:17 | 2021-07-12 15:33 | 1681 | 001:16 | T | DESGANCHE | DISPARO CON R/R OFF SE ABRIO MACHETE CAMINO LOS GUANOS Y SE CERRO INTERRUPTOR 85% EN SERVICIO Y 100% DEL 1346-6 | S21071200092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2021-07-12 | 127756 | keep | 0 | Jul | 2021 | 0.087014 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-07-12 14:17 | 2021-07-12 15:33 | 1598 | 001:16 | T | DESGANCHE | DISPARO CON R/R OFF SE ABRIO MACHETE CAMINO LOS GUANOS Y SE CERRO INTERRUPTOR 85% EN SERVICIO Y 100% DEL 1346-6 | S21071200092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2021-07-12 | 121448 | keep | 0 | Jul | 2021 | 0.082718 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
MAYAGÃœEZ | 2021-07-12 14:39 | 2021-07-12 15:45 | 80 | 001:06 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21071200303 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2021-07-12 | 5280 | keep | 0 | Jul | 2021 | 0.0035962 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-07-12 14:43 | 2021-07-12 15:30 | 15 | 000:47 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA POR 50 KVA | A21071200050 | New_Event | Service Transformer Failure | Include | Include | Equipment | 47 | 2021-07-12 | 705 | keep | 0 | Jul | 2021 | 0.00048017 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-07-12 15:15 | 2021-07-12 15:45 | 12 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | M21071200000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2021-07-12 | 360 | keep | 0 | Jul | 2021 | 0.00024519 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-07-12 15:33 | 2021-07-12 16:00 | 300 | 000:27 | P | DESGANCHE | SE RETIRO BAMBUAS SOBRE LINEA Y SE CERRO MACHETE 100% EN SERVICIO | S21071200092 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 27 | 2021-07-12 | 8100 | keep | 0 | Jul | 2021 | 0.0055169 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-07-12 15:46 | 2021-07-12 17:26 | 1935 | 001:40 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 | B21071200179 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 100 | 2021-07-12 | 193500 | keep | 0 | Jul | 2021 | 0.13179 | 0.0013179 | Sustained | FALSE | TRUE | Not_TMED_Event | 1935
BAYAMON | 2021-07-12 15:46 | 2021-07-12 17:26 | 3 | 001:40 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 | B21071200179 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 100 | 2021-07-12 | 300 | keep | 0 | Jul | 2021 | 0.00020433 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
BAYAMON | 2021-07-12 15:46 | 2021-07-12 17:26 | 61 | 001:40 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 | B21071200179 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 100 | 2021-07-12 | 6100 | keep | 0 | Jul | 2021 | 0.0041547 | 4.1547e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 61
BAYAMON | 2021-07-12 15:46 | 2021-07-12 17:26 | 1501 | 001:40 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 | B21071200179 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 100 | 2021-07-12 | 150100 | keep | 0 | Jul | 2021 | 0.10223 | 0.0010223 | Sustained | FALSE | TRUE | Not_TMED_Event | 1501
BAYAMON | 2021-07-12 15:46 | 2021-07-12 17:26 | 546 | 001:40 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 | B21071200179 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 100 | 2021-07-12 | 54600 | keep | 0 | Jul | 2021 | 0.037188 | 0.00037188 | Sustained | FALSE | TRUE | Not_TMED_Event | 546
BAYAMON | 2021-07-12 15:46 | 2021-07-12 17:26 | 959 | 001:40 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 CARGA DE SUBESTACION A TRAVES DE LA BARRA DE LA 1904 | S21071200235 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 100 | 2021-07-12 | 95900 | keep | 0 | Jul | 2021 | 0.065317 | 0.00065317 | Sustained | FALSE | TRUE | Not_TMED_Event | 959
BAYAMON | 2021-07-12 15:46 | 2021-07-12 17:26 | 1297 | 001:40 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 CARGA DE SUBESTACION A TRAVES DE LA BARRA DE LA 1904 | S21071200235 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 100 | 2021-07-12 | 129700 | keep | 0 | Jul | 2021 | 0.088338 | 0.00088338 | Sustained | FALSE | TRUE | Not_TMED_Event | 1297
BAYAMON | 2021-07-12 15:46 | 2021-07-12 17:26 | 451 | 001:40 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 CARGA DE SUBESTACION A TRAVES DE LA BARRA DE LA 1904 | S21071200235 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 100 | 2021-07-12 | 45100 | keep | 0 | Jul | 2021 | 0.030717 | 0.00030717 | Sustained | FALSE | TRUE | Not_TMED_Event | 451
BAYAMON | 2021-07-12 15:46 | 2021-07-12 17:26 | 1264 | 001:40 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 CARGA DE SUBESTACION A TRAVES DE LA BARRA DE LA 1904 | S21071200235 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 100 | 2021-07-12 | 126400 | keep | 0 | Jul | 2021 | 0.08609 | 0.0008609 | Sustained | FALSE | TRUE | Not_TMED_Event | 1264
BAYAMON | 2021-07-12 15:46 | 2021-07-12 17:26 | 620 | 001:40 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 CARGA DE SUBESTACION A TRAVES DE LA BARRA DE LA 1904 | S21071200235 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 100 | 2021-07-12 | 62000 | keep | 0 | Jul | 2021 | 0.042228 | 0.00042228 | Sustained | FALSE | TRUE | Not_TMED_Event | 620
SAN JUAN | 2021-07-12 15:58 | 2021-07-12 16:27 | 570 | 000:29 | T | DESCONECTIVO DEFECTUOSO | SE ABRE INTERRUPTOR PARA REMPLAZAR MACHETE QUEMADO EN N/O 1328-2 Y 5 AVE MUÃ‘OZ RIVERA FTE. DEALER TOYOTA CARGA POR EL 1338-02 | S21071200062 | New_Event | Switch Failure | Include | Include | Equipment | 29 | 2021-07-12 | 16530 | keep | 0 | Jul | 2021 | 0.011259 | 0.00038822 | Sustained | FALSE | FALSE | Not_TMED_Event | 570
SAN JUAN | 2021-07-12 15:58 | 2021-07-12 16:27 | 155 | 000:29 | T | DESCONECTIVO DEFECTUOSO | SE ABRE INTERRUPTOR PARA REMPLAZAR MACHETE QUEMADO EN N/O 1328-2 Y 5 AVE MUÃ‘OZ RIVERA FTE. DEALER TOYOTA CARGA POR EL 1338-02 | S21071200062 | New_Event | Switch Failure | Include | Include | Equipment | 29 | 2021-07-12 | 4495 | keep | 0 | Jul | 2021 | 0.0030615 | 0.00010557 | Sustained | FALSE | FALSE | Not_TMED_Event | 155
SAN JUAN | 2021-07-12 15:58 | 2021-07-12 16:27 | 928 | 000:29 | T | DESCONECTIVO DEFECTUOSO | SE ABRE INTERRUPTOR PARA REMPLAZAR MACHETE QUEMADO EN N/O 1328-2 Y 5 AVE MUÃ‘OZ RIVERA FTE. DEALER TOYOTA LLEVA CARGA 1328-2 1328-5 1422-5 Y PARTE DE 1422-3 | S21071200062 | New_Event | Switch Failure | Include | Include | Equipment | 29 | 2021-07-12 | 26912 | keep | 0 | Jul | 2021 | 0.01833 | 0.00063206 | Sustained | FALSE | FALSE | Not_TMED_Event | 928
SAN JUAN | 2021-07-12 15:58 | 2021-07-12 16:27 | 150 | 000:29 | P | DESCONECTIVO DEFECTUOSO | SE ABRE INTERRUPTOR PARA REMPLAZAR MACHETE QUEMADO EN N/O 1328-2 Y 5 AVE MUÃ‘OZ RIVERA FTE. DEALER TOYOTA CARGA POR EL 1338-02 | S21071200062 | New_Event | Switch Failure | Include | Include | Equipment | 29 | 2021-07-12 | 4350 | keep | 0 | Jul | 2021 | 0.0029628 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2021-07-12 15:58 | 2021-07-12 16:27 | 637 | 000:29 | T | DESCONECTIVO DEFECTUOSO | SE ABRE INTERRUPTOR PARA REMPLAZAR MACHETE QUEMADO EN N/O 1328-2 Y 5 AVE MUÃ‘OZ RIVERA FTE. DEALER TOYOTA CARGA POR EL 1338-02 | S21071200062 | New_Event | Switch Failure | Include | Include | Equipment | 29 | 2021-07-12 | 18473 | keep | 0 | Jul | 2021 | 0.012582 | 0.00043386 | Sustained | FALSE | FALSE | Not_TMED_Event | 637
MAYAGÃœEZ | 2021-07-12 16:00 | 2021-07-12 18:35 | 200 | 002:35 | P | DESGANCHE | 2 X 140 EN CORTE DE LINEA DESGANCHE | M21071200337 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2021-07-12 | 31000 | keep | 0 | Jul | 2021 | 0.021114 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-07-12 16:00 | 2021-07-12 16:55 | 4 | 000:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | M21071100083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 55 | 2021-07-12 | 220 | keep | 0 | Jul | 2021 | 0.00014984 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-07-12 16:07 | 2021-07-12 17:39 | 50 | 001:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | B21071200147 | New_Event | Wire Down | Include | Include | Equipment | 92 | 2021-07-12 | 4600 | keep | 0 | Jul | 2021 | 0.003133 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-07-12 16:18 | 2021-07-12 18:40 | 110 | 002:22 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTE DE LINEA | C21071200106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2021-07-12 | 15620 | keep | 0 | Jul | 2021 | 0.010639 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
PONCE | 2021-07-12 16:24 | 2021-07-12 17:54 | 752 | 001:30 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR POR AVERIA SOTERRADA. SE SECCIONALIZO ALIMENTADOR Y SE CERRO INTERRUPTOR. | P21071200048 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 90 | 2021-07-12 | 67680 | keep | 0 | Jul | 2021 | 0.046097 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
PONCE | 2021-07-12 16:24 | 2021-07-12 19:32 | 2696 | 003:08 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR POR AVERIA SOTERRADA EN MH-412. SE SECCIONALIZO AVERIA Y SE CERRO INTERRUPTOR. | P21071200048 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 188 | 2021-07-12 | 506848 | keep | 0 | Jul | 2021 | 0.34521 | 0.0018362 | Sustained | FALSE | FALSE | Not_TMED_Event | 2696
BAYAMON | 2021-07-12 16:31 | 2021-07-12 19:51 | 12 | 003:20 | P | CABLE SOTERRADO AVERIADO | 1 X 15 EN AEREO PROVISIONAL SE CONSTRUYO AEREO PROVISIONAL DE EXISTENTE A T8 | B21071100084 | New_Event | UG Cable Fault | Include | Include | Equipment | 200 | 2021-07-12 | 2400 | keep | 0 | Jul | 2021 | 0.0016346 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2021-07-12 16:34 | 2021-07-12 18:25 | 10 | 001:51 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M21071000226 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2021-07-12 | 1110 | keep | 0 | Jul | 2021 | 0.00075602 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-12 16:43 | 2021-07-12 16:44 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 6007-05 | M21071200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-12 | 393 | keep | 0 | Jul | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2021-07-12 16:43 | 2021-07-12 16:44 | 4 | 000:01 | T | NO SE REPORTO CAUSA | CARGA POR 6007-04 | M21071200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-12 | 4 | keep | 0 | Jul | 2021 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-07-12 16:54 | 2021-07-13 14:36 | 30 | 021:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21071200348 | New_Event | Bad Weather | Include | Include | Weather | 1302 | 2021-07-12 | 39060 | keep | 0 | Jul | 2021 | 0.026604 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-07-12 16:56 | 2021-07-13 12:00 | 70 | 019:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTE DE LINEA AVE | M21071200349 | New_Event |  |  | Include | Wildlife | 1144 | 2021-07-12 | 80080 | keep | 0 | Jul | 2021 | 0.054542 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
FAJARDO | 2021-07-12 17:02 | 2021-07-13 00:12 | 50 | 007:10 | P | ESTRUCTURA AVERIADA | ABRIO CORTE DE LINEA PARA REMPLAZAR POSTE PARTIDO | R21071200034 | New_Event | Defective Pole | Include | Include | Equipment | 430 | 2021-07-12 | 21500 | keep | 0 | Jul | 2021 | 0.014644 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-07-12 17:25 | 2021-07-12 18:52 | 20 | 001:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | M21071200000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 87 | 2021-07-12 | 1740 | keep | 0 | Jul | 2021 | 0.0011851 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-07-12 17:26 | 2021-07-12 17:27 | 1 | 000:01 | S | LINEA DE TRANSMISION 38KV | SE ABRE 3410 PARA REALIZAR OPERACIONES EN LINEA Y SECCIONALIZAR TRAMO EN EL PISO FTE. COSTCO AVE. LOS FILTROS Y ENERGIZER SUBSETACION 1904 Y 1707 | S21071200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-12 | 1 | keep | 0 | Jul | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-07-12 17:26 | 2021-07-12 17:27 | 1844 | 000:01 | S | LINEA DE TRANSMISION 38KV | SE ABRE 3410 PARA REALIZAR OPERACIONES EN LINEA Y SECCIONALIZAR TRAMO EN EL PISO FTE. COSTCO AVE. LOS FILTROS Y ENERGIZR SUBSETACION 1904 Y 1707 | S21071200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-12 | 1844 | keep | 0 | Jul | 2021 | 0.0012559 | 0.0012559 | Momentary | FALSE | TRUE | Not_TMED_Event | 1844
SAN JUAN | 2021-07-12 17:26 | 2021-07-12 17:27 | 2422 | 000:01 | S | LINEA DE TRANSMISION 38KV | SE ABRE 3410 PARA REALIZAR OPERACIONES EN LINEA Y SECCIONALIZAR TRAMO EN EL PISO FTE. COSTCO AVE. LOS FILTROS Y ENERGIZER SUBSETACION 1904 Y 1707 | S21071200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-12 | 2422 | keep | 0 | Jul | 2021 | 0.0016496 | 0.0016496 | Momentary | FALSE | TRUE | Not_TMED_Event | 2422
SAN JUAN | 2021-07-12 17:30 | 2021-07-13 09:38 | 55 | 016:08 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21071200288 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 968 | 2021-07-12 | 53240 | keep | 0 | Jul | 2021 | 0.036262 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
FAJARDO | 2021-07-12 17:48 | 2021-07-12 19:47 | 110 | 001:59 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | R21071200035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 119 | 2021-07-12 | 13090 | keep | 0 | Jul | 2021 | 0.0089155 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
PONCE | 2021-07-12 17:54 | 2021-07-12 19:29 | 376 | 001:35 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR AL REALIZAR PRUEBAS A LINEA SOTERRADA | P21071200064 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 95 | 2021-07-12 | 35720 | keep | 0 | Jul | 2021 | 0.024329 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CANOVANAS | 2021-07-12 17:57 | 2021-07-12 18:45 | 6 | 000:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE HACA CAJA PRIMARIA DE TRANSFORMADOR | R21071200036 | New_Event | Wire Down | Include | Include | Equipment | 48 | 2021-07-12 | 288 | keep | 0 | Jul | 2021 | 0.00019616 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2021-07-12 17:58 | 2021-07-12 18:54 | 12 | 000:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONECTORES EN BAJANTE SECUNDARIO DE TRANSFORMADOR | B21071200192 | New_Event | Secondary Wire Down | Include | Include | Equipment | 56 | 2021-07-12 | 672 | keep | 0 | Jul | 2021 | 0.0004577 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2021-07-12 17:59 | 2021-07-12 18:00 | 240 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21071200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-12 | 240 | keep | 0 | Jul | 2021 | 0.00016346 | 0.00016346 | Momentary | FALSE | FALSE | Not_TMED_Event | 240
MAYAGÃœEZ | 2021-07-12 18:03 | 2021-07-13 18:21 | 50 | 024:18 | P | PARARRAYOS DEFECTUOSO | 2 X 50 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO Y SE REALIZO DESGANCHE | M21071300361 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1458 | 2021-07-12 | 72900 | keep | 0 | Jul | 2021 | 0.049652 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-07-12 18:08 | 2021-07-13 10:00 | 40 | 015:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | M21071200363 | New_Event | Bad Weather | Include | Include | Weather | 952 | 2021-07-12 | 38080 | keep | 0 | Jul | 2021 | 0.025936 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
GUAYAMA | 2021-07-12 18:11 | 2021-07-12 18:12 | 464 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21071200065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-12 | 464 | keep | 0 | Jul | 2021 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
MAYAGÃœEZ | 2021-07-12 18:14 | 2021-07-12 18:31 | 5 | 000:17 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA POR 37.5 KVA | M21071200365 | New_Event | Service Transformer Failure | Include | Include | Equipment | 17 | 2021-07-12 | 85 | keep | 0 | Jul | 2021 | 5.7893e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-07-12 18:16 | 2021-07-12 18:47 | 10211 | 000:31 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO CON R/R OFF SE ENCONTRO CONDUCTOR SAFADO SOBRE CRUCETA SE REPARO Y SE CERRO INTERRUPTOR CARGA POR 1206-03 | S21071200291 | New_Event | Wire Down | Include | Include | Equipment | 31 | 2021-07-12 | 316541 | keep | 0 | Jul | 2021 | 0.21559 | 0.0069547 | Sustained | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-07-12 18:16 | 2021-07-12 18:47 | 4133 | 000:31 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO CON R/R OFF SE ENCONTRO CONDUCTOR SAFADO SOBRE CRUCETA SE REPARO Y SE CERRO INTERRUPTOR LLEVA CARGA 1204-5 | S21071200291 | New_Event | Wire Down | Include | Include | Equipment | 31 | 2021-07-12 | 128123 | keep | 0 | Jul | 2021 | 0.087264 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
BAYAMON | 2021-07-12 18:25 | 2021-07-13 17:26 | 12 | 023:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21071200300 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1381 | 2021-07-12 | 16572 | keep | 0 | Jul | 2021 | 0.011287 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-07-12 18:25 | 2021-07-12 20:00 | 1000 | 001:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO SE CERRO MACHETES | M21071200366 | Additional_clients | Wire Down | Include | Include | Equipment | 95 | 2021-07-12 | 95000 | keep | 0 | Jul | 2021 | 0.064704 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-07-12 18:29 | 2021-07-12 20:40 | 95 | 002:11 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER Y 1 X 80 EN CORTE DE LINEA | R21071200038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 131 | 2021-07-12 | 12445 | keep | 0 | Jul | 2021 | 0.0084762 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
AGUADILLA | 2021-07-12 18:30 | 2021-07-13 17:52 | 10 | 023:22 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA X 50 KVA | M21071300068 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1402 | 2021-07-12 | 14020 | keep | 0 | Jul | 2021 | 0.009549 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-12 18:31 | 2021-07-12 18:35 | 528 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVA LA CARGA DEL 6012-05 Y DEL 6014-03 | M21071200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-07-12 | 2112 | keep | 0 | Jul | 2021 | 0.0014385 | 0.00035962 | Momentary | FALSE | FALSE | Not_TMED_Event | 528
MAYAGÃœEZ | 2021-07-12 18:31 | 2021-07-12 18:35 | 1352 | 000:04 | T | NO SE REPORTO CAUSA | CARGA POR 6012-01 | M21071200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-07-12 | 5408 | keep | 0 | Jul | 2021 | 0.0036834 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2021-07-12 18:31 | 2021-07-12 18:35 | 871 | 000:04 | T | NO SE REPORTO CAUSA | CARGA POR 6012-05 | M21071200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-07-12 | 3484 | keep | 0 | Jul | 2021 | 0.0023729 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2021-07-12 18:35 | 2021-07-13 09:16 | 5 | 014:41 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA X 35 KVA | M21071200365 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 881 | 2021-07-12 | 4405 | keep | 0 | Jul | 2021 | 0.0030002 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-07-12 19:00 | 2021-07-12 21:10 | 12 | 002:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO NEUTRAL PRIMARIO | A21071200060 | New_Event | Wire Down | Include | Include | Equipment | 130 | 2021-07-12 | 1560 | keep | 0 | Jul | 2021 | 0.0010625 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-07-12 19:28 | 2021-07-12 19:48 | 3630 | 000:20 | T | OTRAS CAUSAS | DISPARO INTERRUPTOR EN OPERACIONES DE TRANSFERIRLE CARGA DEL 6014-01 | M21071200000 | New_Event | Other Causes | Include | Include | Other | 20 | 2021-07-12 | 72600 | keep | 0 | Jul | 2021 | 0.049448 | 0.0024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 3630
PONCE | 2021-07-12 19:29 | 2021-07-12 19:30 | 752 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR AL REALIZAR PRUEBAS AL SOTERRADO | P210712000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-12 | 752 | keep | 0 | Jul | 2021 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
CANOVANAS | 2021-07-12 19:42 | 2021-07-12 19:43 | 2708 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21071200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-12 | 2708 | keep | 0 | Jul | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
BARRANQUITAS | 2021-07-12 20:00 | 2021-07-12 20:01 | 3296 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO | C21071200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-12 | 3296 | keep | 0 | Jul | 2021 | 0.0022449 | 0.0022449 | Momentary | FALSE | FALSE | Not_TMED_Event | 3296
MAYAGÃœEZ | 2021-07-12 20:22 | 2021-07-13 14:33 | 100 | 018:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE REPARO LINEA CRUZADA | M21071200385 | New_Event | Wire Down | Include | Include | Equipment | 1091 | 2021-07-12 | 109100 | keep | 0 | Jul | 2021 | 0.074308 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-12 20:46 | 2021-07-13 12:07 | 50 | 015:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO DE LINEA A MACHETE | B21071200200 | New_Event | Wire Down | Include | Include | Equipment | 921 | 2021-07-12 | 46050 | keep | 0 | Jul | 2021 | 0.031364 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-12 20:49 | 2021-07-12 21:35 | 1381 | 000:46 | T | DESCONECTIVO DEFECTUOSO | MACHETE QUEMADO CARR.181 FTE. ESC. MEDARDO CARRAZO Y SE CERRO INTERRUPTOR SE DE UNA FASE ABIERTA PARA MANANA REMPLAZARLO CARGA POR EL 1206-04 | S21071200356 | New_Event | Switch Failure | Include | Include | Equipment | 46 | 2021-07-12 | 63526 | keep | 0 | Jul | 2021 | 0.043267 | 0.00094059 | Sustained | FALSE | FALSE | Not_TMED_Event | 1381
SAN JUAN | 2021-07-12 20:49 | 2021-07-12 21:35 | 1799 | 000:46 | T | DESCONECTIVO DEFECTUOSO | MACHETE QUEMADO CARR 181 FTE ESC MEDARDO CARRAZO Y SE CERRO INTERRUPTOR SE DE UNA FASE ABIERTA PARA MANANA REMPLAZARLO | S21071200356 | New_Event | Switch Failure | Include | Include | Equipment | 46 | 2021-07-12 | 82754 | keep | 0 | Jul | 2021 | 0.056363 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2021-07-12 20:49 | 2021-07-12 21:35 | 300 | 000:46 | P | DESCONECTIVO DEFECTUOSO | MACHETE QUEMADO CARR.181 FTE. ESC. MEDARDO CARRAZO Y SE CERRO INTERRUPTOR SE DE UNA FASE ABIERTA PARA MANANA REMPLAZARLO | S21071200356 | New_Event | Switch Failure | Include | Include | Equipment | 46 | 2021-07-12 | 13800 | keep | 0 | Jul | 2021 | 0.0093991 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2021-07-12 20:50 | 2021-07-14 12:39 | 10 | 039:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE DE SECUNDARIA | B21071200201 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2389 | 2021-07-12 | 23890 | keep | 0 | Jul | 2021 | 0.016271 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-12 20:59 | 2021-07-13 20:04 | 20 | 023:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21071200202 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1385 | 2021-07-12 | 27700 | keep | 0 | Jul | 2021 | 0.018866 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-07-12 21:20 | 2021-07-13 10:41 | 100 | 013:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | C21071200115 | New_Event | Wire Down | Include | Include | Equipment | 801 | 2021-07-12 | 80100 | keep | 0 | Jul | 2021 | 0.054556 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2021-07-12 21:25 | 2021-07-12 21:26 | 2708 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21071200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-12 | 2708 | keep | 0 | Jul | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
MAYAGÃœEZ | 2021-07-12 21:54 | 2021-07-13 12:10 | 100 | 014:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | M21071200388 | New_Event | Bad Weather | Include | Include | Weather | 856 | 2021-07-12 | 85600 | keep | 0 | Jul | 2021 | 0.058302 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-07-12 22:01 | 2021-07-16 11:41 | 10 | 085:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO NEUTRAL SECUNDARIA | P21071200074 | New_Event | Secondary Wire Down | Include | Include | Equipment | 5140 | 2021-07-12 | 51400 | keep | 0 | Jul | 2021 | 0.035008 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-07-12 22:03 | 2021-07-13 09:30 | 150 | 011:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR MAL TIEMPO | A21071200067 | New_Event | Bad Weather | Include | Include | Weather | 687 | 2021-07-12 | 103050 | keep | 0 | Jul | 2021 | 0.070187 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-07-12 23:33 | 2021-07-13 10:20 | 75 | 010:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE REPARARON LINEAS PRIMARIAS PARTIDAS | A21071200074 | New_Event | Wire Down | Include | Include | Equipment | 647 | 2021-07-12 | 48525 | keep | 0 | Jul | 2021 | 0.03305 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
SAN JUAN | 2021-07-13 01:38 | 2021-07-13 11:07 | 40 | 009:29 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21071300013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 569 | 2021-07-13 | 22760 | keep | 0 | Jul | 2021 | 0.015502 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-13 02:01 | 2021-07-13 13:38 | 35 | 011:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | B21071300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 697 | 2021-07-13 | 24395 | keep | 0 | Jul | 2021 | 0.016615 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
CANOVANAS | 2021-07-13 02:56 | 2021-07-13 02:57 | 2708 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | R21071300005 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-13 | 2708 | keep | 0 | Jul | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
BAYAMON | 2021-07-13 03:00 | 2021-07-13 11:28 | 60 | 008:28 | P | CABLE SOTERRADO AVERIADO | 1 X 25 EN RISER AVERIA NUEVA DE T-117 @ T-116 AVERIA VIEJA DE T-116 @ T-115 SE DEJO FUERA EL T-116 Y SE CREO EVENTO NUEVO B21071300038 | B21071300004 | New_Event | UG Cable Fault | Include | Include | Equipment | 508 | 2021-07-13 | 30480 | keep | 0 | Jul | 2021 | 0.02076 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-07-13 03:02 | 2021-07-13 16:19 | 90 | 013:17 | P | CABLE SOTERRADO AVERIADO | 1 X 125 SMU EN SU-3 Y 1 X 80 EN RISER SECCIONALIZARON AVERIA T-4 @ T-5 | R21071300001 | New_Event | UG Cable Fault | Include | Include | Equipment | 797 | 2021-07-13 | 71730 | keep | 0 | Jul | 2021 | 0.048855 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2021-07-13 03:02 | 2021-07-13 03:03 | 2708 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | R21071300005 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-07-13 | 2708 | keep | 0 | Jul | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2021-07-13 03:15 | 2021-07-13 03:16 | 2708 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | R21071300005 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-07-13 | 2708 | keep | 0 | Jul | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CAGUAS | 2021-07-13 04:49 | 2021-07-13 12:53 | 80 | 008:04 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21071300009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 484 | 2021-07-13 | 38720 | keep | 0 | Jul | 2021 | 0.026372 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-07-13 05:17 | 2021-07-13 10:39 | 65 | 005:22 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE NECESITA REALIZAR DESGANCHE EN EL AREA | B21071300010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 322 | 2021-07-13 | 20930 | keep | 0 | Jul | 2021 | 0.014255 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
CANOVANAS | 2021-07-13 05:49 | 2021-07-13 06:05 | 2708 | 000:16 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRADO ELECTRICAMENTE NO RTU | R21071300005 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 16 | 2021-07-13 | 43328 | keep | 0 | Jul | 2021 | 0.029511 | 0.0018444 | Sustained | FALSE | FALSE | Not_TMED_Event | 2708
MAYAGÃœEZ | 2021-07-13 06:00 | 2021-07-13 14:05 | 30 | 008:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR FUERTES VIENTOS | M21071300000 | New_Event | Bad Weather | Include | Include | Weather | 485 | 2021-07-13 | 14550 | keep | 0 | Jul | 2021 | 0.0099099 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
AGUADILLA | 2021-07-13 06:00 | 2021-07-13 12:00 | 15 | 006:00 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA X 50 KVA | M21071300000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 360 | 2021-07-13 | 5400 | keep | 0 | Jul | 2021 | 0.0036779 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2021-07-13 06:00 | 2021-07-13 14:36 | 12 | 008:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21071300000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 516 | 2021-07-13 | 6192 | keep | 0 | Jul | 2021 | 0.0042173 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2021-07-13 06:11 | 2021-07-13 10:59 | 99 | 004:48 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA SE PATRULLO | C21071300004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 288 | 2021-07-13 | 28512 | keep | 0 | Jul | 2021 | 0.019419 | 6.7428e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 99
BARRANQUITAS | 2021-07-13 06:13 | 2021-07-13 11:23 | 100 | 005:10 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21071300005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 310 | 2021-07-13 | 31000 | keep | 0 | Jul | 2021 | 0.021114 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-07-13 06:21 | 2021-07-13 09:50 | 50 | 003:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 25 EN CORTE DE LINEA SE REEMPLAZARON DOS CAJAS PRIMARIAS DEFECTUOSAS | A21071300007 | New_Event | Cutout Failure | Include | Include | Equipment | 209 | 2021-07-13 | 10450 | keep | 0 | Jul | 2021 | 0.0071174 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-07-13 06:39 | 2021-07-13 11:00 | 10 | 004:21 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO 25 X 25KVA | B21071300013 | New_Event | Service Transformer Failure | Include | Include | Equipment | 261 | 2021-07-13 | 2610 | keep | 0 | Jul | 2021 | 0.0017777 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-07-13 06:42 | 2021-07-13 06:43 | 2450 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C21071300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-13 | 2450 | keep | 0 | Jul | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
ARECIBO | 2021-07-13 07:04 | 2021-07-13 12:45 | 100 | 005:41 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | A21071300009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 341 | 2021-07-13 | 34100 | keep | 0 | Jul | 2021 | 0.023225 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-07-13 07:09 | 2021-07-13 12:10 | 100 | 005:01 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA DESGANCHE | M21071300011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 301 | 2021-07-13 | 30100 | keep | 0 | Jul | 2021 | 0.020501 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-07-13 07:11 | 2021-07-13 10:22 | 2708 | 003:11 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO | R21071300000 | Partial_restoration | Wire Down | Include | Include | Equipment | 191 | 2021-07-13 | 517228 | keep | 0 | Jul | 2021 | 0.35228 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-13 07:16 | 2021-07-14 11:16 | 15 | 028:00 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | S21071300037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1680 | 2021-07-13 | 25200 | keep | 0 | Jul | 2021 | 0.017164 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
GUAYAMA | 2021-07-13 07:19 | 2021-07-13 09:40 | 135 | 002:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA | P21071300007 | New_Event |  |  | Include | Wildlife | 141 | 2021-07-13 | 19035 | keep | 0 | Jul | 2021 | 0.012965 | 9.1948e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 135
ARECIBO | 2021-07-13 07:19 | 2021-07-13 12:00 | 25 | 004:41 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 20 EN CORTE DE LINEA SE REEMPLAZARON AISLADORES PARTIDOS | A21071300010 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 281 | 2021-07-13 | 7025 | keep | 0 | Jul | 2021 | 0.0047847 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-07-13 07:22 | 2021-07-13 07:23 | 492 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21071300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-13 | 492 | keep | 0 | Jul | 2021 | 0.0003351 | 0.0003351 | Momentary | FALSE | FALSE | Not_TMED_Event | 492
BAYAMON | 2021-07-13 07:23 | 2021-07-13 18:01 | 1 | 010:38 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU 212 | B21071300050 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 638 | 2021-07-13 | 638 | keep | 0 | Jul | 2021 | 0.00043454 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-07-13 07:43 | 2021-07-13 18:35 | 5 | 010:52 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER Y 1 X 20 EN SU-2 | R21071300032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 652 | 2021-07-13 | 3260 | keep | 0 | Jul | 2021 | 0.0022204 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2021-07-13 07:44 | 2021-07-13 09:31 | 70 | 001:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A21071300014 | New_Event | Bad Weather | Include | Include | Weather | 107 | 2021-07-13 | 7490 | keep | 0 | Jul | 2021 | 0.0051014 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
PONCE | 2021-07-13 08:05 | 2021-07-13 12:05 | 116 | 004:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA | P21071200068 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 240 | 2021-07-13 | 27840 | keep | 0 | Jul | 2021 | 0.018962 | 7.9007e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 116
CAGUAS | 2021-07-13 08:06 | 2021-07-13 14:48 | 50 | 006:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C21071300036 | New_Event |  |  | Include | Wildlife | 402 | 2021-07-13 | 20100 | keep | 0 | Jul | 2021 | 0.01369 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-13 08:07 | 2021-07-13 14:57 | 313 | 006:50 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S21071300064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 410 | 2021-07-13 | 128330 | keep | 0 | Jul | 2021 | 0.087405 | 0.00021318 | Sustained | FALSE | TRUE | Not_TMED_Event | 313
SAN JUAN | 2021-07-13 08:12 | 2021-07-13 08:13 | 5779 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04 QUE A SU VEZ LLEVA LA CARGA PARCIAL DE LOS ALIMENTADORES 1336-07 UN 90% Y 1336-10 UN 85% | S21071200378 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-13 | 5779 | keep | 0 | Jul | 2021 | 0.0039361 | 0.0039361 | Momentary | FALSE | FALSE | Not_TMED_Event | 5779
SAN JUAN | 2021-07-13 08:12 | 2021-07-13 08:13 | 342 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04 QUE A SU VEZ LLEVA LA CARGA PARCIAL DE LOS ALIMENTADORES 1336-07 UN 90% Y 1336-10 UN 85% | S21071200378 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-13 | 342 | keep | 0 | Jul | 2021 | 0.00023293 | 0.00023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 342
SAN JUAN | 2021-07-13 08:12 | 2021-07-13 08:13 | 172 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04 QUE A SU VEZ LLEVA LA CARGA PARCIAL DE LOS ALIMENTADORES 1336-07 UN 90% Y 1336-10 UN 85% | S21071200378 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-13 | 172 | keep | 0 | Jul | 2021 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
HUMACAO | 2021-07-13 08:30 | 2021-07-13 14:11 | 1 | 005:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN BANCO DE TRANSFORMADORES REPARO SECUNDARIA | C21071300015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 341 | 2021-07-13 | 341 | keep | 0 | Jul | 2021 | 0.00023225 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-07-13 08:38 | 2021-07-13 11:18 | 1 | 002:40 | P | NO SE REPORTO CAUSA | 2 X 15 EN TRANSFORMADOR SE INSPECCIONO | C21071300016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 160 | 2021-07-13 | 160 | keep | 0 | Jul | 2021 | 0.00010898 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-07-13 08:41 | 2021-07-13 08:42 | 2697 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR MAL TIEMPO | A21071300000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-13 | 2697 | keep | 0 | Jul | 2021 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
ARECIBO | 2021-07-13 08:43 | 2021-07-13 14:30 | 200 | 005:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA | A21071300029 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 347 | 2021-07-13 | 69400 | keep | 0 | Jul | 2021 | 0.047268 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
AGUADILLA | 2021-07-13 08:45 | 2021-07-13 08:46 | 3041 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M21071300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-13 | 3041 | keep | 0 | Jul | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2021-07-13 08:46 | 2021-07-14 16:16 | 80 | 031:30 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | M21071300076 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1890 | 2021-07-13 | 151200 | keep | 0 | Jul | 2021 | 0.10298 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
VEGA BAJA | 2021-07-13 08:46 | 2021-07-13 17:28 | 1 | 008:42 | P | OTRAS CAUSAS | 2 X 50 EN CORTE DE LINEA Y 2 X 15 EN RISER SE REALIZO BYPASS A EQUIPOS DE MEDICION | B21071300027 | New_Event | Other Causes | Include | Include | Other | 522 | 2021-07-13 | 522 | keep | 0 | Jul | 2021 | 0.00035553 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-07-13 08:48 | 2021-07-13 11:42 | 35 | 002:54 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21071300084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2021-07-13 | 6090 | keep | 0 | Jul | 2021 | 0.0041479 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
SAN JUAN | 2021-07-13 08:49 | 2021-07-13 08:50 | 4291 | 000:01 | T | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR 1303-02 QUE A SU VEZ LLEVA LA CARGA PARCIAL DE LOS ALIMENTADORES 1346-05 60% Y 1204-02 100% SE CERRO POR SCADA | S21071200000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-07-13 | 4291 | keep | 0 | Jul | 2021 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
SAN JUAN | 2021-07-13 08:49 | 2021-07-13 08:50 | 2435 | 000:01 | T | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR 1303-02 QUE A SU VEZ LLEVA LA CARGA PARCIAL DE LOS ALIMENTADORES 1346-05 60% Y 1204-02 100% SE CERRO POR SCADA | S21071200000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-07-13 | 2435 | keep | 0 | Jul | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2021-07-13 08:49 | 2021-07-13 08:50 | 600 | 000:01 | P | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR 1303-02 QUE A SU VEZ LLEVA LA CARGA PARCIAL DE LOS ALIMENTADORES 1346-05 60% Y 1204-02 100% | S21071200000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-07-13 | 600 | keep | 0 | Jul | 2021 | 0.00040866 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
BAYAMON | 2021-07-13 09:05 | 2021-07-13 09:06 | 2617 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21071300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-13 | 2617 | keep | 0 | Jul | 2021 | 0.0017824 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
PONCE | 2021-07-13 09:10 | 2021-07-13 10:30 | 615 | 001:20 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRE RISER PARA FIJAR AISLADOR | P21071300019 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 80 | 2021-07-13 | 49200 | keep | 0 | Jul | 2021 | 0.03351 | 0.00041887 | Sustained | FALSE | FALSE | Not_TMED_Event | 615
MAYAGÃœEZ | 2021-07-13 09:16 | 2021-07-13 19:00 | 12 | 009:44 | P | CABLE SOTERRADO AVERIADO | SE REEMPLAZO CABLE SOTERRADO AVERIADO | M21071200381 | New_Event | UG Cable Fault | Include | Include | Equipment | 584 | 2021-07-13 | 7008 | keep | 0 | Jul | 2021 | 0.0047731 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2021-07-13 09:21 | 2021-07-13 14:18 | 30 | 004:57 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21071300022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 297 | 2021-07-13 | 8910 | keep | 0 | Jul | 2021 | 0.0060686 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-07-13 09:23 | 2021-07-13 15:39 | 15 | 006:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA SE RETIRO AVE CRUZANDO LINEAS | B21071300032 | New_Event |  |  | Include | Wildlife | 376 | 2021-07-13 | 5640 | keep | 0 | Jul | 2021 | 0.0038414 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-07-13 09:29 | 2021-07-13 15:57 | 80 | 006:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADORES ROTOS EN LINEA PRIMARIA | M21071300049 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 388 | 2021-07-13 | 31040 | keep | 0 | Jul | 2021 | 0.021141 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-07-13 09:32 | 2021-07-13 09:33 | 199 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21071300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-13 | 199 | keep | 0 | Jul | 2021 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
VEGA BAJA | 2021-07-13 09:36 | 2021-07-14 17:08 | 20 | 031:32 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21071300055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1892 | 2021-07-13 | 37840 | keep | 0 | Jul | 2021 | 0.025773 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-07-13 09:38 | 2021-07-13 13:40 | 100 | 004:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA POR PAJARO QUE CRUZO LINEAS | A21071300031 | New_Event |  |  | Include | Wildlife | 242 | 2021-07-13 | 24200 | keep | 0 | Jul | 2021 | 0.016483 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-07-13 09:40 | 2021-07-13 11:04 | 100 | 001:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | C21071300024 | New_Event |  |  | Include | Wildlife | 84 | 2021-07-13 | 8400 | keep | 0 | Jul | 2021 | 0.0057212 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-13 09:48 | 2021-07-13 09:49 | 1935 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA NO RECERRO | B21071300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-13 | 1935 | keep | 0 | Jul | 2021 | 0.0013179 | 0.0013179 | Momentary | FALSE | FALSE | Not_TMED_Event | 1935
SAN JUAN | 2021-07-13 09:49 | 2021-07-13 16:21 | 40 | 006:32 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REEMPLAZAR POSTE AVERIADO | R21071300079 | New_Event | Defective Pole | Include | Include | Equipment | 392 | 2021-07-13 | 15680 | keep | 0 | Jul | 2021 | 0.01068 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-07-13 09:55 | 2021-07-13 09:56 | 29 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21071300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-13 | 29 | keep | 0 | Jul | 2021 | 1.9752e-05 | 1.9752e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 29
PONCE | 2021-07-13 10:00 | 2021-07-13 10:43 | 16 | 000:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REMPLAZO DE LINEA SECUNDARIA | P21071300022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 43 | 2021-07-13 | 688 | keep | 0 | Jul | 2021 | 0.00046859 | 1.0898e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 16
MAYAGÃœEZ | 2021-07-13 10:12 | 2021-07-13 16:58 | 25 | 006:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA AVERIADA | M21071300061 | New_Event | Wire Down | Include | Include | Equipment | 406 | 2021-07-13 | 10150 | keep | 0 | Jul | 2021 | 0.0069131 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CANOVANAS | 2021-07-13 10:22 | 2021-07-13 19:45 | 700 | 009:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO Y REEMPLAZO AISLADOR | R21071300000 | New_Event | Wire Down | Include | Include | Equipment | 563 | 2021-07-13 | 394100 | keep | 0 | Jul | 2021 | 0.26842 | 0.00047677 | Sustained | FALSE | FALSE | Not_TMED_Event | 700
YAUCO | 2021-07-13 10:28 | 2021-07-13 10:37 | 50 | 000:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X DE 50 EN CORTE DE LINEA MAL TIEMPO | P21071300011 | New_Event | Bad Weather | Include | Include | Weather | 9 | 2021-07-13 | 450 | keep | 0 | Jul | 2021 | 0.00030649 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-13 10:38 | 2021-07-13 13:03 | 10 | 002:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE CERRO SECUNDARIA ABIERTA | S21071200339 | New_Event | Secondary Wire Down | Include | Include | Equipment | 145 | 2021-07-13 | 1450 | keep | 0 | Jul | 2021 | 0.00098759 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-07-13 11:00 | 2021-07-13 11:47 | 68 | 000:47 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | P21071300053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 47 | 2021-07-13 | 3196 | keep | 0 | Jul | 2021 | 0.0021768 | 4.6314e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 68
MAYAGÃœEZ | 2021-07-13 11:14 | 2021-07-13 11:15 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21071300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-13 | 393 | keep | 0 | Jul | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
BAYAMON | 2021-07-13 11:28 | 2021-07-16 12:52 | 12 | 073:24 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO DE T-117 A T-116 | B21071400187 | New_Event | UG Cable Fault | Include | Include | Equipment | 4404 | 2021-07-13 | 52848 | keep | 0 | Jul | 2021 | 0.035995 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-07-13 11:38 | 2021-07-13 15:30 | 100 | 003:52 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO Y SE REPARO LINEA PARTIDA | M21071300086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2021-07-13 | 23200 | keep | 0 | Jul | 2021 | 0.015801 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-07-13 11:42 | 2021-07-13 15:30 | 40 | 003:48 | P | DESGANCHE | 1 X 30 EN CORTE DE LINE | A21071300057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2021-07-13 | 9120 | keep | 0 | Jul | 2021 | 0.0062116 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-07-13 11:50 | 2021-07-13 18:28 | 60 | 006:38 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S21071200052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 398 | 2021-07-13 | 23880 | keep | 0 | Jul | 2021 | 0.016265 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-07-13 11:51 | 2021-07-13 13:42 | 12 | 001:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 15 EN TRANSFORMADOR SE REEMPLAZARON CAJAS PRIMARIAS DEFECTUOSAS | A21071300059 | New_Event | Cutout Failure | Include | Include | Equipment | 111 | 2021-07-13 | 1332 | keep | 0 | Jul | 2021 | 0.00090722 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-07-13 12:07 | 2021-07-13 12:57 | 100 | 000:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES Y SE CERRO PUENTE DE LINEA A MACHETE | B21071200200 | Additional_clients | Wire Down | Include | Include | Equipment | 50 | 2021-07-13 | 5000 | keep | 0 | Jul | 2021 | 0.0034055 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CANOVANAS | 2021-07-13 12:28 | 2021-07-14 09:29 | 24 | 021:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA CRUCE CON AVE | R21071300088 | New_Event |  |  | Include | Wildlife | 1261 | 2021-07-13 | 30264 | keep | 0 | Jul | 2021 | 0.020613 | 1.6346e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 24
BAYAMON | 2021-07-13 13:07 | 2021-07-13 20:28 | 5 | 007:21 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S21071200072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 441 | 2021-07-13 | 2205 | keep | 0 | Jul | 2021 | 0.0015018 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-07-13 13:13 | 2021-07-13 13:18 | 1863 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P21071300062 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-07-13 | 9315 | keep | 0 | Jul | 2021 | 0.0063444 | 0.0012689 | Momentary | FALSE | TRUE | Not_TMED_Event | 1863
PONCE | 2021-07-13 13:13 | 2021-07-13 13:18 | 708 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P21071300062 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-07-13 | 3540 | keep | 0 | Jul | 2021 | 0.0024111 | 0.00048222 | Momentary | FALSE | TRUE | Not_TMED_Event | 708
YAUCO | 2021-07-13 13:13 | 2021-07-13 13:18 | 502 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P21071300062 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-07-13 | 2510 | keep | 0 | Jul | 2021 | 0.0017095 | 0.00034191 | Momentary | FALSE | TRUE | Not_TMED_Event | 502
YAUCO | 2021-07-13 13:13 | 2021-07-13 13:18 | 2747 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P21071300062 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-07-13 | 13735 | keep | 0 | Jul | 2021 | 0.0093548 | 0.001871 | Momentary | FALSE | TRUE | Not_TMED_Event | 2747
YAUCO | 2021-07-13 13:13 | 2021-07-13 13:18 | 1587 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P21071300062 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-07-13 | 7935 | keep | 0 | Jul | 2021 | 0.0054045 | 0.0010809 | Momentary | FALSE | TRUE | Not_TMED_Event | 1587
YAUCO | 2021-07-13 13:13 | 2021-07-13 13:18 | 2671 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P21071300062 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-07-13 | 13355 | keep | 0 | Jul | 2021 | 0.009096 | 0.0018192 | Momentary | FALSE | TRUE | Not_TMED_Event | 2671
YAUCO | 2021-07-13 13:13 | 2021-07-13 13:18 | 508 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P21071300062 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-07-13 | 2540 | keep | 0 | Jul | 2021 | 0.00173 | 0.000346 | Momentary | FALSE | TRUE | Not_TMED_Event | 508
YAUCO | 2021-07-13 13:13 | 2021-07-13 13:18 | 64 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P21071300062 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-07-13 | 320 | keep | 0 | Jul | 2021 | 0.00021795 | 4.359e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 64
PONCE | 2021-07-13 13:13 | 2021-07-13 15:28 | 200 | 002:15 | P | SOBRECARGA | 1 X 200 CORTE DE LINEA POR CARGA | P21071300004 | New_Event | Trip Due To Overload | Include | Include | Other | 135 | 2021-07-13 | 27000 | keep | 0 | Jul | 2021 | 0.01839 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-07-13 13:19 | 2021-07-13 13:21 | 3654 | 000:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR NO RECERRO CON RECIERRE EN ON | A21071300000 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2021-07-13 | 7308 | keep | 0 | Jul | 2021 | 0.0049774 | 0.0024887 | Momentary | FALSE | FALSE | Not_TMED_Event | 3654
ARECIBO | 2021-07-13 13:21 | 2021-07-13 19:51 | 3654 | 006:30 | T | DESCONECTIVO DEFECTUOSO | SE PASO CARGA AL 8404-2 MACHETES DEFECTUOSO | A21071300000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 390 | 2021-07-13 | 1425060 | keep | 0 | Jul | 2021 | 0.9706 | 0.0024887 | Sustained | FALSE | FALSE | Not_TMED_Event | 3654
CAGUAS | 2021-07-13 13:26 | 2021-07-13 19:21 | 662 | 005:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 Y 2 X 100 EN CORTES DE LINEA SE REEMPLAZO CAJA PRIMARIA | C21071300058 | New_Event | Cutout Failure | Include | Include | Equipment | 355 | 2021-07-13 | 235010 | keep | 0 | Jul | 2021 | 0.16006 | 0.00045089 | Sustained | FALSE | TRUE | Not_TMED_Event | 662
ARECIBO | 2021-07-13 13:30 | 2021-07-13 23:48 | 150 | 010:18 | P | ESTRUCTURA AVERIADA | 2 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y SE REMPLAZO POSTE PRIMARIO | A21071300164 | New_Event | Defective Pole | Include | Include | Equipment | 618 | 2021-07-13 | 92700 | keep | 0 | Jul | 2021 | 0.063138 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-07-13 13:31 | 2021-07-13 22:10 | 15 | 008:39 | P | SECUNDARIA/ESTRUCTURA AVERIADA | 2 X 15 EN TRANSFORMADOR SE REMPLAZO POSTE SECUNDARIO PARTIDO | A21071300071 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 519 | 2021-07-13 | 7785 | keep | 0 | Jul | 2021 | 0.0053023 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-07-13 13:34 | 2021-07-13 15:56 | 10 | 002:22 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | R21071300100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 142 | 2021-07-13 | 1420 | keep | 0 | Jul | 2021 | 0.00096716 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
HUMACAO | 2021-07-13 13:40 | 2021-07-13 19:24 | 40 | 005:44 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21071300048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 344 | 2021-07-13 | 13760 | keep | 0 | Jul | 2021 | 0.0093719 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
AGUADILLA | 2021-07-13 13:41 | 2021-07-14 17:00 | 20 | 027:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE | M21071300112 | New_Event | Wire Down | Include | Include | Equipment | 1639 | 2021-07-13 | 32780 | keep | 0 | Jul | 2021 | 0.022326 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-07-13 14:20 | 2021-07-13 16:46 | 40 | 002:26 | P | DESGANCHE | ABRIO CORTE DE LINEA PARA DESGANCHAR Y REPARAR CONDUCTOR PRIMARIO WR 5888925 | C21071300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2021-07-13 | 5840 | keep | 0 | Jul | 2021 | 0.0039776 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-07-13 14:40 | 2021-07-14 09:49 | 70 | 019:09 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | S21071300087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1149 | 2021-07-13 | 80430 | keep | 0 | Jul | 2021 | 0.054781 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BAYAMON | 2021-07-13 14:40 | 2021-07-13 15:50 | 12 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA LEVANTAR SECUNDARIA | S21071200001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2021-07-13 | 840 | keep | 0 | Jul | 2021 | 0.00057212 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-07-13 14:55 | 2021-07-13 18:08 | 40 | 003:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR REMPLAZO CAJA Y PARARRAYO | C21071300051 | New_Event | Cutout Failure | Include | Include | Equipment | 193 | 2021-07-13 | 7720 | keep | 0 | Jul | 2021 | 0.0052581 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-07-13 14:57 | 2021-07-13 17:40 | 60 | 002:43 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | A21071300106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2021-07-13 | 9780 | keep | 0 | Jul | 2021 | 0.0066611 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
AGUADILLA | 2021-07-13 14:58 | 2021-07-13 16:44 | 50 | 001:46 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADORES ROTOS | M21071300124 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 106 | 2021-07-13 | 5300 | keep | 0 | Jul | 2021 | 0.0036098 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-07-13 15:05 | 2021-07-13 15:07 | 5779 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04 CON RECIERRE EN OFF LLEVA 90% DEL 1336-7 Y 85% DEL 1336-10 SE PROBO QUEDO EN SERVICIO | S21071300142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-13 | 11558 | keep | 0 | Jul | 2021 | 0.0078721 | 0.0039361 | Momentary | FALSE | FALSE | Not_TMED_Event | 5779
SAN JUAN | 2021-07-13 15:05 | 2021-07-13 15:07 | 342 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04 CON RECIERRE EN OFF LLEVA 90% DEL 1336-7 Y 85% DEL 1336-10 SE PROBO QUEDO EN SERVICIO | S21071300142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-13 | 684 | keep | 0 | Jul | 2021 | 0.00046587 | 0.00023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 342
SAN JUAN | 2021-07-13 15:05 | 2021-07-13 15:07 | 172 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON RECIERRE EN OFF LLEVA 90% DEL 1336-7 Y 85% DEL 1336-10 SE PROBO QUEDO EN SERVICIO | S21071300142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-13 | 344 | keep | 0 | Jul | 2021 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2021-07-13 15:11 | 2021-07-14 11:00 | 68 | 019:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 100 EN CORTE DE LINEA Y SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | S21071300145 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1189 | 2021-07-13 | 80852 | keep | 0 | Jul | 2021 | 0.055068 | 4.6314e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 68
UTUADO | 2021-07-13 15:13 | 2021-07-14 11:10 | 12 | 019:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | A21071300115 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1197 | 2021-07-13 | 14364 | keep | 0 | Jul | 2021 | 0.0097833 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
UTUADO | 2021-07-13 15:15 | 2021-07-13 18:00 | 15 | 002:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | A21071300000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 165 | 2021-07-13 | 2475 | keep | 0 | Jul | 2021 | 0.0016857 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-07-13 15:43 | 2021-07-14 13:18 | 50 | 021:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MUCHA LLUVIA | B21071300047 | New_Event | Bad Weather | Include | Include | Weather | 1295 | 2021-07-13 | 64750 | keep | 0 | Jul | 2021 | 0.044101 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-13 15:45 | 2021-07-14 10:46 | 30 | 019:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S21071300148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1141 | 2021-07-13 | 34230 | keep | 0 | Jul | 2021 | 0.023314 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-07-13 15:47 | 2021-07-13 20:56 | 60 | 005:09 | P | CABLE SOTERRADO AVERIADO | 1 X 65 EN CORTE DE LINEA Y 1 X 40 EN CORTE DE LINEA HAY AVERIA DE T 32 A T 31 | B21071300049 | New_Event | UG Cable Fault | Include | Include | Equipment | 309 | 2021-07-13 | 18540 | keep | 0 | Jul | 2021 | 0.012628 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-07-13 15:55 | 2021-07-13 17:40 | 40 | 001:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CLIENTES DESGANCHANDO | C21071300053 | New_Event |  |  | Include | Wildlife | 105 | 2021-07-13 | 4200 | keep | 0 | Jul | 2021 | 0.0028606 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-13 15:57 | 2021-07-13 15:58 | 1420 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR 1530-06 | S21071300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-13 | 1420 | keep | 0 | Jul | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-07-13 15:57 | 2021-07-13 15:58 | 437 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1526-2 | S21071300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-13 | 437 | keep | 0 | Jul | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
PONCE | 2021-07-13 16:00 | 2021-07-13 18:55 | 25 | 002:55 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | P210713000XX | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2021-07-13 | 4375 | keep | 0 | Jul | 2021 | 0.0029798 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
AGUADILLA | 2021-07-13 16:00 | 2021-07-13 17:30 | 30 | 001:30 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21071100119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2021-07-13 | 2700 | keep | 0 | Jul | 2021 | 0.001839 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-07-13 16:05 | 2021-07-14 19:16 | 75 | 027:11 | P | DESGANCHE | 1 X 50 Y 1 X 65 EN CORTE DE LINEA | M21071300143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1631 | 2021-07-13 | 122325 | keep | 0 | Jul | 2021 | 0.083315 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
MAYAGÃœEZ | 2021-07-13 16:09 | 2021-07-15 16:53 | 60 | 048:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | M21071300144 | New_Event | Wire Down | Include | Include | Equipment | 2924 | 2021-07-13 | 175440 | keep | 0 | Jul | 2021 | 0.11949 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
YAUCO | 2021-07-13 16:12 | 2021-07-14 12:39 | 50 | 020:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE FIJO BAJANTE PRIMARIO A CAJA DE TRANSFORMADOR | P21071300085 | New_Event | Wire Down | Include | Include | Equipment | 1227 | 2021-07-13 | 61350 | keep | 0 | Jul | 2021 | 0.041785 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-13 16:14 | 2021-07-16 11:40 | 8 | 067:26 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR AVERIADO DE 50KVA X 50KVA | C21071300112 | New_Event | Service Transformer Failure | Include | Include | Equipment | 4046 | 2021-07-13 | 32368 | keep | 0 | Jul | 2021 | 0.022046 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-07-13 16:19 | 2021-07-16 17:48 | 10 | 073:29 | P | CABLE SOTERRADO AVERIADO | 1 X 10 EN TRANSFORMADOR CONSTRUYO AEREO PROVISIONAL DEL T - 4 AL T - 5 | R21071400033 | New_Event | UG Cable Fault | Include | Include | Equipment | 4409 | 2021-07-13 | 44090 | keep | 0 | Jul | 2021 | 0.030029 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-07-13 16:30 | 2021-07-13 19:50 | 100 | 003:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | S21071300055 | New_Event | Cutout Failure | Include | Include | Equipment | 200 | 2021-07-13 | 20000 | keep | 0 | Jul | 2021 | 0.013622 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
GUAYAMA | 2021-07-13 16:41 | 2021-07-13 16:42 | 1945 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO OPERO RECIERRE | P21071200087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-13 | 1945 | keep | 0 | Jul | 2021 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
PONCE | 2021-07-13 16:41 | 2021-07-13 16:42 | 100 | 000:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | P21071200073 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-07-13 | 100 | keep | 0 | Jul | 2021 | 6.811e-05 | 6.811e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-07-13 16:44 | 2021-07-14 13:35 | 45 | 020:51 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M21071300151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1251 | 2021-07-13 | 56295 | keep | 0 | Jul | 2021 | 0.038342 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BARRANQUITAS | 2021-07-13 16:59 | 2021-07-13 17:00 | 1364 | 000:01 | T | DESGANCHE | RECIERRE | C21071300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-13 | 1364 | keep | 0 | Jul | 2021 | 0.00092901 | 0.00092901 | Momentary | FALSE | FALSE | Not_TMED_Event | 1364
BARRANQUITAS | 2021-07-13 17:00 | 2021-07-13 18:10 | 55 | 001:10 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21071300054 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 70 | 2021-07-13 | 3850 | keep | 0 | Jul | 2021 | 0.0026222 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
FAJARDO | 2021-07-13 17:15 | 2021-07-13 17:16 | 1394 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | R21071300000 | New_Event |  |  | Include | Wildlife | 1 | 2021-07-13 | 1394 | keep | 0 | Jul | 2021 | 0.00094945 | 0.00094945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1394
FAJARDO | 2021-07-13 17:16 | 2021-07-13 19:58 | 30 | 002:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA CRUCE POR AVE | R21071300116 | 1st_after_momentary |  |  | Include | Wildlife | 162 | 2021-07-13 | 4860 | keep | 0 | Jul | 2021 | 0.0033101 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-07-13 17:25 | 2021-07-14 11:51 | 50 | 018:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | A21071300159 | New_Event | Wire Down | Include | Include | Equipment | 1106 | 2021-07-13 | 55300 | keep | 0 | Jul | 2021 | 0.037665 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-13 17:36 | 2021-07-13 17:37 | 2179 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21071300118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-13 | 2179 | keep | 0 | Jul | 2021 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
BAYAMON | 2021-07-13 17:37 | 2021-07-13 20:30 | 40 | 002:53 | P | HERRAJE ROTO O PODRIDO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CRUCETA PARTIDA SE REMPLAZO CAJA QUEMADA SE REMPLAZO SECUNDARIA Y SE REALIZO DESGANCHE | S21071300163 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 173 | 2021-07-13 | 6920 | keep | 0 | Jul | 2021 | 0.0047132 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-07-13 18:03 | 2021-07-14 11:42 | 15 | 017:39 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | M21071300177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1059 | 2021-07-13 | 15885 | keep | 0 | Jul | 2021 | 0.010819 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
SAN JUAN | 2021-07-13 18:21 | 2021-07-14 08:56 | 50 | 014:35 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21071300147 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 875 | 2021-07-13 | 43750 | keep | 0 | Jul | 2021 | 0.029798 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-13 19:00 | 2021-07-14 10:35 | 5 | 015:35 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA X 37.5 KVA | M21071200365 | New_Event | Service Transformer Failure | Include | Include | Equipment | 935 | 2021-07-13 | 4675 | keep | 0 | Jul | 2021 | 0.0031841 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-07-13 19:05 | 2021-07-14 18:22 | 20 | 023:17 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21071300060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1397 | 2021-07-13 | 27940 | keep | 0 | Jul | 2021 | 0.01903 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-07-13 19:21 | 2021-07-13 19:22 | 4369 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21071300056 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2021-07-13 | 4369 | keep | 0 | Jul | 2021 | 0.0029757 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-07-13 19:21 | 2021-07-13 19:22 | 1378 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21071300057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-13 | 1378 | keep | 0 | Jul | 2021 | 0.00093855 | 0.00093855 | Momentary | FALSE | FALSE | Not_TMED_Event | 1378
CAGUAS | 2021-07-13 19:22 | 2021-07-14 11:17 | 662 | 015:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 Y 2 X 100 EN CORTES DE LINEA SE REEMPLAZO CAJA PRIMARIA | C21071300058 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 955 | 2021-07-13 | 632210 | keep | 0 | Jul | 2021 | 0.4306 | 0.00045089 | Sustained | FALSE | TRUE | Not_TMED_Event | 662
BAYAMON | 2021-07-13 19:46 | 2021-07-14 12:22 | 10 | 016:36 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REPARO AISLACION PARTIDA | S21071300172 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 996 | 2021-07-13 | 9960 | keep | 0 | Jul | 2021 | 0.0067837 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-13 20:05 | 2021-07-13 22:34 | 60 | 002:29 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21071300064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 149 | 2021-07-13 | 8940 | keep | 0 | Jul | 2021 | 0.006089 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-07-13 20:12 | 2021-07-13 21:08 | 95 | 000:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR GLOBO DE HELIO | R21071300128 | New_Event |  |  | Include | Wildlife | 56 | 2021-07-13 | 5320 | keep | 0 | Jul | 2021 | 0.0036234 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
HUMACAO | 2021-07-13 20:13 | 2021-07-14 16:36 | 7 | 020:23 | P | OTRAS CAUSAS | 2 X 40 EN CORTE DE LINEA SE AJUSTARON MUELAS EN PULLOUT | C21071300068 | New_Event | Other Causes | Include | Include | Other | 1223 | 2021-07-13 | 8561 | keep | 0 | Jul | 2021 | 0.0058309 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-07-13 20:53 | 2021-07-14 16:59 | 3 | 020:06 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 15KVA X 15 KVA | M21071300191 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1206 | 2021-07-13 | 3618 | keep | 0 | Jul | 2021 | 0.0024642 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2021-07-13 21:03 | 2021-07-14 12:42 | 423 | 015:39 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN CORTES DE LINEA SE DESGANCHO Y REEMPLAZARON DISCO ROTO | C21071300078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 939 | 2021-07-13 | 397197 | keep | 0 | Jul | 2021 | 0.27053 | 0.0002881 | Sustained | FALSE | TRUE | Not_TMED_Event | 423
ARECIBO | 2021-07-13 21:47 | 2021-07-14 10:18 | 30 | 012:31 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA PARARRAYO | A21071300175 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 751 | 2021-07-13 | 22530 | keep | 0 | Jul | 2021 | 0.015345 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-07-13 23:08 | 2021-07-14 13:35 | 20 | 014:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 35 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | B21071300073 | New_Event | Cutout Failure | Include | Include | Equipment | 867 | 2021-07-13 | 17340 | keep | 0 | Jul | 2021 | 0.01181 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
AGUADILLA | 2021-07-13 23:13 | 2021-07-14 12:25 | 300 | 013:12 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | M21071300209 | New_Event | Vegetation Contact | Include | Include | Vegetation | 792 | 2021-07-13 | 237600 | keep | 0 | Jul | 2021 | 0.16183 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
CANOVANAS | 2021-07-13 23:14 | 2021-07-14 08:51 | 200 | 009:37 | P | DESGANCHE | 1 X 140 EN CORTE E LINEA | R21071300139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 577 | 2021-07-13 | 115400 | keep | 0 | Jul | 2021 | 0.078598 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-07-14 00:14 | 2021-07-14 10:05 | 10 | 009:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B21071400001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 591 | 2021-07-14 | 5910 | keep | 0 | Jul | 2021 | 0.0040253 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-14 01:43 | 2021-07-14 02:22 | 527 | 000:39 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO EL INTERRUPTOR 6404-4 POR SEGURIDAD A PETICION DE FELIX CASIANO PARA QUE LOS BOMBEROS APAGARAN FUEGO EL LA BASE DE TORRE DE LINEA 1600 CAUSADO POR GROUND DE POSTE ZAFADO HACIENDO CONTACTO CON EL ALIMENTADOR. ESTE ESTA LLEVANDO LA CARGA DEL 6404-3 | M21071400004 | New_Event | Wire Down | Include | Include | Equipment | 39 | 2021-07-14 | 20553 | keep | 0 | Jul | 2021 | 0.013999 | 0.00035894 | Sustained | FALSE | TRUE | Not_TMED_Event | 527
MAYAGÃœEZ | 2021-07-14 01:43 | 2021-07-14 02:22 | 671 | 000:39 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO EL INTERRUPTOR 6404-4 POR SEGURIDAD A PETICION DE FELIX CASIANO PARA QUE LOS BOMBEROS APAGARAN FUEGO EL LA BASE DE TORRE DE LINEA 1600 CAUSADO POR GROUND DE POSTE ZAFADO HACIENDO CONTACTO CON EL ALIMENTADOR. | M21071400004 | New_Event | Wire Down | Include | Include | Equipment | 39 | 2021-07-14 | 26169 | keep | 0 | Jul | 2021 | 0.017824 | 0.00045702 | Sustained | FALSE | TRUE | Not_TMED_Event | 671
HUMACAO | 2021-07-14 01:57 | 2021-07-14 01:59 | 2450 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C21071400002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-14 | 4900 | keep | 0 | Jul | 2021 | 0.0033374 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
PONCE | 2021-07-14 03:02 | 2021-07-14 03:03 | 449 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21071400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-14 | 449 | keep | 0 | Jul | 2021 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
MAYAGÃœEZ | 2021-07-14 03:26 | 2021-07-14 03:27 | 470 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21071400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-14 | 470 | keep | 0 | Jul | 2021 | 0.00032011 | 0.00032011 | Momentary | FALSE | FALSE | Not_TMED_Event | 470
BAYAMON | 2021-07-14 05:31 | 2021-07-14 05:32 | 5809 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO | B21071400000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-14 | 5809 | keep | 0 | Jul | 2021 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
CAGUAS | 2021-07-14 05:50 | 2021-07-14 05:51 | 598 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3800 | C21071400006 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-14 | 598 | keep | 0 | Jul | 2021 | 0.0004073 | 0.0004073 | Momentary | FALSE | TRUE | Not_TMED_Event | 598
CAGUAS | 2021-07-14 05:50 | 2021-07-14 05:51 | 2486 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3800 | C21071400007 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-14 | 2486 | keep | 0 | Jul | 2021 | 0.0016932 | 0.0016932 | Momentary | FALSE | TRUE | Not_TMED_Event | 2486
CAGUAS | 2021-07-14 05:50 | 2021-07-14 05:51 | 1403 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3800 | C21071400007 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-14 | 1403 | keep | 0 | Jul | 2021 | 0.00095558 | 0.00095558 | Momentary | FALSE | TRUE | Not_TMED_Event | 1403
CAGUAS | 2021-07-14 05:50 | 2021-07-14 05:51 | 1001 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3800 | C21071400007 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-14 | 1001 | keep | 0 | Jul | 2021 | 0.00068178 | 0.00068178 | Momentary | FALSE | TRUE | Not_TMED_Event | 1001
MAYAGÃœEZ | 2021-07-14 06:00 | 2021-07-14 17:00 | 100 | 011:00 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA DESGANCHE | M21071400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 660 | 2021-07-14 | 66000 | keep | 0 | Jul | 2021 | 0.044952 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-07-14 06:00 | 2021-07-14 18:30 | 35 | 012:30 | P | LINEA DE TRANSMISION 38KV | SE ABRIO CORTE DE LINEA PARA TRABAJOS DE LINEA 2700 | M21071400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 750 | 2021-07-14 | 26250 | keep | 0 | Jul | 2021 | 0.017879 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
AGUADILLA | 2021-07-14 06:00 | 2021-07-14 18:05 | 6 | 012:05 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25KVA QUEMADO X LO MISMO | M21071400000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 725 | 2021-07-14 | 4350 | keep | 0 | Jul | 2021 | 0.0029628 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-07-14 06:00 | 2021-07-14 18:44 | 1 | 012:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REPARO LINEA PRIMARIA PARTIDA POR VEHICULO PESADO | A21071400000 | New_Event |  |  | Include | Wildlife | 764 | 2021-07-14 | 764 | keep | 0 | Jul | 2021 | 0.00052036 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-07-14 06:00 | 2021-07-14 17:35 | 1 | 011:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE A CORTE DE LINEA PARTIDO | A21071400002 | New_Event | Wire Down | Include | Include | Equipment | 695 | 2021-07-14 | 695 | keep | 0 | Jul | 2021 | 0.00047336 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-07-14 06:10 | 2021-07-14 11:15 | 70 | 005:05 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M21071400013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 305 | 2021-07-14 | 21350 | keep | 0 | Jul | 2021 | 0.014541 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
SAN JUAN | 2021-07-14 06:17 | 2021-07-14 06:18 | 2782 | 000:01 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR SE CERRO POR CONTROL | S21071400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-14 | 2782 | keep | 0 | Jul | 2021 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
CANOVANAS | 2021-07-14 06:17 | 2021-07-14 12:18 | 100 | 006:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REEMPLAZARON DISCOS | R21071400008 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 361 | 2021-07-14 | 36100 | keep | 0 | Jul | 2021 | 0.024588 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-07-14 06:31 | 2021-07-14 06:32 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21071400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-14 | 1310 | keep | 0 | Jul | 2021 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
AGUADILLA | 2021-07-14 06:43 | 2021-07-14 06:44 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21071400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-14 | 1827 | keep | 0 | Jul | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2021-07-14 06:43 | 2021-07-14 06:44 | 1047 | 000:01 | T | NO SE REPORTO CAUSA | CARGA POR 7011-01 | M21071400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-14 | 1047 | keep | 0 | Jul | 2021 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
PONCE | 2021-07-14 06:46 | 2021-07-14 06:47 | 4035 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210814000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-14 | 4035 | keep | 0 | Jul | 2021 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
MAYAGÃœEZ | 2021-07-14 06:50 | 2021-07-14 06:51 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CERRADO POR SCADA | M21071400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-14 | 3458 | keep | 0 | Jul | 2021 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
MAYAGÃœEZ | 2021-07-14 07:12 | 2021-07-14 14:27 | 80 | 007:15 | P | LINEA DE TRANSMISION 38KV | SE ABRIO CORTE DE LINEA PARA TRABAJOS EN LINEA DE TRANSMISION | M21071400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 435 | 2021-07-14 | 34800 | keep | 0 | Jul | 2021 | 0.023702 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-07-14 07:13 | 2021-07-14 10:39 | 152 | 003:26 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | C21071400011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2021-07-14 | 31312 | keep | 0 | Jul | 2021 | 0.021326 | 0.00010353 | Sustained | FALSE | TRUE | Not_TMED_Event | 152
BAYAMON | 2021-07-14 07:16 | 2021-07-14 07:17 | 58 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21071400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-14 | 58 | keep | 0 | Jul | 2021 | 3.9504e-05 | 3.9504e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 58
MAYAGÃœEZ | 2021-07-14 07:18 | 2021-07-14 14:38 | 100 | 007:20 | P | LINEA DE TRANSMISION 38KV | SE ABRIO CORTE DE LINEA PARA TRABAJOS EN LINEA DE TRANSMISION | M21071400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 440 | 2021-07-14 | 44000 | keep | 0 | Jul | 2021 | 0.029968 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-07-14 07:21 | 2021-07-14 11:26 | 200 | 004:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80, 1 X 65 Y 1 X 20 EN CORTE DE LINEA CRUCE CON AVE | R21071400012 | New_Event |  |  | Include | Wildlife | 245 | 2021-07-14 | 49000 | keep | 0 | Jul | 2021 | 0.033374 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
PONCE | 2021-07-14 07:21 | 2021-07-14 11:05 | 80 | 003:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA, AVE CRUZO FASE. | P21071400003 | New_Event |  |  | Include | Wildlife | 224 | 2021-07-14 | 17920 | keep | 0 | Jul | 2021 | 0.012205 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-07-14 07:56 | 2021-07-14 17:05 | 200 | 009:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA REPARO ALAMBRE PARTIDO | M21071400023 | New_Event | Wire Down | Include | Include | Equipment | 549 | 2021-07-14 | 109800 | keep | 0 | Jul | 2021 | 0.074784 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-07-14 08:00 | 2021-07-14 12:20 | 60 | 004:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | A21071400017 | New_Event | Bad Weather | Include | Include | Weather | 260 | 2021-07-14 | 15600 | keep | 0 | Jul | 2021 | 0.010625 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
FAJARDO | 2021-07-14 08:08 | 2021-07-14 15:58 | 40 | 007:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA REMPLAZO CAJA QUEMADA | R21071400016 | New_Event | Cutout Failure | Include | Include | Equipment | 470 | 2021-07-14 | 18800 | keep | 0 | Jul | 2021 | 0.012805 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-07-14 08:09 | 2021-07-15 16:05 | 20 | 031:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R21071400017 | New_Event |  |  | Include | Wildlife | 1916 | 2021-07-14 | 38320 | keep | 0 | Jul | 2021 | 0.0261 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2021-07-14 08:16 | 2021-07-14 11:50 | 20 | 003:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21071400020 | New_Event | Bad Weather | Include | Include | Weather | 214 | 2021-07-14 | 4280 | keep | 0 | Jul | 2021 | 0.0029151 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-07-14 08:22 | 2021-07-14 13:50 | 80 | 005:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | A21071400022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 328 | 2021-07-14 | 26240 | keep | 0 | Jul | 2021 | 0.017872 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-07-14 08:40 | 2021-07-14 12:20 | 25 | 003:40 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA DESGANCHE | A21071400024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2021-07-14 | 5500 | keep | 0 | Jul | 2021 | 0.003746 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
PONCE | 2021-07-14 08:56 | 2021-07-15 20:00 | 89 | 035:04 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | P21071500005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2104 | 2021-07-14 | 187256 | keep | 0 | Jul | 2021 | 0.12754 | 6.0617e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 89
VEGA BAJA | 2021-07-14 08:56 | 2021-07-15 16:24 | 5 | 031:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO BAJANTE SECUNDARIO | B21071500008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1888 | 2021-07-14 | 9440 | keep | 0 | Jul | 2021 | 0.0064295 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-07-14 09:01 | 2021-07-15 15:59 | 10 | 030:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO DE LINEA A PARARRAYO | S21071400083 | New_Event | Wire Down | Include | Include | Equipment | 1858 | 2021-07-14 | 18580 | keep | 0 | Jul | 2021 | 0.012655 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-07-14 09:10 | 2021-07-14 17:06 | 1 | 007:56 | P | OTRAS CAUSAS | 1 X 30 EN CORTE DE LINEA POR PROBLEMA INTERNO | A21071400029 | New_Event | Other Causes | Include | Include | Other | 476 | 2021-07-14 | 476 | keep | 0 | Jul | 2021 | 0.0003242 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-07-14 09:16 | 2021-07-14 14:25 | 40 | 005:09 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL DE EXISTENTE A SU 3 | B21071400013 | New_Event | UG Cable Fault | Include | Include | Equipment | 309 | 2021-07-14 | 12360 | keep | 0 | Jul | 2021 | 0.0084183 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-07-14 09:22 | 2021-07-14 10:56 | 10 | 001:34 | P | OTRAS CAUSAS | SE ABRIO TRANSFORMADOR PARA REPARAR ALUMBRADO AVERIADO AL TRABAJAR EN PROVISIONAL AEREO | B21071400014 | New_Event | Other Causes | Include | Include | Other | 94 | 2021-07-14 | 940 | keep | 0 | Jul | 2021 | 0.00064023 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-07-14 09:27 | 2021-07-14 20:20 | 1 | 010:53 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | R21071400026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 653 | 2021-07-14 | 653 | keep | 0 | Jul | 2021 | 0.00044476 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-07-14 09:47 | 2021-07-14 09:48 | 1105 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | A21071400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-14 | 1105 | keep | 0 | Jul | 2021 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
SAN JUAN | 2021-07-14 09:48 | 2021-07-16 10:19 | 7 | 048:31 | P | NO SE REPORTO CAUSA | 1 X 20 EN BANCO DE TRANSFORMADOR | R21071400029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2911 | 2021-07-14 | 20377 | keep | 0 | Jul | 2021 | 0.013879 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2021-07-14 09:52 | 2021-07-14 18:54 | 1 | 009:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 8 EN BANCO DE TRANSFORMADORES CRUCE POR AVE | R21071400030 | New_Event |  |  | Include | Wildlife | 542 | 2021-07-14 | 542 | keep | 0 | Jul | 2021 | 0.00036915 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2021-07-14 09:57 | 2021-07-14 16:13 | 20 | 006:16 | P | ESTRUCTURA AVERIADA | SE ABRE CORTE DE LINEA DE EMERGENCIA PARA REMPLAZAR POSTE PRIMARIO PARTIDO | P210714000XX | New_Event | Defective Pole | Include | Include | Equipment | 376 | 2021-07-14 | 7520 | keep | 0 | Jul | 2021 | 0.0051218 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-07-14 10:04 | 2021-07-14 10:05 | 5 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21071400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-14 | 5 | keep | 0 | Jul | 2021 | 3.4055e-06 | 3.4055e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-07-14 10:04 | 2021-07-14 10:05 | 1702 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR | C21071400039 | New_Event |  |  | Include | Wildlife | 1 | 2021-07-14 | 1702 | keep | 0 | Jul | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2021-07-14 10:05 | 2021-07-14 16:21 | 109 | 006:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C21071400061 | 1st_after_momentary |  |  | Include | Wildlife | 376 | 2021-07-14 | 40984 | keep | 0 | Jul | 2021 | 0.027914 | 7.4239e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 109
BAYAMON | 2021-07-14 10:14 | 2021-07-15 09:32 | 10 | 023:18 | P | NO SE REPORTO CAUSA | 1 X 20 EN MONTURA DE TRANSFORMADOR | S21071400041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1398 | 2021-07-14 | 13980 | keep | 0 | Jul | 2021 | 0.0095217 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-07-14 10:15 | 2021-07-14 15:00 | 125 | 004:45 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | A21071400045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 285 | 2021-07-14 | 35625 | keep | 0 | Jul | 2021 | 0.024264 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
BAYAMON | 2021-07-14 10:26 | 2021-07-14 10:27 | 1180 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21071400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-14 | 1180 | keep | 0 | Jul | 2021 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
MAYAGÃœEZ | 2021-07-14 10:35 | 2021-07-14 11:55 | 12 | 001:20 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REPARO CONEXIONES Y LINEA EN PM #16 | M21071400063 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 80 | 2021-07-14 | 960 | keep | 0 | Jul | 2021 | 0.00065385 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
BARRANQUITAS | 2021-07-14 10:47 | 2021-07-14 15:55 | 1 | 005:08 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN TRANSFORMADOR SE RETIRO ENREDADERA | C21071400048 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 308 | 2021-07-14 | 308 | keep | 0 | Jul | 2021 | 0.00020978 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-07-14 10:51 | 2021-07-14 18:45 | 562 | 007:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17900 | P21071400011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 474 | 2021-07-14 | 266388 | keep | 0 | Jul | 2021 | 0.18144 | 0.00038278 | Sustained | FALSE | TRUE | Not_TMED_Event | 562
PONCE | 2021-07-14 10:51 | 2021-07-14 18:45 | 688 | 007:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17900 | P21071400011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 474 | 2021-07-14 | 326112 | keep | 0 | Jul | 2021 | 0.22211 | 0.00046859 | Sustained | FALSE | TRUE | Not_TMED_Event | 688
PONCE | 2021-07-14 10:51 | 2021-07-14 18:45 | 658 | 007:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17900 | P21071400011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 474 | 2021-07-14 | 311892 | keep | 0 | Jul | 2021 | 0.21243 | 0.00044816 | Sustained | FALSE | TRUE | Not_TMED_Event | 658
PONCE | 2021-07-14 10:51 | 2021-07-14 18:45 | 4009 | 007:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17900 | P21071400011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 474 | 2021-07-14 | 1900266 | keep | 0 | Jul | 2021 | 1.2943 | 0.0027305 | Sustained | FALSE | TRUE | Not_TMED_Event | 4009
BAYAMON | 2021-07-14 10:59 | 2021-07-14 11:00 | 5809 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | B21071400000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-14 | 5809 | keep | 0 | Jul | 2021 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
BAYAMON | 2021-07-14 11:01 | 2021-07-14 13:21 | 5809 | 002:20 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO INTERRUPTOR ABRIENDO MACHETES EN AVENIDA HOSTOS FRENTE A ASILO DE ANCIANOS URBANIZACION IRLANDA HEIGHTS | B21071400000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 140 | 2021-07-14 | 813260 | keep | 0 | Jul | 2021 | 0.55391 | 0.0039565 | Sustained | FALSE | FALSE | Not_TMED_Event | 5809
CAGUAS | 2021-07-14 11:45 | 2021-07-14 16:36 | 43 | 004:51 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL DE LA LINEA Y RETEZAR LINEA | C21071400056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 291 | 2021-07-14 | 12513 | keep | 0 | Jul | 2021 | 0.0085225 | 2.9287e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 43
BAYAMON | 2021-07-14 11:47 | 2021-07-14 17:20 | 20 | 005:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | B21071400059 | New_Event | Wire Down | Include | Include | Equipment | 333 | 2021-07-14 | 6660 | keep | 0 | Jul | 2021 | 0.0045361 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-07-14 11:48 | 2021-07-14 17:28 | 10 | 005:40 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO VACCUM SWITCH | M21071300190 | New_Event | Switch Failure | Include | Include | Equipment | 340 | 2021-07-14 | 3400 | keep | 0 | Jul | 2021 | 0.0023157 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-14 11:55 | 2021-07-14 12:00 | 5 | 000:05 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA X 37.5 | M21071200365 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 5 | 2021-07-14 | 25 | keep | 0 | Jul | 2021 | 1.7027e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-07-14 12:13 | 2021-07-14 15:17 | 25 | 003:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21071400071 | New_Event | Bad Weather | Include | Include | Weather | 184 | 2021-07-14 | 4600 | keep | 0 | Jul | 2021 | 0.003133 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
FAJARDO | 2021-07-14 12:14 | 2021-07-14 14:29 | 1 | 002:15 | P | OTRAS CAUSAS | 1 X 25 EN RISER PROBLEMA INTERNO | R21071400036 | New_Event | Other Causes | Include | Include | Other | 135 | 2021-07-14 | 135 | keep | 0 | Jul | 2021 | 9.1948e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-07-14 12:23 | 2021-07-14 17:43 | 100 | 005:20 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | M21071400082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 320 | 2021-07-14 | 32000 | keep | 0 | Jul | 2021 | 0.021795 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-07-14 12:27 | 2021-07-14 18:00 | 80 | 005:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21071400084 | New_Event | Bad Weather | Include | Include | Weather | 333 | 2021-07-14 | 26640 | keep | 0 | Jul | 2021 | 0.018144 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
GUAYAMA | 2021-07-14 12:30 | 2021-07-14 16:00 | 25 | 003:30 | P | DESGANCHE | SE ABRE CORTE DE LINEA PARA REALIZAR DESGANCHE | P210714000XX | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2021-07-14 | 5250 | keep | 0 | Jul | 2021 | 0.0035758 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-07-14 12:36 | 2021-07-14 14:06 | 93 | 001:30 | T | DESGANCHE | SE RETIRO BAMBUAS Y SE CERRO INTERRUPTOR | M21071400087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2021-07-14 | 8370 | keep | 0 | Jul | 2021 | 0.0057008 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
SAN JUAN | 2021-07-14 12:45 | 2021-07-14 14:52 | 100 | 002:07 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21071400055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2021-07-14 | 12700 | keep | 0 | Jul | 2021 | 0.0086499 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-14 12:45 | 2021-07-14 12:47 | 1715 | 000:02 | T | DESGANCHE | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA CARGA POR EL 1708-03 | B21071400095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-07-14 | 3430 | keep | 0 | Jul | 2021 | 0.0023362 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2021-07-14 12:45 | 2021-07-14 12:47 | 1498 | 000:02 | T | DESGANCHE | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA LLEVANDO LA CARGA DEL 1708-03 | B21071400095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-07-14 | 2996 | keep | 0 | Jul | 2021 | 0.0020406 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
HUMACAO | 2021-07-14 12:45 | 2021-07-14 17:08 | 21 | 004:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21071400059 | New_Event | Bad Weather | Include | Include | Weather | 263 | 2021-07-14 | 5523 | keep | 0 | Jul | 2021 | 0.0037617 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BAYAMON | 2021-07-14 12:48 | 2021-07-14 12:50 | 1715 | 000:02 | T | DESGANCHE | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA CARGA POR EL 1708-03 | B21071400095 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-07-14 | 3430 | keep | 0 | Jul | 2021 | 0.0023362 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2021-07-14 12:48 | 2021-07-14 12:50 | 1498 | 000:02 | T | DESGANCHE | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA LLEVANDO LA CARGA DEL 1708-03 | B21071400095 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-07-14 | 2996 | keep | 0 | Jul | 2021 | 0.0020406 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2021-07-14 13:04 | 2021-07-15 10:10 | 3 | 021:06 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | S21071400057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1266 | 2021-07-14 | 3798 | keep | 0 | Jul | 2021 | 0.0025868 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
CAGUAS | 2021-07-14 13:17 | 2021-07-15 11:51 | 50 | 022:34 | P | OTRAS CAUSAS | 1 X 30 EN CORTE DE LINEA PROBLEMA DEL CLIENTE | C21071400062 | New_Event | Other Causes | Include | Include | Other | 1354 | 2021-07-14 | 67700 | keep | 0 | Jul | 2021 | 0.04611 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-14 13:21 | 2021-07-14 13:50 | 2400 | 000:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO MACHETES EN AVENIDA HOSTOS FRENTE A ASILO DE ANCIANOS URBANIZACION IRLANDA HEIGHTS ABRIENDO EN AVENIDA HOSTOS ESQUINA CARRETERA 831 POR CONDUCTOR PRIMARIO EN EL PISO | B21071400000 | Partial_restoration | Wire Down | Include | Include | Equipment | 29 | 2021-07-14 | 69600 | keep | 0 | Jul | 2021 | 0.047404 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-07-14 13:24 | 2021-07-14 17:53 | 70 | 004:29 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | A21071400099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 269 | 2021-07-14 | 18830 | keep | 0 | Jul | 2021 | 0.012825 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
ARECIBO | 2021-07-14 13:29 | 2021-07-14 14:40 | 75 | 001:11 | P | DESGANCHE | SE RETIRO RAMAS SOBRE LINEA PRIMARIA | A21071400008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2021-07-14 | 5325 | keep | 0 | Jul | 2021 | 0.0036268 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
UTUADO | 2021-07-14 13:29 | 2021-07-14 14:45 | 20 | 001:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUAS SOBRE LA LINEA | A21071400097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2021-07-14 | 1520 | keep | 0 | Jul | 2021 | 0.0010353 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-07-14 13:30 | 2021-07-14 13:33 | 353 | 000:03 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR SE CERRO POR CONTROL | S21071400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-07-14 | 1059 | keep | 0 | Jul | 2021 | 0.00072128 | 0.00024043 | Momentary | FALSE | FALSE | Not_TMED_Event | 353
CAGUAS | 2021-07-14 13:39 | 2021-07-15 15:41 | 10 | 026:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA REMPLAZO CAJA QUEMADA | C21071400064 | New_Event | Cutout Failure | Include | Include | Equipment | 1562 | 2021-07-14 | 15620 | keep | 0 | Jul | 2021 | 0.010639 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-07-14 13:42 | 2021-07-14 16:24 | 140 | 002:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | A21071400102 | New_Event | Cutout Failure | Include | Include | Equipment | 162 | 2021-07-14 | 22680 | keep | 0 | Jul | 2021 | 0.015447 | 9.5353e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 140
BAYAMON | 2021-07-14 13:50 | 2021-07-14 19:25 | 100 | 005:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO Y SE LEVANTO CONDUCTOR PRIMARIO | B21071400000 | Partial_restoration | Wire Down | Include | Include | Equipment | 335 | 2021-07-14 | 33500 | keep | 0 | Jul | 2021 | 0.022817 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2021-07-14 13:54 | 2021-07-14 16:22 | 1 | 002:28 | P | NO SE REPORTO CAUSA | 2 X 40 Y 2 X 65 EN CORTES DE LINEA | R21071400040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 148 | 2021-07-14 | 148 | keep | 0 | Jul | 2021 | 0.0001008 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-07-14 14:08 | 2021-07-14 17:00 | 30 | 002:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO THREE WIRE PARTIDO | A21071400105 | New_Event | Wire Down | Include | Include | Equipment | 172 | 2021-07-14 | 5160 | keep | 0 | Jul | 2021 | 0.0035145 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2021-07-14 14:14 | 2021-07-14 15:32 | 6 | 001:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | R21071400042 | New_Event |  |  | Include | Wildlife | 78 | 2021-07-14 | 468 | keep | 0 | Jul | 2021 | 0.00031875 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
PONCE | 2021-07-14 14:16 | 2021-07-14 14:17 | 2584 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21071400095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-14 | 2584 | keep | 0 | Jul | 2021 | 0.00176 | 0.00176 | Momentary | FALSE | FALSE | Not_TMED_Event | 2584
MAYAGÃœEZ | 2021-07-14 14:17 | 2021-07-14 19:43 | 300 | 005:26 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | M21071400113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 326 | 2021-07-14 | 97800 | keep | 0 | Jul | 2021 | 0.066611 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
BARRANQUITAS | 2021-07-14 14:22 | 2021-07-14 17:08 | 14 | 002:46 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C21071400073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2021-07-14 | 2324 | keep | 0 | Jul | 2021 | 0.0015829 | 9.5353e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 14
BAYAMON | 2021-07-14 14:25 | 2021-07-14 14:30 | 4533 | 000:05 | S | LINEA DE TRANSMISION 115KV | SE DISPARO LINEA DE TRANSMISION 37400 | B21071400144 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-07-14 | 22665 | keep | 0 | Jul | 2021 | 0.015437 | 0.0030874 | Momentary | FALSE | TRUE | Not_TMED_Event | 4533
BAYAMON | 2021-07-14 14:25 | 2021-07-14 14:30 | 911 | 000:05 | S | LINEA DE TRANSMISION 115KV | SE DISPARO LINEA DE TRANSMISION 37400 | B21071400144 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-07-14 | 4555 | keep | 0 | Jul | 2021 | 0.0031024 | 0.00062048 | Momentary | FALSE | TRUE | Not_TMED_Event | 911
BAYAMON | 2021-07-14 14:25 | 2021-07-14 14:30 | 4431 | 000:05 | S | LINEA DE TRANSMISION 115KV | SE DISPARO LINEA DE TRANSMISION 37400 | B21071400144 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-07-14 | 22155 | keep | 0 | Jul | 2021 | 0.01509 | 0.0030179 | Momentary | FALSE | TRUE | Not_TMED_Event | 4431
BAYAMON | 2021-07-14 14:25 | 2021-07-14 14:30 | 1362 | 000:05 | S | LINEA DE TRANSMISION 115KV | SE DISPARO LINEA DE TRANSMISION 37400 | B21071400144 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-07-14 | 6810 | keep | 0 | Jul | 2021 | 0.0046383 | 0.00092765 | Momentary | FALSE | TRUE | Not_TMED_Event | 1362
BAYAMON | 2021-07-14 14:25 | 2021-07-14 14:30 | 341 | 000:05 | S | LINEA DE TRANSMISION 115KV | SE DISPARO LINEA DE TRANSMISION 37400 | B21071400144 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-07-14 | 1705 | keep | 0 | Jul | 2021 | 0.0011613 | 0.00023225 | Momentary | FALSE | TRUE | Not_TMED_Event | 341
BAYAMON | 2021-07-14 14:30 | 2021-07-14 18:05 | 40 | 003:35 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL DE EXISTENTE A SU 3 | B21071400013 | New_Event | UG Cable Fault | Include | Include | Equipment | 215 | 2021-07-14 | 8600 | keep | 0 | Jul | 2021 | 0.0058574 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-07-14 14:30 | 2021-07-14 23:35 | 75 | 009:05 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 40 EN PROVISIONALES AEREOS | B21071400151 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 545 | 2021-07-14 | 40875 | keep | 0 | Jul | 2021 | 0.02784 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2021-07-14 14:36 | 2021-07-14 16:21 | 1675 | 001:45 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE CERRO INTERRUPTOR REEMPLAZANDO AISLADORES ROTOS SE REALIZO DESGANCHE Y SE ABRIO BAJA DE CONVERTIDOR | B21071400148 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 105 | 2021-07-14 | 175875 | keep | 0 | Jul | 2021 | 0.11979 | 0.0011408 | Sustained | FALSE | FALSE | Not_TMED_Event | 1675
VEGA BAJA | 2021-07-14 15:10 | 2021-07-14 15:11 | 27 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21071400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-14 | 27 | keep | 0 | Jul | 2021 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2021-07-14 15:13 | 2021-07-14 15:18 | 2435 | 000:05 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1909-08 | S21071400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-07-14 | 12175 | keep | 0 | Jul | 2021 | 0.0082923 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-07-14 15:13 | 2021-07-14 15:18 | 2956 | 000:05 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR SE CERRO POR SCADA LLEVA 1907-05 | S21071400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-07-14 | 14780 | keep | 0 | Jul | 2021 | 0.010067 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
MAYAGÃœEZ | 2021-07-14 15:14 | 2021-07-14 20:38 | 100 | 005:24 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | M21071400143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 324 | 2021-07-14 | 32400 | keep | 0 | Jul | 2021 | 0.022067 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-14 15:15 | 2021-07-14 15:27 | 570 | 000:12 | T | DESCONECTIVO DEFECTUOSO | SE ABRE INTERRUPTOR SE REMPLAZO MACHETE QUEMADO EN AVENIDA MUNOZ RIVERA CARGA POR EL 1338-02 | S21071400073 | New_Event | Switch Failure | Include | Include | Equipment | 12 | 2021-07-14 | 6840 | keep | 0 | Jul | 2021 | 0.0046587 | 0.00038822 | Sustained | FALSE | FALSE | Not_TMED_Event | 570
SAN JUAN | 2021-07-14 15:15 | 2021-07-14 15:27 | 155 | 000:12 | T | DESCONECTIVO DEFECTUOSO | SE ABRE INTERRUPTOR SE REMPLAZO MACHETE QUEMADO EN AVENIDA MUNOZ RIVERA CARGA POR EL 1338-02 | S21071400073 | New_Event | Switch Failure | Include | Include | Equipment | 12 | 2021-07-14 | 1860 | keep | 0 | Jul | 2021 | 0.0012668 | 0.00010557 | Sustained | FALSE | FALSE | Not_TMED_Event | 155
SAN JUAN | 2021-07-14 15:15 | 2021-07-14 15:27 | 928 | 000:12 | T | DESCONECTIVO DEFECTUOSO | SE ABRE INTERRUPTOR SE REMPLAZO MACHETE QUEMADO EN AVENIDA MUNOZ RIVERA LLEVA 1328-02, 1328-05, 1422-05 Y PARTE 1422-03 | S21071400073 | New_Event | Switch Failure | Include | Include | Equipment | 12 | 2021-07-14 | 11136 | keep | 0 | Jul | 2021 | 0.0075847 | 0.00063206 | Sustained | FALSE | FALSE | Not_TMED_Event | 928
SAN JUAN | 2021-07-14 15:15 | 2021-07-14 15:27 | 150 | 000:12 | P | DESCONECTIVO DEFECTUOSO | SE ABRE INTERRUPTOR SE REMPLAZO MACHETE QUEMADO EN AVENIDA MUNOZ RIVERA CARGA POR EL 1338-02 | S21071400073 | New_Event | Switch Failure | Include | Include | Equipment | 12 | 2021-07-14 | 1800 | keep | 0 | Jul | 2021 | 0.001226 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2021-07-14 15:15 | 2021-07-14 15:27 | 637 | 000:12 | T | DESCONECTIVO DEFECTUOSO | SE ABRE INTERRUPTOR SE REMPLAZO MACHETE QUEMADO EN AVENIDA MUNOZ RIVERA CARGA POR EL 1338-02 | S21071400073 | New_Event | Switch Failure | Include | Include | Equipment | 12 | 2021-07-14 | 7644 | keep | 0 | Jul | 2021 | 0.0052063 | 0.00043386 | Sustained | FALSE | FALSE | Not_TMED_Event | 637
CANOVANAS | 2021-07-14 15:15 | 2021-07-14 16:17 | 7 | 001:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR Y AJUSTO CONEXIONES EN PEDESTAL WR - 5778327 | R21071400000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 62 | 2021-07-14 | 434 | keep | 0 | Jul | 2021 | 0.0002956 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-07-14 15:22 | 2021-07-15 17:27 | 5 | 026:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | S21071400078 | New_Event | Cutout Failure | Include | Include | Equipment | 1565 | 2021-07-14 | 7825 | keep | 0 | Jul | 2021 | 0.0053296 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
ARECIBO | 2021-07-14 15:47 | 2021-07-15 17:39 | 200 | 025:52 | P | ESTRUCTURA AVERIADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO POSTE PARTIDO | A21071400112 | New_Event | Defective Pole | Include | Include | Equipment | 1552 | 2021-07-14 | 310400 | keep | 0 | Jul | 2021 | 0.21141 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-07-14 15:55 | 2021-07-15 10:07 | 4 | 018:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES SULFATADOS | C21071400080 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1092 | 2021-07-14 | 4368 | keep | 0 | Jul | 2021 | 0.002975 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-07-14 15:58 | 2021-07-14 20:46 | 7 | 004:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | M21071400150 | New_Event | Bad Weather | Include | Include | Weather | 288 | 2021-07-14 | 2016 | keep | 0 | Jul | 2021 | 0.0013731 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2021-07-14 16:00 | 2021-07-14 21:00 | 222 | 005:00 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 300 | P21071400124 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 300 | 2021-07-14 | 66600 | keep | 0 | Jul | 2021 | 0.045361 | 0.0001512 | Sustained | FALSE | TRUE | Not_TMED_Event | 222
PONCE | 2021-07-14 16:00 | 2021-07-14 21:00 | 537 | 005:00 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 300 | P21071400124 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 300 | 2021-07-14 | 161100 | keep | 0 | Jul | 2021 | 0.10972 | 0.00036575 | Sustained | FALSE | TRUE | Not_TMED_Event | 537
PONCE | 2021-07-14 16:00 | 2021-07-14 16:01 | 1033 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 7900 | P21071400125 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-14 | 1033 | keep | 0 | Jul | 2021 | 0.00070357 | 0.00070357 | Momentary | FALSE | TRUE | Not_TMED_Event | 1033
PONCE | 2021-07-14 16:00 | 2021-07-14 16:01 | 2035 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21071400096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-14 | 2035 | keep | 0 | Jul | 2021 | 0.001386 | 0.001386 | Momentary | FALSE | FALSE | Not_TMED_Event | 2035
PONCE | 2021-07-14 16:01 | 2021-07-14 16:02 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21071400099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-14 | 1746 | keep | 0 | Jul | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
PONCE | 2021-07-14 16:01 | 2021-07-14 16:02 | 752 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21071400097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-14 | 752 | keep | 0 | Jul | 2021 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
PONCE | 2021-07-14 16:01 | 2021-07-14 16:02 | 2696 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210714000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-14 | 2696 | keep | 0 | Jul | 2021 | 0.0018362 | 0.0018362 | Momentary | FALSE | FALSE | Not_TMED_Event | 2696
MAYAGÃœEZ | 2021-07-14 16:19 | 2021-07-15 11:00 | 80 | 018:41 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21071400155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1121 | 2021-07-14 | 89680 | keep | 0 | Jul | 2021 | 0.061081 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-07-14 16:21 | 2021-07-14 16:29 | 600 | 000:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE CERRO FUSIBLE DE BAJA DE CONVERTIDOR INSTALANDO AISLACION EN LINEAS PRIMARIAS | B21071400148 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 8 | 2021-07-14 | 4800 | keep | 0 | Jul | 2021 | 0.0032693 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
HUMACAO | 2021-07-14 16:22 | 2021-07-14 18:22 | 1089 | 002:00 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A RIO BLANCO SE SECCIONALIZO BAMBUAS SOBRE LINEA | C21071400082 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2021-07-14 | 130680 | keep | 0 | Jul | 2021 | 0.089006 | 0.00074171 | Sustained | FALSE | TRUE | Not_TMED_Event | 1089
HUMACAO | 2021-07-14 16:22 | 2021-07-14 18:22 | 3896 | 002:00 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A RIO BLANCO SE SECCIONALIZO BAMBUAS SOBRE LINEA | C21071400082 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2021-07-14 | 467520 | keep | 0 | Jul | 2021 | 0.31843 | 0.0026535 | Sustained | FALSE | TRUE | Not_TMED_Event | 3896
HUMACAO | 2021-07-14 16:22 | 2021-07-14 18:22 | 1467 | 002:00 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A RIO BLANCO SE SECCIONALIZO BAMBUAS SOBRE LINEA | C21071400082 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2021-07-14 | 176040 | keep | 0 | Jul | 2021 | 0.1199 | 0.00099917 | Sustained | FALSE | TRUE | Not_TMED_Event | 1467
BAYAMON | 2021-07-14 16:45 | 2021-07-15 18:08 | 15 | 025:23 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21071400195 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1523 | 2021-07-14 | 22845 | keep | 0 | Jul | 2021 | 0.01556 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-07-14 16:55 | 2021-07-14 16:56 | 1588 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | B21071400000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-07-14 | 1588 | keep | 0 | Jul | 2021 | 0.0010816 | 0.0010816 | Momentary | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2021-07-14 16:56 | 2021-07-15 14:15 | 40 | 021:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B21071400217 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1279 | 2021-07-14 | 51160 | keep | 0 | Jul | 2021 | 0.034845 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-07-14 17:15 | 2021-07-14 20:51 | 36 | 003:36 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA Y SE REMPLAZO PORTAFUSIBLE EN TRANSFORMADOR | S21071200027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 216 | 2021-07-14 | 7776 | keep | 0 | Jul | 2021 | 0.0052962 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
SAN JUAN | 2021-07-14 17:25 | 2021-07-14 19:24 | 4291 | 001:59 | T | PARARRAYOS DEFECTUOSO | SE ABRIO MACHETE CARR 844 INT 199 FRENTE A CONDOMINIO EL BOSQUE Y SE CERRO INTERRUPTOR 100% EN SERVICIO 1303-02, 50% 1204-02 Y 60% 1346-05 | S21071400090 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 119 | 2021-07-14 | 510629 | keep | 0 | Jul | 2021 | 0.34779 | 0.0029226 | Sustained | FALSE | FALSE | Not_TMED_Event | 4291
SAN JUAN | 2021-07-14 17:25 | 2021-07-14 19:24 | 2435 | 001:59 | T | PARARRAYOS DEFECTUOSO | SE ABRIO MACHETE EN CARR 844 INT 199 FRENTE A CONDOMINIO EL BOSQUE Y SE CERRO INTERRUPTOR 100% EN SERVICIO 1303-02, 50% 1204-02 Y 60% 1346-05 | S21071400090 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 119 | 2021-07-14 | 289765 | keep | 0 | Jul | 2021 | 0.19736 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2021-07-14 17:25 | 2021-07-14 19:24 | 600 | 001:59 | P | PARARRAYOS DEFECTUOSO | SE ABRIO MACHETE CARR 844 INT 199 FRENTE A CONDOMINIO EL BOSQUE Y SE CERRO INTERRUPTOR 100% EN SERVICIO 1303-02, 50% 1204-02 Y 60% 1346-05 | S21071400090 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 119 | 2021-07-14 | 71400 | keep | 0 | Jul | 2021 | 0.04863 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
PONCE | 2021-07-14 17:25 | 2021-07-15 11:12 | 100 | 017:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 POR MAL TIEMPO | P21071400118 | New_Event | Bad Weather | Include | Include | Weather | 1067 | 2021-07-14 | 106700 | keep | 0 | Jul | 2021 | 0.072673 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-07-14 18:11 | 2021-07-16 17:29 | 10 | 047:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTE SECUNDARIO | S21071400097 | New_Event | Wire Down | Include | Include | Equipment | 2838 | 2021-07-14 | 28380 | keep | 0 | Jul | 2021 | 0.019329 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-07-14 18:18 | 2021-07-14 21:01 | 1033 | 002:43 | S | LINEA DE TRANSMISION 38KV | SE ABRE LINEA 7900 POR AVERIA EN LINEA 39000 | P21071400129 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 163 | 2021-07-14 | 168379 | keep | 0 | Jul | 2021 | 0.11468 | 0.00070357 | Sustained | FALSE | TRUE | Not_TMED_Event | 1033
MAYAGÃœEZ | 2021-07-14 18:21 | 2021-07-15 16:00 | 15 | 021:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA POR LINEA PRIMARIA PARTIDA | M21071400169 | New_Event | Wire Down | Include | Include | Equipment | 1299 | 2021-07-14 | 19485 | keep | 0 | Jul | 2021 | 0.013271 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
SAN JUAN | 2021-07-14 18:23 | 2021-07-14 19:06 | 1381 | 000:43 | T | DESGANCHE | SE DISPARO INTERRUPTOR SE ENCONTRO BAMBUA SOBRE LINEA CARR 175 SECTOR EL SARTEN LLEVA CARGA 60 AMP 1303-02 Y LLEVA 1204-03 | S21071400099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 43 | 2021-07-14 | 59383 | keep | 0 | Jul | 2021 | 0.040445 | 0.00094059 | Sustained | FALSE | TRUE | Not_TMED_Event | 1381
SAN JUAN | 2021-07-14 18:23 | 2021-07-14 19:06 | 1799 | 000:43 | T | DESGANCHE | SE DISPARO INTERRUPTOR SE ENCONTRO BAMBUA SOBRE LINEA CARR 175 SECTOR EL SARTEN LLEVA CARGA 60 AMP 1303-02 Y LLEVA 1204-03 | S21071400099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 43 | 2021-07-14 | 77357 | keep | 0 | Jul | 2021 | 0.052688 | 0.0012253 | Sustained | FALSE | TRUE | Not_TMED_Event | 1799
SAN JUAN | 2021-07-14 18:23 | 2021-07-14 19:06 | 600 | 000:43 | P | DESGANCHE | DISPARO SE ENCONTRO BAMBUA SOBRE LINEA CARR.175 SECTOR EL SARTEN LLEVA CARGA 60 AMP. 1303-2 Y LLEVA 1204-3 | S21071400099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 43 | 2021-07-14 | 25800 | keep | 0 | Jul | 2021 | 0.017572 | 0.00040866 | Sustained | FALSE | TRUE | Not_TMED_Event | 600
VEGA BAJA | 2021-07-14 19:19 | 2021-07-15 20:10 | 12 | 024:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO CONECTOR EN NEUTRAL | B21071500041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1491 | 2021-07-14 | 17892 | keep | 0 | Jul | 2021 | 0.012186 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-07-14 19:21 | 2021-07-14 21:23 | 1715 | 002:02 | T | DESGANCHE | SE CERRO MACHETES DE AMARRE CON 1708-03 EN CALLE DAKAR Y ABRIENDO MACHETES EN URBANIZACION SANTA JUANITA CALLE 23 ESQUINA 24 POR ARBOL ENCIMA DE LINEAS | B21071400209 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2021-07-14 | 209230 | keep | 0 | Jul | 2021 | 0.14251 | 0.0011681 | Sustained | FALSE | TRUE | Not_TMED_Event | 1715
BAYAMON | 2021-07-14 19:21 | 2021-07-14 20:08 | 1498 | 000:47 | T | DESGANCHE | SE CERRO INTERRUPTOR ABRIENDO MACHETES DE AMARRE CON 1708-02 EN CALLE DAKAR POR ARBOL ENCIMA DE LINEA | B21071400209 | New_Event | Vegetation Contact | Include | Include | Vegetation | 47 | 2021-07-14 | 70406 | keep | 0 | Jul | 2021 | 0.047953 | 0.0010203 | Sustained | FALSE | TRUE | Not_TMED_Event | 1498
SAN JUAN | 2021-07-14 19:24 | 2021-07-14 20:07 | 2500 | 000:43 | P | PARARRAYOS DEFECTUOSO | DISPARO AL CERRAR MACHETE EN CARR 844 INT 199 SE ENCONTRO PARARRAYO AVERIADO | S21071400090 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 43 | 2021-07-14 | 107500 | keep | 0 | Jul | 2021 | 0.073218 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-07-14 19:27 | 2021-07-14 20:25 | 2035 | 000:58 | T | LINEA DE TRANSMISION 115KV | SE ABRIO BKR POR TRABAJOS EN LINEA 39000 | P21071400130 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 58 | 2021-07-14 | 118030 | keep | 0 | Jul | 2021 | 0.08039 | 0.001386 | Sustained | FALSE | TRUE | Not_TMED_Event | 2035
ARECIBO | 2021-07-14 19:42 | 2021-07-14 20:42 | 50 | 001:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21071400151 | New_Event | Bad Weather | Include | Include | Weather | 60 | 2021-07-14 | 3000 | keep | 0 | Jul | 2021 | 0.0020433 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-07-14 19:54 | 2021-07-15 09:10 | 100 | 013:16 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMA | A21071400152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 796 | 2021-07-14 | 79600 | keep | 0 | Jul | 2021 | 0.054215 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-07-14 20:01 | 2021-07-14 20:02 | 150 | 000:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | M21071100119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-14 | 150 | keep | 0 | Jul | 2021 | 0.00010216 | 0.00010216 | Momentary | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-07-14 20:07 | 2021-07-14 20:20 | 4291 | 000:13 | T | PARARRAYOS DEFECTUOSO | SE RETIRO PUENTE A PARARRAYO Y SE CERRO INTERRUPTOR 100% EN SERVICIO | S21071400090 | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 13 | 2021-07-14 | 55783 | keep | 0 | Jul | 2021 | 0.037994 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-14 20:07 | 2021-07-14 20:20 | 2435 | 000:13 | T | PARARRAYOS DEFECTUOSO | SE RETIRO PUENTE A PARARRAYO Y SE CERRO INTERRUPTOR 100% EN SERVICIO | S21071400090 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 13 | 2021-07-14 | 31655 | keep | 0 | Jul | 2021 | 0.02156 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-14 20:07 | 2021-07-14 20:20 | 600 | 000:13 | P | PARARRAYOS DEFECTUOSO | SE RETIRO PUENTE A PARARRAYO Y SE CERRO INTERRUPTOR 100% EN SERVICIO | S21071400090 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 13 | 2021-07-14 | 7800 | keep | 0 | Jul | 2021 | 0.0053125 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-14 20:28 | 2021-07-15 14:12 | 20 | 017:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN C/L POR DESCARGAS ELECTRICAS | M21071400175 | New_Event | Bad Weather | Include | Include | Weather | 1064 | 2021-07-14 | 21280 | keep | 0 | Jul | 2021 | 0.014494 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-07-14 20:36 | 2021-07-15 10:18 | 30 | 013:42 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA PRINCIPAL Y 1 X 40 EN CORTE DE LINEA INTERMEDIO | B21071400219 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 822 | 2021-07-14 | 24660 | keep | 0 | Jul | 2021 | 0.016796 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-07-14 20:37 | 2021-07-15 09:09 | 375 | 012:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 200 EN RISER HACIA SU - 1 CRUCE POR RATA | R21071400056 | New_Event |  |  | Include | Wildlife | 752 | 2021-07-14 | 282000 | keep | 0 | Jul | 2021 | 0.19207 | 0.00025541 | Sustained | FALSE | FALSE | Not_TMED_Event | 375
MAYAGÃœEZ | 2021-07-14 20:39 | 2021-07-15 13:15 | 80 | 016:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE RETIRO CAJA PRIMARIA DEFECTUOSA | M21071400178 | New_Event | Cutout Failure | Include | Include | Equipment | 996 | 2021-07-14 | 79680 | keep | 0 | Jul | 2021 | 0.05427 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BARRANQUITAS | 2021-07-14 20:54 | 2021-07-15 11:12 | 6 | 014:18 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C21071400110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 858 | 2021-07-14 | 5148 | keep | 0 | Jul | 2021 | 0.0035063 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-07-14 21:07 | 2021-07-15 13:03 | 200 | 015:56 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21071400111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 956 | 2021-07-14 | 191200 | keep | 0 | Jul | 2021 | 0.13023 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-07-14 21:21 | 2021-07-15 10:07 | 12 | 012:46 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21071400227 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 766 | 2021-07-14 | 9192 | keep | 0 | Jul | 2021 | 0.0062606 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-07-14 21:22 | 2021-07-15 14:35 | 40 | 017:13 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | C21071400112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1033 | 2021-07-14 | 41320 | keep | 0 | Jul | 2021 | 0.028143 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-14 21:23 | 2021-07-14 21:27 | 600 | 000:04 | P | DESGANCHE | SE PASO PARTE DE CARGA AL 1707-01 ABRIENDO MACHETES EN CALLE 33 SANTA JUANITA Y CERRANDO MACHETES DE AMARRE EN AVENIDA LAUREL AL LADO GASOLINERA SHELL EN LOMAS VERDES | B21071400209 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 4 | 2021-07-14 | 2400 | keep | 0 | Jul | 2021 | 0.0016346 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
CANOVANAS | 2021-07-14 21:41 | 2021-07-15 10:24 | 2 | 012:43 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR ENREDADERA | R21071400059 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 763 | 2021-07-14 | 1526 | keep | 0 | Jul | 2021 | 0.0010394 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2021-07-14 21:47 | 2021-07-15 17:27 | 25 | 019:40 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21071400023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1180 | 2021-07-14 | 29500 | keep | 0 | Jul | 2021 | 0.020092 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-07-14 23:54 | 2021-07-14 23:55 | 1533 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21071400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-14 | 1533 | keep | 0 | Jul | 2021 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
PONCE | 2021-07-15 00:02 | 2021-07-15 12:24 | 200 | 012:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO PORTA FUSIBLE QUEMADO | P21071500001 | New_Event | Cutout Failure | Include | Include | Equipment | 742 | 2021-07-15 | 148400 | keep | 0 | Jul | 2021 | 0.10107 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-07-15 00:05 | 2021-07-15 14:43 | 98 | 014:38 | P | DESCONECTIVO DEFECTUOSO | SE CAMBIO TRES MACHETES TRES CAJAS PRIMARIAS Y SE RELOCALIZO NEUTRAL PRIMARIO | S21071500001 | New_Event | Switch Failure | Include | Include | Equipment | 878 | 2021-07-15 | 86044 | keep | 0 | Jul | 2021 | 0.058604 | 6.6747e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 98
UTUADO | 2021-07-15 00:21 | 2021-07-15 09:54 | 15 | 009:33 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A21071500002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 573 | 2021-07-15 | 8595 | keep | 0 | Jul | 2021 | 0.005854 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CAGUAS | 2021-07-15 02:29 | 2021-07-15 07:54 | 2906 | 005:25 | T | ESTRUCTURA AVERIADA | DISPARO | C21071500000 | New_Event | Defective Pole | Include | Include | Equipment | 325 | 2021-07-15 | 944450 | keep | 0 | Jul | 2021 | 0.64326 | 0.0019793 | Sustained | FALSE | FALSE | Not_TMED_Event | 2906
CAGUAS | 2021-07-15 04:25 | 2021-07-15 04:27 | 853 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C21071500023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-15 | 1706 | keep | 0 | Jul | 2021 | 0.0011619 | 0.00058097 | Momentary | FALSE | FALSE | Not_TMED_Event | 853
PONCE | 2021-07-15 04:43 | 2021-07-15 13:44 | 60 | 009:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21071500003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 541 | 2021-07-15 | 32460 | keep | 0 | Jul | 2021 | 0.022108 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-07-15 05:06 | 2021-07-15 13:22 | 175 | 008:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN RISER Y 1 RVA DE 100 CRUCE POR RATA | R21071500002 | New_Event |  |  | Include | Wildlife | 496 | 2021-07-15 | 86800 | keep | 0 | Jul | 2021 | 0.059119 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
MAYAGÃœEZ | 2021-07-15 06:00 | 2021-07-15 21:20 | 50 | 015:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21071500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 920 | 2021-07-15 | 46000 | keep | 0 | Jul | 2021 | 0.03133 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-15 06:00 | 2021-07-15 17:29 | 25 | 011:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21071500000 | New_Event | Bad Weather | Include | Include | Weather | 689 | 2021-07-15 | 17225 | keep | 0 | Jul | 2021 | 0.011732 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-07-15 06:00 | 2021-07-15 21:00 | 1 | 015:00 | P | MAL TIEMPO/RAYOS/WET ASH | SE REEMPLAZO 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21071500000 | New_Event | Bad Weather | Include | Include | Weather | 900 | 2021-07-15 | 900 | keep | 0 | Jul | 2021 | 0.00061299 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-07-15 06:00 | 2021-07-15 16:00 | 20 | 010:00 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | A21071500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 600 | 2021-07-15 | 12000 | keep | 0 | Jul | 2021 | 0.0081731 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-07-15 06:12 | 2021-07-15 06:13 | 3046 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECERRO INTERRUPTOR | R21071500004 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-07-15 | 3046 | keep | 0 | Jul | 2021 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2021-07-15 06:13 | 2021-07-15 17:35 | 125 | 011:22 | P | PARARRAYOS DEFECTUOSO | 1 X 65 Y 1 X 50 EN CORTES DE LINEA SE REEMPLAZO PARARRAYOS | R21071500008 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 682 | 2021-07-15 | 85250 | keep | 0 | Jul | 2021 | 0.058063 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
ARECIBO | 2021-07-15 06:24 | 2021-07-15 06:25 | 2697 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DE INTERRUPTOR | A21071500000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2021-07-15 | 2697 | keep | 0 | Jul | 2021 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
ARECIBO | 2021-07-15 06:25 | 2021-07-15 13:20 | 100 | 006:55 | P | DESCONECTIVO DEFECTUOSO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO MACHETE QUEMADO | A21071500011 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 415 | 2021-07-15 | 41500 | keep | 0 | Jul | 2021 | 0.028265 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-15 06:35 | 2021-07-15 06:36 | 4431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21071500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-15 | 4431 | keep | 0 | Jul | 2021 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
ARECIBO | 2021-07-15 06:40 | 2021-07-15 11:05 | 100 | 004:25 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO RAMA | A21071500009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 265 | 2021-07-15 | 26500 | keep | 0 | Jul | 2021 | 0.018049 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-07-15 06:54 | 2021-07-15 06:55 | 1916 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | A21071500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-15 | 1916 | keep | 0 | Jul | 2021 | 0.001305 | 0.001305 | Momentary | FALSE | FALSE | Not_TMED_Event | 1916
CAGUAS | 2021-07-15 06:58 | 2021-07-15 11:38 | 50 | 004:40 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21071500069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2021-07-15 | 14000 | keep | 0 | Jul | 2021 | 0.0095353 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-15 07:16 | 2021-07-15 18:41 | 50 | 011:25 | P | LINEA DE TRANSMISION 38KV | SE ABRIO CORTE DE LINEA PARA TRABAJOS CON LINEA DE TRANSMISION | M21071500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 685 | 2021-07-15 | 34250 | keep | 0 | Jul | 2021 | 0.023328 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-07-15 07:37 | 2021-07-15 13:15 | 50 | 005:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO | A21071500016 | New_Event | Wire Down | Include | Include | Equipment | 338 | 2021-07-15 | 16900 | keep | 0 | Jul | 2021 | 0.011511 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-07-15 07:39 | 2021-07-15 10:28 | 225 | 002:49 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO CARGA POR EL 1908-03 | S21071400057 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 169 | 2021-07-15 | 38025 | keep | 0 | Jul | 2021 | 0.025899 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-07-15 07:39 | 2021-07-15 10:28 | 3957 | 002:49 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE LEVANTO CONDUCTOR PRIMARIO Y SE REMPLAZARON AISLADORES LLEVA 1303-04 | S21071400057 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 169 | 2021-07-15 | 668733 | keep | 0 | Jul | 2021 | 0.45547 | 0.0026951 | Sustained | FALSE | FALSE | Not_TMED_Event | 3957
CAGUAS | 2021-07-15 07:54 | 2021-07-15 17:41 | 150 | 009:47 | P | ESTRUCTURA AVERIADA | 3 X 80 EN CORTE DE LINEA REMPLAZO 2 POSTES PARTIDOS | C21071500113 | Partial_restoration | Defective Pole | Include | Include | Equipment | 587 | 2021-07-15 | 88050 | keep | 0 | Jul | 2021 | 0.05997 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-07-15 08:00 | 2021-07-15 13:03 | 5 | 005:03 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REPARO PEDESTAL SE DESGANCHO PRIMARIA Y SECUNDARIA SE RETEZO SECUNDARIA ABIERTA | S21071500014 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 303 | 2021-07-15 | 1515 | keep | 0 | Jul | 2021 | 0.0010319 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-07-15 08:01 | 2021-07-15 08:02 | 1510 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21071500110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-15 | 1510 | keep | 0 | Jul | 2021 | 0.0010285 | 0.0010285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1510
SAN JUAN | 2021-07-15 08:07 | 2021-07-15 11:13 | 100 | 003:06 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA | S21071500022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 186 | 2021-07-15 | 18600 | keep | 0 | Jul | 2021 | 0.012668 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-07-15 08:09 | 2021-07-15 08:10 | 638 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21071500113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-15 | 638 | keep | 0 | Jul | 2021 | 0.00043454 | 0.00043454 | Momentary | FALSE | FALSE | Not_TMED_Event | 638
VEGA BAJA | 2021-07-15 08:10 | 2021-07-15 11:39 | 12 | 003:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR SE RETIRO GLOBO METALICO | B21071400010 | New_Event |  |  | Include | Wildlife | 209 | 2021-07-15 | 2508 | keep | 0 | Jul | 2021 | 0.0017082 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2021-07-15 08:26 | 2021-07-15 15:42 | 4 | 007:16 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REMPLAZO PEDESTAL | B21071500005 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 436 | 2021-07-15 | 1744 | keep | 0 | Jul | 2021 | 0.0011878 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2021-07-15 08:29 | 2021-07-15 15:53 | 40 | 007:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C21071500116 | New_Event |  |  | Include | Wildlife | 444 | 2021-07-15 | 17760 | keep | 0 | Jul | 2021 | 0.012096 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-07-15 08:45 | 2021-07-15 08:46 | 1227 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | A21071500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-15 | 1227 | keep | 0 | Jul | 2021 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
BARRANQUITAS | 2021-07-15 09:02 | 2021-07-15 15:27 | 80 | 006:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO CORTE DE LINEA PARA CERRAR PUENTE | C21071500109 | New_Event | Wire Down | Include | Include | Equipment | 385 | 2021-07-15 | 30800 | keep | 0 | Jul | 2021 | 0.020978 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-07-15 09:11 | 2021-07-15 15:50 | 15 | 006:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21071400049 | New_Event | Bad Weather | Include | Include | Weather | 399 | 2021-07-15 | 5985 | keep | 0 | Jul | 2021 | 0.0040764 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-07-15 09:38 | 2021-07-15 10:11 | 40 | 000:33 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA PRINCIPAL Y 1 X 65 EN CORTE DE LINEA INTERMEDIO | B21071500007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 33 | 2021-07-15 | 1320 | keep | 0 | Jul | 2021 | 0.00089905 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
FAJARDO | 2021-07-15 09:39 | 2021-07-15 11:18 | 41 | 001:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 Y 1 X 20 EN CORTES DE LINEA CRUCE POR AVE | R21071500010 | New_Event |  |  | Include | Wildlife | 99 | 2021-07-15 | 4059 | keep | 0 | Jul | 2021 | 0.0027646 | 2.7925e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 41
CAGUAS | 2021-07-15 10:09 | 2021-07-15 17:44 | 150 | 007:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 Y 2 X 65 EN CORTES DE LINEA REMPLAZO CAJA QUEMADA | C21071500123 | New_Event | Cutout Failure | Include | Include | Equipment | 455 | 2021-07-15 | 68250 | keep | 0 | Jul | 2021 | 0.046485 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BARRANQUITAS | 2021-07-15 10:14 | 2021-07-15 11:04 | 20 | 000:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | C21071500125 | New_Event | Cutout Failure | Include | Include | Equipment | 50 | 2021-07-15 | 1000 | keep | 0 | Jul | 2021 | 0.0006811 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-07-15 10:18 | 2021-07-15 15:05 | 100 | 004:47 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21071500126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 287 | 2021-07-15 | 28700 | keep | 0 | Jul | 2021 | 0.019547 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-07-15 10:30 | 2021-07-15 19:15 | 40 | 008:45 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO 2 POSTES PARTIDOS Y SE CERRO CORTE DE LINEA | A21071500000 | New_Event | Defective Pole | Include | Include | Equipment | 525 | 2021-07-15 | 21000 | keep | 0 | Jul | 2021 | 0.014303 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-15 11:08 | 2021-07-16 11:30 | 10 | 024:22 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE SECUNDARIO | B21071500008 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1462 | 2021-07-15 | 14620 | keep | 0 | Jul | 2021 | 0.0099576 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-07-15 11:27 | 2021-07-15 11:28 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21071500014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-15 | 1746 | keep | 0 | Jul | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
PONCE | 2021-07-15 11:27 | 2021-07-15 13:14 | 752 | 001:47 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ENCONTRARON BAJANTES PRIMARIOS CRUZADOS | P21071500012 | New_Event | Wire Down | Include | Include | Equipment | 107 | 2021-07-15 | 80464 | keep | 0 | Jul | 2021 | 0.054804 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
PONCE | 2021-07-15 11:27 | 2021-07-15 13:14 | 2696 | 001:47 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ENCONTRARON BAJANTES PRIMARIOS CRUZADOS | P21071500012 | New_Event | Wire Down | Include | Include | Equipment | 107 | 2021-07-15 | 288472 | keep | 0 | Jul | 2021 | 0.19648 | 0.0018362 | Sustained | FALSE | FALSE | Not_TMED_Event | 2696
BARRANQUITAS | 2021-07-15 11:46 | 2021-07-15 14:10 | 40 | 002:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO NEUTRAL PRIMARIO Y CERRO CORTE DE LINEA NO FUNDIO | C21071500134 | New_Event | Wire Down | Include | Include | Equipment | 144 | 2021-07-15 | 5760 | keep | 0 | Jul | 2021 | 0.0039231 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-15 11:49 | 2021-07-15 14:38 | 5 | 002:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REPARO SECUNDARIA QUE CAMION SE LLEVO ENREDADA | B21071500009 | New_Event |  |  | Include | Wildlife | 169 | 2021-07-15 | 845 | keep | 0 | Jul | 2021 | 0.00057553 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-07-15 12:13 | 2021-07-15 12:14 | 1746 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR BAJANTE PRIMARIO SOBRE MONTURA TRIFASICA | P21071500044 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-15 | 1746 | keep | 0 | Jul | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
AGUADILLA | 2021-07-15 12:30 | 2021-07-15 13:24 | 709 | 000:54 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO DA INDICACION DE ABIERTO | M21071500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 54 | 2021-07-15 | 38286 | keep | 0 | Jul | 2021 | 0.026076 | 0.0004829 | Sustained | FALSE | FALSE | Not_TMED_Event | 709
BAYAMON | 2021-07-15 13:04 | 2021-07-16 18:54 | 10 | 029:50 | P | CABLE SOTERRADO AVERIADO | 1 X 15 EN RISER SE REPARO CABLE SOTERRADO DE RISER A T155 | B21071500010 | New_Event | UG Cable Fault | Include | Include | Equipment | 1790 | 2021-07-15 | 17900 | keep | 0 | Jul | 2021 | 0.012192 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-07-15 13:04 | 2021-07-15 14:26 | 50 | 001:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR CHANGO | R21071500022 | New_Event |  |  | Include | Wildlife | 82 | 2021-07-15 | 4100 | keep | 0 | Jul | 2021 | 0.0027925 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-15 13:24 | 2021-07-15 20:34 | 50 | 007:10 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHO Y LEVANTO CONDUCTOR | C21071500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 430 | 2021-07-15 | 21500 | keep | 0 | Jul | 2021 | 0.014644 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-15 13:41 | 2021-07-15 13:42 | 2782 | 000:01 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR SE CERRO POR CONTROL | S21071500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-15 | 2782 | keep | 0 | Jul | 2021 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
SAN JUAN | 2021-07-15 13:41 | 2021-07-15 18:52 | 146 | 005:11 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA CRUCE POR RAMA | R21071500023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 311 | 2021-07-15 | 45406 | keep | 0 | Jul | 2021 | 0.030926 | 9.944e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 146
ARECIBO | 2021-07-15 13:42 | 2021-07-15 15:40 | 5 | 001:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES | A21071500000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 118 | 2021-07-15 | 590 | keep | 0 | Jul | 2021 | 0.00040185 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-07-15 14:15 | 2021-07-15 14:17 | 1588 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE DISPARO INTERRUPTOR POR PETICION DE LUIS ANDUJAR POR CAJA PRIMARIA ARQUEANDO SE CERRO POR SCADA LLEVA CARGA DEL 1711-03 | B21071500014 | Additional_clients | Cutout Failure | Include | Include | Equipment | 2 | 2021-07-15 | 3176 | keep | 0 | Jul | 2021 | 0.0021632 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-15 14:15 | 2021-07-15 14:17 | 13 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE DISPARO INTERRUPTOR POR CAJA PRIMARIA ARQUEANDO SE CERRO POR SCADA CARGA POR EL 1711-01 | B21071500014 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2021-07-15 | 26 | keep | 0 | Jul | 2021 | 1.7708e-05 | 8.8542e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 13
CANOVANAS | 2021-07-15 14:16 | 2021-07-15 15:56 | 35 | 001:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | R21071500024 | New_Event |  |  | Include | Wildlife | 100 | 2021-07-15 | 3500 | keep | 0 | Jul | 2021 | 0.0023838 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-07-15 14:17 | 2021-07-15 15:11 | 40 | 000:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B21071400217 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 54 | 2021-07-15 | 2160 | keep | 0 | Jul | 2021 | 0.0014712 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-07-15 14:41 | 2021-07-15 15:35 | 60 | 000:54 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21071500054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2021-07-15 | 3240 | keep | 0 | Jul | 2021 | 0.0022067 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
UTUADO | 2021-07-15 14:44 | 2021-07-15 18:33 | 50 | 003:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | A21071500032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2021-07-15 | 11450 | keep | 0 | Jul | 2021 | 0.0077985 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-15 14:57 | 2021-07-15 15:00 | 5191 | 000:03 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR SE CERRO POR SCADA | B21071500017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-07-15 | 15573 | keep | 0 | Jul | 2021 | 0.010607 | 0.0035356 | Momentary | FALSE | FALSE | Not_TMED_Event | 5191
MAYAGÃœEZ | 2021-07-15 14:58 | 2021-07-15 15:15 | 35 | 000:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21071400134 | New_Event | Bad Weather | Include | Include | Weather | 17 | 2021-07-15 | 595 | keep | 0 | Jul | 2021 | 0.00040525 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-07-15 15:00 | 2021-07-16 16:12 | 90 | 025:12 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21071500019 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1512 | 2021-07-15 | 136080 | keep | 0 | Jul | 2021 | 0.092683 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
VEGA BAJA | 2021-07-15 15:01 | 2021-07-15 19:20 | 12 | 004:19 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B21071300045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 259 | 2021-07-15 | 3108 | keep | 0 | Jul | 2021 | 0.0021168 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-07-15 15:15 | 2021-07-15 20:44 | 80 | 005:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE LEVANTO LINEA PRIMARIA | S21071400010 | New_Event | Wire Down | Include | Include | Equipment | 329 | 2021-07-15 | 26320 | keep | 0 | Jul | 2021 | 0.017926 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-07-15 15:27 | 2021-07-15 16:42 | 463 | 001:15 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21071500056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2021-07-15 | 34725 | keep | 0 | Jul | 2021 | 0.023651 | 0.00031535 | Sustained | FALSE | TRUE | Not_TMED_Event | 463
BAYAMON | 2021-07-15 15:40 | 2021-07-15 16:27 | 25 | 000:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA Y SE REPARO BUSHING SECUNDARIO | S21071300057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 47 | 2021-07-15 | 1175 | keep | 0 | Jul | 2021 | 0.00080029 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2021-07-15 15:49 | 2021-07-16 17:12 | 60 | 025:23 | P | ESTRUCTURA AVERIADA | 2 X 40 EN CORTE DE LINEA SE REEMPLAZO PORTE PARTIDO | M21071500021 | New_Event | Defective Pole | Include | Include | Equipment | 1523 | 2021-07-15 | 91380 | keep | 0 | Jul | 2021 | 0.062239 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-07-15 16:01 | 2021-07-16 11:51 | 10 | 019:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA Y PARARRAYO EN TRANSFORMADOR | B21071500018 | New_Event | Cutout Failure | Include | Include | Equipment | 1190 | 2021-07-15 | 11900 | keep | 0 | Jul | 2021 | 0.008105 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-07-15 16:17 | 2021-07-15 16:35 | 569 | 000:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21071500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2021-07-15 | 10242 | keep | 0 | Jul | 2021 | 0.0069758 | 0.00038754 | Sustained | FALSE | TRUE | Not_TMED_Event | 569
AGUADILLA | 2021-07-15 16:17 | 2021-07-15 16:35 | 1245 | 000:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21071500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2021-07-15 | 22410 | keep | 0 | Jul | 2021 | 0.015263 | 0.00084796 | Sustained | FALSE | TRUE | Not_TMED_Event | 1245
AGUADILLA | 2021-07-15 16:17 | 2021-07-15 16:35 | 1155 | 000:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21071500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2021-07-15 | 20790 | keep | 0 | Jul | 2021 | 0.01416 | 0.00078667 | Sustained | FALSE | TRUE | Not_TMED_Event | 1155
AGUADILLA | 2021-07-15 16:17 | 2021-07-15 16:35 | 867 | 000:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21071500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2021-07-15 | 15606 | keep | 0 | Jul | 2021 | 0.010629 | 0.00059051 | Sustained | FALSE | TRUE | Not_TMED_Event | 867
AGUADILLA | 2021-07-15 16:17 | 2021-07-15 16:35 | 257 | 000:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21071500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2021-07-15 | 4626 | keep | 0 | Jul | 2021 | 0.0031507 | 0.00017504 | Sustained | FALSE | TRUE | Not_TMED_Event | 257
AGUADILLA | 2021-07-15 16:17 | 2021-07-15 16:35 | 1336 | 000:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21071500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2021-07-15 | 24048 | keep | 0 | Jul | 2021 | 0.016379 | 0.00090994 | Sustained | FALSE | TRUE | Not_TMED_Event | 1336
AGUADILLA | 2021-07-15 16:17 | 2021-07-15 16:35 | 3315 | 000:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21071500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2021-07-15 | 59670 | keep | 0 | Jul | 2021 | 0.040641 | 0.0022578 | Sustained | FALSE | TRUE | Not_TMED_Event | 3315
AGUADILLA | 2021-07-15 16:17 | 2021-07-15 16:35 | 1718 | 000:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21071500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2021-07-15 | 30924 | keep | 0 | Jul | 2021 | 0.021062 | 0.0011701 | Sustained | FALSE | TRUE | Not_TMED_Event | 1718
SAN JUAN | 2021-07-15 16:32 | 2021-07-17 11:07 | 78 | 042:35 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21071400084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2555 | 2021-07-15 | 199290 | keep | 0 | Jul | 2021 | 0.13574 | 5.3125e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 78
FAJARDO | 2021-07-15 16:38 | 2021-07-15 18:10 | 30 | 001:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | R21071500026 | New_Event |  |  | Include | Wildlife | 92 | 2021-07-15 | 2760 | keep | 0 | Jul | 2021 | 0.0018798 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
AGUADILLA | 2021-07-15 16:39 | 2021-07-15 19:31 | 100 | 002:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21071500030 | New_Event | Bad Weather | Include | Include | Weather | 172 | 2021-07-15 | 17200 | keep | 0 | Jul | 2021 | 0.011715 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-07-15 16:42 | 2021-07-15 17:09 | 569 | 000:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21071500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2021-07-15 | 15363 | keep | 0 | Jul | 2021 | 0.010464 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-07-15 16:42 | 2021-07-15 17:09 | 1245 | 000:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21071500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2021-07-15 | 33615 | keep | 0 | Jul | 2021 | 0.022895 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-07-15 16:42 | 2021-07-15 17:09 | 1155 | 000:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21071500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2021-07-15 | 31185 | keep | 0 | Jul | 2021 | 0.02124 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-07-15 16:42 | 2021-07-15 17:09 | 867 | 000:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21071500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2021-07-15 | 23409 | keep | 0 | Jul | 2021 | 0.015944 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-07-15 16:42 | 2021-07-15 17:09 | 257 | 000:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21071500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2021-07-15 | 6939 | keep | 0 | Jul | 2021 | 0.0047261 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-07-15 16:42 | 2021-07-15 17:09 | 1336 | 000:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21071500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2021-07-15 | 36072 | keep | 0 | Jul | 2021 | 0.024568 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-07-15 16:42 | 2021-07-15 17:09 | 3315 | 000:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21071500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2021-07-15 | 89505 | keep | 0 | Jul | 2021 | 0.060961 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-07-15 16:42 | 2021-07-15 17:09 | 1718 | 000:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21071500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2021-07-15 | 46386 | keep | 0 | Jul | 2021 | 0.031593 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
PONCE | 2021-07-15 16:49 | 2021-07-15 16:50 | 1478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21071500040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-15 | 1478 | keep | 0 | Jul | 2021 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
CANOVANAS | 2021-07-15 17:02 | 2021-07-15 17:53 | 20 | 000:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA LIMPIAR BANDERAS Y BARRA SULFATADA | R21071500027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 51 | 2021-07-15 | 1020 | keep | 0 | Jul | 2021 | 0.00069472 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-07-15 17:04 | 2021-07-15 17:07 | 870 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO | S21071500061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-07-15 | 2610 | keep | 0 | Jul | 2021 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
AGUADILLA | 2021-07-15 17:09 | 2021-07-15 19:14 | 5 | 002:05 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 35.5KVA X 37.5 KVA AVERIADO | M21071400164 | New_Event | Service Transformer Failure | Include | Include | Equipment | 125 | 2021-07-15 | 625 | keep | 0 | Jul | 2021 | 0.00042568 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-07-15 17:10 | 2021-07-16 10:25 | 10 | 017:15 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B21071500020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1035 | 2021-07-15 | 10350 | keep | 0 | Jul | 2021 | 0.0070493 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-07-15 17:14 | 2021-07-15 17:15 | 4188 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | R21071500030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-15 | 4188 | keep | 0 | Jul | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
SAN JUAN | 2021-07-15 17:27 | 2021-07-15 19:20 | 266 | 001:53 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR SE VERIFICO LOCALMENTE Y SE CERRO POR SCADA | S21071500062 | New_Event | UG Cable Fault | Include | Include | Equipment | 113 | 2021-07-15 | 30058 | keep | 0 | Jul | 2021 | 0.020472 | 0.00018117 | Sustained | FALSE | FALSE | Not_TMED_Event | 266
PONCE | 2021-07-15 17:45 | 2021-07-15 22:03 | 1033 | 004:18 | S | LINEA DE TRANSMISION 38KV | SE ABRE INTERRUPTOR PARA RETIRAR CARGA SUBESTACION 5805-00 PARA TRABAJOS EN LINEA 39000 | P21071500033 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 258 | 2021-07-15 | 266514 | keep | 0 | Jul | 2021 | 0.18152 | 0.00070357 | Sustained | FALSE | TRUE | Not_TMED_Event | 1033
CANOVANAS | 2021-07-15 18:09 | 2021-07-15 18:11 | 2106 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE VERIFICO PERSONAL FUERA CERRADO POR CONTROL | R21071500029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-15 | 4212 | keep | 0 | Jul | 2021 | 0.0028688 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
BARRANQUITAS | 2021-07-15 18:25 | 2021-07-15 20:07 | 1 | 001:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA REPARO PUENTE | C21071500153 | New_Event | Wire Down | Include | Include | Equipment | 102 | 2021-07-15 | 102 | keep | 0 | Jul | 2021 | 6.9472e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
PONCE | 2021-07-15 18:30 | 2021-07-15 18:45 | 2035 | 000:15 | T | LINEA DE TRANSMISION 115KV | SE ABRE ALIMENTADOR PARA ABRIR PUENTES PRIMARIOS PARA TRABAJOS EN LINEA 39000 | P21071500034 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 15 | 2021-07-15 | 30525 | keep | 0 | Jul | 2021 | 0.02079 | 0.001386 | Sustained | FALSE | TRUE | Not_TMED_Event | 2035
PONCE | 2021-07-15 18:46 | 2021-07-15 20:52 | 1000 | 002:06 | P | LINEA DE TRANSMISION 115KV | PUENTES ABIERTOS PARA SECCIONALIZAR LINEA Y TRABAJAR CON LINEA 39000 | P21071500036 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 126 | 2021-07-15 | 126000 | keep | 0 | Jul | 2021 | 0.085818 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-15 18:53 | 2021-07-16 16:00 | 70 | 021:07 | P | DESGANCHE | 2 X 40 EN CORTE DE LNEA | M21071500044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1267 | 2021-07-15 | 88690 | keep | 0 | Jul | 2021 | 0.060406 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2021-07-15 19:19 | 2021-07-15 21:47 | 200 | 002:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21071500047 | New_Event | Bad Weather | Include | Include | Weather | 148 | 2021-07-15 | 29600 | keep | 0 | Jul | 2021 | 0.02016 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-07-15 19:23 | 2021-07-15 19:28 | 266 | 000:05 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR SE VERIFICO LOCALMENTE Y SE CERRO POR SCADA | S21071500062 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 5 | 2021-07-15 | 1330 | keep | 0 | Jul | 2021 | 0.00090586 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-15 19:39 | 2021-07-16 17:00 | 15 | 021:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE TRANSFORMADOR | S21071500067 | New_Event | Wire Down | Include | Include | Equipment | 1281 | 2021-07-15 | 19215 | keep | 0 | Jul | 2021 | 0.013087 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CAGUAS | 2021-07-15 19:40 | 2021-07-16 19:50 | 90 | 024:10 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C21071500154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1450 | 2021-07-15 | 130500 | keep | 0 | Jul | 2021 | 0.088883 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
SAN JUAN | 2021-07-15 20:03 | 2021-07-15 20:14 | 1615 | 0:11 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR | S21071500000 | New_Event | Wire Down | Include | Include | Equipment | 11 | 2021-07-15 | 17765 | keep | 0 | Jul | 2021 | 0.0121 | 0.0011 | Sustained | FALSE | FALSE | Not_TMED_Event | 1615
SAN JUAN | 2021-07-15 20:14 | 2021-07-16 09:49 | 600 | 013:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO CONDUCTOR ROTO Y SE CERRO MACHETES | R21071600005 | Partial_restoration | Wire Down | Include | Include | Equipment | 815 | 2021-07-15 | 489000 | keep | 0 | Jul | 2021 | 0.33306 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-15 20:16 | 2021-07-15 20:21 | 1310 | 000:05 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR CON RECIERRE EN OFF SE PROBO POR CONTROL QUEDO EN SERVICIO | S21071500076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-07-15 | 6550 | keep | 0 | Jul | 2021 | 0.0044612 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
PONCE | 2021-07-15 20:28 | 2021-07-15 20:29 | 2446 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21071500042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-15 | 2446 | keep | 0 | Jul | 2021 | 0.001666 | 0.001666 | Momentary | FALSE | FALSE | Not_TMED_Event | 2446
PONCE | 2021-07-15 20:52 | 2021-07-15 21:18 | 2035 | 000:26 | T | LINEA DE TRANSMISION 115KV | SE ABRE ALIMENTADOR PARA CERRAR PUENTES ABIERTOS | P21071500043 | Additional_clients | 115 kV Transmission Line Source | Include | Include | Power supply | 26 | 2021-07-15 | 52910 | keep | 0 | Jul | 2021 | 0.036037 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-15 22:15 | 2021-07-16 16:04 | 60 | 017:49 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | M21071500051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1069 | 2021-07-15 | 64140 | keep | 0 | Jul | 2021 | 0.043685 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-07-15 22:53 | 2021-07-16 16:03 | 25 | 017:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S21071500106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1030 | 2021-07-15 | 25750 | keep | 0 | Jul | 2021 | 0.017538 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
AGUADILLA | 2021-07-16 00:41 | 2021-07-16 00:42 | 390 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21071600001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-16 | 390 | keep | 0 | Jul | 2021 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
HUMACAO | 2021-07-16 00:51 | 2021-07-16 14:25 | 32 | 013:34 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO AISLADOR | C21071600001 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 814 | 2021-07-16 | 26048 | keep | 0 | Jul | 2021 | 0.017741 | 2.1795e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 32
SAN JUAN | 2021-07-16 01:18 | 2021-07-16 01:19 | 172 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21071600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-16 | 172 | keep | 0 | Jul | 2021 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
AGUADILLA | 2021-07-16 01:28 | 2021-07-16 01:29 | 390 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21071600002 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-16 | 390 | keep | 0 | Jul | 2021 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
YAUCO | 2021-07-16 01:47 | 2021-07-16 10:30 | 15 | 008:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR POR CAJA PRIMARIA QUEMADA | P21071600002 | New_Event | Cutout Failure | Include | Include | Equipment | 523 | 2021-07-16 | 7845 | keep | 0 | Jul | 2021 | 0.0053432 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-07-16 02:34 | 2021-07-16 02:35 | 1253 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M21071600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-16 | 1253 | keep | 0 | Jul | 2021 | 0.00085341 | 0.00085341 | Momentary | FALSE | TRUE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2021-07-16 02:34 | 2021-07-16 02:35 | 1266 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M21071600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-16 | 1266 | keep | 0 | Jul | 2021 | 0.00086227 | 0.00086227 | Momentary | FALSE | TRUE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2021-07-16 02:34 | 2021-07-16 02:35 | 411 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M21071600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-16 | 411 | keep | 0 | Jul | 2021 | 0.00027993 | 0.00027993 | Momentary | FALSE | TRUE | Not_TMED_Event | 411
MAYAGÃœEZ | 2021-07-16 02:34 | 2021-07-16 02:35 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M21071600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-16 | 1617 | keep | 0 | Jul | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | TRUE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-07-16 02:34 | 2021-07-16 02:35 | 1017 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M21071600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-16 | 1017 | keep | 0 | Jul | 2021 | 0.00069267 | 0.00069267 | Momentary | FALSE | TRUE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-07-16 02:34 | 2021-07-16 02:35 | 828 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M21071600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-16 | 828 | keep | 0 | Jul | 2021 | 0.00056395 | 0.00056395 | Momentary | FALSE | TRUE | Not_TMED_Event | 828
MAYAGÃœEZ | 2021-07-16 02:34 | 2021-07-16 02:35 | 863 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M21071600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-16 | 863 | keep | 0 | Jul | 2021 | 0.00058779 | 0.00058779 | Momentary | FALSE | TRUE | Not_TMED_Event | 863
MAYAGÃœEZ | 2021-07-16 02:34 | 2021-07-16 02:35 | 309 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M21071600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-16 | 309 | keep | 0 | Jul | 2021 | 0.00021046 | 0.00021046 | Momentary | FALSE | TRUE | Not_TMED_Event | 309
MAYAGÃœEZ | 2021-07-16 02:34 | 2021-07-16 02:35 | 176 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M21071600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-16 | 176 | keep | 0 | Jul | 2021 | 0.00011987 | 0.00011987 | Momentary | FALSE | TRUE | Not_TMED_Event | 176
MAYAGÃœEZ | 2021-07-16 02:34 | 2021-07-16 02:35 | 108 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M21071600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-16 | 108 | keep | 0 | Jul | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 108
MAYAGÃœEZ | 2021-07-16 02:34 | 2021-07-16 02:35 | 974 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M21071600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-16 | 974 | keep | 0 | Jul | 2021 | 0.00066339 | 0.00066339 | Momentary | FALSE | TRUE | Not_TMED_Event | 974
FAJARDO | 2021-07-16 03:59 | 2021-07-16 04:00 | 76 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | R21071600001 | New_Event |  |  | Include | Wildlife | 1 | 2021-07-16 | 76 | keep | 0 | Jul | 2021 | 5.1763e-05 | 5.1763e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 76
FAJARDO | 2021-07-16 04:00 | 2021-07-16 10:40 | 60 | 006:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | R21071600002 | 1st_after_momentary |  |  | Include | Wildlife | 400 | 2021-07-16 | 24000 | keep | 0 | Jul | 2021 | 0.016346 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-07-16 05:28 | 2021-07-16 05:29 | 1268 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21071600003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-16 | 1268 | keep | 0 | Jul | 2021 | 0.00086363 | 0.00086363 | Momentary | FALSE | FALSE | Not_TMED_Event | 1268
ARECIBO | 2021-07-16 05:35 | 2021-07-16 09:53 | 40 | 004:18 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE RETIRO PARARRAYOS CRUZADO | A21071600001 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 258 | 2021-07-16 | 10320 | keep | 0 | Jul | 2021 | 0.0070289 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-07-16 06:00 | 2021-07-16 21:41 | 60 | 015:41 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PARTIDO | M21071600000 | New_Event | Defective Pole | Include | Include | Equipment | 941 | 2021-07-16 | 56460 | keep | 0 | Jul | 2021 | 0.038455 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-07-16 06:00 | 2021-07-16 16:28 | 8 | 010:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA PARTIDA | A21071600000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 628 | 2021-07-16 | 5024 | keep | 0 | Jul | 2021 | 0.0034218 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
ARECIBO | 2021-07-16 06:00 | 2021-07-16 17:31 | 5 | 011:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA PARTIDA | A21071600000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 691 | 2021-07-16 | 3455 | keep | 0 | Jul | 2021 | 0.0023532 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
UTUADO | 2021-07-16 06:00 | 2021-07-16 17:49 | 7 | 011:49 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 15 KVA POR 25 KVA | A21071600000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 709 | 2021-07-16 | 4963 | keep | 0 | Jul | 2021 | 0.0033803 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2021-07-16 06:00 | 2021-07-16 20:43 | 80 | 014:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REPARO CAJA PRIMARIA PARTIDA | A21071600000 | New_Event | Cutout Failure | Include | Include | Equipment | 883 | 2021-07-16 | 70640 | keep | 0 | Jul | 2021 | 0.048113 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-07-16 06:14 | 2021-07-16 16:04 | 120 | 009:50 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE MASIVO | M21071600004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 590 | 2021-07-16 | 70800 | keep | 0 | Jul | 2021 | 0.048222 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
BARRANQUITAS | 2021-07-16 06:16 | 2021-07-16 13:36 | 89 | 007:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE DESPEGO BAJANTE DE CRUCETA | C21071600002 | New_Event | Wire Down | Include | Include | Equipment | 440 | 2021-07-16 | 39160 | keep | 0 | Jul | 2021 | 0.026672 | 6.0617e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 89
MAYAGÃœEZ | 2021-07-16 06:53 | 2021-07-16 15:31 | 70 | 008:38 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE MASIVO | M21071600006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 518 | 2021-07-16 | 36260 | keep | 0 | Jul | 2021 | 0.024697 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
HUMACAO | 2021-07-16 07:11 | 2021-07-16 13:42 | 302 | 006:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21071600004 | New_Event | Bad Weather | Include | Include | Weather | 391 | 2021-07-16 | 118082 | keep | 0 | Jul | 2021 | 0.080425 | 0.00020569 | Sustained | FALSE | TRUE | Not_TMED_Event | 302
MAYAGÃœEZ | 2021-07-16 07:18 | 2021-07-16 18:31 | 30 | 011:13 | P | LINEA DE TRANSMISION 38KV | SE ABRIO CORTE DE LINEA PARA TRABAJOS EN LINEAS 1500 Y 2000 | M21071600008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 673 | 2021-07-16 | 20190 | keep | 0 | Jul | 2021 | 0.013751 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-07-16 07:35 | 2021-07-16 10:38 | 75 | 003:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | M21071600010 | New_Event |  |  | Include | Wildlife | 183 | 2021-07-16 | 13725 | keep | 0 | Jul | 2021 | 0.009348 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
MAYAGÃœEZ | 2021-07-16 07:52 | 2021-07-16 16:12 | 20 | 008:20 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | M21071600015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 500 | 2021-07-16 | 10000 | keep | 0 | Jul | 2021 | 0.006811 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-07-16 07:53 | 2021-07-17 11:32 | 95 | 027:39 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21071600012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1659 | 2021-07-16 | 157605 | keep | 0 | Jul | 2021 | 0.10734 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
BAYAMON | 2021-07-16 08:00 | 2021-07-16 14:20 | 15 | 006:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE DE LA SECUNDARIA PORTATIL 8 | S21071600006 | New_Event | Secondary Wire Down | Include | Include | Equipment | 380 | 2021-07-16 | 5700 | keep | 0 | Jul | 2021 | 0.0038822 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-07-16 08:09 | 2021-07-16 10:44 | 5 | 002:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE DE TRANSFORMADOR SECUNDARIO | B21071600005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 155 | 2021-07-16 | 775 | keep | 0 | Jul | 2021 | 0.00052785 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-07-16 08:13 | 2021-07-16 10:29 | 1 | 002:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO PENCA DE LA LINEA | C21071600016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2021-07-16 | 136 | keep | 0 | Jul | 2021 | 9.2629e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-07-16 08:17 | 2021-07-16 11:28 | 1 | 003:11 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE DESGANCHO Y SE ELIMINO TENSOR VACANTE | C21071600017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2021-07-16 | 191 | keep | 0 | Jul | 2021 | 0.00013009 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-07-16 08:19 | 2021-07-16 14:35 | 10 | 006:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21071600018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 376 | 2021-07-16 | 3760 | keep | 0 | Jul | 2021 | 0.0025609 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-07-16 08:21 | 2021-07-16 17:54 | 100 | 009:33 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 100 EN RISER Y 1 RBA DE 80 AMP EN EL SU - 3 TERMINACION EN SU-3 | R21071600015 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 573 | 2021-07-16 | 57300 | keep | 0 | Jul | 2021 | 0.039027 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2021-07-16 08:24 | 2021-07-16 12:45 | 15 | 004:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21071600012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 261 | 2021-07-16 | 3915 | keep | 0 | Jul | 2021 | 0.0026665 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
SAN JUAN | 2021-07-16 08:33 | 2021-07-16 12:09 | 50 | 003:36 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S21071600015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 216 | 2021-07-16 | 10800 | keep | 0 | Jul | 2021 | 0.0073558 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-07-16 08:33 | 2021-07-16 17:24 | 35 | 008:51 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S21071600008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 531 | 2021-07-16 | 18585 | keep | 0 | Jul | 2021 | 0.012658 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
HUMACAO | 2021-07-16 08:42 | 2021-07-16 10:05 | 334 | 001:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CONDUCTOR PRIMARIO EN EL SUELO | C21071600021 | New_Event | Wire Down | Include | Include | Equipment | 83 | 2021-07-16 | 27722 | keep | 0 | Jul | 2021 | 0.018881 | 0.00022749 | Sustained | FALSE | FALSE | Not_TMED_Event | 334
PONCE | 2021-07-16 08:44 | 2021-07-16 13:06 | 10 | 004:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJAS PRIMARIAS | P21071600028 | New_Event | Cutout Failure | Include | Include | Equipment | 262 | 2021-07-16 | 2620 | keep | 0 | Jul | 2021 | 0.0017845 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-07-16 08:55 | 2021-07-16 17:28 | 90 | 008:33 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | M21071600034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 513 | 2021-07-16 | 46170 | keep | 0 | Jul | 2021 | 0.031446 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
SAN JUAN | 2021-07-16 08:56 | 2021-07-16 13:40 | 105 | 004:44 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA Y 2 X 65 EN CORTE DE LINEA | S21071600024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 284 | 2021-07-16 | 29820 | keep | 0 | Jul | 2021 | 0.02031 | 7.1515e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 105
BAYAMON | 2021-07-16 09:00 | 2021-07-16 12:20 | 20 | 003:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE LEVANTO CONDUCTOR EN EL PISO | S21071300057 | New_Event | Wire Down | Include | Include | Equipment | 200 | 2021-07-16 | 4000 | keep | 0 | Jul | 2021 | 0.0027244 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-07-16 09:03 | 2021-07-16 11:42 | 492 | 002:39 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21071600026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2021-07-16 | 78228 | keep | 0 | Jul | 2021 | 0.053281 | 0.0003351 | Sustained | FALSE | TRUE | Not_TMED_Event | 492
YAUCO | 2021-07-16 09:06 | 2021-07-16 12:18 | 50 | 003:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN RISER POR AVE CRUZAR FASE | P21071600009 | New_Event |  |  | Include | Wildlife | 192 | 2021-07-16 | 9600 | keep | 0 | Jul | 2021 | 0.0065385 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-07-16 09:07 | 2021-07-16 10:00 | 25 | 000:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE A TRANSFORMADOR | P21071600010 | New_Event | Wire Down | Include | Include | Equipment | 53 | 2021-07-16 | 1325 | keep | 0 | Jul | 2021 | 0.00090245 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2021-07-16 09:12 | 2021-07-16 10:54 | 10 | 001:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21071600027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 102 | 2021-07-16 | 1020 | keep | 0 | Jul | 2021 | 0.00069472 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-07-16 09:16 | 2021-07-16 11:45 | 20 | 002:29 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21071600021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2021-07-16 | 2980 | keep | 0 | Jul | 2021 | 0.0020297 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
AGUADILLA | 2021-07-16 09:20 | 2021-07-16 13:00 | 15 | 003:40 | P | DESGANCHE | SE ABRIO PUENTES PARA REALIZAR DESGANCHE MASIVO | M21071600038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2021-07-16 | 3300 | keep | 0 | Jul | 2021 | 0.0022476 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-07-16 09:23 | 2021-07-17 09:40 | 15 | 024:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M21071600041 | New_Event | Bad Weather | Include | Include | Weather | 1457 | 2021-07-16 | 21855 | keep | 0 | Jul | 2021 | 0.014885 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-07-16 09:47 | 2021-07-16 13:09 | 16 | 003:22 | P | DESGANCHE | 1 X 15 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21071500011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2021-07-16 | 3232 | keep | 0 | Jul | 2021 | 0.0022013 | 1.0898e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 16
ARECIBO | 2021-07-16 09:59 | 2021-07-16 12:30 | 8 | 002:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A21071600026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 151 | 2021-07-16 | 1208 | keep | 0 | Jul | 2021 | 0.00082276 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-07-16 10:00 | 2021-07-16 13:15 | 90 | 003:15 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21071600038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2021-07-16 | 17550 | keep | 0 | Jul | 2021 | 0.011953 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
HUMACAO | 2021-07-16 10:05 | 2021-07-16 12:52 | 1003 | 002:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE ABRIO CORTE DE LINEA TOTAL CON LB PARA LEVANTAR CONDUCTOR PRIMARIO DEL SUELO | C21071600021 | New_Event | Wire Down | Include | Include | Equipment | 167 | 2021-07-16 | 167501 | keep | 0 | Jul | 2021 | 0.11408 | 0.00068314 | Sustained | FALSE | TRUE | Not_TMED_Event | 1003
SAN JUAN | 2021-07-16 10:36 | 2021-07-17 10:37 | 25 | 024:01 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21071600141 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1441 | 2021-07-16 | 36025 | keep | 0 | Jul | 2021 | 0.024536 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-07-16 10:40 | 2021-07-16 16:20 | 1 | 005:40 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 EN CORTE DE LINEA SE REPARO AISLADOR ROTO | A21071600028 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 340 | 2021-07-16 | 340 | keep | 0 | Jul | 2021 | 0.00023157 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-07-16 10:45 | 2021-07-16 12:33 | 40 | 001:48 | P | HERRAJE ROTO O PODRIDO | SE ABRIO PUENTES PARA REMPLAZAR CRUCETA PODRIDA | A21071600033 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 108 | 2021-07-16 | 4320 | keep | 0 | Jul | 2021 | 0.0029423 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-07-16 10:50 | 2021-07-16 16:45 | 12 | 005:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO PUENTE ABIERTO EN LINEA SECUNDARIA | A21071600030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 355 | 2021-07-16 | 4260 | keep | 0 | Jul | 2021 | 0.0029015 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
CAGUAS | 2021-07-16 10:56 | 2021-07-16 14:31 | 1 | 003:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C21071600036 | New_Event |  |  | Include | Wildlife | 215 | 2021-07-16 | 215 | keep | 0 | Jul | 2021 | 0.00014644 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-07-16 11:10 | 2021-07-17 10:00 | 80 | 022:50 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21071600051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1370 | 2021-07-16 | 109600 | keep | 0 | Jul | 2021 | 0.074648 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-07-16 11:28 | 2021-07-17 18:38 | 18 | 031:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA EN EL PISO | P21071600025 | New_Event | Wire Down | Include | Include | Equipment | 1870 | 2021-07-16 | 33660 | keep | 0 | Jul | 2021 | 0.022926 | 1.226e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 18
ARECIBO | 2021-07-16 11:30 | 2021-07-16 11:51 | 10 | 000:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A21071600034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 21 | 2021-07-16 | 210 | keep | 0 | Jul | 2021 | 0.00014303 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-16 11:34 | 2021-07-16 19:30 | 30 | 007:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA SE RETIRO AVE | B21071600025 | New_Event |  |  | Include | Wildlife | 476 | 2021-07-16 | 14280 | keep | 0 | Jul | 2021 | 0.009726 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-07-16 11:41 | 2021-07-16 16:59 | 1 | 005:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN RISER SE REEMPLAZO CAJA PRIMARIA | C21071600045 | New_Event | Cutout Failure | Include | Include | Equipment | 318 | 2021-07-16 | 318 | keep | 0 | Jul | 2021 | 0.00021659 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-07-16 11:43 | 2021-07-16 16:14 | 30 | 004:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN CORTE DE LINEA SE RETEZO LINEA | B21071600027 | New_Event | Wire Down | Include | Include | Equipment | 271 | 2021-07-16 | 8130 | keep | 0 | Jul | 2021 | 0.0055373 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-07-16 12:03 | 2021-07-16 17:45 | 100 | 005:42 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21071600058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 342 | 2021-07-16 | 34200 | keep | 0 | Jul | 2021 | 0.023293 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-07-16 12:14 | 2021-07-16 16:18 | 40 | 004:04 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21071600045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 244 | 2021-07-16 | 9760 | keep | 0 | Jul | 2021 | 0.0066475 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-07-16 12:26 | 2021-07-16 12:30 | 3630 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR EN OPERACIONES PARA TRANSFERIR CARGAS SE VERIFICO PERSONAL SE CERRO INTERRUPTOR | M21071600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-07-16 | 14520 | keep | 0 | Jul | 2021 | 0.0098895 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
ARECIBO | 2021-07-16 12:45 | 2021-07-16 18:37 | 2 | 005:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A21071600032 | New_Event | Bad Weather | Include | Include | Weather | 352 | 2021-07-16 | 704 | keep | 0 | Jul | 2021 | 0.00047949 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2021-07-16 13:06 | 2021-07-16 17:21 | 10 | 004:15 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE SECUNDARIO | B21071600016 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 255 | 2021-07-16 | 2550 | keep | 0 | Jul | 2021 | 0.0017368 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-07-16 13:06 | 2021-07-16 13:07 | 1979 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210716000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-16 | 1979 | keep | 0 | Jul | 2021 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2021-07-16 13:06 | 2021-07-16 13:07 | 5069 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210716000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-16 | 5069 | keep | 0 | Jul | 2021 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2021-07-16 13:06 | 2021-07-16 13:07 | 5063 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21071600039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-16 | 5063 | keep | 0 | Jul | 2021 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
ARECIBO | 2021-07-16 13:07 | 2021-07-16 18:50 | 50 | 005:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA | A21071600037 | New_Event | Wire Down | Include | Include | Equipment | 343 | 2021-07-16 | 17150 | keep | 0 | Jul | 2021 | 0.011681 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-07-16 13:17 | 2021-07-16 15:18 | 5 | 002:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA AVERIADA | A21071600040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 121 | 2021-07-16 | 605 | keep | 0 | Jul | 2021 | 0.00041206 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-07-16 13:18 | 2021-07-16 16:00 | 7 | 002:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN TRANSFORMADOR MAL TEIMPO DESCARGAS ELECTRICAS | M21071600078 | New_Event | Bad Weather | Include | Include | Weather | 162 | 2021-07-16 | 1134 | keep | 0 | Jul | 2021 | 0.00077236 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2021-07-16 13:31 | 2021-07-16 16:17 | 8 | 002:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | C21071600035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 166 | 2021-07-16 | 1328 | keep | 0 | Jul | 2021 | 0.00090449 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
BAYAMON | 2021-07-16 13:35 | 2021-07-16 14:05 | 100 | 000:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIERON MACHETES PARA CERRAR PUENTE Y NORMALIZAR LAS CARGAS ENTRE EL 1711-02 Y 1716-03 | B21071600035 | New_Event | Wire Down | Include | Include | Equipment | 30 | 2021-07-16 | 3000 | keep | 0 | Jul | 2021 | 0.0020433 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2021-07-16 13:40 | 2021-07-16 13:41 | 215 | 000:01 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR SE CERRO POR SCADA | B21071600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-16 | 215 | keep | 0 | Jul | 2021 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2021-07-16 13:41 | 2021-07-16 17:05 | 60 | 003:24 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21071600037 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 204 | 2021-07-16 | 12240 | keep | 0 | Jul | 2021 | 0.0083366 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CANOVANAS | 2021-07-16 13:42 | 2021-07-16 14:18 | 10 | 000:36 | P | AISLADOR ROTO, PARTIDO O SAFADO | ABRIO CORTE DE LINEA PARA REMPLAZAR AISLADOR DEFECTUOSO Y RETEZAR LINEA | R21071600051 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 36 | 2021-07-16 | 360 | keep | 0 | Jul | 2021 | 0.00024519 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
SAN JUAN | 2021-07-16 13:44 | 2021-07-16 14:35 | 325 | 000:51 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE RETIRO RAMA Y SE CERRO POR SCADA | S21070600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 51 | 2021-07-16 | 16575 | keep | 0 | Jul | 2021 | 0.011289 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
ARECIBO | 2021-07-16 13:45 | 2021-07-16 16:25 | 15 | 002:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA PARTIDA | A21071600044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 160 | 2021-07-16 | 2400 | keep | 0 | Jul | 2021 | 0.0016346 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
GUAYAMA | 2021-07-16 13:51 | 2021-07-16 17:00 | 40 | 003:09 | P | NO SE REPORTO CAUSA | 1 FUSE DE 40 EN C/L CABLES CRUZADOS | P21071600040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 189 | 2021-07-16 | 7560 | keep | 0 | Jul | 2021 | 0.0051491 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-07-16 13:52 | 2021-07-16 14:28 | 5 | 000:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21071600033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 36 | 2021-07-16 | 180 | keep | 0 | Jul | 2021 | 0.0001226 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-07-16 14:02 | 2021-07-16 15:55 | 7 | 001:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR RISER SECUNDARIO Y SE REEMPLAZO 3 BARRAS EN PEDESTAL | C21071600033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 113 | 2021-07-16 | 791 | keep | 0 | Jul | 2021 | 0.00053875 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-07-16 14:12 | 2021-07-16 18:44 | 75 | 004:32 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | M21071600093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 272 | 2021-07-16 | 20400 | keep | 0 | Jul | 2021 | 0.013894 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BARRANQUITAS | 2021-07-16 14:16 | 2021-07-16 18:18 | 5 | 004:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 8 EN TRANSFORMADOR SE CERRO PUENTE DE LINEA A CAJA Y REPARARON SECUNDARIA | C21071600051 | New_Event | Wire Down | Include | Include | Equipment | 242 | 2021-07-16 | 1210 | keep | 0 | Jul | 2021 | 0.00082413 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
CANOVANAS | 2021-07-16 14:19 | 2021-07-16 17:31 | 40 | 003:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | R21071600060 | New_Event |  |  | Include | Wildlife | 192 | 2021-07-16 | 7680 | keep | 0 | Jul | 2021 | 0.0052308 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-16 14:21 | 2021-07-16 15:56 | 10 | 001:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO SECUNDARIA Y PUENTE DE LINEA A CAJA | S21071600000 | New_Event | Wire Down | Include | Include | Equipment | 95 | 2021-07-16 | 950 | keep | 0 | Jul | 2021 | 0.00064704 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-07-16 14:23 | 2021-07-16 18:55 | 101 | 004:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR IGUANA | C21071600052 | New_Event |  |  | Include | Wildlife | 272 | 2021-07-16 | 27472 | keep | 0 | Jul | 2021 | 0.018711 | 6.8791e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 101
AGUADILLA | 2021-07-16 14:30 | 2021-07-16 17:03 | 693 | 002:33 | T | BREAKER DEFECTUOSO O NO OPERA | DISPARO DE INTERRUPTOR AVERIADO SE PASO LA CARGA AL 7002-02 | M21071600100 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 153 | 2021-07-16 | 106029 | keep | 0 | Jul | 2021 | 0.072216 | 0.000472 | Sustained | FALSE | FALSE | Not_TMED_Event | 693
MAYAGÃœEZ | 2021-07-16 14:41 | 2021-07-16 19:09 | 75 | 004:28 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21071600111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2021-07-16 | 20100 | keep | 0 | Jul | 2021 | 0.01369 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
UTUADO | 2021-07-16 14:42 | 2021-07-16 19:28 | 40 | 004:46 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUAS | A21071600049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 286 | 2021-07-16 | 11440 | keep | 0 | Jul | 2021 | 0.0077917 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-07-16 14:47 | 2021-07-16 18:36 | 35 | 003:49 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | M21071600115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2021-07-16 | 8015 | keep | 0 | Jul | 2021 | 0.005459 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
PONCE | 2021-07-16 14:50 | 2021-07-16 18:41 | 100 | 003:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON 3 CAJAS PRIMARIAS | P2107160046 | New_Event | Cutout Failure | Include | Include | Equipment | 231 | 2021-07-16 | 23100 | keep | 0 | Jul | 2021 | 0.015733 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2021-07-16 15:05 | 2021-07-16 16:51 | 5 | 001:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 10 EN TRANSFORMADOR REPARO BAJANTE DE LINEA A CAJA WR - 5896132 | R21071600000 | New_Event | Wire Down | Include | Include | Equipment | 106 | 2021-07-16 | 530 | keep | 0 | Jul | 2021 | 0.00036098 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
PONCE | 2021-07-16 15:10 | 2021-07-16 18:00 | 100 | 002:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PRIMARIO | P21071600036 | New_Event | Wire Down | Include | Include | Equipment | 170 | 2021-07-16 | 17000 | keep | 0 | Jul | 2021 | 0.011579 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-07-16 15:20 | 2021-07-16 19:21 | 100 | 004:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA REMPLAZO DISCO PARTIDO | R21071600068 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 241 | 2021-07-16 | 24100 | keep | 0 | Jul | 2021 | 0.016414 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-07-16 15:26 | 2021-07-16 16:43 | 15 | 001:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | M21071600000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 77 | 2021-07-16 | 1155 | keep | 0 | Jul | 2021 | 0.00078667 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-07-16 15:37 | 2021-07-17 09:22 | 8 | 017:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BARRA EN PEDESTAL | R21071600069 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1065 | 2021-07-16 | 8520 | keep | 0 | Jul | 2021 | 0.0058029 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2021-07-16 15:38 | 2021-07-16 18:04 | 25 | 002:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21071600060 | New_Event | Bad Weather | Include | Include | Weather | 146 | 2021-07-16 | 3650 | keep | 0 | Jul | 2021 | 0.002486 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-07-16 15:40 | 2021-07-16 16:00 | 40 | 000:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21071600061 | New_Event | Bad Weather | Include | Include | Weather | 20 | 2021-07-16 | 800 | keep | 0 | Jul | 2021 | 0.00054488 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-07-16 15:45 | 2021-07-16 19:25 | 25 | 003:40 | P | HERRAJE ROTO O PODRIDO | SE REMPLAZO CRUCETA PARTIDA | M21071600000 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 220 | 2021-07-16 | 5500 | keep | 0 | Jul | 2021 | 0.003746 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2021-07-16 15:47 | 2021-07-16 18:30 | 20 | 002:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21071600062 | New_Event | Bad Weather | Include | Include | Weather | 163 | 2021-07-16 | 3260 | keep | 0 | Jul | 2021 | 0.0022204 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-07-16 15:56 | 2021-07-17 14:08 | 200 | 022:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE LEVANTO CONDUCTOR EN EL SUELO | S21071600070 | New_Event | Wire Down | Include | Include | Equipment | 1332 | 2021-07-16 | 266400 | keep | 0 | Jul | 2021 | 0.18144 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-07-16 16:01 | 2021-07-16 22:58 | 125 | 006:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21071600159 | New_Event | Bad Weather | Include | Include | Weather | 417 | 2021-07-16 | 52125 | keep | 0 | Jul | 2021 | 0.035502 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
MAYAGÃœEZ | 2021-07-16 16:02 | 2021-07-17 12:00 | 45 | 019:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA | M21071600209 | New_Event | Wire Down | Include | Include | Equipment | 1198 | 2021-07-16 | 53910 | keep | 0 | Jul | 2021 | 0.036718 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
AGUADILLA | 2021-07-16 16:02 | 2021-07-17 16:27 | 11 | 024:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21071600064 | New_Event | Bad Weather | Include | Include | Weather | 1465 | 2021-07-16 | 16115 | keep | 0 | Jul | 2021 | 0.010976 | 7.492e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 11
UTUADO | 2021-07-16 16:15 | 2021-07-16 17:30 | 70 | 001:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21071600066 | New_Event | Bad Weather | Include | Include | Weather | 75 | 2021-07-16 | 5250 | keep | 0 | Jul | 2021 | 0.0035758 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
HUMACAO | 2021-07-16 16:19 | 2021-07-16 18:13 | 7 | 001:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | C21071600055 | New_Event |  |  | Include | Wildlife | 114 | 2021-07-16 | 798 | keep | 0 | Jul | 2021 | 0.00054351 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-07-16 16:19 | 2021-07-16 23:25 | 80 | 007:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21071600163 | New_Event | Bad Weather | Include | Include | Weather | 426 | 2021-07-16 | 34080 | keep | 0 | Jul | 2021 | 0.023212 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-07-16 16:20 | 2021-07-16 17:25 | 117 | 001:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 Y 2 X 50 EN CORTES DE LINEA CRUCE POR PALOMA | C21071600056 | New_Event |  |  | Include | Wildlife | 65 | 2021-07-16 | 7605 | keep | 0 | Jul | 2021 | 0.0051797 | 7.9688e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 117
AGUADILLA | 2021-07-16 16:29 | 2021-07-16 16:30 | 1336 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21071600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-16 | 1336 | keep | 0 | Jul | 2021 | 0.00090994 | 0.00090994 | Momentary | FALSE | FALSE | Not_TMED_Event | 1336
AGUADILLA | 2021-07-16 16:31 | 2021-07-16 17:49 | 1155 | 001:18 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR LINEA PARTIDA EN TRONCAL | M21071600000 | New_Event | Wire Down | Include | Include | Equipment | 78 | 2021-07-16 | 90090 | keep | 0 | Jul | 2021 | 0.06136 | 0.00078667 | Sustained | FALSE | TRUE | Not_TMED_Event | 1155
BAYAMON | 2021-07-16 16:32 | 2021-07-16 20:10 | 35 | 003:38 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21071600044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 218 | 2021-07-16 | 7630 | keep | 0 | Jul | 2021 | 0.0051968 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
HUMACAO | 2021-07-16 16:36 | 2021-07-16 17:17 | 20 | 000:41 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANFORMADOR SE AJUSTO BUSHING SECUNDARIO Y REPARARON BAJANTE | C21071600046 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 41 | 2021-07-16 | 820 | keep | 0 | Jul | 2021 | 0.0005585 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-07-16 16:42 | 2021-07-16 19:28 | 10 | 002:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE CERRO BAJANTE SECUNDARIO | B21071600045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 166 | 2021-07-16 | 1660 | keep | 0 | Jul | 2021 | 0.0011306 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-07-16 16:47 | 2021-07-17 13:18 | 17 | 020:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA ABIERTA | C21071600061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1231 | 2021-07-16 | 20927 | keep | 0 | Jul | 2021 | 0.014253 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
MAYAGÃœEZ | 2021-07-16 16:59 | 2021-07-17 13:00 | 150 | 020:01 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21071600173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1201 | 2021-07-16 | 180150 | keep | 0 | Jul | 2021 | 0.1227 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-07-16 17:18 | 2021-07-16 18:38 | 30 | 001:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE RETIRO BOMBAS DE CUMPLEAÃ‘OS QUE CRUZARON LA LINEA | A21071600070 | New_Event |  |  | Include | Wildlife | 80 | 2021-07-16 | 2400 | keep | 0 | Jul | 2021 | 0.0016346 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
YAUCO | 2021-07-16 17:41 | 2021-07-17 10:30 | 81 | 016:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN CORTE DE LINEA CRUCE DE LINEA | P21071600053 | New_Event | Wire Down | Include | Include | Equipment | 1009 | 2021-07-16 | 81729 | keep | 0 | Jul | 2021 | 0.055665 | 5.5169e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 81
MAYAGÃœEZ | 2021-07-16 17:42 | 2021-07-17 11:30 | 80 | 017:48 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21071600185 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1068 | 2021-07-16 | 85440 | keep | 0 | Jul | 2021 | 0.058193 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-07-16 18:05 | 2021-07-17 08:16 | 40 | 014:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE CORRIGIO LINEA CRUZADA | M21071600189 | New_Event | Wire Down | Include | Include | Equipment | 851 | 2021-07-16 | 34040 | keep | 0 | Jul | 2021 | 0.023184 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-07-16 18:17 | 2021-07-17 14:29 | 60 | 020:12 | P | DESGANCHE | 1 X 25 Y 1 X 50 EN CORTES DE LINEA | C21071600067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1212 | 2021-07-16 | 72720 | keep | 0 | Jul | 2021 | 0.049529 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-07-16 18:27 | 2021-07-16 18:35 | 620 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7100 | S21071600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-07-16 | 4960 | keep | 0 | Jul | 2021 | 0.0033782 | 0.00042228 | Sustained | FALSE | TRUE | Not_TMED_Event | 620
BAYAMON | 2021-07-16 18:27 | 2021-07-16 18:35 | 451 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7100 | S21071600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-07-16 | 3608 | keep | 0 | Jul | 2021 | 0.0024574 | 0.00030717 | Sustained | FALSE | TRUE | Not_TMED_Event | 451
BAYAMON | 2021-07-16 18:27 | 2021-07-16 18:35 | 333 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7100 | S21071600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-07-16 | 2664 | keep | 0 | Jul | 2021 | 0.0018144 | 0.0002268 | Sustained | FALSE | TRUE | Not_TMED_Event | 333
SAN JUAN | 2021-07-16 18:27 | 2021-07-16 18:28 | 5290 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR 1336-08 QUE A SU VEZ LLEVA LA CARGA DEL 1336-09 | S21071600000 | New_Event |  |  | Include | Wildlife | 1 | 2021-07-16 | 5290 | keep | 0 | Jul | 2021 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2021-07-16 18:27 | 2021-07-16 18:28 | 207 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE CARGA POR EL 1336-08 | S21071600000 | New_Event |  |  | Include | Wildlife | 1 | 2021-07-16 | 207 | keep | 0 | Jul | 2021 | 0.00014099 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2021-07-16 18:34 | 2021-07-16 21:56 | 435 | 003:22 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO DEBIDO A AVERIA DE ARBOL SOBRE LA LINEA ABRIENDO PUENTE Y SE CERRO POR SCADA | S21071600095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2021-07-16 | 87870 | keep | 0 | Jul | 2021 | 0.059848 | 0.00029628 | Sustained | FALSE | TRUE | Not_TMED_Event | 435
MAYAGÃœEZ | 2021-07-16 18:37 | 2021-07-17 13:04 | 15 | 018:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | M21071600193 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1107 | 2021-07-16 | 16605 | keep | 0 | Jul | 2021 | 0.01131 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
AGUADILLA | 2021-07-16 18:41 | 2021-07-17 14:27 | 90 | 019:46 | P | DESGANCHE | SE REALIZO DESGANCHE EN LINEA PRIMARIA | M21071600197 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1186 | 2021-07-16 | 106740 | keep | 0 | Jul | 2021 | 0.0727 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
VEGA BAJA | 2021-07-16 18:41 | 2021-07-17 12:15 | 12 | 017:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO PUENTE SECUNDARIO | B21071600048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1054 | 2021-07-16 | 12648 | keep | 0 | Jul | 2021 | 0.0086145 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-07-16 18:58 | 2021-07-16 19:12 | 5290 | 000:14 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO INTERRUPTOR EN EMERGENCIA POR POSTE EN EL SUELO SE SECCIONALIZO AVERIA Y SE CERRO POR SCADA 5% FUERA | S21071600000 | 1st_after_momentary |  |  | Include | Wildlife | 14 | 2021-07-16 | 74060 | keep | 0 | Jul | 2021 | 0.050442 | 0.003603 | Sustained | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2021-07-16 18:58 | 2021-07-16 19:12 | 207 | 000:14 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO INTERRUPTOR EN EMERGENCIA POR POSTE EN EL SUELO SE SECCIONALIZO AVERIA Y SE CERRO POR SCADA CARGA POR EL 1336-08 | S21071600000 | 1st_after_momentary |  |  | Include | Wildlife | 14 | 2021-07-16 | 2898 | keep | 0 | Jul | 2021 | 0.0019738 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
ARECIBO | 2021-07-16 18:58 | 2021-07-16 19:12 | 2697 | 000:14 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR SE CONFIRMO PERSONAL FUERA DE PELIGRO SE REALIZO PRUEBA Y QUEDO EN SERVICIO | A21071600080 | New_Event | Bad Weather | Include | Include | Weather | 14 | 2021-07-16 | 37758 | keep | 0 | Jul | 2021 | 0.025717 | 0.0018369 | Sustained | FALSE | FALSE | Not_TMED_Event | 2697
BARRANQUITAS | 2021-07-16 19:00 | 2021-07-16 20:54 | 5 | 001:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RETIRO CARGA A TRANSFORMADOR PARA LEVANTAR NEUTRAL PRIMARIO | C21071600049 | New_Event | Wire Down | Include | Include | Equipment | 114 | 2021-07-16 | 570 | keep | 0 | Jul | 2021 | 0.00038822 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-07-16 19:10 | 2021-07-16 19:11 | 1026 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21071600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-16 | 1026 | keep | 0 | Jul | 2021 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
SAN JUAN | 2021-07-16 19:12 | 2021-07-16 23:02 | 2000 | 003:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REMPLAZO POSTE IMPACTADO POR AUTO | S21071600000 | Partial_restoration |  |  | Include | Wildlife | 230 | 2021-07-16 | 460000 | keep | 0 | Jul | 2021 | 0.3133 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-07-16 19:12 | 2021-07-16 20:22 | 150 | 001:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | A21071600075 | Partial_restoration | Bad Weather | Include | Include | Weather | 70 | 2021-07-16 | 10500 | keep | 0 | Jul | 2021 | 0.0071515 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-07-16 19:34 | 2021-07-17 19:12 | 1 | 023:38 | P | NO SE REPORTO CAUSA | 1 X 80 Y SE REENMPLAZO CAJA | S21071600138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1418 | 2021-07-16 | 1418 | keep | 0 | Jul | 2021 | 0.00096579 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-07-16 19:41 | 2021-07-16 20:50 | 20 | 001:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO | M21071600140 | New_Event | Wire Down | Include | Include | Equipment | 69 | 2021-07-16 | 1380 | keep | 0 | Jul | 2021 | 0.00093991 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-07-16 19:47 | 2021-07-17 15:32 | 10 | 019:45 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21071600051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1185 | 2021-07-16 | 11850 | keep | 0 | Jul | 2021 | 0.008071 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2021-07-16 20:18 | 2021-07-17 09:00 | 240 | 012:42 | P | DESGANCHE | 1 X 40 1 X 65 EN CORTE DE LINEA | P21071500058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 762 | 2021-07-16 | 182880 | keep | 0 | Jul | 2021 | 0.12456 | 0.00016346 | Sustained | FALSE | TRUE | Not_TMED_Event | 240
BAYAMON | 2021-07-16 20:40 | 2021-07-17 01:28 | 3708 | 004:48 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA DE TRANSMISION | S21071600137 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 288 | 2021-07-16 | 1067904 | keep | 0 | Jul | 2021 | 0.72734 | 0.0025255 | Sustained | FALSE | TRUE | Not_TMED_Event | 3708
BAYAMON | 2021-07-16 20:40 | 2021-07-17 01:28 | 24 | 004:48 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA DE TRANSMISION | S21071600137 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 288 | 2021-07-16 | 6912 | keep | 0 | Jul | 2021 | 0.0047077 | 1.6346e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 24
BAYAMON | 2021-07-16 20:40 | 2021-07-17 01:28 | 1 | 004:48 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA DE TRANSMISION | S21071600137 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 288 | 2021-07-16 | 288 | keep | 0 | Jul | 2021 | 0.00019616 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
PONCE | 2021-07-16 20:40 | 2021-07-16 22:17 | 8 | 001:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO A CAJA EN TRANSFORMADOR | P21071600059 | New_Event | Wire Down | Include | Include | Equipment | 97 | 2021-07-16 | 776 | keep | 0 | Jul | 2021 | 0.00052853 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-07-16 21:03 | 2021-07-17 10:10 | 300 | 013:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21071700010 | New_Event | Bad Weather | Include | Include | Weather | 787 | 2021-07-16 | 236100 | keep | 0 | Jul | 2021 | 0.16081 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-07-16 21:03 | 2021-07-17 10:10 | 8 | 013:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21071600202 | New_Event | Bad Weather | Include | Include | Weather | 787 | 2021-07-16 | 6296 | keep | 0 | Jul | 2021 | 0.0042882 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
VEGA BAJA | 2021-07-16 21:47 | 2021-07-17 15:40 | 10 | 017:53 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21071600054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1073 | 2021-07-16 | 10730 | keep | 0 | Jul | 2021 | 0.0073082 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-07-16 21:48 | 2021-07-17 17:40 | 100 | 019:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 40 EN CORTE DE LINEA SE REEMPLAZARON 3 CAJAS QUEMADAS | S21071600164 | New_Event | Cutout Failure | Include | Include | Equipment | 1192 | 2021-07-16 | 119200 | keep | 0 | Jul | 2021 | 0.081187 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-16 21:56 | 2021-07-17 12:18 | 400 | 014:22 | P | DESGANCHE | SE LEVANTO CONDUCTOR PRIMARIO | S21071600141 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 862 | 2021-07-16 | 344800 | keep | 0 | Jul | 2021 | 0.23484 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-07-16 21:59 | 2021-07-18 09:42 | 25 | 035:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21071600219 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2143 | 2021-07-16 | 53575 | keep | 0 | Jul | 2021 | 0.03649 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CAGUAS | 2021-07-16 23:04 | 2021-07-16 23:05 | 2859 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21071600070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-16 | 2859 | keep | 0 | Jul | 2021 | 0.0019473 | 0.0019473 | Momentary | FALSE | FALSE | Not_TMED_Event | 2859
MAYAGÃœEZ | 2021-07-16 23:09 | 2021-07-17 16:30 | 15 | 017:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21071600223 | New_Event | Bad Weather | Include | Include | Weather | 1041 | 2021-07-16 | 15615 | keep | 0 | Jul | 2021 | 0.010635 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
SAN JUAN | 2021-07-17 00:31 | 2021-07-18 13:47 | 27 | 037:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21071700001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2236 | 2021-07-17 | 60372 | keep | 0 | Jul | 2021 | 0.041119 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
PONCE | 2021-07-17 01:01 | 2021-07-17 01:02 | 396 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P21071700002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-17 | 396 | keep | 0 | Jul | 2021 | 0.00026971 | 0.00026971 | Momentary | FALSE | FALSE | Not_TMED_Event | 396
BAYAMON | 2021-07-17 01:15 | 2021-07-17 10:19 | 390 | 009:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO DOS CAJAS PRIMARIAS | S21071700007 | New_Event | Cutout Failure | Include | Include | Equipment | 544 | 2021-07-17 | 212160 | keep | 0 | Jul | 2021 | 0.1445 | 0.00026563 | Sustained | FALSE | TRUE | Not_TMED_Event | 390
BARRANQUITAS | 2021-07-17 01:45 | 2021-07-17 11:20 | 125 | 009:35 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | C21071700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 575 | 2021-07-17 | 71875 | keep | 0 | Jul | 2021 | 0.048954 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
FAJARDO | 2021-07-17 02:01 | 2021-07-17 04:17 | 2343 | 002:16 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO POSTE PARTIDO POR IMPACTO DE AUTO | R21071700000 | New_Event |  |  | Include | Wildlife | 136 | 2021-07-17 | 318648 | keep | 0 | Jul | 2021 | 0.21703 | 0.0015958 | Sustained | FALSE | FALSE | Not_TMED_Event | 2343
HUMACAO | 2021-07-17 02:45 | 2021-07-17 10:38 | 1 | 007:53 | P | NO SE REPORTO CAUSA | 1 X 25 EN BANCO DE TRANSFORMADOR | C21071700003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 473 | 2021-07-17 | 473 | keep | 0 | Jul | 2021 | 0.00032216 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-07-17 02:55 | 2021-07-17 09:35 | 86 | 006:40 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C21071700004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 400 | 2021-07-17 | 34400 | keep | 0 | Jul | 2021 | 0.02343 | 5.8574e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 86
BAYAMON | 2021-07-17 02:56 | 2021-07-18 14:28 | 10 | 035:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO TRANSFORMADOR Y SE REEMPLAZARON CAJAS QUEMADAS Y BAJANTE SECUNDARIO | B21071700009 | New_Event | Cutout Failure | Include | Include | Equipment | 2132 | 2021-07-17 | 21320 | keep | 0 | Jul | 2021 | 0.014521 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-07-17 03:00 | 2021-07-17 03:01 | 2675 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21071700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-17 | 2675 | keep | 0 | Jul | 2021 | 0.0018219 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
SAN JUAN | 2021-07-17 03:35 | 2021-07-17 03:36 | 1026 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21071700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-17 | 1026 | keep | 0 | Jul | 2021 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
PONCE | 2021-07-17 03:57 | 2021-07-17 03:58 | 1478 | 000:01 | T | RELEVO DE CARGA AUTOMATICO | RECIERRE | P21071500006 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 1 | 2021-07-17 | 1478 | keep | 0 | Jul | 2021 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
BAYAMON | 2021-07-17 04:09 | 2021-07-17 04:10 | 1802 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO | S21071700011 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-07-17 | 1802 | keep | 0 | Jul | 2021 | 0.0012273 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
BAYAMON | 2021-07-17 04:10 | 2021-07-18 10:50 | 52 | 030:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | S21071700050 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1840 | 2021-07-17 | 95680 | keep | 0 | Jul | 2021 | 0.065167 | 3.5417e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 52
FAJARDO | 2021-07-17 04:17 | 2021-07-17 13:44 | 1991 | 009:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO POSTE PARTIDO POR IMPACTO DE AUTO | R21071700020 | Partial_restoration |  |  | Include | Wildlife | 567 | 2021-07-17 | 1128897 | keep | 0 | Jul | 2021 | 0.76889 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-17 06:00 | 2021-07-17 18:15 | 130 | 012:15 | P | LINEA DE TRANSMISION 38KV | SE ABRIO CORTE DE LINEA PARA TRABAJOS EN LA LINEAS DE TRANSMISION 1500 Y 2000 | M21007170004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 735 | 2021-07-17 | 95550 | keep | 0 | Jul | 2021 | 0.065079 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
MAYAGÃœEZ | 2021-07-17 06:10 | 2021-07-17 17:54 | 25 | 011:44 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA DESGANCHAR EN LINEA 1500 Y 2000 | M21071700003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 704 | 2021-07-17 | 17600 | keep | 0 | Jul | 2021 | 0.011987 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
PONCE | 2021-07-17 06:20 | 2021-07-17 10:00 | 106 | 003:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO FASES | P21071700004 | New_Event |  |  | Include | Wildlife | 220 | 2021-07-17 | 23320 | keep | 0 | Jul | 2021 | 0.015883 | 7.2196e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 106
ARECIBO | 2021-07-17 06:41 | 2021-07-17 13:30 | 20 | 006:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 25 EN TRANSFORMADOR SECUNDARIA AVERIADA | A21071700003 | New_Event | Secondary Wire Down | Include | Include | Equipment | 409 | 2021-07-17 | 8180 | keep | 0 | Jul | 2021 | 0.0055714 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-07-17 07:06 | 2021-07-17 16:49 | 15 | 009:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | C21071700007 | New_Event |  |  | Include | Wildlife | 583 | 2021-07-17 | 8745 | keep | 0 | Jul | 2021 | 0.0059562 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
HUMACAO | 2021-07-17 07:07 | 2021-07-17 13:10 | 140 | 006:03 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN CORTES DE LINEAS | C21071700008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 363 | 2021-07-17 | 50820 | keep | 0 | Jul | 2021 | 0.034613 | 9.5353e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 140
CAGUAS | 2021-07-17 07:12 | 2021-07-17 15:36 | 50 | 008:24 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO CAUSA | C21071700010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 504 | 2021-07-17 | 25200 | keep | 0 | Jul | 2021 | 0.017164 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-17 07:16 | 2021-07-19 11:15 | 20 | 051:59 | P | NO SE REPORTO CAUSA | 2 X 15 EN TRANSFORMADOR | S21071700010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3119 | 2021-07-17 | 62380 | keep | 0 | Jul | 2021 | 0.042487 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2021-07-17 07:23 | 2021-07-18 11:03 | 12 | 027:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21071700008 | New_Event | Bad Weather | Include | Include | Weather | 1660 | 2021-07-17 | 19920 | keep | 0 | Jul | 2021 | 0.013567 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2021-07-17 07:28 | 2021-07-17 15:09 | 41 | 007:41 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO CAUSA | C21071700012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 461 | 2021-07-17 | 18901 | keep | 0 | Jul | 2021 | 0.012873 | 2.7925e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 41
VEGA BAJA | 2021-07-17 07:43 | 2021-07-17 07:48 | 215 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21071700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-07-17 | 1075 | keep | 0 | Jul | 2021 | 0.00073218 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
CANOVANAS | 2021-07-17 07:50 | 2021-07-17 10:03 | 50 | 002:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R21071700024 | New_Event |  |  | Include | Wildlife | 133 | 2021-07-17 | 6650 | keep | 0 | Jul | 2021 | 0.0045293 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-07-17 07:53 | 2021-07-17 19:34 | 7 | 011:41 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA X 50 KVA | C21071700014 | New_Event | Service Transformer Failure | Include | Include | Equipment | 701 | 2021-07-17 | 4907 | keep | 0 | Jul | 2021 | 0.0033421 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2021-07-17 08:17 | 2021-07-17 11:45 | 59 | 003:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA RECONECTAR PUENTE SAFADO | P21071700007 | New_Event | Wire Down | Include | Include | Equipment | 208 | 2021-07-17 | 12272 | keep | 0 | Jul | 2021 | 0.0083584 | 4.0185e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 59
BAYAMON | 2021-07-17 08:19 | 2021-07-17 12:31 | 50 | 004:12 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21071700005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 252 | 2021-07-17 | 12600 | keep | 0 | Jul | 2021 | 0.0085818 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-17 08:24 | 2021-07-17 17:00 | 3 | 008:36 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERAS | M21071600024 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 516 | 2021-07-17 | 1548 | keep | 0 | Jul | 2021 | 0.0010543 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-07-17 08:38 | 2021-07-17 13:14 | 45 | 004:36 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21071700085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 276 | 2021-07-17 | 12420 | keep | 0 | Jul | 2021 | 0.0084592 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
ARECIBO | 2021-07-17 08:46 | 2021-07-18 10:00 | 200 | 025:14 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21071700046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1514 | 2021-07-17 | 302800 | keep | 0 | Jul | 2021 | 0.20624 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-07-17 08:51 | 2021-07-17 11:22 | 15 | 002:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21071400028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 151 | 2021-07-17 | 2265 | keep | 0 | Jul | 2021 | 0.0015427 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2021-07-17 08:54 | 2021-07-17 16:39 | 7 | 007:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CAMION IMPACTO POSTE | A21071700017 | New_Event |  |  | Include | Wildlife | 465 | 2021-07-17 | 3255 | keep | 0 | Jul | 2021 | 0.002217 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-07-17 08:58 | 2021-07-17 13:41 | 592 | 004:43 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO | R21071700029 | New_Event | Bad Weather | Include | Include | Weather | 283 | 2021-07-17 | 167536 | keep | 0 | Jul | 2021 | 0.11411 | 0.00040321 | Sustained | FALSE | TRUE | Not_TMED_Event | 592
BAYAMON | 2021-07-17 09:03 | 2021-07-17 12:14 | 12 | 003:11 | P | SECUNDARIA/DESGANCHE | SE REPARO BAJANTE Y SE REALIZO DESGANCHE | S21071700033 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 191 | 2021-07-17 | 2292 | keep | 0 | Jul | 2021 | 0.0015611 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-07-17 09:06 | 2021-07-17 09:07 | 1362 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21071700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-17 | 1362 | keep | 0 | Jul | 2021 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
ARECIBO | 2021-07-17 09:16 | 2021-07-17 09:17 | 2697 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21071700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-17 | 2697 | keep | 0 | Jul | 2021 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
PONCE | 2021-07-17 09:17 | 2021-07-17 14:27 | 979 | 005:10 | P | DESGANCHE | 2 X 140 EN CORTE DE LINEA | P21071700012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 310 | 2021-07-17 | 303490 | keep | 0 | Jul | 2021 | 0.20671 | 0.00066679 | Sustained | FALSE | TRUE | Not_TMED_Event | 979
AGUADILLA | 2021-07-17 09:30 | 2021-07-17 11:40 | 200 | 002:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO CORTE DE LINEA PARA REMOVER POSTE DE TELEFONOS SOBRE LAS LINEAS | M21071700015 | New_Event |  |  | Include | Wildlife | 130 | 2021-07-17 | 26000 | keep | 0 | Jul | 2021 | 0.017708 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-07-17 09:34 | 2021-07-17 11:18 | 10 | 001:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21071700006 | New_Event | Secondary Wire Down | Include | Include | Equipment | 104 | 2021-07-17 | 1040 | keep | 0 | Jul | 2021 | 0.00070834 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-07-17 10:06 | 2021-07-17 10:39 | 2106 | 000:33 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO INTERRUPTOR SE SECCIONALIZO TENSOR IMPACTADO POR MAQUINA CERRADO POR CONTROL | R21071700040 | New_Event |  |  | Include | Wildlife | 33 | 2021-07-17 | 69498 | keep | 0 | Jul | 2021 | 0.047335 | 0.0014344 | Sustained | FALSE | FALSE | Not_TMED_Event | 2106
MAYAGÃœEZ | 2021-07-17 10:15 | 2021-07-17 15:13 | 100 | 004:58 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21071700006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 298 | 2021-07-17 | 29800 | keep | 0 | Jul | 2021 | 0.020297 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-07-17 10:33 | 2021-07-17 12:20 | 6 | 001:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR REPARO SECUNDARIA ABIERTA | C21071700028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 107 | 2021-07-17 | 642 | keep | 0 | Jul | 2021 | 0.00043726 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2021-07-17 10:39 | 2021-07-17 11:42 | 1895 | 001:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE RETIRO TENSOR IMPACTADO CRUZADO CON LA LINEA SE CERRO MACHETES | R21071700040 | Partial_restoration |  |  | Include | Wildlife | 63 | 2021-07-17 | 119385 | keep | 0 | Jul | 2021 | 0.081313 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-07-17 10:51 | 2021-07-17 13:34 | 80 | 002:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C21071700027 | New_Event |  |  | Include | Wildlife | 163 | 2021-07-17 | 13040 | keep | 0 | Jul | 2021 | 0.0088815 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-07-17 10:55 | 2021-07-17 14:19 | 315 | 003:24 | T | DESGANCHE | SE PATRULLO SE RETIRO RAMA SOBRE LINEA Y SE CERRO POR SCADA | S21071700064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2021-07-17 | 64260 | keep | 0 | Jul | 2021 | 0.043767 | 0.00021455 | Sustained | FALSE | TRUE | Not_TMED_Event | 315
MAYAGÃœEZ | 2021-07-17 10:59 | 2021-07-17 17:00 | 7 | 006:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | M21071700030 | New_Event | Bad Weather | Include | Include | Weather | 361 | 2021-07-17 | 2527 | keep | 0 | Jul | 2021 | 0.0017211 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-07-17 11:02 | 2021-07-17 17:00 | 15 | 005:58 | P | NO SE REPORTO CAUSA | 2 X 80 EN SU-B | B21071700011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 358 | 2021-07-17 | 5370 | keep | 0 | Jul | 2021 | 0.0036575 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2021-07-17 11:04 | 2021-07-17 16:08 | 60 | 005:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA | P21071700017 | New_Event | Cutout Failure | Include | Include | Equipment | 304 | 2021-07-17 | 18240 | keep | 0 | Jul | 2021 | 0.012423 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BARRANQUITAS | 2021-07-17 11:07 | 2021-07-17 13:50 | 60 | 002:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21071700030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2021-07-17 | 9780 | keep | 0 | Jul | 2021 | 0.0066611 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-07-17 11:16 | 2021-07-17 12:36 | 14 | 001:20 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | A21071700018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2021-07-17 | 1120 | keep | 0 | Jul | 2021 | 0.00076283 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2021-07-17 11:25 | 2021-07-17 14:13 | 60 | 002:48 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21071700034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2021-07-17 | 10080 | keep | 0 | Jul | 2021 | 0.0068654 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-07-17 11:43 | 2021-07-17 11:44 | 73 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21071700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-17 | 73 | keep | 0 | Jul | 2021 | 4.972e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
BAYAMON | 2021-07-17 11:57 | 2021-07-18 16:20 | 10 | 028:23 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 20 EN TRANSFORMADOR SE REEMPLAZO PIN POLE TOP AVERIADO | S21071700073 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1703 | 2021-07-17 | 17030 | keep | 0 | Jul | 2021 | 0.011599 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-07-17 12:01 | 2021-07-17 15:47 | 100 | 003:46 | P | DESGANCHE | 2 X 80 Y 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUAS | A21071700019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2021-07-17 | 22600 | keep | 0 | Jul | 2021 | 0.015393 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-17 12:31 | 2021-07-17 15:27 | 125 | 002:56 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21071700016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2021-07-17 | 22000 | keep | 0 | Jul | 2021 | 0.014984 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
UTUADO | 2021-07-17 13:02 | 2021-07-17 17:00 | 80 | 003:58 | P | DESGANCHE | SE ABRIO CORTE DE LINEA Y SE RETIRO BAMBUES SOBRE LINEA | A21071700004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2021-07-17 | 19040 | keep | 0 | Jul | 2021 | 0.012968 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-07-17 13:40 | 2021-07-18 09:07 | 1 | 019:27 | P | NO SE REPORTO CAUSA | 1 X 15 EN RISER | B21071700020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1167 | 2021-07-17 | 1167 | keep | 0 | Jul | 2021 | 0.00079484 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-07-17 13:42 | 2021-07-17 17:21 | 3 | 003:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | M21071600046 | New_Event | Bad Weather | Include | Include | Weather | 219 | 2021-07-17 | 657 | keep | 0 | Jul | 2021 | 0.00044748 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2021-07-17 13:44 | 2021-07-17 22:24 | 500 | 008:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REEMPLAZARON 2 POSTES PARTIDOS POR IMPACTO DE AUTO | R21071700000 | New_Event |  |  | Include | Wildlife | 520 | 2021-07-17 | 260000 | keep | 0 | Jul | 2021 | 0.17708 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
AGUADILLA | 2021-07-17 13:52 | 2021-07-17 16:33 | 25 | 002:41 | P | DESGANCHE | SE REPARO THREE WIRE A TRANSFORMADOR | M21071600173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2021-07-17 | 4025 | keep | 0 | Jul | 2021 | 0.0027414 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2021-07-17 14:06 | 2021-07-18 10:38 | 4 | 020:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA ABIERTA | C21071700034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1232 | 2021-07-17 | 4928 | keep | 0 | Jul | 2021 | 0.0033564 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-07-17 14:13 | 2021-07-17 15:53 | 7 | 001:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA AVERIADA | M21071700049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 100 | 2021-07-17 | 700 | keep | 0 | Jul | 2021 | 0.00047677 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
CANOVANAS | 2021-07-17 14:17 | 2021-07-17 18:17 | 20 | 004:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO CORTE DE LINEA MONOFASICO PARA REEMPLAZAR POSTE PRIMARIO IMPACTADO PARTIDO | R21071700091 | New_Event |  |  | Include | Wildlife | 240 | 2021-07-17 | 4800 | keep | 0 | Jul | 2021 | 0.0032693 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-07-17 14:26 | 2021-07-18 11:49 | 50 | 021:23 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21071700035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1283 | 2021-07-17 | 64150 | keep | 0 | Jul | 2021 | 0.043692 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-17 14:57 | 2021-07-18 08:59 | 52 | 018:02 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21071700094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1082 | 2021-07-17 | 56264 | keep | 0 | Jul | 2021 | 0.038321 | 3.5417e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 52
HUMACAO | 2021-07-17 15:10 | 2021-07-17 17:13 | 6 | 002:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BUSHING SECUNDARIO | C21071700036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 123 | 2021-07-17 | 738 | keep | 0 | Jul | 2021 | 0.00050265 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-07-17 15:44 | 2021-07-17 15:45 | 1212 | 000:01 | T | DESGANCHE | RECIERRE | P21071700028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-17 | 1212 | keep | 0 | Jul | 2021 | 0.00082549 | 0.00082549 | Momentary | FALSE | FALSE | Not_TMED_Event | 1212
PONCE | 2021-07-17 15:44 | 2021-07-17 15:45 | 198 | 000:01 | P | DESGANCHE | RECIERRE | P21071700028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-17 | 198 | keep | 0 | Jul | 2021 | 0.00013486 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
MAYAGÃœEZ | 2021-07-17 15:47 | 2021-07-18 17:20 | 40 | 025:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | M21071700061 | New_Event | Bad Weather | Include | Include | Weather | 1533 | 2021-07-17 | 61320 | keep | 0 | Jul | 2021 | 0.041765 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-07-17 15:54 | 2021-07-17 17:20 | 25 | 001:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE DE LINEA A CAJA NO FUNDIO | C21071700037 | New_Event | Wire Down | Include | Include | Equipment | 86 | 2021-07-17 | 2150 | keep | 0 | Jul | 2021 | 0.0014644 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
PONCE | 2021-07-17 16:08 | 2021-07-17 16:09 | 1212 | 000:01 | T | DESGANCHE | RECIERRE | P21071700031 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-17 | 1212 | keep | 0 | Jul | 2021 | 0.00082549 | 0.00082549 | Momentary | FALSE | FALSE | Not_TMED_Event | 1212
PONCE | 2021-07-17 16:09 | 2021-07-17 18:45 | 57 | 002:36 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | P21071700034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2021-07-17 | 8892 | keep | 0 | Jul | 2021 | 0.0060563 | 3.8822e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 57
HUMACAO | 2021-07-17 16:15 | 2021-07-17 16:30 | 1 | 000:15 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C21071700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2021-07-17 | 15 | keep | 0 | Jul | 2021 | 1.0216e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-07-17 16:40 | 2021-07-17 17:43 | 80 | 001:03 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21071700026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2021-07-17 | 5040 | keep | 0 | Jul | 2021 | 0.0034327 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-07-17 17:43 | 2021-07-17 21:19 | 30 | 003:36 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21071700041 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 216 | 2021-07-17 | 6480 | keep | 0 | Jul | 2021 | 0.0044135 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-07-17 17:48 | 2021-07-17 17:49 | 1381 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUTPTOR SE CERRO POR SCADA CARGA POR EL 1206-04 | S21071700000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-17 | 1381 | keep | 0 | Jul | 2021 | 0.00094059 | 0.00094059 | Momentary | FALSE | FALSE | Not_TMED_Event | 1381
SAN JUAN | 2021-07-17 17:48 | 2021-07-17 17:49 | 1799 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA CARGA DEL 1204-03 | S21071700000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-17 | 1799 | keep | 0 | Jul | 2021 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2021-07-17 17:48 | 2021-07-17 17:49 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUTPTOR SE CERRO POR SCADA | S21071700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-17 | 870 | keep | 0 | Jul | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2021-07-17 17:49 | 2021-07-17 19:03 | 600 | 001:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA CARGA DEL 1204-03 | S21071700000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 74 | 2021-07-17 | 44400 | keep | 0 | Jul | 2021 | 0.030241 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
BAYAMON | 2021-07-17 18:06 | 2021-07-17 18:07 | 271 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21071700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-17 | 271 | keep | 0 | Jul | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
FAJARDO | 2021-07-17 18:15 | 2021-07-18 11:47 | 5 | 017:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO SECUNDARIA ABIERTA | R21071700107 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1052 | 2021-07-17 | 5260 | keep | 0 | Jul | 2021 | 0.0035826 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-07-17 18:53 | 2021-07-17 19:29 | 2366 | 000:36 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21071700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 36 | 2021-07-17 | 85176 | keep | 0 | Jul | 2021 | 0.058013 | 0.0016115 | Sustained | FALSE | TRUE | Not_TMED_Event | 2366
SAN JUAN | 2021-07-17 19:03 | 2021-07-17 19:38 | 1381 | 000:35 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1206-04 PARA CERRAR PUENTE ABIERTO A LA SALIDA ADEMAS CARGA POR EL 1206-04 | S21071700157 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 35 | 2021-07-17 | 48335 | keep | 0 | Jul | 2021 | 0.032921 | 0.00094059 | Sustained | FALSE | FALSE | Not_TMED_Event | 1381
SAN JUAN | 2021-07-17 19:03 | 2021-07-17 19:38 | 1799 | 000:35 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1206-04 PARA CERRAR PUENTE ABIERTO A LA SALIDA ADEMAS LLEVA LA CARGA DEL 1204-03 | S21071700157 | Additional_clients | Wire Down | Include | Include | Equipment | 35 | 2021-07-17 | 62965 | keep | 0 | Jul | 2021 | 0.042885 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-17 19:07 | 2021-07-18 10:20 | 200 | 015:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | M21071700090 | New_Event |  |  | Include | Wildlife | 913 | 2021-07-17 | 182600 | keep | 0 | Jul | 2021 | 0.12437 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
PONCE | 2021-07-17 19:08 | 2021-07-17 19:09 | 195 | 000:01 | P | DESGANCHE | RECIERRE | P21071700031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-17 | 195 | keep | 0 | Jul | 2021 | 0.00013281 | 0.00013281 | Momentary | FALSE | FALSE | Not_TMED_Event | 195
BAYAMON | 2021-07-17 19:19 | 2021-07-18 09:38 | 10 | 014:19 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21071700039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 859 | 2021-07-17 | 8590 | keep | 0 | Jul | 2021 | 0.0058506 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-07-17 19:29 | 2021-07-17 19:30 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21071700042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-17 | 3718 | keep | 0 | Jul | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
CANOVANAS | 2021-07-17 19:31 | 2021-07-18 09:23 | 19 | 013:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR REEMPLAZO PORTAFUSIBLE AVERIADO | R21071700112 | New_Event | Cutout Failure | Include | Include | Equipment | 832 | 2021-07-17 | 15808 | keep | 0 | Jul | 2021 | 0.010767 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
MAYAGÃœEZ | 2021-07-17 19:47 | 2021-07-19 12:15 | 3 | 040:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21071700094 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2428 | 2021-07-17 | 7284 | keep | 0 | Jul | 2021 | 0.0049611 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
AGUADILLA | 2021-07-17 19:55 | 2021-07-18 17:15 | 40 | 021:20 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | M21071700095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1280 | 2021-07-17 | 51200 | keep | 0 | Jul | 2021 | 0.034872 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-07-17 20:18 | 2021-07-18 09:54 | 8 | 013:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 8 EN TRANSFORMADOR SE REPARO TOMA ROTA | C21071700044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 816 | 2021-07-17 | 6528 | keep | 0 | Jul | 2021 | 0.0044462 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-07-17 20:29 | 2021-07-18 15:50 | 50 | 019:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA | M21071700098 | New_Event | Wire Down | Include | Include | Equipment | 1161 | 2021-07-17 | 58050 | keep | 0 | Jul | 2021 | 0.039538 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-17 20:50 | 2021-07-17 20:51 | 5252 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21071700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-17 | 5252 | keep | 0 | Jul | 2021 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
MAYAGÃœEZ | 2021-07-17 21:00 | 2021-07-18 11:10 | 5 | 014:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR VEHICULO IMPACTO POSTE SECUNDARIO | M21071800026 | New_Event |  |  | Include | Wildlife | 850 | 2021-07-17 | 4250 | keep | 0 | Jul | 2021 | 0.0028947 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-07-17 21:38 | 2021-07-18 09:07 | 50 | 011:29 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21071700046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 689 | 2021-07-17 | 34450 | keep | 0 | Jul | 2021 | 0.023464 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-07-17 21:40 | 2021-07-18 12:05 | 34 | 014:25 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | P21071700046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 865 | 2021-07-17 | 29410 | keep | 0 | Jul | 2021 | 0.020031 | 2.3157e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 34
PONCE | 2021-07-17 21:55 | 2021-07-17 22:30 | 25 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P21071700045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2021-07-17 | 875 | keep | 0 | Jul | 2021 | 0.00059596 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
PONCE | 2021-07-17 22:31 | 2021-07-18 10:43 | 647 | 012:12 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | P21071700051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 732 | 2021-07-17 | 473604 | keep | 0 | Jul | 2021 | 0.32257 | 0.00044067 | Sustained | FALSE | TRUE | Not_TMED_Event | 647
BAYAMON | 2021-07-17 23:22 | 2021-07-18 01:12 | 200 | 001:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA SE REPORTO ACCIDENTE DE AUTO | B21071700049 | New_Event |  |  | Include | Wildlife | 110 | 2021-07-17 | 22000 | keep | 0 | Jul | 2021 | 0.014984 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-07-17 23:36 | 2021-07-18 10:32 | 2 | 010:56 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA 1 X 65 CORTE DE LINEA | S21071700190 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 656 | 2021-07-17 | 1312 | keep | 0 | Jul | 2021 | 0.0008936 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
MAYAGÃœEZ | 2021-07-18 00:11 | 2021-07-18 13:44 | 80 | 013:33 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | M21071800001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 813 | 2021-07-18 | 65040 | keep | 0 | Jul | 2021 | 0.044298 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-07-18 01:11 | 2021-07-18 10:00 | 50 | 008:49 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21071800002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 529 | 2021-07-18 | 26450 | keep | 0 | Jul | 2021 | 0.018015 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-07-18 01:24 | 2021-07-18 10:05 | 170 | 008:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 Y 1 X 50 EN CORTES DE LINEAS CRUCE POR AVE | R21071800001 | New_Event |  |  | Include | Wildlife | 521 | 2021-07-18 | 88570 | keep | 0 | Jul | 2021 | 0.060325 | 0.00011579 | Sustained | FALSE | TRUE | Not_TMED_Event | 170
ARECIBO | 2021-07-18 01:48 | 2021-07-18 10:50 | 30 | 009:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | A21071800001 | New_Event |  |  | Include | Wildlife | 542 | 2021-07-18 | 16260 | keep | 0 | Jul | 2021 | 0.011075 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-07-18 02:44 | 2021-07-18 02:45 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | INTERRUPTOR DISPARO Y SE CERRO POR CONTROL | S21071800002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-18 | 2435 | keep | 0 | Jul | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-07-18 03:23 | 2021-07-18 06:17 | 4398 | 002:54 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO Y SE CERRO POR SCADA | S21071800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2021-07-18 | 765252 | keep | 0 | Jul | 2021 | 0.52121 | 0.0029955 | Sustained | FALSE | FALSE | Not_TMED_Event | 4398
BAYAMON | 2021-07-18 03:37 | 2021-07-18 03:40 | 2234 | 000:03 | T | MAL TIEMPO/RAYOS/WET ASH | INTERRUPTOR DISPARO Y SE CERRO POR SCADA | B21071800003 | New_Event | Bad Weather | Include | Include | Weather | 3 | 2021-07-18 | 6702 | keep | 0 | Jul | 2021 | 0.0045647 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
PONCE | 2021-07-18 03:39 | 2021-07-18 03:40 | 2113 | 000:01 | T | RELEVO DE CARGA AUTOMATICO | RECIERRE | P210719000XX | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 1 | 2021-07-18 | 2113 | keep | 0 | Jul | 2021 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
BAYAMON | 2021-07-18 03:40 | 2021-07-19 13:16 | 20 | 033:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | B21071800010 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 2016 | 2021-07-18 | 40320 | keep | 0 | Jul | 2021 | 0.027462 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-07-18 03:49 | 2021-07-19 11:06 | 70 | 031:17 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA REEMPLAZO AISLADOR ROTO | R21071800008 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1877 | 2021-07-18 | 131390 | keep | 0 | Jul | 2021 | 0.089489 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
ARECIBO | 2021-07-18 04:47 | 2021-07-18 04:48 | 2720 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21071800003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-18 | 2720 | keep | 0 | Jul | 2021 | 0.0018526 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
ARECIBO | 2021-07-18 05:11 | 2021-07-18 05:12 | 1916 | 000:01 | T | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | RECIERRE DE INTERRUPTOR | A21071800000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1 | 2021-07-18 | 1916 | keep | 0 | Jul | 2021 | 0.001305 | 0.001305 | Momentary | FALSE | FALSE | Not_TMED_Event | 1916
BAYAMON | 2021-07-18 06:17 | 2021-07-18 07:31 | 398 | 001:14 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRARON MACHETES | S21071800000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 74 | 2021-07-18 | 29452 | keep | 0 | Jul | 2021 | 0.02006 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-18 06:19 | 2021-07-18 06:20 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21071800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-18 | 641 | keep | 0 | Jul | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
BAYAMON | 2021-07-18 06:21 | 2021-07-18 09:15 | 15 | 002:54 | P | NO SE REPORTO CAUSA | 1 X 20 EN PROVISIONAL | B21071800004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2021-07-18 | 2610 | keep | 0 | Jul | 2021 | 0.0017777 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-07-18 06:38 | 2021-07-18 06:39 | 1916 | 000:01 | T | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21071800000 | 1st_after_momentary | Secondary Wire Down | Include | Include | Equipment | 1 | 2021-07-18 | 1916 | keep | 0 | Jul | 2021 | 0.001305 | 0.001305 | Momentary | FALSE | FALSE | Not_TMED_Event | 1916
ARECIBO | 2021-07-18 06:39 | 2021-07-18 13:40 | 5 | 007:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21071800001 | 1st_after_momentary | Secondary Wire Down | Include | Include | Equipment | 421 | 2021-07-18 | 2105 | keep | 0 | Jul | 2021 | 0.0014337 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2021-07-18 07:03 | 2021-07-18 11:36 | 60 | 004:33 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA REEMPLAZO AISLADOR Y REPARO LINEAS CRUZADAS | C21071800003 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 273 | 2021-07-18 | 16380 | keep | 0 | Jul | 2021 | 0.011156 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-07-18 07:11 | 2021-07-18 20:50 | 80 | 013:39 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | M21071800007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 819 | 2021-07-18 | 65520 | keep | 0 | Jul | 2021 | 0.044625 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-07-18 07:14 | 2021-07-18 10:52 | 52 | 003:38 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | S21071800040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 218 | 2021-07-18 | 11336 | keep | 0 | Jul | 2021 | 0.0077209 | 3.5417e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 52
SAN JUAN | 2021-07-18 07:14 | 2021-07-18 07:15 | 143 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | S21071800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-18 | 143 | keep | 0 | Jul | 2021 | 9.7397e-05 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
MAYAGÃœEZ | 2021-07-18 07:23 | 2021-07-18 14:20 | 250 | 006:57 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 140 EN CORTE DE LINEA SE REPARO LINEA CRUZADAS DEL AILADOR | M21071800003 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 417 | 2021-07-18 | 104250 | keep | 0 | Jul | 2021 | 0.071004 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
MAYAGÃœEZ | 2021-07-18 07:23 | 2021-07-18 17:15 | 100 | 009:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | M21071800012 | New_Event | Bad Weather | Include | Include | Weather | 592 | 2021-07-18 | 59200 | keep | 0 | Jul | 2021 | 0.040321 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-07-18 07:28 | 2021-07-18 15:12 | 20 | 007:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA CRUZADA | A21071800007 | New_Event | Wire Down | Include | Include | Equipment | 464 | 2021-07-18 | 9280 | keep | 0 | Jul | 2021 | 0.0063206 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-07-18 07:41 | 2021-07-18 07:42 | 1227 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21071800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-18 | 1227 | keep | 0 | Jul | 2021 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
SAN JUAN | 2021-07-18 07:55 | 2021-07-18 10:15 | 46 | 002:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR FASE PRIMARIA CONECTADA COMO NEUTRAL PRIMARIO | R21071800015 | New_Event | Wire Down | Include | Include | Equipment | 140 | 2021-07-18 | 6440 | keep | 0 | Jul | 2021 | 0.0043863 | 3.133e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 46
BAYAMON | 2021-07-18 08:13 | 2021-07-18 10:19 | 16 | 002:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21071700079 | New_Event | Secondary Wire Down | Include | Include | Equipment | 126 | 2021-07-18 | 2016 | keep | 0 | Jul | 2021 | 0.0013731 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
GUAYAMA | 2021-07-18 08:13 | 2021-07-18 12:35 | 15 | 004:22 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | P21071800007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 262 | 2021-07-18 | 3930 | keep | 0 | Jul | 2021 | 0.0026767 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-07-18 08:24 | 2021-07-18 10:42 | 36 | 002:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA SE RETIRO PALOMA | B21071800045 | New_Event |  |  | Include | Wildlife | 138 | 2021-07-18 | 4968 | keep | 0 | Jul | 2021 | 0.0033837 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
PONCE | 2021-07-18 08:33 | 2021-07-19 14:10 | 200 | 029:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 100 EN CORTE DE LINEA Y SE CAMBIARON 3 CAJAS DE 200A QUEMADAS | P21071800009 | New_Event | Cutout Failure | Include | Include | Equipment | 1777 | 2021-07-18 | 355400 | keep | 0 | Jul | 2021 | 0.24206 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-07-18 09:08 | 2021-07-18 09:09 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21071800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-18 | 2605 | keep | 0 | Jul | 2021 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
FAJARDO | 2021-07-18 09:23 | 2021-07-18 12:08 | 1 | 002:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR PORTAFUSIBLE DEFECTUOSO | R21071800020 | New_Event | Cutout Failure | Include | Include | Equipment | 165 | 2021-07-18 | 165 | keep | 0 | Jul | 2021 | 0.00011238 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-07-18 09:31 | 2021-07-18 10:07 | 27 | 000:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21071800001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 36 | 2021-07-18 | 972 | keep | 0 | Jul | 2021 | 0.00066202 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
BARRANQUITAS | 2021-07-18 09:32 | 2021-07-18 17:43 | 75 | 008:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21071800008 | New_Event | Bad Weather | Include | Include | Weather | 491 | 2021-07-18 | 36825 | keep | 0 | Jul | 2021 | 0.025081 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
MAYAGÃœEZ | 2021-07-18 09:41 | 2021-07-19 10:30 | 100 | 024:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21071800149 | New_Event | Bad Weather | Include | Include | Weather | 1489 | 2021-07-18 | 148900 | keep | 0 | Jul | 2021 | 0.10142 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BARRANQUITAS | 2021-07-18 09:58 | 2021-07-18 18:01 | 3 | 008:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO | C21071800010 | New_Event | Bad Weather | Include | Include | Weather | 483 | 2021-07-18 | 1449 | keep | 0 | Jul | 2021 | 0.00098691 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-07-18 10:10 | 2021-07-18 19:24 | 10 | 009:14 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO 50 X 50 KVA | B21071800008 | New_Event | Service Transformer Failure | Include | Include | Equipment | 554 | 2021-07-18 | 5540 | keep | 0 | Jul | 2021 | 0.0037733 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-07-18 10:25 | 2021-07-18 16:07 | 50 | 005:42 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21071800011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 342 | 2021-07-18 | 17100 | keep | 0 | Jul | 2021 | 0.011647 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-18 10:40 | 2021-07-18 16:30 | 3 | 005:50 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR POSTE SECUNDARIO | C21071800000 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 350 | 2021-07-18 | 1050 | keep | 0 | Jul | 2021 | 0.00071515 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-07-18 10:40 | 2021-07-18 11:07 | 10 | 000:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21071800012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 27 | 2021-07-18 | 270 | keep | 0 | Jul | 2021 | 0.0001839 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-18 10:42 | 2021-07-18 12:35 | 8 | 001:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21071600042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 113 | 2021-07-18 | 904 | keep | 0 | Jul | 2021 | 0.00061571 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-07-18 10:50 | 2021-07-18 13:16 | 8 | 002:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN CORTE DE LINEA REPARO CAJA DE TRANSFORMADOR PEGADA AL POSTE | C21071800014 | New_Event | Cutout Failure | Include | Include | Equipment | 146 | 2021-07-18 | 1168 | keep | 0 | Jul | 2021 | 0.00079552 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
UTUADO | 2021-07-18 11:00 | 2021-07-18 12:00 | 10 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR NEUTRAL | A21071800013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2021-07-18 | 600 | keep | 0 | Jul | 2021 | 0.00040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-07-18 11:07 | 2021-07-18 16:41 | 98 | 005:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR CHANGO | C21071800016 | New_Event |  |  | Include | Wildlife | 334 | 2021-07-18 | 32732 | keep | 0 | Jul | 2021 | 0.022294 | 6.6747e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 98
BAYAMON | 2021-07-18 11:15 | 2021-07-18 16:05 | 70 | 004:50 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA Y 1 X 50 EN CORTE DE LINEA DISTINTO | B21071800020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 290 | 2021-07-18 | 20300 | keep | 0 | Jul | 2021 | 0.013826 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
VEGA BAJA | 2021-07-18 11:22 | 2021-07-18 12:34 | 1284 | 001:12 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO PUENTE ABIERTO Y SE CERRO POR SCADA | B21081800000 | New_Event | Wire Down | Include | Include | Equipment | 72 | 2021-07-18 | 92448 | keep | 0 | Jul | 2021 | 0.062966 | 0.00087453 | Sustained | FALSE | FALSE | Not_TMED_Event | 1284
AGUADILLA | 2021-07-18 12:00 | 2021-07-18 19:06 | 2366 | 007:06 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO INTERRUPTOR NO DA INDICACION DE ABIERTO MAL TIEMPO | M21071800000 | New_Event | Bad Weather | Include | Include | Weather | 426 | 2021-07-18 | 1007916 | keep | 0 | Jul | 2021 | 0.68649 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
SAN JUAN | 2021-07-18 12:04 | 2021-07-18 12:39 | 1799 | 000:35 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZO DESGANCHE Y SE CERRO POR SCADA | S21071800058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 35 | 2021-07-18 | 62965 | keep | 0 | Jul | 2021 | 0.042885 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
FAJARDO | 2021-07-18 12:14 | 2021-07-18 15:29 | 35 | 003:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA PORTAFUSIBLE QUEMADO | R21071800079 | New_Event | Cutout Failure | Include | Include | Equipment | 195 | 2021-07-18 | 6825 | keep | 0 | Jul | 2021 | 0.0046485 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
PONCE | 2021-07-18 12:30 | 2021-07-18 13:05 | 224 | 000:35 | P | ESTRUCTURA AVERIADA | POSTE PRIMARIO PARTIDO | P210717000XX | New_Event | Defective Pole | Include | Include | Equipment | 35 | 2021-07-18 | 7840 | keep | 0 | Jul | 2021 | 0.0053398 | 0.00015257 | Sustained | FALSE | FALSE | Not_TMED_Event | 224
VEGA BAJA | 2021-07-18 12:34 | 2021-07-18 13:42 | 790 | 001:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO PUENTE ABIERTO Y DISPARO NUEVAMENTE | B21081800000 | Partial_restoration | Wire Down | Include | Include | Equipment | 68 | 2021-07-18 | 53720 | keep | 0 | Jul | 2021 | 0.036588 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-18 12:35 | 2021-07-19 14:23 | 40 | 025:48 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 25 EN SU - 2 HACIA T - 27 CONTAMINACION | R21071800023 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1548 | 2021-07-18 | 61920 | keep | 0 | Jul | 2021 | 0.042173 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2021-07-18 12:48 | 2021-07-18 17:40 | 100 | 004:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA | P21071800016 | New_Event | Wire Down | Include | Include | Equipment | 292 | 2021-07-18 | 29200 | keep | 0 | Jul | 2021 | 0.019888 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-18 13:01 | 2021-07-20 16:25 | 25 | 051:24 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR 50KVA X 50KVA | S21071800088 | New_Event | Service Transformer Failure | Include | Include | Equipment | 3084 | 2021-07-18 | 77100 | keep | 0 | Jul | 2021 | 0.052512 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2021-07-18 13:05 | 2021-07-18 19:40 | 40 | 006:35 | P | ESTRUCTURA AVERIADA | REMPLAZO DE POSTE PARTIDO | P21071700019 | Partial_restoration | Defective Pole | Include | Include | Equipment | 395 | 2021-07-18 | 15800 | keep | 0 | Jul | 2021 | 0.010761 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-18 13:05 | 2021-07-18 16:27 | 810 | 003:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21071800051 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 202 | 2021-07-18 | 163620 | keep | 0 | Jul | 2021 | 0.11144 | 0.00055169 | Sustained | FALSE | TRUE | Not_TMED_Event | 810
MAYAGÃœEZ | 2021-07-18 13:05 | 2021-07-18 16:27 | 1235 | 003:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21071800051 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 202 | 2021-07-18 | 249470 | keep | 0 | Jul | 2021 | 0.16991 | 0.00084115 | Sustained | FALSE | TRUE | Not_TMED_Event | 1235
MAYAGÃœEZ | 2021-07-18 13:05 | 2021-07-18 16:27 | 93 | 003:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21071800051 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 202 | 2021-07-18 | 18786 | keep | 0 | Jul | 2021 | 0.012795 | 6.3342e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 93
MAYAGÃœEZ | 2021-07-18 13:05 | 2021-07-18 16:27 | 1825 | 003:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21071800051 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 202 | 2021-07-18 | 368650 | keep | 0 | Jul | 2021 | 0.25109 | 0.001243 | Sustained | FALSE | TRUE | Not_TMED_Event | 1825
MAYAGÃœEZ | 2021-07-18 13:05 | 2021-07-18 16:27 | 3230 | 003:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M21071800051 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 202 | 2021-07-18 | 652460 | keep | 0 | Jul | 2021 | 0.44439 | 0.0021999 | Sustained | FALSE | TRUE | Not_TMED_Event | 3230
ARECIBO | 2021-07-18 13:07 | 2021-07-18 13:08 | 2266 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21071800018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-18 | 2266 | keep | 0 | Jul | 2021 | 0.0015434 | 0.0015434 | Momentary | FALSE | FALSE | Not_TMED_Event | 2266
BARRANQUITAS | 2021-07-18 13:40 | 2021-07-18 15:30 | 108 | 001:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE ELIMINO TENSOR DE LA LINEA | C21071800019 | New_Event | Wire Down | Include | Include | Equipment | 110 | 2021-07-18 | 11880 | keep | 0 | Jul | 2021 | 0.0080914 | 7.3558e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 108
VEGA BAJA | 2021-07-18 13:42 | 2021-07-18 16:06 | 1284 | 002:24 | T | DESGANCHE | DESPUES DE SECCIONALIZADO EL PUENTE ABIERTO DISPARO ALIMENTADOR POR ARBOL SOBRE LINEA SE REALIZO DESGANCHE Y SE CERRO INTERRUPTOR | B21081800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2021-07-18 | 184896 | keep | 0 | Jul | 2021 | 0.12593 | 0.00087453 | Sustained | FALSE | TRUE | Not_TMED_Event | 1284
VEGA BAJA | 2021-07-18 13:51 | 2021-07-18 13:52 | 215 | 000:01 | T | DESGANCHE | DISPARO Y SE CERRO POR SCADA | B21071800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-18 | 215 | keep | 0 | Jul | 2021 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2021-07-18 13:52 | 2021-07-18 19:35 | 80 | 005:43 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21071800071 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 343 | 2021-07-18 | 27440 | keep | 0 | Jul | 2021 | 0.018689 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-07-18 14:03 | 2021-07-18 14:04 | 128 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVANDO LA CARGA DEL 3009-3 Y 3009-4 | C21071800023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-18 | 128 | keep | 0 | Jul | 2021 | 8.718e-05 | 8.718e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 128
CAGUAS | 2021-07-18 14:03 | 2021-07-18 14:04 | 273 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR CARGA POR EL 3009-02 | C21071800023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-18 | 273 | keep | 0 | Jul | 2021 | 0.00018594 | 0.00018594 | Momentary | FALSE | FALSE | Not_TMED_Event | 273
CAGUAS | 2021-07-18 14:03 | 2021-07-18 14:04 | 1772 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR CARGA POR EL 3009-02 | C21071800023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-18 | 1772 | keep | 0 | Jul | 2021 | 0.0012069 | 0.0012069 | Momentary | FALSE | FALSE | Not_TMED_Event | 1772
PONCE | 2021-07-18 14:10 | 2021-07-18 14:30 | 473 | 000:20 | P | ESTRUCTURA AVERIADA | SE ABREN MACHETES PARA PODER ABRIR PUENTES PRIMARIOS Y REMPLAZAR POSTE | P21071700018 | New_Event | Defective Pole | Include | Include | Equipment | 20 | 2021-07-18 | 9460 | keep | 0 | Jul | 2021 | 0.0064432 | 0.00032216 | Sustained | FALSE | FALSE | Not_TMED_Event | 473
AGUADILLA | 2021-07-18 14:10 | 2021-07-18 14:11 | 1155 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21071800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-18 | 1155 | keep | 0 | Jul | 2021 | 0.00078667 | 0.00078667 | Momentary | FALSE | FALSE | Not_TMED_Event | 1155
BAYAMON | 2021-07-18 14:14 | 2021-07-18 17:39 | 100 | 003:25 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE ARBOL | S21071800094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2021-07-18 | 20500 | keep | 0 | Jul | 2021 | 0.013962 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-07-18 14:30 | 2021-07-18 18:50 | 175 | 004:20 | P | ESTRUCTURA AVERIADA | REMPLAZO DE POSTE PARTIDO | P21071700020 | Partial_restoration | Defective Pole | Include | Include | Equipment | 260 | 2021-07-18 | 45500 | keep | 0 | Jul | 2021 | 0.03099 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-07-18 14:39 | 2021-07-18 16:20 | 50 | 001:41 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA POR MAL TIEMPO | A21071800024 | New_Event | Bad Weather | Include | Include | Weather | 101 | 2021-07-18 | 5050 | keep | 0 | Jul | 2021 | 0.0034395 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-18 14:40 | 2021-07-18 16:30 | 6 | 001:50 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO AISLADOR ROTO | C21071800024 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 110 | 2021-07-18 | 660 | keep | 0 | Jul | 2021 | 0.00044952 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
UTUADO | 2021-07-18 14:52 | 2021-07-18 19:20 | 50 | 004:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA CRUZADA | A21071800028 | New_Event | Wire Down | Include | Include | Equipment | 268 | 2021-07-18 | 13400 | keep | 0 | Jul | 2021 | 0.0091267 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-18 14:59 | 2021-07-18 15:00 | 2457 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21071800028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-18 | 2457 | keep | 0 | Jul | 2021 | 0.0016735 | 0.0016735 | Momentary | FALSE | FALSE | Not_TMED_Event | 2457
BAYAMON | 2021-07-18 15:02 | 2021-07-18 18:30 | 30 | 003:28 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B21071800029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 208 | 2021-07-18 | 6240 | keep | 0 | Jul | 2021 | 0.00425 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-07-18 15:04 | 2021-07-18 23:19 | 1 | 008:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA EN CORTE DE LINEA | S21071800099 | New_Event | Wire Down | Include | Include | Equipment | 495 | 2021-07-18 | 495 | keep | 0 | Jul | 2021 | 0.00033714 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CANOVANAS | 2021-07-18 15:11 | 2021-07-18 17:03 | 7 | 001:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA FUSIBLE SULFATADO | R21071800026 | New_Event | Cutout Failure | Include | Include | Equipment | 112 | 2021-07-18 | 784 | keep | 0 | Jul | 2021 | 0.00053398 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
CANOVANAS | 2021-07-18 15:34 | 2021-07-18 17:03 | 260 | 001:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA MAL TIEMPO | R21071800027 | New_Event | Bad Weather | Include | Include | Weather | 89 | 2021-07-18 | 23140 | keep | 0 | Jul | 2021 | 0.015761 | 0.00017708 | Sustained | FALSE | TRUE | Not_TMED_Event | 260
UTUADO | 2021-07-18 15:45 | 2021-07-18 17:00 | 25 | 001:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR MAL TIEMPO | A21071800029 | New_Event | Bad Weather | Include | Include | Weather | 75 | 2021-07-18 | 1875 | keep | 0 | Jul | 2021 | 0.0012771 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
FAJARDO | 2021-07-18 15:48 | 2021-07-18 17:10 | 111 | 001:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R21071800029 | New_Event |  |  | Include | Wildlife | 82 | 2021-07-18 | 9102 | keep | 0 | Jul | 2021 | 0.0061993 | 7.5602e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 111
AGUADILLA | 2021-07-18 16:00 | 2021-07-19 12:50 | 70 | 020:50 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21071900005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1250 | 2021-07-18 | 87500 | keep | 0 | Jul | 2021 | 0.059596 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BAYAMON | 2021-07-18 16:05 | 2021-07-18 23:28 | 15 | 007:23 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21071800073 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 443 | 2021-07-18 | 6645 | keep | 0 | Jul | 2021 | 0.0045259 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
VEGA BAJA | 2021-07-18 16:06 | 2021-07-18 16:52 | 790 | 000:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO Y SE CERRARON MACHETES | B21081800000 | Partial_restoration | Wire Down | Include | Include | Equipment | 46 | 2021-07-18 | 36340 | keep | 0 | Jul | 2021 | 0.024751 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-07-18 16:16 | 2021-07-19 12:50 | 8 | 020:34 | P | PARARRAYOS DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PARARRAYOS DEFECTUOSO | A21071800030 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1234 | 2021-07-18 | 9872 | keep | 0 | Jul | 2021 | 0.0067238 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2021-07-18 16:20 | 2021-07-18 20:34 | 60 | 004:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO | M21071800089 | New_Event | Wire Down | Include | Include | Equipment | 254 | 2021-07-18 | 15240 | keep | 0 | Jul | 2021 | 0.01038 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
UTUADO | 2021-07-18 16:28 | 2021-07-19 18:00 | 40 | 025:32 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21071800031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1532 | 2021-07-18 | 61280 | keep | 0 | Jul | 2021 | 0.041738 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-07-18 16:34 | 2021-07-19 13:30 | 80 | 020:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | M21071800098 | New_Event | Bad Weather | Include | Include | Weather | 1256 | 2021-07-18 | 100480 | keep | 0 | Jul | 2021 | 0.068436 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-07-18 16:38 | 2021-07-18 20:14 | 50 | 003:36 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | B21071800078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 216 | 2021-07-18 | 10800 | keep | 0 | Jul | 2021 | 0.0073558 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-18 16:44 | 2021-07-19 13:45 | 1 | 021:01 | P | NO SE REPORTO CAUSA | 2 X 20 EN TRASFORMADOR | S21071800101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1261 | 2021-07-18 | 1261 | keep | 0 | Jul | 2021 | 0.00085886 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-07-18 16:49 | 2021-07-18 18:25 | 75 | 001:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | M21071800104 | New_Event | Bad Weather | Include | Include | Weather | 96 | 2021-07-18 | 7200 | keep | 0 | Jul | 2021 | 0.0049039 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
VEGA BAJA | 2021-07-18 16:51 | 2021-07-19 14:50 | 10 | 021:59 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO 25 X 25 KVA | B21071800085 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1319 | 2021-07-18 | 13190 | keep | 0 | Jul | 2021 | 0.0089836 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-18 17:03 | 2021-07-19 17:00 | 15 | 023:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR POR MAL TIEMPO | M21071800109 | New_Event | Bad Weather | Include | Include | Weather | 1437 | 2021-07-18 | 21555 | keep | 0 | Jul | 2021 | 0.014681 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-07-18 17:07 | 2021-07-18 20:30 | 200 | 003:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA MAL TIEMPO | M21071800111 | New_Event | Bad Weather | Include | Include | Weather | 203 | 2021-07-18 | 40600 | keep | 0 | Jul | 2021 | 0.027652 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
YAUCO | 2021-07-18 17:15 | 2021-07-18 17:50 | 211 | 000:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO DE TRES CAJAS PRIMARIAS | P21071800036 | New_Event | Cutout Failure | Include | Include | Equipment | 35 | 2021-07-18 | 7385 | keep | 0 | Jul | 2021 | 0.0050299 | 0.00014371 | Sustained | FALSE | FALSE | Not_TMED_Event | 211
ARECIBO | 2021-07-18 17:16 | 2021-07-18 18:16 | 15 | 001:00 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE RELOCALIZO LINEA SECUNDARIA POR POSTE SECUNDARIO PARTIDO | A21071800033 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 60 | 2021-07-18 | 900 | keep | 0 | Jul | 2021 | 0.00061299 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
AGUADILLA | 2021-07-18 17:18 | 2021-07-19 13:30 | 30 | 020:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21071800115 | New_Event | Wire Down | Include | Include | Equipment | 1212 | 2021-07-18 | 36360 | keep | 0 | Jul | 2021 | 0.024765 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-07-18 17:18 | 2021-07-19 12:08 | 25 | 018:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21071800034 | New_Event | Bad Weather | Include | Include | Weather | 1130 | 2021-07-18 | 28250 | keep | 0 | Jul | 2021 | 0.019241 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CAGUAS | 2021-07-18 17:43 | 2021-07-18 20:22 | 13 | 002:39 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21071800035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2021-07-18 | 2067 | keep | 0 | Jul | 2021 | 0.0014078 | 8.8542e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 13
UTUADO | 2021-07-18 17:43 | 2021-07-18 20:00 | 30 | 002:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CONVERTIDOR POR MAL TIEMPO | A21071800035 | New_Event | Bad Weather | Include | Include | Weather | 137 | 2021-07-18 | 4110 | keep | 0 | Jul | 2021 | 0.0027993 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-07-18 18:23 | 2021-07-18 18:24 | 1 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO Y SE CERRO POR SCADA EN COORDINACION DE A.A.A | B21071800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-18 | 1 | keep | 0 | Jul | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-07-18 18:26 | 2021-07-18 20:06 | 1825 | 001:40 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21071800000 | New_Event | Cutout Failure | Include | Include | Equipment | 100 | 2021-07-18 | 182500 | keep | 0 | Jul | 2021 | 0.1243 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
BAYAMON | 2021-07-18 18:26 | 2021-07-18 20:06 | 4398 | 001:40 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21071800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 100 | 2021-07-18 | 439800 | keep | 0 | Jul | 2021 | 0.29955 | 0.0029955 | Sustained | FALSE | FALSE | Not_TMED_Event | 4398
ARECIBO | 2021-07-18 18:26 | 2021-07-19 09:26 | 10 | 015:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21071800036 | New_Event | Bad Weather | Include | Include | Weather | 900 | 2021-07-18 | 9000 | keep | 0 | Jul | 2021 | 0.0061299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-18 18:27 | 2021-07-19 12:28 | 9 | 018:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR Y SE REMPLAZO PORTAFUSIBLE | B21071800098 | New_Event | Cutout Failure | Include | Include | Equipment | 1081 | 2021-07-18 | 9729 | keep | 0 | Jul | 2021 | 0.0066264 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-07-18 18:32 | 2021-07-18 18:38 | 1 | 000:06 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO Y SE CERRO POR SCADA EN COORDINACION DE A.A.A | B21071800000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 6 | 2021-07-18 | 6 | keep | 0 | Jul | 2021 | 4.0866e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-07-18 18:40 | 2021-07-18 22:35 | 1 | 003:55 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONECCION EN CONDUCTOR PRIMARIO Y SE REALIZO DESGANCHE PRIMARIO | B21071800000 | Partial_restoration | Wire Down | Include | Include | Equipment | 235 | 2021-07-18 | 235 | keep | 0 | Jul | 2021 | 0.00016006 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-07-18 18:45 | 2021-07-18 20:43 | 1382 | 001:58 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE SECCIONALIZO SE SIGUE PATRULLANDO | A21071800038 | New_Event | Wire Down | Include | Include | Equipment | 118 | 2021-07-18 | 163076 | keep | 0 | Jul | 2021 | 0.11107 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
PONCE | 2021-07-18 18:50 | 2021-07-18 20:00 | 473 | 001:10 | P | ESTRUCTURA AVERIADA | REMPLAZO DE POSTE PARTIDO | P21071700020 | Additional_clients | Defective Pole | Include | Include | Equipment | 70 | 2021-07-18 | 33110 | keep | 0 | Jul | 2021 | 0.022551 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-07-18 18:55 | 2021-07-18 21:17 | 3309 | 002:22 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE REPARO PUENTE PRIMARIO | A21071800040 | New_Event | Wire Down | Include | Include | Equipment | 142 | 2021-07-18 | 469878 | keep | 0 | Jul | 2021 | 0.32003 | 0.0022537 | Sustained | FALSE | FALSE | Not_TMED_Event | 3309
CAGUAS | 2021-07-18 18:57 | 2021-07-18 18:58 | 1403 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C21071800037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-18 | 1403 | keep | 0 | Jul | 2021 | 0.00095558 | 0.00095558 | Momentary | FALSE | FALSE | Not_TMED_Event | 1403
PONCE | 2021-07-18 19:00 | 2021-07-19 10:50 | 10 | 015:50 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | P21071700035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 950 | 2021-07-18 | 9500 | keep | 0 | Jul | 2021 | 0.0064704 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-07-18 19:27 | 2021-07-19 17:08 | 10 | 021:41 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA X 50 KVA | C21071800038 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1301 | 2021-07-18 | 13010 | keep | 0 | Jul | 2021 | 0.0088611 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-18 19:38 | 2021-07-19 13:31 | 120 | 017:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 80 EN CORTE DE LINEA Y SE REMPLAZARON 3 CAJAS PRIMARIAS | S21071800140 | New_Event | Cutout Failure | Include | Include | Equipment | 1073 | 2021-07-18 | 128760 | keep | 0 | Jul | 2021 | 0.087698 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
PONCE | 2021-07-18 19:40 | 2021-07-18 19:55 | 224 | 000:15 | P | ESTRUCTURA AVERIADA | SE ABRE CORTE DE LINEA PARA CERRAR PUENTES ABIERTOS QUE SECCIONALIZABAN POSTE PRIMARIO PARTIDO | P21071700019 | Additional_clients | Defective Pole | Include | Include | Equipment | 15 | 2021-07-18 | 3360 | keep | 0 | Jul | 2021 | 0.0022885 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-18 19:52 | 2021-07-19 14:30 | 50 | 018:38 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | M21071800141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1118 | 2021-07-18 | 55900 | keep | 0 | Jul | 2021 | 0.038073 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-18 19:53 | 2021-07-19 12:05 | 9 | 016:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21071800040 | New_Event | Bad Weather | Include | Include | Weather | 972 | 2021-07-18 | 8748 | keep | 0 | Jul | 2021 | 0.0059582 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2021-07-18 19:57 | 2021-07-19 14:09 | 30 | 018:12 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21071800103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1092 | 2021-07-18 | 32760 | keep | 0 | Jul | 2021 | 0.022313 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
AGUADILLA | 2021-07-18 19:58 | 2021-07-20 03:00 | 11 | 031:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21071800147 | New_Event | Bad Weather | Include | Include | Weather | 1862 | 2021-07-18 | 20482 | keep | 0 | Jul | 2021 | 0.01395 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2021-07-18 20:00 | 2021-07-19 12:30 | 7 | 016:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M21071800000 | New_Event | Bad Weather | Include | Include | Weather | 990 | 2021-07-18 | 6930 | keep | 0 | Jul | 2021 | 0.00472 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-07-18 20:06 | 2021-07-18 22:04 | 150 | 001:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CERRO MACHETES EN CALLE LOIZA FRENTE A ESCUELA LUIS RODRIGUEZ ABRIENDO MACHETES EN CALLE MCLEARY ESQUINA MARIA MOCZO POR CAJA PRIMARIA QUEMADA | S21071800000 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 118 | 2021-07-18 | 17700 | keep | 0 | Jul | 2021 | 0.012055 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-18 20:06 | 2021-07-19 11:29 | 10 | 015:23 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | S21071800104 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 923 | 2021-07-18 | 9230 | keep | 0 | Jul | 2021 | 0.0062865 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-07-18 20:22 | 2021-07-19 14:00 | 10 | 017:38 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR POR DESGANCHE | P21071800025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1058 | 2021-07-18 | 10580 | keep | 0 | Jul | 2021 | 0.007206 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-07-18 20:30 | 2021-07-18 21:50 | 1108 | 001:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ELIMINO TENSOR SUELTO | P21071800028 | New_Event |  |  | Include | Wildlife | 80 | 2021-07-18 | 88640 | keep | 0 | Jul | 2021 | 0.060372 | 0.00075465 | Sustained | FALSE | FALSE | Not_TMED_Event | 1108
ARECIBO | 2021-07-18 21:00 | 2021-07-19 10:35 | 30 | 013:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21071800053 | New_Event | Bad Weather | Include | Include | Weather | 815 | 2021-07-18 | 24450 | keep | 0 | Jul | 2021 | 0.016653 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-07-18 21:17 | 2021-07-19 12:00 | 1000 | 014:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEAS PRIMARIAS CRUZADAS SE CERRO CORTE DE LINEA | A21071900005 | New_Event | Wire Down | Include | Include | Equipment | 883 | 2021-07-18 | 883000 | keep | 0 | Jul | 2021 | 0.60141 | 0.0006811 | Sustained | FALSE | TRUE | Not_TMED_Event | 1000
VEGA BAJA | 2021-07-18 21:52 | 2021-07-19 11:43 | 30 | 013:51 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21071800106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 831 | 2021-07-18 | 24930 | keep | 0 | Jul | 2021 | 0.01698 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-07-18 22:04 | 2021-07-19 00:59 | 150 | 002:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CERRO MACHETES EN CALLE MCLEARY ESQUINA MARIA MOCZO SE REMPLAZO CAJA QUEMADA Y SE LLEVO CONDUCTOR DE 1105 05 A AISLADOR | S21071800000 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 175 | 2021-07-18 | 26250 | keep | 0 | Jul | 2021 | 0.017879 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-07-18 22:04 | 2021-07-19 10:07 | 110 | 012:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA Y 1 X 80 EN RISER CRUCE POR AVE | C21071800043 | New_Event |  |  | Include | Wildlife | 723 | 2021-07-18 | 79530 | keep | 0 | Jul | 2021 | 0.054168 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
BAYAMON | 2021-07-18 22:38 | 2021-07-18 22:39 | 2402 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21071800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-18 | 2402 | keep | 0 | Jul | 2021 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2021-07-18 22:48 | 2021-07-19 10:22 | 50 | 011:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA Y SE RETIRO UN AVE | B21071800154 | New_Event |  |  | Include | Wildlife | 694 | 2021-07-18 | 34700 | keep | 0 | Jul | 2021 | 0.023634 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-18 23:08 | 2021-07-19 16:00 | 30 | 016:52 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21071800109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1012 | 2021-07-18 | 30360 | keep | 0 | Jul | 2021 | 0.020678 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-07-18 23:14 | 2021-07-19 09:36 | 15 | 010:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO BAJANTE SECUNDARIO ABIERTO EN TRANSFORMADOR | R21071800044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 622 | 2021-07-18 | 9330 | keep | 0 | Jul | 2021 | 0.0063546 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-07-18 23:19 | 2021-07-19 00:51 | 559 | 001:32 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERUPTOR POR CONDUCTOR SAFADO CRUZANDO CAJA PRIMARIA DE 1118 08 LLEVA CARGA DE 1105 05 | S21071800155 | Additional_clients | Wire Down | Include | Include | Equipment | 92 | 2021-07-18 | 51428 | keep | 0 | Jul | 2021 | 0.035027 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-18 23:19 | 2021-07-19 00:51 | 370 | 001:32 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERUPTOR POR CONDUCTOR SAFADO CRUZANDO CAJA PRIMARIA DE 1118 08 LLEVA CARGA DE 1105 05 | S21071800155 | New_Event | Wire Down | Include | Include | Equipment | 92 | 2021-07-18 | 34040 | keep | 0 | Jul | 2021 | 0.023184 | 0.00025201 | Sustained | FALSE | FALSE | Not_TMED_Event | 370
CANOVANAS | 2021-07-18 23:21 | 2021-07-19 09:17 | 50 | 009:56 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21071800046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 596 | 2021-07-18 | 29800 | keep | 0 | Jul | 2021 | 0.020297 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-18 23:35 | 2021-07-20 11:50 | 40 | 036:15 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21071800048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2175 | 2021-07-18 | 87000 | keep | 0 | Jul | 2021 | 0.059255 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-07-19 00:47 | 2021-07-19 00:48 | 1185 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21071900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-19 | 1185 | keep | 0 | Jul | 2021 | 0.0008071 | 0.0008071 | Momentary | FALSE | FALSE | Not_TMED_Event | 1185
BAYAMON | 2021-07-19 00:51 | 2021-07-19 11:28 | 1 | 010:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | S21071800099 | Partial_restoration | Wire Down | Include | Include | Equipment | 637 | 2021-07-19 | 637 | keep | 0 | Jul | 2021 | 0.00043386 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
HUMACAO | 2021-07-19 00:58 | 2021-07-19 00:59 | 1827 | 000:01 | T | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | RECIERRE | C21071900001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1 | 2021-07-19 | 1827 | keep | 0 | Jul | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
HUMACAO | 2021-07-19 00:59 | 2021-07-19 13:36 | 11 | 012:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRASFORMADOR REPARO SECUNDARIA | C21071900000 | 1st_after_momentary | Secondary Wire Down | Include | Include | Equipment | 757 | 2021-07-19 | 8327 | keep | 0 | Jul | 2021 | 0.0056715 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
ARECIBO | 2021-07-19 01:16 | 2021-07-19 16:55 | 20 | 015:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN TRANSFORMADOR | A21071900003 | New_Event | Cutout Failure | Include | Include | Equipment | 939 | 2021-07-19 | 18780 | keep | 0 | Jul | 2021 | 0.012791 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-07-19 01:18 | 2021-07-19 01:19 | 3431 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21071900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-19 | 3431 | keep | 0 | Jul | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
MAYAGÃœEZ | 2021-07-19 03:05 | 2021-07-19 03:06 | 990 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21071900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-19 | 990 | keep | 0 | Jul | 2021 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
MAYAGÃœEZ | 2021-07-19 03:06 | 2021-07-19 18:30 | 30 | 015:24 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | M21071900040 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 924 | 2021-07-19 | 27720 | keep | 0 | Jul | 2021 | 0.01888 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
HUMACAO | 2021-07-19 04:14 | 2021-07-19 04:15 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21071900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-19 | 2354 | keep | 0 | Jul | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
MAYAGÃœEZ | 2021-07-19 04:20 | 2021-07-19 08:57 | 200 | 004:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN CORTE DE LINEA AVE CRUZO LINEAS | M21071900002 | New_Event |  |  | Include | Wildlife | 277 | 2021-07-19 | 55400 | keep | 0 | Jul | 2021 | 0.037733 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-07-19 04:29 | 2021-07-19 04:30 | 329 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21071900005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-19 | 329 | keep | 0 | Jul | 2021 | 0.00022408 | 0.00022408 | Momentary | FALSE | FALSE | Not_TMED_Event | 329
CAGUAS | 2021-07-19 04:30 | 2021-07-19 13:12 | 130 | 008:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA REEMPLAZO PORTAFUSIBLE | C21071900004 | New_Event | Cutout Failure | Include | Include | Equipment | 522 | 2021-07-19 | 67860 | keep | 0 | Jul | 2021 | 0.046219 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
CANOVANAS | 2021-07-19 05:02 | 2021-07-19 05:03 | 2039 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21071900001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-19 | 2039 | keep | 0 | Jul | 2021 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
VEGA BAJA | 2021-07-19 05:41 | 2021-07-19 09:26 | 8 | 003:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANFORMADOR Y SE RETIRO TOMA DE SERVICIO CRUZADA | B21071900006 | New_Event | Secondary Wire Down | Include | Include | Equipment | 225 | 2021-07-19 | 1800 | keep | 0 | Jul | 2021 | 0.001226 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-07-19 05:52 | 2021-07-19 05:54 | 215 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO POR SCADA | B21071900000 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2021-07-19 | 430 | keep | 0 | Jul | 2021 | 0.00029287 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2021-07-19 05:54 | 2021-07-19 14:35 | 50 | 008:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE CERRO PUENTE DE LINEA A CAJA | B21071900038 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 521 | 2021-07-19 | 26050 | keep | 0 | Jul | 2021 | 0.017743 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-07-19 06:17 | 2021-07-19 10:14 | 90 | 003:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | R21071900003 | New_Event |  |  | Include | Wildlife | 237 | 2021-07-19 | 21330 | keep | 0 | Jul | 2021 | 0.014528 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
VEGA BAJA | 2021-07-19 06:19 | 2021-07-19 10:53 | 35 | 004:34 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21071900009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 274 | 2021-07-19 | 9590 | keep | 0 | Jul | 2021 | 0.0065317 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
CAGUAS | 2021-07-19 06:22 | 2021-07-19 11:29 | 45 | 005:07 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21071900006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 307 | 2021-07-19 | 13815 | keep | 0 | Jul | 2021 | 0.0094093 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
ARECIBO | 2021-07-19 06:36 | 2021-07-19 06:37 | 3431 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21071900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-19 | 3431 | keep | 0 | Jul | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2021-07-19 06:37 | 2021-07-19 11:50 | 200 | 005:13 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21071900007 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 313 | 2021-07-19 | 62600 | keep | 0 | Jul | 2021 | 0.042637 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-07-19 07:00 | 2021-07-19 11:00 | 1 | 004:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO PORTA FUSIBLE AVERIADO | A21071900047 | New_Event | Cutout Failure | Include | Include | Equipment | 240 | 2021-07-19 | 240 | keep | 0 | Jul | 2021 | 0.00016346 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-07-19 07:00 | 2021-07-19 13:15 | 20 | 006:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21071900011 | New_Event | Bad Weather | Include | Include | Weather | 375 | 2021-07-19 | 7500 | keep | 0 | Jul | 2021 | 0.0051082 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-07-19 07:01 | 2021-07-19 20:47 | 63 | 013:46 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21071900003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 826 | 2021-07-19 | 52038 | keep | 0 | Jul | 2021 | 0.035443 | 4.2909e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 63
BARRANQUITAS | 2021-07-19 07:01 | 2021-07-19 07:02 | 3565 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21071900007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-19 | 3565 | keep | 0 | Jul | 2021 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
BARRANQUITAS | 2021-07-19 07:02 | 2021-07-19 11:36 | 65 | 004:34 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C21071900010 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 274 | 2021-07-19 | 17810 | keep | 0 | Jul | 2021 | 0.01213 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
SAN JUAN | 2021-07-19 07:10 | 2021-07-19 20:05 | 90 | 012:55 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21071900004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 775 | 2021-07-19 | 69750 | keep | 0 | Jul | 2021 | 0.047506 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
UTUADO | 2021-07-19 07:19 | 2021-07-19 11:30 | 6 | 004:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON 2 CAJAS PRIMARIAS AVERIADAS | A21071900012 | New_Event | Cutout Failure | Include | Include | Equipment | 251 | 2021-07-19 | 1506 | keep | 0 | Jul | 2021 | 0.0010257 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2021-07-19 07:28 | 2021-07-19 07:29 | 3000 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21071900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-19 | 3000 | keep | 0 | Jul | 2021 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
CAGUAS | 2021-07-19 07:55 | 2021-07-19 11:37 | 65 | 003:42 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA REEMPLAZO AISLADOR ROTO | C21071900012 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 222 | 2021-07-19 | 14430 | keep | 0 | Jul | 2021 | 0.0098282 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BAYAMON | 2021-07-19 08:00 | 2021-07-19 14:56 | 30 | 006:56 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21071900018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 416 | 2021-07-19 | 12480 | keep | 0 | Jul | 2021 | 0.0085001 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-07-19 08:05 | 2021-07-19 18:00 | 7 | 009:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA PARTIDA | M21071900015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 595 | 2021-07-19 | 4165 | keep | 0 | Jul | 2021 | 0.0028368 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
VEGA BAJA | 2021-07-19 08:12 | 2021-07-19 15:55 | 25 | 007:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21071900023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 463 | 2021-07-19 | 11575 | keep | 0 | Jul | 2021 | 0.0078837 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-07-19 08:15 | 2021-07-19 11:33 | 15 | 003:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA Y SE RETIRO AVE | B21071900024 | New_Event |  |  | Include | Wildlife | 198 | 2021-07-19 | 2970 | keep | 0 | Jul | 2021 | 0.0020229 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-07-19 08:17 | 2021-07-19 13:46 | 25 | 005:29 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21071900043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 329 | 2021-07-19 | 8225 | keep | 0 | Jul | 2021 | 0.005602 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-07-19 08:17 | 2021-07-19 16:12 | 1 | 007:55 | T | DESGANCHE | DISPARO Y SE PATRULLO SE REALIZO DESGANCHE Y SE REEMPALZO DOS MACHETES SALIDA DEL ALIMENTADOR | B21071900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 475 | 2021-07-19 | 475 | keep | 0 | Jul | 2021 | 0.00032352 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-07-19 08:25 | 2021-07-19 17:05 | 12 | 008:40 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA X 50 KVA | A21071900020 | New_Event | Service Transformer Failure | Include | Include | Equipment | 520 | 2021-07-19 | 6240 | keep | 0 | Jul | 2021 | 0.00425 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-07-19 08:48 | 2021-07-19 15:52 | 30 | 007:04 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | S21071900015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 424 | 2021-07-19 | 12720 | keep | 0 | Jul | 2021 | 0.0086635 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-07-19 09:00 | 2021-07-19 11:39 | 1 | 002:39 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR RETIRO ENREDADERA | C21071900019 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 159 | 2021-07-19 | 159 | keep | 0 | Jul | 2021 | 0.00010829 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-07-19 09:23 | 2021-07-19 12:06 | 11 | 002:43 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR | C21071900022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2021-07-19 | 1793 | keep | 0 | Jul | 2021 | 0.0012212 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
ARECIBO | 2021-07-19 09:24 | 2021-07-19 13:50 | 70 | 004:26 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A21071900027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2021-07-19 | 18620 | keep | 0 | Jul | 2021 | 0.012682 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BAYAMON | 2021-07-19 09:34 | 2021-07-19 13:03 | 5 | 003:29 | P | TRANSFORMADOR AVERIADO | 2 X 10 EN TRANSFORMADOR Y SE REMPLAZO TRANSFORMADOR AVERIADO DE 15KVA POR 15KVA EN BANCO DE TRANSFORMADORES | B21071900028 | New_Event | Service Transformer Failure | Include | Include | Equipment | 209 | 2021-07-19 | 1045 | keep | 0 | Jul | 2021 | 0.00071174 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-07-19 09:35 | 2021-07-19 13:00 | 15 | 003:25 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE POSTE SECUNDARIO PARTIDO | A21071900034 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 205 | 2021-07-19 | 3075 | keep | 0 | Jul | 2021 | 0.0020944 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-07-19 10:02 | 2021-07-19 16:04 | 10 | 006:02 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21071900047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 362 | 2021-07-19 | 3620 | keep | 0 | Jul | 2021 | 0.0024656 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BAYAMON | 2021-07-19 10:04 | 2021-07-19 10:05 | 514 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR CARGA POR EL 1520-05 | S21071900000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-19 | 514 | keep | 0 | Jul | 2021 | 0.00035008 | 0.00035008 | Momentary | FALSE | FALSE | Not_TMED_Event | 514
BAYAMON | 2021-07-19 10:04 | 2021-07-19 10:05 | 752 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR CARGA POR EL 1520-05 | S21071900000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-19 | 752 | keep | 0 | Jul | 2021 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
BAYAMON | 2021-07-19 10:04 | 2021-07-19 10:05 | 68 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR 1520-05 QUE A SU VEZ LLEVA LA CARGA DEL 1520-01 Y 1520-04 | S21071900000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-19 | 68 | keep | 0 | Jul | 2021 | 4.6314e-05 | 4.6314e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 68
BAYAMON | 2021-07-19 10:05 | 2021-07-19 18:09 | 136 | 008:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A MACHETE | S21071900101 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 484 | 2021-07-19 | 65824 | keep | 0 | Jul | 2021 | 0.044832 | 9.2629e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 136
ARECIBO | 2021-07-19 10:06 | 2021-07-19 12:40 | 75 | 002:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A21071900042 | New_Event | Wire Down | Include | Include | Equipment | 154 | 2021-07-19 | 11550 | keep | 0 | Jul | 2021 | 0.0078667 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
PONCE | 2021-07-19 10:09 | 2021-07-19 13:42 | 100 | 003:33 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA DESGANCHE | P21071900007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2021-07-19 | 21300 | keep | 0 | Jul | 2021 | 0.014507 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-07-19 10:23 | 2021-07-19 18:20 | 300 | 007:57 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE | M21071900051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 477 | 2021-07-19 | 143100 | keep | 0 | Jul | 2021 | 0.097465 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
AGUADILLA | 2021-07-19 10:25 | 2021-07-19 16:56 | 200 | 006:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REALIZO CAMBIO PRIMARIO A POSTE NUEVO | M21071900053 | New_Event | Wire Down | Include | Include | Equipment | 391 | 2021-07-19 | 78200 | keep | 0 | Jul | 2021 | 0.053262 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2021-07-19 10:26 | 2021-07-20 14:52 | 25 | 028:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M21071900054 | New_Event | Bad Weather | Include | Include | Weather | 1706 | 2021-07-19 | 42650 | keep | 0 | Jul | 2021 | 0.029049 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-07-19 10:36 | 2021-07-19 17:30 | 12 | 006:54 | P | HERRAJE ROTO O PODRIDO | SE REEMPLAZO CRUCETA PARTIDA | M21071900056 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 414 | 2021-07-19 | 4968 | keep | 0 | Jul | 2021 | 0.0033837 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-07-19 10:44 | 2021-07-20 10:40 | 1 | 023:56 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21071900058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1436 | 2021-07-19 | 1436 | keep | 0 | Jul | 2021 | 0.00097805 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-07-19 10:49 | 2021-07-19 12:38 | 3000 | 001:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES PARA REPARAR PUENTE PRIMARIO | A21071900057 | New_Event | Wire Down | Include | Include | Equipment | 109 | 2021-07-19 | 327000 | keep | 0 | Jul | 2021 | 0.22272 | 0.0020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 3000
BARRANQUITAS | 2021-07-19 10:53 | 2021-07-19 14:04 | 20 | 003:11 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | C21071900030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2021-07-19 | 3820 | keep | 0 | Jul | 2021 | 0.0026018 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
AGUADILLA | 2021-07-19 11:23 | 2021-07-19 11:24 | 1155 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21071900066 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-19 | 1155 | keep | 0 | Jul | 2021 | 0.00078667 | 0.00078667 | Momentary | FALSE | FALSE | Not_TMED_Event | 1155
AGUADILLA | 2021-07-19 11:24 | 2021-07-20 14:00 | 3 | 026:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M21071900069 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1596 | 2021-07-19 | 4788 | keep | 0 | Jul | 2021 | 0.0032611 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2021-07-19 11:30 | 2021-07-19 16:45 | 18 | 005:15 | P | ESTRUCTURA AVERIADA | SE ABRE CORTE DE LINEA PARA REEMPLAZO DE POSTE PRIMARIO/ SE HIZO EL CAMBIO | P21071900014 | New_Event | Defective Pole | Include | Include | Equipment | 315 | 2021-07-19 | 5670 | keep | 0 | Jul | 2021 | 0.0038618 | 1.226e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 18
CAGUAS | 2021-07-19 11:33 | 2021-07-19 13:27 | 11 | 001:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR REPARO BAJANTE SECUNDARIO | C21071900032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 114 | 2021-07-19 | 1254 | keep | 0 | Jul | 2021 | 0.00085409 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2021-07-19 11:39 | 2021-07-19 11:40 | 1356 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S21071900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-19 | 1356 | keep | 0 | Jul | 2021 | 0.00092357 | 0.00092357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1356
CAGUAS | 2021-07-19 11:44 | 2021-07-19 11:45 | 1271 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21071900034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-19 | 1271 | keep | 0 | Jul | 2021 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
VEGA BAJA | 2021-07-19 12:03 | 2021-07-19 17:25 | 50 | 005:22 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21071900060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 322 | 2021-07-19 | 16100 | keep | 0 | Jul | 2021 | 0.010966 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-19 12:04 | 2021-07-19 12:33 | 9 | 000:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO NEUTRAL SECUNDARIO ABIERTO TENIA 129V QUEDO EN 118V WR5897049 | C21071900000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 29 | 2021-07-19 | 261 | keep | 0 | Jul | 2021 | 0.00017777 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2021-07-19 12:18 | 2021-07-19 13:10 | 50 | 000:52 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA MAL TIEMPO | M21071900000 | New_Event | Bad Weather | Include | Include | Weather | 52 | 2021-07-19 | 2600 | keep | 0 | Jul | 2021 | 0.0017708 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-19 12:33 | 2021-07-19 16:11 | 20 | 003:38 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | B21071900063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 218 | 2021-07-19 | 4360 | keep | 0 | Jul | 2021 | 0.0029696 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-07-19 12:42 | 2021-07-19 13:05 | 30 | 000:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | M21071900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 23 | 2021-07-19 | 690 | keep | 0 | Jul | 2021 | 0.00046996 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
FAJARDO | 2021-07-19 12:45 | 2021-07-19 15:29 | 50 | 002:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA REEMPLAZO CAJA QUEMADA Y REPARO 2 BAJANTES | R21071900022 | New_Event | Cutout Failure | Include | Include | Equipment | 164 | 2021-07-19 | 8200 | keep | 0 | Jul | 2021 | 0.005585 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-19 12:49 | 2021-07-19 20:35 | 80 | 007:46 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER | S21071900053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 466 | 2021-07-19 | 37280 | keep | 0 | Jul | 2021 | 0.025391 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2021-07-19 12:54 | 2021-07-19 17:03 | 100 | 004:09 | P | NO SE REPORTO CAUSA | 2 X 40 EN CORTE DE LINEA NO CAUSA | C21071900038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 249 | 2021-07-19 | 24900 | keep | 0 | Jul | 2021 | 0.016959 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-19 13:01 | 2021-07-19 19:20 | 10 | 006:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE CERRO BAJANTE SECUNDARIO Y NEUTRAL | B21071900068 | New_Event | Secondary Wire Down | Include | Include | Equipment | 379 | 2021-07-19 | 3790 | keep | 0 | Jul | 2021 | 0.0025814 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-19 13:04 | 2021-07-19 20:04 | 40 | 007:00 | P | CABLE SOTERRADO AVERIADO | 1 X 65 EN CORTE DE LINEA AVERIA NUEVA DE T-27 @ T-28 Y AVERIA VIEJA DE T-28 @ T-29. T- 28 CONTINUA FUERA DE SERVICIO | B21071900069 | New_Event | UG Cable Fault | Include | Include | Equipment | 420 | 2021-07-19 | 16800 | keep | 0 | Jul | 2021 | 0.011442 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-07-19 13:27 | 2021-07-19 19:04 | 35 | 005:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21071900071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 337 | 2021-07-19 | 11795 | keep | 0 | Jul | 2021 | 0.0080335 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-07-19 13:45 | 2021-07-19 13:47 | 3708 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7100 | S21071900061 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-19 | 7416 | keep | 0 | Jul | 2021 | 0.005051 | 0.0025255 | Momentary | FALSE | TRUE | Not_TMED_Event | 3708
BAYAMON | 2021-07-19 13:45 | 2021-07-19 13:47 | 24 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7100 | S21071900061 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-19 | 48 | keep | 0 | Jul | 2021 | 3.2693e-05 | 1.6346e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 24
BAYAMON | 2021-07-19 13:45 | 2021-07-19 13:47 | 1 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7100 | S21071900061 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-19 | 2 | keep | 0 | Jul | 2021 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-07-19 13:45 | 2021-07-19 13:47 | 620 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7100 | S21071900061 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-19 | 1240 | keep | 0 | Jul | 2021 | 0.00084456 | 0.00042228 | Momentary | FALSE | TRUE | Not_TMED_Event | 620
BAYAMON | 2021-07-19 13:45 | 2021-07-19 13:47 | 451 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7100 | S21071900061 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-19 | 902 | keep | 0 | Jul | 2021 | 0.00061435 | 0.00030717 | Momentary | FALSE | TRUE | Not_TMED_Event | 451
BAYAMON | 2021-07-19 13:45 | 2021-07-19 13:47 | 333 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7100 | S21071900061 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-19 | 666 | keep | 0 | Jul | 2021 | 0.00045361 | 0.0002268 | Momentary | FALSE | TRUE | Not_TMED_Event | 333
BAYAMON | 2021-07-19 13:47 | 2021-07-19 13:50 | 1 | 000:03 | P | NO SE REPORTO CAUSA | 2 X 20 EN TRASFORMADOR | S21071800101 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-07-19 | 3 | keep | 0 | Jul | 2021 | 2.0433e-06 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-19 13:50 | 2021-07-19 15:32 | 3708 | 001:42 | S | LINEA DE TRANSMISION 38KV | DISPARO L-7100 SE SECCIONALIZO LINEA TRAMO EN EL PISO ENTRE 7107A Y 7101 | S21071900064 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2021-07-19 | 378216 | keep | 0 | Jul | 2021 | 0.2576 | 0.0025255 | Sustained | FALSE | TRUE | Not_TMED_Event | 3708
BAYAMON | 2021-07-19 13:50 | 2021-07-19 15:32 | 24 | 001:42 | S | LINEA DE TRANSMISION 38KV | DISPARO L-7100 SE SECCIONALIZO LINEA TRAMO EN EL PISO ENTRE 7107A Y 7101 | S21071900064 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2021-07-19 | 2448 | keep | 0 | Jul | 2021 | 0.0016673 | 1.6346e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 24
BAYAMON | 2021-07-19 13:50 | 2021-07-19 15:33 | 1 | 001:43 | S | LINEA DE TRANSMISION 38KV | DISPARO L-7100 SE SECCIONALIZO LINEA TRAMO EN EL PISO ENTRE 7107A Y 7101 | S21071900064 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 103 | 2021-07-19 | 103 | keep | 0 | Jul | 2021 | 7.0153e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-07-19 13:50 | 2021-07-19 13:51 | 620 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CARGA POR EL 1133-02 | S21071900155 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-19 | 620 | keep | 0 | Jul | 2021 | 0.00042228 | 0.00042228 | Momentary | FALSE | FALSE | Not_TMED_Event | 620
BAYAMON | 2021-07-19 13:50 | 2021-07-19 13:51 | 451 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA LLEVANDO LA CARGA DEL 1133-01 | S21071900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-19 | 451 | keep | 0 | Jul | 2021 | 0.00030717 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
UTUADO | 2021-07-19 14:07 | 2021-07-19 19:35 | 20 | 005:28 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A21071900073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 328 | 2021-07-19 | 6560 | keep | 0 | Jul | 2021 | 0.004468 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-07-19 14:12 | 2021-07-19 15:15 | 6 | 001:03 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | M21071900087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2021-07-19 | 378 | keep | 0 | Jul | 2021 | 0.00025745 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
HUMACAO | 2021-07-19 14:13 | 2021-07-19 17:19 | 50 | 003:06 | P | TRANSFORMADOR AVERIADO | 1 X 65 EN RISER Y 1 SMU 20 DE 40 AMP EN EL SU - 1 SECCIONALIZO EL T - 2 QUE ESTABA EN FUEGO | C21071900040 | New_Event | Service Transformer Failure | Include | Include | Equipment | 186 | 2021-07-19 | 9300 | keep | 0 | Jul | 2021 | 0.0063342 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-07-19 14:25 | 2021-07-19 15:45 | 60 | 001:20 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | S21071900020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2021-07-19 | 4800 | keep | 0 | Jul | 2021 | 0.0032693 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-07-19 14:26 | 2021-07-19 16:00 | 5 | 001:34 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMA | A21071900075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2021-07-19 | 470 | keep | 0 | Jul | 2021 | 0.00032011 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
SAN JUAN | 2021-07-19 14:44 | 2021-07-20 14:13 | 20 | 023:29 | P | DESGANCHE | 1 X 40 CORTE DE LINEA | S21071900094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1409 | 2021-07-19 | 28180 | keep | 0 | Jul | 2021 | 0.019193 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-07-19 15:10 | 2021-07-19 16:10 | 12 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | S21071600061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2021-07-19 | 720 | keep | 0 | Jul | 2021 | 0.00049039 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-07-19 15:10 | 2021-07-20 13:10 | 2 | 022:00 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO 25 KVA X 25 KVA CAJAS QUEMADAS Y PARARRAYOS | M21071900099 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1320 | 2021-07-19 | 2640 | keep | 0 | Jul | 2021 | 0.0017981 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2021-07-19 15:12 | 2021-07-19 21:16 | 80 | 006:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR REPTIL | C21071900045 | New_Event |  |  | Include | Wildlife | 364 | 2021-07-19 | 29120 | keep | 0 | Jul | 2021 | 0.019833 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-07-19 15:14 | 2021-07-20 15:34 | 12 | 024:20 | P | NO SE REPORTO CAUSA | 1 X 10 EN T-32 | B21071900082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1460 | 2021-07-19 | 17520 | keep | 0 | Jul | 2021 | 0.011933 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-07-19 15:23 | 2021-07-19 19:25 | 4161 | 004:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO NEUTRAL PRIMARIO | C21071900048 | New_Event | Wire Down | Include | Include | Equipment | 242 | 2021-07-19 | 1006962 | keep | 0 | Jul | 2021 | 0.68584 | 0.002834 | Sustained | FALSE | FALSE | Not_TMED_Event | 4161
SAN JUAN | 2021-07-19 15:26 | 2021-07-19 15:30 | 929 | 000:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO CON RECIERRE EN OFF SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA CARGA 1421-04 Y 1421-03 | S21071900000 | New_Event | Wire Down | Include | Include | Equipment | 4 | 2021-07-19 | 3716 | keep | 0 | Jul | 2021 | 0.002531 | 0.00063274 | Momentary | FALSE | FALSE | Not_TMED_Event | 929
SAN JUAN | 2021-07-19 15:26 | 2021-07-19 15:30 | 451 | 000:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO CON RECIERRE EN OFF SE PROBO POR CONTROL QUEDO EN SERVICIO CARGA POR EL 1414-04 | S21071900000 | New_Event | Wire Down | Include | Include | Equipment | 4 | 2021-07-19 | 1804 | keep | 0 | Jul | 2021 | 0.0012287 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
SAN JUAN | 2021-07-19 15:26 | 2021-07-19 15:30 | 451 | 000:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO CON RECIERRE EN OFF SE PROBO POR CONTROL QUEDO EN SERVICIO CARGA POR EL 1414-04 | S21071900000 | New_Event | Wire Down | Include | Include | Equipment | 4 | 2021-07-19 | 1804 | keep | 0 | Jul | 2021 | 0.0012287 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
SAN JUAN | 2021-07-19 15:30 | 2021-07-20 09:23 | 310 | 017:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO EN EL TRONCAL LLEVANDO CARGA DEL 1421-03 Y 1421-04 | S21071900135 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1073 | 2021-07-19 | 332630 | keep | 0 | Jul | 2021 | 0.22655 | 0.00021114 | Sustained | FALSE | FALSE | Not_TMED_Event | 310
SAN JUAN | 2021-07-19 15:30 | 2021-07-20 09:23 | 150 | 017:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO CARGA POR EL 1414-04 | S21071900135 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1073 | 2021-07-19 | 160950 | keep | 0 | Jul | 2021 | 0.10962 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2021-07-19 15:30 | 2021-07-20 09:23 | 180 | 017:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO CARGA POR EL 1414-04 | S21071900135 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1073 | 2021-07-19 | 193140 | keep | 0 | Jul | 2021 | 0.13155 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
BAYAMON | 2021-07-19 15:33 | 2021-07-20 06:15 | 1 | 014:42 | P | NO SE REPORTO CAUSA | 2 X 20 EN TRASFORMADOR | S21071800101 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 882 | 2021-07-19 | 882 | keep | 0 | Jul | 2021 | 0.00060073 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-07-19 15:51 | 2021-07-19 18:06 | 569 | 002:15 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE RETIRARON BAMBUAS | M21071900104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2021-07-19 | 76815 | keep | 0 | Jul | 2021 | 0.052318 | 0.00038754 | Sustained | FALSE | FALSE | Not_TMED_Event | 569
BARRANQUITAS | 2021-07-19 15:52 | 2021-07-19 19:20 | 1 | 003:28 | P | NO SE REPORTO CAUSA | 1 X 15 EN BANCO DE TRANSFORMADORES | C21071900055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 208 | 2021-07-19 | 208 | keep | 0 | Jul | 2021 | 0.00014167 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-07-19 16:00 | 2021-07-19 17:00 | 8 | 001:00 | P | PARARRAYOS DEFECTUOSO | 1 X 25 EN TRANSFORMADOR SE REMPLAZO PARARRAYO CRUZADO | A21071900000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 60 | 2021-07-19 | 480 | keep | 0 | Jul | 2021 | 0.00032693 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-07-19 16:00 | 2021-07-19 18:26 | 50 | 002:26 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21071900083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2021-07-19 | 7300 | keep | 0 | Jul | 2021 | 0.004972 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-19 16:10 | 2021-07-19 16:42 | 6 | 000:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA WR5897197 | C21071900000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 32 | 2021-07-19 | 192 | keep | 0 | Jul | 2021 | 0.00013077 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-07-19 16:18 | 2021-07-19 16:22 | 726 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO CON RECIERRE EN OFF SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA CARGA 1346-04 | S21071900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-07-19 | 2904 | keep | 0 | Jul | 2021 | 0.0019779 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-07-19 16:18 | 2021-07-19 16:22 | 3932 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO CON RECIERRE EN OFF SE PROBO POR CONTROL QUEDO EN SERVICIO CARGA POR 1303-03 | S21071900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-07-19 | 15728 | keep | 0 | Jul | 2021 | 0.010712 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
BAYAMON | 2021-07-19 16:29 | 2021-07-19 19:20 | 10 | 002:51 | P | PARARRAYOS DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE REEMPLAZO PARARRAYO | S21071800105 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 171 | 2021-07-19 | 1710 | keep | 0 | Jul | 2021 | 0.0011647 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-19 16:40 | 2021-07-19 18:08 | 3 | 001:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO AISLADOR Y SE LLEVO LINEA A SU LUGAR | B21071900087 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 88 | 2021-07-19 | 264 | keep | 0 | Jul | 2021 | 0.00017981 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-07-19 16:52 | 2021-07-19 18:39 | 50 | 001:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | M21071900112 | New_Event | Cutout Failure | Include | Include | Equipment | 107 | 2021-07-19 | 5350 | keep | 0 | Jul | 2021 | 0.0036439 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-19 17:07 | 2021-07-19 17:08 | 90 | 000:01 | T | LINEA DE TRANSMISION 38KV | SE ABRE INTERRUPTOR A PETICION DE JAVIER ALICANO PARA LEVANTAR OVERHEAD LLEVA 1109-01 Y 1109-04 | S21071900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-19 | 90 | keep | 0 | Jul | 2021 | 6.1299e-05 | 6.1299e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2021-07-19 17:07 | 2021-07-19 17:08 | 1105 | 000:01 | T | LINEA DE TRANSMISION 38KV | SE ABRE INTERRUPTOR A PETICION DE JAVIER ALICANO PARA LEVANTAR OVERHEAD CARGA POR 1100-05 | S21071900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-19 | 1105 | keep | 0 | Jul | 2021 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
SAN JUAN | 2021-07-19 17:07 | 2021-07-19 17:08 | 351 | 000:01 | T | LINEA DE TRANSMISION 38KV | SE ABRE INTERRUPTOR A PETICION DE JAVIER ALICANO PARA LEVANTAR OVERHEAD CARGA POR 1100-05 | S21071900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-19 | 351 | keep | 0 | Jul | 2021 | 0.00023906 | 0.00023906 | Momentary | FALSE | FALSE | Not_TMED_Event | 351
SAN JUAN | 2021-07-19 17:09 | 2021-07-19 17:10 | 200 | 000:01 | P | LINEA DE TRANSMISION 38KV | SE ABRE INTERRUPTOR POR AVERIA EN L-7100 CARGA POR EL 1113-03 | S21071900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-19 | 200 | keep | 0 | Jul | 2021 | 0.00013622 | 0.00013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-07-19 17:09 | 2021-07-19 17:10 | 181 | 000:01 | T | LINEA DE TRANSMISION 38KV | SE ABRE INTERRUPTOR POR AVERIA EN L-7100 CARGA POR EL 1113-03 | S21071900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-19 | 181 | keep | 0 | Jul | 2021 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
SAN JUAN | 2021-07-19 17:09 | 2021-07-19 17:10 | 570 | 000:01 | T | LINEA DE TRANSMISION 38KV | SE ABRE INTERRUPTOR POR AVERIA EN L-7100 CARGA POR EL 1113-03 | S21071900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-19 | 570 | keep | 0 | Jul | 2021 | 0.00038822 | 0.00038822 | Momentary | FALSE | FALSE | Not_TMED_Event | 570
SAN JUAN | 2021-07-19 17:09 | 2021-07-19 17:10 | 32 | 000:01 | T | LINEA DE TRANSMISION 38KV | SE ABRE INTERRUPTOR POR AVERIA EN L-7100 LLEVA CARGA 1109-05, PARTE DEL 1105-01 Y LLEVA 1109-02 | S21071900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-19 | 32 | keep | 0 | Jul | 2021 | 2.1795e-05 | 2.1795e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 32
BAYAMON | 2021-07-19 17:13 | 2021-07-19 18:23 | 620 | 001:10 | T | LINEA DE TRANSMISION 38KV | SE ABRE INTERRUPTOR PARA LEVANTAR OVERHEAD L-7100 CARGA POR EL 1133-02 | S21071900155 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 70 | 2021-07-19 | 43400 | keep | 0 | Jul | 2021 | 0.02956 | 0.00042228 | Sustained | FALSE | FALSE | Not_TMED_Event | 620
BAYAMON | 2021-07-19 17:13 | 2021-07-19 18:23 | 451 | 001:10 | T | LINEA DE TRANSMISION 38KV | SE ABRE INTERRUPTOR PARA LEVANTAR OVERHEAD L-7100 LLEVANDO LA CARGA DEL 1133-01 | S21071900155 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 70 | 2021-07-19 | 31570 | keep | 0 | Jul | 2021 | 0.021502 | 0.00030717 | Sustained | FALSE | FALSE | Not_TMED_Event | 451
HUMACAO | 2021-07-19 17:19 | 2021-07-20 17:02 | 30 | 023:43 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO T-2 AVERIADO DE 50KVA X 50KVA Y TIRO PROVISIONAL AEREO DEL T-1 A T-2 | C21071900040 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 1423 | 2021-07-19 | 42690 | keep | 0 | Jul | 2021 | 0.029076 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-07-19 17:32 | 2021-07-20 10:40 | 20 | 017:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21071900084 | New_Event | Bad Weather | Include | Include | Weather | 1028 | 2021-07-19 | 20560 | keep | 0 | Jul | 2021 | 0.014003 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-07-19 17:46 | 2021-07-20 13:07 | 19 | 019:21 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C21071900080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1161 | 2021-07-19 | 22059 | keep | 0 | Jul | 2021 | 0.015024 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
ARECIBO | 2021-07-19 17:48 | 2021-07-19 20:45 | 80 | 002:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 40 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A21071900085 | New_Event | Wire Down | Include | Include | Equipment | 177 | 2021-07-19 | 14160 | keep | 0 | Jul | 2021 | 0.0096443 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-07-19 18:00 | 2021-07-20 11:56 | 95 | 017:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 Y 1 X 40 EN CORTES DE LINEAS SE RETEZO NEUTRAL PRIMARIO | C21071900083 | New_Event | Wire Down | Include | Include | Equipment | 1076 | 2021-07-19 | 102220 | keep | 0 | Jul | 2021 | 0.069622 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
AGUADILLA | 2021-07-19 18:17 | 2021-07-19 22:35 | 8 | 004:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO LINEA SECUNDARIA PARTIDA | M21071900119 | New_Event | Secondary Wire Down | Include | Include | Equipment | 258 | 2021-07-19 | 2064 | keep | 0 | Jul | 2021 | 0.0014058 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
CAGUAS | 2021-07-19 18:19 | 2021-07-19 20:46 | 40 | 002:27 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21071900089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2021-07-19 | 5880 | keep | 0 | Jul | 2021 | 0.0040048 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-07-19 18:21 | 2021-07-20 15:28 | 12 | 021:07 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR AVERIADO DE 50KVA X 50KVA | C21071900091 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1267 | 2021-07-19 | 15204 | keep | 0 | Jul | 2021 | 0.010355 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-07-19 18:22 | 2021-07-20 09:55 | 1 | 015:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN TRANSFORMADOR CULEBRA CRUZO LINEAS | A21071900089 | New_Event |  |  | Include | Wildlife | 933 | 2021-07-19 | 933 | keep | 0 | Jul | 2021 | 0.00063546 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-07-19 18:31 | 2021-07-19 22:20 | 50 | 003:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C21071900092 | New_Event |  |  | Include | Wildlife | 229 | 2021-07-19 | 11450 | keep | 0 | Jul | 2021 | 0.0077985 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-19 18:56 | 2021-07-20 10:43 | 50 | 015:47 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S21071900169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 947 | 2021-07-19 | 47350 | keep | 0 | Jul | 2021 | 0.03225 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-19 19:24 | 2021-07-20 11:51 | 10 | 016:27 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B21071900093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 987 | 2021-07-19 | 9870 | keep | 0 | Jul | 2021 | 0.0067224 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-07-19 19:24 | 2021-07-20 03:12 | 45 | 007:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21071900099 | New_Event | Bad Weather | Include | Include | Weather | 468 | 2021-07-19 | 21060 | keep | 0 | Jul | 2021 | 0.014344 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
MAYAGÃœEZ | 2021-07-19 19:39 | 2021-07-20 13:00 | 80 | 017:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | M21071900127 | New_Event | Wire Down | Include | Include | Equipment | 1041 | 2021-07-19 | 83280 | keep | 0 | Jul | 2021 | 0.056722 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-07-19 19:49 | 2021-07-19 19:50 | 3701 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21071900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-19 | 3701 | keep | 0 | Jul | 2021 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
BARRANQUITAS | 2021-07-19 19:50 | 2021-07-20 11:28 | 55 | 015:38 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C21071900101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 938 | 2021-07-19 | 51590 | keep | 0 | Jul | 2021 | 0.035138 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
BAYAMON | 2021-07-19 19:55 | 2021-07-20 12:02 | 10 | 016:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | B21071900095 | New_Event | Secondary Wire Down | Include | Include | Equipment | 967 | 2021-07-19 | 9670 | keep | 0 | Jul | 2021 | 0.0065862 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-07-19 19:58 | 2021-07-19 19:59 | 3701 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21071900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-19 | 3701 | keep | 0 | Jul | 2021 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
BAYAMON | 2021-07-19 20:04 | 2021-07-20 10:28 | 10 | 014:24 | P | CABLE SOTERRADO AVERIADO | SE PREPARO PROVISIONAL AEREO PARA DAR SERVICIO A T-28 | B21072000087 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 864 | 2021-07-19 | 8640 | keep | 0 | Jul | 2021 | 0.0058847 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-07-19 20:29 | 2021-07-19 20:30 | 3701 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21071900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-19 | 3701 | keep | 0 | Jul | 2021 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
BAYAMON | 2021-07-19 20:34 | 2021-07-20 21:56 | 100 | 025:22 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21071900183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1522 | 2021-07-19 | 152200 | keep | 0 | Jul | 2021 | 0.10366 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-19 21:22 | 2021-07-20 20:15 | 15 | 022:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B21071900103 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1373 | 2021-07-19 | 20595 | keep | 0 | Jul | 2021 | 0.014027 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-07-19 21:33 | 2021-07-22 12:03 | 20 | 062:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B21071900104 | New_Event | Secondary Wire Down | Include | Include | Equipment | 3750 | 2021-07-19 | 75000 | keep | 0 | Jul | 2021 | 0.051082 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-07-19 21:37 | 2021-07-20 06:36 | 656 | 008:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO | P21071900034 | New_Event | Bad Weather | Include | Include | Weather | 539 | 2021-07-19 | 353584 | keep | 0 | Jul | 2021 | 0.24082 | 0.0004468 | Sustained | FALSE | TRUE | Not_TMED_Event | 656
MAYAGÃœEZ | 2021-07-19 21:53 | 2021-07-20 22:45 | 25 | 024:52 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21071900138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1492 | 2021-07-19 | 37300 | keep | 0 | Jul | 2021 | 0.025405 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-07-19 22:56 | 2021-07-19 22:57 | 1253 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M210719000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-19 | 1253 | keep | 0 | Jul | 2021 | 0.00085341 | 0.00085341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1253
BAYAMON | 2021-07-20 01:16 | 2021-07-20 05:39 | 700 | 004:23 | T | DESCONECTIVO DEFECTUOSO | SE CERRO INTERRUPTOR ABRIENDO MACHETES EN CARRETERA 2 FRENTE A GIMNASIO MUNICIPAL LLEVA CARGA 1711-03 | B21072000001 | New_Event | Switch Failure | Include | Include | Equipment | 263 | 2021-07-20 | 184100 | keep | 0 | Jul | 2021 | 0.12539 | 0.00047677 | Sustained | FALSE | FALSE | Not_TMED_Event | 700
BAYAMON | 2021-07-20 01:16 | 2021-07-20 14:56 | 13 | 013:40 | T | DESCONECTIVO DEFECTUOSO | DISPARO CARGA POR EL 1711-01 | B21072000000 | New_Event | Switch Failure | Include | Include | Equipment | 820 | 2021-07-20 | 10660 | keep | 0 | Jul | 2021 | 0.0072605 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2021-07-20 01:54 | 2021-07-20 11:21 | 10 | 009:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA Y PARARRAYO | B21072000004 | New_Event | Cutout Failure | Include | Include | Equipment | 567 | 2021-07-20 | 5670 | keep | 0 | Jul | 2021 | 0.0038618 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-20 03:00 | 2021-07-20 03:01 | 6285 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M21072000000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-20 | 6285 | keep | 0 | Jul | 2021 | 0.0042807 | 0.0042807 | Momentary | FALSE | FALSE | Not_TMED_Event | 6285
AGUADILLA | 2021-07-20 03:01 | 2021-07-20 09:45 | 11 | 006:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21071800147 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 404 | 2021-07-20 | 4444 | keep | 0 | Jul | 2021 | 0.0030268 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
ARECIBO | 2021-07-20 03:02 | 2021-07-20 16:10 | 15 | 013:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | A21072000002 | New_Event | Wire Down | Include | Include | Equipment | 788 | 2021-07-20 | 11820 | keep | 0 | Jul | 2021 | 0.0080505 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-07-20 03:12 | 2021-07-20 03:13 | 1827 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | C21072000003 | Additional_clients | Bad Weather | Include | Include | Weather | 1 | 2021-07-20 | 1827 | keep | 0 | Jul | 2021 | 0.0012444 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-07-20 03:13 | 2021-07-20 11:30 | 45 | 008:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21071900099 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 497 | 2021-07-20 | 22365 | keep | 0 | Jul | 2021 | 0.015233 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
SAN JUAN | 2021-07-20 03:22 | 2021-07-20 10:23 | 5290 | 007:01 | T | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO MACHETES AVERIADOS Y SE CERRO POR SCADA LLEVA 1336-09 | S21072000000 | New_Event | Switch Failure | Include | Include | Equipment | 421 | 2021-07-20 | 2227090 | keep | 0 | Jul | 2021 | 1.5169 | 0.003603 | Sustained | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2021-07-20 03:22 | 2021-07-20 10:23 | 207 | 007:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO CARGA POR EL 1336-08 | S21072000000 | New_Event | Switch Failure | Include | Include | Equipment | 421 | 2021-07-20 | 87147 | keep | 0 | Jul | 2021 | 0.059355 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
CAGUAS | 2021-07-20 04:30 | 2021-07-20 15:38 | 10 | 011:08 | P | NO SE REPORTO CAUSA | 1 X 10 EN BANCO DE TRANSFORMADOR | C21072000033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 668 | 2021-07-20 | 6680 | keep | 0 | Jul | 2021 | 0.0045497 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-07-20 05:10 | 2021-07-20 12:50 | 65 | 007:40 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21072000004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 460 | 2021-07-20 | 29900 | keep | 0 | Jul | 2021 | 0.020365 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
HUMACAO | 2021-07-20 05:19 | 2021-07-20 17:05 | 55 | 011:46 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21072000006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 706 | 2021-07-20 | 38830 | keep | 0 | Jul | 2021 | 0.026447 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
BAYAMON | 2021-07-20 05:39 | 2021-07-20 06:52 | 300 | 001:13 | P | DESCONECTIVO DEFECTUOSO | ALIMENTADOR SECCIONALIZADO LLEVA CARGA 1711-03 | B21072000001 | Partial_restoration | Switch Failure | Include | Include | Equipment | 73 | 2021-07-20 | 21900 | keep | 0 | Jul | 2021 | 0.014916 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-07-20 06:00 | 2021-07-20 12:31 | 80 | 006:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA Y REPARO CONDUCTOR ROTO NO FUNDIO FUSIBLE | C21072000007 | New_Event | Wire Down | Include | Include | Equipment | 391 | 2021-07-20 | 31280 | keep | 0 | Jul | 2021 | 0.021305 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
AGUADILLA | 2021-07-20 06:00 | 2021-07-20 22:20 | 20 | 016:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21072200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 980 | 2021-07-20 | 19600 | keep | 0 | Jul | 2021 | 0.013349 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-07-20 06:15 | 2021-07-20 11:55 | 3708 | 005:40 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | SUBESTACION EN LOCK-OUT SE REPARARON TIERRAS ABIERTAS EN TRANSFORMADOR 1114-00 Y SE NORMALIZARON CARGAS | S21072000110 | New_Event | Wire Down | Include | Include | Equipment | 340 | 2021-07-20 | 1260720 | keep | 0 | Jul | 2021 | 0.85867 | 0.0025255 | Sustained | FALSE | FALSE | Not_TMED_Event | 3708
BAYAMON | 2021-07-20 06:15 | 2021-07-20 11:55 | 24 | 005:40 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | SUBESTACION EN LOCK-OUT SE REPARARON TIERRAS ABIERTAS EN TRANSFORMADOR 1114-00 Y SE NORMALIZARON CARGAS | S21072000110 | New_Event | Wire Down | Include | Include | Equipment | 340 | 2021-07-20 | 8160 | keep | 0 | Jul | 2021 | 0.0055577 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2021-07-20 06:15 | 2021-07-20 11:55 | 1 | 005:40 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | SUBESTACION EN LOCK-OUT SE REPARARON TIERRAS ABIERTAS EN TRANSFORMADOR 1114-00 Y SE NORMALIZARON CARGAS | S21072000110 | New_Event | Wire Down | Include | Include | Equipment | 340 | 2021-07-20 | 340 | keep | 0 | Jul | 2021 | 0.00023157 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-07-20 06:35 | 2021-07-20 10:08 | 60 | 003:33 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE RETIRO PARARRAYOS DEFECTUOSO | A21072000004 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 213 | 2021-07-20 | 12780 | keep | 0 | Jul | 2021 | 0.0087044 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
YAUCO | 2021-07-20 06:43 | 2021-07-20 06:44 | 1924 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISAPRO DE LINEA 700 | P21072000002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-20 | 1924 | keep | 0 | Jul | 2021 | 0.0013104 | 0.0013104 | Momentary | FALSE | TRUE | Not_TMED_Event | 1924
YAUCO | 2021-07-20 06:43 | 2021-07-20 06:44 | 968 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISAPRO DE LINEA 700 | P21072000002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-20 | 968 | keep | 0 | Jul | 2021 | 0.0006593 | 0.0006593 | Momentary | FALSE | TRUE | Not_TMED_Event | 968
YAUCO | 2021-07-20 06:43 | 2021-07-20 06:44 | 680 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISAPRO DE LINEA 700 | P21072000002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-20 | 680 | keep | 0 | Jul | 2021 | 0.00046314 | 0.00046314 | Momentary | FALSE | TRUE | Not_TMED_Event | 680
YAUCO | 2021-07-20 06:43 | 2021-07-20 06:44 | 2246 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISAPRO DE LINEA 700 | P21072000002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-20 | 2246 | keep | 0 | Jul | 2021 | 0.0015297 | 0.0015297 | Momentary | FALSE | TRUE | Not_TMED_Event | 2246
YAUCO | 2021-07-20 06:43 | 2021-07-20 06:45 | 2470 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072000002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-20 | 4940 | keep | 0 | Jul | 2021 | 0.0033646 | 0.0016823 | Momentary | FALSE | TRUE | Not_TMED_Event | 2470
YAUCO | 2021-07-20 06:43 | 2021-07-20 06:45 | 1182 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072000002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-20 | 2364 | keep | 0 | Jul | 2021 | 0.0016101 | 0.00080505 | Momentary | FALSE | TRUE | Not_TMED_Event | 1182
YAUCO | 2021-07-20 06:43 | 2021-07-20 06:45 | 2340 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072000002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-20 | 4680 | keep | 0 | Jul | 2021 | 0.0031875 | 0.0015938 | Momentary | FALSE | TRUE | Not_TMED_Event | 2340
YAUCO | 2021-07-20 06:43 | 2021-07-20 06:45 | 1637 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072000002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-20 | 3274 | keep | 0 | Jul | 2021 | 0.0022299 | 0.001115 | Momentary | FALSE | TRUE | Not_TMED_Event | 1637
YAUCO | 2021-07-20 06:43 | 2021-07-20 06:45 | 1475 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072000002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-20 | 2950 | keep | 0 | Jul | 2021 | 0.0020092 | 0.0010046 | Momentary | FALSE | TRUE | Not_TMED_Event | 1475
YAUCO | 2021-07-20 06:43 | 2021-07-20 06:45 | 661 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072000002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-20 | 1322 | keep | 0 | Jul | 2021 | 0.00090041 | 0.0004502 | Momentary | FALSE | TRUE | Not_TMED_Event | 661
YAUCO | 2021-07-20 06:43 | 2021-07-20 06:45 | 1569 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072000002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-20 | 3138 | keep | 0 | Jul | 2021 | 0.0021373 | 0.0010686 | Momentary | FALSE | TRUE | Not_TMED_Event | 1569
YAUCO | 2021-07-20 06:43 | 2021-07-20 06:45 | 2309 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072000002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-20 | 4618 | keep | 0 | Jul | 2021 | 0.0031453 | 0.0015726 | Momentary | FALSE | TRUE | Not_TMED_Event | 2309
YAUCO | 2021-07-20 06:43 | 2021-07-20 06:45 | 2179 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072000002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-20 | 4358 | keep | 0 | Jul | 2021 | 0.0029682 | 0.0014841 | Momentary | FALSE | TRUE | Not_TMED_Event | 2179
YAUCO | 2021-07-20 06:43 | 2021-07-20 06:45 | 2440 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072000002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-20 | 4880 | keep | 0 | Jul | 2021 | 0.0033237 | 0.0016619 | Momentary | FALSE | TRUE | Not_TMED_Event | 2440
YAUCO | 2021-07-20 06:43 | 2021-07-20 06:45 | 1352 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072000002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-20 | 2704 | keep | 0 | Jul | 2021 | 0.0018417 | 0.00092084 | Momentary | FALSE | TRUE | Not_TMED_Event | 1352
YAUCO | 2021-07-20 06:43 | 2021-07-20 06:45 | 3973 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072000002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-20 | 7946 | keep | 0 | Jul | 2021 | 0.005412 | 0.002706 | Momentary | FALSE | TRUE | Not_TMED_Event | 3973
YAUCO | 2021-07-20 06:43 | 2021-07-20 06:45 | 2484 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072000002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-20 | 4968 | keep | 0 | Jul | 2021 | 0.0033837 | 0.0016918 | Momentary | FALSE | TRUE | Not_TMED_Event | 2484
UTUADO | 2021-07-20 06:50 | 2021-07-20 12:53 | 50 | 006:03 | P | PARARRAYOS DEFECTUOSO | 2 X 30 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSOS | A21072000005 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 363 | 2021-07-20 | 18150 | keep | 0 | Jul | 2021 | 0.012362 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-20 06:52 | 2021-07-20 06:57 | 700 | 000:05 | T | DESCONECTIVO DEFECTUOSO | SE CERRO INTERRUPTOR ABRIENDO MACHETES EN ALTURAS DE FLAMBOYAN LLEVA CARGA 1711 03 | B21072000001 | Additional_clients | Switch Failure | Include | Include | Equipment | 5 | 2021-07-20 | 3500 | keep | 0 | Jul | 2021 | 0.0023838 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-20 06:57 | 2021-07-20 14:56 | 300 | 007:59 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZARON MACHETES QUEMADOS Y SE NORMALIZARON LAS CARGAS | B21072000001 | Partial_restoration | Switch Failure | Include | Include | Equipment | 479 | 2021-07-20 | 143700 | keep | 0 | Jul | 2021 | 0.097873 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-20 07:10 | 2021-07-20 07:11 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21072000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-20 | 2605 | keep | 0 | Jul | 2021 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
ARECIBO | 2021-07-20 07:20 | 2021-07-20 13:18 | 50 | 005:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A21072000010 | New_Event | Cutout Failure | Include | Include | Equipment | 358 | 2021-07-20 | 17900 | keep | 0 | Jul | 2021 | 0.012192 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-20 07:22 | 2021-07-20 07:23 | 1001 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21072000010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-20 | 1001 | keep | 0 | Jul | 2021 | 0.00068178 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
PONCE | 2021-07-20 07:27 | 2021-07-20 07:28 | 836 | 000:01 | T | ESTRUCTURA AVERIADA | RECIERRE | P21072000005 | New_Event | Defective Pole | Include | Include | Equipment | 1 | 2021-07-20 | 836 | keep | 0 | Jul | 2021 | 0.0005694 | 0.0005694 | Momentary | FALSE | FALSE | Not_TMED_Event | 836
PONCE | 2021-07-20 07:28 | 2021-07-20 17:30 | 120 | 010:02 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PRIMARIO | P21072000019 | 1st_after_momentary | Defective Pole | Include | Include | Equipment | 602 | 2021-07-20 | 72240 | keep | 0 | Jul | 2021 | 0.049202 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
ARECIBO | 2021-07-20 07:28 | 2021-07-20 07:29 | 2107 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21072000012 | New_Event |  |  | Include | Wildlife | 1 | 2021-07-20 | 2107 | keep | 0 | Jul | 2021 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
UTUADO | 2021-07-20 07:42 | 2021-07-20 11:28 | 100 | 003:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21072000016 | New_Event | Bad Weather | Include | Include | Weather | 226 | 2021-07-20 | 22600 | keep | 0 | Jul | 2021 | 0.015393 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-07-20 07:59 | 2021-07-20 12:32 | 400 | 004:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ABIERTO SE ABRIO INTERRUPTOR | M21072000020 | New_Event | Wire Down | Include | Include | Equipment | 273 | 2021-07-20 | 109200 | keep | 0 | Jul | 2021 | 0.074376 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
MAYAGÃœEZ | 2021-07-20 08:00 | 2021-07-20 14:10 | 25 | 006:10 | P | LINEA DE TRANSMISION 38KV | SE ABRIO CORTE DE LINEA PARA REMPLAZO DE TORRE DE LINEA 1200 | M21072000015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 370 | 2021-07-20 | 9250 | keep | 0 | Jul | 2021 | 0.0063001 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
PONCE | 2021-07-20 08:01 | 2021-07-20 13:38 | 79 | 005:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE CRUZO LINEAS | P21072000006 | New_Event |  |  | Include | Wildlife | 337 | 2021-07-20 | 26623 | keep | 0 | Jul | 2021 | 0.018133 | 5.3807e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 79
BAYAMON | 2021-07-20 08:05 | 2021-07-20 13:02 | 50 | 004:57 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21072000035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 297 | 2021-07-20 | 14850 | keep | 0 | Jul | 2021 | 0.010114 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-20 08:07 | 2021-07-20 14:36 | 60 | 006:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | B21072000036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 389 | 2021-07-20 | 23340 | keep | 0 | Jul | 2021 | 0.015897 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-07-20 08:14 | 2021-07-20 08:15 | 3458 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21072000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-20 | 3458 | keep | 0 | Jul | 2021 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
BAYAMON | 2021-07-20 08:23 | 2021-07-20 18:21 | 50 | 009:58 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO AISLADOR | B21072000124 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 598 | 2021-07-20 | 29900 | keep | 0 | Jul | 2021 | 0.020365 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-07-20 08:34 | 2021-07-20 11:04 | 19 | 002:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORAMDOR PARA REEMPLAZAR BARRA EN PEDESTAL | R21072000004 | New_Event | Secondary Wire Down | Include | Include | Equipment | 150 | 2021-07-20 | 2850 | keep | 0 | Jul | 2021 | 0.0019411 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
CAGUAS | 2021-07-20 08:36 | 2021-07-20 09:57 | 1 | 001:21 | P | DESGANCHE | 3 X 40 EN CORTE DE LINEA | C21072000014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2021-07-20 | 81 | keep | 0 | Jul | 2021 | 5.5169e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-07-20 08:51 | 2021-07-20 10:40 | 40 | 001:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21072000026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2021-07-20 | 4360 | keep | 0 | Jul | 2021 | 0.0029696 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
GUAYAMA | 2021-07-20 09:00 | 2021-07-20 14:08 | 15 | 005:08 | P | ESTRUCTURA AVERIADA | SE CAMBIO POSTE PRIMARIO | P21072000007 | New_Event | Defective Pole | Include | Include | Equipment | 308 | 2021-07-20 | 4620 | keep | 0 | Jul | 2021 | 0.0031467 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-07-20 09:07 | 2021-07-20 11:50 | 100 | 002:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEAS PRIMARIAS ARRIADAS | A21072000030 | New_Event | Wire Down | Include | Include | Equipment | 163 | 2021-07-20 | 16300 | keep | 0 | Jul | 2021 | 0.011102 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-20 09:09 | 2021-07-20 09:10 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S21072000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-20 | 2435 | keep | 0 | Jul | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2021-07-20 09:23 | 2021-07-20 10:22 | 929 | 000:59 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1414-04 QUE LLEVA 1421-04 Y 1421-03 PARA CERRAR PUENTE ABIERTO DEL TRONCAL | S21071900135 | Additional_clients | Wire Down | Include | Include | Equipment | 59 | 2021-07-20 | 54811 | keep | 0 | Jul | 2021 | 0.037332 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-20 09:23 | 2021-07-20 10:22 | 533 | 000:59 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1414-04 QUE LLEVA 1421-03 PARA CERRAR PUENTE ABIERTO DEL TRONCAL | S21071900135 | Additional_clients | Wire Down | Include | Include | Equipment | 59 | 2021-07-20 | 31447 | keep | 0 | Jul | 2021 | 0.021418 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-20 09:23 | 2021-07-20 10:22 | 451 | 000:59 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1414-04 QUE LLEVA 1421-04 PARA CERRAR PUENTE ABIERTO DEL TRONCAL | S21071900135 | Additional_clients | Wire Down | Include | Include | Equipment | 59 | 2021-07-20 | 26609 | keep | 0 | Jul | 2021 | 0.018123 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-07-20 09:23 | 2021-07-20 16:13 | 1036 | 006:50 | T | ESTRUCTURA AVERIADA | CARGA POR 7301-05 | M21072000036 | New_Event | Defective Pole | Include | Include | Equipment | 410 | 2021-07-20 | 424760 | keep | 0 | Jul | 2021 | 0.2893 | 0.00070561 | Sustained | FALSE | FALSE | Not_TMED_Event | 1036
AGUADILLA | 2021-07-20 09:23 | 2021-07-20 16:13 | 1036 | 006:50 | T | ESTRUCTURA AVERIADA | SE ABRIO INTERRUPTOR PARA REMPLAZAR POSTE PARTIDO | M21072000036 | New_Event | Defective Pole | Include | Include | Equipment | 410 | 2021-07-20 | 424760 | keep | 0 | Jul | 2021 | 0.2893 | 0.00070561 | Sustained | FALSE | FALSE | Not_TMED_Event | 1036
BARRANQUITAS | 2021-07-20 09:30 | 2021-07-20 12:30 | 20 | 003:00 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | C21072000017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 180 | 2021-07-20 | 3600 | keep | 0 | Jul | 2021 | 0.0024519 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-07-20 09:38 | 2021-07-20 12:14 | 1 | 002:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 10 EN BANCO DE TRANSFORMADOR SE CORRIGIO LINEA CRUZADA | C21072000019 | New_Event | Wire Down | Include | Include | Equipment | 156 | 2021-07-20 | 156 | keep | 0 | Jul | 2021 | 0.00010625 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-07-20 09:40 | 2021-07-20 10:48 | 40 | 001:08 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21071900042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2021-07-20 | 2720 | keep | 0 | Jul | 2021 | 0.0018526 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-07-20 10:00 | 2021-07-20 10:01 | 2106 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO RR/OFF PERMANENTE | R21072000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-20 | 2106 | keep | 0 | Jul | 2021 | 0.0014344 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
BAYAMON | 2021-07-20 10:16 | 2021-07-20 12:00 | 10 | 001:44 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | S21072000075 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 104 | 2021-07-20 | 1040 | keep | 0 | Jul | 2021 | 0.00070834 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-07-20 10:16 | 2021-07-20 11:27 | 12 | 001:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y REPARO SECUNDARIA ROTA POR ARBOL | C21072000021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 71 | 2021-07-20 | 852 | keep | 0 | Jul | 2021 | 0.00058029 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-07-20 10:20 | 2021-07-20 12:30 | 20 | 002:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIO | M21072000042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 130 | 2021-07-20 | 2600 | keep | 0 | Jul | 2021 | 0.0017708 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-07-20 10:23 | 2021-07-20 17:12 | 5000 | 006:49 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO MACHETES AVERIADOS Y SE CERRO POR SCADA LLEVA 1336-09 | S21072000000 | New_Event | Switch Failure | Include | Include | Equipment | 409 | 2021-07-20 | 2045000 | keep | 0 | Jul | 2021 | 1.3928 | 0.0034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 5000
BAYAMON | 2021-07-20 10:24 | 2021-07-20 15:43 | 12 | 005:19 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21072000078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 319 | 2021-07-20 | 3828 | keep | 0 | Jul | 2021 | 0.0026072 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-07-20 10:28 | 2021-07-20 10:29 | 5809 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECERRO | B21072000000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-07-20 | 5809 | keep | 0 | Jul | 2021 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
BAYAMON | 2021-07-20 10:29 | 2021-07-20 14:25 | 60 | 003:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE | B21071900106 | New_Event | Wire Down | Include | Include | Equipment | 236 | 2021-07-20 | 14160 | keep | 0 | Jul | 2021 | 0.0096443 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-07-20 10:29 | 2021-07-21 14:28 | 10 | 027:59 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE PREPARO PROVISIONAL AEREO PARA DAR SERVICIO A T-28 | B21072000087 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 1679 | 2021-07-20 | 16790 | keep | 0 | Jul | 2021 | 0.011436 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-20 10:29 | 2021-07-20 17:18 | 15 | 006:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | B21072000081 | New_Event | Secondary Wire Down | Include | Include | Equipment | 409 | 2021-07-20 | 6135 | keep | 0 | Jul | 2021 | 0.0041785 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-07-20 10:30 | 2021-07-20 11:32 | 1 | 001:02 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | R21072000006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 62 | 2021-07-20 | 62 | keep | 0 | Jul | 2021 | 4.2228e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-07-20 10:32 | 2021-07-20 11:52 | 72 | 001:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 AMP EN CORTE DE LINEA AVE CRUZO LINEAS | P21072000016 | New_Event |  |  | Include | Wildlife | 80 | 2021-07-20 | 5760 | keep | 0 | Jul | 2021 | 0.0039231 | 4.9039e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 72
VEGA BAJA | 2021-07-20 10:35 | 2021-07-20 13:01 | 10 | 002:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21072000082 | New_Event | Secondary Wire Down | Include | Include | Equipment | 146 | 2021-07-20 | 1460 | keep | 0 | Jul | 2021 | 0.0009944 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-07-20 11:00 | 2021-07-20 13:54 | 10 | 002:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | P21072000017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 174 | 2021-07-20 | 1740 | keep | 0 | Jul | 2021 | 0.0011851 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-20 11:00 | 2021-07-20 12:30 | 1 | 001:30 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25KVA X 25 KVA | M21072000059 | New_Event | Service Transformer Failure | Include | Include | Equipment | 90 | 2021-07-20 | 90 | keep | 0 | Jul | 2021 | 6.1299e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-07-20 11:41 | 2021-07-20 11:44 | 4027 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 16800 Y 2200 | B21072000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-20 | 12081 | keep | 0 | Jul | 2021 | 0.0082283 | 0.0027428 | Momentary | FALSE | TRUE | Not_TMED_Event | 4027
VEGA BAJA | 2021-07-20 11:41 | 2021-07-20 11:44 | 2468 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 16800 Y 2200 | B21072000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-20 | 7404 | keep | 0 | Jul | 2021 | 0.0050428 | 0.0016809 | Momentary | FALSE | TRUE | Not_TMED_Event | 2468
VEGA BAJA | 2021-07-20 11:41 | 2021-07-20 11:44 | 1494 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 16800 Y 2200 | B21072000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-20 | 4482 | keep | 0 | Jul | 2021 | 0.0030527 | 0.0010176 | Momentary | FALSE | TRUE | Not_TMED_Event | 1494
VEGA BAJA | 2021-07-20 11:41 | 2021-07-20 11:44 | 2368 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 16800 Y 2200 | B21072000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-20 | 7104 | keep | 0 | Jul | 2021 | 0.0048385 | 0.0016128 | Momentary | FALSE | TRUE | Not_TMED_Event | 2368
VEGA BAJA | 2021-07-20 11:41 | 2021-07-20 11:44 | 538 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 16800 Y 2200 | B21072000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-20 | 1614 | keep | 0 | Jul | 2021 | 0.0010993 | 0.00036643 | Momentary | FALSE | TRUE | Not_TMED_Event | 538
VEGA BAJA | 2021-07-20 11:41 | 2021-07-20 11:44 | 1284 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 16800 Y 2200 | B21072000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-20 | 3852 | keep | 0 | Jul | 2021 | 0.0026236 | 0.00087453 | Momentary | FALSE | TRUE | Not_TMED_Event | 1284
VEGA BAJA | 2021-07-20 11:41 | 2021-07-20 11:44 | 1310 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 16800 Y 2200 | B21072000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-20 | 3930 | keep | 0 | Jul | 2021 | 0.0026767 | 0.00089224 | Momentary | FALSE | TRUE | Not_TMED_Event | 1310
VEGA BAJA | 2021-07-20 11:41 | 2021-07-20 11:44 | 215 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 16800 Y 2200 | B21072000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-20 | 645 | keep | 0 | Jul | 2021 | 0.00043931 | 0.00014644 | Momentary | FALSE | TRUE | Not_TMED_Event | 215
VEGA BAJA | 2021-07-20 11:41 | 2021-07-20 11:44 | 1 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 16800 Y 2200 | B21072000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-20 | 3 | keep | 0 | Jul | 2021 | 2.0433e-06 | 6.811e-07 | Momentary | FALSE | TRUE | Not_TMED_Event | 1
VEGA BAJA | 2021-07-20 11:41 | 2021-07-20 11:44 | 652 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 16800 Y 2200 | B21072000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-20 | 1956 | keep | 0 | Jul | 2021 | 0.0013322 | 0.00044407 | Momentary | FALSE | TRUE | Not_TMED_Event | 652
VEGA BAJA | 2021-07-20 11:41 | 2021-07-20 11:44 | 2704 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 16800 Y 2200 | B21072000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-20 | 8112 | keep | 0 | Jul | 2021 | 0.005525 | 0.0018417 | Momentary | FALSE | TRUE | Not_TMED_Event | 2704
VEGA BAJA | 2021-07-20 11:44 | 2021-07-20 17:33 | 20 | 005:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REALIZO DESGANCHE Y SE REPARO SECUNDARIA | B2107200070 | New_Event | Secondary Wire Down | Include | Include | Equipment | 349 | 2021-07-20 | 6980 | keep | 0 | Jul | 2021 | 0.004754 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-07-20 11:55 | 2021-07-20 13:24 | 1 | 001:29 | P | NO SE REPORTO CAUSA | 2 X 20 EN TRASFORMADOR | S21071800101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 89 | 2021-07-20 | 89 | keep | 0 | Jul | 2021 | 6.0617e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-07-20 12:00 | 2021-07-20 14:42 | 10 | 002:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN TRANSFORMADOR | M21072000074 | New_Event | Cutout Failure | Include | Include | Equipment | 162 | 2021-07-20 | 1620 | keep | 0 | Jul | 2021 | 0.0011034 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-20 12:03 | 2021-07-20 13:30 | 50 | 001:27 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR SE RETIRO ENREDADERAS | M21072000068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2021-07-20 | 4350 | keep | 0 | Jul | 2021 | 0.0029628 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-07-20 12:13 | 2021-07-21 13:54 | 18 | 025:41 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO | C21072000024 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1541 | 2021-07-20 | 27738 | keep | 0 | Jul | 2021 | 0.018892 | 1.226e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 18
BAYAMON | 2021-07-20 12:23 | 2021-07-20 12:24 | 748 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21072000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-20 | 748 | keep | 0 | Jul | 2021 | 0.00050946 | 0.00050946 | Momentary | FALSE | FALSE | Not_TMED_Event | 748
BAYAMON | 2021-07-20 12:25 | 2021-07-20 14:56 | 40 | 002:31 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO AISLACION | B21072000113 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 151 | 2021-07-20 | 6040 | keep | 0 | Jul | 2021 | 0.0041138 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-07-20 12:26 | 2021-07-20 15:15 | 50 | 002:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | A21072000054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2021-07-20 | 8450 | keep | 0 | Jul | 2021 | 0.0057553 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-20 12:32 | 2021-07-20 13:12 | 1253 | 000:40 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO SE CERRO INTERRUPTOR | M21072000072 | New_Event | Wire Down | Include | Include | Equipment | 40 | 2021-07-20 | 50120 | keep | 0 | Jul | 2021 | 0.034137 | 0.00085341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1253
AGUADILLA | 2021-07-20 12:40 | 2021-07-20 15:40 | 40 | 003:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | M21072000073 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 180 | 2021-07-20 | 7200 | keep | 0 | Jul | 2021 | 0.0049039 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-20 12:48 | 2021-07-20 14:40 | 12 | 001:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y PUENTE DE LINEA A TRANSFORMADOR | B21071900064 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 112 | 2021-07-20 | 1344 | keep | 0 | Jul | 2021 | 0.00091539 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
GUAYAMA | 2021-07-20 13:00 | 2021-07-20 13:14 | 922 | 000:14 | T | FUEGO | SE ABRE INTERRUPTOR DE EMERGENCIA POSTE EN FUEGO | P21082000027 | New_Event | Fire | Include | Include | Public | 14 | 2021-07-20 | 12908 | keep | 0 | Jul | 2021 | 0.0087916 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2021-07-20 13:00 | 2021-07-20 13:14 | 2844 | 000:14 | T | FUEGO | SE ABRE INTERRUPTOR DE EMERGENCIA POSTE EN FUEGO | P21072000027 | New_Event | Fire | Include | Include | Public | 14 | 2021-07-20 | 39816 | keep | 0 | Jul | 2021 | 0.027118 | 0.001937 | Sustained | FALSE | FALSE | Not_TMED_Event | 2844
MAYAGÃœEZ | 2021-07-20 13:00 | 2021-07-20 17:15 | 50 | 004:15 | P | LINEA DE TRANSMISION 38KV | SE ABRIO CORTE DE LINEA PARA REMPLAZO DE TORRE DE LINEA 1200 | M21072000082 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 255 | 2021-07-20 | 12750 | keep | 0 | Jul | 2021 | 0.008684 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-20 13:05 | 2021-07-20 13:56 | 10 | 000:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | C21072000028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 51 | 2021-07-20 | 510 | keep | 0 | Jul | 2021 | 0.00034736 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-07-20 13:10 | 2021-07-20 16:04 | 21 | 002:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR REEMPLAZO CAJA DE TRANSFORMADOR AVERIADA | C21072000019 | New_Event | Cutout Failure | Include | Include | Equipment | 174 | 2021-07-20 | 3654 | keep | 0 | Jul | 2021 | 0.0024887 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
ARECIBO | 2021-07-20 13:11 | 2021-07-22 10:36 | 8 | 045:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA EN TRANSFORMADOR | A21072000055 | New_Event | Cutout Failure | Include | Include | Equipment | 2725 | 2021-07-20 | 21800 | keep | 0 | Jul | 2021 | 0.014848 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2021-07-20 13:14 | 2021-07-20 15:15 | 140 | 002:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN CORTE DE LINEA POR IMPACTO DE CAMION A POSTE. RELACIONADO AL EVENTO DEL FEEDER | P21072000030 | New_Event |  |  | Include | Wildlife | 121 | 2021-07-20 | 16940 | keep | 0 | Jul | 2021 | 0.011538 | 9.5353e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 140
SAN JUAN | 2021-07-20 13:21 | 2021-07-20 13:22 | 1447 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1112-04 Y SE CERRO POR SCADA LLEVA 1419-09 | S21072000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-20 | 1447 | keep | 0 | Jul | 2021 | 0.00098555 | 0.00098555 | Momentary | FALSE | FALSE | Not_TMED_Event | 1447
SAN JUAN | 2021-07-20 13:21 | 2021-07-20 13:22 | 266 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1112-04 Y SE CERRO POR SCADA LLEVA 1419-09 | S21072000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-20 | 266 | keep | 0 | Jul | 2021 | 0.00018117 | 0.00018117 | Momentary | FALSE | FALSE | Not_TMED_Event | 266
ARECIBO | 2021-07-20 13:25 | 2021-07-20 19:50 | 300 | 006:25 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | A21072000057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 385 | 2021-07-20 | 115500 | keep | 0 | Jul | 2021 | 0.078667 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
PONCE | 2021-07-20 13:34 | 2021-07-20 17:23 | 42 | 003:49 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA A 4160 X LO MISMO | P21072000031 | New_Event | Service Transformer Failure | Include | Include | Equipment | 229 | 2021-07-20 | 9618 | keep | 0 | Jul | 2021 | 0.0065508 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
MAYAGÃœEZ | 2021-07-20 13:44 | 2021-07-20 16:15 | 70 | 002:31 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M21072000085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2021-07-20 | 10570 | keep | 0 | Jul | 2021 | 0.0071992 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
UTUADO | 2021-07-20 13:48 | 2021-07-20 17:10 | 6 | 003:22 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | A21072000059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2021-07-20 | 1212 | keep | 0 | Jul | 2021 | 0.00082549 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-07-20 14:00 | 2021-07-20 15:00 | 75 | 001:00 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21072000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2021-07-20 | 4500 | keep | 0 | Jul | 2021 | 0.0030649 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
VEGA BAJA | 2021-07-20 14:00 | 2021-07-20 14:53 | 7 | 000:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B21072000127 | New_Event | Secondary Wire Down | Include | Include | Equipment | 53 | 2021-07-20 | 371 | keep | 0 | Jul | 2021 | 0.00025269 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-07-20 14:07 | 2021-07-20 14:08 | 176 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21072000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-20 | 176 | keep | 0 | Jul | 2021 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2021-07-20 14:30 | 2021-07-20 15:30 | 30 | 001:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN TRANSFORMADOR | M21072000000 | New_Event | Cutout Failure | Include | Include | Equipment | 60 | 2021-07-20 | 1800 | keep | 0 | Jul | 2021 | 0.001226 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-07-20 14:36 | 2021-07-21 10:28 | 20 | 019:52 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21072000367 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1192 | 2021-07-20 | 23840 | keep | 0 | Jul | 2021 | 0.016237 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CANOVANAS | 2021-07-20 14:38 | 2021-07-20 17:04 | 12 | 002:26 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR REEMPLAZO SECUNDARIA AVERIADA Y POSTE SECUNDARIO | R21071900017 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 146 | 2021-07-20 | 1752 | keep | 0 | Jul | 2021 | 0.0011933 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-07-20 14:40 | 2021-07-20 18:11 | 7 | 003:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BAJANTE SECUNDARIO DE TRANSFORMADOR | C21072000035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 211 | 2021-07-20 | 1477 | keep | 0 | Jul | 2021 | 0.001006 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2021-07-20 14:43 | 2021-07-20 17:30 | 10 | 002:47 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA DESGANCHE | A21072000066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2021-07-20 | 1670 | keep | 0 | Jul | 2021 | 0.0011374 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
SAN JUAN | 2021-07-20 14:47 | 2021-07-20 14:50 | 5620 | 000:03 | P | DESGANCHE | DISPARO DE INTERRUPTOR 90% DE LA CARGA POR EL 1620-04 | S21072000376 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-07-20 | 16860 | keep | 0 | Jul | 2021 | 0.011483 | 0.0038278 | Momentary | FALSE | FALSE | Not_TMED_Event | 5620
SAN JUAN | 2021-07-20 14:47 | 2021-07-20 14:50 | 345 | 000:03 | P | DESGANCHE | DISPARO DE INTERRUPTOR 85% DE LA CARGA POR EL 1620-04 | S21072000376 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-07-20 | 1035 | keep | 0 | Jul | 2021 | 0.00070493 | 0.00023498 | Momentary | FALSE | FALSE | Not_TMED_Event | 345
SAN JUAN | 2021-07-20 14:47 | 2021-07-20 14:50 | 36 | 000:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR CARGA POR EL 1620-04 | S21072000376 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-07-20 | 108 | keep | 0 | Jul | 2021 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-07-20 14:47 | 2021-07-20 14:50 | 172 | 000:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA LLEVA EL 1620-01 Y EL 85% DEL 1336-10 Y EL 90% DEL 1336-07 | S21072000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-07-20 | 516 | keep | 0 | Jul | 2021 | 0.00035145 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2021-07-20 14:50 | 2021-07-20 14:52 | 135 | 000:02 | P | DESGANCHE | SE SECCIONALIZO EL 5% DEL ALIMENTADOR Y SE CERRO POR SCADA LLEVA EL 1620-01 Y EL 85% DEL 1336-10 Y EL 90% DEL 1336-07 | S21072000000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-07-20 | 270 | keep | 0 | Jul | 2021 | 0.0001839 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
VEGA BAJA | 2021-07-20 14:50 | 2021-07-20 16:51 | 9 | 002:01 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 50 KVA X 50 KVA CON DERRAME DE ACEITE | B21071900026 | New_Event | Service Transformer Failure | Include | Include | Equipment | 121 | 2021-07-20 | 1089 | keep | 0 | Jul | 2021 | 0.00074171 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2021-07-20 14:52 | 2021-07-20 16:12 | 5620 | 001:20 | P | DESGANCHE | DISPARO DE INTERRUPTOR 90% DE LA CARGA POR EL 1620-04 | S21072000376 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 80 | 2021-07-20 | 449600 | keep | 0 | Jul | 2021 | 0.30622 | 0.0038278 | Sustained | FALSE | FALSE | Not_TMED_Event | 5620
SAN JUAN | 2021-07-20 14:52 | 2021-07-20 16:12 | 345 | 001:20 | P | DESGANCHE | DISPARO DE INTERRUPTOR 85% DE LA CARGA POR EL 1620-04 | S21072000376 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 80 | 2021-07-20 | 27600 | keep | 0 | Jul | 2021 | 0.018798 | 0.00023498 | Sustained | FALSE | FALSE | Not_TMED_Event | 345
SAN JUAN | 2021-07-20 14:52 | 2021-07-20 16:12 | 36 | 001:20 | T | DESGANCHE | DISPARO DE INTERRUPTOR CARGA POR EL 1620-04 | S21072000376 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 80 | 2021-07-20 | 2880 | keep | 0 | Jul | 2021 | 0.0019616 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-07-20 14:52 | 2021-07-20 16:12 | 172 | 001:20 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO EL 5% DEL ALIMENTADOR Y SE CERRO POR SCADA LLEVA EL 1620-01 Y EL 85% DEL 1336-10 Y EL 90% DEL 1336-07 | S21072000000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 80 | 2021-07-20 | 13760 | keep | 0 | Jul | 2021 | 0.0093719 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
MAYAGÃœEZ | 2021-07-20 15:21 | 2021-07-20 17:10 | 40 | 001:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21072000099 | New_Event | Bad Weather | Include | Include | Weather | 109 | 2021-07-20 | 4360 | keep | 0 | Jul | 2021 | 0.0029696 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-20 15:42 | 2021-07-20 20:27 | 40 | 004:45 | P | NO SE REPORTO CAUSA | 1 X 30 EN PROVISIONAL | B21072000152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 285 | 2021-07-20 | 11400 | keep | 0 | Jul | 2021 | 0.0077645 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2021-07-20 15:44 | 2021-07-20 15:45 | 2379 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21072000043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-20 | 2379 | keep | 0 | Jul | 2021 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
ARECIBO | 2021-07-20 16:08 | 2021-07-20 19:50 | 100 | 003:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | A21072000076 | New_Event | Wire Down | Include | Include | Equipment | 222 | 2021-07-20 | 22200 | keep | 0 | Jul | 2021 | 0.01512 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-07-20 16:10 | 2021-07-20 17:06 | 35 | 000:56 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO CORTE DE LINEA PARA REEMPLAZAR AISLADOR ROTO | R21072000014 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 56 | 2021-07-20 | 1960 | keep | 0 | Jul | 2021 | 0.0013349 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
VEGA BAJA | 2021-07-20 16:10 | 2021-07-20 17:06 | 8 | 000:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA REPARANDO SECUNDARIA | B21072000000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 56 | 2021-07-20 | 448 | keep | 0 | Jul | 2021 | 0.00030513 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-07-20 16:12 | 2021-07-20 16:14 | 135 | 000:02 | P | DESGANCHE | SE SECCIONALIZO EL 5% DEL ALIMENTADOR Y SE CERRO POR SCADA LLEVA EL 1620-01 Y EL 85% DEL 1336-10 Y EL 90% DEL 1336-07 | S21072000000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-07-20 | 270 | keep | 0 | Jul | 2021 | 0.0001839 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-07-20 16:13 | 2021-07-21 13:20 | 1415 | 021:07 | T | DESCONECTIVO DEFECTUOSO | MACHETES DE AMARRE QUEMADOS | M21072000036 | New_Event | Switch Failure | Include | Include | Equipment | 1267 | 2021-07-20 | 1792805 | keep | 0 | Jul | 2021 | 1.2211 | 0.00096375 | Sustained | FALSE | FALSE | Not_TMED_Event | 1415
AGUADILLA | 2021-07-20 16:13 | 2021-07-21 11:43 | 1036 | 019:30 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA REEMPLAZAR MACHETES DE AMARRE QUEMADOS | M21072100072 | New_Event | Switch Failure | Include | Include | Equipment | 1170 | 2021-07-20 | 1212120 | keep | 0 | Jul | 2021 | 0.82557 | 0.00070561 | Sustained | FALSE | FALSE | Not_TMED_Event | 1036
SAN JUAN | 2021-07-20 16:14 | 2021-07-20 18:25 | 36 | 002:11 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO EL 5% DEL ALIMENTADOR Y SE CERRO POR SCADA LLEVA EL 1620-01 Y EL 85% DEL 1336-10 Y EL 90% DEL 1336-07 | S21072000376 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 131 | 2021-07-20 | 4716 | keep | 0 | Jul | 2021 | 0.003212 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-20 16:14 | 2021-07-20 17:52 | 172 | 001:38 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO EL 5% DEL ALIMENTADOR Y SE CERRO POR SCADA LLEVA EL 1620-01 Y EL 85% DEL 1336-10 Y EL 90% DEL 1336-07 | S21072000000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 98 | 2021-07-20 | 16856 | keep | 0 | Jul | 2021 | 0.011481 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
CAGUAS | 2021-07-20 16:28 | 2021-07-21 13:22 | 12 | 020:54 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR ROTO Y LEVANTARON CONDUCTOR PRIMARIO SE CERRO PUENTE | C21072000043 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1254 | 2021-07-20 | 15048 | keep | 0 | Jul | 2021 | 0.010249 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-07-20 16:39 | 2021-07-21 11:58 | 165 | 019:19 | P | AISLADOR ROTO, PARTIDO O SAFADO | 3 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE REEMPLAZO PIN POLE TOP | C21072000044 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1159 | 2021-07-20 | 191235 | keep | 0 | Jul | 2021 | 0.13025 | 0.00011238 | Sustained | FALSE | TRUE | Not_TMED_Event | 165
YAUCO | 2021-07-20 16:40 | 2021-07-20 17:21 | 20 | 000:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | P21072000026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 41 | 2021-07-20 | 820 | keep | 0 | Jul | 2021 | 0.0005585 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-07-20 16:42 | 2021-07-21 10:22 | 100 | 017:40 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR | B21072000165 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1060 | 2021-07-20 | 106000 | keep | 0 | Jul | 2021 | 0.072196 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-20 16:54 | 2021-07-20 16:55 | 2782 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTROR Y SE CERRO POR SCADA | S21072000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-20 | 2782 | keep | 0 | Jul | 2021 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
BARRANQUITAS | 2021-07-20 17:07 | 2021-07-20 19:11 | 55 | 002:04 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C21072000046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 124 | 2021-07-20 | 6820 | keep | 0 | Jul | 2021 | 0.0046451 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
SAN JUAN | 2021-07-20 17:12 | 2021-07-20 17:13 | 5290 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO Y SE CERRO POR SCADA LLEVANDO LA CARGA DEL 1336-09 | S21072000000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-20 | 5290 | keep | 0 | Jul | 2021 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2021-07-20 17:12 | 2021-07-20 17:13 | 207 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO CARGA POR EL 1336-08 | S21072000000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2021-07-20 | 207 | keep | 0 | Jul | 2021 | 0.00014099 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2021-07-20 17:13 | 2021-07-20 18:19 | 1750 | 001:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO | S21072000000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 66 | 2021-07-20 | 115500 | keep | 0 | Jul | 2021 | 0.078667 | 0.0011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 1750
FAJARDO | 2021-07-20 17:49 | 2021-07-20 19:36 | 55 | 001:47 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21072000021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 107 | 2021-07-20 | 5885 | keep | 0 | Jul | 2021 | 0.0040082 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
SAN JUAN | 2021-07-20 17:52 | 2021-07-20 18:43 | 135 | 000:51 | P | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO EL 5% DEL ALIMENTADOR Y SE CERRO POR SCADA LLEVA EL 1620-01 Y EL 85% DEL 1336-10 Y EL 90% DEL 1336-07 | S21072000376 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 51 | 2021-07-20 | 6885 | keep | 0 | Jul | 2021 | 0.0046893 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-07-20 18:10 | 2021-07-21 08:42 | 8 | 014:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO | C21072000049 | New_Event | Bad Weather | Include | Include | Weather | 872 | 2021-07-20 | 6976 | keep | 0 | Jul | 2021 | 0.0047513 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-07-20 18:19 | 2021-07-20 19:45 | 5290 | 001:26 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE LLEVANDO LA CARGA DEL 1336-09 | S21072000000 | Additional_clients | Wire Down | Include | Include | Equipment | 86 | 2021-07-20 | 454940 | keep | 0 | Jul | 2021 | 0.30986 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-20 18:19 | 2021-07-20 19:45 | 207 | 001:26 | T | DESCONECTIVO DEFECTUOSO | DISPARO CARGA POR EL 1336-08 | S21072000000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 86 | 2021-07-20 | 17802 | keep | 0 | Jul | 2021 | 0.012125 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2021-07-20 18:25 | 2021-07-20 21:09 | 345 | 002:44 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE NORMALIZO LA CARGA | S21072000376 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 164 | 2021-07-20 | 56580 | keep | 0 | Jul | 2021 | 0.038536 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-20 18:43 | 2021-07-20 21:09 | 5620 | 002:26 | P | DESGANCHE | SE REALIZE DESGANCHE Y SE NORMALIZO LAS CARGAS | S21072000376 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 146 | 2021-07-20 | 820520 | keep | 0 | Jul | 2021 | 0.55885 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-20 18:43 | 2021-07-20 21:09 | 36 | 002:26 | T | DESGANCHE | SE REALIZO DESGANCHE Y SE NORMALIZO LAS CARGAS | S21072000000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 146 | 2021-07-20 | 5256 | keep | 0 | Jul | 2021 | 0.0035798 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-20 18:43 | 2021-07-20 18:44 | 172 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO EL 5% DEL ALIMENTADOR Y SE CERRO POR SCADA LLEVA EL 1620-01 Y EL 85% DEL 1336-10 Y EL 90% DEL 1336-07 | S21072000000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-20 | 172 | keep | 0 | Jul | 2021 | 0.00011715 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-07-20 18:43 | 2021-07-20 19:57 | 100 | 001:14 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | B21072000175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2021-07-20 | 7400 | keep | 0 | Jul | 2021 | 0.0050401 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-20 18:44 | 2021-07-20 18:47 | 135 | 000:03 | P | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO EL 5% DEL ALIMENTADOR Y SE CERRO POR SCADA LLEVA EL 1620-01 Y EL 85% DEL 1336-10 Y EL 90% DEL 1336-07 | S21072000376 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-07-20 | 405 | keep | 0 | Jul | 2021 | 0.00027584 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2021-07-20 18:47 | 2021-07-20 18:50 | 172 | 000:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO EL 5% DEL ALIMENTADOR Y SE CERRO POR SCADA LLEVA EL 1620-01 Y EL 85% DEL 1336-10 Y EL 90% DEL 1336-07 | S21072000000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-07-20 | 516 | keep | 0 | Jul | 2021 | 0.00035145 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2021-07-20 18:50 | 2021-07-20 18:51 | 135 | 000:01 | P | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO EL 5% DEL ALIMENTADOR Y SE CERRO POR SCADA LLEVA EL 1620-01 Y EL 85% DEL 1336-10 Y EL 90% DEL 1336-07 | S21072000376 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-20 | 135 | keep | 0 | Jul | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2021-07-20 18:51 | 2021-07-20 19:23 | 172 | 000:32 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO EL 5% DEL ALIMENTADOR Y SE CERRO POR SCADA LLEVA EL 1620-01 Y EL 85% DEL 1336-10 Y EL 90% DEL 1336-07 | S21072000000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 32 | 2021-07-20 | 5504 | keep | 0 | Jul | 2021 | 0.0037487 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
CAGUAS | 2021-07-20 19:06 | 2021-07-20 20:02 | 9 | 000:56 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR AVERIADO DE 25KVA X 25KVA | C21072000050 | New_Event | Service Transformer Failure | Include | Include | Equipment | 56 | 2021-07-20 | 504 | keep | 0 | Jul | 2021 | 0.00034327 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2021-07-20 19:14 | 2021-07-21 14:15 | 3 | 019:01 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21072000178 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1141 | 2021-07-20 | 3423 | keep | 0 | Jul | 2021 | 0.0023314 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-07-20 19:18 | 2021-07-20 19:19 | 331 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO | R21072000026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-20 | 331 | keep | 0 | Jul | 2021 | 0.00022544 | 0.00022544 | Momentary | FALSE | FALSE | Not_TMED_Event | 331
SAN JUAN | 2021-07-20 19:23 | 2021-07-20 19:25 | 135 | 000:02 | P | DESGANCHE | SE SECCIONALIZO EL 5% DEL ALIMENTADOR Y SE CERRO POR SCADA LLEVA EL 1620-01 Y EL 85% DEL 1336-10 Y EL 90% DEL 1336-07 | S21072000000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-07-20 | 270 | keep | 0 | Jul | 2021 | 0.0001839 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-07-20 19:24 | 2021-07-21 08:36 | 40 | 013:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | R21072000027 | New_Event |  |  | Include | Wildlife | 792 | 2021-07-20 | 31680 | keep | 0 | Jul | 2021 | 0.021577 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-07-20 19:25 | 2021-07-20 20:11 | 172 | 000:46 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO EL 5% DEL ALIMENTADOR Y SE CERRO POR SCADA LLEVA EL 1620-01 Y EL 85% DEL 1336-10 Y EL 90% DEL 1336-07 | S21072000000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 46 | 2021-07-20 | 7912 | keep | 0 | Jul | 2021 | 0.0053888 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
FAJARDO | 2021-07-20 19:27 | 2021-07-21 11:57 | 40 | 016:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA QUEMADA NO FUNDIO | R21072000028 | New_Event | Cutout Failure | Include | Include | Equipment | 990 | 2021-07-20 | 39600 | keep | 0 | Jul | 2021 | 0.026971 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2021-07-20 19:28 | 2021-07-21 11:20 | 880 | 015:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE CERRO PUENTE DE LINEA A LINEA | C21072000052 | New_Event | Wire Down | Include | Include | Equipment | 952 | 2021-07-20 | 837760 | keep | 0 | Jul | 2021 | 0.57059 | 0.00059936 | Sustained | FALSE | TRUE | Not_TMED_Event | 880
MAYAGÃœEZ | 2021-07-20 20:00 | 2021-07-21 08:15 | 3087 | 012:15 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO AVERIA DE LINEA PARTIDA Y SE CERRO INTERRUPTOR | M21072000122 | New_Event | Wire Down | Include | Include | Equipment | 735 | 2021-07-20 | 2268945 | keep | 0 | Jul | 2021 | 1.5454 | 0.0021025 | Sustained | FALSE | TRUE | Not_TMED_Event | 3087
MAYAGÃœEZ | 2021-07-20 20:00 | 2021-07-21 10:01 | 9 | 014:01 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR | M21072000122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 841 | 2021-07-20 | 7569 | keep | 0 | Jul | 2021 | 0.0051552 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2021-07-20 20:11 | 2021-07-21 09:50 | 100 | 013:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA Y VIENTO | A21072000092 | New_Event | Bad Weather | Include | Include | Weather | 819 | 2021-07-20 | 81900 | keep | 0 | Jul | 2021 | 0.055782 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-07-20 21:30 | 2021-07-21 13:03 | 220 | 015:33 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE DESGANCHO ENREDADERA | C21072000062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 933 | 2021-07-20 | 205260 | keep | 0 | Jul | 2021 | 0.1398 | 0.00014984 | Sustained | FALSE | TRUE | Not_TMED_Event | 220
BAYAMON | 2021-07-20 22:17 | 2021-07-22 19:28 | 12 | 045:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | C21072000065 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2711 | 2021-07-20 | 32532 | keep | 0 | Jul | 2021 | 0.022157 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-07-20 22:41 | 2021-07-21 09:32 | 55 | 010:51 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21072000038 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 651 | 2021-07-20 | 35805 | keep | 0 | Jul | 2021 | 0.024387 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-07-20 23:58 | 2021-07-22 11:18 | 20 | 035:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21072000650 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2120 | 2021-07-20 | 42400 | keep | 0 | Jul | 2021 | 0.028878 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-07-21 00:17 | 2021-07-21 13:33 | 8 | 013:16 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR PROBO MALO SE TRANSFIRIO LA CARGA A TRANSFORMADOR CERCANO | C21072100001 | New_Event | Service Transformer Failure | Include | Include | Equipment | 796 | 2021-07-21 | 6368 | keep | 0 | Jul | 2021 | 0.0043372 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-07-21 00:45 | 2021-07-24 13:00 | 35 | 084:15 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21072100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5055 | 2021-07-21 | 176925 | keep | 0 | Jul | 2021 | 0.1205 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
CAGUAS | 2021-07-21 03:41 | 2021-07-21 10:12 | 5 | 006:31 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO BAMBUA DE LA LINEA | C21072100004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 391 | 2021-07-21 | 1955 | keep | 0 | Jul | 2021 | 0.0013315 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
VEGA BAJA | 2021-07-21 03:55 | 2021-07-21 10:29 | 200 | 006:34 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | B21072100005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 394 | 2021-07-21 | 78800 | keep | 0 | Jul | 2021 | 0.05367 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-07-21 04:07 | 2021-07-21 12:00 | 350 | 007:53 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 140 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS SE RETEZO LINEA PRIMARIA Y SE REALIZO DESGANCHE | A21072100014 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 473 | 2021-07-21 | 165550 | keep | 0 | Jul | 2021 | 0.11276 | 0.00023838 | Sustained | FALSE | TRUE | Not_TMED_Event | 350
BARRANQUITAS | 2021-07-21 04:55 | 2021-07-21 04:56 | 2410 | 000:01 | T | DESGANCHE | RECIERRE | C21072100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-21 | 2410 | keep | 0 | Jul | 2021 | 0.0016414 | 0.0016414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2410
BARRANQUITAS | 2021-07-21 04:56 | 2021-07-21 14:00 | 10 | 009:04 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21072100006 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 544 | 2021-07-21 | 5440 | keep | 0 | Jul | 2021 | 0.0037052 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CANOVANAS | 2021-07-21 06:02 | 2021-07-21 10:12 | 1 | 004:10 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA Y 1 X 20 SMU 20 EN SU - 1 | R21072100004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 250 | 2021-07-21 | 250 | keep | 0 | Jul | 2021 | 0.00017027 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-07-21 06:17 | 2021-07-22 13:16 | 50 | 030:59 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | A21072100100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1859 | 2021-07-21 | 92950 | keep | 0 | Jul | 2021 | 0.063308 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-21 06:20 | 2021-07-21 10:44 | 40 | 004:24 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | S21072100008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 264 | 2021-07-21 | 10560 | keep | 0 | Jul | 2021 | 0.0071924 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-21 06:32 | 2021-07-21 15:05 | 200 | 008:33 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | S21072100009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 513 | 2021-07-21 | 102600 | keep | 0 | Jul | 2021 | 0.06988 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
PONCE | 2021-07-21 06:46 | 2021-07-21 10:25 | 149 | 003:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO DE CAJA PRIMARIA QUEMADA | P21072100001 | New_Event | Cutout Failure | Include | Include | Equipment | 219 | 2021-07-21 | 32631 | keep | 0 | Jul | 2021 | 0.022225 | 0.00010148 | Sustained | FALSE | FALSE | Not_TMED_Event | 149
MAYAGÃœEZ | 2021-07-21 07:00 | 2021-07-21 10:15 | 50 | 003:15 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | M21072100009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2021-07-21 | 9750 | keep | 0 | Jul | 2021 | 0.0066407 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-07-21 07:25 | 2021-07-21 17:10 | 50 | 009:45 | P | HERRAJE ROTO O PODRIDO | 2 X 40 EN CORTE DE LINEA SE REMPLAZO CRUCETAS | A21072100022 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 585 | 2021-07-21 | 29250 | keep | 0 | Jul | 2021 | 0.019922 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-07-21 07:29 | 2021-07-21 13:52 | 75 | 006:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A21072100017 | New_Event |  |  | Include | Wildlife | 383 | 2021-07-21 | 28725 | keep | 0 | Jul | 2021 | 0.019564 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
MAYAGÃœEZ | 2021-07-21 07:49 | 2021-07-21 13:00 | 15 | 005:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA AVE CRUZO LINEA | M21072100043 | New_Event |  |  | Include | Wildlife | 311 | 2021-07-21 | 4665 | keep | 0 | Jul | 2021 | 0.0031773 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-07-21 07:50 | 2021-07-21 09:27 | 1 | 001:37 | P | DESGANCHE | 2 X 10 EN CORTE DE LINEA | M21072100014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2021-07-21 | 97 | keep | 0 | Jul | 2021 | 6.6066e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
GUAYAMA | 2021-07-21 08:00 | 2021-07-21 18:30 | 35 | 010:30 | P | ESTRUCTURA AVERIADA | SE ABRE CORTE DE LINEA PARA REMPLAZO DE POSTE PRIMARIO | P210721000XX | New_Event | Defective Pole | Include | Include | Equipment | 630 | 2021-07-21 | 22050 | keep | 0 | Jul | 2021 | 0.015018 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-07-21 08:15 | 2021-07-21 10:50 | 300 | 002:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES Y SE CERRO INTERRUPTOR | M21072000122 | New_Event | Wire Down | Include | Include | Equipment | 155 | 2021-07-21 | 46500 | keep | 0 | Jul | 2021 | 0.031671 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-07-21 08:24 | 2021-07-22 21:35 | 9 | 037:11 | P | ESTRUCTURA AVERIADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO | M21072100024 | New_Event | Defective Pole | Include | Include | Equipment | 2231 | 2021-07-21 | 20079 | keep | 0 | Jul | 2021 | 0.013676 | 6.1299e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 9
CAGUAS | 2021-07-21 08:40 | 2021-07-21 15:27 | 43 | 006:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C21072100011 | New_Event |  |  | Include | Wildlife | 407 | 2021-07-21 | 17501 | keep | 0 | Jul | 2021 | 0.01192 | 2.9287e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 43
SAN JUAN | 2021-07-21 08:59 | 2021-07-21 20:47 | 50 | 011:48 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21072100024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 708 | 2021-07-21 | 35400 | keep | 0 | Jul | 2021 | 0.024111 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-07-21 09:07 | 2021-07-21 11:00 | 1 | 001:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA AVERIADA | R21072100016 | New_Event | Cutout Failure | Include | Include | Equipment | 113 | 2021-07-21 | 113 | keep | 0 | Jul | 2021 | 7.6964e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-07-21 09:16 | 2021-07-21 14:36 | 1 | 005:20 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R21072100015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 320 | 2021-07-21 | 320 | keep | 0 | Jul | 2021 | 0.00021795 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-07-21 09:24 | 2021-07-21 16:58 | 33 | 007:34 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA BAMBUA SOBRE LINEA | C21072100018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 454 | 2021-07-21 | 14982 | keep | 0 | Jul | 2021 | 0.010204 | 2.2476e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 33
CAGUAS | 2021-07-21 09:33 | 2021-07-21 09:49 | 11 | 000:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA DESGANCHAR Y REPARAR SECUNDARIA | C21072000048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 16 | 2021-07-21 | 176 | keep | 0 | Jul | 2021 | 0.00011987 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
HUMACAO | 2021-07-21 09:34 | 2021-07-21 14:42 | 12 | 005:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | C21072100020 | New_Event |  |  | Include | Wildlife | 308 | 2021-07-21 | 3696 | keep | 0 | Jul | 2021 | 0.0025173 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2021-07-21 09:39 | 2021-07-21 16:00 | 30 | 006:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | A21072100031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 381 | 2021-07-21 | 11430 | keep | 0 | Jul | 2021 | 0.0077849 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-07-21 09:42 | 2021-07-21 14:00 | 4 | 004:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR PEDESTAL | R21072100018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 258 | 2021-07-21 | 1032 | keep | 0 | Jul | 2021 | 0.00070289 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-07-21 09:51 | 2021-07-21 13:12 | 10 | 003:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21072100028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 201 | 2021-07-21 | 2010 | keep | 0 | Jul | 2021 | 0.001369 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-07-21 09:51 | 2021-07-21 19:23 | 2 | 009:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21072100023 | New_Event | Bad Weather | Include | Include | Weather | 572 | 2021-07-21 | 1144 | keep | 0 | Jul | 2021 | 0.00077917 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
AGUADILLA | 2021-07-21 10:15 | 2021-07-21 19:00 | 60 | 008:45 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21072100049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 525 | 2021-07-21 | 31500 | keep | 0 | Jul | 2021 | 0.021455 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
VEGA BAJA | 2021-07-21 10:24 | 2021-07-21 12:30 | 8 | 002:06 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE POSTE SECUNDARIO | B21072100039 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 126 | 2021-07-21 | 1008 | keep | 0 | Jul | 2021 | 0.00068654 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-07-21 10:26 | 2021-07-21 14:35 | 64 | 004:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21072100029 | New_Event | Bad Weather | Include | Include | Weather | 249 | 2021-07-21 | 15936 | keep | 0 | Jul | 2021 | 0.010854 | 4.359e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 64
ARECIBO | 2021-07-21 10:31 | 2021-07-21 10:32 | 2697 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21072100036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-21 | 2697 | keep | 0 | Jul | 2021 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
CAGUAS | 2021-07-21 10:42 | 2021-07-21 13:01 | 8 | 002:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZO DE CONECTORES EN BAJANTE SECUNDARIO | C21072000061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 139 | 2021-07-21 | 1112 | keep | 0 | Jul | 2021 | 0.00075738 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-07-21 10:50 | 2021-07-21 10:52 | 3087 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRA MACHETES | M21072000122 | Partial_restoration | Wire Down | Include | Include | Equipment | 2 | 2021-07-21 | 6174 | keep | 0 | Jul | 2021 | 0.0042051 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2021-07-21 11:00 | 2021-07-21 15:50 | 35 | 004:50 | P | ESTRUCTURA AVERIADA | SE ABRE CORTE DE LINEA PARA REMPLAZO DE POSTE PORIMARIO PARTIDO | P21072100020 | New_Event | Defective Pole | Include | Include | Equipment | 290 | 2021-07-21 | 10150 | keep | 0 | Jul | 2021 | 0.0069131 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-07-21 11:03 | 2021-07-21 14:10 | 100 | 003:07 | P | HERRAJE ROTO O PODRIDO | SE ABRIO CORTE DE LINEA AUTORIZADO POR EDWIN COSME PARA REMPLAZAR CRUCETA PODRIDA | A21072100040 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 187 | 2021-07-21 | 18700 | keep | 0 | Jul | 2021 | 0.012736 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-07-21 11:17 | 2021-07-21 15:45 | 161 | 004:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | C21072100035 | New_Event |  |  | Include | Wildlife | 268 | 2021-07-21 | 43148 | keep | 0 | Jul | 2021 | 0.029388 | 0.00010966 | Sustained | FALSE | TRUE | Not_TMED_Event | 161
SAN JUAN | 2021-07-21 11:27 | 2021-07-21 11:28 | 870 | 000:01 | T | DESGANCHE | SE CERRO POR CONTROL | S21072100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-21 | 870 | keep | 0 | Jul | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
HUMACAO | 2021-07-21 11:53 | 2021-07-22 11:56 | 1 | 024:03 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | C21072100039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1443 | 2021-07-21 | 1443 | keep | 0 | Jul | 2021 | 0.00098282 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-07-21 12:01 | 2021-07-21 12:04 | 870 | 000:03 | T | DESGANCHE | SE CERRO POR CONTROL | S21072100000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-07-21 | 2610 | keep | 0 | Jul | 2021 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2021-07-21 12:27 | 2021-07-21 13:57 | 870 | 001:30 | T | DESGANCHE | DISPARO INTERRUPTOR NO RECERRO SE PROBO POR CONTROL A PETICION RANGEL VAZQUEZ QUEDO EN SERVICIO | S21072100000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 90 | 2021-07-21 | 78300 | keep | 0 | Jul | 2021 | 0.05333 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
AGUADILLA | 2021-07-21 12:44 | 2021-07-21 21:35 | 20 | 008:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO PARTIDO | M21072100073 | New_Event | Wire Down | Include | Include | Equipment | 531 | 2021-07-21 | 10620 | keep | 0 | Jul | 2021 | 0.0072332 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2021-07-21 13:03 | 2021-07-21 23:33 | 20 | 010:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | M21072100078 | New_Event | Bad Weather | Include | Include | Weather | 630 | 2021-07-21 | 12600 | keep | 0 | Jul | 2021 | 0.0085818 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BARRANQUITAS | 2021-07-21 13:17 | 2021-07-21 17:42 | 58 | 004:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE INSTALO PIN POLE TOP PARA DER DESPEJO A CONDUCTOR PRIMARIO | C21072100045 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 265 | 2021-07-21 | 15370 | keep | 0 | Jul | 2021 | 0.010468 | 3.9504e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 58
MAYAGÃœEZ | 2021-07-21 13:19 | 2021-07-21 16:00 | 10 | 002:41 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA X 37.5 KVA | M21072100082 | New_Event | Service Transformer Failure | Include | Include | Equipment | 161 | 2021-07-21 | 1610 | keep | 0 | Jul | 2021 | 0.0010966 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-21 13:24 | 2021-07-22 10:20 | 80 | 020:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21072100083 | New_Event | Bad Weather | Include | Include | Weather | 1256 | 2021-07-21 | 100480 | keep | 0 | Jul | 2021 | 0.068436 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-07-21 13:48 | 2021-07-21 16:24 | 60 | 002:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 Y 1 X 50 EN CORTE DE LINEA DIFERENTES LINEAS CRUZADAS | B21072100053 | New_Event | Wire Down | Include | Include | Equipment | 156 | 2021-07-21 | 9360 | keep | 0 | Jul | 2021 | 0.0063751 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-07-21 14:01 | 2021-07-21 16:39 | 67 | 002:38 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | C21072100053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2021-07-21 | 10586 | keep | 0 | Jul | 2021 | 0.0072101 | 4.5633e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 67
CANOVANAS | 2021-07-21 14:04 | 2021-07-21 16:32 | 1 | 002:28 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21072100030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2021-07-21 | 148 | keep | 0 | Jul | 2021 | 0.0001008 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-07-21 14:07 | 2021-07-21 19:27 | 80 | 005:20 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S21072100065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 320 | 2021-07-21 | 25600 | keep | 0 | Jul | 2021 | 0.017436 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BARRANQUITAS | 2021-07-21 14:08 | 2021-07-21 16:48 | 3 | 002:40 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO AISLADOR ROTO | C21072100055 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 160 | 2021-07-21 | 480 | keep | 0 | Jul | 2021 | 0.00032693 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
SAN JUAN | 2021-07-21 14:10 | 2021-07-21 21:21 | 118 | 007:11 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21072100066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 431 | 2021-07-21 | 50858 | keep | 0 | Jul | 2021 | 0.034639 | 8.0369e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 118
CAGUAS | 2021-07-21 14:18 | 2021-07-21 21:32 | 574 | 007:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE DESGANCHO Y LEVANTARON CONDUCTOR SE CERRO CORTE DE LINEA | C21072100059 | New_Event | Wire Down | Include | Include | Equipment | 434 | 2021-07-21 | 249116 | keep | 0 | Jul | 2021 | 0.16967 | 0.00039095 | Sustained | FALSE | TRUE | Not_TMED_Event | 574
MAYAGÃœEZ | 2021-07-21 14:24 | 2021-07-21 17:15 | 6 | 002:51 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | M21072100103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2021-07-21 | 1026 | keep | 0 | Jul | 2021 | 0.0006988 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-07-21 14:24 | 2021-07-21 17:30 | 65 | 003:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21072100106 | New_Event | Bad Weather | Include | Include | Weather | 186 | 2021-07-21 | 12090 | keep | 0 | Jul | 2021 | 0.0082344 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
MAYAGÃœEZ | 2021-07-21 14:27 | 2021-07-21 17:40 | 125 | 003:13 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M21072100104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2021-07-21 | 24125 | keep | 0 | Jul | 2021 | 0.016431 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
VEGA BAJA | 2021-07-21 14:33 | 2021-07-21 16:30 | 50 | 001:57 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B21072100044 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 117 | 2021-07-21 | 5850 | keep | 0 | Jul | 2021 | 0.0039844 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-07-21 14:55 | 2021-07-21 18:21 | 48 | 003:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21072100064 | New_Event | Bad Weather | Include | Include | Weather | 206 | 2021-07-21 | 9888 | keep | 0 | Jul | 2021 | 0.0067347 | 3.2693e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 48
CAGUAS | 2021-07-21 14:55 | 2021-07-21 17:58 | 3 | 003:03 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25 KVA X 25 KVA | C21072100063 | New_Event | Service Transformer Failure | Include | Include | Equipment | 183 | 2021-07-21 | 549 | keep | 0 | Jul | 2021 | 0.00037392 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2021-07-21 15:07 | 2021-07-21 17:08 | 250 | 002:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA AVERIADA Y SE CERRO MACHETES | A21072100063 | New_Event | Wire Down | Include | Include | Equipment | 121 | 2021-07-21 | 30250 | keep | 0 | Jul | 2021 | 0.020603 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
AGUADILLA | 2021-07-21 15:10 | 2021-07-21 20:15 | 50 | 005:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21072100019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 305 | 2021-07-21 | 15250 | keep | 0 | Jul | 2021 | 0.010387 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BARRANQUITAS | 2021-07-21 15:17 | 2021-07-21 19:30 | 354 | 004:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C21072100068 | New_Event | Bad Weather | Include | Include | Weather | 253 | 2021-07-21 | 89562 | keep | 0 | Jul | 2021 | 0.061 | 0.00024111 | Sustained | FALSE | TRUE | Not_TMED_Event | 354
SAN JUAN | 2021-07-21 15:22 | 2021-07-21 16:38 | 870 | 001:16 | T | DESGANCHE | SE ABRIO A PETICION DE RANGEL VAZQUEZ DEBIDO A ARBOL CRUZANDO FASE POSTE LLENO DE ABEJAS | S21072100000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 76 | 2021-07-21 | 66120 | keep | 0 | Jul | 2021 | 0.045034 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-07-21 15:22 | 2021-07-21 17:10 | 9 | 001:48 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REEMPLAZO DE POSTE SECUNDARIO | C21072100071 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 108 | 2021-07-21 | 972 | keep | 0 | Jul | 2021 | 0.00066202 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2021-07-21 15:26 | 2021-07-22 11:33 | 80 | 020:07 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21072100125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1207 | 2021-07-21 | 96560 | keep | 0 | Jul | 2021 | 0.065767 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-07-21 15:39 | 2021-07-21 18:50 | 40 | 003:11 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | A21072100074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2021-07-21 | 7640 | keep | 0 | Jul | 2021 | 0.0052036 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-21 15:50 | 2021-07-21 17:36 | 89 | 001:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR PARA REPARAR CONECTOR PARTIDO EN AZOTEA DE MUSEO DE ARTE CALLE NORZAGARRAY AL CERRAR DIO PROBLEMAS CERRAR AUXIALIAR DE LINEA SE LLAMO PERSONAL CDS 75% DE LA CARGA POR EL 1011-5 | S21072100078 | New_Event | Wire Down | Include | Include | Equipment | 106 | 2021-07-21 | 9434 | keep | 0 | Jul | 2021 | 0.0064255 | 6.0617e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 89
BAYAMON | 2021-07-21 15:50 | 2021-07-21 17:36 | 719 | 001:46 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR PARA REPARAR CONECTOR PARTIDO EN AZOTEA DE MUSEO DE ARTE CALLE NORZAGARRAY AL CERRAR DIO PROBLEMAS CERRAR AUXIALIAR DE LINEA SE LLAMO PERSONAL CDS LLEVANDO 75% DE LA CARGA DEL 1011-02 | S21072100078 | New_Event | Wire Down | Include | Include | Equipment | 106 | 2021-07-21 | 76214 | keep | 0 | Jul | 2021 | 0.051909 | 0.00048971 | Sustained | FALSE | TRUE | Not_TMED_Event | 719
CANOVANAS | 2021-07-21 15:50 | 2021-07-21 18:26 | 40 | 002:36 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21072100035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2021-07-21 | 6240 | keep | 0 | Jul | 2021 | 0.00425 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-21 16:00 | 2021-07-21 19:31 | 50 | 003:31 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21072100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 211 | 2021-07-21 | 10550 | keep | 0 | Jul | 2021 | 0.0071856 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-07-21 16:00 | 2021-07-21 18:49 | 283 | 002:49 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | P21072100018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2021-07-21 | 47827 | keep | 0 | Jul | 2021 | 0.032575 | 0.00019275 | Sustained | FALSE | TRUE | Not_TMED_Event | 283
BAYAMON | 2021-07-21 16:08 | 2021-07-21 23:24 | 12 | 007:16 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR | S21072100083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 436 | 2021-07-21 | 5232 | keep | 0 | Jul | 2021 | 0.0035635 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2021-07-21 16:15 | 2021-07-21 18:30 | 30 | 002:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B21072100063 | New_Event | Cutout Failure | Include | Include | Equipment | 135 | 2021-07-21 | 4050 | keep | 0 | Jul | 2021 | 0.0027584 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-07-21 16:28 | 2021-07-22 14:50 | 20 | 022:22 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | M21072100141 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1342 | 2021-07-21 | 26840 | keep | 0 | Jul | 2021 | 0.018281 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BARRANQUITAS | 2021-07-21 16:35 | 2021-07-22 14:05 | 8 | 021:30 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | C21072100079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1290 | 2021-07-21 | 10320 | keep | 0 | Jul | 2021 | 0.0070289 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
CANOVANAS | 2021-07-21 16:36 | 2021-07-21 19:20 | 40 | 002:44 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21072100036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2021-07-21 | 6560 | keep | 0 | Jul | 2021 | 0.004468 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-07-21 16:44 | 2021-07-21 18:47 | 40 | 002:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO HOT CLAMP A LA LINEA | R21072100037 | New_Event | Wire Down | Include | Include | Equipment | 123 | 2021-07-21 | 4920 | keep | 0 | Jul | 2021 | 0.003351 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-07-21 16:49 | 2021-07-21 19:10 | 100 | 002:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | A21072100089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2021-07-21 | 14100 | keep | 0 | Jul | 2021 | 0.0096034 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-21 16:50 | 2021-07-21 21:50 | 12 | 005:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE PARA REPARAR PEDESTAL Y FASE AVERIADA | S21072100031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 300 | 2021-07-21 | 3600 | keep | 0 | Jul | 2021 | 0.0024519 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-07-21 16:50 | 2021-07-22 19:27 | 15 | 026:37 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | B21072100065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1597 | 2021-07-21 | 23955 | keep | 0 | Jul | 2021 | 0.016316 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-07-21 16:54 | 2021-07-22 10:07 | 40 | 017:13 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S21072100098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1033 | 2021-07-21 | 41320 | keep | 0 | Jul | 2021 | 0.028143 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-07-21 17:02 | 2021-07-22 09:12 | 50 | 016:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C21072100085 | New_Event |  |  | Include | Wildlife | 970 | 2021-07-21 | 48500 | keep | 0 | Jul | 2021 | 0.033033 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-07-21 17:42 | 2021-07-21 18:28 | 10 | 000:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P21072100007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 46 | 2021-07-21 | 460 | keep | 0 | Jul | 2021 | 0.0003133 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
YAUCO | 2021-07-21 18:41 | 2021-07-21 22:50 | 1 | 004:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN MONTURA POR MAL TIEMPO | P21072100025 | New_Event | Bad Weather | Include | Include | Weather | 249 | 2021-07-21 | 249 | keep | 0 | Jul | 2021 | 0.00016959 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-07-21 19:27 | 2021-07-22 13:34 | 7 | 018:07 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50 KVA X 50 KVA | R21072100045 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1087 | 2021-07-21 | 7609 | keep | 0 | Jul | 2021 | 0.0051825 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2021-07-21 19:39 | 2021-07-22 15:29 | 7 | 019:50 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHO | C21072100094 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1190 | 2021-07-21 | 8330 | keep | 0 | Jul | 2021 | 0.0056735 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-07-21 20:27 | 2021-07-22 11:21 | 100 | 014:54 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | S21072100110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 894 | 2021-07-21 | 89400 | keep | 0 | Jul | 2021 | 0.06089 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-07-21 20:27 | 2021-07-22 09:38 | 25 | 013:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | P21072100032 | New_Event | Wire Down | Include | Include | Equipment | 791 | 2021-07-21 | 19775 | keep | 0 | Jul | 2021 | 0.013469 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2021-07-21 20:31 | 2021-07-22 09:20 | 17 | 012:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR CONTAMINACION | R21072100048 | New_Event | Cutout Failure | Include | Include | Equipment | 769 | 2021-07-21 | 13073 | keep | 0 | Jul | 2021 | 0.008904 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
MAYAGÃœEZ | 2021-07-21 20:56 | 2021-07-22 11:26 | 12 | 014:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | M21072100165 | New_Event | Cutout Failure | Include | Include | Equipment | 870 | 2021-07-21 | 10440 | keep | 0 | Jul | 2021 | 0.0071106 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-07-21 21:05 | 2021-07-22 12:30 | 12 | 015:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA DE TRANSFORMADOR | M21072100166 | New_Event | Cutout Failure | Include | Include | Equipment | 925 | 2021-07-21 | 11100 | keep | 0 | Jul | 2021 | 0.0075602 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2021-07-21 21:08 | 2021-07-22 09:47 | 12 | 012:39 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR | B21072100077 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 759 | 2021-07-21 | 9108 | keep | 0 | Jul | 2021 | 0.0062034 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-07-21 21:25 | 2021-07-22 10:45 | 10 | 013:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO TOMA DE SERVICIO | B21072100084 | New_Event | Secondary Wire Down | Include | Include | Equipment | 800 | 2021-07-21 | 8000 | keep | 0 | Jul | 2021 | 0.0054488 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-07-21 23:30 | 2021-07-22 10:16 | 60 | 010:46 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | R21072100056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 646 | 2021-07-21 | 38760 | keep | 0 | Jul | 2021 | 0.026399 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
AGUADILLA | 2021-07-21 23:54 | 2021-07-22 17:00 | 200 | 017:06 | P | DESGANCHE | SE REALIZO DESGANCHE MASIVO | M21072100175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1026 | 2021-07-21 | 205200 | keep | 0 | Jul | 2021 | 0.13976 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2021-07-22 00:08 | 2021-07-22 00:09 | 1234 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21072200001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-22 | 1234 | keep | 0 | Jul | 2021 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
PONCE | 2021-07-22 01:53 | 2021-07-22 01:54 | 449 | 000:01 | T | OTRAS CAUSAS | RECIERRE | P210822000XX | New_Event | Other Causes | Include | Include | Other | 1 | 2021-07-22 | 449 | keep | 0 | Jul | 2021 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
HUMACAO | 2021-07-22 02:01 | 2021-07-22 02:02 | 3701 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21072200001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-22 | 3701 | keep | 0 | Jul | 2021 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
CAGUAS | 2021-07-22 02:02 | 2021-07-22 02:03 | 1709 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21072200002 | New_Event |  |  | Include | Wildlife | 1 | 2021-07-22 | 1709 | keep | 0 | Jul | 2021 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
CAGUAS | 2021-07-22 02:03 | 2021-07-22 10:19 | 80 | 008:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 SMU 20 DE 80 AMP EN EL SU - 10 CRUCE POR RATON | C21072200005 | 1st_after_momentary |  |  | Include | Wildlife | 496 | 2021-07-22 | 39680 | keep | 0 | Jul | 2021 | 0.027026 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2021-07-22 02:11 | 2021-07-22 15:13 | 25 | 013:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21072200003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 782 | 2021-07-22 | 19550 | keep | 0 | Jul | 2021 | 0.013315 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-07-22 02:43 | 2021-07-22 13:53 | 79 | 011:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN AEREO PROVISIONAL | R21072200003 | New_Event | Cutout Failure | Include | Include | Equipment | 670 | 2021-07-22 | 52930 | keep | 0 | Jul | 2021 | 0.03605 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
CAGUAS | 2021-07-22 03:14 | 2021-07-22 03:15 | 1271 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21072200006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-22 | 1271 | keep | 0 | Jul | 2021 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
CANOVANAS | 2021-07-22 03:30 | 2021-07-22 09:16 | 20 | 005:46 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN CORTES DE LINEA SE REALIZO DESGANCHE | R21072200004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 346 | 2021-07-22 | 6920 | keep | 0 | Jul | 2021 | 0.0047132 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-07-22 03:30 | 2021-07-22 06:49 | 725 | 003:19 | T | DESGANCHE | SE RETIRO ARBOL DE LAS LINEAS | C21072200007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2021-07-22 | 144275 | keep | 0 | Jul | 2021 | 0.098265 | 0.00049379 | Sustained | FALSE | TRUE | Not_TMED_Event | 725
BARRANQUITAS | 2021-07-22 03:38 | 2021-07-22 03:39 | 1364 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO SE CERRO POR CONTROL | C21072200012 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-07-22 | 1364 | keep | 0 | Jul | 2021 | 0.00092901 | 0.00092901 | Momentary | FALSE | FALSE | Not_TMED_Event | 1364
BARRANQUITAS | 2021-07-22 03:39 | 2021-07-22 10:47 | 300 | 007:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | REMPLAZO AISLADOR Y REPARO CONDUCTOR | C21072200027 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 428 | 2021-07-22 | 128400 | keep | 0 | Jul | 2021 | 0.087453 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
GUAYAMA | 2021-07-22 04:30 | 2021-07-22 09:31 | 200 | 005:01 | P | TRANSFORMADOR AVERIADO | 1 X 65 EN GABINETE PM AMARRADO | P21072200001 | New_Event | Service Transformer Failure | Include | Include | Equipment | 301 | 2021-07-22 | 60200 | keep | 0 | Jul | 2021 | 0.041002 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-07-22 05:31 | 2021-07-22 05:32 | 3046 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | R21072200009 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-22 | 3046 | keep | 0 | Jul | 2021 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2021-07-22 05:32 | 2021-07-24 13:58 | 2 | 056:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | R21072200058 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 3386 | 2021-07-22 | 6772 | keep | 0 | Jul | 2021 | 0.0046124 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
BAYAMON | 2021-07-22 06:06 | 2021-07-22 06:07 | 4533 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21072200005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-22 | 4533 | keep | 0 | Jul | 2021 | 0.0030874 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
BAYAMON | 2021-07-22 06:07 | 2021-07-22 15:36 | 10 | 009:29 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21072200013 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 569 | 2021-07-22 | 5690 | keep | 0 | Jul | 2021 | 0.0038754 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-07-22 06:15 | 2021-07-22 15:08 | 80 | 008:53 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA DESGANCHE | S21072200007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 533 | 2021-07-22 | 42640 | keep | 0 | Jul | 2021 | 0.029042 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-07-22 06:49 | 2021-07-23 11:49 | 338 | 028:60 | P | DESGANCHE | SE CERRO PUENTE DE LINEA A LINEA POR DESGANCHE | C21072200096 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1740 | 2021-07-22 | 588120 | keep | 0 | Jul | 2021 | 0.40057 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-07-22 06:49 | 2021-07-22 16:34 | 462 | 009:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE REMPLAZO MACHETE AVERIADO Y DISCO PARTIDO | C21072200019 | New_Event | Wire Down | Include | Include | Equipment | 585 | 2021-07-22 | 270270 | keep | 0 | Jul | 2021 | 0.18408 | 0.00031467 | Sustained | FALSE | FALSE | Not_TMED_Event | 462
CANOVANAS | 2021-07-22 07:04 | 2021-07-22 10:25 | 18 | 003:21 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA DESGANCHE | R21072200010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2021-07-22 | 3618 | keep | 0 | Jul | 2021 | 0.0024642 | 1.226e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 18
BARRANQUITAS | 2021-07-22 07:15 | 2021-07-22 12:19 | 80 | 005:04 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA REMPLAZO AISLADOR Y REPARO CONDUCTOR | C21072200018 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 304 | 2021-07-22 | 24320 | keep | 0 | Jul | 2021 | 0.016564 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-07-22 07:19 | 2021-07-22 11:08 | 75 | 003:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA REMPLAZO CAJA | A21072200025 | New_Event | Cutout Failure | Include | Include | Equipment | 229 | 2021-07-22 | 17175 | keep | 0 | Jul | 2021 | 0.011698 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
SAN JUAN | 2021-07-22 08:12 | 2021-07-23 15:04 | 150 | 030:52 | P | TRANSFORMADOR AVERIADO | 1 X 80 EN CORTE DE LINEA Y 1 X 50 EN T - 161 CONTAMINACION | R21072200013 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1852 | 2021-07-22 | 277800 | keep | 0 | Jul | 2021 | 0.18921 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CANOVANAS | 2021-07-22 08:19 | 2021-07-22 13:45 | 2 | 005:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR IGUANA | R21072200014 | New_Event |  |  | Include | Wildlife | 326 | 2021-07-22 | 652 | keep | 0 | Jul | 2021 | 0.00044407 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
VEGA BAJA | 2021-07-22 08:19 | 2021-07-22 11:47 | 12 | 003:28 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21072200018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2021-07-22 | 2496 | keep | 0 | Jul | 2021 | 0.0017 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
CAGUAS | 2021-07-22 08:51 | 2021-07-22 11:55 | 3 | 003:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA Y 1 X 50 EN RISER CRUCE POR AVE | C21072200039 | New_Event |  |  | Include | Wildlife | 184 | 2021-07-22 | 552 | keep | 0 | Jul | 2021 | 0.00037596 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
BARRANQUITAS | 2021-07-22 08:51 | 2021-07-22 14:47 | 50 | 005:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA DESPEGO BAJANTE PRIMARIO DEL POSTE | C21072200038 | New_Event | Wire Down | Include | Include | Equipment | 356 | 2021-07-22 | 17800 | keep | 0 | Jul | 2021 | 0.012123 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-22 09:01 | 2021-07-22 16:47 | 40 | 007:46 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21072200041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 466 | 2021-07-22 | 18640 | keep | 0 | Jul | 2021 | 0.012696 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-07-22 09:11 | 2021-07-22 09:12 | 538 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21072200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-22 | 538 | keep | 0 | Jul | 2021 | 0.00036643 | 0.00036643 | Momentary | FALSE | FALSE | Not_TMED_Event | 538
BARRANQUITAS | 2021-07-22 09:16 | 2021-07-22 16:31 | 10 | 007:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR REMPLAZO PARARRAYO Y CAJA AVERIADA | C21072200045 | New_Event | Cutout Failure | Include | Include | Equipment | 435 | 2021-07-22 | 4350 | keep | 0 | Jul | 2021 | 0.0029628 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-22 09:25 | 2021-07-22 17:00 | 200 | 007:35 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO | M21072200030 | New_Event | Defective Pole | Include | Include | Equipment | 455 | 2021-07-22 | 91000 | keep | 0 | Jul | 2021 | 0.06198 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2021-07-22 09:27 | 2021-07-22 13:43 | 1 | 004:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C21072200048 | New_Event |  |  | Include | Wildlife | 256 | 2021-07-22 | 256 | keep | 0 | Jul | 2021 | 0.00017436 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-07-22 09:28 | 2021-07-22 20:36 | 15 | 011:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21072100031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 668 | 2021-07-22 | 10020 | keep | 0 | Jul | 2021 | 0.0068246 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-07-22 09:40 | 2021-07-22 17:28 | 400 | 007:48 | P | ESTRUCTURA AVERIADA | 3 X 140 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO | M21072200021 | New_Event | Defective Pole | Include | Include | Equipment | 468 | 2021-07-22 | 187200 | keep | 0 | Jul | 2021 | 0.1275 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
CAGUAS | 2021-07-22 09:41 | 2021-07-22 17:15 | 16 | 007:34 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 EN CORTE DE LINEA REMPLAZO PARARRAYO Y PIN POLE TOP | C21072200052 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 454 | 2021-07-22 | 7264 | keep | 0 | Jul | 2021 | 0.0049475 | 1.0898e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 16
SAN JUAN | 2021-07-22 09:42 | 2021-07-22 10:57 | 1862 | 001:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE CANOVANAS A BARRAZA SE SECCIONALIZO BANNER SOBRE LINEA | R21072200020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 75 | 2021-07-22 | 139650 | keep | 0 | Jul | 2021 | 0.095115 | 0.0012682 | Sustained | FALSE | TRUE | Not_TMED_Event | 1862
SAN JUAN | 2021-07-22 09:42 | 2021-07-22 10:57 | 1613 | 001:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE CANOVANAS A BARRAZA SE SECCIONALIZO BANNER SOBRE LINEA | R21072200020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 75 | 2021-07-22 | 120975 | keep | 0 | Jul | 2021 | 0.082396 | 0.0010986 | Sustained | FALSE | TRUE | Not_TMED_Event | 1613
SAN JUAN | 2021-07-22 09:42 | 2021-07-22 10:57 | 1448 | 001:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE CANOVANAS A BARRAZA SE SECCIONALIZO BANNER SOBRE LINEA | R21072200020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 75 | 2021-07-22 | 108600 | keep | 0 | Jul | 2021 | 0.073967 | 0.00098623 | Sustained | FALSE | TRUE | Not_TMED_Event | 1448
PONCE | 2021-07-22 09:42 | 2021-07-22 09:43 | 2379 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21072200011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-22 | 2379 | keep | 0 | Jul | 2021 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
UTUADO | 2021-07-22 09:45 | 2021-07-22 11:00 | 50 | 001:15 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE | A21072200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2021-07-22 | 3750 | keep | 0 | Jul | 2021 | 0.0025541 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-22 09:46 | 2021-07-22 14:58 | 50 | 005:12 | P | NO SE REPORTO CAUSA | SE REPARO PUENTE DE LINEA A CAJA | B21072200035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 312 | 2021-07-22 | 15600 | keep | 0 | Jul | 2021 | 0.010625 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-22 09:47 | 2021-07-22 16:51 | 15 | 007:04 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHO Y LEVANTO CONDUCTOR | C21072200054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 424 | 2021-07-22 | 6360 | keep | 0 | Jul | 2021 | 0.0043318 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-07-22 09:48 | 2021-07-22 12:27 | 80 | 002:39 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21072200026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2021-07-22 | 12720 | keep | 0 | Jul | 2021 | 0.0086635 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-07-22 09:57 | 2021-07-24 11:13 | 10 | 049:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTE SECUNDARIO | S21072200032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2956 | 2021-07-22 | 29560 | keep | 0 | Jul | 2021 | 0.020133 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2021-07-22 10:09 | 2021-07-22 10:10 | 3973 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | P21072200014 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-07-22 | 3973 | keep | 0 | Jul | 2021 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
PONCE | 2021-07-22 10:11 | 2021-07-22 16:12 | 5 | 006:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | P21072200012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 361 | 2021-07-22 | 1805 | keep | 0 | Jul | 2021 | 0.0012294 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-07-22 10:25 | 2021-07-22 11:07 | 40 | 000:42 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21072200042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 42 | 2021-07-22 | 1680 | keep | 0 | Jul | 2021 | 0.0011442 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-07-22 10:30 | 2021-07-22 20:55 | 80 | 010:25 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO | M21072200012 | New_Event | Defective Pole | Include | Include | Equipment | 625 | 2021-07-22 | 50000 | keep | 0 | Jul | 2021 | 0.034055 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2021-07-22 10:45 | 2021-07-22 10:46 | 2708 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR | R21072200031 | New_Event |  |  | Include | Wildlife | 1 | 2021-07-22 | 2708 | keep | 0 | Jul | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2021-07-22 10:46 | 2021-07-22 16:04 | 5 | 005:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR IGUANA | R21072200043 | 1st_after_momentary |  |  | Include | Wildlife | 318 | 2021-07-22 | 1590 | keep | 0 | Jul | 2021 | 0.0010829 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
ARECIBO | 2021-07-22 11:14 | 2021-07-22 15:56 | 2694 | 004:42 | S | PROTECCION DEFECTUOSA | SE CALIBRO RELE EN TRANSFORMADOR | A21072200056 | New_Event | Protection Miscoordination | Include | Include | Other | 282 | 2021-07-22 | 759708 | keep | 0 | Jul | 2021 | 0.51743 | 0.0018349 | Sustained | FALSE | FALSE | Not_TMED_Event | 2694
ARECIBO | 2021-07-22 11:14 | 2021-07-22 15:56 | 2228 | 004:42 | S | PROTECCION DEFECTUOSA | SE CALIBRO RELE EN TRANSFORMADOR | A21072200056 | New_Event | Protection Miscoordination | Include | Include | Other | 282 | 2021-07-22 | 628296 | keep | 0 | Jul | 2021 | 0.42793 | 0.0015175 | Sustained | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2021-07-22 11:14 | 2021-07-22 15:56 | 438 | 004:42 | S | PROTECCION DEFECTUOSA | SE CALIBRO RELE EN TRANSFORMADOR | A21072200056 | New_Event | Protection Miscoordination | Include | Include | Other | 282 | 2021-07-22 | 123516 | keep | 0 | Jul | 2021 | 0.084126 | 0.00029832 | Sustained | FALSE | FALSE | Not_TMED_Event | 438
SAN JUAN | 2021-07-22 11:27 | 2021-07-22 16:22 | 1 | 004:55 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | R21072200038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 295 | 2021-07-22 | 295 | keep | 0 | Jul | 2021 | 0.00020092 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-07-22 11:42 | 2021-07-23 18:28 | 10 | 030:46 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR UNO DE IGUAL CAPACIDAD | S21072200052 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1846 | 2021-07-22 | 18460 | keep | 0 | Jul | 2021 | 0.012573 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-22 11:47 | 2021-07-22 12:26 | 20 | 000:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RETEZO LINEA Y CERRO PUENTE | B21072200049 | New_Event | Wire Down | Include | Include | Equipment | 39 | 2021-07-22 | 780 | keep | 0 | Jul | 2021 | 0.00053125 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-07-22 11:48 | 2021-07-22 20:10 | 85 | 008:22 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR | S21072200053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 502 | 2021-07-22 | 42670 | keep | 0 | Jul | 2021 | 0.029062 | 5.7893e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 85
VEGA BAJA | 2021-07-22 12:01 | 2021-07-22 15:48 | 12 | 003:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B21072200050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 227 | 2021-07-22 | 2724 | keep | 0 | Jul | 2021 | 0.0018553 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-07-22 12:18 | 2021-07-22 13:31 | 5290 | 001:13 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE PATRULLO SE ENCONTRO AISLADOR PARTIDO EN RAMAL 8 SE REPARO Y SE PROBO QUEDO 100% EN SERVICIO LLEVA CARGA 1336-09 | S21072200000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 73 | 2021-07-22 | 386170 | keep | 0 | Jul | 2021 | 0.26302 | 0.003603 | Sustained | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2021-07-22 12:18 | 2021-07-22 13:31 | 207 | 001:13 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE PATRULLO SE ENCONTRO AISLADOR PARTIDO EN RAMAL 8 SE REPARO Y SE PROBO QUEDO 100% CARGA POR EL 1336-08 | S21072200000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 73 | 2021-07-22 | 15111 | keep | 0 | Jul | 2021 | 0.010292 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2021-07-22 12:19 | 2021-07-23 09:59 | 40 | 021:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE LINEA A CAJA | R21072200039 | New_Event | Wire Down | Include | Include | Equipment | 1300 | 2021-07-22 | 52000 | keep | 0 | Jul | 2021 | 0.035417 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-22 12:35 | 2021-07-22 17:22 | 150 | 004:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO EN TRONCAL TRASPATIO | B21072200051 | New_Event | Wire Down | Include | Include | Equipment | 287 | 2021-07-22 | 43050 | keep | 0 | Jul | 2021 | 0.029321 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2021-07-22 12:58 | 2021-07-22 16:56 | 80 | 003:58 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | S21072200094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2021-07-22 | 19040 | keep | 0 | Jul | 2021 | 0.012968 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
AGUADILLA | 2021-07-22 13:00 | 2021-07-22 16:10 | 15 | 003:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | M21072100141 | New_Event | Secondary Wire Down | Include | Include | Equipment | 190 | 2021-07-22 | 2850 | keep | 0 | Jul | 2021 | 0.0019411 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-07-22 13:10 | 2021-07-23 00:30 | 50 | 011:20 | P | DESGANCHE | 1 X 75 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | A21072200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 680 | 2021-07-22 | 34000 | keep | 0 | Jul | 2021 | 0.023157 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-22 13:16 | 2021-07-23 19:27 | 1 | 030:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN RISER MAL TIEMPO | R21072200044 | New_Event | Bad Weather | Include | Include | Weather | 1811 | 2021-07-22 | 1811 | keep | 0 | Jul | 2021 | 0.0012335 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-07-22 13:18 | 2021-07-22 15:55 | 383 | 002:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA LEVANTAR CONDUCTOR NEUTRAL PRIMARIO | R21072200046 | New_Event | Wire Down | Include | Include | Equipment | 157 | 2021-07-22 | 60131 | keep | 0 | Jul | 2021 | 0.040955 | 0.00026086 | Sustained | FALSE | TRUE | Not_TMED_Event | 383
CANOVANAS | 2021-07-22 13:36 | 2021-07-22 17:14 | 10 | 003:38 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL DE LA LINEA | R21072200048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 218 | 2021-07-22 | 2180 | keep | 0 | Jul | 2021 | 0.0014848 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CANOVANAS | 2021-07-22 13:46 | 2021-07-22 14:26 | 27 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | R21072100049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2021-07-22 | 1080 | keep | 0 | Jul | 2021 | 0.00073558 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
PONCE | 2021-07-22 13:48 | 2021-07-22 16:22 | 1 | 002:34 | P | OTRAS CAUSAS | 2 X 100 EN RISER POR AVERIA INTERNA | P21072200020 | New_Event | Other Causes | Include | Include | Other | 154 | 2021-07-22 | 154 | keep | 0 | Jul | 2021 | 0.00010489 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2021-07-22 13:50 | 2021-07-22 16:54 | 200 | 003:04 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21072200022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2021-07-22 | 36800 | keep | 0 | Jul | 2021 | 0.025064 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-07-22 13:55 | 2021-07-22 14:02 | 353 | 000:07 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S21072200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2021-07-22 | 2471 | keep | 0 | Jul | 2021 | 0.001683 | 0.00024043 | Sustained | FALSE | FALSE | Not_TMED_Event | 353
BAYAMON | 2021-07-22 13:58 | 2021-07-22 13:59 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA EL 99% DEL 1909-09 | S21072200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-22 | 222 | keep | 0 | Jul | 2021 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2021-07-22 13:58 | 2021-07-22 13:59 | 4411 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 99% DE LA CARGA POR EL 1907-03 | S21072400072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-22 | 4411 | keep | 0 | Jul | 2021 | 0.0030043 | 0.0030043 | Momentary | FALSE | FALSE | Not_TMED_Event | 4411
SAN JUAN | 2021-07-22 14:01 | 2021-07-22 14:05 | 870 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S21072200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-07-22 | 3480 | keep | 0 | Jul | 2021 | 0.0023702 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
HUMACAO | 2021-07-22 14:10 | 2021-07-22 15:57 | 40 | 001:47 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR NO CAUSA | C21072200077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 107 | 2021-07-22 | 4280 | keep | 0 | Jul | 2021 | 0.0029151 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-22 14:26 | 2021-07-22 14:27 | 1420 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1530-06 | S21072200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-22 | 1420 | keep | 0 | Jul | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-07-22 14:26 | 2021-07-22 14:27 | 437 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 1526-02 | S21072200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-22 | 437 | keep | 0 | Jul | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
CAGUAS | 2021-07-22 14:26 | 2021-07-22 16:15 | 8 | 001:49 | P | SECUNDARIA/DESGANCHE | ABRIO TRANSFORMADOR PARA DESGANCHAR Y REPARAR SECUNDARIA | C21072200079 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 109 | 2021-07-22 | 872 | keep | 0 | Jul | 2021 | 0.00059392 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2021-07-22 14:37 | 2021-07-22 19:05 | 80 | 004:28 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M21072200055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2021-07-22 | 21440 | keep | 0 | Jul | 2021 | 0.014603 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
VEGA BAJA | 2021-07-22 15:06 | 2021-07-22 21:06 | 20 | 006:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE LENVANTO 3 CONDUCTORES PRIMARIOS Y SE REALIZO DESGANCHE | B21072200076 | New_Event | Wire Down | Include | Include | Equipment | 360 | 2021-07-22 | 7200 | keep | 0 | Jul | 2021 | 0.0049039 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-07-22 15:10 | 2021-07-22 20:14 | 6 | 005:04 | P | SECUNDARIA/DESGANCHE | ABRIO TRANSFORMADOR PARA DESGANCHAR REMPLAZAR BAJANTE Y TRAMO SECUNDARIO | C21072200088 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 304 | 2021-07-22 | 1824 | keep | 0 | Jul | 2021 | 0.0012423 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-07-22 15:17 | 2021-07-22 18:58 | 7 | 003:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21072200090 | New_Event | Secondary Wire Down | Include | Include | Equipment | 221 | 2021-07-22 | 1547 | keep | 0 | Jul | 2021 | 0.0010537 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-07-22 15:21 | 2021-07-22 15:22 | 5 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21072200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-22 | 5 | keep | 0 | Jul | 2021 | 3.4055e-06 | 3.4055e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-07-22 15:30 | 2021-07-22 16:48 | 10 | 001:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA PARTIDA | A21072200096 | New_Event | Secondary Wire Down | Include | Include | Equipment | 78 | 2021-07-22 | 780 | keep | 0 | Jul | 2021 | 0.00053125 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
SAN JUAN | 2021-07-22 16:00 | 2021-07-22 18:30 | 12 | 002:30 | P | SECUNDARIA/DESGANCHE | SE ABRE MONTURA PARA REALIZAR DESGANCHE SECUNDARIO | S21072200000 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 150 | 2021-07-22 | 1800 | keep | 0 | Jul | 2021 | 0.001226 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-07-22 16:01 | 2021-07-22 18:19 | 60 | 002:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA CERRAR PUENTE PRIMARIO DE LINEA A CAJA | S21072200134 | New_Event | Wire Down | Include | Include | Equipment | 138 | 2021-07-22 | 8280 | keep | 0 | Jul | 2021 | 0.0056395 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-07-22 16:08 | 2021-07-22 19:27 | 30 | 003:19 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE ENDEREZO POSTE | B21072200083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2021-07-22 | 5970 | keep | 0 | Jul | 2021 | 0.0040661 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-07-22 16:10 | 2021-07-23 14:43 | 7 | 022:33 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21072200084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1353 | 2021-07-22 | 9471 | keep | 0 | Jul | 2021 | 0.0064507 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-07-22 16:15 | 2021-07-24 10:54 | 10 | 042:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21072200065 | New_Event | Bad Weather | Include | Include | Weather | 2559 | 2021-07-22 | 25590 | keep | 0 | Jul | 2021 | 0.017429 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-07-22 16:51 | 2021-07-23 16:10 | 10 | 023:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR Y SE REPARO SECUNDARIA | P21072200015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1399 | 2021-07-22 | 13990 | keep | 0 | Jul | 2021 | 0.0095285 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-07-22 17:10 | 2021-07-22 19:11 | 20 | 002:01 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 40 EN CORTE DE LINEA REPARO TERMINACION | C21072200097 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 121 | 2021-07-22 | 2420 | keep | 0 | Jul | 2021 | 0.0016483 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-07-22 17:28 | 2021-07-22 21:14 | 12 | 003:46 | P | SECUNDARIA/DESGANCHE | SE ABRE MONTURA PARA REMPLAZAR SECUNDARIA Y DESGANCHAR | S21072200064 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 226 | 2021-07-22 | 2712 | keep | 0 | Jul | 2021 | 0.0018471 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-07-22 17:28 | 2021-07-22 17:30 | 1617 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21072200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-22 | 3234 | keep | 0 | Jul | 2021 | 0.0022027 | 0.0011013 | Momentary | FALSE | TRUE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-07-22 17:28 | 2021-07-22 17:30 | 1017 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21072200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-22 | 2034 | keep | 0 | Jul | 2021 | 0.0013853 | 0.00069267 | Momentary | FALSE | TRUE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-07-22 17:28 | 2021-07-22 17:30 | 828 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21072200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-22 | 1656 | keep | 0 | Jul | 2021 | 0.0011279 | 0.00056395 | Momentary | FALSE | TRUE | Not_TMED_Event | 828
MAYAGÃœEZ | 2021-07-22 17:28 | 2021-07-22 17:30 | 863 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | 211000000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-22 | 1726 | keep | 0 | Jul | 2021 | 0.0011756 | 0.00058779 | Momentary | FALSE | TRUE | Not_TMED_Event | 863
MAYAGÃœEZ | 2021-07-22 17:28 | 2021-07-22 17:30 | 309 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | 211000000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-22 | 618 | keep | 0 | Jul | 2021 | 0.00042092 | 0.00021046 | Momentary | FALSE | TRUE | Not_TMED_Event | 309
MAYAGÃœEZ | 2021-07-22 17:28 | 2021-07-22 17:30 | 176 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | 211000000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-22 | 352 | keep | 0 | Jul | 2021 | 0.00023975 | 0.00011987 | Momentary | FALSE | TRUE | Not_TMED_Event | 176
MAYAGÃœEZ | 2021-07-22 17:28 | 2021-07-22 17:30 | 108 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | 211000000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-22 | 216 | keep | 0 | Jul | 2021 | 0.00014712 | 7.3558e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 108
MAYAGÃœEZ | 2021-07-22 17:28 | 2021-07-22 17:30 | 974 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21072200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-22 | 1948 | keep | 0 | Jul | 2021 | 0.0013268 | 0.00066339 | Momentary | FALSE | TRUE | Not_TMED_Event | 974
MAYAGÃœEZ | 2021-07-22 17:30 | 2021-07-22 20:50 | 400 | 003:20 | P | ESTRUCTURA AVERIADA | 3 X 140 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO | M21072200021 | New_Event | Defective Pole | Include | Include | Equipment | 200 | 2021-07-22 | 80000 | keep | 0 | Jul | 2021 | 0.054488 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
ARECIBO | 2021-07-22 17:30 | 2021-07-23 11:21 | 30 | 017:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21072200105 | New_Event | Bad Weather | Include | Include | Weather | 1071 | 2021-07-22 | 32130 | keep | 0 | Jul | 2021 | 0.021884 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-07-22 17:57 | 2021-07-23 13:46 | 80 | 019:49 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | S21072200141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1189 | 2021-07-22 | 95120 | keep | 0 | Jul | 2021 | 0.064786 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-07-22 18:08 | 2021-07-22 20:20 | 50 | 002:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | A21072200107 | New_Event | Bad Weather | Include | Include | Weather | 132 | 2021-07-22 | 6600 | keep | 0 | Jul | 2021 | 0.0044952 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-22 18:19 | 2021-07-22 19:07 | 100 | 000:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA CERRAR PUENTE PRIMARIO DE LINEA A CAJA | S21072200134 | Additional_clients | Wire Down | Include | Include | Equipment | 48 | 2021-07-22 | 4800 | keep | 0 | Jul | 2021 | 0.0032693 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-07-22 18:33 | 2021-07-22 18:34 | 2608 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21072200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-22 | 2608 | keep | 0 | Jul | 2021 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
PONCE | 2021-07-22 18:41 | 2021-07-22 21:03 | 300 | 002:22 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X DE 220 EN CORTE DE LINEA POR AISLADORES ROTOS SE REEMPLAZARON AISLADORES | P21072200031 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 142 | 2021-07-22 | 42600 | keep | 0 | Jul | 2021 | 0.029015 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
CAGUAS | 2021-07-22 19:45 | 2021-07-23 11:58 | 9 | 016:13 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA | C21072200105 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 973 | 2021-07-22 | 8757 | keep | 0 | Jul | 2021 | 0.0059644 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2021-07-22 19:51 | 2021-07-23 11:08 | 20 | 015:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA REMPLAZO CAJA QUEMADA | R21072200065 | New_Event | Cutout Failure | Include | Include | Equipment | 917 | 2021-07-22 | 18340 | keep | 0 | Jul | 2021 | 0.012491 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-07-22 19:58 | 2021-07-22 22:37 | 171 | 002:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRARON DOS PUENTES ABIERTOS | P21072200034 | New_Event | Wire Down | Include | Include | Equipment | 159 | 2021-07-22 | 27189 | keep | 0 | Jul | 2021 | 0.018518 | 0.00011647 | Sustained | FALSE | FALSE | Not_TMED_Event | 171
MAYAGÃœEZ | 2021-07-22 20:07 | 2021-07-22 20:08 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | M21072120000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-22 | 312 | keep | 0 | Jul | 2021 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
ARECIBO | 2021-07-22 20:30 | 2021-07-23 10:55 | 150 | 014:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | A21072200113 | New_Event | Cutout Failure | Include | Include | Equipment | 865 | 2021-07-22 | 129750 | keep | 0 | Jul | 2021 | 0.088372 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-07-22 20:34 | 2021-07-23 12:12 | 60 | 015:38 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A21072200115 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 938 | 2021-07-22 | 56280 | keep | 0 | Jul | 2021 | 0.038332 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
PONCE | 2021-07-22 20:42 | 2021-07-23 16:48 | 10 | 020:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA Y SE HIZO DESGANCHE | P21072200035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1206 | 2021-07-22 | 12060 | keep | 0 | Jul | 2021 | 0.008214 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-07-22 21:08 | 2021-07-23 12:57 | 150 | 015:49 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | P21072200037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 949 | 2021-07-22 | 142350 | keep | 0 | Jul | 2021 | 0.096954 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-07-22 21:28 | 2021-07-23 17:07 | 35 | 019:39 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | B21072200188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1179 | 2021-07-22 | 41265 | keep | 0 | Jul | 2021 | 0.028105 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-07-22 22:10 | 2021-07-22 22:11 | 1420 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1530-06 | S21072200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-22 | 1420 | keep | 0 | Jul | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-07-22 22:10 | 2021-07-22 22:11 | 437 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 1526-02 | S21072200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-22 | 437 | keep | 0 | Jul | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
CAGUAS | 2021-07-22 22:31 | 2021-07-23 10:57 | 350 | 012:26 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO ENREDADERA | C21072200118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 746 | 2021-07-22 | 261100 | keep | 0 | Jul | 2021 | 0.17783 | 0.00023838 | Sustained | FALSE | TRUE | Not_TMED_Event | 350
VEGA BAJA | 2021-07-22 23:54 | 2021-07-22 23:55 | 3000 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21072200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-22 | 3000 | keep | 0 | Jul | 2021 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
HUMACAO | 2021-07-23 02:31 | 2021-07-23 08:57 | 95 | 006:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C21072300003 | New_Event | Bad Weather | Include | Include | Weather | 386 | 2021-07-23 | 36670 | keep | 0 | Jul | 2021 | 0.024976 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
CAGUAS | 2021-07-23 04:55 | 2021-07-23 10:50 | 22 | 005:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN RISER Y 1 SMU DE 25 EN SU-2 CRUCE POR RATA | C21072300004 | New_Event |  |  | Include | Wildlife | 355 | 2021-07-23 | 7810 | keep | 0 | Jul | 2021 | 0.0053194 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
CAGUAS | 2021-07-23 05:23 | 2021-07-23 10:51 | 117 | 005:28 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO PARARRAYOS | C21072300005 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 328 | 2021-07-23 | 38376 | keep | 0 | Jul | 2021 | 0.026138 | 7.9688e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 117
HUMACAO | 2021-07-23 05:57 | 2021-07-23 05:58 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21072300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-23 | 2354 | keep | 0 | Jul | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
MAYAGÃœEZ | 2021-07-23 06:31 | 2021-07-23 10:15 | 100 | 003:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21072300002 | New_Event | Bad Weather | Include | Include | Weather | 224 | 2021-07-23 | 22400 | keep | 0 | Jul | 2021 | 0.015257 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-07-23 06:44 | 2021-07-23 10:28 | 100 | 003:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTE DE LINEA | M21072300003 | New_Event |  |  | Include | Wildlife | 224 | 2021-07-23 | 22400 | keep | 0 | Jul | 2021 | 0.015257 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-23 06:53 | 2021-07-24 09:48 | 10 | 026:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE CERRO BAJANTE SECUNDARIO | S21072300002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1615 | 2021-07-23 | 16150 | keep | 0 | Jul | 2021 | 0.011 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-23 06:57 | 2021-07-23 13:00 | 60 | 006:03 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | S21072200012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 363 | 2021-07-23 | 21780 | keep | 0 | Jul | 2021 | 0.014834 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-07-23 07:05 | 2021-07-23 07:06 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21072300008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-23 | 1827 | keep | 0 | Jul | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
MAYAGÃœEZ | 2021-07-23 07:22 | 2021-07-24 12:16 | 50 | 028:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M21072300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1734 | 2021-07-23 | 86700 | keep | 0 | Jul | 2021 | 0.059051 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-23 07:40 | 2021-07-23 14:57 | 3 | 007:17 | P | SECUNDARIA/DESGANCHE | 2 X 15 EN BANCO DE TRANSFORMADORES DESGANCHE | C21072300014 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 437 | 2021-07-23 | 1311 | keep | 0 | Jul | 2021 | 0.00089292 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2021-07-23 07:41 | 2021-07-23 17:42 | 80 | 010:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA QUEMADA | C21072300015 | New_Event | Cutout Failure | Include | Include | Equipment | 601 | 2021-07-23 | 48080 | keep | 0 | Jul | 2021 | 0.032747 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-07-23 07:43 | 2021-07-23 11:20 | 220 | 003:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80, 1 X 65 Y 1 X 50 EN CORTES DE LINEA MAL TIEMPO | C21072300016 | New_Event | Bad Weather | Include | Include | Weather | 217 | 2021-07-23 | 47740 | keep | 0 | Jul | 2021 | 0.032515 | 0.00014984 | Sustained | FALSE | TRUE | Not_TMED_Event | 220
GUAYAMA | 2021-07-23 07:52 | 2021-07-23 08:30 | 8 | 000:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR SE REMPLAZO PORTA FUSIBLE AVERIADO | P21072300010 | New_Event | Cutout Failure | Include | Include | Equipment | 38 | 2021-07-23 | 304 | keep | 0 | Jul | 2021 | 0.00020705 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-07-23 07:54 | 2021-07-23 13:23 | 93 | 005:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA CRUCE POR AVE | C21072300017 | New_Event |  |  | Include | Wildlife | 329 | 2021-07-23 | 30597 | keep | 0 | Jul | 2021 | 0.020839 | 6.3342e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 93
ARECIBO | 2021-07-23 08:05 | 2021-07-23 13:15 | 14 | 005:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO DOS CAJA PRIMARIAS EN TRANSFORMADOR | A21072300004 | New_Event | Cutout Failure | Include | Include | Equipment | 310 | 2021-07-23 | 4340 | keep | 0 | Jul | 2021 | 0.002956 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
VEGA BAJA | 2021-07-23 08:10 | 2021-07-23 19:18 | 25 | 011:08 | P | DESGANCHE | SE SECCIONALIZO CORTE DE LINEA PARA CONTRATISTA REALIZAR DESGANCHE Y SE NORMALIZO | B21072300008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 668 | 2021-07-23 | 16700 | keep | 0 | Jul | 2021 | 0.011374 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-07-23 08:12 | 2021-07-23 18:50 | 25 | 010:38 | P | LINEA DE TRANSMISION 38KV | SE ABRIO CORTE DE LINEA REALIZAR TRABAJOS EN LINEA 2000 | M21072300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 638 | 2021-07-23 | 15950 | keep | 0 | Jul | 2021 | 0.010863 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
AGUADILLA | 2021-07-23 08:15 | 2021-07-23 17:00 | 80 | 008:45 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE | M21072200075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 525 | 2021-07-23 | 42000 | keep | 0 | Jul | 2021 | 0.028606 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-07-23 08:19 | 2021-07-23 10:56 | 300 | 002:37 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE RETIRO RAMA | P21072300012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2021-07-23 | 47100 | keep | 0 | Jul | 2021 | 0.03208 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
SAN JUAN | 2021-07-23 08:28 | 2021-07-23 16:39 | 100 | 008:11 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21072300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 491 | 2021-07-23 | 49100 | keep | 0 | Jul | 2021 | 0.033442 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-07-23 08:31 | 2021-07-23 15:48 | 17 | 007:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 Y 1 X 30 EN CORTES DE LINEA SE RETEZO LINEA PRIMARIA | C21072300025 | New_Event | Wire Down | Include | Include | Equipment | 437 | 2021-07-23 | 7429 | keep | 0 | Jul | 2021 | 0.0050599 | 1.1579e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 17
FAJARDO | 2021-07-23 08:32 | 2021-07-23 09:58 | 80 | 001:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | R21072300007 | New_Event |  |  | Include | Wildlife | 86 | 2021-07-23 | 6880 | keep | 0 | Jul | 2021 | 0.0046859 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
VEGA BAJA | 2021-07-23 08:33 | 2021-07-23 10:06 | 60 | 001:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 Y 1 X 80 EN CORTE DE LINEA DIFERENTES SE RETIRO AVE | B21072300009 | New_Event |  |  | Include | Wildlife | 93 | 2021-07-23 | 5580 | keep | 0 | Jul | 2021 | 0.0038005 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-07-23 08:49 | 2021-07-23 13:00 | 70 | 004:11 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE | M21072300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2021-07-23 | 17570 | keep | 0 | Jul | 2021 | 0.011967 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BAYAMON | 2021-07-23 08:50 | 2021-07-23 18:14 | 50 | 009:24 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | B21072300010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 564 | 2021-07-23 | 28200 | keep | 0 | Jul | 2021 | 0.019207 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-23 08:51 | 2021-07-23 15:00 | 100 | 006:09 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETES PRIMARIOS QUEMADOS | M21072300013 | New_Event | Switch Failure | Include | Include | Equipment | 369 | 2021-07-23 | 36900 | keep | 0 | Jul | 2021 | 0.025132 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2021-07-23 09:02 | 2021-07-23 18:25 | 20 | 009:23 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR | P21072300016 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 563 | 2021-07-23 | 11260 | keep | 0 | Jul | 2021 | 0.0076691 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-07-23 09:25 | 2021-07-23 18:00 | 100 | 008:35 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO | M21072300016 | New_Event | Defective Pole | Include | Include | Equipment | 515 | 2021-07-23 | 51500 | keep | 0 | Jul | 2021 | 0.035076 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-07-23 09:39 | 2021-07-23 16:27 | 25 | 006:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | S21072300012 | New_Event | Cutout Failure | Include | Include | Equipment | 408 | 2021-07-23 | 10200 | keep | 0 | Jul | 2021 | 0.0069472 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-07-23 09:43 | 2021-07-23 13:01 | 10 | 003:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21072300000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 198 | 2021-07-23 | 1980 | keep | 0 | Jul | 2021 | 0.0013486 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-07-23 09:58 | 2021-07-23 13:52 | 4 | 003:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BARRA DE NEUTRALES EN EL PEDESTAL | R21072300009 | New_Event | Secondary Wire Down | Include | Include | Equipment | 234 | 2021-07-23 | 936 | keep | 0 | Jul | 2021 | 0.00063751 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2021-07-23 10:03 | 2021-07-23 12:28 | 231 | 002:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO | C21072300048 | New_Event | Bad Weather | Include | Include | Weather | 145 | 2021-07-23 | 33495 | keep | 0 | Jul | 2021 | 0.022813 | 0.00015733 | Sustained | FALSE | TRUE | Not_TMED_Event | 231
AGUADILLA | 2021-07-23 10:05 | 2021-07-23 12:52 | 1 | 002:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR LINEAS SECUNDARIAS | M21072300000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 167 | 2021-07-23 | 167 | keep | 0 | Jul | 2021 | 0.00011374 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-07-23 10:06 | 2021-07-23 10:39 | 14 | 000:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C21072200103 | New_Event | Secondary Wire Down | Include | Include | Equipment | 33 | 2021-07-23 | 462 | keep | 0 | Jul | 2021 | 0.00031467 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2021-07-23 10:07 | 2021-07-23 10:08 | 10 | 000:01 | P | NO SE REPORTO CAUSA | 1 X 15 EN CORTE DE LINEA | B21072200099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-23 | 10 | keep | 0 | Jul | 2021 | 6.811e-06 | 6.811e-06 | Momentary | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-07-23 10:30 | 2021-07-23 14:00 | 8 | 003:30 | P | HERRAJE ROTO O PODRIDO | SE REMPLAZO CRUCETA PARTIDA CON TRANSFORMADOR | A21072300012 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 210 | 2021-07-23 | 1680 | keep | 0 | Jul | 2021 | 0.0011442 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-07-23 10:31 | 2021-07-23 14:07 | 8 | 003:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTE | B21072300017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 216 | 2021-07-23 | 1728 | keep | 0 | Jul | 2021 | 0.0011769 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-07-23 10:40 | 2021-07-23 11:51 | 15 | 001:11 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR POSTE SECUNDARIO | M21072300000 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 71 | 2021-07-23 | 1065 | keep | 0 | Jul | 2021 | 0.00072537 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2021-07-23 10:56 | 2021-07-23 12:14 | 80 | 001:18 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO CAUSA | R21072300012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2021-07-23 | 6240 | keep | 0 | Jul | 2021 | 0.00425 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-07-23 11:17 | 2021-07-24 13:50 | 15 | 026:33 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR 50KVA X 50KVA | B21072300014 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1593 | 2021-07-23 | 23895 | keep | 0 | Jul | 2021 | 0.016275 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-07-23 11:38 | 2021-07-23 12:43 | 8 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BARRA DE PEDESTAL | R21072300015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2021-07-23 | 520 | keep | 0 | Jul | 2021 | 0.00035417 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-07-23 11:47 | 2021-07-23 15:04 | 20 | 003:17 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR PAD-MOUNTED T-522 100KVA POR 100KVA | B21072300023 | New_Event | Service Transformer Failure | Include | Include | Equipment | 197 | 2021-07-23 | 3940 | keep | 0 | Jul | 2021 | 0.0026835 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-07-23 12:10 | 2021-07-23 14:06 | 9 | 001:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO SECUNDARIA | C21072300069 | New_Event | Secondary Wire Down | Include | Include | Equipment | 116 | 2021-07-23 | 1044 | keep | 0 | Jul | 2021 | 0.00071106 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2021-07-23 12:14 | 2021-07-23 16:40 | 3 | 004:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21072300032 | New_Event | Bad Weather | Include | Include | Weather | 266 | 2021-07-23 | 798 | keep | 0 | Jul | 2021 | 0.00054351 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
FAJARDO | 2021-07-23 12:16 | 2021-07-23 12:18 | 625 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | R21072300022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-23 | 1250 | keep | 0 | Jul | 2021 | 0.00085137 | 0.00042568 | Momentary | FALSE | FALSE | Not_TMED_Event | 625
PONCE | 2021-07-23 12:29 | 2021-07-23 18:15 | 50 | 005:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA DE CORTE DE LINEA QUEMADA | P21072300036 | New_Event | Cutout Failure | Include | Include | Equipment | 346 | 2021-07-23 | 17300 | keep | 0 | Jul | 2021 | 0.011783 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-23 12:30 | 2021-07-23 13:20 | 50 | 000:50 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE | M21072300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 50 | 2021-07-23 | 2500 | keep | 0 | Jul | 2021 | 0.0017027 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-23 12:33 | 2021-07-24 15:26 | 40 | 026:53 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA DESGANCHE | S21072300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1613 | 2021-07-23 | 64520 | keep | 0 | Jul | 2021 | 0.043944 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-07-23 12:51 | 2021-07-23 14:34 | 7 | 001:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21072300064 | New_Event | Bad Weather | Include | Include | Weather | 103 | 2021-07-23 | 721 | keep | 0 | Jul | 2021 | 0.00049107 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
HUMACAO | 2021-07-23 12:51 | 2021-07-23 18:03 | 1 | 005:12 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO CAUSA | C21072300064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 312 | 2021-07-23 | 312 | keep | 0 | Jul | 2021 | 0.0002125 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
PONCE | 2021-07-23 12:59 | 2021-07-23 15:00 | 156 | 002:01 | P | SOBRECARGA | 1 X 100 EN CORTE DE LINEA FUSIBLE FUNDE AL TRANSFERIR CARGA DE OTRO CIRCUITO | P21072300040 | New_Event | Trip Due To Overload | Include | Include | Other | 121 | 2021-07-23 | 18876 | keep | 0 | Jul | 2021 | 0.012856 | 0.00010625 | Sustained | FALSE | TRUE | Not_TMED_Event | 156
SAN JUAN | 2021-07-23 13:05 | 2021-07-24 18:15 | 35 | 029:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE DESGANCHO | R21072300025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1750 | 2021-07-23 | 61250 | keep | 0 | Jul | 2021 | 0.041717 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-07-23 13:05 | 2021-07-23 22:10 | 40 | 009:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 80 EN CORTE DE LINEA SE LEVANTO CONDUCTOR SECUNDARIO | S21072300021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 545 | 2021-07-23 | 21800 | keep | 0 | Jul | 2021 | 0.014848 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-07-23 13:24 | 2021-07-23 19:00 | 40 | 005:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 25 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A21072300020 | New_Event | Cutout Failure | Include | Include | Equipment | 336 | 2021-07-23 | 13440 | keep | 0 | Jul | 2021 | 0.0091539 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-23 13:32 | 2021-07-23 17:37 | 36 | 004:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | B21072300027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2021-07-23 | 8820 | keep | 0 | Jul | 2021 | 0.0060073 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
BAYAMON | 2021-07-23 13:37 | 2021-07-23 18:47 | 20 | 005:10 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50KVA AVERIADO POR UNO DE IGUAL CAPACIDAD | B21072300028 | New_Event | Service Transformer Failure | Include | Include | Equipment | 310 | 2021-07-23 | 6200 | keep | 0 | Jul | 2021 | 0.0042228 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2021-07-23 13:39 | 2021-07-24 13:15 | 10 | 023:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21072300037 | New_Event | Bad Weather | Include | Include | Weather | 1416 | 2021-07-23 | 14160 | keep | 0 | Jul | 2021 | 0.0096443 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-07-23 13:40 | 2021-07-23 16:50 | 12 | 003:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21072300021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 190 | 2021-07-23 | 2280 | keep | 0 | Jul | 2021 | 0.0015529 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-07-23 13:44 | 2021-07-23 16:19 | 18 | 002:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZO DE 250 PIES DE SECUNDARIA 3/4 ALUMINIO | C21072300066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 155 | 2021-07-23 | 2790 | keep | 0 | Jul | 2021 | 0.0019003 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2021-07-23 13:47 | 2021-07-23 20:30 | 50 | 006:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21072300026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 403 | 2021-07-23 | 20150 | keep | 0 | Jul | 2021 | 0.013724 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-23 13:52 | 2021-07-25 00:44 | 15 | 034:52 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR 37KVA X 37KVA | B21072300025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2092 | 2021-07-23 | 31380 | keep | 0 | Jul | 2021 | 0.021373 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2021-07-23 14:09 | 2021-07-23 15:09 | 20 | 001:00 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R21072300027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2021-07-23 | 1200 | keep | 0 | Jul | 2021 | 0.00081731 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-07-23 14:14 | 2021-07-23 18:18 | 80 | 004:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21072300047 | New_Event | Bad Weather | Include | Include | Weather | 244 | 2021-07-23 | 19520 | keep | 0 | Jul | 2021 | 0.013295 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-07-23 14:26 | 2021-07-23 17:52 | 450 | 003:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C21072300068 | New_Event |  |  | Include | Wildlife | 206 | 2021-07-23 | 92700 | keep | 0 | Jul | 2021 | 0.063138 | 0.00030649 | Sustained | FALSE | TRUE | Not_TMED_Event | 450
AGUADILLA | 2021-07-23 14:26 | 2021-07-25 16:11 | 80 | 049:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21072300049 | New_Event | Bad Weather | Include | Include | Weather | 2985 | 2021-07-23 | 238800 | keep | 0 | Jul | 2021 | 0.16265 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-07-23 14:34 | 2021-07-23 18:35 | 10 | 004:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21072300026 | New_Event | Bad Weather | Include | Include | Weather | 241 | 2021-07-23 | 2410 | keep | 0 | Jul | 2021 | 0.0016414 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-07-23 14:53 | 2021-07-23 17:24 | 150 | 002:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 Y 1 X 80 EN CORTES DE LINEA MAL TIEMPO | C21072300073 | New_Event | Bad Weather | Include | Include | Weather | 151 | 2021-07-23 | 22650 | keep | 0 | Jul | 2021 | 0.015427 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
PONCE | 2021-07-23 14:54 | 2021-07-23 18:55 | 20 | 004:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA Y 2 TOMAS | P21072300047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 241 | 2021-07-23 | 4820 | keep | 0 | Jul | 2021 | 0.0032829 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-07-23 14:56 | 2021-07-23 16:40 | 2 | 001:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | A21072300028 | New_Event | Wire Down | Include | Include | Equipment | 104 | 2021-07-23 | 208 | keep | 0 | Jul | 2021 | 0.00014167 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2021-07-23 14:57 | 2021-07-25 13:30 | 13 | 046:33 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA X LO MISMO | M21072300055 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2793 | 2021-07-23 | 36309 | keep | 0 | Jul | 2021 | 0.02473 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2021-07-23 15:30 | 2021-07-23 22:20 | 2366 | 006:50 | T | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR FUERTES VIENTOS | M21072300067 | New_Event | Bad Weather | Include | Include | Weather | 410 | 2021-07-23 | 970060 | keep | 0 | Jul | 2021 | 0.6607 | 0.0016115 | Sustained | FALSE | TRUE | Not_TMED_Event | 2366
CANOVANAS | 2021-07-23 15:34 | 2021-07-23 17:32 | 4 | 001:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | R21072300034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 118 | 2021-07-23 | 472 | keep | 0 | Jul | 2021 | 0.00032148 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-07-23 15:35 | 2021-07-23 18:35 | 5 | 003:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21072300029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 180 | 2021-07-23 | 900 | keep | 0 | Jul | 2021 | 0.00061299 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-07-23 15:43 | 2021-07-23 17:45 | 40 | 002:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21072300030 | New_Event | Bad Weather | Include | Include | Weather | 122 | 2021-07-23 | 4880 | keep | 0 | Jul | 2021 | 0.0033237 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-07-23 15:50 | 2021-07-23 17:40 | 18 | 001:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21072300018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 110 | 2021-07-23 | 1980 | keep | 0 | Jul | 2021 | 0.0013486 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
FAJARDO | 2021-07-23 16:00 | 2021-07-23 16:58 | 14 | 000:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BARRAS DE PEDESTAL | R21072300035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 58 | 2021-07-23 | 812 | keep | 0 | Jul | 2021 | 0.00055305 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2021-07-23 16:38 | 2021-07-23 19:23 | 12 | 002:45 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | S21072300032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 165 | 2021-07-23 | 1980 | keep | 0 | Jul | 2021 | 0.0013486 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-07-23 17:04 | 2021-07-23 18:18 | 20 | 001:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA Y REPARO SECUNDARIA | R21072300038 | New_Event | Wire Down | Include | Include | Equipment | 74 | 2021-07-23 | 1480 | keep | 0 | Jul | 2021 | 0.001008 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-07-23 17:16 | 2021-07-23 20:49 | 100 | 003:33 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA Y 1 X 40 EN CORTE DE LINEA | S21072300034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2021-07-23 | 21300 | keep | 0 | Jul | 2021 | 0.014507 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-07-23 17:33 | 2021-07-23 19:19 | 5 | 001:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21072300081 | New_Event | Secondary Wire Down | Include | Include | Equipment | 106 | 2021-07-23 | 530 | keep | 0 | Jul | 2021 | 0.00036098 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-07-23 17:42 | 2021-07-24 10:39 | 328 | 016:57 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR ROTO SE CERRO MACHETES | C21072300015 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1017 | 2021-07-23 | 333576 | keep | 0 | Jul | 2021 | 0.2272 | 0.0002234 | Sustained | FALSE | FALSE | Not_TMED_Event | 328
AGUADILLA | 2021-07-23 18:00 | 2021-07-23 20:20 | 100 | 002:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21072300000 | New_Event | Bad Weather | Include | Include | Weather | 140 | 2021-07-23 | 14000 | keep | 0 | Jul | 2021 | 0.0095353 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-23 18:08 | 2021-07-23 18:09 | 5961 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21072300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-23 | 5961 | keep | 0 | Jul | 2021 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2021-07-23 18:20 | 2021-07-23 19:17 | 50 | 000:57 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUAS | B21072300037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2021-07-23 | 2850 | keep | 0 | Jul | 2021 | 0.0019411 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-07-23 18:35 | 2021-07-23 18:36 | 1648 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | RECIERRE | R21072300039 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-07-23 | 1648 | keep | 0 | Jul | 2021 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2021-07-23 18:36 | 2021-07-24 09:08 | 167 | 014:32 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 100 EN CORTE DE LINEA Y 1 X 20 EN RISER TERMINACION EN RISER DE CHURCH PEGADA AL PARARRAYO | R21072300040 | 1st_after_momentary | UG - Broken Splice / Terminal | Include | Include | Equipment | 872 | 2021-07-23 | 145624 | keep | 0 | Jul | 2021 | 0.099184 | 0.00011374 | Sustained | FALSE | TRUE | Not_TMED_Event | 167
CAGUAS | 2021-07-23 19:13 | 2021-07-23 19:14 | 3005 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C21072300086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-23 | 3005 | keep | 0 | Jul | 2021 | 0.0020467 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
CAGUAS | 2021-07-23 19:19 | 2021-07-23 19:20 | 1001 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C21072300087 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-23 | 1001 | keep | 0 | Jul | 2021 | 0.00068178 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
CAGUAS | 2021-07-23 19:20 | 2021-07-23 22:08 | 200 | 002:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES PARA SECCIONALIZAR CONDUCTOR ROTO Y CERRO N/O CON EL 3403-01 | C21072300087 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 168 | 2021-07-23 | 33600 | keep | 0 | Jul | 2021 | 0.022885 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-07-23 19:27 | 2021-07-23 19:28 | 2179 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | R21072300042 | Additional_clients | Bad Weather | Include | Include | Weather | 1 | 2021-07-23 | 2179 | keep | 0 | Jul | 2021 | 0.0014841 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-23 19:28 | 2021-07-24 11:51 | 1 | 016:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN RISER MAL TIEMPO | R21072200044 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 983 | 2021-07-23 | 983 | keep | 0 | Jul | 2021 | 0.00066952 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-07-23 19:32 | 2021-07-24 09:57 | 223 | 014:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21072300090 | New_Event | Bad Weather | Include | Include | Weather | 865 | 2021-07-23 | 192895 | keep | 0 | Jul | 2021 | 0.13138 | 0.00015188 | Sustained | FALSE | TRUE | Not_TMED_Event | 223
PONCE | 2021-07-23 19:32 | 2021-07-24 11:11 | 8 | 015:39 | P | SECUNDARIA/DESGANCHE | 2 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA EN LINEA SECUNDANRIA | P21072300053 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 939 | 2021-07-23 | 7512 | keep | 0 | Jul | 2021 | 0.0051164 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
CAGUAS | 2021-07-23 19:42 | 2021-07-24 09:36 | 62 | 013:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21072300092 | New_Event | Bad Weather | Include | Include | Weather | 834 | 2021-07-23 | 51708 | keep | 0 | Jul | 2021 | 0.035218 | 4.2228e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 62
CANOVANAS | 2021-07-23 19:46 | 2021-07-23 19:48 | 635 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | R21072300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-23 | 1270 | keep | 0 | Jul | 2021 | 0.00086499 | 0.0004325 | Momentary | FALSE | FALSE | Not_TMED_Event | 635
YAUCO | 2021-07-23 19:50 | 2021-07-24 10:35 | 15 | 014:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR DESCARGA ELECTRICA | P21072300054 | New_Event | Bad Weather | Include | Include | Weather | 885 | 2021-07-23 | 13275 | keep | 0 | Jul | 2021 | 0.0090415 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-07-23 19:55 | 2021-07-24 10:50 | 2 | 014:55 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR ENREDADERA | C21072300095 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 895 | 2021-07-23 | 1790 | keep | 0 | Jul | 2021 | 0.0012192 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2021-07-23 20:02 | 2021-07-24 11:54 | 337 | 015:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO NEUTRAL | S21072300041 | New_Event | Wire Down | Include | Include | Equipment | 952 | 2021-07-23 | 320824 | keep | 0 | Jul | 2021 | 0.21851 | 0.00022953 | Sustained | FALSE | TRUE | Not_TMED_Event | 337
GUAYAMA | 2021-07-23 21:29 | 2021-07-24 08:51 | 100 | 011:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZA FASE PRIMARIA | P21072300057 | New_Event |  |  | Include | Wildlife | 682 | 2021-07-23 | 68200 | keep | 0 | Jul | 2021 | 0.046451 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-07-23 22:08 | 2021-07-24 13:20 | 97 | 015:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTORES SE CERRO MACHETES | C21072300091 | Partial_restoration | Wire Down | Include | Include | Equipment | 912 | 2021-07-23 | 88464 | keep | 0 | Jul | 2021 | 0.060252 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-23 22:40 | 2021-07-24 11:44 | 100 | 013:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 Y 1 X 80 EN CORTE DE LINEA DIFERENTES SE LEVANTO CONDUCTOR | B21072300051 | New_Event | Wire Down | Include | Include | Equipment | 784 | 2021-07-23 | 78400 | keep | 0 | Jul | 2021 | 0.053398 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-07-24 00:07 | 2021-07-24 09:35 | 90 | 009:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN RISER CRUCE POR RATA | C21072400001 | New_Event |  |  | Include | Wildlife | 568 | 2021-07-24 | 51120 | keep | 0 | Jul | 2021 | 0.034818 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
ARECIBO | 2021-07-24 00:19 | 2021-07-24 11:08 | 16 | 010:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR CAMION IMPACTO POSTE | A21072400001 | New_Event |  |  | Include | Wildlife | 649 | 2021-07-24 | 10384 | keep | 0 | Jul | 2021 | 0.0070725 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
ARECIBO | 2021-07-24 00:37 | 2021-07-24 15:45 | 125 | 015:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES QUEMADO | A21072400003 | New_Event | Cutout Failure | Include | Include | Equipment | 908 | 2021-07-24 | 113500 | keep | 0 | Jul | 2021 | 0.077304 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
ARECIBO | 2021-07-24 00:56 | 2021-07-24 09:32 | 100 | 008:36 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | A21072400004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 516 | 2021-07-24 | 51600 | keep | 0 | Jul | 2021 | 0.035145 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-24 02:01 | 2021-07-24 02:02 | 5800 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04 LLEVA LA CARGA DEL 1620-01 QUE A SU VEZ LLEVA EL 90% DEL 1336-07 Y 85% DEL 1336-10 | S21072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-24 | 5800 | keep | 0 | Jul | 2021 | 0.0039504 | 0.0039504 | Momentary | FALSE | FALSE | Not_TMED_Event | 5800
SAN JUAN | 2021-07-24 02:01 | 2021-07-24 02:02 | 350 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04 QUE A SU VEZ LLEVA LA CARGA DEL 1620-01 QUE A SU VEZ LLEVA EL 90% DEL 1336-07 Y 85% DEL 1336-10 | S21072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-24 | 350 | keep | 0 | Jul | 2021 | 0.00023838 | 0.00023838 | Momentary | FALSE | FALSE | Not_TMED_Event | 350
SAN JUAN | 2021-07-24 02:01 | 2021-07-24 02:02 | 1825 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-24 | 1825 | keep | 0 | Jul | 2021 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2021-07-24 02:01 | 2021-07-24 02:02 | 36 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04 QUE LLEVA LA CARGA DEL 1620-01 QUE A SU VEZ LLEVA EL 90% DEL 1336-07 Y 85% DEL 1336-10 | S21072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-24 | 36 | keep | 0 | Jul | 2021 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-07-24 02:01 | 2021-07-24 02:02 | 172 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04 QUE LLEVA LA CARGA DEL 1620-01 QUE A SU VEZ LLEVA EL 90% DEL 1336-07 Y 85% DEL 1336-10 | S21072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-24 | 172 | keep | 0 | Jul | 2021 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
ARECIBO | 2021-07-24 02:01 | 2021-07-24 16:50 | 50 | 014:49 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSOS | A21072400006 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 889 | 2021-07-24 | 44450 | keep | 0 | Jul | 2021 | 0.030275 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-07-24 02:14 | 2021-07-24 02:15 | 3387 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | B21072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-24 | 3387 | keep | 0 | Jul | 2021 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
ARECIBO | 2021-07-24 02:29 | 2021-07-24 09:23 | 2756 | 006:54 | T | ANIMAL U OBJETO EXTRAÃ‘O | VEHICULO IMPACTO POSTE | A21072400009 | New_Event |  |  | Include | Wildlife | 414 | 2021-07-24 | 1140984 | keep | 0 | Jul | 2021 | 0.77712 | 0.0018771 | Sustained | FALSE | FALSE | Not_TMED_Event | 2756
VEGA BAJA | 2021-07-24 02:34 | 2021-07-24 09:38 | 200 | 007:04 | P | OTRAS CAUSAS | 1 X 200 EN CORTE DE LINEA SE SECCIONALIZO MONTURA PRIVADA CON AVERIA | B21072400002 | New_Event | Other Causes | Include | Include | Other | 424 | 2021-07-24 | 84800 | keep | 0 | Jul | 2021 | 0.057757 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-07-24 03:53 | 2021-07-24 13:30 | 150 | 009:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA REPARO LINEA PRIMARIA PARTIDA | A21072400016 | New_Event | Wire Down | Include | Include | Equipment | 577 | 2021-07-24 | 86550 | keep | 0 | Jul | 2021 | 0.058949 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
UTUADO | 2021-07-24 04:11 | 2021-07-24 17:23 | 8 | 013:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21072400068 | New_Event | Bad Weather | Include | Include | Weather | 792 | 2021-07-24 | 6336 | keep | 0 | Jul | 2021 | 0.0043154 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2021-07-24 04:18 | 2021-07-24 04:19 | 464 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | P21072400001 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-07-24 | 464 | keep | 0 | Jul | 2021 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2021-07-24 04:19 | 2021-07-24 09:28 | 15 | 005:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO CAJA EN TRANSFORMADOR | P21072400002 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 309 | 2021-07-24 | 4635 | keep | 0 | Jul | 2021 | 0.0031569 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-07-24 04:42 | 2021-07-24 04:45 | 723 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA LLEVANDO CARGA DEL 1711-05 | B21072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-07-24 | 2169 | keep | 0 | Jul | 2021 | 0.0014773 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2021-07-24 04:43 | 2021-07-24 04:45 | 1588 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA LLEVANDO LA CARGA DEL 1711-03 | B21072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-24 | 3176 | keep | 0 | Jul | 2021 | 0.0021632 | 0.0010816 | Momentary | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2021-07-24 04:43 | 2021-07-24 04:45 | 13 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA CARGA POR EL 1711-01 | B21072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-24 | 26 | keep | 0 | Jul | 2021 | 1.7708e-05 | 8.8542e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2021-07-24 04:45 | 2021-07-24 04:46 | 1976 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA CARGA POR EL 1711-02 | B21072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-24 | 1976 | keep | 0 | Jul | 2021 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2021-07-24 04:55 | 2021-07-24 04:57 | 1983 | 000:02 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL CARGA POR EL 1801-02 | B21072400016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-07-24 | 3966 | keep | 0 | Jul | 2021 | 0.0027012 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-07-24 04:55 | 2021-07-24 04:57 | 186 | 000:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA LLEVANDO LA CARGA DEL 1711-04 | B21072400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-07-24 | 372 | keep | 0 | Jul | 2021 | 0.00025337 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2021-07-24 05:01 | 2021-07-24 05:02 | 1983 | 000:01 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL CARGA POR EL 1801-02 | B21072400016 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-24 | 1983 | keep | 0 | Jul | 2021 | 0.0013506 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-07-24 05:01 | 2021-07-24 05:02 | 186 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA LLEVANDO LA CARGA DEL 1711-04 | B21072400000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-24 | 186 | keep | 0 | Jul | 2021 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
SAN JUAN | 2021-07-24 05:14 | 2021-07-24 05:15 | 870 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S21072400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-24 | 870 | keep | 0 | Jul | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2021-07-24 05:44 | 2021-07-24 05:45 | 1983 | 000:01 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL CARGA POR EL 1801-02 | B21072400016 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-24 | 1983 | keep | 0 | Jul | 2021 | 0.0013506 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-07-24 05:44 | 2021-07-24 05:45 | 186 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR LLEVANDO LA CARGA DEL 1711-04 | B21072400013 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-24 | 186 | keep | 0 | Jul | 2021 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2021-07-24 06:23 | 2021-07-24 06:24 | 1983 | 000:01 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL CARGA POR EL 1801-02 | B21072400016 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-24 | 1983 | keep | 0 | Jul | 2021 | 0.0013506 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-07-24 06:23 | 2021-07-24 06:24 | 186 | 000:01 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL LLEVANDO LA CARGA DEL 1711-04 | B21072400016 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-24 | 186 | keep | 0 | Jul | 2021 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2021-07-24 06:24 | 2021-07-24 06:25 | 1983 | 000:01 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL CARGA POR EL 1801-02 | B21072400016 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-24 | 1983 | keep | 0 | Jul | 2021 | 0.0013506 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-07-24 06:24 | 2021-07-24 06:25 | 186 | 000:01 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL LLEVANDO LA CARGA DEL 1711-04 | B21072400016 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-24 | 186 | keep | 0 | Jul | 2021 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2021-07-24 06:26 | 2021-07-24 08:09 | 1983 | 001:43 | T | DESGANCHE | SE CERRO MACHETES Y SE DIO SERVICIO CARGA POR EL 1801-02 | B21072400016 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 103 | 2021-07-24 | 204249 | keep | 0 | Jul | 2021 | 0.13911 | 0.0013506 | Sustained | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-07-24 06:26 | 2021-07-24 07:36 | 186 | 001:10 | T | DESGANCHE | SE SECCIONALIZO ALIMENTADOR LLEVANDO LA CARGA DEL 1711-04 | B21072400016 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 70 | 2021-07-24 | 13020 | keep | 0 | Jul | 2021 | 0.0088679 | 0.00012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 186
SAN JUAN | 2021-07-24 06:33 | 2021-07-24 07:54 | 1381 | 001:21 | T | NO SE REPORTO CAUSA | DISPARO 1206-04 LLEVANDO LA CARGA DEL 1204-03 SE PATRULLO Y SE CERRO PERO NO SE ENCONTRO CAUSA | S21072400010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2021-07-24 | 111861 | keep | 0 | Jul | 2021 | 0.076188 | 0.00094059 | Sustained | FALSE | FALSE | Not_TMED_Event | 1381
SAN JUAN | 2021-07-24 06:33 | 2021-07-24 07:54 | 1799 | 001:21 | T | NO SE REPORTO CAUSA | DISPARO 1206-04 LLEVANDO LA CARGA DEL 1204-03 SE PATRULLO Y SE CERRO PERO NO SE ENCONTRO CAUSA | S21072400010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2021-07-24 | 145719 | keep | 0 | Jul | 2021 | 0.099249 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2021-07-24 06:42 | 2021-07-24 06:43 | 870 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S21072400000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-24 | 870 | keep | 0 | Jul | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2021-07-24 06:48 | 2021-07-24 06:49 | 1447 | 000:01 | T | CABLE SOTERRADO AVERIADO | DISPARO Y SE CERRO POR SCADA LLEVA LA CARGA DEL 1419-09 | S21072400000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2021-07-24 | 1447 | keep | 0 | Jul | 2021 | 0.00098555 | 0.00098555 | Momentary | FALSE | FALSE | Not_TMED_Event | 1447
SAN JUAN | 2021-07-24 06:48 | 2021-07-24 06:49 | 266 | 000:01 | T | CABLE SOTERRADO AVERIADO | DISPARO 1112-04 LLEVANDO LA CARGA DEL 1419-09 | S21072400000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2021-07-24 | 266 | keep | 0 | Jul | 2021 | 0.00018117 | 0.00018117 | Momentary | FALSE | FALSE | Not_TMED_Event | 266
SAN JUAN | 2021-07-24 06:49 | 2021-07-25 10:42 | 20 | 027:53 | P | CABLE SOTERRADO AVERIADO | SE CERRO N/O DEL T-2 @ T-3 AVERIADO DE SU-1 @ T-3 | S21072400021 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 1673 | 2021-07-24 | 33460 | keep | 0 | Jul | 2021 | 0.022789 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-07-24 06:55 | 2021-07-24 09:49 | 651 | 002:54 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE PATRULLO Y NO SE ENCONTRO CAUSA. SE CERRO POR CONTROL | B21072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2021-07-24 | 113274 | keep | 0 | Jul | 2021 | 0.07715 | 0.00044339 | Sustained | FALSE | FALSE | Not_TMED_Event | 651
BAYAMON | 2021-07-24 07:21 | 2021-07-24 10:27 | 75 | 003:06 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21072400021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 186 | 2021-07-24 | 13950 | keep | 0 | Jul | 2021 | 0.0095013 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-07-24 07:21 | 2021-07-24 16:28 | 27 | 009:07 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21072400020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 547 | 2021-07-24 | 14769 | keep | 0 | Jul | 2021 | 0.010059 | 1.839e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 27
MAYAGÃœEZ | 2021-07-24 07:22 | 2021-07-24 11:00 | 50 | 003:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21072400002 | New_Event | Bad Weather | Include | Include | Weather | 218 | 2021-07-24 | 10900 | keep | 0 | Jul | 2021 | 0.0074239 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-07-24 07:26 | 2021-07-24 09:37 | 509 | 002:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO | C21072400006 | New_Event | Bad Weather | Include | Include | Weather | 131 | 2021-07-24 | 66679 | keep | 0 | Jul | 2021 | 0.045415 | 0.00034668 | Sustained | FALSE | TRUE | Not_TMED_Event | 509
BAYAMON | 2021-07-24 07:36 | 2021-07-24 10:44 | 52 | 003:08 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRARON MACHETES PREVIAMENTE ABIERTOS | B21061700000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 188 | 2021-07-24 | 9776 | keep | 0 | Jul | 2021 | 0.0066584 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-07-24 07:40 | 2021-07-24 17:05 | 52 | 009:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE LLEVO PUENTE A CAJA | B21072400020 | New_Event | Cutout Failure | Include | Include | Equipment | 565 | 2021-07-24 | 29380 | keep | 0 | Jul | 2021 | 0.020011 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
SAN JUAN | 2021-07-24 07:45 | 2021-07-24 09:42 | 870 | 001:57 | T | DESGANCHE | SE REALIZO DESGANCHE DE BAMBUAS Y SE CERRO POR SCADA | S21072400000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 117 | 2021-07-24 | 101790 | keep | 0 | Jul | 2021 | 0.069329 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2021-07-24 07:58 | 2021-07-24 15:51 | 16 | 007:53 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21072400026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 473 | 2021-07-24 | 7568 | keep | 0 | Jul | 2021 | 0.0051545 | 1.0898e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 16
SAN JUAN | 2021-07-24 08:00 | 2021-07-24 11:20 | 35 | 003:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN RISER SE LEVANTO PROVISIONAL AEREO | S21072400039 | New_Event | Wire Down | Include | Include | Equipment | 200 | 2021-07-24 | 7000 | keep | 0 | Jul | 2021 | 0.0047677 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2021-07-24 08:02 | 2021-07-24 17:30 | 160 | 009:28 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 2 X 80 EN CORTE DE LINEA 1 X 65 EN CORTE DE LINEA SE REPARO BUSHING Y PISTOLA | S21072400040 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 568 | 2021-07-24 | 90880 | keep | 0 | Jul | 2021 | 0.061898 | 0.00010898 | Sustained | FALSE | TRUE | Not_TMED_Event | 160
SAN JUAN | 2021-07-24 08:07 | 2021-07-24 15:20 | 180 | 007:13 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | R21072400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 433 | 2021-07-24 | 77940 | keep | 0 | Jul | 2021 | 0.053085 | 0.0001226 | Sustained | FALSE | TRUE | Not_TMED_Event | 180
BAYAMON | 2021-07-24 08:13 | 2021-07-24 08:36 | 1812 | 000:23 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21072400037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 23 | 2021-07-24 | 41676 | keep | 0 | Jul | 2021 | 0.028385 | 0.0012341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1812
CANOVANAS | 2021-07-24 08:14 | 2021-07-24 10:13 | 12 | 001:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR REPTIL | R21072400003 | New_Event |  |  | Include | Wildlife | 119 | 2021-07-24 | 1428 | keep | 0 | Jul | 2021 | 0.0009726 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
YAUCO | 2021-07-24 08:16 | 2021-07-24 08:17 | 1352 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR CARGA POR 5602-02 | P21072400003 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-07-24 | 1352 | keep | 0 | Jul | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
YAUCO | 2021-07-24 08:16 | 2021-07-24 08:17 | 3973 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR | P21072400003 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-07-24 | 3973 | keep | 0 | Jul | 2021 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
BAYAMON | 2021-07-24 08:18 | 2021-07-24 11:49 | 60 | 003:31 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21072400040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2021-07-24 | 12660 | keep | 0 | Jul | 2021 | 0.0086227 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BARRANQUITAS | 2021-07-24 08:51 | 2021-07-24 14:17 | 50 | 005:26 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA REMPLAZO AISLADOR | C21072400018 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 326 | 2021-07-24 | 16300 | keep | 0 | Jul | 2021 | 0.011102 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-24 09:01 | 2021-07-24 10:17 | 5 | 001:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZO DE BARRA EN PEDESTAL | C21072400012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 76 | 2021-07-24 | 380 | keep | 0 | Jul | 2021 | 0.00025882 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-07-24 09:04 | 2021-07-24 09:05 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21072400007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-24 | 3718 | keep | 0 | Jul | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
AGUADILLA | 2021-07-24 09:10 | 2021-07-24 17:30 | 135 | 008:20 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE MASIVO POR PERSONAL DE XPERTS | M21072200075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 500 | 2021-07-24 | 67500 | keep | 0 | Jul | 2021 | 0.045974 | 9.1948e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 135
SAN JUAN | 2021-07-24 09:19 | 2021-07-24 18:10 | 50 | 008:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO INTERRUPTOR POR SEGURIDAD PARA REMPLAZO DE CAJA PRIMARIA | S21072400060 | New_Event | Cutout Failure | Include | Include | Equipment | 531 | 2021-07-24 | 26550 | keep | 0 | Jul | 2021 | 0.018083 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-07-24 09:19 | 2021-07-24 10:47 | 38 | 001:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21072400024 | New_Event | Bad Weather | Include | Include | Weather | 88 | 2021-07-24 | 3344 | keep | 0 | Jul | 2021 | 0.0022776 | 2.5882e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 38
CAGUAS | 2021-07-24 09:19 | 2021-07-24 12:23 | 381 | 003:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 Y 1 X 80 EN CORTES DE LINEA CRUCE POR AVE | C21072400023 | New_Event |  |  | Include | Wildlife | 184 | 2021-07-24 | 70104 | keep | 0 | Jul | 2021 | 0.047748 | 0.0002595 | Sustained | FALSE | TRUE | Not_TMED_Event | 381
BAYAMON | 2021-07-24 09:23 | 2021-07-24 10:35 | 60 | 001:12 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21072400062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2021-07-24 | 4320 | keep | 0 | Jul | 2021 | 0.0029423 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-07-24 09:23 | 2021-07-24 16:20 | 2456 | 006:57 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO SE CERRO MACHETES | A21072400014 | New_Event | Defective Pole | Include | Include | Equipment | 417 | 2021-07-24 | 1024152 | keep | 0 | Jul | 2021 | 0.69755 | 0.0016728 | Sustained | FALSE | FALSE | Not_TMED_Event | 2456
CANOVANAS | 2021-07-24 09:37 | 2021-07-24 10:11 | 12 | 000:34 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR CONECTOR | R21072400001 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 34 | 2021-07-24 | 408 | keep | 0 | Jul | 2021 | 0.00027789 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-07-24 09:46 | 2021-07-24 12:30 | 15 | 002:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES | A21072300027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 164 | 2021-07-24 | 2460 | keep | 0 | Jul | 2021 | 0.0016755 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-07-24 09:47 | 2021-07-24 09:48 | 222 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO LLEVA EL 99% DEL 1909-09 | S21072400072 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-24 | 222 | keep | 0 | Jul | 2021 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2021-07-24 09:47 | 2021-07-24 09:48 | 4411 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO 99% DE LA CARGA POR EL 1907-03 | S21072400072 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-24 | 4411 | keep | 0 | Jul | 2021 | 0.0030043 | 0.0030043 | Momentary | FALSE | FALSE | Not_TMED_Event | 4411
BAYAMON | 2021-07-24 09:48 | 2021-07-24 15:02 | 150 | 005:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO EN MACHETE | S21072400074 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 314 | 2021-07-24 | 47100 | keep | 0 | Jul | 2021 | 0.03208 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-07-24 09:52 | 2021-07-25 11:52 | 100 | 025:60 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | M21072500022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1560 | 2021-07-24 | 156000 | keep | 0 | Jul | 2021 | 0.10625 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-24 10:01 | 2021-07-24 14:13 | 175 | 004:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | R21072400009 | New_Event | Bad Weather | Include | Include | Weather | 252 | 2021-07-24 | 44100 | keep | 0 | Jul | 2021 | 0.030036 | 0.00011919 | Sustained | FALSE | TRUE | Not_TMED_Event | 175
CAGUAS | 2021-07-24 10:09 | 2021-07-24 12:51 | 4 | 002:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REEMPLAZO 400 PIES DE SECUNDARIA | C21072300010 | New_Event | Secondary Wire Down | Include | Include | Equipment | 162 | 2021-07-24 | 648 | keep | 0 | Jul | 2021 | 0.00044135 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2021-07-24 10:09 | 2021-07-24 10:10 | 1352 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | P21072400043 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-07-24 | 1352 | keep | 0 | Jul | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
PONCE | 2021-07-24 10:11 | 2021-07-24 10:43 | 562 | 000:32 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV JUANA DIAZ TC | P21072400036 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 32 | 2021-07-24 | 17984 | keep | 0 | Jul | 2021 | 0.012249 | 0.00038278 | Sustained | FALSE | FALSE | Not_TMED_Event | 562
PONCE | 2021-07-24 10:11 | 2021-07-24 10:43 | 688 | 000:32 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV JUANA DIAZ TC | P21072400036 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 32 | 2021-07-24 | 22016 | keep | 0 | Jul | 2021 | 0.014995 | 0.00046859 | Sustained | FALSE | FALSE | Not_TMED_Event | 688
PONCE | 2021-07-24 10:11 | 2021-07-24 10:43 | 658 | 000:32 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV JUANA DIAZ TC | P21072400036 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 32 | 2021-07-24 | 21056 | keep | 0 | Jul | 2021 | 0.014341 | 0.00044816 | Sustained | FALSE | FALSE | Not_TMED_Event | 658
PONCE | 2021-07-24 10:11 | 2021-07-24 10:28 | 1717 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 300 | P21072400037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2021-07-24 | 29189 | keep | 0 | Jul | 2021 | 0.01988 | 0.0011694 | Sustained | FALSE | TRUE | Not_TMED_Event | 1717
PONCE | 2021-07-24 10:11 | 2021-07-24 10:28 | 974 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 300 | P21072400037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2021-07-24 | 16558 | keep | 0 | Jul | 2021 | 0.011278 | 0.00066339 | Sustained | FALSE | TRUE | Not_TMED_Event | 974
PONCE | 2021-07-24 10:11 | 2021-07-24 10:28 | 1905 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 300 | P21072400037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2021-07-24 | 32385 | keep | 0 | Jul | 2021 | 0.022057 | 0.0012975 | Sustained | FALSE | TRUE | Not_TMED_Event | 1905
PONCE | 2021-07-24 10:11 | 2021-07-24 10:28 | 1262 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 300 | P21072400037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2021-07-24 | 21454 | keep | 0 | Jul | 2021 | 0.014612 | 0.00085954 | Sustained | FALSE | TRUE | Not_TMED_Event | 1262
PONCE | 2021-07-24 10:11 | 2021-07-24 10:28 | 200 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 300 | P21072400037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2021-07-24 | 3400 | keep | 0 | Jul | 2021 | 0.0023157 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
PONCE | 2021-07-24 10:11 | 2021-07-24 10:43 | 4009 | 000:32 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38KV JUANA DIAZ TC | P21072400035 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 32 | 2021-07-24 | 128288 | keep | 0 | Jul | 2021 | 0.087376 | 0.0027305 | Sustained | FALSE | FALSE | Not_TMED_Event | 4009
PONCE | 2021-07-24 10:11 | 2021-07-24 10:28 | 222 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 300 | P21072400031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2021-07-24 | 3774 | keep | 0 | Jul | 2021 | 0.0025705 | 0.0001512 | Sustained | FALSE | TRUE | Not_TMED_Event | 222
PONCE | 2021-07-24 10:11 | 2021-07-24 10:28 | 537 | 000:17 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 300 | P21072400031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2021-07-24 | 9129 | keep | 0 | Jul | 2021 | 0.0062177 | 0.00036575 | Sustained | FALSE | TRUE | Not_TMED_Event | 537
SAN JUAN | 2021-07-24 10:13 | 2021-07-24 14:26 | 11 | 004:13 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHE | R21072400011 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 253 | 2021-07-24 | 2783 | keep | 0 | Jul | 2021 | 0.0018955 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2021-07-24 10:21 | 2021-07-24 15:21 | 52 | 005:00 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO TERMINACION | B21072400085 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 300 | 2021-07-24 | 15600 | keep | 0 | Jul | 2021 | 0.010625 | 3.5417e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 52
BAYAMON | 2021-07-24 10:23 | 2021-07-24 12:06 | 10 | 001:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA EN VARIOS PUNTOS | S21072300003 | New_Event | Secondary Wire Down | Include | Include | Equipment | 103 | 2021-07-24 | 1030 | keep | 0 | Jul | 2021 | 0.00070153 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-24 10:28 | 2021-07-24 21:30 | 1825 | 011:02 | T | LINEA DE TRANSMISION | SE ABRIO INTERRUPTOR PARA TRABAJOS EN TORRE DE LINEA LINEA 50500 POR AVERIA EN TUBERIA AAA | M21072400024 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 662 | 2021-07-24 | 1208150 | keep | 0 | Jul | 2021 | 0.82287 | 0.001243 | Sustained | FALSE | TRUE | Not_TMED_Event | 1825
MAYAGÃœEZ | 2021-07-24 10:31 | 2021-07-24 15:47 | 300 | 005:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21072400025 | New_Event | Bad Weather | Include | Include | Weather | 316 | 2021-07-24 | 94800 | keep | 0 | Jul | 2021 | 0.064568 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
FAJARDO | 2021-07-24 10:40 | 2021-07-24 12:03 | 3003 | 001:23 | T | DESGANCHE | DISPARO INTERRUPTOR SE RETIRO RAMA DE LA LINEA CERRADO POR CONTROL | R21072400013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2021-07-24 | 249249 | keep | 0 | Jul | 2021 | 0.16976 | 0.0020453 | Sustained | FALSE | TRUE | Not_TMED_Event | 3003
SAN JUAN | 2021-07-24 10:41 | 2021-07-24 10:42 | 870 | 000:01 | T | DESGANCHE | DISPARO Y SE CERRO POR SCADA | S21072400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-24 | 870 | keep | 0 | Jul | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2021-07-24 10:44 | 2021-07-24 10:46 | 1983 | 000:02 | T | DESGANCHE | DISPARO HACIENDO OPERACIONES CARGA POR EL 1801-02 | B21072400016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-07-24 | 3966 | keep | 0 | Jul | 2021 | 0.0027012 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-07-24 10:44 | 2021-07-24 10:46 | 186 | 000:02 | T | DESGANCHE | SE SECCIONALIZO ALIMENTADOR LLEVANDO LA CARGA DEL 1711-04 | B21072400016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-07-24 | 372 | keep | 0 | Jul | 2021 | 0.00025337 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
YAUCO | 2021-07-24 10:54 | 2021-07-24 10:58 | 591 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072400042 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 2364 | keep | 0 | Jul | 2021 | 0.0016101 | 0.00040253 | Momentary | FALSE | TRUE | Not_TMED_Event | 591
YAUCO | 2021-07-24 10:54 | 2021-07-24 10:58 | 1924 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072400044 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 7696 | keep | 0 | Jul | 2021 | 0.0052417 | 0.0013104 | Momentary | FALSE | TRUE | Not_TMED_Event | 1924
YAUCO | 2021-07-24 10:54 | 2021-07-24 10:58 | 968 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072400044 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 3872 | keep | 0 | Jul | 2021 | 0.0026372 | 0.0006593 | Momentary | FALSE | TRUE | Not_TMED_Event | 968
YAUCO | 2021-07-24 10:54 | 2021-07-24 10:58 | 680 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072400044 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 2720 | keep | 0 | Jul | 2021 | 0.0018526 | 0.00046314 | Momentary | FALSE | TRUE | Not_TMED_Event | 680
YAUCO | 2021-07-24 10:54 | 2021-07-24 10:58 | 2246 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072400044 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 8984 | keep | 0 | Jul | 2021 | 0.006119 | 0.0015297 | Momentary | FALSE | TRUE | Not_TMED_Event | 2246
YAUCO | 2021-07-24 10:54 | 2021-07-24 10:58 | 2470 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072400045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 9880 | keep | 0 | Jul | 2021 | 0.0067292 | 0.0016823 | Momentary | FALSE | TRUE | Not_TMED_Event | 2470
YAUCO | 2021-07-24 10:54 | 2021-07-24 10:58 | 1182 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072400045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 4728 | keep | 0 | Jul | 2021 | 0.0032202 | 0.00080505 | Momentary | FALSE | TRUE | Not_TMED_Event | 1182
YAUCO | 2021-07-24 10:54 | 2021-07-24 10:58 | 2340 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072400045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 9360 | keep | 0 | Jul | 2021 | 0.0063751 | 0.0015938 | Momentary | FALSE | TRUE | Not_TMED_Event | 2340
YAUCO | 2021-07-24 10:54 | 2021-07-24 10:58 | 1637 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072400045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 6548 | keep | 0 | Jul | 2021 | 0.0044598 | 0.001115 | Momentary | FALSE | TRUE | Not_TMED_Event | 1637
YAUCO | 2021-07-24 10:54 | 2021-07-24 10:58 | 1475 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072400046 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 5900 | keep | 0 | Jul | 2021 | 0.0040185 | 0.0010046 | Momentary | FALSE | TRUE | Not_TMED_Event | 1475
YAUCO | 2021-07-24 10:54 | 2021-07-24 10:58 | 661 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072400046 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 2644 | keep | 0 | Jul | 2021 | 0.0018008 | 0.0004502 | Momentary | FALSE | TRUE | Not_TMED_Event | 661
YAUCO | 2021-07-24 10:54 | 2021-07-24 10:58 | 1569 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072400047 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 6276 | keep | 0 | Jul | 2021 | 0.0042746 | 0.0010686 | Momentary | FALSE | TRUE | Not_TMED_Event | 1569
YAUCO | 2021-07-24 10:54 | 2021-07-24 10:58 | 2309 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072400047 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 9236 | keep | 0 | Jul | 2021 | 0.0062906 | 0.0015726 | Momentary | FALSE | TRUE | Not_TMED_Event | 2309
YAUCO | 2021-07-24 10:54 | 2021-07-24 10:58 | 2179 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072400047 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 8716 | keep | 0 | Jul | 2021 | 0.0059364 | 0.0014841 | Momentary | FALSE | TRUE | Not_TMED_Event | 2179
YAUCO | 2021-07-24 10:54 | 2021-07-24 10:58 | 2440 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072400047 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 9760 | keep | 0 | Jul | 2021 | 0.0066475 | 0.0016619 | Momentary | FALSE | TRUE | Not_TMED_Event | 2440
YAUCO | 2021-07-24 10:54 | 2021-07-24 10:58 | 1352 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072400043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 5408 | keep | 0 | Jul | 2021 | 0.0036834 | 0.00092084 | Momentary | FALSE | TRUE | Not_TMED_Event | 1352
YAUCO | 2021-07-24 10:54 | 2021-07-24 10:58 | 3973 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072400043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 15892 | keep | 0 | Jul | 2021 | 0.010824 | 0.002706 | Momentary | FALSE | TRUE | Not_TMED_Event | 3973
YAUCO | 2021-07-24 10:54 | 2021-07-24 10:58 | 2484 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072400043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 9936 | keep | 0 | Jul | 2021 | 0.0067674 | 0.0016918 | Momentary | FALSE | TRUE | Not_TMED_Event | 2484
MAYAGÃœEZ | 2021-07-24 10:54 | 2021-07-24 10:58 | 281 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | M21072400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 1124 | keep | 0 | Jul | 2021 | 0.00076555 | 0.00019139 | Momentary | FALSE | TRUE | Not_TMED_Event | 281
MAYAGÃœEZ | 2021-07-24 10:54 | 2021-07-24 10:58 | 1252 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | M21072400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 5008 | keep | 0 | Jul | 2021 | 0.0034109 | 0.00085273 | Momentary | FALSE | TRUE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2021-07-24 10:54 | 2021-07-24 10:55 | 1268 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1200 | M21072400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-24 | 1268 | keep | 0 | Jul | 2021 | 0.00086363 | 0.00086363 | Momentary | FALSE | TRUE | Not_TMED_Event | 1268
MAYAGÃœEZ | 2021-07-24 10:54 | 2021-07-24 10:55 | 2064 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1200 | M21072400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-24 | 2064 | keep | 0 | Jul | 2021 | 0.0014058 | 0.0014058 | Momentary | FALSE | TRUE | Not_TMED_Event | 2064
MAYAGÃœEZ | 2021-07-24 10:54 | 2021-07-24 10:55 | 3036 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1200 | M21072400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-24 | 3036 | keep | 0 | Jul | 2021 | 0.0020678 | 0.0020678 | Momentary | FALSE | TRUE | Not_TMED_Event | 3036
MAYAGÃœEZ | 2021-07-24 10:54 | 2021-07-24 10:55 | 2952 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1200 | M21072400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-24 | 2952 | keep | 0 | Jul | 2021 | 0.0020106 | 0.0020106 | Momentary | FALSE | TRUE | Not_TMED_Event | 2952
MAYAGÃœEZ | 2021-07-24 10:54 | 2021-07-24 10:58 | 595 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | M21072400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 2380 | keep | 0 | Jul | 2021 | 0.001621 | 0.00040525 | Momentary | FALSE | TRUE | Not_TMED_Event | 595
MAYAGÃœEZ | 2021-07-24 10:54 | 2021-07-24 10:58 | 51 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | M21072400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 204 | keep | 0 | Jul | 2021 | 0.00013894 | 3.4736e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 51
MAYAGÃœEZ | 2021-07-24 10:54 | 2021-07-24 10:58 | 721 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | M21072400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 2884 | keep | 0 | Jul | 2021 | 0.0019643 | 0.00049107 | Momentary | FALSE | TRUE | Not_TMED_Event | 721
UTUADO | 2021-07-24 10:54 | 2021-07-24 10:58 | 1382 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | A21072400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 5528 | keep | 0 | Jul | 2021 | 0.0037651 | 0.00094127 | Momentary | FALSE | TRUE | Not_TMED_Event | 1382
UTUADO | 2021-07-24 10:54 | 2021-07-24 10:58 | 654 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | A21072400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-07-24 | 2616 | keep | 0 | Jul | 2021 | 0.0017817 | 0.00044544 | Momentary | FALSE | TRUE | Not_TMED_Event | 654
AGUADILLA | 2021-07-24 10:55 | 2021-07-24 10:56 | 4882 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M21072400033 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-24 | 4882 | keep | 0 | Jul | 2021 | 0.0033251 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
AGUADILLA | 2021-07-24 10:56 | 2021-07-24 15:04 | 80 | 004:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEAS | M21072400040 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 248 | 2021-07-24 | 19840 | keep | 0 | Jul | 2021 | 0.013513 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-07-24 10:58 | 2021-07-24 16:40 | 10 | 005:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21072200065 | Partial_restoration | Bad Weather | Include | Include | Weather | 342 | 2021-07-24 | 3420 | keep | 0 | Jul | 2021 | 0.0023293 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-07-24 11:00 | 2021-07-24 15:30 | 60 | 004:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO MONTURA DE TRANSFORMADORES PARA REPARAR CONECCIONES | A21072400000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 270 | 2021-07-24 | 16200 | keep | 0 | Jul | 2021 | 0.011034 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2021-07-24 11:03 | 2021-07-24 15:30 | 12 | 004:27 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE DESGANCHO | R21072400016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 267 | 2021-07-24 | 3204 | keep | 0 | Jul | 2021 | 0.0021822 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
CAGUAS | 2021-07-24 11:07 | 2021-07-24 12:43 | 35 | 001:36 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | C21072400033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2021-07-24 | 3360 | keep | 0 | Jul | 2021 | 0.0022885 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-07-24 11:08 | 2021-07-24 11:18 | 150 | 000:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CAMION IMPACTO POSTE CRUZANDO LAS LINEAS MOMENTANEAMENTE | A21072400040 | Additional_clients |  |  | Include | Wildlife | 10 | 2021-07-24 | 1500 | keep | 0 | Jul | 2021 | 0.0010216 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-07-24 11:10 | 2021-07-24 14:03 | 60 | 002:53 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21072400081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 173 | 2021-07-24 | 10380 | keep | 0 | Jul | 2021 | 0.0070698 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-07-24 11:17 | 2021-07-24 15:21 | 171 | 004:04 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA Y 2 X 80 EN RISER MAL TIEMPO | C21072400034 | New_Event | Bad Weather | Include | Include | Weather | 244 | 2021-07-24 | 41724 | keep | 0 | Jul | 2021 | 0.028418 | 0.00011647 | Sustained | FALSE | TRUE | Not_TMED_Event | 171
CAGUAS | 2021-07-24 11:29 | 2021-07-24 13:15 | 1 | 001:46 | P | SECUNDARIA/DESGANCHE | 2 X 10 EN BANCO DE TRANSFORMADORES SE REALIZO DESGANCHE | C21072400036 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 106 | 2021-07-24 | 106 | keep | 0 | Jul | 2021 | 7.2196e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-07-24 11:31 | 2021-07-24 16:55 | 70 | 005:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN RISER SE REEMPLAZO CAJA PRIMARIA | R21072400024 | New_Event | Cutout Failure | Include | Include | Equipment | 324 | 2021-07-24 | 22680 | keep | 0 | Jul | 2021 | 0.015447 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2021-07-24 11:42 | 2021-07-24 16:59 | 100 | 005:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21072400038 | New_Event | Bad Weather | Include | Include | Weather | 317 | 2021-07-24 | 31700 | keep | 0 | Jul | 2021 | 0.021591 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-07-24 11:46 | 2021-07-24 16:34 | 30 | 004:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21072400039 | New_Event | Bad Weather | Include | Include | Weather | 288 | 2021-07-24 | 8640 | keep | 0 | Jul | 2021 | 0.0058847 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
FAJARDO | 2021-07-24 11:47 | 2021-07-24 11:48 | 1234 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | R21072400030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-24 | 1234 | keep | 0 | Jul | 2021 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
FAJARDO | 2021-07-24 11:48 | 2021-07-24 14:03 | 91 | 002:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | R21072400029 | New_Event |  |  | Include | Wildlife | 135 | 2021-07-24 | 12285 | keep | 0 | Jul | 2021 | 0.0083673 | 6.198e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 91
SAN JUAN | 2021-07-24 11:50 | 2021-07-24 15:28 | 50 | 003:38 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21072400083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 218 | 2021-07-24 | 10900 | keep | 0 | Jul | 2021 | 0.0074239 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BARRANQUITAS | 2021-07-24 11:50 | 2021-07-24 17:47 | 40 | 005:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA FIJO BAJANTE DE LINEA A CAJA | C21072400040 | New_Event | Wire Down | Include | Include | Equipment | 357 | 2021-07-24 | 14280 | keep | 0 | Jul | 2021 | 0.009726 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-07-24 12:00 | 2021-07-25 13:29 | 20 | 025:29 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21072400034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1529 | 2021-07-24 | 30580 | keep | 0 | Jul | 2021 | 0.020828 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CANOVANAS | 2021-07-24 12:25 | 2021-07-24 15:18 | 12 | 002:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | R21072400036 | New_Event |  |  | Include | Wildlife | 173 | 2021-07-24 | 2076 | keep | 0 | Jul | 2021 | 0.001414 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
CANOVANAS | 2021-07-24 12:39 | 2021-07-24 18:10 | 35 | 005:31 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | R21072400037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 331 | 2021-07-24 | 11585 | keep | 0 | Jul | 2021 | 0.0078905 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-07-24 12:50 | 2021-07-24 12:51 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-24 | 2605 | keep | 0 | Jul | 2021 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
ARECIBO | 2021-07-24 13:02 | 2021-07-24 14:44 | 200 | 001:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES QUEMADO | A21072400059 | New_Event | Cutout Failure | Include | Include | Equipment | 102 | 2021-07-24 | 20400 | keep | 0 | Jul | 2021 | 0.013894 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-07-24 13:12 | 2021-07-24 17:22 | 16 | 004:10 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21072400110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 250 | 2021-07-24 | 4000 | keep | 0 | Jul | 2021 | 0.0027244 | 1.0898e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 16
CAGUAS | 2021-07-24 13:20 | 2021-07-24 19:31 | 5 | 006:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21072300081 | New_Event | Secondary Wire Down | Include | Include | Equipment | 371 | 2021-07-24 | 1855 | keep | 0 | Jul | 2021 | 0.0012634 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-07-24 13:37 | 2021-07-24 16:38 | 870 | 003:01 | T | DESGANCHE | SE INSTALO TIGUERO ENTRE VIVO Y NEUTRAL SE REQUIERE DESGANCHE MASIVO POR ARBOLES ENCIMA DE LINEAS | S21072400000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 181 | 2021-07-24 | 157470 | keep | 0 | Jul | 2021 | 0.10725 | 0.00059255 | Sustained | FALSE | TRUE | Not_TMED_Event | 870
CAGUAS | 2021-07-24 13:48 | 2021-07-24 13:50 | 1879 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C21072400049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-24 | 3758 | keep | 0 | Jul | 2021 | 0.0025596 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
CAGUAS | 2021-07-24 13:50 | 2021-07-24 16:22 | 725 | 002:32 | T | DESGANCHE | SE SECCIONALIZO EL ALIMENTADOR PARA DESGANCHE | C21072400050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2021-07-24 | 110200 | keep | 0 | Jul | 2021 | 0.075057 | 0.00049379 | Sustained | FALSE | FALSE | Not_TMED_Event | 725
PONCE | 2021-07-24 13:50 | 2021-07-24 19:14 | 100 | 005:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | P21072400050 | New_Event | Cutout Failure | Include | Include | Equipment | 324 | 2021-07-24 | 32400 | keep | 0 | Jul | 2021 | 0.022067 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-07-24 13:52 | 2021-07-25 09:39 | 30 | 019:47 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21072400099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1187 | 2021-07-24 | 35610 | keep | 0 | Jul | 2021 | 0.024254 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-07-24 13:52 | 2021-07-24 13:53 | 6197 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR | C21072400051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-24 | 6197 | keep | 0 | Jul | 2021 | 0.0042207 | 0.0042207 | Momentary | FALSE | FALSE | Not_TMED_Event | 6197
CAGUAS | 2021-07-24 13:53 | 2021-07-24 17:10 | 150 | 003:17 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | C21072400055 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 197 | 2021-07-24 | 29550 | keep | 0 | Jul | 2021 | 0.020126 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-07-24 13:59 | 2021-07-24 15:57 | 1 | 001:58 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN BANCO DE TRANSFORMADORES ENREDADERA | R21072400041 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 118 | 2021-07-24 | 118 | keep | 0 | Jul | 2021 | 8.0369e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-07-24 14:03 | 2021-07-24 16:44 | 80 | 002:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | R21072400042 | New_Event | Wire Down | Include | Include | Equipment | 161 | 2021-07-24 | 12880 | keep | 0 | Jul | 2021 | 0.0087725 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CANOVANAS | 2021-07-24 14:05 | 2021-07-24 15:29 | 8 | 001:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR FUSIBLE SULFATADO | R21072400044 | New_Event | Cutout Failure | Include | Include | Equipment | 84 | 2021-07-24 | 672 | keep | 0 | Jul | 2021 | 0.0004577 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-07-24 14:08 | 2021-07-24 16:08 | 40 | 002:00 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21072400058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2021-07-24 | 4800 | keep | 0 | Jul | 2021 | 0.0032693 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-07-24 14:08 | 2021-07-24 16:20 | 40 | 002:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C21072400059 | New_Event |  |  | Include | Wildlife | 132 | 2021-07-24 | 5280 | keep | 0 | Jul | 2021 | 0.0035962 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-07-24 14:08 | 2021-07-24 14:59 | 1 | 000:51 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | B21072400124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 51 | 2021-07-24 | 51 | keep | 0 | Jul | 2021 | 3.4736e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CANOVANAS | 2021-07-24 14:14 | 2021-07-24 17:33 | 133 | 003:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | R21072400061 | New_Event | Bad Weather | Include | Include | Weather | 199 | 2021-07-24 | 26467 | keep | 0 | Jul | 2021 | 0.018027 | 9.0586e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 133
BAYAMON | 2021-07-24 14:17 | 2021-07-24 14:19 | 1983 | 000:02 | T | DESGANCHE | DISPARO HACIENDO OPERACIONES CARGA POR EL 1801-02 | B21072400016 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-07-24 | 3966 | keep | 0 | Jul | 2021 | 0.0027012 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
CAGUAS | 2021-07-24 14:30 | 2021-07-24 14:31 | 1606 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21072400065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-24 | 1606 | keep | 0 | Jul | 2021 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
ARECIBO | 2021-07-24 14:37 | 2021-07-24 17:18 | 100 | 002:41 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21072400064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2021-07-24 | 16100 | keep | 0 | Jul | 2021 | 0.010966 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-07-24 14:40 | 2021-07-24 15:34 | 5 | 000:54 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE POSTE SECUNDARIO | M21072400054 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 54 | 2021-07-24 | 270 | keep | 0 | Jul | 2021 | 0.0001839 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-07-24 14:43 | 2021-07-24 18:34 | 52 | 003:51 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | B21072400123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 231 | 2021-07-24 | 12012 | keep | 0 | Jul | 2021 | 0.0081813 | 3.5417e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 52
SAN JUAN | 2021-07-24 14:46 | 2021-07-24 14:47 | 135 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S21072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-24 | 135 | keep | 0 | Jul | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
HUMACAO | 2021-07-24 14:47 | 2021-07-24 17:59 | 6 | 003:12 | P | ESTRUCTURA AVERIADA | 1 X 10 EN TRANSFORMADOR SECCIONALIZO POSTE PARTIDO | C21072400067 | New_Event | Defective Pole | Include | Include | Equipment | 192 | 2021-07-24 | 1152 | keep | 0 | Jul | 2021 | 0.00078462 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-07-24 14:50 | 2021-07-24 18:16 | 100 | 003:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO PRIMARIA Y SE CERRO MACHETES | S21072400117 | New_Event | Wire Down | Include | Include | Equipment | 206 | 2021-07-24 | 20600 | keep | 0 | Jul | 2021 | 0.014031 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-07-24 14:53 | 2021-07-24 14:54 | 186 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVANDO LA CARGA DEL 1711-04 | B21072400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-24 | 186 | keep | 0 | Jul | 2021 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2021-07-24 14:54 | 2021-07-24 18:56 | 52 | 004:02 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRARON MACHETES | B21072400016 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 242 | 2021-07-24 | 12584 | keep | 0 | Jul | 2021 | 0.0085709 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
YAUCO | 2021-07-24 14:59 | 2021-07-24 17:16 | 11 | 002:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA CRUZADA | P21072400055 | New_Event | Secondary Wire Down | Include | Include | Equipment | 137 | 2021-07-24 | 1507 | keep | 0 | Jul | 2021 | 0.0010264 | 7.492e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 11
AGUADILLA | 2021-07-24 15:04 | 2021-07-24 15:05 | 4882 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21072400056 | Additional_clients | Bad Weather | Include | Include | Weather | 1 | 2021-07-24 | 4882 | keep | 0 | Jul | 2021 | 0.0033251 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-07-24 15:05 | 2021-07-25 11:20 | 80 | 020:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEAS MAL TIEMPO | M21072400040 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1215 | 2021-07-24 | 97200 | keep | 0 | Jul | 2021 | 0.066202 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-07-24 15:14 | 2021-07-25 10:51 | 6 | 019:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTES SECUNDARIOS EN TRANSFORMADOR | A21072400066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1177 | 2021-07-24 | 7062 | keep | 0 | Jul | 2021 | 0.0048099 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2021-07-24 15:17 | 2021-07-24 15:18 | 390 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21072400057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-24 | 390 | keep | 0 | Jul | 2021 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
FAJARDO | 2021-07-24 15:20 | 2021-07-24 17:35 | 10 | 002:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | R21072400050 | New_Event | Bad Weather | Include | Include | Weather | 135 | 2021-07-24 | 1350 | keep | 0 | Jul | 2021 | 0.00091948 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-07-24 15:29 | 2021-07-24 17:49 | 45 | 002:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21072400071 | New_Event | Bad Weather | Include | Include | Weather | 140 | 2021-07-24 | 6300 | keep | 0 | Jul | 2021 | 0.0042909 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BAYAMON | 2021-07-24 15:49 | 2021-07-24 15:50 | 295 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S21072400115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-24 | 295 | keep | 0 | Jul | 2021 | 0.00020092 | 0.00020092 | Momentary | FALSE | FALSE | Not_TMED_Event | 295
MAYAGÃœEZ | 2021-07-24 15:49 | 2021-07-24 15:50 | 3630 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS | M21072400000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-24 | 3630 | keep | 0 | Jul | 2021 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2021-07-24 15:53 | 2021-07-24 15:54 | 192 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 1200 MAL TIEMPO DESCARGAS ELECTRICAS | M21072400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-24 | 192 | keep | 0 | Jul | 2021 | 0.00013077 | 0.00013077 | Momentary | FALSE | TRUE | Not_TMED_Event | 192
MAYAGÃœEZ | 2021-07-24 15:53 | 2021-07-24 15:54 | 20 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 1200 MAL TIEMPO DESCARGAS ELECTRICAS | M21072400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-24 | 20 | keep | 0 | Jul | 2021 | 1.3622e-05 | 1.3622e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-07-24 15:53 | 2021-07-24 15:54 | 406 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 1200 MAL TIEMPO DESCARGAS ELECTRICAS | M21072400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-24 | 406 | keep | 0 | Jul | 2021 | 0.00027652 | 0.00027652 | Momentary | FALSE | TRUE | Not_TMED_Event | 406
MAYAGÃœEZ | 2021-07-24 15:53 | 2021-07-24 15:54 | 793 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 1200 MAL TIEMPO DESCARGAS ELECTRICAS | M21072400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-24 | 793 | keep | 0 | Jul | 2021 | 0.00054011 | 0.00054011 | Momentary | FALSE | TRUE | Not_TMED_Event | 793
MAYAGÃœEZ | 2021-07-24 15:53 | 2021-07-24 15:54 | 1509 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 1200 MAL TIEMPO DESCARGAS ELECTRICAS | M21072400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-24 | 1509 | keep | 0 | Jul | 2021 | 0.0010278 | 0.0010278 | Momentary | FALSE | TRUE | Not_TMED_Event | 1509
BARRANQUITAS | 2021-07-24 15:53 | 2021-07-24 20:14 | 30 | 004:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA REMPLAZO CAJA AVERIADA | C21072400075 | New_Event | Cutout Failure | Include | Include | Equipment | 261 | 2021-07-24 | 7830 | keep | 0 | Jul | 2021 | 0.005333 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-07-24 16:03 | 2021-07-24 16:04 | 4641 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS | M21072400000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-24 | 4641 | keep | 0 | Jul | 2021 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
PONCE | 2021-07-24 16:09 | 2021-07-24 19:29 | 15 | 003:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA FUERTES VIENTOS | P21072400058 | New_Event | Bad Weather | Include | Include | Weather | 200 | 2021-07-24 | 3000 | keep | 0 | Jul | 2021 | 0.0020433 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-07-24 16:14 | 2021-07-24 20:15 | 1145 | 004:01 | T | DESGANCHE | SE ABRIO MACHETES PARA SECCIONALIZAR BAMUS SOBRE LINEA PRIMARIA SE CERRO INTERRUPTOR | M21072400068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2021-07-24 | 275945 | keep | 0 | Jul | 2021 | 0.18794 | 0.00077985 | Sustained | FALSE | TRUE | Not_TMED_Event | 1145
BAYAMON | 2021-07-24 16:19 | 2021-07-24 17:52 | 16 | 001:33 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | B21072400133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2021-07-24 | 1488 | keep | 0 | Jul | 2021 | 0.0010135 | 1.0898e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 16
MAYAGÃœEZ | 2021-07-24 16:19 | 2021-07-24 16:20 | 528 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS LLEVA LA CARGA DEL 6012-05 | M21072400071 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-24 | 528 | keep | 0 | Jul | 2021 | 0.00035962 | 0.00035962 | Momentary | FALSE | FALSE | Not_TMED_Event | 528
MAYAGÃœEZ | 2021-07-24 16:19 | 2021-07-24 16:20 | 1352 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | CARGA POR 6012-01 MAL TIEMPO | M21072400071 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-24 | 1352 | keep | 0 | Jul | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
CAGUAS | 2021-07-24 16:22 | 2021-07-24 17:19 | 692 | 000:57 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE NORMALIZO | C21072400050 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 57 | 2021-07-24 | 39444 | keep | 0 | Jul | 2021 | 0.026865 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2021-07-24 16:23 | 2021-07-24 16:24 | 1902 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE PALMER TC A FAJARDO | R21072400054 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-24 | 1902 | keep | 0 | Jul | 2021 | 0.0012954 | 0.0012954 | Momentary | FALSE | TRUE | Not_TMED_Event | 1902
FAJARDO | 2021-07-24 16:23 | 2021-07-24 16:24 | 970 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE PALMER TC A FAJARDO | R21072400054 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-24 | 970 | keep | 0 | Jul | 2021 | 0.00066066 | 0.00066066 | Momentary | FALSE | TRUE | Not_TMED_Event | 970
FAJARDO | 2021-07-24 16:23 | 2021-07-24 16:24 | 3003 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE PALMER TC A FAJARDO | R21072400054 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-24 | 3003 | keep | 0 | Jul | 2021 | 0.0020453 | 0.0020453 | Momentary | FALSE | TRUE | Not_TMED_Event | 3003
FAJARDO | 2021-07-24 16:23 | 2021-07-24 16:24 | 1234 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INERRUPTOR | R21072400055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-24 | 1234 | keep | 0 | Jul | 2021 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
FAJARDO | 2021-07-24 16:23 | 2021-07-24 16:24 | 2343 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE PALMER TC A FAJARDO | R21072400053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-24 | 2343 | keep | 0 | Jul | 2021 | 0.0015958 | 0.0015958 | Momentary | FALSE | TRUE | Not_TMED_Event | 2343
FAJARDO | 2021-07-24 16:23 | 2021-07-24 16:24 | 1830 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE PALMER TC A FAJARDO | R21072400053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-24 | 1830 | keep | 0 | Jul | 2021 | 0.0012464 | 0.0012464 | Momentary | FALSE | TRUE | Not_TMED_Event | 1830
FAJARDO | 2021-07-24 16:23 | 2021-07-24 16:24 | 710 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE PALMER TC A FAJARDO | R21072400053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-24 | 710 | keep | 0 | Jul | 2021 | 0.00048358 | 0.00048358 | Momentary | FALSE | TRUE | Not_TMED_Event | 710
FAJARDO | 2021-07-24 16:23 | 2021-07-24 16:24 | 969 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE PALMER TC A FAJARDO | R21072400053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-24 | 969 | keep | 0 | Jul | 2021 | 0.00065998 | 0.00065998 | Momentary | FALSE | TRUE | Not_TMED_Event | 969
SAN JUAN | 2021-07-24 16:24 | 2021-07-24 18:57 | 26 | 002:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA Y SE RETEZO LINEA | S21072400121 | New_Event | Cutout Failure | Include | Include | Equipment | 153 | 2021-07-24 | 3978 | keep | 0 | Jul | 2021 | 0.0027094 | 1.7708e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 26
UTUADO | 2021-07-24 16:29 | 2021-07-25 10:58 | 8 | 018:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTES SECUNDARIOS EN TRANSFORMADOR | A21072400069 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1109 | 2021-07-24 | 8872 | keep | 0 | Jul | 2021 | 0.0060427 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-07-24 16:30 | 2021-07-24 16:31 | 1378 | 000:01 | T | DESGANCHE | RECIERRE | C21072400083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-24 | 1378 | keep | 0 | Jul | 2021 | 0.00093855 | 0.00093855 | Momentary | FALSE | FALSE | Not_TMED_Event | 1378
CAGUAS | 2021-07-24 16:31 | 2021-07-24 18:14 | 80 | 001:43 | P | DESGANCHE | 2 X 65 Y 2 X 40 EN CORTES DE LINEA | C21072400089 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 103 | 2021-07-24 | 8240 | keep | 0 | Jul | 2021 | 0.0056122 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-07-24 16:31 | 2021-07-24 16:33 | 870 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR SCADA | C21072400084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-24 | 1740 | keep | 0 | Jul | 2021 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
AGUADILLA | 2021-07-24 16:31 | 2021-07-25 18:25 | 100 | 025:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21072400077 | New_Event | Bad Weather | Include | Include | Weather | 1554 | 2021-07-24 | 155400 | keep | 0 | Jul | 2021 | 0.10584 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
FAJARDO | 2021-07-24 16:33 | 2021-07-24 16:34 | 1902 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 DE PALMER TC A FAJARDO TC | R21072400057 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-24 | 1902 | keep | 0 | Jul | 2021 | 0.0012954 | 0.0012954 | Momentary | FALSE | TRUE | Not_TMED_Event | 1902
FAJARDO | 2021-07-24 16:33 | 2021-07-24 16:34 | 970 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 DE PALMER TC A FAJARDO TC | R21072400057 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-24 | 970 | keep | 0 | Jul | 2021 | 0.00066066 | 0.00066066 | Momentary | FALSE | TRUE | Not_TMED_Event | 970
FAJARDO | 2021-07-24 16:33 | 2021-07-24 16:34 | 3003 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 DE PALMER TC A FAJARDO TC | R21072400057 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-24 | 3003 | keep | 0 | Jul | 2021 | 0.0020453 | 0.0020453 | Momentary | FALSE | TRUE | Not_TMED_Event | 3003
FAJARDO | 2021-07-24 16:33 | 2021-07-24 16:34 | 2343 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 DE PALMER TC A FAJARDO TC | R21072400056 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-24 | 2343 | keep | 0 | Jul | 2021 | 0.0015958 | 0.0015958 | Momentary | FALSE | TRUE | Not_TMED_Event | 2343
FAJARDO | 2021-07-24 16:33 | 2021-07-24 16:34 | 1830 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 DE PALMER TC A FAJARDO TC | R21072400056 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-24 | 1830 | keep | 0 | Jul | 2021 | 0.0012464 | 0.0012464 | Momentary | FALSE | TRUE | Not_TMED_Event | 1830
FAJARDO | 2021-07-24 16:33 | 2021-07-24 16:34 | 710 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 DE PALMER TC A FAJARDO TC | R21072400056 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-24 | 710 | keep | 0 | Jul | 2021 | 0.00048358 | 0.00048358 | Momentary | FALSE | TRUE | Not_TMED_Event | 710
FAJARDO | 2021-07-24 16:33 | 2021-07-24 16:34 | 969 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 DE PALMER TC A FAJARDO TC | R21072400056 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-24 | 969 | keep | 0 | Jul | 2021 | 0.00065998 | 0.00065998 | Momentary | FALSE | TRUE | Not_TMED_Event | 969
MAYAGÃœEZ | 2021-07-24 16:33 | 2021-07-25 11:35 | 100 | 019:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA REPARO ALAMBRE PARTIDO | M21072400078 | New_Event | Wire Down | Include | Include | Equipment | 1142 | 2021-07-24 | 114200 | keep | 0 | Jul | 2021 | 0.077781 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-24 16:34 | 2021-07-24 17:11 | 30 | 000:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | S21072300029 | New_Event | Wire Down | Include | Include | Equipment | 37 | 2021-07-24 | 1110 | keep | 0 | Jul | 2021 | 0.00075602 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2021-07-24 16:38 | 2021-07-24 17:29 | 1902 | 000:51 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 DE PALMER TC A FAJARDO TC SE SECCIONALIZO CONDUCTOR PRIMARIO EN EL SUELO | R21072400057 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2021-07-24 | 97002 | keep | 0 | Jul | 2021 | 0.066068 | 0.0012954 | Sustained | FALSE | TRUE | Not_TMED_Event | 1902
FAJARDO | 2021-07-24 16:38 | 2021-07-24 17:29 | 970 | 000:51 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 DE PALMER TC A FAJARDO TC SE SECCIONALIZO CONDUCTOR PRIMARIO EN EL SUELO | R21072400057 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2021-07-24 | 49470 | keep | 0 | Jul | 2021 | 0.033694 | 0.00066066 | Sustained | FALSE | TRUE | Not_TMED_Event | 970
FAJARDO | 2021-07-24 16:38 | 2021-07-24 17:29 | 3003 | 000:51 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 DE PALMER TC A FAJARDO TC SE SECCIONALIZO CONDUCTOR PRIMARIO EN EL SUELO | R21072400057 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2021-07-24 | 153153 | keep | 0 | Jul | 2021 | 0.10431 | 0.0020453 | Sustained | FALSE | TRUE | Not_TMED_Event | 3003
FAJARDO | 2021-07-24 16:38 | 2021-07-24 17:13 | 2343 | 000:35 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 DE PALMER TC A FAJARDO TC SE SECCIONALIZO CONDUCTOR DE 38 KV EN EL SUELO | R21072400056 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 35 | 2021-07-24 | 82005 | keep | 0 | Jul | 2021 | 0.055853 | 0.0015958 | Sustained | FALSE | TRUE | Not_TMED_Event | 2343
FAJARDO | 2021-07-24 16:38 | 2021-07-24 17:13 | 1830 | 000:35 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 DE PALMER TC A FAJARDO TC SE SECCIONALIZO CONDUCTOR DE 38 KV EN EL SUELO | R21072400056 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 35 | 2021-07-24 | 64050 | keep | 0 | Jul | 2021 | 0.043624 | 0.0012464 | Sustained | FALSE | TRUE | Not_TMED_Event | 1830
FAJARDO | 2021-07-24 16:38 | 2021-07-24 17:13 | 710 | 000:35 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 DE PALMER TC A FAJARDO TC SE SECCIONALIZO CONDUCTOR DE 38 KV EN EL SUELO | R21072400056 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 35 | 2021-07-24 | 24850 | keep | 0 | Jul | 2021 | 0.016925 | 0.00048358 | Sustained | FALSE | TRUE | Not_TMED_Event | 710
FAJARDO | 2021-07-24 16:38 | 2021-07-24 17:13 | 969 | 000:35 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 DE PALMER TC A FAJARDO TC SE SECCIONALIZO CONDUCTOR DE 38 KV EN EL SUELO | R21072400056 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 35 | 2021-07-24 | 33915 | keep | 0 | Jul | 2021 | 0.023099 | 0.00065998 | Sustained | FALSE | TRUE | Not_TMED_Event | 969
CANOVANAS | 2021-07-24 16:47 | 2021-07-24 19:43 | 115 | 002:56 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA PRINCIPAL SECCIONALIZO TRAMO PROBANDO MALO PARA PATRULLAJE DE DIA | R21072400083 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 176 | 2021-07-24 | 20240 | keep | 0 | Jul | 2021 | 0.013785 | 7.8326e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 115
CANOVANAS | 2021-07-24 16:47 | 2021-07-24 19:43 | 400 | 002:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN LA SALIDA DEL CONVERTIDOR Y 1 X 25 EN CORTE DE LINEA MAL TIEMPO | R21072400059 | New_Event | Bad Weather | Include | Include | Weather | 176 | 2021-07-24 | 70400 | keep | 0 | Jul | 2021 | 0.047949 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
CAGUAS | 2021-07-24 16:48 | 2021-07-24 16:49 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR SCADA | C21072400084 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-24 | 870 | keep | 0 | Jul | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CANOVANAS | 2021-07-24 17:00 | 2021-07-24 18:55 | 400 | 001:55 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 Y 2 X 65 EN CORTES DE LINEA MAL TIEMPO | R21072400063 | New_Event | Bad Weather | Include | Include | Weather | 115 | 2021-07-24 | 46000 | keep | 0 | Jul | 2021 | 0.03133 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
AGUADILLA | 2021-07-24 17:08 | 2021-07-24 19:15 | 200 | 002:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 200 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21072300080 | New_Event | Wire Down | Include | Include | Equipment | 127 | 2021-07-24 | 25400 | keep | 0 | Jul | 2021 | 0.0173 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-07-24 17:14 | 2021-07-24 17:15 | 4622 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-24 | 4622 | keep | 0 | Jul | 2021 | 0.003148 | 0.003148 | Momentary | FALSE | FALSE | Not_TMED_Event | 4622
SAN JUAN | 2021-07-24 17:18 | 2021-07-24 17:19 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-24 | 2203 | keep | 0 | Jul | 2021 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
AGUADILLA | 2021-07-24 17:24 | 2021-07-24 20:15 | 150 | 002:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21072400085 | New_Event | Bad Weather | Include | Include | Weather | 171 | 2021-07-24 | 25650 | keep | 0 | Jul | 2021 | 0.01747 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-07-24 17:26 | 2021-07-25 14:39 | 75 | 021:13 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHO Y CERRO PUENTE | C21072400095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1273 | 2021-07-24 | 95475 | keep | 0 | Jul | 2021 | 0.065028 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-07-24 17:30 | 2021-07-25 12:18 | 60 | 018:48 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER Y 1 X 65 EN CORTE DE LINEA | B21072400138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1128 | 2021-07-24 | 67680 | keep | 0 | Jul | 2021 | 0.046097 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
FAJARDO | 2021-07-24 17:36 | 2021-07-24 17:48 | 1234 | 000:12 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR TRAMO DE LINEA PARA TRABAJOS CON LINEA DE 38 KV | R21072400076 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-07-24 | 14808 | keep | 0 | Jul | 2021 | 0.010086 | 0.00084047 | Sustained | FALSE | TRUE | Not_TMED_Event | 1234
CANOVANAS | 2021-07-24 17:39 | 2021-07-24 19:35 | 65 | 001:56 | P | DESGANCHE | 1 X 50 EN CORT DE LINEA DESGANCHE | R21072400077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2021-07-24 | 7540 | keep | 0 | Jul | 2021 | 0.0051355 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
CAGUAS | 2021-07-24 17:47 | 2021-07-25 10:14 | 80 | 016:27 | P | DESGANCHE | 1 X 65 Y 1 X 30 EN CORTES DE LINEA Y 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE Y MAL TIEMPO EN EL AREA | C21072400098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 987 | 2021-07-24 | 78960 | keep | 0 | Jul | 2021 | 0.053779 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-07-24 17:48 | 2021-07-25 13:15 | 80 | 019:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21072400088 | New_Event | Bad Weather | Include | Include | Weather | 1167 | 2021-07-24 | 93360 | keep | 0 | Jul | 2021 | 0.063587 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-07-24 17:52 | 2021-07-24 21:05 | 100 | 003:13 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | S21072400124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2021-07-24 | 19300 | keep | 0 | Jul | 2021 | 0.013145 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-07-24 17:59 | 2021-07-25 20:28 | 30 | 026:29 | P | ESTRUCTURA AVERIADA | REMPLAZO 2 POSTES PARTIDOS Y CERRO CORTE DE LINEA | C21072400067 | Additional_clients | Defective Pole | Include | Include | Equipment | 1589 | 2021-07-24 | 47670 | keep | 0 | Jul | 2021 | 0.032468 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-07-24 18:04 | 2021-07-26 17:03 | 55 | 046:59 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21072400100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2819 | 2021-07-24 | 155045 | keep | 0 | Jul | 2021 | 0.1056 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
SAN JUAN | 2021-07-24 18:05 | 2021-07-24 18:08 | 1061 | 000:03 | T | ERROR HUMANO | SE ABRIO POR ERROR PARA REMPLAZO DE CAJA PELIGROSA | S21072400126 | New_Event | Human Error | Include | Include | Other | 3 | 2021-07-24 | 3183 | keep | 0 | Jul | 2021 | 0.0021679 | 0.00072264 | Momentary | FALSE | FALSE | Not_TMED_Event | 1061
SAN JUAN | 2021-07-24 18:10 | 2021-07-24 18:24 | 1208 | 000:14 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO INTERRUPTOR POR SEGURIDAD PARA REMPLAZO DE CAJA PRIMARIA | S21072400127 | New_Event | Cutout Failure | Include | Include | Equipment | 14 | 2021-07-24 | 16912 | keep | 0 | Jul | 2021 | 0.011519 | 0.00082276 | Sustained | FALSE | FALSE | Not_TMED_Event | 1208
MAYAGÃœEZ | 2021-07-24 18:13 | 2021-07-25 11:35 | 75 | 017:22 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | M21072400092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1042 | 2021-07-24 | 78150 | keep | 0 | Jul | 2021 | 0.053228 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-07-24 18:20 | 2021-07-25 09:50 | 15 | 015:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA | B21072400042 | New_Event | Cutout Failure | Include | Include | Equipment | 930 | 2021-07-24 | 13950 | keep | 0 | Jul | 2021 | 0.0095013 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-07-24 18:24 | 2021-07-24 20:32 | 50 | 002:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO Y SE REMPLAZO CAJA PRIMARIA | S21072400060 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 128 | 2021-07-24 | 6400 | keep | 0 | Jul | 2021 | 0.004359 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
PONCE | 2021-07-24 18:27 | 2021-07-25 13:43 | 97 | 019:16 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA. SE REALIZO DESGANCHE Y SE REEMPLAZO CAJA PRIMARIA QUEMADA | P21072500063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1156 | 2021-07-24 | 112132 | keep | 0 | Jul | 2021 | 0.076373 | 6.6066e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 97
AGUADILLA | 2021-07-24 18:34 | 2021-07-25 17:06 | 10 | 022:32 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21072400096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1352 | 2021-07-24 | 13520 | keep | 0 | Jul | 2021 | 0.0092084 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
GUAYAMA | 2021-07-24 18:41 | 2021-07-25 09:20 | 65 | 014:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | P21072400064 | New_Event | Bad Weather | Include | Include | Weather | 879 | 2021-07-24 | 57135 | keep | 0 | Jul | 2021 | 0.038914 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
CAGUAS | 2021-07-24 18:45 | 2021-07-25 15:11 | 40 | 020:26 | P | CABLE SOTERRADO AVERIADO | 1 X 65 EN RISER CERRO EN T - 3 HACIA T - 2 AVERIA DEL SU - 1 HACIA T - 1 | C21072500103 | New_Event | UG Cable Fault | Include | Include | Equipment | 1226 | 2021-07-24 | 49040 | keep | 0 | Jul | 2021 | 0.033401 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2021-07-24 18:46 | 2021-07-25 10:58 | 50 | 016:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21072400075 | New_Event | Bad Weather | Include | Include | Weather | 972 | 2021-07-24 | 48600 | keep | 0 | Jul | 2021 | 0.033101 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
YAUCO | 2021-07-24 18:51 | 2021-07-24 18:52 | 1352 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE INTERRUPTOR CARGA POR 5602-02 | P21072400065 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-07-24 | 1352 | keep | 0 | Jul | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
YAUCO | 2021-07-24 18:51 | 2021-07-24 18:52 | 3973 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE INTERRUPTOR | P21072400065 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-07-24 | 3973 | keep | 0 | Jul | 2021 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2021-07-24 18:55 | 2021-07-25 01:30 | 1352 | 006:35 | T | AISLADOR ROTO, PARTIDO O SAFADO | REMPLAZO DE AISLADORES Y REPARANDO ALAMBRE | P21072400076 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 395 | 2021-07-24 | 534040 | keep | 0 | Jul | 2021 | 0.36373 | 0.00092084 | Sustained | FALSE | FALSE | Not_TMED_Event | 1352
YAUCO | 2021-07-24 18:55 | 2021-07-24 20:03 | 3973 | 001:08 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO INTERRUPTOR CON CARGA DE 5602-01 SE ABRIO MACHETES EN AREA DE MALECON Y SE REALIZO PRUEBA QUEDANDO EN SERVICIO | P21072400066 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 68 | 2021-07-24 | 270164 | keep | 0 | Jul | 2021 | 0.18401 | 0.002706 | Sustained | FALSE | FALSE | Not_TMED_Event | 3973
CAGUAS | 2021-07-24 18:58 | 2021-07-25 13:33 | 55 | 018:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21072400105 | New_Event | Bad Weather | Include | Include | Weather | 1115 | 2021-07-24 | 61325 | keep | 0 | Jul | 2021 | 0.041768 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
CANOVANAS | 2021-07-24 19:00 | 2021-07-24 22:25 | 45 | 003:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | R21072400085 | New_Event | Bad Weather | Include | Include | Weather | 205 | 2021-07-24 | 9225 | keep | 0 | Jul | 2021 | 0.0062831 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
CAGUAS | 2021-07-24 19:03 | 2021-07-25 19:17 | 40 | 024:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y CERRO CORTE DE LINEA | C21072400106 | New_Event | Wire Down | Include | Include | Equipment | 1454 | 2021-07-24 | 58160 | keep | 0 | Jul | 2021 | 0.039613 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-07-24 19:06 | 2021-07-24 19:07 | 11 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | P21072400070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-24 | 11 | keep | 0 | Jul | 2021 | 7.492e-06 | 7.492e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 11
YAUCO | 2021-07-24 19:26 | 2021-07-24 19:27 | 1475 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | P21072400072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-24 | 1475 | keep | 0 | Jul | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
BAYAMON | 2021-07-24 19:40 | 2021-07-25 11:06 | 10 | 015:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21072400147 | New_Event | Secondary Wire Down | Include | Include | Equipment | 926 | 2021-07-24 | 9260 | keep | 0 | Jul | 2021 | 0.0063069 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-24 19:41 | 2021-07-25 13:10 | 80 | 017:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE ENTRE LAS LINEAS | M21072400108 | New_Event |  |  | Include | Wildlife | 1049 | 2021-07-24 | 83920 | keep | 0 | Jul | 2021 | 0.057158 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-07-24 19:43 | 2021-07-24 21:49 | 149 | 002:06 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S21072400132 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2021-07-24 | 18774 | keep | 0 | Jul | 2021 | 0.012787 | 0.00010148 | Sustained | FALSE | FALSE | Not_TMED_Event | 149
CANOVANAS | 2021-07-24 19:43 | 2021-07-25 13:25 | 150 | 017:42 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN CORTE DE LINEA SE REEMPLAZO AISLADOR PARTIDO | R21072400083 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1062 | 2021-07-24 | 159300 | keep | 0 | Jul | 2021 | 0.1085 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-24 20:15 | 2021-07-25 09:45 | 300 | 013:30 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETES | M21072400073 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 810 | 2021-07-24 | 243000 | keep | 0 | Jul | 2021 | 0.16551 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-07-24 20:58 | 2021-07-25 14:06 | 11 | 017:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR REPARO SECUNDARIA | C21072400113 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1028 | 2021-07-24 | 11308 | keep | 0 | Jul | 2021 | 0.0077018 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
HUMACAO | 2021-07-24 21:01 | 2021-07-25 18:06 | 20 | 021:05 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA REMPLAZO AISLADOR Y CAJA AVERIADA | C21072400114 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1265 | 2021-07-24 | 25300 | keep | 0 | Jul | 2021 | 0.017232 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
HUMACAO | 2021-07-24 21:18 | 2021-07-25 12:00 | 217 | 014:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 Y 1 X 30 EN CORTES DE LINEA SE CERRO PUENTE Y SE SECCIONALIZO 2 TRANSFORMADORES AVERIADO POR RAYO | C21072400115 | New_Event | Bad Weather | Include | Include | Weather | 882 | 2021-07-24 | 191394 | keep | 0 | Jul | 2021 | 0.13036 | 0.0001478 | Sustained | FALSE | TRUE | Not_TMED_Event | 217
CANOVANAS | 2021-07-24 21:19 | 2021-07-24 21:20 | 2675 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | R21072400099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-24 | 2675 | keep | 0 | Jul | 2021 | 0.0018219 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
CANOVANAS | 2021-07-24 21:53 | 2021-07-25 08:37 | 125 | 010:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA REMPLAZO PORTAFUSIBLE QUEMADO | R21072400100 | New_Event | Cutout Failure | Include | Include | Equipment | 644 | 2021-07-24 | 80500 | keep | 0 | Jul | 2021 | 0.054828 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
MAYAGÃœEZ | 2021-07-24 22:10 | 2021-07-25 14:46 | 15 | 016:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE DE TRANSFORMADOR | M21072400115 | New_Event | Secondary Wire Down | Include | Include | Equipment | 996 | 2021-07-24 | 14940 | keep | 0 | Jul | 2021 | 0.010176 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-07-24 22:55 | 2021-07-25 11:24 | 125 | 012:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21072400118 | New_Event | Bad Weather | Include | Include | Weather | 749 | 2021-07-24 | 93625 | keep | 0 | Jul | 2021 | 0.063768 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
ARECIBO | 2021-07-24 23:06 | 2021-07-25 10:07 | 60 | 011:01 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21072400085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 661 | 2021-07-24 | 39660 | keep | 0 | Jul | 2021 | 0.027012 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-07-24 23:53 | 2021-07-24 23:54 | 125 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO RR/OFF | C21072400119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-24 | 125 | keep | 0 | Jul | 2021 | 8.5137e-05 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
FAJARDO | 2021-07-25 00:29 | 2021-07-25 13:34 | 150 | 013:05 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 100 EN CORTE DE LINEA Y 1 X 80 EN SU - 1 DEJO ABIERTO DEL SU - 2 HACIA SU - 3 POR AISLADOR ROTO EN EL SU - 3 NO HAY CLIENTES FUERA | R21072500001 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 785 | 2021-07-25 | 117750 | keep | 0 | Jul | 2021 | 0.080199 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-07-25 00:43 | 2021-07-25 10:26 | 28 | 009:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21072500002 | New_Event | Bad Weather | Include | Include | Weather | 583 | 2021-07-25 | 16324 | keep | 0 | Jul | 2021 | 0.011118 | 1.9071e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 28
SAN JUAN | 2021-07-25 01:08 | 2021-07-25 01:09 | 4133 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | S21072500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-25 | 4133 | keep | 0 | Jul | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-07-25 01:09 | 2021-07-25 09:38 | 35 | 008:29 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21072500012 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 509 | 2021-07-25 | 17815 | keep | 0 | Jul | 2021 | 0.012134 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
SAN JUAN | 2021-07-25 01:09 | 2021-07-25 15:06 | 40 | 013:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21072500023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 837 | 2021-07-25 | 33480 | keep | 0 | Jul | 2021 | 0.022803 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-07-25 01:23 | 2021-07-25 10:44 | 12 | 009:21 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | C21072500003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 561 | 2021-07-25 | 6732 | keep | 0 | Jul | 2021 | 0.0045851 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
ARECIBO | 2021-07-25 01:55 | 2021-07-25 11:08 | 10 | 009:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADORSE LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21072500001 | New_Event | Bad Weather | Include | Include | Weather | 553 | 2021-07-25 | 5530 | keep | 0 | Jul | 2021 | 0.0037665 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-07-25 02:03 | 2021-07-25 02:04 | 5062 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 5062 | keep | 0 | Jul | 2021 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
GUAYAMA | 2021-07-25 02:50 | 2021-07-25 09:15 | 50 | 006:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P21072500002 | New_Event | Bad Weather | Include | Include | Weather | 385 | 2021-07-25 | 19250 | keep | 0 | Jul | 2021 | 0.013111 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-07-25 02:55 | 2021-07-25 09:21 | 66 | 006:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | P21072500003 | New_Event | Bad Weather | Include | Include | Weather | 386 | 2021-07-25 | 25476 | keep | 0 | Jul | 2021 | 0.017352 | 4.4952e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 66
PONCE | 2021-07-25 02:56 | 2021-07-25 02:57 | 485 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21072500005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 485 | keep | 0 | Jul | 2021 | 0.00033033 | 0.00033033 | Momentary | FALSE | FALSE | Not_TMED_Event | 485
CAGUAS | 2021-07-25 03:19 | 2021-07-25 09:27 | 313 | 006:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 Y 1 X 50 EN CORTES DE LINEA MAL TIEMPO | C21072500005 | New_Event | Bad Weather | Include | Include | Weather | 368 | 2021-07-25 | 115184 | keep | 0 | Jul | 2021 | 0.078451 | 0.00021318 | Sustained | FALSE | TRUE | Not_TMED_Event | 313
CAGUAS | 2021-07-25 03:46 | 2021-07-25 03:47 | 3131 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | C21072500006 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-07-25 | 3131 | keep | 0 | Jul | 2021 | 0.0021325 | 0.0021325 | Momentary | FALSE | FALSE | Not_TMED_Event | 3131
CAGUAS | 2021-07-25 03:47 | 2021-07-25 13:47 | 154 | 010:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO AISLADOR QUEMADO Y SE CERRO PUENTE | C21072500007 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 600 | 2021-07-25 | 92400 | keep | 0 | Jul | 2021 | 0.062933 | 0.00010489 | Sustained | FALSE | TRUE | Not_TMED_Event | 154
YAUCO | 2021-07-25 04:10 | 2021-07-25 12:22 | 50 | 008:12 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P210725000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 492 | 2021-07-25 | 24600 | keep | 0 | Jul | 2021 | 0.016755 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-25 04:27 | 2021-07-25 04:28 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CARGA POR EL 1909-08 | S21072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 2435 | keep | 0 | Jul | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-07-25 04:27 | 2021-07-25 04:28 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVANDO LA CARGA DEL 1907-05 | S21072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 2956 | keep | 0 | Jul | 2021 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2021-07-25 05:08 | 2021-07-25 14:52 | 27 | 009:44 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21072500009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 584 | 2021-07-25 | 15768 | keep | 0 | Jul | 2021 | 0.01074 | 1.839e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 27
BAYAMON | 2021-07-25 05:08 | 2021-07-25 13:14 | 60 | 008:06 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 65 EN CORTE DE LINEA DIFERENTES | B21072500002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 486 | 2021-07-25 | 29160 | keep | 0 | Jul | 2021 | 0.019861 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CANOVANAS | 2021-07-25 05:42 | 2021-07-25 13:20 | 250 | 007:38 | P | DESGANCHE | 2 X 65 Y 2 X 80 EN CORTES DE LINEA DESGANCHO INSTALO AISLADOR | R21072500003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 458 | 2021-07-25 | 114500 | keep | 0 | Jul | 2021 | 0.077985 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
BAYAMON | 2021-07-25 06:41 | 2021-07-25 06:42 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 2605 | keep | 0 | Jul | 2021 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
CANOVANAS | 2021-07-25 06:51 | 2021-07-26 11:30 | 424 | 028:39 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO SE LEVANTO CONDUCTOR DEL SUELO SE REPARO CRUCETA ZAFADA | R21072500129 | New_Event | Wire Down | Include | Include | Equipment | 1719 | 2021-07-25 | 728856 | keep | 0 | Jul | 2021 | 0.49642 | 0.00028878 | Sustained | FALSE | FALSE | Not_TMED_Event | 424
SAN JUAN | 2021-07-25 07:00 | 2021-07-25 07:02 | 550 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO 1529-15 LLEVANDO 30% DEL 1346-02 | S21072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-25 | 1100 | keep | 0 | Jul | 2021 | 0.0007492 | 0.0003746 | Momentary | FALSE | FALSE | Not_TMED_Event | 550
BAYAMON | 2021-07-25 07:00 | 2021-07-25 07:02 | 1802 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO 1529-15 LLEVANDO 30% DEL 1346-02 | S21072500013 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2021-07-25 | 3604 | keep | 0 | Jul | 2021 | 0.0024547 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
SAN JUAN | 2021-07-25 07:02 | 2021-07-25 11:30 | 60 | 004:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | S21072500021 | New_Event | Cutout Failure | Include | Include | Equipment | 268 | 2021-07-25 | 16080 | keep | 0 | Jul | 2021 | 0.010952 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-07-25 07:02 | 2021-07-25 14:20 | 27 | 007:18 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21072500004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 438 | 2021-07-25 | 11826 | keep | 0 | Jul | 2021 | 0.0080546 | 1.839e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 27
SAN JUAN | 2021-07-25 07:10 | 2021-07-25 10:33 | 101 | 003:23 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTES DE LINEA | R21072500011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2021-07-25 | 20503 | keep | 0 | Jul | 2021 | 0.013964 | 6.8791e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 101
SAN JUAN | 2021-07-25 07:12 | 2021-07-25 07:14 | 485 | 000:02 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO 1404-09 LLEVANDO LA CARGA DEL 1420-05 | S21072500000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 2 | 2021-07-25 | 970 | keep | 0 | Jul | 2021 | 0.00066066 | 0.00033033 | Momentary | FALSE | FALSE | Not_TMED_Event | 485
SAN JUAN | 2021-07-25 07:12 | 2021-07-25 07:14 | 4 | 000:02 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO 1404-09 LLEVANDO LA CARGA DEL 1420-05 | S21072500000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 2 | 2021-07-25 | 8 | keep | 0 | Jul | 2021 | 5.4488e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2021-07-25 07:17 | 2021-07-28 17:39 | 33 | 082:22 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5 X 37.5KVA | C21072500009 | New_Event | Service Transformer Failure | Include | Include | Equipment | 4942 | 2021-07-25 | 163086 | keep | 0 | Jul | 2021 | 0.11108 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
YAUCO | 2021-07-25 07:30 | 2021-07-25 12:21 | 51 | 004:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P21072500006 | New_Event | Bad Weather | Include | Include | Weather | 291 | 2021-07-25 | 14841 | keep | 0 | Jul | 2021 | 0.010108 | 3.4736e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 51
HUMACAO | 2021-07-25 07:33 | 2021-07-25 16:05 | 20 | 008:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21072500018 | New_Event | Bad Weather | Include | Include | Weather | 512 | 2021-07-25 | 10240 | keep | 0 | Jul | 2021 | 0.0069744 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-07-25 07:43 | 2021-07-25 07:45 | 380 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO 1401-08 LLEVANDO 40% DEL 1346-05 | S21072500014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-25 | 760 | keep | 0 | Jul | 2021 | 0.00051763 | 0.00025882 | Momentary | FALSE | FALSE | Not_TMED_Event | 380
SAN JUAN | 2021-07-25 07:43 | 2021-07-25 07:45 | 135 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO 1401-08 LLEVANDO 40% DEL 1346-05 | S21072500014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-25 | 270 | keep | 0 | Jul | 2021 | 0.0001839 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
FAJARDO | 2021-07-25 07:47 | 2021-07-25 07:48 | 2722 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | R21072500016 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-25 | 2722 | keep | 0 | Jul | 2021 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
BAYAMON | 2021-07-25 07:48 | 2021-07-25 07:49 | 112 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21072500008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 112 | keep | 0 | Jul | 2021 | 7.6283e-05 | 7.6283e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 112
FAJARDO | 2021-07-25 07:48 | 2021-07-25 21:12 | 80 | 013:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | R21072500095 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 804 | 2021-07-25 | 64320 | keep | 0 | Jul | 2021 | 0.043808 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-07-25 07:48 | 2021-07-25 07:49 | 24 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21072500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 24 | keep | 0 | Jul | 2021 | 1.6346e-05 | 1.6346e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 24
VEGA BAJA | 2021-07-25 07:53 | 2021-07-26 18:28 | 30 | 034:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE INSTALO JUMPER A LINEA PRIMARIA PARA ENERGIZAR CARGAS MONOFASICAS POR PUENTE ABIERTO EN MONTE SIN ACCESO | B21072500009 | New_Event | Wire Down | Include | Include | Equipment | 2075 | 2021-07-25 | 62250 | keep | 0 | Jul | 2021 | 0.042398 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
FAJARDO | 2021-07-25 08:01 | 2021-07-25 09:16 | 50 | 001:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | R21072500017 | New_Event | Bad Weather | Include | Include | Weather | 75 | 2021-07-25 | 3750 | keep | 0 | Jul | 2021 | 0.0025541 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-25 08:02 | 2021-07-25 10:00 | 30 | 001:58 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | M21072400007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 118 | 2021-07-25 | 3540 | keep | 0 | Jul | 2021 | 0.0024111 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-07-25 08:02 | 2021-07-25 14:37 | 200 | 006:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21072500004 | New_Event | Bad Weather | Include | Include | Weather | 395 | 2021-07-25 | 79000 | keep | 0 | Jul | 2021 | 0.053807 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CANOVANAS | 2021-07-25 08:04 | 2021-07-25 10:33 | 80 | 002:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | R21072500018 | New_Event |  |  | Include | Wildlife | 149 | 2021-07-25 | 11920 | keep | 0 | Jul | 2021 | 0.0081187 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-07-25 08:07 | 2021-07-25 08:08 | 3597 | 000:01 | T | DESGANCHE | RECERRO | B21072500042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-25 | 3597 | keep | 0 | Jul | 2021 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
HUMACAO | 2021-07-25 08:07 | 2021-07-25 08:09 | 2126 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C21072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-25 | 4252 | keep | 0 | Jul | 2021 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
BAYAMON | 2021-07-25 08:08 | 2021-07-26 11:46 | 20 | 027:38 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | B21072500048 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1658 | 2021-07-25 | 33160 | keep | 0 | Jul | 2021 | 0.022585 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
FAJARDO | 2021-07-25 08:08 | 2021-07-25 18:32 | 1 | 010:24 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 15 EN TRANSFORMADOR CAJA AVERIADA CAMBIO LA PISTOLA DE BUSHING Y COLOCO LA OTRA EN PARKING BUSHING | R21072500020 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 624 | 2021-07-25 | 624 | keep | 0 | Jul | 2021 | 0.000425 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-07-25 08:09 | 2021-07-25 11:05 | 12 | 002:56 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | M21072500006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2021-07-25 | 2112 | keep | 0 | Jul | 2021 | 0.0014385 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
CAGUAS | 2021-07-25 08:12 | 2021-07-25 10:40 | 19 | 002:28 | P | DESGANCHE | 1 X 50 EN AEREO PROVISIONAL DESGANCHE | C21072500024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2021-07-25 | 2812 | keep | 0 | Jul | 2021 | 0.0019152 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2021-07-25 08:15 | 2021-07-25 08:16 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 2203 | keep | 0 | Jul | 2021 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
PONCE | 2021-07-25 08:19 | 2021-07-25 08:20 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21072500008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 1746 | keep | 0 | Jul | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
HUMACAO | 2021-07-25 08:21 | 2021-07-25 19:05 | 40 | 010:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21072500028 | New_Event | Bad Weather | Include | Include | Weather | 644 | 2021-07-25 | 25760 | keep | 0 | Jul | 2021 | 0.017545 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-07-25 08:24 | 2021-07-25 10:41 | 87 | 002:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21072500029 | New_Event | Bad Weather | Include | Include | Weather | 137 | 2021-07-25 | 11919 | keep | 0 | Jul | 2021 | 0.008118 | 5.9255e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 87
VEGA BAJA | 2021-07-25 08:29 | 2021-07-25 15:49 | 27 | 007:20 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | B21072500010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 440 | 2021-07-25 | 11880 | keep | 0 | Jul | 2021 | 0.0080914 | 1.839e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 27
HUMACAO | 2021-07-25 08:30 | 2021-07-25 17:09 | 250 | 008:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA, 1 X 80 ENTRADA DE RISER Y 1 X 65 EN LA SALIDA DEL RISER MAL TIEMPO | C21072500030 | New_Event | Bad Weather | Include | Include | Weather | 519 | 2021-07-25 | 129750 | keep | 0 | Jul | 2021 | 0.088372 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
CAGUAS | 2021-07-25 08:31 | 2021-07-25 21:58 | 40 | 013:27 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE CRITICO SOBRE LINEAS | C21072500048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 807 | 2021-07-25 | 32280 | keep | 0 | Jul | 2021 | 0.021986 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
FAJARDO | 2021-07-25 08:35 | 2021-07-25 15:06 | 30 | 006:31 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA REMPLAZO AISLADOR | R21072500027 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 391 | 2021-07-25 | 11730 | keep | 0 | Jul | 2021 | 0.0079892 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-07-25 08:36 | 2021-07-25 19:54 | 40 | 011:18 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | R21072500028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 678 | 2021-07-25 | 27120 | keep | 0 | Jul | 2021 | 0.018471 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2021-07-25 08:37 | 2021-07-25 08:38 | 2126 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C21072500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 2126 | keep | 0 | Jul | 2021 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
CAGUAS | 2021-07-25 08:44 | 2021-07-25 12:24 | 10 | 003:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21072500034 | New_Event | Bad Weather | Include | Include | Weather | 220 | 2021-07-25 | 2200 | keep | 0 | Jul | 2021 | 0.0014984 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-07-25 08:46 | 2021-07-25 13:50 | 60 | 005:04 | P | DESGANCHE | 1 X 40 Y 1 X 80 EN CORTES DE LINEA SE REALIZO DESGANCHE | A21072500005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 304 | 2021-07-25 | 18240 | keep | 0 | Jul | 2021 | 0.012423 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-07-25 08:53 | 2021-07-25 16:12 | 7 | 007:19 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER NO CAUSA | C21072500035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 439 | 2021-07-25 | 3073 | keep | 0 | Jul | 2021 | 0.002093 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
YAUCO | 2021-07-25 08:54 | 2021-07-25 12:58 | 25 | 004:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA, AVE CRUZO FASE. | P21072500010 | New_Event |  |  | Include | Wildlife | 244 | 2021-07-25 | 6100 | keep | 0 | Jul | 2021 | 0.0041547 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
GUAYAMA | 2021-07-25 08:56 | 2021-07-25 10:46 | 110 | 001:50 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA POR MAL TIEMPO | P21072500011 | New_Event | Bad Weather | Include | Include | Weather | 110 | 2021-07-25 | 12100 | keep | 0 | Jul | 2021 | 0.0082413 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
SAN JUAN | 2021-07-25 09:00 | 2021-07-25 18:05 | 50 | 009:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21072500020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 545 | 2021-07-25 | 27250 | keep | 0 | Jul | 2021 | 0.01856 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-25 09:01 | 2021-07-25 12:19 | 49 | 003:18 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN AEREO PROVISIONAL AVERIA DEL SU-2 AL T-4 | C21072500036 | New_Event | UG Cable Fault | Include | Include | Equipment | 198 | 2021-07-25 | 9702 | keep | 0 | Jul | 2021 | 0.006608 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
SAN JUAN | 2021-07-25 09:16 | 2021-07-25 16:38 | 40 | 007:22 | P | NO SE REPORTO CAUSA | 1 SMU 20 DE 80 AMP EN SU - 1 HACIA SU - 5A | R21072500036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 442 | 2021-07-25 | 17680 | keep | 0 | Jul | 2021 | 0.012042 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2021-07-25 09:25 | 2021-07-25 18:13 | 100 | 008:48 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 40 EN CORTES DE LINEA | R21072500038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 528 | 2021-07-25 | 52800 | keep | 0 | Jul | 2021 | 0.035962 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-07-25 09:25 | 2021-07-25 09:26 | 4035 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210725000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 4035 | keep | 0 | Jul | 2021 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
CAGUAS | 2021-07-25 09:30 | 2021-07-25 16:31 | 40 | 007:01 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21072500039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 421 | 2021-07-25 | 16840 | keep | 0 | Jul | 2021 | 0.01147 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-07-25 09:37 | 2021-07-27 10:57 | 10 | 049:20 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S21072500149 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2960 | 2021-07-25 | 29600 | keep | 0 | Jul | 2021 | 0.02016 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-25 09:56 | 2021-07-25 18:00 | 200 | 008:04 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO | M21072500014 | New_Event | Defective Pole | Include | Include | Equipment | 484 | 2021-07-25 | 96800 | keep | 0 | Jul | 2021 | 0.06593 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2021-07-25 10:00 | 2021-07-25 11:02 | 13 | 001:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A21072500009 | New_Event | Secondary Wire Down | Include | Include | Equipment | 62 | 2021-07-25 | 806 | keep | 0 | Jul | 2021 | 0.00054896 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
PONCE | 2021-07-25 10:05 | 2021-07-25 10:06 | 1293 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210725000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 1293 | keep | 0 | Jul | 2021 | 0.00088066 | 0.00088066 | Momentary | FALSE | FALSE | Not_TMED_Event | 1293
UTUADO | 2021-07-25 10:06 | 2021-07-25 16:30 | 40 | 006:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21072500010 | New_Event | Bad Weather | Include | Include | Weather | 384 | 2021-07-25 | 15360 | keep | 0 | Jul | 2021 | 0.010462 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-07-25 10:09 | 2021-07-25 13:18 | 3 | 003:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR 150 PIES DE SECUNDARIA | C21072400107 | New_Event | Secondary Wire Down | Include | Include | Equipment | 189 | 2021-07-25 | 567 | keep | 0 | Jul | 2021 | 0.00038618 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2021-07-25 10:15 | 2021-07-25 16:33 | 85 | 006:18 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | R21072500046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 378 | 2021-07-25 | 32130 | keep | 0 | Jul | 2021 | 0.021884 | 5.7893e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 85
BARRANQUITAS | 2021-07-25 10:21 | 2021-07-26 10:34 | 170 | 024:13 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21072500047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1453 | 2021-07-25 | 247010 | keep | 0 | Jul | 2021 | 0.16824 | 0.00011579 | Sustained | FALSE | TRUE | Not_TMED_Event | 170
BAYAMON | 2021-07-25 10:42 | 2021-07-25 10:43 | 4411 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 99% DE LA CARGA POR EL 1907-03 | S21072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 4411 | keep | 0 | Jul | 2021 | 0.0030043 | 0.0030043 | Momentary | FALSE | FALSE | Not_TMED_Event | 4411
SAN JUAN | 2021-07-25 10:52 | 2021-07-25 10:54 | 1681 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1303-04 QUE LLEVA REALMENTE EL 1303-01 Y 1346-06 Y SE CERRO POR SCADA | S21072500026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-25 | 3362 | keep | 0 | Jul | 2021 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-07-25 10:52 | 2021-07-25 10:53 | 225 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1908-03 LLEVANDO LA CARGA DEL 1303-04 | S21072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 225 | keep | 0 | Jul | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-07-25 10:52 | 2021-07-25 10:54 | 1598 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1303-04 QUE LLEVA REALMENTE EL 1303-01 Y 1346-06 Y SE CERRO POR SCADA | S21072500026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-25 | 3196 | keep | 0 | Jul | 2021 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2021-07-25 10:52 | 2021-07-25 10:53 | 3957 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVANDO LA CARGA DEL 1303-04 | S21072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 3957 | keep | 0 | Jul | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
CAGUAS | 2021-07-25 10:58 | 2021-07-26 17:38 | 19 | 030:40 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR | C21072500055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1840 | 2021-07-25 | 34960 | keep | 0 | Jul | 2021 | 0.023811 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
UTUADO | 2021-07-25 11:01 | 2021-07-25 17:55 | 5 | 006:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21072500015 | New_Event | Bad Weather | Include | Include | Weather | 414 | 2021-07-25 | 2070 | keep | 0 | Jul | 2021 | 0.0014099 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2021-07-25 11:05 | 2021-07-25 11:06 | 1173 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210725000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 1173 | keep | 0 | Jul | 2021 | 0.00079892 | 0.00079892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1173
CAGUAS | 2021-07-25 11:07 | 2021-07-26 13:34 | 70 | 026:27 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN RISER AVERIA T33 AL T32 SE SECCIONALIZO AVERIA | C21072500128 | New_Event | UG Cable Fault | Include | Include | Equipment | 1587 | 2021-07-25 | 111090 | keep | 0 | Jul | 2021 | 0.075663 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2021-07-25 11:08 | 2021-07-25 16:58 | 150 | 005:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTE DE LINEA CRUCE POR AVE | R21072500052 | New_Event |  |  | Include | Wildlife | 350 | 2021-07-25 | 52500 | keep | 0 | Jul | 2021 | 0.035758 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-07-25 11:15 | 2021-07-25 12:34 | 50 | 001:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | M21072500019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2021-07-25 | 3950 | keep | 0 | Jul | 2021 | 0.0026903 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-25 11:17 | 2021-07-25 13:22 | 60 | 002:05 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER | S21072500030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 125 | 2021-07-25 | 7500 | keep | 0 | Jul | 2021 | 0.0051082 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2021-07-25 11:20 | 2021-07-25 15:53 | 3830 | 004:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO PUENTE ABIERTO EN LA SALIDA DEL ALIMENTADOR Y SE TRANSFIRIO LA CARGA AL 2401-02 | R21072500020 | New_Event | Wire Down | Include | Include | Equipment | 273 | 2021-07-25 | 1045590 | keep | 0 | Jul | 2021 | 0.71215 | 0.0026086 | Sustained | FALSE | FALSE | Not_TMED_Event | 3830
ARECIBO | 2021-07-25 11:24 | 2021-07-25 12:21 | 15 | 000:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA Y VIENTO | A21072500017 | New_Event | Bad Weather | Include | Include | Weather | 57 | 2021-07-25 | 855 | keep | 0 | Jul | 2021 | 0.00058234 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2021-07-25 11:35 | 2021-07-25 20:26 | 6 | 008:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 Y 1 X 10 EN TRANSFORMADORES MAL TIEMPO | R21072500057 | New_Event | Bad Weather | Include | Include | Weather | 531 | 2021-07-25 | 3186 | keep | 0 | Jul | 2021 | 0.00217 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-07-25 11:36 | 2021-07-25 17:19 | 485 | 005:43 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REMPLAZO PISTOLA EN CAJA SECA Y SE CERRO POR SCADA LLEVA 1420-05 | S21072500034 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 343 | 2021-07-25 | 166355 | keep | 0 | Jul | 2021 | 0.1133 | 0.00033033 | Sustained | FALSE | FALSE | Not_TMED_Event | 485
SAN JUAN | 2021-07-25 11:36 | 2021-07-25 17:19 | 4 | 005:43 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REMPLAZO PISTOLA EN CAJA SECA Y SE CERRO POR SCADA LLEVA 1420-05 | S21072500034 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 343 | 2021-07-25 | 1372 | keep | 0 | Jul | 2021 | 0.00093446 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2021-07-25 11:45 | 2021-07-25 15:51 | 100 | 004:06 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21072500058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2021-07-25 | 24600 | keep | 0 | Jul | 2021 | 0.016755 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-07-25 11:50 | 2021-07-25 15:30 | 334 | 003:40 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 140 Y 1 X 50 EN CORTE DE LINEA | P21072500017 | New_Event | Bad Weather | Include | Include | Weather | 220 | 2021-07-25 | 73480 | keep | 0 | Jul | 2021 | 0.050047 | 0.00022749 | Sustained | FALSE | TRUE | Not_TMED_Event | 334
AGUADILLA | 2021-07-25 11:50 | 2021-07-25 12:24 | 6 | 000:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA Y SE CERRO TRANSFORMADOR | M21072300058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 34 | 2021-07-25 | 204 | keep | 0 | Jul | 2021 | 0.00013894 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2021-07-25 11:52 | 2021-07-26 18:27 | 34 | 030:35 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5 X 37.5KVA | C21072500063 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1835 | 2021-07-25 | 62390 | keep | 0 | Jul | 2021 | 0.042494 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
YAUCO | 2021-07-25 12:03 | 2021-07-25 14:00 | 65 | 001:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | P21072500019 | New_Event | Bad Weather | Include | Include | Weather | 117 | 2021-07-25 | 7605 | keep | 0 | Jul | 2021 | 0.0051797 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
SAN JUAN | 2021-07-25 12:04 | 2021-07-25 17:37 | 45 | 005:33 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R21072500063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 333 | 2021-07-25 | 14985 | keep | 0 | Jul | 2021 | 0.010206 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
HUMACAO | 2021-07-25 12:09 | 2021-07-26 17:04 | 50 | 028:55 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZARON TRANSFORMADORES QUEMADOS DE 37.5KVA Y 25KVA POR IGUALES | C21072500066 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1735 | 2021-07-25 | 86750 | keep | 0 | Jul | 2021 | 0.059085 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-07-25 12:13 | 2021-07-25 12:14 | 3511 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 3511 | keep | 0 | Jul | 2021 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
CAGUAS | 2021-07-25 12:19 | 2021-07-25 12:22 | 676 | 000:03 | T | CABLE SOTERRADO AVERIADO | DISPARO INTERRUPTOR PERSONAL REALIZANDO OPERACIONES CERRADO POR CONTROL | C21072500068 | New_Event | UG Cable Fault | Include | Include | Equipment | 3 | 2021-07-25 | 2028 | keep | 0 | Jul | 2021 | 0.0013813 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
UTUADO | 2021-07-25 12:20 | 2021-07-25 14:00 | 30 | 001:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21072500021 | New_Event | Bad Weather | Include | Include | Weather | 100 | 2021-07-25 | 3000 | keep | 0 | Jul | 2021 | 0.0020433 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-07-25 12:24 | 2021-07-25 12:26 | 906 | 000:02 | T | DESGANCHE | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C21072500069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-07-25 | 1812 | keep | 0 | Jul | 2021 | 0.0012341 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
CAGUAS | 2021-07-25 12:26 | 2021-07-25 15:19 | 150 | 002:53 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | C21072500070 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 173 | 2021-07-25 | 25950 | keep | 0 | Jul | 2021 | 0.017674 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-07-25 12:26 | 2021-07-25 13:58 | 10 | 001:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21072500034 | New_Event | Bad Weather | Include | Include | Weather | 92 | 2021-07-25 | 920 | keep | 0 | Jul | 2021 | 0.00062661 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-07-25 12:38 | 2021-07-25 12:39 | 2782 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S21072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 2782 | keep | 0 | Jul | 2021 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
MAYAGÃœEZ | 2021-07-25 12:42 | 2021-07-25 19:03 | 50 | 006:21 | P | MAL TIEMPO/RAYOS/WET ASH | SE CERRO CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21072500025 | New_Event | Bad Weather | Include | Include | Weather | 381 | 2021-07-25 | 19050 | keep | 0 | Jul | 2021 | 0.012975 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-07-25 12:59 | 2021-07-25 14:47 | 7 | 001:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | R21072500070 | New_Event | Bad Weather | Include | Include | Weather | 108 | 2021-07-25 | 756 | keep | 0 | Jul | 2021 | 0.00051491 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-07-25 13:07 | 2021-07-25 18:59 | 50 | 005:52 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21072500035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 352 | 2021-07-25 | 17600 | keep | 0 | Jul | 2021 | 0.011987 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-25 13:17 | 2021-07-25 19:50 | 90 | 006:33 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | C21072500076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 393 | 2021-07-25 | 35370 | keep | 0 | Jul | 2021 | 0.02409 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
MAYAGÃœEZ | 2021-07-25 13:17 | 2021-07-25 15:30 | 50 | 002:13 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21072500037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2021-07-25 | 6650 | keep | 0 | Jul | 2021 | 0.0045293 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-07-25 13:27 | 2021-07-25 16:35 | 20 | 003:08 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21072500025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2021-07-25 | 3760 | keep | 0 | Jul | 2021 | 0.0025609 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-07-25 14:05 | 2021-07-25 16:38 | 80 | 002:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C21072500080 | New_Event | Bad Weather | Include | Include | Weather | 153 | 2021-07-25 | 12240 | keep | 0 | Jul | 2021 | 0.0083366 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-07-25 14:06 | 2021-07-25 16:04 | 50 | 001:58 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21072500044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 118 | 2021-07-25 | 5900 | keep | 0 | Jul | 2021 | 0.0040185 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-25 14:13 | 2021-07-25 14:14 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21072500039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 1192 | keep | 0 | Jul | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
ARECIBO | 2021-07-25 14:13 | 2021-07-26 14:25 | 10 | 024:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21072500050 | New_Event | Bad Weather | Include | Include | Weather | 1452 | 2021-07-25 | 14520 | keep | 0 | Jul | 2021 | 0.0098895 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-07-25 14:25 | 2021-07-25 15:30 | 90 | 001:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A21072500027 | New_Event | Wire Down | Include | Include | Equipment | 65 | 2021-07-25 | 5850 | keep | 0 | Jul | 2021 | 0.0039844 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
ARECIBO | 2021-07-25 14:25 | 2021-07-25 14:43 | 6 | 000:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | A21072500024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 18 | 2021-07-25 | 108 | keep | 0 | Jul | 2021 | 7.3558e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-07-25 14:28 | 2021-07-25 17:32 | 52 | 003:04 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | S21072500046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 184 | 2021-07-25 | 9568 | keep | 0 | Jul | 2021 | 0.0065167 | 3.5417e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 52
ARECIBO | 2021-07-25 14:28 | 2021-07-25 14:29 | 1607 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21072400029 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-25 | 1607 | keep | 0 | Jul | 2021 | 0.0010945 | 0.0010945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1607
ARECIBO | 2021-07-25 14:29 | 2021-07-25 20:00 | 60 | 005:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21072500030 | New_Event | Bad Weather | Include | Include | Weather | 331 | 2021-07-25 | 19860 | keep | 0 | Jul | 2021 | 0.013527 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-07-25 14:29 | 2021-07-25 16:25 | 10 | 001:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21072500032 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 116 | 2021-07-25 | 1160 | keep | 0 | Jul | 2021 | 0.00079007 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-07-25 14:30 | 2021-07-25 16:56 | 60 | 002:26 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21072500082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2021-07-25 | 8760 | keep | 0 | Jul | 2021 | 0.0059664 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CANOVANAS | 2021-07-25 14:39 | 2021-07-25 18:32 | 70 | 003:53 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTES DE LINEA | R21072500091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2021-07-25 | 16310 | keep | 0 | Jul | 2021 | 0.011109 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
CAGUAS | 2021-07-25 14:45 | 2021-07-25 17:31 | 2907 | 002:46 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y SE TRANSFIRIO LA CARGA AL 3401-01 POR QUE EL 3401-03 PROBO MALO SIN CARGA | C21072500083 | New_Event | Wire Down | Include | Include | Equipment | 166 | 2021-07-25 | 482562 | keep | 0 | Jul | 2021 | 0.32867 | 0.0019799 | Sustained | FALSE | FALSE | Not_TMED_Event | 2907
VEGA BAJA | 2021-07-25 14:45 | 2021-07-25 19:03 | 52 | 004:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO NEUTRAL Y SE CERRARON MACHETES | B21072500023 | New_Event | Wire Down | Include | Include | Equipment | 258 | 2021-07-25 | 13416 | keep | 0 | Jul | 2021 | 0.0091376 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
PONCE | 2021-07-25 14:57 | 2021-07-25 15:25 | 7 | 000:28 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | P21072500026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 28 | 2021-07-25 | 196 | keep | 0 | Jul | 2021 | 0.00013349 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
SAN JUAN | 2021-07-25 14:58 | 2021-07-25 17:03 | 60 | 002:05 | P | NO SE REPORTO CAUSA | 1 X 40 SMU EN SU | S21072500048 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 125 | 2021-07-25 | 7500 | keep | 0 | Jul | 2021 | 0.0051082 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-25 15:02 | 2021-07-25 16:03 | 36 | 001:01 | P | HERRAJE ROTO O PODRIDO | SE REMPLAZO CRUCETA PARTIDA | S21072500000 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 61 | 2021-07-25 | 2196 | keep | 0 | Jul | 2021 | 0.0014957 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
BAYAMON | 2021-07-25 15:03 | 2021-07-26 10:34 | 50 | 019:31 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | B21072500031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1171 | 2021-07-25 | 58550 | keep | 0 | Jul | 2021 | 0.039878 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-25 15:26 | 2021-07-25 17:51 | 30 | 002:25 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 30 EN RISER REMPLAZO TERMINACION EN EL T - 28 | R21072500101 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 145 | 2021-07-25 | 4350 | keep | 0 | Jul | 2021 | 0.0029628 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-07-25 15:39 | 2021-07-25 15:41 | 315 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S21072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-25 | 630 | keep | 0 | Jul | 2021 | 0.00042909 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
SAN JUAN | 2021-07-25 15:40 | 2021-07-26 17:17 | 40 | 025:37 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21072500053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1537 | 2021-07-25 | 61480 | keep | 0 | Jul | 2021 | 0.041874 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-25 15:46 | 2021-07-25 15:47 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVANDO EL 99% DEL 1909-09 | S21072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 222 | keep | 0 | Jul | 2021 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
SAN JUAN | 2021-07-25 15:53 | 2021-07-25 15:58 | 2435 | 000:05 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO Y SE CERRO POR SCADA | S21072500058 | New_Event | Wire Down | Include | Include | Equipment | 5 | 2021-07-25 | 12175 | keep | 0 | Jul | 2021 | 0.0082923 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-07-25 15:53 | 2021-07-26 12:42 | 30 | 020:49 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21072500032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1249 | 2021-07-25 | 37470 | keep | 0 | Jul | 2021 | 0.025521 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-07-25 15:53 | 2021-07-25 16:04 | 8 | 000:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO EL INTERRUPTOR PARA ABRIR MACHETES N/C SOLO AFECTO 1 TRANSFORMADOR | R21072500109 | Partial_restoration | Wire Down | Include | Include | Equipment | 11 | 2021-07-25 | 88 | keep | 0 | Jul | 2021 | 5.9936e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-25 15:58 | 2021-07-26 08:30 | 300 | 016:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO ABRIENDO MACHETES LLEVADO PARTE DE LA CARGA POR EL 1336-08 | S21072600004 | Partial_restoration | Wire Down | Include | Include | Equipment | 992 | 2021-07-25 | 297600 | keep | 0 | Jul | 2021 | 0.20269 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-07-25 16:01 | 2021-07-25 17:25 | 13 | 001:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21072500035 | New_Event | Bad Weather | Include | Include | Weather | 84 | 2021-07-25 | 1092 | keep | 0 | Jul | 2021 | 0.00074376 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2021-07-25 16:02 | 2021-07-25 18:00 | 100 | 001:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21072500046 | New_Event | Bad Weather | Include | Include | Weather | 118 | 2021-07-25 | 11800 | keep | 0 | Jul | 2021 | 0.0080369 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-25 16:04 | 2021-07-25 18:47 | 52 | 002:43 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | B21072500064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2021-07-25 | 8476 | keep | 0 | Jul | 2021 | 0.005773 | 3.5417e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 52
CANOVANAS | 2021-07-25 16:04 | 2021-07-28 08:58 | 6 | 064:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN CORTE DE LINEA PORTAFUSIBLE QUEMADO | R21072500098 | New_Event | Cutout Failure | Include | Include | Equipment | 3894 | 2021-07-25 | 23364 | keep | 0 | Jul | 2021 | 0.015913 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-07-25 16:05 | 2021-07-25 19:40 | 75 | 003:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21072500047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2021-07-25 | 16125 | keep | 0 | Jul | 2021 | 0.010983 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-07-25 16:19 | 2021-07-26 13:35 | 15 | 021:16 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | B21072500040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1276 | 2021-07-25 | 19140 | keep | 0 | Jul | 2021 | 0.013036 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BARRANQUITAS | 2021-07-25 16:25 | 2021-07-26 14:36 | 19 | 022:11 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21072500105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1331 | 2021-07-25 | 25289 | keep | 0 | Jul | 2021 | 0.017224 | 1.2941e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 19
VEGA BAJA | 2021-07-25 16:38 | 2021-07-26 09:45 | 20 | 017:07 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO PARARRAYO Y AISLADOR | B21072500042 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1027 | 2021-07-25 | 20540 | keep | 0 | Jul | 2021 | 0.01399 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-07-25 16:40 | 2021-07-25 17:39 | 40 | 000:59 | P | NO SE REPORTO CAUSA | 2 X 25 EN SU - 1 | R21072500113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 59 | 2021-07-25 | 2360 | keep | 0 | Jul | 2021 | 0.0016074 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-07-25 16:43 | 2021-07-25 17:48 | 16 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO NEUTRAL SECUNDARIO ABIERTO | B21072500043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2021-07-25 | 1040 | keep | 0 | Jul | 2021 | 0.00070834 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2021-07-25 16:46 | 2021-07-26 09:20 | 6 | 016:34 | P | SECUNDARIA/DESGANCHE | 2 X 15 EN BANCO DE TRANSFORMADOR SE RETIRO ENREDADERA | C21072500111 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 994 | 2021-07-25 | 5964 | keep | 0 | Jul | 2021 | 0.0040621 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-07-25 16:51 | 2021-07-25 17:50 | 200 | 000:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 Y 1 X 50 EN CORTES DE LINEA CRUCE POR AVE | C21072500112 | New_Event |  |  | Include | Wildlife | 59 | 2021-07-25 | 11800 | keep | 0 | Jul | 2021 | 0.0080369 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-07-25 17:01 | 2021-07-26 09:34 | 59 | 016:33 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | C21072500114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 993 | 2021-07-25 | 58587 | keep | 0 | Jul | 2021 | 0.039903 | 4.0185e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 59
CAGUAS | 2021-07-25 17:03 | 2021-07-25 17:04 | 1378 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 1378 | keep | 0 | Jul | 2021 | 0.00093855 | 0.00093855 | Momentary | FALSE | FALSE | Not_TMED_Event | 1378
PONCE | 2021-07-25 17:10 | 2021-07-25 19:00 | 16 | 001:50 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | P21072500028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2021-07-25 | 1760 | keep | 0 | Jul | 2021 | 0.0011987 | 1.0898e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 16
ARECIBO | 2021-07-25 17:16 | 2021-07-25 18:15 | 12 | 000:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21072500038 | New_Event | Bad Weather | Include | Include | Weather | 59 | 2021-07-25 | 708 | keep | 0 | Jul | 2021 | 0.00048222 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-07-25 17:19 | 2021-07-25 18:07 | 20 | 000:48 | P | DESGANCHE | SE REALIZO DESGANCHE Y CERRO MACHETES | C21072400094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 48 | 2021-07-25 | 960 | keep | 0 | Jul | 2021 | 0.00065385 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-07-25 17:26 | 2021-07-26 00:23 | 45 | 006:57 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA, 1 X 65 EN CORTE DE LINEA, 1 X 30 EN BANCO DE TRANSFORMADOR Y 1 X 10 EN TRANSFORMADOR | B21072500046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 417 | 2021-07-25 | 18765 | keep | 0 | Jul | 2021 | 0.012781 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
ARECIBO | 2021-07-25 17:30 | 2021-07-25 18:32 | 12 | 001:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RETIRO CARGA DE TRANSFORMADOR PARA REPARAR NEUTRAL PRIMARIO | A21072500019 | New_Event | Wire Down | Include | Include | Equipment | 62 | 2021-07-25 | 744 | keep | 0 | Jul | 2021 | 0.00050674 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2021-07-25 17:33 | 2021-07-26 15:35 | 12 | 022:02 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21072500047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1322 | 2021-07-25 | 15864 | keep | 0 | Jul | 2021 | 0.010805 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-07-25 17:42 | 2021-07-26 20:27 | 4 | 026:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO HACIA TRANSFORMADOR | C21072500122 | New_Event | Wire Down | Include | Include | Equipment | 1605 | 2021-07-25 | 6420 | keep | 0 | Jul | 2021 | 0.0043726 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-07-25 18:02 | 2021-07-25 18:03 | 5961 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 5961 | keep | 0 | Jul | 2021 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
CAGUAS | 2021-07-25 18:15 | 2021-07-26 19:53 | 100 | 025:38 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 80, 2 X 65, 1 X 30 Y 1 X 15 EN CORTES DE LINEA Y TRANSFORMADOR LLUVIAS | C21072500203 | New_Event | Bad Weather | Include | Include | Weather | 1538 | 2021-07-25 | 153800 | keep | 0 | Jul | 2021 | 0.10475 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-07-25 18:23 | 2021-07-25 18:24 | 2107 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21072500041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 2107 | keep | 0 | Jul | 2021 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
BAYAMON | 2021-07-25 18:38 | 2021-07-26 12:14 | 40 | 017:36 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | B21072500052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1056 | 2021-07-25 | 42240 | keep | 0 | Jul | 2021 | 0.028769 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-07-25 18:51 | 2021-07-26 12:03 | 100 | 017:12 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA POR DESGANCHE | A21072500043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1032 | 2021-07-25 | 103200 | keep | 0 | Jul | 2021 | 0.070289 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-25 18:52 | 2021-07-26 12:17 | 270 | 017:25 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA LLUVIAS | R21072500120 | New_Event | Bad Weather | Include | Include | Weather | 1045 | 2021-07-25 | 282150 | keep | 0 | Jul | 2021 | 0.19217 | 0.0001839 | Sustained | FALSE | TRUE | Not_TMED_Event | 270
SAN JUAN | 2021-07-25 18:54 | 2021-07-26 05:08 | 55 | 010:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REALIZO REPARACION PROVISIONAL DE POSTE IMPACTADO POR AUTO Y SE RELOCALIZO CRUCETA EN EL MISMO POSTE PARTIDO | S21072500078 | New_Event |  |  | Include | Wildlife | 614 | 2021-07-25 | 33770 | keep | 0 | Jul | 2021 | 0.023001 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CAGUAS | 2021-07-25 19:03 | 2021-07-25 19:04 | 5 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO | C21072500044 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-25 | 5 | keep | 0 | Jul | 2021 | 3.4055e-06 | 3.4055e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-07-25 19:14 | 2021-07-26 16:07 | 12 | 020:53 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA X 37.5 KVA | A21072500044 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1253 | 2021-07-25 | 15036 | keep | 0 | Jul | 2021 | 0.010241 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-07-25 19:18 | 2021-07-26 12:30 | 10 | 017:12 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA POR DESGANCHE | A21072500045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1032 | 2021-07-25 | 10320 | keep | 0 | Jul | 2021 | 0.0070289 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BAYAMON | 2021-07-25 19:31 | 2021-07-25 19:32 | 723 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO LLEVANDO LA CARGA DEL 1711-05 | B21072500000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-25 | 723 | keep | 0 | Jul | 2021 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2021-07-25 19:31 | 2021-07-25 19:32 | 1976 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO CARGA POR EL 1711-02 | S21072500000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-25 | 1976 | keep | 0 | Jul | 2021 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
PONCE | 2021-07-25 19:34 | 2021-07-25 19:35 | 3744 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P21072500031 | New_Event |  |  | Include | Wildlife | 1 | 2021-07-25 | 3744 | keep | 0 | Jul | 2021 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2021-07-25 19:35 | 2021-07-26 08:06 | 125 | 012:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA, AVE CRUZO FASE. | P21072500032 | 1st_after_momentary |  |  | Include | Wildlife | 751 | 2021-07-25 | 93875 | keep | 0 | Jul | 2021 | 0.063938 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
CAGUAS | 2021-07-25 19:41 | 2021-07-26 12:12 | 29 | 016:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE CON AVE | C21072500127 | New_Event |  |  | Include | Wildlife | 991 | 2021-07-25 | 28739 | keep | 0 | Jul | 2021 | 0.019574 | 1.9752e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 29
ARECIBO | 2021-07-25 19:57 | 2021-07-25 19:58 | 67 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21072500048 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-25 | 67 | keep | 0 | Jul | 2021 | 4.5633e-05 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
ARECIBO | 2021-07-25 19:58 | 2021-07-26 10:30 | 50 | 014:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | A21072500055 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 872 | 2021-07-25 | 43600 | keep | 0 | Jul | 2021 | 0.029696 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-07-25 20:08 | 2021-07-26 10:19 | 2 | 014:11 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR POR DESGANCHE | A21072500052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 851 | 2021-07-25 | 1702 | keep | 0 | Jul | 2021 | 0.0011592 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2021-07-25 20:38 | 2021-07-26 12:37 | 100 | 015:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C21072500129 | New_Event | Cutout Failure | Include | Include | Equipment | 959 | 2021-07-25 | 95900 | keep | 0 | Jul | 2021 | 0.065317 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-07-25 20:55 | 2021-07-25 22:05 | 10 | 001:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO PUENTES PARA SECCIONALIZAR ALAMBRE PARTIDO | M21072500056 | New_Event | Wire Down | Include | Include | Equipment | 70 | 2021-07-25 | 700 | keep | 0 | Jul | 2021 | 0.00047677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-07-25 21:03 | 2021-07-25 21:05 | 1902 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21072500128 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-25 | 3804 | keep | 0 | Jul | 2021 | 0.0025909 | 0.0012954 | Momentary | FALSE | TRUE | Not_TMED_Event | 1902
FAJARDO | 2021-07-25 21:03 | 2021-07-25 21:05 | 970 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21072500128 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-25 | 1940 | keep | 0 | Jul | 2021 | 0.0013213 | 0.00066066 | Momentary | FALSE | TRUE | Not_TMED_Event | 970
FAJARDO | 2021-07-25 21:03 | 2021-07-25 21:05 | 3003 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21072500128 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-25 | 6006 | keep | 0 | Jul | 2021 | 0.0040907 | 0.0020453 | Momentary | FALSE | TRUE | Not_TMED_Event | 3003
FAJARDO | 2021-07-25 21:03 | 2021-07-25 21:05 | 2343 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21072500127 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-25 | 4686 | keep | 0 | Jul | 2021 | 0.0031916 | 0.0015958 | Momentary | FALSE | TRUE | Not_TMED_Event | 2343
FAJARDO | 2021-07-25 21:03 | 2021-07-25 21:05 | 1830 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21072500127 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-25 | 3660 | keep | 0 | Jul | 2021 | 0.0024928 | 0.0012464 | Momentary | FALSE | TRUE | Not_TMED_Event | 1830
FAJARDO | 2021-07-25 21:03 | 2021-07-25 21:05 | 710 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21072500127 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-25 | 1420 | keep | 0 | Jul | 2021 | 0.00096716 | 0.00048358 | Momentary | FALSE | TRUE | Not_TMED_Event | 710
FAJARDO | 2021-07-25 21:03 | 2021-07-25 21:05 | 969 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R21072500127 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-07-25 | 1938 | keep | 0 | Jul | 2021 | 0.00132 | 0.00065998 | Momentary | FALSE | TRUE | Not_TMED_Event | 969
FAJARDO | 2021-07-25 21:03 | 2021-07-25 21:08 | 3012 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO | R21072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-07-25 | 15060 | keep | 0 | Jul | 2021 | 0.010257 | 0.0020515 | Momentary | FALSE | FALSE | Not_TMED_Event | 3012
BAYAMON | 2021-07-25 21:12 | 2021-07-26 17:19 | 150 | 020:07 | P | DESGANCHE | 2 X 100 EN SU-1 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21072500073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1207 | 2021-07-25 | 181050 | keep | 0 | Jul | 2021 | 0.12331 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
AGUADILLA | 2021-07-25 21:30 | 2021-07-26 14:03 | 15 | 016:33 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO 50 KVA X 50 KVA | M21072500022 | New_Event | Service Transformer Failure | Include | Include | Equipment | 993 | 2021-07-25 | 14895 | keep | 0 | Jul | 2021 | 0.010145 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-07-25 21:30 | 2021-07-26 13:54 | 120 | 016:24 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE MASIVO | M21072500057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 984 | 2021-07-25 | 118080 | keep | 0 | Jul | 2021 | 0.080424 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
FAJARDO | 2021-07-25 21:31 | 2021-07-26 11:50 | 17 | 014:19 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R21072500130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 859 | 2021-07-25 | 14603 | keep | 0 | Jul | 2021 | 0.009946 | 1.1579e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 17
CAGUAS | 2021-07-25 21:47 | 2021-07-25 21:48 | 1590 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE MAL TIEMPO | C21072500000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-25 | 1590 | keep | 0 | Jul | 2021 | 0.0010829 | 0.0010829 | Momentary | FALSE | FALSE | Not_TMED_Event | 1590
CAGUAS | 2021-07-25 21:47 | 2021-07-25 21:48 | 1510 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE MAL TIEMPO | C21072500000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-25 | 1510 | keep | 0 | Jul | 2021 | 0.0010285 | 0.0010285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1510
CAGUAS | 2021-07-25 21:47 | 2021-07-25 21:50 | 817 | 000:03 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO MAL TIEMPO | C21072500000 | New_Event | Bad Weather | Include | Include | Weather | 3 | 2021-07-25 | 2451 | keep | 0 | Jul | 2021 | 0.0016694 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
CAGUAS | 2021-07-25 21:48 | 2021-07-26 16:36 | 50 | 018:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA LLUVIAS | C21072500150 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1128 | 2021-07-25 | 56400 | keep | 0 | Jul | 2021 | 0.038414 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-25 21:48 | 2021-07-26 14:18 | 270 | 016:30 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA LLUVIAS | C21072500135 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 990 | 2021-07-25 | 267300 | keep | 0 | Jul | 2021 | 0.18206 | 0.0001839 | Sustained | FALSE | TRUE | Not_TMED_Event | 270
CAGUAS | 2021-07-25 21:50 | 2021-07-25 21:51 | 1342 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE MAL TIEMPO | C21072500000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-25 | 1342 | keep | 0 | Jul | 2021 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
CANOVANAS | 2021-07-25 21:52 | 2021-07-26 09:50 | 150 | 011:58 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTES DE LINEA LLUVIAS | R21072500183 | New_Event | Bad Weather | Include | Include | Weather | 718 | 2021-07-25 | 107700 | keep | 0 | Jul | 2021 | 0.073354 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-07-25 21:54 | 2021-07-25 21:55 | 1862 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE MAL TIEMPO | R21072500000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-25 | 1862 | keep | 0 | Jul | 2021 | 0.0012682 | 0.0012682 | Momentary | FALSE | FALSE | Not_TMED_Event | 1862
CAGUAS | 2021-07-25 21:54 | 2021-07-25 21:55 | 1153 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE MAL TIEMPO | C21072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 1153 | keep | 0 | Jul | 2021 | 0.0007853 | 0.0007853 | Momentary | FALSE | FALSE | Not_TMED_Event | 1153
SAN JUAN | 2021-07-25 21:55 | 2021-07-26 12:17 | 100 | 014:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE LEVANTO CONDUCTOR DEL SUELO | R21072600031 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 862 | 2021-07-25 | 86200 | keep | 0 | Jul | 2021 | 0.05871 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-25 21:56 | 2021-07-25 23:03 | 980 | 001:07 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR 1424-08 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1348-06 UN 80% Y 1348-07 UN 100% | S21072500000 | New_Event | Bad Weather | Include | Include | Weather | 67 | 2021-07-25 | 65660 | keep | 0 | Jul | 2021 | 0.044721 | 0.00066747 | Sustained | FALSE | FALSE | Not_TMED_Event | 980
SAN JUAN | 2021-07-25 21:56 | 2021-07-25 23:03 | 278 | 001:07 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR 1424-08 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1348-06 UN 80% Y 1348-07 UN 100% | S21072500000 | New_Event | Bad Weather | Include | Include | Weather | 67 | 2021-07-25 | 18626 | keep | 0 | Jul | 2021 | 0.012686 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2021-07-25 21:56 | 2021-07-25 23:03 | 9 | 001:07 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR 1424-08 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1348-06 UN 80% Y 1348-07 UN 100% MAL TIEMPO | S21072500000 | New_Event | Bad Weather | Include | Include | Weather | 67 | 2021-07-25 | 603 | keep | 0 | Jul | 2021 | 0.0004107 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2021-07-25 21:58 | 2021-07-25 22:00 | 3005 | 000:02 | T | DESGANCHE | DISPARO SE CERRO POR SCADA | C21072500138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-07-25 | 6010 | keep | 0 | Jul | 2021 | 0.0040934 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
CAGUAS | 2021-07-25 22:00 | 2021-07-26 16:23 | 40 | 018:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE CRITICO | C21072500048 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1103 | 2021-07-25 | 44120 | keep | 0 | Jul | 2021 | 0.03005 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-07-25 22:00 | 2021-07-26 14:43 | 400 | 016:43 | P | DESGANCHE | 3 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE CRITICO | C21072500162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1003 | 2021-07-25 | 401200 | keep | 0 | Jul | 2021 | 0.27326 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
SAN JUAN | 2021-07-25 22:02 | 2021-07-25 22:03 | 225 | 000:01 | T | LINEA DE TRANSMISION 115KV | RECERRO 1908-03 LLEVANDO LA CARGA DEL 1303-04 | S21072500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-25 | 225 | keep | 0 | Jul | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-07-25 22:02 | 2021-07-25 22:03 | 3 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37800 | S21072500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-25 | 3 | keep | 0 | Jul | 2021 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | TRUE | Not_TMED_Event | 3
SAN JUAN | 2021-07-25 22:02 | 2021-07-25 22:03 | 3957 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37800 LLEVANDO LA CARGA DEL 1303-04 | S21072500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-25 | 3957 | keep | 0 | Jul | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | TRUE | Not_TMED_Event | 3957
BAYAMON | 2021-07-25 22:02 | 2021-07-25 22:03 | 58 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37800 | S21072500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-25 | 58 | keep | 0 | Jul | 2021 | 3.9504e-05 | 3.9504e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 58
SAN JUAN | 2021-07-25 22:02 | 2021-07-25 22:03 | 386 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37800 | S21072500000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-25 | 386 | keep | 0 | Jul | 2021 | 0.0002629 | 0.0002629 | Momentary | FALSE | TRUE | Not_TMED_Event | 386
MAYAGÃœEZ | 2021-07-25 22:05 | 2021-07-26 11:30 | 2 | 013:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA | M21072500056 | Partial_restoration | Wire Down | Include | Include | Equipment | 805 | 2021-07-25 | 1610 | keep | 0 | Jul | 2021 | 0.0010966 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-25 22:06 | 2021-07-26 13:54 | 50 | 015:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21072500060 | New_Event | Bad Weather | Include | Include | Weather | 948 | 2021-07-25 | 47400 | keep | 0 | Jul | 2021 | 0.032284 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-25 22:11 | 2021-07-25 23:02 | 1565 | 000:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21072500146 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2021-07-25 | 79815 | keep | 0 | Jul | 2021 | 0.054362 | 0.0010659 | Sustained | FALSE | TRUE | Not_TMED_Event | 1565
CAGUAS | 2021-07-25 22:11 | 2021-07-25 23:02 | 976 | 000:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21072500146 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2021-07-25 | 49776 | keep | 0 | Jul | 2021 | 0.033902 | 0.00066475 | Sustained | FALSE | TRUE | Not_TMED_Event | 976
CAGUAS | 2021-07-25 22:11 | 2021-07-25 23:02 | 548 | 000:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21072500146 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2021-07-25 | 27948 | keep | 0 | Jul | 2021 | 0.019035 | 0.00037324 | Sustained | FALSE | TRUE | Not_TMED_Event | 548
CAGUAS | 2021-07-25 22:11 | 2021-07-25 23:02 | 315 | 000:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21072500147 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2021-07-25 | 16065 | keep | 0 | Jul | 2021 | 0.010942 | 0.00021455 | Sustained | FALSE | TRUE | Not_TMED_Event | 315
CAGUAS | 2021-07-25 22:11 | 2021-07-25 23:02 | 870 | 000:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21072500147 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2021-07-25 | 44370 | keep | 0 | Jul | 2021 | 0.03022 | 0.00059255 | Sustained | FALSE | TRUE | Not_TMED_Event | 870
CAGUAS | 2021-07-25 22:11 | 2021-07-25 23:02 | 2906 | 000:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21072500148 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2021-07-25 | 148206 | keep | 0 | Jul | 2021 | 0.10094 | 0.0019793 | Sustained | FALSE | TRUE | Not_TMED_Event | 2906
CAGUAS | 2021-07-25 22:11 | 2021-07-25 23:02 | 2343 | 000:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C21072500148 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2021-07-25 | 119493 | keep | 0 | Jul | 2021 | 0.081386 | 0.0015958 | Sustained | FALSE | TRUE | Not_TMED_Event | 2343
CAGUAS | 2021-07-25 22:17 | 2021-07-26 18:01 | 200 | 019:44 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | C21072500144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1184 | 2021-07-25 | 236800 | keep | 0 | Jul | 2021 | 0.16128 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-07-25 22:21 | 2021-07-25 22:22 | 2770 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21072500149 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 2770 | keep | 0 | Jul | 2021 | 0.0018866 | 0.0018866 | Momentary | FALSE | FALSE | Not_TMED_Event | 2770
FAJARDO | 2021-07-25 22:33 | 2021-07-26 11:45 | 100 | 013:12 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21072500140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 792 | 2021-07-25 | 79200 | keep | 0 | Jul | 2021 | 0.053943 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-07-25 22:34 | 2021-07-26 14:18 | 100 | 015:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE CERRO PUENTE ABRIERTO | C21072500154 | New_Event | Wire Down | Include | Include | Equipment | 944 | 2021-07-25 | 94400 | keep | 0 | Jul | 2021 | 0.064295 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-25 22:49 | 2021-07-25 22:50 | 651 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | B21072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-25 | 651 | keep | 0 | Jul | 2021 | 0.00044339 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
CANOVANAS | 2021-07-25 22:53 | 2021-07-26 14:36 | 200 | 015:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 Y 1 X 80 EN CORTE DE LINEA CRUCE CON AVE | R21072500142 | New_Event |  |  | Include | Wildlife | 943 | 2021-07-25 | 188600 | keep | 0 | Jul | 2021 | 0.12845 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-07-25 23:02 | 2021-07-26 07:36 | 870 | 008:34 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO | C21072500000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 514 | 2021-07-25 | 447180 | keep | 0 | Jul | 2021 | 0.30457 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2021-07-25 23:23 | 2021-07-25 23:24 | 980 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR 1424-08 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1348-06 UN 80% Y 1348-07 UN 100% | S21072500000 | Partial_restoration | Bad Weather | Include | Include | Weather | 1 | 2021-07-25 | 980 | keep | 0 | Jul | 2021 | 0.00066747 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-25 23:23 | 2021-07-25 23:24 | 278 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR 1424-08 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1348-06 UN 80% Y 1348-07 UN 100% | S21072500000 | Partial_restoration | Bad Weather | Include | Include | Weather | 1 | 2021-07-25 | 278 | keep | 0 | Jul | 2021 | 0.00018934 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-25 23:23 | 2021-07-25 23:24 | 9 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR 1424-08 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1348-06 UN 80% Y 1348-07 UN 100% MAL TIEMPO | S21072500000 | Partial_restoration | Bad Weather | Include | Include | Weather | 1 | 2021-07-25 | 9 | keep | 0 | Jul | 2021 | 6.1299e-06 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2021-07-26 00:03 | 2021-07-26 06:36 | 80 | 006:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA POR CAJA PRIMARIA AVERIADA | P21072600001 | New_Event | Cutout Failure | Include | Include | Equipment | 393 | 2021-07-26 | 31440 | keep | 0 | Jul | 2021 | 0.021414 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-07-26 00:23 | 2021-07-26 10:12 | 100 | 009:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA Y 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B21072600018 | New_Event | Cutout Failure | Include | Include | Equipment | 589 | 2021-07-26 | 58900 | keep | 0 | Jul | 2021 | 0.040117 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-26 00:23 | 2021-07-26 06:15 | 3295 | 005:52 | T | DESGANCHE | SE DISPARO INTERRUPTOR SE CERRO POR SCADA | B21072600001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 352 | 2021-07-26 | 1159840 | keep | 0 | Jul | 2021 | 0.78996 | 0.0022442 | Sustained | FALSE | FALSE | Not_TMED_Event | 3295
CANOVANAS | 2021-07-26 00:24 | 2021-07-26 11:17 | 120 | 010:53 | P | DESGANCHE | 1 X 65 Y 1 X 30 EN CORTE DE LINEA | R21072600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 653 | 2021-07-26 | 78360 | keep | 0 | Jul | 2021 | 0.053371 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
ARECIBO | 2021-07-26 00:44 | 2021-07-26 00:45 | 1494 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR CON RECIERRE EN OFF CERRADO POR SCADA | A21072600002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-26 | 1494 | keep | 0 | Jul | 2021 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
ARECIBO | 2021-07-26 00:45 | 2021-07-26 13:41 | 100 | 012:56 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA POR DESGANCHE | A21072600003 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 776 | 2021-07-26 | 77600 | keep | 0 | Jul | 2021 | 0.052853 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-07-26 01:41 | 2021-07-26 11:53 | 50 | 010:12 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | A21072600006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 612 | 2021-07-26 | 30600 | keep | 0 | Jul | 2021 | 0.020842 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-07-26 02:00 | 2021-07-27 10:50 | 4 | 032:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | R21072600002 | New_Event | Cutout Failure | Include | Include | Equipment | 1970 | 2021-07-26 | 7880 | keep | 0 | Jul | 2021 | 0.005367 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2021-07-26 02:12 | 2021-07-26 06:58 | 3012 | 004:46 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO | R21072600000 | New_Event | Wire Down | Include | Include | Equipment | 286 | 2021-07-26 | 861432 | keep | 0 | Jul | 2021 | 0.58672 | 0.0020515 | Sustained | FALSE | FALSE | Not_TMED_Event | 3012
ARECIBO | 2021-07-26 02:26 | 2021-07-26 11:00 | 30 | 008:34 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | A21072600007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 514 | 2021-07-26 | 15420 | keep | 0 | Jul | 2021 | 0.010502 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
AGUADILLA | 2021-07-26 03:20 | 2021-07-26 03:21 | 1192 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M21072600000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-26 | 1192 | keep | 0 | Jul | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2021-07-26 03:21 | 2021-07-27 10:24 | 10 | 031:03 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR POR MAL TIEMPO | M21072600172 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1863 | 2021-07-26 | 18630 | keep | 0 | Jul | 2021 | 0.012689 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-07-26 05:06 | 2021-07-27 17:24 | 20 | 036:18 | P | CABLE SOTERRADO AVERIADO | AVERIA DEL T33 AL T32 SE CONSTRUYO AEREO PROVSIONAL DE EXISTENTE A T32 | C21072600008 | New_Event | UG Cable Fault | Include | Include | Equipment | 2178 | 2021-07-26 | 43560 | keep | 0 | Jul | 2021 | 0.029669 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-07-26 05:49 | 2021-07-26 05:50 | 215 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | B21072600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-26 | 215 | keep | 0 | Jul | 2021 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
BAYAMON | 2021-07-26 06:15 | 2021-07-26 10:48 | 45 | 004:33 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA, 1 X 65 EN CORTE DE LINEA, 1 X 30 EN BANCO DE TRANSFORMADOR Y 1 X 10 EN TRANSFORMADOR | B21072500046 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 273 | 2021-07-26 | 12285 | keep | 0 | Jul | 2021 | 0.0083673 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-07-26 06:24 | 2021-07-26 06:25 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21072600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-26 | 3431 | keep | 0 | Jul | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
CAGUAS | 2021-07-26 06:52 | 2021-07-27 11:33 | 20 | 028:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIAS | C21072600015 | New_Event | Bad Weather | Include | Include | Weather | 1721 | 2021-07-26 | 34420 | keep | 0 | Jul | 2021 | 0.023443 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-07-26 06:54 | 2021-07-26 11:04 | 20 | 004:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE | B21072600003 | New_Event |  |  | Include | Wildlife | 250 | 2021-07-26 | 5000 | keep | 0 | Jul | 2021 | 0.0034055 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CANOVANAS | 2021-07-26 06:58 | 2021-07-26 15:39 | 170 | 008:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 Y 1 X 50 EN CORTE DE LINEA SE RETORNO CONDUCTOR ZAFADO | R21072600119 | Partial_restoration | Wire Down | Include | Include | Equipment | 521 | 2021-07-26 | 88570 | keep | 0 | Jul | 2021 | 0.060325 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
PONCE | 2021-07-26 07:00 | 2021-07-26 09:00 | 1 | 002:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTE DE LINEA, AVE CRUZO FASE. | P21072600002 | New_Event |  |  | Include | Wildlife | 120 | 2021-07-26 | 120 | keep | 0 | Jul | 2021 | 8.1731e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-07-26 07:12 | 2021-07-26 08:30 | 5290 | 001:18 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO LLEVANDO LAS CARGAS DEL 1336-09 Y PARTE DEL 1303-02. SE SECCIONALIZO CONDUCTOR EN EL SUELO ABRIENDO MACHETES | S21072600004 | New_Event | Wire Down | Include | Include | Equipment | 78 | 2021-07-26 | 412620 | keep | 0 | Jul | 2021 | 0.28103 | 0.003603 | Sustained | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2021-07-26 07:12 | 2021-07-26 08:30 | 207 | 001:18 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO ABRIENDO MACHETES CARGA POR EL 1336-08 | S21072600004 | New_Event | Wire Down | Include | Include | Equipment | 78 | 2021-07-26 | 16146 | keep | 0 | Jul | 2021 | 0.010997 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
FAJARDO | 2021-07-26 07:18 | 2021-07-26 12:24 | 100 | 005:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 Y 1 X 10 EN CORTE DE LINEA Y TRANSFORMADOR CRUCE CON AVE | R21072600011 | New_Event |  |  | Include | Wildlife | 306 | 2021-07-26 | 30600 | keep | 0 | Jul | 2021 | 0.020842 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-07-26 07:24 | 2021-07-26 12:30 | 1 | 005:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO TRAMO DE LINEA SECUNDARIA PARTIDA | A21072600011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 306 | 2021-07-26 | 306 | keep | 0 | Jul | 2021 | 0.00020842 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-07-26 07:30 | 2021-07-27 16:18 | 12 | 032:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO NEUTRAL Y VIVO EN SECUNDARIA | B21072600007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1968 | 2021-07-26 | 23616 | keep | 0 | Jul | 2021 | 0.016085 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-07-26 07:31 | 2021-07-26 07:32 | 1569 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE MAL TIEMPO | C21072600023 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-26 | 1569 | keep | 0 | Jul | 2021 | 0.0010686 | 0.0010686 | Momentary | FALSE | FALSE | Not_TMED_Event | 1569
PONCE | 2021-07-26 07:31 | 2021-07-26 07:32 | 752 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21072600004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-26 | 752 | keep | 0 | Jul | 2021 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
PONCE | 2021-07-26 07:31 | 2021-07-26 07:32 | 2696 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21072600004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-26 | 2696 | keep | 0 | Jul | 2021 | 0.0018362 | 0.0018362 | Momentary | FALSE | FALSE | Not_TMED_Event | 2696
CAGUAS | 2021-07-26 07:36 | 2021-07-26 07:37 | 1565 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21072600025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-26 | 1565 | keep | 0 | Jul | 2021 | 0.0010659 | 0.0010659 | Momentary | FALSE | TRUE | Not_TMED_Event | 1565
CAGUAS | 2021-07-26 07:36 | 2021-07-26 07:37 | 976 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21072600025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-26 | 976 | keep | 0 | Jul | 2021 | 0.00066475 | 0.00066475 | Momentary | FALSE | TRUE | Not_TMED_Event | 976
CAGUAS | 2021-07-26 07:36 | 2021-07-26 07:37 | 548 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21072600025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-26 | 548 | keep | 0 | Jul | 2021 | 0.00037324 | 0.00037324 | Momentary | FALSE | TRUE | Not_TMED_Event | 548
CAGUAS | 2021-07-26 07:36 | 2021-07-26 07:37 | 315 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21072600026 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-26 | 315 | keep | 0 | Jul | 2021 | 0.00021455 | 0.00021455 | Momentary | FALSE | TRUE | Not_TMED_Event | 315
CAGUAS | 2021-07-26 07:36 | 2021-07-26 07:37 | 870 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21072600026 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-26 | 870 | keep | 0 | Jul | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | TRUE | Not_TMED_Event | 870
CAGUAS | 2021-07-26 07:36 | 2021-07-26 07:37 | 2906 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21072600027 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-26 | 2906 | keep | 0 | Jul | 2021 | 0.0019793 | 0.0019793 | Momentary | FALSE | TRUE | Not_TMED_Event | 2906
CAGUAS | 2021-07-26 07:36 | 2021-07-26 07:37 | 2343 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C21072600027 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-26 | 2343 | keep | 0 | Jul | 2021 | 0.0015958 | 0.0015958 | Momentary | FALSE | TRUE | Not_TMED_Event | 2343
CAGUAS | 2021-07-26 07:37 | 2021-07-26 09:30 | 870 | 001:53 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO | C21072600000 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 113 | 2021-07-26 | 98310 | keep | 0 | Jul | 2021 | 0.066958 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-07-26 07:40 | 2021-07-26 13:54 | 10 | 006:14 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA X 37.5 KVA | M21072600005 | New_Event | Service Transformer Failure | Include | Include | Equipment | 374 | 2021-07-26 | 3740 | keep | 0 | Jul | 2021 | 0.0025473 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-07-26 07:53 | 2021-07-26 10:00 | 15 | 002:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA DEFECTUOSA | A21072600012 | New_Event | Cutout Failure | Include | Include | Equipment | 127 | 2021-07-26 | 1905 | keep | 0 | Jul | 2021 | 0.0012975 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
VEGA BAJA | 2021-07-26 07:57 | 2021-07-27 19:08 | 60 | 035:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ELIMINO PUENTE PROVISIONAL SE CERRO PUENTE PRIMARIO Y SE REMPLAZO CAJA PRIMARIA | B21072600009 | New_Event | Wire Down | Include | Include | Equipment | 2111 | 2021-07-26 | 126660 | keep | 0 | Jul | 2021 | 0.086268 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-07-26 08:07 | 2021-07-26 15:28 | 30 | 007:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA LINEA PRIMARIA ARRIADA | M21072600008 | New_Event | Wire Down | Include | Include | Equipment | 441 | 2021-07-26 | 13230 | keep | 0 | Jul | 2021 | 0.0090109 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-07-26 08:11 | 2021-07-26 09:31 | 10 | 001:20 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21072600013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 80 | 2021-07-26 | 800 | keep | 0 | Jul | 2021 | 0.00054488 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-07-26 08:13 | 2021-07-26 16:40 | 15 | 008:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO EN LINEA PRIMARIA | P21072600005 | New_Event | Wire Down | Include | Include | Equipment | 507 | 2021-07-26 | 7605 | keep | 0 | Jul | 2021 | 0.0051797 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
ARECIBO | 2021-07-26 08:15 | 2021-07-26 09:40 | 11 | 001:25 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR POR DESGANCHE | A21072600020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2021-07-26 | 935 | keep | 0 | Jul | 2021 | 0.00063682 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
HUMACAO | 2021-07-26 08:20 | 2021-07-26 16:11 | 99 | 007:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIAS | C21072600040 | New_Event | Bad Weather | Include | Include | Weather | 471 | 2021-07-26 | 46629 | keep | 0 | Jul | 2021 | 0.031759 | 6.7428e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 99
BAYAMON | 2021-07-26 08:25 | 2021-07-26 17:52 | 6 | 009:27 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21072600037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 567 | 2021-07-26 | 3402 | keep | 0 | Jul | 2021 | 0.0023171 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2021-07-26 08:27 | 2021-07-26 11:08 | 6 | 002:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR DE DESCRUZO SECUNDARIA | R21072600036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 161 | 2021-07-26 | 966 | keep | 0 | Jul | 2021 | 0.00065794 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-07-26 08:30 | 2021-07-26 13:35 | 3000 | 005:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y SE CERRARON MACHETES | S21072600004 | Partial_restoration | Wire Down | Include | Include | Equipment | 305 | 2021-07-26 | 915000 | keep | 0 | Jul | 2021 | 0.6232 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-07-26 08:33 | 2021-07-26 19:19 | 119 | 010:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100, 1 X 80, 1 X 20 Y 1 X 15 EN CORTES DE LINEA Y TRANSFORMADORES LLUVIAS | C21072600050 | New_Event | Bad Weather | Include | Include | Weather | 646 | 2021-07-26 | 76874 | keep | 0 | Jul | 2021 | 0.052359 | 8.105e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 119
MAYAGÃœEZ | 2021-07-26 08:34 | 2021-07-26 09:50 | 80 | 001:16 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | M21072600010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2021-07-26 | 6080 | keep | 0 | Jul | 2021 | 0.0041411 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-07-26 08:37 | 2021-07-26 14:05 | 40 | 005:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA SE RETIRO IGUANA CRUZANO LINEAS | B21072600018 | New_Event |  |  | Include | Wildlife | 328 | 2021-07-26 | 13120 | keep | 0 | Jul | 2021 | 0.008936 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-07-26 08:38 | 2021-07-26 20:22 | 3 | 011:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIAS | C21072600053 | New_Event | Bad Weather | Include | Include | Weather | 704 | 2021-07-26 | 2112 | keep | 0 | Jul | 2021 | 0.0014385 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2021-07-26 08:46 | 2021-07-26 16:54 | 119 | 008:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA LLUVIAS | C21072600060 | New_Event | Bad Weather | Include | Include | Weather | 488 | 2021-07-26 | 58072 | keep | 0 | Jul | 2021 | 0.039553 | 8.105e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 119
ARECIBO | 2021-07-26 09:00 | 2021-07-26 18:20 | 40 | 009:20 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR POSTES PARTIDOS | A21072600059 | New_Event | Defective Pole | Include | Include | Equipment | 560 | 2021-07-26 | 22400 | keep | 0 | Jul | 2021 | 0.015257 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-07-26 09:13 | 2021-07-26 15:10 | 3 | 005:57 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO | A21072600000 | New_Event | Defective Pole | Include | Include | Equipment | 357 | 2021-07-26 | 1071 | keep | 0 | Jul | 2021 | 0.00072945 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2021-07-26 09:20 | 2021-07-26 09:21 | 1879 | 000:01 | T | SECUNDARIA/DESGANCHE | DISPARO SE CERRO POR CONTROL | C21072600081 | Additional_clients | Secondary Vegetation | Include | Include | Vegetation | 1 | 2021-07-26 | 1879 | keep | 0 | Jul | 2021 | 0.0012798 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-07-26 09:21 | 2021-07-26 10:37 | 6 | 001:16 | P | SECUNDARIA/DESGANCHE | 2 X 15 EN BANCO DE TRANSFORMADOR SE RETIRO ENREDADERA | C21072500111 | 1st_after_momentary | Secondary Vegetation | Include | Include | Vegetation | 76 | 2021-07-26 | 456 | keep | 0 | Jul | 2021 | 0.00031058 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-07-26 09:30 | 2021-07-26 18:32 | 100 | 009:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZARON DISCOS ROTOS SE LEVANTO CONDUCTOR DEL SUELO Y CRUCETA ZAFADA | C21072600000 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 542 | 2021-07-26 | 54200 | keep | 0 | Jul | 2021 | 0.036915 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2021-07-26 09:30 | 2021-07-26 15:50 | 15 | 006:20 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | P21072600011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 380 | 2021-07-26 | 5700 | keep | 0 | Jul | 2021 | 0.0038822 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-07-26 09:40 | 2021-07-26 16:15 | 12 | 006:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | B21072600025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 395 | 2021-07-26 | 4740 | keep | 0 | Jul | 2021 | 0.0032284 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
YAUCO | 2021-07-26 09:45 | 2021-07-27 15:45 | 65 | 030:00 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | P21072600014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1800 | 2021-07-26 | 117000 | keep | 0 | Jul | 2021 | 0.079688 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
CANOVANAS | 2021-07-26 09:50 | 2021-07-26 11:57 | 10 | 002:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LAS LINEAS SECUNDARIAS | R21072600063 | New_Event | Secondary Wire Down | Include | Include | Equipment | 127 | 2021-07-26 | 1270 | keep | 0 | Jul | 2021 | 0.00086499 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-07-26 10:01 | 2021-07-26 16:57 | 3 | 006:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA ABIERTA | C21072500150 | New_Event | Secondary Wire Down | Include | Include | Equipment | 416 | 2021-07-26 | 1248 | keep | 0 | Jul | 2021 | 0.00085001 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
UTUADO | 2021-07-26 10:04 | 2021-07-26 15:43 | 150 | 005:39 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21072600042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 339 | 2021-07-26 | 50850 | keep | 0 | Jul | 2021 | 0.034634 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-07-26 10:09 | 2021-07-27 13:05 | 1 | 026:56 | P | OTRAS CAUSAS | 2 X 25 EN TRANSCLOSURE PROBLEMA DEL CLIENTE | R21072600073 | New_Event | Other Causes | Include | Include | Other | 1616 | 2021-07-26 | 1616 | keep | 0 | Jul | 2021 | 0.0011007 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-07-26 10:09 | 2021-07-26 15:20 | 110 | 005:11 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | C21072600104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 311 | 2021-07-26 | 34210 | keep | 0 | Jul | 2021 | 0.0233 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
SAN JUAN | 2021-07-26 10:22 | 2021-07-26 10:59 | 10 | 000:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21072500019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 37 | 2021-07-26 | 370 | keep | 0 | Jul | 2021 | 0.00025201 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-07-26 10:25 | 2021-07-26 23:15 | 8 | 012:50 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA X LO MISMO | A21072600053 | New_Event | Service Transformer Failure | Include | Include | Equipment | 770 | 2021-07-26 | 6160 | keep | 0 | Jul | 2021 | 0.0041955 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-07-26 10:39 | 2021-07-26 17:09 | 20 | 006:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIAS | C21072600118 | New_Event | Bad Weather | Include | Include | Weather | 390 | 2021-07-26 | 7800 | keep | 0 | Jul | 2021 | 0.0053125 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-07-26 10:43 | 2021-07-26 18:28 | 300 | 007:45 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA LLUVIAS | C21072600119 | New_Event | Bad Weather | Include | Include | Weather | 465 | 2021-07-26 | 139500 | keep | 0 | Jul | 2021 | 0.095013 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
BAYAMON | 2021-07-26 10:43 | 2021-07-26 19:53 | 10 | 009:10 | P | NO SE REPORTO CAUSA | 2 X 30 EN CORTE DE LINEA | B21072600036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 550 | 2021-07-26 | 5500 | keep | 0 | Jul | 2021 | 0.003746 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
VEGA BAJA | 2021-07-26 11:05 | 2021-07-27 19:08 | 40 | 032:03 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21072600040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1923 | 2021-07-26 | 76920 | keep | 0 | Jul | 2021 | 0.05239 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-26 11:15 | 2021-07-26 16:21 | 30 | 005:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN CORTE DE LINEA SE REMPLAZO LIGADURA EN AISLADOR Y SE REALIZO DESGANCHE | B21072600042 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 306 | 2021-07-26 | 9180 | keep | 0 | Jul | 2021 | 0.0062525 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-07-26 11:17 | 2021-07-26 11:30 | 4154 | 000:13 | T | CABLE SOTERRADO AVERIADO | AVERIA DEL SU - 2 AL SU - 3 SE CERRO N/O EN EL SU - C | R21072500129 | New_Event | UG Cable Fault | Include | Include | Equipment | 13 | 2021-07-26 | 54002 | keep | 0 | Jul | 2021 | 0.036781 | 0.0028293 | Sustained | FALSE | FALSE | Not_TMED_Event | 4154
SAN JUAN | 2021-07-26 11:19 | 2021-07-26 13:42 | 10 | 002:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21072600096 | New_Event | Secondary Wire Down | Include | Include | Equipment | 143 | 2021-07-26 | 1430 | keep | 0 | Jul | 2021 | 0.00097397 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-07-26 11:25 | 2021-07-26 13:02 | 12 | 001:37 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21072600046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 97 | 2021-07-26 | 1164 | keep | 0 | Jul | 2021 | 0.0007928 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-07-26 11:26 | 2021-07-28 16:05 | 200 | 052:39 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R21072600095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3159 | 2021-07-26 | 631800 | keep | 0 | Jul | 2021 | 0.43032 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CANOVANAS | 2021-07-26 11:30 | 2021-07-26 13:22 | 75 | 001:52 | P | CABLE SOTERRADO AVERIADO | AVERIA DEL SU - 2 AL SU - 3 SE CERRO N/O EN EL SU - C | R21072500129 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 112 | 2021-07-26 | 8400 | keep | 0 | Jul | 2021 | 0.0057212 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-07-26 11:30 | 2021-07-26 17:04 | 99 | 005:34 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21072600108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 334 | 2021-07-26 | 33066 | keep | 0 | Jul | 2021 | 0.022521 | 6.7428e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 99
CANOVANAS | 2021-07-26 11:30 | 2021-07-26 15:49 | 120 | 004:19 | P | DESGANCHE | 1 X 65 Y 1 X 30 EN CORTE DE LINEA | R21072600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2021-07-26 | 31080 | keep | 0 | Jul | 2021 | 0.021168 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
MAYAGÃœEZ | 2021-07-26 11:30 | 2021-07-26 12:30 | 15 | 001:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA CERRAR PUENTE PRIMARIO | M21072500056 | Additional_clients | Wire Down | Include | Include | Equipment | 60 | 2021-07-26 | 900 | keep | 0 | Jul | 2021 | 0.00061299 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-07-26 11:46 | 2021-07-26 15:12 | 45 | 003:26 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21072600052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2021-07-26 | 9270 | keep | 0 | Jul | 2021 | 0.0063138 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
HUMACAO | 2021-07-26 11:55 | 2021-07-26 11:56 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21072600143 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-26 | 1827 | keep | 0 | Jul | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
UTUADO | 2021-07-26 12:30 | 2021-07-26 14:20 | 20 | 001:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A21072600000 | New_Event | Cutout Failure | Include | Include | Equipment | 110 | 2021-07-26 | 2200 | keep | 0 | Jul | 2021 | 0.0014984 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-07-26 12:30 | 2021-07-26 17:16 | 100 | 004:46 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR POSTE PARTIDO | A21072600000 | New_Event | Defective Pole | Include | Include | Equipment | 286 | 2021-07-26 | 28600 | keep | 0 | Jul | 2021 | 0.019479 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
FAJARDO | 2021-07-26 12:58 | 2021-07-26 16:51 | 5 | 003:53 | P | DESGANCHE | 1 X 20 EN TRANSFRORMADOR | R21072600113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2021-07-26 | 1165 | keep | 0 | Jul | 2021 | 0.00079348 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2021-07-26 13:02 | 2021-07-27 17:38 | 15 | 028:36 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50KVA X 50KVA | R21072600114 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1716 | 2021-07-26 | 25740 | keep | 0 | Jul | 2021 | 0.017531 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2021-07-26 13:07 | 2021-07-26 14:10 | 3 | 001:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN CORTE DE LINEA LLUVIAS | R21072600115 | New_Event | Bad Weather | Include | Include | Weather | 63 | 2021-07-26 | 189 | keep | 0 | Jul | 2021 | 0.00012873 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
FAJARDO | 2021-07-26 13:44 | 2021-07-27 10:11 | 1 | 020:27 | P | OTRAS CAUSAS | 1 X 25 EN TRANSFORMADOR PROBLEMA DEL CLIENTE | R21072600123 | New_Event | Other Causes | Include | Include | Other | 1227 | 2021-07-26 | 1227 | keep | 0 | Jul | 2021 | 0.0008357 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-07-26 13:47 | 2021-07-26 19:44 | 1 | 005:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO BAJANTE SECUNDARIO DE TRANSFORMADOR Y SE REMPLAZO CONECTORES EN LA TOMA | B21072600058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 357 | 2021-07-26 | 357 | keep | 0 | Jul | 2021 | 0.00024315 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-07-26 13:47 | 2021-07-26 16:30 | 60 | 002:43 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | A21072600073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2021-07-26 | 9780 | keep | 0 | Jul | 2021 | 0.0066611 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-07-26 13:54 | 2021-07-26 14:00 | 1617 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21072600072 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-07-26 | 9702 | keep | 0 | Jul | 2021 | 0.006608 | 0.0011013 | Sustained | FALSE | TRUE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-07-26 13:54 | 2021-07-26 14:00 | 1017 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21072600072 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-07-26 | 6102 | keep | 0 | Jul | 2021 | 0.004156 | 0.00069267 | Sustained | FALSE | TRUE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-07-26 13:54 | 2021-07-26 14:00 | 828 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21072600072 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-07-26 | 4968 | keep | 0 | Jul | 2021 | 0.0033837 | 0.00056395 | Sustained | FALSE | TRUE | Not_TMED_Event | 828
MAYAGÃœEZ | 2021-07-26 13:54 | 2021-07-26 14:00 | 863 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21072600073 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-07-26 | 5178 | keep | 0 | Jul | 2021 | 0.0035267 | 0.00058779 | Sustained | FALSE | TRUE | Not_TMED_Event | 863
MAYAGÃœEZ | 2021-07-26 13:54 | 2021-07-26 14:00 | 309 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21072600073 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-07-26 | 1854 | keep | 0 | Jul | 2021 | 0.0012628 | 0.00021046 | Sustained | FALSE | TRUE | Not_TMED_Event | 309
MAYAGÃœEZ | 2021-07-26 13:54 | 2021-07-26 14:00 | 176 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21072600073 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-07-26 | 1056 | keep | 0 | Jul | 2021 | 0.00071924 | 0.00011987 | Sustained | FALSE | TRUE | Not_TMED_Event | 176
MAYAGÃœEZ | 2021-07-26 13:54 | 2021-07-26 14:00 | 108 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21072600074 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-07-26 | 648 | keep | 0 | Jul | 2021 | 0.00044135 | 7.3558e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 108
MAYAGÃœEZ | 2021-07-26 13:54 | 2021-07-26 14:00 | 974 | 000:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M21072600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-07-26 | 5844 | keep | 0 | Jul | 2021 | 0.0039803 | 0.00066339 | Sustained | FALSE | TRUE | Not_TMED_Event | 974
AGUADILLA | 2021-07-26 13:54 | 2021-07-26 13:55 | 569 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21072600063 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-26 | 569 | keep | 0 | Jul | 2021 | 0.00038754 | 0.00038754 | Momentary | FALSE | TRUE | Not_TMED_Event | 569
AGUADILLA | 2021-07-26 13:54 | 2021-07-26 13:55 | 1245 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21072600063 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-26 | 1245 | keep | 0 | Jul | 2021 | 0.00084796 | 0.00084796 | Momentary | FALSE | TRUE | Not_TMED_Event | 1245
AGUADILLA | 2021-07-26 13:54 | 2021-07-26 13:55 | 1155 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21072600063 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-26 | 1155 | keep | 0 | Jul | 2021 | 0.00078667 | 0.00078667 | Momentary | FALSE | TRUE | Not_TMED_Event | 1155
AGUADILLA | 2021-07-26 13:54 | 2021-07-26 13:55 | 867 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21072600064 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-26 | 867 | keep | 0 | Jul | 2021 | 0.00059051 | 0.00059051 | Momentary | FALSE | TRUE | Not_TMED_Event | 867
AGUADILLA | 2021-07-26 13:54 | 2021-07-26 13:55 | 257 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21072600064 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-26 | 257 | keep | 0 | Jul | 2021 | 0.00017504 | 0.00017504 | Momentary | FALSE | TRUE | Not_TMED_Event | 257
AGUADILLA | 2021-07-26 13:54 | 2021-07-26 13:55 | 1336 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21072600064 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-26 | 1336 | keep | 0 | Jul | 2021 | 0.00090994 | 0.00090994 | Momentary | FALSE | TRUE | Not_TMED_Event | 1336
AGUADILLA | 2021-07-26 13:54 | 2021-07-26 13:55 | 3315 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21072600066 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-26 | 3315 | keep | 0 | Jul | 2021 | 0.0022578 | 0.0022578 | Momentary | FALSE | TRUE | Not_TMED_Event | 3315
AGUADILLA | 2021-07-26 13:54 | 2021-07-26 13:55 | 1718 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21072600066 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-26 | 1718 | keep | 0 | Jul | 2021 | 0.0011701 | 0.0011701 | Momentary | FALSE | TRUE | Not_TMED_Event | 1718
MAYAGÃœEZ | 2021-07-26 13:54 | 2021-07-26 15:08 | 3087 | 001:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA SAN SEBASTIAN | M21072600067 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 74 | 2021-07-26 | 228438 | keep | 0 | Jul | 2021 | 0.15559 | 0.0021025 | Sustained | FALSE | FALSE | Not_TMED_Event | 3087
MAYAGÃœEZ | 2021-07-26 13:54 | 2021-07-26 15:08 | 770 | 001:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA SAN SEBASTIAN | M21072600067 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 74 | 2021-07-26 | 56980 | keep | 0 | Jul | 2021 | 0.038809 | 0.00052444 | Sustained | FALSE | FALSE | Not_TMED_Event | 770
MAYAGÃœEZ | 2021-07-26 13:54 | 2021-07-26 15:08 | 1192 | 001:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA SAN SEBASTIAN | M21072600067 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 74 | 2021-07-26 | 88208 | keep | 0 | Jul | 2021 | 0.060078 | 0.00081187 | Sustained | FALSE | FALSE | Not_TMED_Event | 1192
MAYAGÃœEZ | 2021-07-26 13:54 | 2021-07-26 15:08 | 1772 | 001:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA SAN SEBASTIAN | M21072600067 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 74 | 2021-07-26 | 131128 | keep | 0 | Jul | 2021 | 0.089311 | 0.0012069 | Sustained | FALSE | FALSE | Not_TMED_Event | 1772
MAYAGÃœEZ | 2021-07-26 13:54 | 2021-07-26 15:08 | 2174 | 001:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA SAN SEBASTIAN | M21072600069 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 74 | 2021-07-26 | 160876 | keep | 0 | Jul | 2021 | 0.10957 | 0.0014807 | Sustained | FALSE | FALSE | Not_TMED_Event | 2174
MAYAGÃœEZ | 2021-07-26 13:54 | 2021-07-26 15:08 | 64 | 001:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA SAN SEBASTIAN | M21072600069 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 74 | 2021-07-26 | 4736 | keep | 0 | Jul | 2021 | 0.0032257 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
MAYAGÃœEZ | 2021-07-26 13:54 | 2021-07-26 15:08 | 2658 | 001:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA SAN SEBASTIAN | M21072600069 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 74 | 2021-07-26 | 196692 | keep | 0 | Jul | 2021 | 0.13397 | 0.0018104 | Sustained | FALSE | FALSE | Not_TMED_Event | 2658
MAYAGÃœEZ | 2021-07-26 13:54 | 2021-07-26 15:08 | 3522 | 001:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA SAN SEBASTIAN | M21072600070 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 74 | 2021-07-26 | 260628 | keep | 0 | Jul | 2021 | 0.17751 | 0.0023988 | Sustained | FALSE | FALSE | Not_TMED_Event | 3522
MAYAGÃœEZ | 2021-07-26 13:54 | 2021-07-26 15:08 | 1337 | 001:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA SAN SEBASTIAN | M21072600070 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 74 | 2021-07-26 | 98938 | keep | 0 | Jul | 2021 | 0.067386 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
MAYAGÃœEZ | 2021-07-26 13:54 | 2021-07-26 15:08 | 2825 | 001:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA SAN SEBASTIAN | M21072600070 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 74 | 2021-07-26 | 209050 | keep | 0 | Jul | 2021 | 0.14238 | 0.0019241 | Sustained | FALSE | FALSE | Not_TMED_Event | 2825
MAYAGÃœEZ | 2021-07-26 13:54 | 2021-07-26 15:08 | 1287 | 001:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA SAN SEBASTIAN | M21072600070 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 74 | 2021-07-26 | 95238 | keep | 0 | Jul | 2021 | 0.064866 | 0.00087657 | Sustained | FALSE | FALSE | Not_TMED_Event | 1287
MAYAGÃœEZ | 2021-07-26 13:54 | 2021-07-26 15:08 | 1417 | 001:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA SAN SEBASTIAN | M21072600071 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 74 | 2021-07-26 | 104858 | keep | 0 | Jul | 2021 | 0.071418 | 0.00096511 | Sustained | FALSE | FALSE | Not_TMED_Event | 1417
MAYAGÃœEZ | 2021-07-26 13:54 | 2021-07-26 15:08 | 80 | 001:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA SAN SEBASTIAN | M21072600071 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 74 | 2021-07-26 | 5920 | keep | 0 | Jul | 2021 | 0.0040321 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2021-07-26 13:55 | 2021-07-26 18:50 | 120 | 004:55 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE MASIVO | M21072500057 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 295 | 2021-07-26 | 35400 | keep | 0 | Jul | 2021 | 0.024111 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-07-26 13:55 | 2021-07-27 16:00 | 10 | 026:05 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA X 37.5 KVA | M21072600005 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1565 | 2021-07-26 | 15650 | keep | 0 | Jul | 2021 | 0.010659 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-26 13:58 | 2021-07-26 13:59 | 5 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO | S21072600000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-26 | 5 | keep | 0 | Jul | 2021 | 3.4055e-06 | 3.4055e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-07-26 14:17 | 2021-07-28 12:23 | 14 | 046:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO CONDUCTOR NO FUNDIO | C21072600170 | New_Event | Wire Down | Include | Include | Equipment | 2766 | 2021-07-26 | 38724 | keep | 0 | Jul | 2021 | 0.026375 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
VEGA BAJA | 2021-07-26 14:18 | 2021-07-26 14:19 | 652 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21072600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-26 | 652 | keep | 0 | Jul | 2021 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
MAYAGÃœEZ | 2021-07-26 14:25 | 2021-07-26 15:46 | 1235 | 001:21 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO INTERRUPTOR LINEAS CRUZADAS | M21072600102 | New_Event | Wire Down | Include | Include | Equipment | 81 | 2021-07-26 | 100035 | keep | 0 | Jul | 2021 | 0.068133 | 0.00084115 | Sustained | FALSE | TRUE | Not_TMED_Event | 1235
BAYAMON | 2021-07-26 14:41 | 2021-07-26 14:42 | 5 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | S21072600000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-07-26 | 5 | keep | 0 | Jul | 2021 | 3.4055e-06 | 3.4055e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-07-26 14:47 | 2021-07-26 18:37 | 70 | 003:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIAS | C21072600173 | New_Event | Bad Weather | Include | Include | Weather | 230 | 2021-07-26 | 16100 | keep | 0 | Jul | 2021 | 0.010966 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
YAUCO | 2021-07-26 15:05 | 2021-07-26 20:50 | 10 | 005:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON DOS CAJAS PRIMARIAS EN TRANSFORMADOR | P21072600025 | New_Event | Cutout Failure | Include | Include | Equipment | 345 | 2021-07-26 | 3450 | keep | 0 | Jul | 2021 | 0.0023498 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-26 15:06 | 2021-07-26 15:07 | 5 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO Y SE CERRO POR SCADA | S21072600137 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-07-26 | 5 | keep | 0 | Jul | 2021 | 3.4055e-06 | 3.4055e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-07-26 15:08 | 2021-07-26 16:48 | 50 | 001:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21072500060 | Partial_restoration | Bad Weather | Include | Include | Weather | 100 | 2021-07-26 | 5000 | keep | 0 | Jul | 2021 | 0.0034055 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-07-26 15:10 | 2021-07-26 16:45 | 100 | 001:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21072600155 | New_Event | Bad Weather | Include | Include | Weather | 95 | 2021-07-26 | 9500 | keep | 0 | Jul | 2021 | 0.0064704 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-07-26 15:14 | 2021-07-26 18:16 | 100 | 003:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO PUENTE ABIERTO Y SE RETIRO TOPE DE POSTE PARTIDO | R21072600134 | New_Event | Wire Down | Include | Include | Equipment | 182 | 2021-07-26 | 18200 | keep | 0 | Jul | 2021 | 0.012396 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-26 15:15 | 2021-07-27 18:58 | 31 | 027:43 | P | DESGANCHE | 2 X 30 EN CORTES DE LINEA | R21072600136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1663 | 2021-07-26 | 51553 | keep | 0 | Jul | 2021 | 0.035113 | 2.1114e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 31
BAYAMON | 2021-07-26 15:20 | 2021-07-26 17:50 | 5 | 002:30 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO PRIMARIA Y SE CERRO POR SCADA | S21072600138 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 150 | 2021-07-26 | 750 | keep | 0 | Jul | 2021 | 0.00051082 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-07-26 15:22 | 2021-07-26 19:34 | 12 | 004:12 | P | DESGANCHE | 1 X 20 EN TRANSFORMAFDOR SE REALIZO DESGANCHE | S21072600139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 252 | 2021-07-26 | 3024 | keep | 0 | Jul | 2021 | 0.0020596 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2021-07-26 15:22 | 2021-07-26 16:55 | 100 | 001:33 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21072600161 | New_Event | Bad Weather | Include | Include | Weather | 93 | 2021-07-26 | 9300 | keep | 0 | Jul | 2021 | 0.0063342 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-07-26 15:22 | 2021-07-26 18:45 | 70 | 003:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21072600160 | New_Event | Bad Weather | Include | Include | Weather | 203 | 2021-07-26 | 14210 | keep | 0 | Jul | 2021 | 0.0096784 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
CANOVANAS | 2021-07-26 15:24 | 2021-07-26 18:15 | 120 | 002:51 | P | AISLADOR ROTO, PARTIDO O SAFADO | 3 X 40 EN CORTE DE LINEA SE REEMPLAZARON DISCOS ROTOS EN LINEA AEREA Y AISLADORES EN SU | R21072600136 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 171 | 2021-07-26 | 20520 | keep | 0 | Jul | 2021 | 0.013976 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
AGUADILLA | 2021-07-26 15:25 | 2021-07-27 16:38 | 1 | 025:13 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21072600163 | New_Event | Bad Weather | Include | Include | Weather | 1513 | 2021-07-26 | 1513 | keep | 0 | Jul | 2021 | 0.0010305 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-07-26 15:28 | 2021-07-26 16:39 | 20 | 001:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA | M21072600153 | New_Event | Wire Down | Include | Include | Equipment | 71 | 2021-07-26 | 1420 | keep | 0 | Jul | 2021 | 0.00096716 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
AGUADILLA | 2021-07-26 15:33 | 2021-07-27 11:00 | 40 | 019:27 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | M21072600166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1167 | 2021-07-26 | 46680 | keep | 0 | Jul | 2021 | 0.031794 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-07-26 15:39 | 2021-07-26 19:08 | 70 | 003:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR MAL TIEMPO | R21072600141 | New_Event | Bad Weather | Include | Include | Weather | 209 | 2021-07-26 | 14630 | keep | 0 | Jul | 2021 | 0.0099644 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BAYAMON | 2021-07-26 15:40 | 2021-07-26 19:24 | 7 | 003:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA Y UNA TOMA | S21072600140 | New_Event | Secondary Wire Down | Include | Include | Equipment | 224 | 2021-07-26 | 1568 | keep | 0 | Jul | 2021 | 0.001068 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2021-07-26 15:40 | 2021-07-26 18:43 | 59 | 003:03 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21072600137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2021-07-26 | 10797 | keep | 0 | Jul | 2021 | 0.0073538 | 4.0185e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 59
VEGA BAJA | 2021-07-26 15:48 | 2021-07-26 15:49 | 1494 | 000:01 | T | DESGANCHE | RECIERRE | B21072600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-26 | 1494 | keep | 0 | Jul | 2021 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
VEGA BAJA | 2021-07-26 15:49 | 2021-07-27 12:14 | 25 | 020:25 | P | DESGANCHE | 2 X 15 EN TRANSFORMADOR | B21072600077 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1225 | 2021-07-26 | 30625 | keep | 0 | Jul | 2021 | 0.020859 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2021-07-26 16:00 | 2021-07-26 18:13 | 100 | 002:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21072600175 | New_Event | Bad Weather | Include | Include | Weather | 133 | 2021-07-26 | 13300 | keep | 0 | Jul | 2021 | 0.0090586 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
FAJARDO | 2021-07-26 16:02 | 2021-07-26 18:18 | 10 | 002:16 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | R21072600139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 136 | 2021-07-26 | 1360 | keep | 0 | Jul | 2021 | 0.00092629 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CANOVANAS | 2021-07-26 16:02 | 2021-07-26 19:22 | 2 | 003:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | R21072600150 | New_Event | Bad Weather | Include | Include | Weather | 200 | 2021-07-26 | 400 | keep | 0 | Jul | 2021 | 0.00027244 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
MAYAGÃœEZ | 2021-07-26 16:15 | 2021-07-26 17:57 | 100 | 001:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21072600178 | New_Event | Bad Weather | Include | Include | Weather | 102 | 2021-07-26 | 10200 | keep | 0 | Jul | 2021 | 0.0069472 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-26 16:20 | 2021-07-27 13:39 | 10 | 021:19 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21072600068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1279 | 2021-07-26 | 12790 | keep | 0 | Jul | 2021 | 0.0087112 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-07-26 16:28 | 2021-07-27 12:24 | 30 | 019:56 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA POR MAL TIEMPO | M21072600184 | New_Event | Bad Weather | Include | Include | Weather | 1196 | 2021-07-26 | 35880 | keep | 0 | Jul | 2021 | 0.024438 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-07-26 16:32 | 2021-07-26 16:46 | 25 | 000:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A21072600082 | New_Event | Cutout Failure | Include | Include | Equipment | 14 | 2021-07-26 | 350 | keep | 0 | Jul | 2021 | 0.00023838 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-07-26 16:33 | 2021-07-26 17:45 | 11 | 001:12 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJAS DEL TRANSFORMADOR PARA REALIZAR DESGANCHE SECUNDARIO | A21072600056 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 72 | 2021-07-26 | 792 | keep | 0 | Jul | 2021 | 0.00053943 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
PONCE | 2021-07-26 16:40 | 2021-07-26 17:05 | 170 | 000:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABREN MACHETES PARA CERRAR PUENTES ABIERTOS | P21072600005 | New_Event | Wire Down | Include | Include | Equipment | 25 | 2021-07-26 | 4250 | keep | 0 | Jul | 2021 | 0.0028947 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
FAJARDO | 2021-07-26 16:42 | 2021-07-26 18:48 | 30 | 002:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA QUEMADA | R21072600143 | New_Event | Cutout Failure | Include | Include | Equipment | 126 | 2021-07-26 | 3780 | keep | 0 | Jul | 2021 | 0.0025745 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-07-26 16:50 | 2021-07-26 19:05 | 1444 | 002:15 | T | DESGANCHE | CARGA POR 6014-02 | M21072600191 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2021-07-26 | 194940 | keep | 0 | Jul | 2021 | 0.13277 | 0.0009835 | Sustained | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2021-07-26 16:50 | 2021-07-26 19:05 | 3630 | 002:15 | T | DESGANCHE | SE RETIRO ARBOL BAMBUES Y ENRREDADERA SOBRE LINEAS SE REMPLAZO AISLADOR QUEMADO Y SE CERRO INTERRUPTOR LLEVA LA CARGA DEL 6014-01 | M21072600190 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2021-07-26 | 490050 | keep | 0 | Jul | 2021 | 0.33377 | 0.0024724 | Sustained | FALSE | TRUE | Not_TMED_Event | 3630
CAGUAS | 2021-07-26 16:54 | 2021-07-26 20:43 | 70 | 003:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE SECCIONALIZO | C21072600189 | New_Event | Wire Down | Include | Include | Equipment | 229 | 2021-07-26 | 16030 | keep | 0 | Jul | 2021 | 0.010918 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BAYAMON | 2021-07-26 17:06 | 2021-07-26 17:07 | 2466 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21072600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-26 | 2466 | keep | 0 | Jul | 2021 | 0.0016796 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
AGUADILLA | 2021-07-26 17:16 | 2021-07-26 17:17 | 4882 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | M21072600206 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-26 | 4882 | keep | 0 | Jul | 2021 | 0.0033251 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
YAUCO | 2021-07-26 17:25 | 2021-07-26 17:50 | 13 | 000:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P21072600012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 25 | 2021-07-26 | 325 | keep | 0 | Jul | 2021 | 0.00022136 | 8.8542e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 13
VEGA BAJA | 2021-07-26 17:34 | 2021-07-26 17:36 | 4702 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | B21072600074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-26 | 9404 | keep | 0 | Jul | 2021 | 0.006405 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
MAYAGÃœEZ | 2021-07-26 17:56 | 2021-07-26 18:45 | 80 | 000:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21072600215 | New_Event | Bad Weather | Include | Include | Weather | 49 | 2021-07-26 | 3920 | keep | 0 | Jul | 2021 | 0.0026699 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-07-26 18:06 | 2021-07-27 17:44 | 200 | 023:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 EN CORTE DE LINEA SE LEVANTO CONDUCTOR DEL SUELO | C21072600201 | New_Event | Wire Down | Include | Include | Equipment | 1418 | 2021-07-26 | 283600 | keep | 0 | Jul | 2021 | 0.19316 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
PONCE | 2021-07-26 18:06 | 2021-07-26 19:00 | 125 | 000:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA | P21072600029 | New_Event |  |  | Include | Wildlife | 54 | 2021-07-26 | 6750 | keep | 0 | Jul | 2021 | 0.0045974 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
AGUADILLA | 2021-07-26 18:50 | 2021-07-26 19:40 | 15 | 000:50 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA RETIRAR ARBOL SOBRE LINEAS SECUNDARIAS | M21072600036 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 50 | 2021-07-26 | 750 | keep | 0 | Jul | 2021 | 0.00051082 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CANOVANAS | 2021-07-26 19:01 | 2021-07-26 19:18 | 1 | 000:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO | R21072600151 | New_Event | Bad Weather | Include | Include | Weather | 17 | 2021-07-26 | 17 | keep | 0 | Jul | 2021 | 1.1579e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-07-26 19:09 | 2021-07-27 11:24 | 10 | 016:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON VARIAS CONDICIONES EN LA LINEA | C21072600211 | New_Event | Secondary Wire Down | Include | Include | Equipment | 975 | 2021-07-26 | 9750 | keep | 0 | Jul | 2021 | 0.0066407 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
AGUADILLA | 2021-07-26 19:48 | 2021-07-26 21:47 | 100 | 001:59 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21072600225 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2021-07-26 | 11900 | keep | 0 | Jul | 2021 | 0.008105 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-07-26 19:58 | 2021-07-26 19:59 | 15 | 000:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | B21072600031 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-07-26 | 15 | keep | 0 | Jul | 2021 | 1.0216e-05 | 1.0216e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 15
CAGUAS | 2021-07-26 20:01 | 2021-07-27 21:03 | 25 | 025:02 | P | CABLE SOTERRADO AVERIADO | CONSTRUYO PROVISIONAL AEREO DE AEREO EXISTENTE AL T-3 | C21072600217 | New_Event | UG Cable Fault | Include | Include | Equipment | 1502 | 2021-07-26 | 37550 | keep | 0 | Jul | 2021 | 0.025575 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2021-07-26 20:43 | 2021-07-28 09:43 | 45 | 037:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE LEVANTO CONDUCTOR | C21072600189 | Partial_restoration | Wire Down | Include | Include | Equipment | 2220 | 2021-07-26 | 99900 | keep | 0 | Jul | 2021 | 0.068041 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
PONCE | 2021-07-26 20:45 | 2021-07-27 07:45 | 527 | 011:00 | T | DESGANCHE | DISPARO INTERRUPTOR, SE RETIRO ARBOL SOBRE LA LINEA Y SE CERRO PUENTE EN TRONCAL DE ALIMENTADOR | P21072600032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 660 | 2021-07-26 | 347820 | keep | 0 | Jul | 2021 | 0.2369 | 0.00035894 | Sustained | FALSE | TRUE | Not_TMED_Event | 527
ARECIBO | 2021-07-26 21:07 | 2021-07-26 21:08 | 2231 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 14700 | A21072600089 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-26 | 2231 | keep | 0 | Jul | 2021 | 0.0015195 | 0.0015195 | Momentary | FALSE | TRUE | Not_TMED_Event | 2231
ARECIBO | 2021-07-26 21:07 | 2021-07-26 21:08 | 1923 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 14700 | A21072600089 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-26 | 1923 | keep | 0 | Jul | 2021 | 0.0013097 | 0.0013097 | Momentary | FALSE | TRUE | Not_TMED_Event | 1923
ARECIBO | 2021-07-26 21:07 | 2021-07-26 21:08 | 1066 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 14700 | A21072600089 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-26 | 1066 | keep | 0 | Jul | 2021 | 0.00072605 | 0.00072605 | Momentary | FALSE | TRUE | Not_TMED_Event | 1066
ARECIBO | 2021-07-26 21:07 | 2021-07-26 21:08 | 141 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 14700 | A21072600089 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-26 | 141 | keep | 0 | Jul | 2021 | 9.6034e-05 | 9.6034e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 141
ARECIBO | 2021-07-26 21:07 | 2021-07-26 21:08 | 2107 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 14700 | A21072600090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-26 | 2107 | keep | 0 | Jul | 2021 | 0.0014351 | 0.0014351 | Momentary | FALSE | TRUE | Not_TMED_Event | 2107
ARECIBO | 2021-07-26 21:07 | 2021-07-26 21:08 | 308 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 14700 | A21072600090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-26 | 308 | keep | 0 | Jul | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | TRUE | Not_TMED_Event | 308
ARECIBO | 2021-07-26 21:07 | 2021-07-26 21:08 | 2697 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 14700 | A21072600090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-26 | 2697 | keep | 0 | Jul | 2021 | 0.0018369 | 0.0018369 | Momentary | FALSE | TRUE | Not_TMED_Event | 2697
ARECIBO | 2021-07-26 21:07 | 2021-07-26 21:08 | 67 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 14700 | A21072600090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-26 | 67 | keep | 0 | Jul | 2021 | 4.5633e-05 | 4.5633e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 67
AGUADILLA | 2021-07-26 21:18 | 2021-07-27 11:45 | 16 | 014:27 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50KVA X 50KVA | M21072600228 | New_Event | Service Transformer Failure | Include | Include | Equipment | 867 | 2021-07-26 | 13872 | keep | 0 | Jul | 2021 | 0.0094482 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
HUMACAO | 2021-07-26 21:28 | 2021-07-26 21:29 | 2450 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C21072600022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-26 | 2450 | keep | 0 | Jul | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
FAJARDO | 2021-07-26 21:35 | 2021-07-27 10:10 | 70 | 012:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 Y 1 X 30 EN CORTES DE LINEA SE LEVANTANTO CONDUCTOR DEL SUELO | R21072600223 | New_Event | Wire Down | Include | Include | Equipment | 755 | 2021-07-26 | 52850 | keep | 0 | Jul | 2021 | 0.035996 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
SAN JUAN | 2021-07-26 21:50 | 2021-07-27 09:46 | 40 | 011:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA Y SE REALIZO DESGANCHE | S21072600146 | New_Event | Cutout Failure | Include | Include | Equipment | 716 | 2021-07-26 | 28640 | keep | 0 | Jul | 2021 | 0.019507 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-26 22:23 | 2021-07-27 09:28 | 50 | 011:05 | P | NO SE REPORTO CAUSA | 1 X 100 EN CONVERTIDOR | B21072600084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 665 | 2021-07-26 | 33250 | keep | 0 | Jul | 2021 | 0.022646 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-07-26 22:32 | 2021-07-27 13:00 | 14 | 014:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE RFEPARARON BAJANTES SECUNDARIOS DE TRANSFORMADOR | A21072600093 | New_Event | Secondary Wire Down | Include | Include | Equipment | 868 | 2021-07-26 | 12152 | keep | 0 | Jul | 2021 | 0.0082767 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CAGUAS | 2021-07-26 22:49 | 2021-07-27 13:32 | 100 | 014:43 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO TERMINACION QUEMADA | C21072600121 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 883 | 2021-07-26 | 88300 | keep | 0 | Jul | 2021 | 0.060141 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-07-26 22:51 | 2021-07-27 16:28 | 150 | 017:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21072600231 | New_Event | Bad Weather | Include | Include | Weather | 1057 | 2021-07-26 | 158550 | keep | 0 | Jul | 2021 | 0.10799 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-07-26 22:56 | 2021-07-27 13:27 | 50 | 014:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21072600094 | New_Event | Bad Weather | Include | Include | Weather | 871 | 2021-07-26 | 43550 | keep | 0 | Jul | 2021 | 0.029662 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-07-26 23:03 | 2021-07-27 08:22 | 1377 | 009:19 | P | DESCONECTIVO DEFECTUOSO | SE AMARRO ALIMENTADOR CON EL 4003-03 POR MACHETE DE AUXILIAR DE LINEA QUEMADO | P21072600040 | New_Event | Switch Failure | Include | Include | Equipment | 559 | 2021-07-26 | 769743 | keep | 0 | Jul | 2021 | 0.52427 | 0.00093787 | Sustained | FALSE | TRUE | Not_TMED_Event | 1377
SAN JUAN | 2021-07-26 23:53 | 2021-07-27 10:55 | 50 | 011:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21072600149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 662 | 2021-07-26 | 33100 | keep | 0 | Jul | 2021 | 0.022544 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-26 23:59 | 2021-07-27 | 1026 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21072600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-26 | 1026 | keep | 0 | Jul | 2021 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
CAGUAS | 2021-07-27 00:43 | 2021-07-27 00:44 | 1261 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21072700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-27 | 1261 | keep | 0 | Jul | 2021 | 0.00085886 | 0.00085886 | Momentary | FALSE | FALSE | Not_TMED_Event | 1261
CAGUAS | 2021-07-27 00:43 | 2021-07-27 00:44 | 1922 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21072700002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-27 | 1922 | keep | 0 | Jul | 2021 | 0.0013091 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
HUMACAO | 2021-07-27 01:36 | 2021-07-27 10:14 | 99 | 008:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 Y 1 X 50 EN CORTES DE LINEA CRUCE CON AVE | C21072700003 | New_Event |  |  | Include | Wildlife | 518 | 2021-07-27 | 51282 | keep | 0 | Jul | 2021 | 0.034928 | 6.7428e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 99
BAYAMON | 2021-07-27 04:35 | 2021-07-27 04:36 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-27 | 3941 | keep | 0 | Jul | 2021 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
AGUADILLA | 2021-07-27 04:41 | 2021-07-27 19:20 | 100 | 014:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO | M21072700033 | New_Event | Wire Down | Include | Include | Equipment | 879 | 2021-07-27 | 87900 | keep | 0 | Jul | 2021 | 0.059868 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2021-07-27 05:38 | 2021-07-27 05:39 | 2708 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | R21072700003 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-07-27 | 2708 | keep | 0 | Jul | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2021-07-27 05:39 | 2021-07-27 12:17 | 400 | 006:38 | P | AISLADOR ROTO, PARTIDO O SAFADO | 3 X 100 EN CORTES DE LINEA SE REPARARON VARIAS CONDICIONES EN LA LINEA PRIMARIA SE REEMPLAZARON AISLADORES | R21072700006 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 398 | 2021-07-27 | 159200 | keep | 0 | Jul | 2021 | 0.10843 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
SAN JUAN | 2021-07-27 06:45 | 2021-07-27 06:46 | 2179 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21072700009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-27 | 2179 | keep | 0 | Jul | 2021 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
ARECIBO | 2021-07-27 07:00 | 2021-07-27 11:15 | 10 | 004:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21072700002 | New_Event | Bad Weather | Include | Include | Weather | 255 | 2021-07-27 | 2550 | keep | 0 | Jul | 2021 | 0.0017368 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2021-07-27 07:06 | 2021-07-27 20:14 | 400 | 013:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 50 EN CORTE DE LINEA LINEAS PRIMARIAS ARRIADAS | P21072700020 | New_Event | Wire Down | Include | Include | Equipment | 788 | 2021-07-27 | 315200 | keep | 0 | Jul | 2021 | 0.21468 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
VEGA BAJA | 2021-07-27 07:08 | 2021-07-27 16:08 | 25 | 009:00 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21072700009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 540 | 2021-07-27 | 13500 | keep | 0 | Jul | 2021 | 0.0091948 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
HUMACAO | 2021-07-27 07:10 | 2021-07-27 14:18 | 90 | 007:08 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21072700005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 428 | 2021-07-27 | 38520 | keep | 0 | Jul | 2021 | 0.026236 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
VEGA BAJA | 2021-07-27 07:28 | 2021-07-27 08:59 | 20 | 001:31 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21072700022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 91 | 2021-07-27 | 1820 | keep | 0 | Jul | 2021 | 0.0012396 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
AGUADILLA | 2021-07-27 07:30 | 2021-07-27 19:20 | 125 | 011:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M21072700008 | New_Event | Cutout Failure | Include | Include | Equipment | 710 | 2021-07-27 | 88750 | keep | 0 | Jul | 2021 | 0.060447 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
PONCE | 2021-07-27 07:43 | 2021-07-27 09:14 | 20 | 001:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | P21072700010 | New_Event | Secondary Wire Down | Include | Include | Equipment | 91 | 2021-07-27 | 1820 | keep | 0 | Jul | 2021 | 0.0012396 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-07-27 07:45 | 2021-07-27 08:31 | 377 | 000:46 | P | DESGANCHE | INTERRUPTOR SECCIONALIZADO YA QUE INTERRUPTOR NO CIERRA CON LA CARGA TOTAL | P21072700012 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 46 | 2021-07-27 | 17342 | keep | 0 | Jul | 2021 | 0.011812 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-27 08:23 | 2021-07-27 18:30 | 100 | 010:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21072700004 | New_Event | Bad Weather | Include | Include | Weather | 607 | 2021-07-27 | 60700 | keep | 0 | Jul | 2021 | 0.041342 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-27 08:30 | 2021-07-27 19:02 | 100 | 010:32 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO QUE TENIA TRNSFORMADOR CARGA POR EL 1310-04 | S21072700007 | New_Event | Defective Pole | Include | Include | Equipment | 632 | 2021-07-27 | 63200 | keep | 0 | Jul | 2021 | 0.043045 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2021-07-27 08:31 | 2021-07-27 08:37 | 527 | 000:06 | T | DESGANCHE | DISPARO INTERRUPTOR AL REGRESARLE CARGAS. SE CERRO MANUALMENTE | P210727000XX | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 6 | 2021-07-27 | 3162 | keep | 0 | Jul | 2021 | 0.0021536 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-07-27 08:46 | 2021-07-27 10:43 | 8 | 001:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE ABIERTO EN TRONCAL CERCA DE LA SALIDA DEL ALIMENTADOR POR PERSONAL DE RAFAEL QUINTERO | R21072700042 | New_Event | Wire Down | Include | Include | Equipment | 117 | 2021-07-27 | 936 | keep | 0 | Jul | 2021 | 0.00063751 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-07-27 08:54 | 2021-07-27 08:55 | 5809 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR FUE PATRULLADO POR HECTOR GIERBOLINI Y LUIS ANDUJAR NO SE ENCONTRO CAUSA Y SE PROCEDIO A CERRAR POR SCADA A PETICION DE HECTOR GIERBOLINI Y LUIS ANDUJAR | B21072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-27 | 5809 | keep | 0 | Jul | 2021 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
SAN JUAN | 2021-07-27 09:20 | 2021-07-28 09:21 | 30 | 024:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA Y SE REMPLAZO CAJA PRIMARIA | S21072700073 | New_Event | Cutout Failure | Include | Include | Equipment | 1441 | 2021-07-27 | 43230 | keep | 0 | Jul | 2021 | 0.029444 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-07-27 09:20 | 2021-07-27 17:00 | 7 | 007:40 | P | ESTRUCTURA AVERIADA | SE REMPLAZARON POSTES PRIMARIOS | A21072700000 | New_Event | Defective Pole | Include | Include | Equipment | 460 | 2021-07-27 | 3220 | keep | 0 | Jul | 2021 | 0.0021931 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2021-07-27 09:43 | 2021-07-27 09:44 | 1516 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-27 | 1516 | keep | 0 | Jul | 2021 | 0.0010325 | 0.0010325 | Momentary | FALSE | FALSE | Not_TMED_Event | 1516
BAYAMON | 2021-07-27 09:51 | 2021-07-27 13:04 | 10 | 003:13 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANFORMADOR Y SE REPARO SECUNDARIA | S21072500057 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 193 | 2021-07-27 | 1930 | keep | 0 | Jul | 2021 | 0.0013145 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-07-27 10:05 | 2021-07-27 19:15 | 30 | 009:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | A21072700000 | New_Event | Wire Down | Include | Include | Equipment | 550 | 2021-07-27 | 16500 | keep | 0 | Jul | 2021 | 0.011238 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-07-27 10:18 | 2021-07-27 19:45 | 8 | 009:27 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO BEJUCO | P21072700026 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 567 | 2021-07-27 | 4536 | keep | 0 | Jul | 2021 | 0.0030894 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-07-27 10:27 | 2021-07-27 10:28 | 1342 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-27 | 1342 | keep | 0 | Jul | 2021 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
CAGUAS | 2021-07-27 10:28 | 2021-07-27 14:29 | 120 | 004:01 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA SE PATRULLO | C21072700029 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 241 | 2021-07-27 | 28920 | keep | 0 | Jul | 2021 | 0.019697 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
MAYAGÃœEZ | 2021-07-27 10:39 | 2021-07-27 10:41 | 192 | 000:02 | S | NO SE REPORTO CAUSA | DISPARO DE LINEA 1200 | M21072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-27 | 384 | keep | 0 | Jul | 2021 | 0.00026154 | 0.00013077 | Momentary | FALSE | TRUE | Not_TMED_Event | 192
MAYAGÃœEZ | 2021-07-27 10:39 | 2021-07-27 10:41 | 20 | 000:02 | S | NO SE REPORTO CAUSA | DISPARO DE LINEA 1200 | M21072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-27 | 40 | keep | 0 | Jul | 2021 | 2.7244e-05 | 1.3622e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-07-27 10:39 | 2021-07-27 10:41 | 406 | 000:02 | S | NO SE REPORTO CAUSA | DISPARO DE LINEA 1200 | M21072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-27 | 812 | keep | 0 | Jul | 2021 | 0.00055305 | 0.00027652 | Momentary | FALSE | TRUE | Not_TMED_Event | 406
MAYAGÃœEZ | 2021-07-27 10:39 | 2021-07-27 10:41 | 793 | 000:02 | S | NO SE REPORTO CAUSA | DISPARO DE LINEA 1200 | M21072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-27 | 1586 | keep | 0 | Jul | 2021 | 0.0010802 | 0.00054011 | Momentary | FALSE | TRUE | Not_TMED_Event | 793
MAYAGÃœEZ | 2021-07-27 10:39 | 2021-07-27 10:41 | 1509 | 000:02 | S | NO SE REPORTO CAUSA | DISPARO DE LINEA 1200 | M21072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-27 | 3018 | keep | 0 | Jul | 2021 | 0.0020555 | 0.0010278 | Momentary | FALSE | TRUE | Not_TMED_Event | 1509
PONCE | 2021-07-27 10:44 | 2021-07-27 17:57 | 4 | 007:13 | P | SECUNDARIA/DESGANCHE | 1 X 25 EN TRANSFORMADOR SE RETIRO ENREDADERA | P21072700027 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 433 | 2021-07-27 | 1732 | keep | 0 | Jul | 2021 | 0.0011797 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2021-07-27 11:00 | 2021-07-27 15:20 | 10 | 004:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21072600029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 260 | 2021-07-27 | 2600 | keep | 0 | Jul | 2021 | 0.0017708 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-27 11:16 | 2021-07-27 18:15 | 100 | 006:59 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M21072700031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 419 | 2021-07-27 | 41900 | keep | 0 | Jul | 2021 | 0.028538 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-07-27 11:30 | 2021-07-27 11:31 | 1590 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-27 | 1590 | keep | 0 | Jul | 2021 | 0.0010829 | 0.0010829 | Momentary | FALSE | FALSE | Not_TMED_Event | 1590
MAYAGÃœEZ | 2021-07-27 11:34 | 2021-07-27 12:30 | 35 | 000:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21072700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2021-07-27 | 1960 | keep | 0 | Jul | 2021 | 0.0013349 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-07-27 11:55 | 2021-07-27 19:19 | 59 | 007:24 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO INTERRUPTOR 1117-09 POR SEGURIDAD PARA ABRIR EN SU-1 EDIFICIO NEOS Y SECCIONALIZAR AVERIA EN BOVEDA NEOS Y REPARAR QUE DA SERVICIO A SU VEZ EL 50% DEL 1115-02 | S21072700000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 444 | 2021-07-27 | 26196 | keep | 0 | Jul | 2021 | 0.017842 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
BAYAMON | 2021-07-27 11:55 | 2021-07-27 19:19 | 134 | 007:24 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO INTERRUPTOR 1117-09 POR SEGURIDAD PARA ABRIR EN SU-1 EDIFICIO NEOS Y SECCIONALIZAR AVERIA EN BOVEDA NEOS Y REPARAR QUE DA SERVICIO A SU VEZ EL 1115-03 | S21072700000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 444 | 2021-07-27 | 59496 | keep | 0 | Jul | 2021 | 0.040522 | 9.1267e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 134
BAYAMON | 2021-07-27 11:55 | 2021-07-27 19:19 | 34 | 007:24 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO INTERRUPTOR 1117-09 POR SEGURIDAD PARA ABRIR EN SU-1 EDIFICIO NEOS Y SECCIONALIZAR AVERIA EN BOVEDA NEOS Y REPARAR QUE DA SERVICIO A SU VEZ EL 30% DEL 1115-04 | S21072700000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 444 | 2021-07-27 | 15096 | keep | 0 | Jul | 2021 | 0.010282 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
BAYAMON | 2021-07-27 11:55 | 2021-07-27 12:26 | 316 | 000:31 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO INTERRUPTOR 1117-09 POR SEGURIDAD PARA ABRIR EN SU-1 EDIFICIO NEOS Y SECCIONALIZAR AVERIA EN BOVEDA NEOS QUE DA SERVICIO A SU VEZ AL 1115-03, 30% DEL 1115-04 Y 50% 1115-02 | S21072700000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 31 | 2021-07-27 | 9796 | keep | 0 | Jul | 2021 | 0.006672 | 0.00021523 | Sustained | FALSE | FALSE | Not_TMED_Event | 316
AGUADILLA | 2021-07-27 12:18 | 2021-07-27 23:40 | 1192 | 011:22 | S | OTRAS CAUSAS | SE REALIZO LIMPIEZA Y DESCONTAMINACION EN LA SUBESTACION | M21072700046 | New_Event | Other Causes | Include | Include | Other | 682 | 2021-07-27 | 812944 | keep | 0 | Jul | 2021 | 0.55369 | 0.00081187 | Sustained | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2021-07-27 12:18 | 2021-07-27 23:40 | 3041 | 011:22 | S | OTRAS CAUSAS | SE REALIZO LIMPIEZA Y DESCONTAMINACION EN LA SUBESTACION | M21072700046 | New_Event | Other Causes | Include | Include | Other | 682 | 2021-07-27 | 2073962 | keep | 0 | Jul | 2021 | 1.4126 | 0.0020712 | Sustained | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2021-07-27 12:18 | 2021-07-27 23:40 | 390 | 011:22 | S | OTRAS CAUSAS | SE REALIZO LIMPIEZA Y DESCONTAMINACION EN LA SUBESTACION | M21072700046 | New_Event | Other Causes | Include | Include | Other | 682 | 2021-07-27 | 265980 | keep | 0 | Jul | 2021 | 0.18116 | 0.00026563 | Sustained | FALSE | FALSE | Not_TMED_Event | 390
AGUADILLA | 2021-07-27 12:18 | 2021-07-27 23:40 | 650 | 011:22 | S | OTRAS CAUSAS | SE REALIZO LIMPIEZA Y DESCONTAMINACION EN LA SUBESTACION | M21072700046 | New_Event | Other Causes | Include | Include | Other | 682 | 2021-07-27 | 443300 | keep | 0 | Jul | 2021 | 0.30193 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
BAYAMON | 2021-07-27 12:26 | 2021-07-27 18:02 | 96 | 005:36 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | TRAMO SECCIONALIZADO ABRIR EN SU-1 EDIFICIO NEOS AVERIA EN BOVEDA NEOS Y REPARAR Y NORMALIZAR LAS CARGAS | S21072700000 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 336 | 2021-07-27 | 32256 | keep | 0 | Jul | 2021 | 0.021969 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-07-27 12:30 | 2021-07-27 15:01 | 1 | 002:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA QUEMADA | R21072700000 | New_Event | Cutout Failure | Include | Include | Equipment | 151 | 2021-07-27 | 151 | keep | 0 | Jul | 2021 | 0.00010285 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-07-27 12:53 | 2021-07-27 14:41 | 663 | 001:48 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO INTERRUPTOR ABRIENDO CORTE LINEA EN CARRETERA 812 KM 3 7 BARRIO DAJAOS POR ALAMBRE PRIMARIO EN EL PISO | B21072700000 | New_Event | Wire Down | Include | Include | Equipment | 108 | 2021-07-27 | 71604 | keep | 0 | Jul | 2021 | 0.048769 | 0.00045157 | Sustained | FALSE | TRUE | Not_TMED_Event | 663
MAYAGÃœEZ | 2021-07-27 13:28 | 2021-07-27 18:16 | 75 | 004:48 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21072700053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2021-07-27 | 21600 | keep | 0 | Jul | 2021 | 0.014712 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
ARECIBO | 2021-07-27 14:08 | 2021-07-27 19:30 | 40 | 005:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | A21072700000 | New_Event | Cutout Failure | Include | Include | Equipment | 322 | 2021-07-27 | 12880 | keep | 0 | Jul | 2021 | 0.0087725 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-07-27 14:20 | 2021-07-27 14:21 | 353 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S21072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-27 | 353 | keep | 0 | Jul | 2021 | 0.00024043 | 0.00024043 | Momentary | FALSE | FALSE | Not_TMED_Event | 353
MAYAGÃœEZ | 2021-07-27 14:32 | 2021-07-27 14:33 | 1192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21072700066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-27 | 1192 | keep | 0 | Jul | 2021 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
SAN JUAN | 2021-07-27 14:37 | 2021-07-27 19:07 | 37 | 004:30 | P | ESTRUCTURA AVERIADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CRUCETA PARTIDA CARGA POR 1329-02 | S21072700000 | New_Event | Defective Pole | Include | Include | Equipment | 270 | 2021-07-27 | 9990 | keep | 0 | Jul | 2021 | 0.0068041 | 2.5201e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 37
SAN JUAN | 2021-07-27 14:40 | 2021-07-27 19:13 | 60 | 004:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | R21072700017 | New_Event | Cutout Failure | Include | Include | Equipment | 273 | 2021-07-27 | 16380 | keep | 0 | Jul | 2021 | 0.011156 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-07-27 14:40 | 2021-07-28 17:08 | 10 | 026:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN RISER CRUCE POR RATA | R21072700014 | New_Event |  |  | Include | Wildlife | 1588 | 2021-07-27 | 15880 | keep | 0 | Jul | 2021 | 0.010816 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-27 14:40 | 2021-07-27 16:30 | 80 | 001:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21072700012 | New_Event | Wire Down | Include | Include | Equipment | 110 | 2021-07-27 | 8800 | keep | 0 | Jul | 2021 | 0.0059936 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-07-27 14:41 | 2021-07-27 19:08 | 12 | 004:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO TRANSFORMADOR | B21072700076 | New_Event | Secondary Wire Down | Include | Include | Equipment | 267 | 2021-07-27 | 3204 | keep | 0 | Jul | 2021 | 0.0021822 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-07-27 14:41 | 2021-07-27 15:14 | 502 | 000:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO ALAMBRE PRIMARIO | B21072700000 | Partial_restoration | Wire Down | Include | Include | Equipment | 33 | 2021-07-27 | 16566 | keep | 0 | Jul | 2021 | 0.011283 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-27 14:41 | 2021-07-27 15:03 | 20 | 000:22 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21072700072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 22 | 2021-07-27 | 440 | keep | 0 | Jul | 2021 | 0.00029968 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-07-27 14:41 | 2021-07-27 17:52 | 1 | 003:11 | P | NO SE REPORTO CAUSA | 1 X 25 EN BANCO DE TRANSFORMADOR SE INSPECCIONO | C21072700025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 191 | 2021-07-27 | 191 | keep | 0 | Jul | 2021 | 0.00013009 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-07-27 14:41 | 2021-07-27 17:56 | 12 | 003:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | B21072700076 | New_Event | Secondary Wire Down | Include | Include | Equipment | 195 | 2021-07-27 | 2340 | keep | 0 | Jul | 2021 | 0.0015938 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
BAYAMON | 2021-07-27 14:42 | 2021-07-27 20:47 | 10 | 006:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21072700062 | New_Event | Secondary Wire Down | Include | Include | Equipment | 365 | 2021-07-27 | 3650 | keep | 0 | Jul | 2021 | 0.002486 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-27 14:42 | 2021-07-27 17:43 | 70 | 003:01 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | B21072700049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2021-07-27 | 12670 | keep | 0 | Jul | 2021 | 0.0086295 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
CANOVANAS | 2021-07-27 14:42 | 2021-07-28 10:59 | 6 | 020:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | R21072700040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1217 | 2021-07-27 | 7302 | keep | 0 | Jul | 2021 | 0.0049734 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2021-07-27 14:42 | 2021-07-27 18:02 | 110 | 003:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 Y 1 X 40 EN CORTES DE LINEA CRUCE CON AVE | R21072700024 | New_Event |  |  | Include | Wildlife | 200 | 2021-07-27 | 22000 | keep | 0 | Jul | 2021 | 0.014984 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
HUMACAO | 2021-07-27 14:42 | 2021-07-27 18:42 | 19 | 004:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30, 1 X 20 Y 1 X 15 EN CORTE DE LINEA Y TRANSFORMADORES SE REEMPLAZARON CAJAS QUEMADAS | C21072700068 | New_Event | Cutout Failure | Include | Include | Equipment | 240 | 2021-07-27 | 4560 | keep | 0 | Jul | 2021 | 0.0031058 | 1.2941e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 19
HUMACAO | 2021-07-27 14:42 | 2021-07-27 18:50 | 21 | 004:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 50 EN CORTE DE LINEA CRUCE CON LINEA SECUNDARIA | C21072700075 | New_Event | Secondary Wire Down | Include | Include | Equipment | 248 | 2021-07-27 | 5208 | keep | 0 | Jul | 2021 | 0.0035471 | 1.4303e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 21
CAGUAS | 2021-07-27 14:42 | 2021-07-30 20:04 | 4 | 077:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21072700076 | New_Event | Secondary Wire Down | Include | Include | Equipment | 4642 | 2021-07-27 | 18568 | keep | 0 | Jul | 2021 | 0.012647 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2021-07-27 14:42 | 2021-07-27 17:29 | 1 | 002:47 | P | OTRAS CAUSAS | 2 X 30 EN BANCO DE TRANSFORMADOR PROBLEMA DEL CLIENTE | C21072600090 | New_Event | Other Causes | Include | Include | Other | 167 | 2021-07-27 | 167 | keep | 0 | Jul | 2021 | 0.00011374 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-07-27 14:42 | 2021-07-28 13:56 | 20 | 023:14 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 15KVA X LO MISMO | A21072700014 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1394 | 2021-07-27 | 27880 | keep | 0 | Jul | 2021 | 0.018989 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-07-27 14:42 | 2021-07-28 15:12 | 50 | 024:30 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21072700082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1470 | 2021-07-27 | 73500 | keep | 0 | Jul | 2021 | 0.050061 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-07-27 14:55 | 2021-07-27 15:20 | 1 | 000:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN TRANSFORMADOR SE REPARO LINEAS CRUZADAS | M21072700000 | New_Event | Wire Down | Include | Include | Equipment | 25 | 2021-07-27 | 25 | keep | 0 | Jul | 2021 | 1.7027e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BARRANQUITAS | 2021-07-27 14:57 | 2021-07-27 16:57 | 300 | 002:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 Y 1 X 40 EN CORTES DE LINEA SE LEVANTO CONDUCTOR DEL SUELO WR 5902333 | C21072700000 | New_Event | Wire Down | Include | Include | Equipment | 120 | 2021-07-27 | 36000 | keep | 0 | Jul | 2021 | 0.024519 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
ARECIBO | 2021-07-27 15:03 | 2021-07-27 18:30 | 17 | 003:27 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REMPLAZARON CONECTORES | A21072700000 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 207 | 2021-07-27 | 3519 | keep | 0 | Jul | 2021 | 0.0023968 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2021-07-27 15:24 | 2021-07-28 16:27 | 10 | 025:03 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR SE REALIZO DESGANCHE | S21072700060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1503 | 2021-07-27 | 15030 | keep | 0 | Jul | 2021 | 0.010237 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-27 15:29 | 2021-07-27 15:30 | 353 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S21072700069 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-27 | 353 | keep | 0 | Jul | 2021 | 0.00024043 | 0.00024043 | Momentary | FALSE | FALSE | Not_TMED_Event | 353
MAYAGÃœEZ | 2021-07-27 15:39 | 2021-07-27 15:50 | 50 | 000:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21072700000 | New_Event | Bad Weather | Include | Include | Weather | 11 | 2021-07-27 | 550 | keep | 0 | Jul | 2021 | 0.0003746 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-27 15:40 | 2021-07-27 15:41 | 1342 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-27 | 1342 | keep | 0 | Jul | 2021 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
ARECIBO | 2021-07-27 15:40 | 2021-07-27 17:00 | 7 | 001:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA EN TRANSFORMADOR | A21072700000 | New_Event | Cutout Failure | Include | Include | Equipment | 80 | 2021-07-27 | 560 | keep | 0 | Jul | 2021 | 0.00038141 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-07-27 16:00 | 2021-07-27 17:05 | 6 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO NEUTRAL SECUNDARIO | A21072700013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2021-07-27 | 390 | keep | 0 | Jul | 2021 | 0.00026563 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-07-27 16:30 | 2021-07-27 16:55 | 60 | 000:25 | P | NO SE REPORTO CAUSA | 2 X 50 EN TRANSCLOSURE | B21072700109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 25 | 2021-07-27 | 1500 | keep | 0 | Jul | 2021 | 0.0010216 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2021-07-27 16:41 | 2021-07-27 18:00 | 14 | 001:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 20 EN CORTE DE LINEA CRUCE CON AVE | C21072700035 | New_Event |  |  | Include | Wildlife | 79 | 2021-07-27 | 1106 | keep | 0 | Jul | 2021 | 0.00075329 | 9.5353e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 14
MAYAGÃœEZ | 2021-07-27 17:12 | 2021-07-27 17:13 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21072700070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-27 | 393 | keep | 0 | Jul | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
ARECIBO | 2021-07-27 17:17 | 2021-07-27 19:35 | 8 | 002:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA EN TRANSFORMADOR | A21072700000 | New_Event | Cutout Failure | Include | Include | Equipment | 138 | 2021-07-27 | 1104 | keep | 0 | Jul | 2021 | 0.00075193 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-07-27 18:02 | 2021-07-27 19:19 | 316 | 001:17 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO INTERRUPTOR 1117-09 POR SEGURIDAD PARA RETIRAR TIERRAS Y HACER PRUEBA DE CABLE EDIFICIO NEOS Y NORMALIZAR LAS CARGAS DE BOVEDA NEOS QUE DA SERVICIO A SU VEZ AL 1115-03, 30% DEL 1115-04 Y 50% 1115-02 | S21072700000 | Additional_clients | UG - Broken Splice / Terminal | Include | Include | Equipment | 77 | 2021-07-27 | 24332 | keep | 0 | Jul | 2021 | 0.016572 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2021-07-27 18:31 | 2021-07-27 19:35 | 3003 | 001:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE CERCA DE LA SALIDA DE LA SUBESTACION | R21072700043 | New_Event | Wire Down | Include | Include | Equipment | 64 | 2021-07-27 | 192192 | keep | 0 | Jul | 2021 | 0.1309 | 0.0020453 | Sustained | FALSE | FALSE | Not_TMED_Event | 3003
SAN JUAN | 2021-07-27 18:41 | 2021-07-27 18:42 | 5062 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-27 | 5062 | keep | 0 | Jul | 2021 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
SAN JUAN | 2021-07-27 18:49 | 2021-07-28 10:09 | 160 | 015:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE CORTE DE LINEA NO FUNDIO FUSIBLE | S21072700072 | New_Event | Wire Down | Include | Include | Equipment | 920 | 2021-07-27 | 147200 | keep | 0 | Jul | 2021 | 0.10026 | 0.00010898 | Sustained | FALSE | TRUE | Not_TMED_Event | 160
BAYAMON | 2021-07-27 18:49 | 2021-07-27 22:07 | 45 | 003:18 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21072700113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 198 | 2021-07-27 | 8910 | keep | 0 | Jul | 2021 | 0.0060686 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
HUMACAO | 2021-07-27 18:50 | 2021-07-27 18:51 | 3420 | 000:01 | T | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | DISPARO SE CERRO POR CONTROL | C21072700000 | Additional_clients | Secondary Wire Down | Include | Include | Equipment | 1 | 2021-07-27 | 3420 | keep | 0 | Jul | 2021 | 0.0023293 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-07-27 18:51 | 2021-07-28 16:50 | 21 | 021:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 50 EN CORTE DE LINEA CRUCE CON LINEA SECUNDARIA | C21072700075 | 1st_after_momentary | Secondary Wire Down | Include | Include | Equipment | 1319 | 2021-07-27 | 27699 | keep | 0 | Jul | 2021 | 0.018866 | 1.4303e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 21
CANOVANAS | 2021-07-27 19:01 | 2021-07-27 20:54 | 1 | 001:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA CRUCE CON AVE | R21072700045 | New_Event |  |  | Include | Wildlife | 113 | 2021-07-27 | 113 | keep | 0 | Jul | 2021 | 7.6964e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CANOVANAS | 2021-07-27 19:07 | 2021-07-27 19:45 | 200 | 000:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | R21072700047 | New_Event | Cutout Failure | Include | Include | Equipment | 38 | 2021-07-27 | 7600 | keep | 0 | Jul | 2021 | 0.0051763 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
AGUADILLA | 2021-07-27 19:20 | 2021-07-27 19:40 | 300 | 000:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES PARA REPARAR PUENTE PRIMARIO ABIERTO | M21072700033 | New_Event | Wire Down | Include | Include | Equipment | 20 | 2021-07-27 | 6000 | keep | 0 | Jul | 2021 | 0.0040866 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
AGUADILLA | 2021-07-27 19:20 | 2021-07-27 19:40 | 300 | 000:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO CORTE DE LINEA ANTERIOR PARA REMPLAZAR CAJA PRIMARIA AVERIADA | M21072700000 | New_Event | Cutout Failure | Include | Include | Equipment | 20 | 2021-07-27 | 6000 | keep | 0 | Jul | 2021 | 0.0040866 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
BAYAMON | 2021-07-27 19:21 | 2021-07-28 08:08 | 1399 | 012:47 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 LLEVANDO LA CARGA DEL 1704-02 | B21072700117 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 767 | 2021-07-27 | 1073033 | keep | 0 | Jul | 2021 | 0.73084 | 0.00095285 | Sustained | FALSE | TRUE | Not_TMED_Event | 1399
BAYAMON | 2021-07-27 19:21 | 2021-07-28 08:09 | 302 | 012:48 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 CARGA POR EL 1704-01 | B21072700117 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 768 | 2021-07-27 | 231936 | keep | 0 | Jul | 2021 | 0.15797 | 0.00020569 | Sustained | FALSE | TRUE | Not_TMED_Event | 302
BAYAMON | 2021-07-27 19:21 | 2021-07-28 08:09 | 1048 | 012:48 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21072700117 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 768 | 2021-07-27 | 804864 | keep | 0 | Jul | 2021 | 0.54819 | 0.00071379 | Sustained | FALSE | TRUE | Not_TMED_Event | 1048
BAYAMON | 2021-07-27 19:21 | 2021-07-28 08:09 | 573 | 012:48 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 LLEVANDO LA CARGA DEL 1704-05 | B21072700117 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 768 | 2021-07-27 | 440064 | keep | 0 | Jul | 2021 | 0.29973 | 0.00039027 | Sustained | FALSE | TRUE | Not_TMED_Event | 573
BAYAMON | 2021-07-27 19:21 | 2021-07-28 08:09 | 1313 | 012:48 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 CARGA POR EL 1704-04 | B21072700117 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 768 | 2021-07-27 | 1008384 | keep | 0 | Jul | 2021 | 0.68681 | 0.00089428 | Sustained | FALSE | TRUE | Not_TMED_Event | 1313
BAYAMON | 2021-07-27 19:21 | 2021-07-27 19:24 | 1715 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21072700118 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-27 | 5145 | keep | 0 | Jul | 2021 | 0.0035042 | 0.0011681 | Momentary | FALSE | TRUE | Not_TMED_Event | 1715
BAYAMON | 2021-07-27 19:21 | 2021-07-27 19:24 | 1498 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 LLEVANDO LA CARGA DEL 1708-02 | B21072700118 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-27 | 4494 | keep | 0 | Jul | 2021 | 0.0030608 | 0.0010203 | Momentary | FALSE | TRUE | Not_TMED_Event | 1498
BAYAMON | 2021-07-27 19:21 | 2021-07-27 19:24 | 1221 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21072700118 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-27 | 3663 | keep | 0 | Jul | 2021 | 0.0024949 | 0.00083162 | Momentary | FALSE | TRUE | Not_TMED_Event | 1221
BAYAMON | 2021-07-27 19:21 | 2021-07-27 19:24 | 1100 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21072700118 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-27 | 3300 | keep | 0 | Jul | 2021 | 0.0022476 | 0.0007492 | Momentary | FALSE | TRUE | Not_TMED_Event | 1100
HUMACAO | 2021-07-27 19:22 | 2021-07-28 14:45 | 120 | 019:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE LEVANTO CONDUCTOR DEL SUELO | C21072700099 | New_Event | Wire Down | Include | Include | Equipment | 1163 | 2021-07-27 | 139560 | keep | 0 | Jul | 2021 | 0.095054 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
BAYAMON | 2021-07-27 19:26 | 2021-07-27 19:27 | 1715 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21072700118 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-27 | 1715 | keep | 0 | Jul | 2021 | 0.0011681 | 0.0011681 | Momentary | FALSE | TRUE | Not_TMED_Event | 1715
BAYAMON | 2021-07-27 19:26 | 2021-07-27 19:27 | 1498 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 LLEVANDO LA CARGA DEL 1708-02 | B21072700118 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-27 | 1498 | keep | 0 | Jul | 2021 | 0.0010203 | 0.0010203 | Momentary | FALSE | TRUE | Not_TMED_Event | 1498
BAYAMON | 2021-07-27 19:26 | 2021-07-27 19:27 | 1221 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21072700118 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-27 | 1221 | keep | 0 | Jul | 2021 | 0.00083162 | 0.00083162 | Momentary | FALSE | TRUE | Not_TMED_Event | 1221
BAYAMON | 2021-07-27 19:26 | 2021-07-27 19:27 | 1100 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B21072700118 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-27 | 1100 | keep | 0 | Jul | 2021 | 0.0007492 | 0.0007492 | Momentary | FALSE | TRUE | Not_TMED_Event | 1100
CAGUAS | 2021-07-27 19:29 | 2021-07-28 19:15 | 22 | 023:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | C21072700101 | New_Event | Wire Down | Include | Include | Equipment | 1426 | 2021-07-27 | 31372 | keep | 0 | Jul | 2021 | 0.021367 | 1.4984e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 22
BAYAMON | 2021-07-27 19:32 | 2021-07-28 13:57 | 40 | 018:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 40 EN CORTE DE LINEA SE REPARO CONDUCTOR | B21072700079 | New_Event | Wire Down | Include | Include | Equipment | 1105 | 2021-07-27 | 44200 | keep | 0 | Jul | 2021 | 0.030104 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-07-27 19:40 | 2021-07-27 20:21 | 200 | 000:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO Y SE CERRO CORTE DE LINEA | A21072700020 | New_Event | Wire Down | Include | Include | Equipment | 41 | 2021-07-27 | 8200 | keep | 0 | Jul | 2021 | 0.005585 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
VEGA BAJA | 2021-07-27 19:41 | 2021-07-28 08:49 | 12 | 013:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | B21072700120 | New_Event | Secondary Wire Down | Include | Include | Equipment | 788 | 2021-07-27 | 9456 | keep | 0 | Jul | 2021 | 0.0064404 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2021-07-27 20:02 | 2021-07-28 13:53 | 10 | 017:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR REPARO SECUNDARIA | R21072700054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1071 | 2021-07-27 | 10710 | keep | 0 | Jul | 2021 | 0.0072945 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-07-27 20:21 | 2021-07-28 13:02 | 50 | 016:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21072700105 | New_Event | Bad Weather | Include | Include | Weather | 1001 | 2021-07-27 | 50050 | keep | 0 | Jul | 2021 | 0.034089 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-27 20:37 | 2021-07-27 20:38 | 3070 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-27 | 3070 | keep | 0 | Jul | 2021 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
GUAYAMA | 2021-07-27 21:39 | 2021-07-28 11:12 | 100 | 013:33 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P21072800036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 813 | 2021-07-27 | 81300 | keep | 0 | Jul | 2021 | 0.055373 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
FAJARDO | 2021-07-27 21:41 | 2021-07-28 05:05 | 30 | 007:24 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21072700056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 444 | 2021-07-27 | 13320 | keep | 0 | Jul | 2021 | 0.0090722 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-07-27 21:47 | 2021-07-28 13:20 | 60 | 015:33 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | A21072700023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 933 | 2021-07-27 | 55980 | keep | 0 | Jul | 2021 | 0.038128 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-07-27 22:22 | 2021-07-28 17:13 | 10 | 018:51 | P | SECUNDARIA/DESGANCHE | 2 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | S21072700089 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1131 | 2021-07-27 | 11310 | keep | 0 | Jul | 2021 | 0.0077032 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-27 22:25 | 2021-07-28 17:00 | 8 | 018:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21072700138 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1115 | 2021-07-27 | 8920 | keep | 0 | Jul | 2021 | 0.0060754 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-07-27 23:04 | 2021-07-28 12:06 | 60 | 013:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | A21072700025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 782 | 2021-07-27 | 46920 | keep | 0 | Jul | 2021 | 0.031957 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-07-27 23:49 | 2021-07-28 11:44 | 35 | 011:55 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21072700090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 715 | 2021-07-27 | 25025 | keep | 0 | Jul | 2021 | 0.017044 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
CAGUAS | 2021-07-27 23:50 | 2021-07-28 16:00 | 6 | 016:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN EL TRANSFORMADOR SE REPARARON VARIAS CONDICIONES EN LA LINEA SECUNDARIA | C21072700112 | New_Event | Secondary Wire Down | Include | Include | Equipment | 970 | 2021-07-27 | 5820 | keep | 0 | Jul | 2021 | 0.003964 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
ARECIBO | 2021-07-28 00:17 | 2021-07-28 00:18 | 2888 | 000:01 | T | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | DISPARO DE INTERRUPTOR CON RECIERRE EN OFF CERRADO POR SCADA | A21072800001 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1 | 2021-07-28 | 2888 | keep | 0 | Jul | 2021 | 0.001967 | 0.001967 | Momentary | FALSE | FALSE | Not_TMED_Event | 2888
ARECIBO | 2021-07-28 00:18 | 2021-07-28 10:00 | 10 | 009:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON BAJANTES SECUNDARIOS EN TRANSFORMADOR | A21072800008 | 1st_after_momentary | Secondary Wire Down | Include | Include | Equipment | 582 | 2021-07-28 | 5820 | keep | 0 | Jul | 2021 | 0.003964 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-28 00:31 | 2021-07-30 10:07 | 45 | 057:36 | P | CABLE SOTERRADO AVERIADO | 1 X 50 RISER SE REPARO TRAMO | B21072800003 | New_Event | UG Cable Fault | Include | Include | Equipment | 3456 | 2021-07-28 | 155520 | keep | 0 | Jul | 2021 | 0.10592 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2021-07-28 00:40 | 2021-07-28 08:27 | 100 | 007:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | R21072800001 | New_Event |  |  | Include | Wildlife | 467 | 2021-07-28 | 46700 | keep | 0 | Jul | 2021 | 0.031807 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-07-28 01:26 | 2021-07-28 13:36 | 50 | 012:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO DESCARGAS ELECTRICAS | M21072800001 | New_Event | Bad Weather | Include | Include | Weather | 730 | 2021-07-28 | 36500 | keep | 0 | Jul | 2021 | 0.02486 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-07-28 02:19 | 2021-07-28 09:34 | 1 | 007:15 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21072800002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 435 | 2021-07-28 | 435 | keep | 0 | Jul | 2021 | 0.00029628 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-07-28 02:24 | 2021-07-28 14:30 | 80 | 012:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 Y 2 X 80 EN CORTE DE LINEA SE DESGANCHO Y SE REPARO CONDUCTOR | B21072800004 | New_Event | Wire Down | Include | Include | Equipment | 726 | 2021-07-28 | 58080 | keep | 0 | Jul | 2021 | 0.039558 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-07-28 02:40 | 2021-07-28 10:47 | 30 | 008:07 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | B21072800005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 487 | 2021-07-28 | 14610 | keep | 0 | Jul | 2021 | 0.0099508 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-07-28 02:45 | 2021-07-28 02:46 | 2560 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21072800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-28 | 2560 | keep | 0 | Jul | 2021 | 0.0017436 | 0.0017436 | Momentary | FALSE | FALSE | Not_TMED_Event | 2560
YAUCO | 2021-07-28 03:32 | 2021-07-28 03:33 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR 5602-02 | P21072800005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-28 | 1352 | keep | 0 | Jul | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
YAUCO | 2021-07-28 03:32 | 2021-07-28 03:33 | 3973 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21072800005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-28 | 3973 | keep | 0 | Jul | 2021 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
FAJARDO | 2021-07-28 03:57 | 2021-07-28 05:05 | 11 | 001:08 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA X 50 KVA | R21072800003 | New_Event | Service Transformer Failure | Include | Include | Equipment | 68 | 2021-07-28 | 748 | keep | 0 | Jul | 2021 | 0.00050946 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2021-07-28 04:00 | 2021-07-28 11:02 | 50 | 007:02 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LA LINEA PRIMARIA | M21072280003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 422 | 2021-07-28 | 21100 | keep | 0 | Jul | 2021 | 0.014371 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-28 04:15 | 2021-07-28 20:14 | 130 | 015:59 | P | ESTRUCTURA AVERIADA | 2 X 65 EN CORTE DE LINEA SE REEMPLAZO POSTE PARTIDO | C21072800015 | New_Event | Defective Pole | Include | Include | Equipment | 959 | 2021-07-28 | 124670 | keep | 0 | Jul | 2021 | 0.084912 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
BAYAMON | 2021-07-28 04:41 | 2021-07-28 10:11 | 100 | 005:30 | P | NO SE REPORTO CAUSA | 1 X 100 EN CONVERTIDOR | S21072800005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 330 | 2021-07-28 | 33000 | keep | 0 | Jul | 2021 | 0.022476 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2021-07-28 05:05 | 2021-07-28 05:06 | 2722 | 000:01 | T | DESGANCHE | RECIERRE | R21072800000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-28 | 2722 | keep | 0 | Jul | 2021 | 0.0018539 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2021-07-28 05:06 | 2021-07-28 09:55 | 30 | 004:49 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21072700056 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 289 | 2021-07-28 | 8670 | keep | 0 | Jul | 2021 | 0.0059051 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
FAJARDO | 2021-07-28 05:06 | 2021-07-28 16:05 | 11 | 010:59 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA X 50 KVA | R21072800003 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 659 | 2021-07-28 | 7249 | keep | 0 | Jul | 2021 | 0.0049373 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-07-28 05:20 | 2021-07-28 05:21 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21072800006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-28 | 3744 | keep | 0 | Jul | 2021 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2021-07-28 05:20 | 2021-07-28 05:21 | 3114 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR CARGA POR 5004-06 | P21072800006 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-28 | 3114 | keep | 0 | Jul | 2021 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
PONCE | 2021-07-28 05:44 | 2021-07-28 05:45 | 1478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21072800008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-28 | 1478 | keep | 0 | Jul | 2021 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
MAYAGÃœEZ | 2021-07-28 06:00 | 2021-07-28 12:08 | 300 | 006:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | WR5902964 | New_Event | Cutout Failure | Include | Include | Equipment | 368 | 2021-07-28 | 110400 | keep | 0 | Jul | 2021 | 0.075193 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
GUAYAMA | 2021-07-28 06:06 | 2021-07-28 10:28 | 65 | 004:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | P21072800009 | New_Event | Bad Weather | Include | Include | Weather | 262 | 2021-07-28 | 17030 | keep | 0 | Jul | 2021 | 0.011599 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
PONCE | 2021-07-28 06:54 | 2021-07-28 12:17 | 140 | 005:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 EN CORTE DE LINEA. LINEA PRIMARIA SOBRE CRUCETA. SE ABREN MACHETES PARA SECCIONALIZAR AVERIA. | P21072800012 | New_Event | Wire Down | Include | Include | Equipment | 323 | 2021-07-28 | 45220 | keep | 0 | Jul | 2021 | 0.030799 | 9.5353e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 140
BAYAMON | 2021-07-28 06:55 | 2021-07-28 09:24 | 40 | 002:29 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21072800011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 149 | 2021-07-28 | 5960 | keep | 0 | Jul | 2021 | 0.0040593 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-07-28 07:00 | 2021-07-28 13:36 | 30 | 006:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA QUEMADA NO FUNDIO | S21072800007 | New_Event | Cutout Failure | Include | Include | Equipment | 396 | 2021-07-28 | 11880 | keep | 0 | Jul | 2021 | 0.0080914 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2021-07-28 07:09 | 2021-07-28 16:00 | 80 | 008:51 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA REMPLAZO DE AISLADOR Y RETEZAR LINEA. | A21072800058 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 531 | 2021-07-28 | 42480 | keep | 0 | Jul | 2021 | 0.028933 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-07-28 07:14 | 2021-07-28 13:25 | 16 | 006:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJAS | A21072800004 | New_Event | Cutout Failure | Include | Include | Equipment | 371 | 2021-07-28 | 5936 | keep | 0 | Jul | 2021 | 0.004043 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
UTUADO | 2021-07-28 07:14 | 2021-07-28 10:37 | 8 | 003:23 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR | A21072800005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2021-07-28 | 1624 | keep | 0 | Jul | 2021 | 0.0011061 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-07-28 07:17 | 2021-07-28 18:20 | 45 | 011:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21072800009 | New_Event | Bad Weather | Include | Include | Weather | 663 | 2021-07-28 | 29835 | keep | 0 | Jul | 2021 | 0.02032 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
ARECIBO | 2021-07-28 07:17 | 2021-07-28 09:20 | 30 | 002:03 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO CRUZADO | A21072800006 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 123 | 2021-07-28 | 3690 | keep | 0 | Jul | 2021 | 0.0025132 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-07-28 07:23 | 2021-07-29 11:35 | 10 | 028:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA EN TRANSFORMADOR | A21072800007 | New_Event | Cutout Failure | Include | Include | Equipment | 1692 | 2021-07-28 | 16920 | keep | 0 | Jul | 2021 | 0.011524 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-07-28 07:31 | 2021-07-28 10:17 | 50 | 002:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21072800011 | New_Event | Bad Weather | Include | Include | Weather | 166 | 2021-07-28 | 8300 | keep | 0 | Jul | 2021 | 0.0056531 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-28 07:55 | 2021-07-28 11:41 | 1 | 003:46 | P | SECUNDARIA/DESGANCHE | ABRIO TRANSFORMADOR PARA DESGANCHAR SECUNDARIA Y BAJO TAP 5 AL 3 QUEDO 124/248V | C21072500022 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 226 | 2021-07-28 | 226 | keep | 0 | Jul | 2021 | 0.00015393 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-07-28 08:04 | 2021-07-28 17:44 | 10 | 009:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE CERRO BAJANTE SECUNDARIO | S21072800012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 580 | 2021-07-28 | 5800 | keep | 0 | Jul | 2021 | 0.0039504 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-28 08:09 | 2021-07-28 14:19 | 40 | 006:10 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21072800024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 370 | 2021-07-28 | 14800 | keep | 0 | Jul | 2021 | 0.01008 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-28 08:10 | 2021-07-28 14:47 | 60 | 006:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | B21072800026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 397 | 2021-07-28 | 23820 | keep | 0 | Jul | 2021 | 0.016224 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-07-28 08:11 | 2021-07-28 11:08 | 20 | 002:57 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21072800027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2021-07-28 | 3540 | keep | 0 | Jul | 2021 | 0.0024111 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-07-28 08:14 | 2021-07-28 13:10 | 30 | 004:56 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | B21072800028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 296 | 2021-07-28 | 8880 | keep | 0 | Jul | 2021 | 0.0060481 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-07-28 08:15 | 2021-07-28 08:16 | 67 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | A21072800000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-28 | 67 | keep | 0 | Jul | 2021 | 4.5633e-05 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
MAYAGÃœEZ | 2021-07-28 08:16 | 2021-07-28 13:53 | 50 | 005:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LONEA PRIMARIA PARTIDA | M21072280000 | New_Event | Wire Down | Include | Include | Equipment | 337 | 2021-07-28 | 16850 | keep | 0 | Jul | 2021 | 0.011476 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-07-28 08:16 | 2021-07-28 13:17 | 67 | 005:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA | A21072800052 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 301 | 2021-07-28 | 20167 | keep | 0 | Jul | 2021 | 0.013736 | 4.5633e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 67
MAYAGÃœEZ | 2021-07-28 08:18 | 2021-07-28 13:53 | 65 | 005:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO NEUTRAL PARTIDO | M21072280000 | New_Event | Wire Down | Include | Include | Equipment | 335 | 2021-07-28 | 21775 | keep | 0 | Jul | 2021 | 0.014831 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2021-07-28 08:30 | 2021-07-28 08:33 | 5620 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO 1620-04 LLEVANDO 1620-01, 85% DEL 1336-10 Y 90% DEL 1336-07 | S21072800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-07-28 | 16860 | keep | 0 | Jul | 2021 | 0.011483 | 0.0038278 | Momentary | FALSE | FALSE | Not_TMED_Event | 5620
SAN JUAN | 2021-07-28 08:30 | 2021-07-28 08:33 | 340 | 000:03 | P | NO SE REPORTO CAUSA | DISPARO 1620-04 LLEVANDO 1620-01, 85% DEL 1336-10 Y 90% DEL 1336-07 | S21072800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-07-28 | 1020 | keep | 0 | Jul | 2021 | 0.00069472 | 0.00023157 | Momentary | FALSE | FALSE | Not_TMED_Event | 340
SAN JUAN | 2021-07-28 08:30 | 2021-07-28 08:33 | 36 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO 1620-04 LLEVANDO 1620-01, 85% DEL 1336-10 Y 90% DEL 1336-07 | S21072800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-07-28 | 108 | keep | 0 | Jul | 2021 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-07-28 08:30 | 2021-07-28 08:33 | 172 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO 1620-04 LLEVANDO 1620-01, 85% DEL 1336-10 Y 90% DEL 1336-07 | S21072800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-07-28 | 516 | keep | 0 | Jul | 2021 | 0.00035145 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
AGUADILLA | 2021-07-28 08:30 | 2021-07-28 17:30 | 150 | 009:00 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE MASIVO | M21072800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 540 | 2021-07-28 | 81000 | keep | 0 | Jul | 2021 | 0.055169 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-07-28 08:34 | 2021-07-28 11:00 | 40 | 002:26 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | A21072800015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2021-07-28 | 5840 | keep | 0 | Jul | 2021 | 0.0039776 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-07-28 08:51 | 2021-07-28 12:00 | 100 | 003:09 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLACION PARTIDA | A21072800016 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 189 | 2021-07-28 | 18900 | keep | 0 | Jul | 2021 | 0.012873 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-07-28 08:57 | 2021-07-28 17:10 | 33 | 008:13 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21072800017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 493 | 2021-07-28 | 16269 | keep | 0 | Jul | 2021 | 0.011081 | 2.2476e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 33
SAN JUAN | 2021-07-28 09:05 | 2021-07-28 12:45 | 1 | 003:40 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR ENREDADERA | R21072800010 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 220 | 2021-07-28 | 220 | keep | 0 | Jul | 2021 | 0.00014984 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-07-28 09:05 | 2021-07-28 17:02 | 60 | 007:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARARON PUENTES CON CONECTORES SULFATADOS EN LINEA PRIMARIA Y SE REEMPLAZARON AISLADORES | C21072800019 | New_Event | Wire Down | Include | Include | Equipment | 477 | 2021-07-28 | 28620 | keep | 0 | Jul | 2021 | 0.019493 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
YAUCO | 2021-07-28 09:11 | 2021-07-28 09:14 | 591 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072800035 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-28 | 1773 | keep | 0 | Jul | 2021 | 0.0012076 | 0.00040253 | Momentary | FALSE | TRUE | Not_TMED_Event | 591
YAUCO | 2021-07-28 09:11 | 2021-07-28 09:14 | 1924 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072800032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-28 | 5772 | keep | 0 | Jul | 2021 | 0.0039313 | 0.0013104 | Momentary | FALSE | TRUE | Not_TMED_Event | 1924
YAUCO | 2021-07-28 09:11 | 2021-07-28 09:14 | 968 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072800032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-28 | 2904 | keep | 0 | Jul | 2021 | 0.0019779 | 0.0006593 | Momentary | FALSE | TRUE | Not_TMED_Event | 968
YAUCO | 2021-07-28 09:11 | 2021-07-28 09:14 | 680 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072800032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-28 | 2040 | keep | 0 | Jul | 2021 | 0.0013894 | 0.00046314 | Momentary | FALSE | TRUE | Not_TMED_Event | 680
YAUCO | 2021-07-28 09:11 | 2021-07-28 09:14 | 2246 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072800032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-28 | 6738 | keep | 0 | Jul | 2021 | 0.0045892 | 0.0015297 | Momentary | FALSE | TRUE | Not_TMED_Event | 2246
YAUCO | 2021-07-28 09:11 | 2021-07-28 09:14 | 2470 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072800037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-28 | 7410 | keep | 0 | Jul | 2021 | 0.0050469 | 0.0016823 | Momentary | FALSE | TRUE | Not_TMED_Event | 2470
YAUCO | 2021-07-28 09:11 | 2021-07-28 09:14 | 1182 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072800037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-28 | 3546 | keep | 0 | Jul | 2021 | 0.0024152 | 0.00080505 | Momentary | FALSE | TRUE | Not_TMED_Event | 1182
YAUCO | 2021-07-28 09:11 | 2021-07-28 09:14 | 2340 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072800037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-28 | 7020 | keep | 0 | Jul | 2021 | 0.0047813 | 0.0015938 | Momentary | FALSE | TRUE | Not_TMED_Event | 2340
YAUCO | 2021-07-28 09:11 | 2021-07-28 09:14 | 1637 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072800037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-28 | 4911 | keep | 0 | Jul | 2021 | 0.0033449 | 0.001115 | Momentary | FALSE | TRUE | Not_TMED_Event | 1637
YAUCO | 2021-07-28 09:11 | 2021-07-28 09:14 | 1569 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072800028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-28 | 4707 | keep | 0 | Jul | 2021 | 0.0032059 | 0.0010686 | Momentary | FALSE | TRUE | Not_TMED_Event | 1569
YAUCO | 2021-07-28 09:11 | 2021-07-28 09:14 | 2309 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072800028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-28 | 6927 | keep | 0 | Jul | 2021 | 0.0047179 | 0.0015726 | Momentary | FALSE | TRUE | Not_TMED_Event | 2309
YAUCO | 2021-07-28 09:11 | 2021-07-28 09:14 | 2179 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072800028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-28 | 6537 | keep | 0 | Jul | 2021 | 0.0044523 | 0.0014841 | Momentary | FALSE | TRUE | Not_TMED_Event | 2179
YAUCO | 2021-07-28 09:11 | 2021-07-28 09:14 | 2440 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072800028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-07-28 | 7320 | keep | 0 | Jul | 2021 | 0.0049856 | 0.0016619 | Momentary | FALSE | TRUE | Not_TMED_Event | 2440
YAUCO | 2021-07-28 09:11 | 2021-07-28 09:36 | 1352 | 000:25 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072800033 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 25 | 2021-07-28 | 33800 | keep | 0 | Jul | 2021 | 0.023021 | 0.00092084 | Sustained | FALSE | TRUE | Not_TMED_Event | 1352
YAUCO | 2021-07-28 09:11 | 2021-07-28 09:36 | 3973 | 000:25 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072800033 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 25 | 2021-07-28 | 99325 | keep | 0 | Jul | 2021 | 0.06765 | 0.002706 | Sustained | FALSE | TRUE | Not_TMED_Event | 3973
YAUCO | 2021-07-28 09:11 | 2021-07-28 09:36 | 2484 | 000:25 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21072800033 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 25 | 2021-07-28 | 62100 | keep | 0 | Jul | 2021 | 0.042296 | 0.0016918 | Sustained | FALSE | TRUE | Not_TMED_Event | 2484
YAUCO | 2021-07-28 09:11 | 2021-07-28 09:12 | 2484 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21072800027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-28 | 2484 | keep | 0 | Jul | 2021 | 0.0016918 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
PONCE | 2021-07-28 09:12 | 2021-07-28 13:16 | 1 | 004:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 65 EN RISER Y SE CAMBIARON LAS 3 CAJAS PRIMARAS | P21072800024 | New_Event | Cutout Failure | Include | Include | Equipment | 244 | 2021-07-28 | 244 | keep | 0 | Jul | 2021 | 0.00016619 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-07-28 09:13 | 2021-07-28 11:48 | 40 | 002:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | R21072800013 | New_Event | Bad Weather | Include | Include | Weather | 155 | 2021-07-28 | 6200 | keep | 0 | Jul | 2021 | 0.0042228 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-07-28 09:22 | 2021-07-29 14:35 | 10 | 029:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | A21072800019 | New_Event | Cutout Failure | Include | Include | Equipment | 1753 | 2021-07-28 | 17530 | keep | 0 | Jul | 2021 | 0.01194 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-07-28 09:32 | 2021-07-28 12:39 | 20 | 003:07 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21072800043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2021-07-28 | 3740 | keep | 0 | Jul | 2021 | 0.0025473 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
FAJARDO | 2021-07-28 09:33 | 2021-07-28 13:42 | 40 | 004:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN CORTE DE LINEA CRUCE POR AVE | R21072800015 | New_Event |  |  | Include | Wildlife | 249 | 2021-07-28 | 9960 | keep | 0 | Jul | 2021 | 0.0067837 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-07-28 09:48 | 2021-07-28 11:51 | 6 | 002:03 | P | SECUNDARIA/DESGANCHE | ABRIO TRANSFORMADOR PARA DESGANCHAR Y REPARAR SECUNDARIA | R21072800017 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 123 | 2021-07-28 | 738 | keep | 0 | Jul | 2021 | 0.00050265 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-07-28 09:49 | 2021-07-28 14:43 | 10 | 004:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIAS | A21072800023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 294 | 2021-07-28 | 2940 | keep | 0 | Jul | 2021 | 0.0020024 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-07-28 09:54 | 2021-07-28 09:55 | 2782 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | S21072800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-28 | 2782 | keep | 0 | Jul | 2021 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
ARECIBO | 2021-07-28 10:07 | 2021-07-28 11:52 | 1105 | 001:45 | T | ANIMAL U OBJETO EXTRAÃ‘O | LINEAS CRUZADAS POR CAMION | A21072800029 | New_Event |  |  | Include | Wildlife | 105 | 2021-07-28 | 116025 | keep | 0 | Jul | 2021 | 0.079024 | 0.00075261 | Sustained | FALSE | TRUE | Not_TMED_Event | 1105
YAUCO | 2021-07-28 10:13 | 2021-07-28 16:30 | 480 | 006:17 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | P21072800066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 377 | 2021-07-28 | 180960 | keep | 0 | Jul | 2021 | 0.12325 | 0.00032693 | Sustained | FALSE | TRUE | Not_TMED_Event | 480
HUMACAO | 2021-07-28 10:20 | 2021-07-28 18:00 | 39 | 007:40 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21072800033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 460 | 2021-07-28 | 17940 | keep | 0 | Jul | 2021 | 0.012219 | 2.6563e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 39
CAGUAS | 2021-07-28 10:30 | 2021-08-01 11:40 | 6 | 097:10 | P | SECUNDARIA/DESGANCHE | ABRIO TRANSFORMADOR PARA DESGANCHAR Y REPARAR SECUNDARIA | C21072800035 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 5830 | 2021-07-28 | 34980 | keep | 0 | Jul | 2021 | 0.023825 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-07-28 10:44 | 2021-07-30 09:27 | 20 | 046:43 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA Y 1 X 80 EN SU 11 | S21072800029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2803 | 2021-07-28 | 56060 | keep | 0 | Jul | 2021 | 0.038182 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-07-28 11:14 | 2021-07-28 11:15 | 5062 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21072800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-28 | 5062 | keep | 0 | Jul | 2021 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
UTUADO | 2021-07-28 11:17 | 2021-07-28 17:00 | 25 | 005:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | A21072800045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 343 | 2021-07-28 | 8575 | keep | 0 | Jul | 2021 | 0.0058404 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-07-28 11:20 | 2021-07-28 17:41 | 50 | 006:21 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | A21072800048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 381 | 2021-07-28 | 19050 | keep | 0 | Jul | 2021 | 0.012975 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-07-28 11:21 | 2021-07-28 14:28 | 10 | 003:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | R21072800021 | New_Event |  |  | Include | Wildlife | 187 | 2021-07-28 | 1870 | keep | 0 | Jul | 2021 | 0.0012736 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-07-28 11:22 | 2021-07-29 09:29 | 1 | 022:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN CORTE DE LINEA CRUCE POR AVE | C21072800043 | New_Event |  |  | Include | Wildlife | 1327 | 2021-07-28 | 1327 | keep | 0 | Jul | 2021 | 0.00090381 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-07-28 11:34 | 2021-07-28 16:44 | 4 | 005:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIAS | A21072800054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 310 | 2021-07-28 | 1240 | keep | 0 | Jul | 2021 | 0.00084456 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-07-28 11:35 | 2021-07-28 15:23 | 1 | 003:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | M21072800024 | New_Event | Wire Down | Include | Include | Equipment | 228 | 2021-07-28 | 228 | keep | 0 | Jul | 2021 | 0.00015529 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-07-28 11:40 | 2021-07-28 11:41 | 112 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21072800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-28 | 112 | keep | 0 | Jul | 2021 | 7.6283e-05 | 7.6283e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 112
CAGUAS | 2021-07-28 11:54 | 2021-07-29 15:47 | 50 | 027:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21072800031 | New_Event | Bad Weather | Include | Include | Weather | 1673 | 2021-07-28 | 83650 | keep | 0 | Jul | 2021 | 0.056974 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-28 11:56 | 2021-07-28 18:43 | 43 | 006:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE CON AVE | C21072800046 | New_Event |  |  | Include | Wildlife | 407 | 2021-07-28 | 17501 | keep | 0 | Jul | 2021 | 0.01192 | 2.9287e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 43
CANOVANAS | 2021-07-28 11:58 | 2021-07-28 14:41 | 171 | 002:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN SU-4 Y 1 X 30 EN AEREO PROVISIONAL SE DESPEGO PUENTE DE CRUCETA | R21072800027 | New_Event | Wire Down | Include | Include | Equipment | 163 | 2021-07-28 | 27873 | keep | 0 | Jul | 2021 | 0.018984 | 0.00011647 | Sustained | FALSE | FALSE | Not_TMED_Event | 171
HUMACAO | 2021-07-28 12:07 | 2021-07-28 17:51 | 8 | 005:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21072800047 | New_Event | Bad Weather | Include | Include | Weather | 344 | 2021-07-28 | 2752 | keep | 0 | Jul | 2021 | 0.0018744 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2021-07-28 12:17 | 2021-07-28 17:47 | 140 | 005:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SMU-20 80 EN SU-3 PUENTE PRIMARIO SOBRE CRUCETA | P21072800074 | New_Event | Wire Down | Include | Include | Equipment | 330 | 2021-07-28 | 46200 | keep | 0 | Jul | 2021 | 0.031467 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
ARECIBO | 2021-07-28 12:17 | 2021-07-28 15:07 | 20 | 002:50 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR Y SE CERRO CORTE DE LINEA | A21072800060 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 170 | 2021-07-28 | 3400 | keep | 0 | Jul | 2021 | 0.0023157 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-07-28 12:17 | 2021-07-28 13:32 | 15 | 001:15 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR | A21072800060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2021-07-28 | 1125 | keep | 0 | Jul | 2021 | 0.00076623 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-07-28 12:30 | 2021-07-28 14:14 | 1026 | 001:44 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR LLEVANDO LA CARGA DEL 1647-10 AVERIA EN MH-B AL MH-C CERRADO POR CONTROL | R21072800037 | New_Event | Switch Failure | Include | Include | Equipment | 104 | 2021-07-28 | 106704 | keep | 0 | Jul | 2021 | 0.072676 | 0.0006988 | Sustained | FALSE | FALSE | Not_TMED_Event | 1026
SAN JUAN | 2021-07-28 12:30 | 2021-07-28 14:14 | 61 | 001:44 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR CARGA POR EL 1646-02 AVERIA EN MH-B AL MH-C CERRADO POR CONTROL | R21072800037 | New_Event | Switch Failure | Include | Include | Equipment | 104 | 2021-07-28 | 6344 | keep | 0 | Jul | 2021 | 0.0043209 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
AGUADILLA | 2021-07-28 12:33 | 2021-07-28 12:36 | 1192 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR | M21072800032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-07-28 | 3576 | keep | 0 | Jul | 2021 | 0.0024356 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
CANOVANAS | 2021-07-28 12:36 | 2021-07-28 16:17 | 33 | 003:41 | P | SECUNDARIA/DESGANCHE | 1 X 30 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR ENREDADERA | R21072800030 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 221 | 2021-07-28 | 7293 | keep | 0 | Jul | 2021 | 0.0049672 | 2.2476e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 33
BAYAMON | 2021-07-28 12:50 | 2021-07-28 14:18 | 30 | 001:28 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | B21072800076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 88 | 2021-07-28 | 2640 | keep | 0 | Jul | 2021 | 0.0017981 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2021-07-28 12:53 | 2021-07-28 17:15 | 12 | 004:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR CULEBRA | R21072800035 | New_Event |  |  | Include | Wildlife | 262 | 2021-07-28 | 3144 | keep | 0 | Jul | 2021 | 0.0021414 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-07-28 13:13 | 2021-07-28 13:14 | 732 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P21072800071 | New_Event |  |  | Include | Wildlife | 1 | 2021-07-28 | 732 | keep | 0 | Jul | 2021 | 0.00049856 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
PONCE | 2021-07-28 13:14 | 2021-07-28 19:52 | 100 | 006:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZA FASE | P21072800076 | 1st_after_momentary |  |  | Include | Wildlife | 398 | 2021-07-28 | 39800 | keep | 0 | Jul | 2021 | 0.027108 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-07-28 13:19 | 2021-07-28 15:59 | 60 | 002:40 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO | A21072800070 | New_Event | Bad Weather | Include | Include | Weather | 160 | 2021-07-28 | 9600 | keep | 0 | Jul | 2021 | 0.0065385 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
AGUADILLA | 2021-07-28 13:55 | 2021-07-28 17:53 | 80 | 003:58 | P | DESGANCHE | 1 X 15 Y 1 X 40 EN CORTES DE LINEA SE REQUIERE DESGANCHE | M21072800034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2021-07-28 | 19040 | keep | 0 | Jul | 2021 | 0.012968 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CANOVANAS | 2021-07-28 14:02 | 2021-07-28 18:52 | 70 | 004:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA Y PIN POLE TOP | R21072800049 | New_Event | Cutout Failure | Include | Include | Equipment | 290 | 2021-07-28 | 20300 | keep | 0 | Jul | 2021 | 0.013826 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-07-28 14:06 | 2021-07-28 15:48 | 1142 | 001:42 | T | DESGANCHE | SE RETIRO ARBOL PEGANDO CON LAS LINEAS Y SE CERRO EL INTERRUPTOR | M21072800036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2021-07-28 | 116484 | keep | 0 | Jul | 2021 | 0.079337 | 0.00077781 | Sustained | FALSE | TRUE | Not_TMED_Event | 1142
UTUADO | 2021-07-28 14:13 | 2021-07-28 19:30 | 20 | 005:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | A21072800085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 317 | 2021-07-28 | 6340 | keep | 0 | Jul | 2021 | 0.0043181 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-07-28 14:14 | 2021-07-28 14:38 | 7 | 000:24 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO VACUUM DEL MHE QUEMADO | R21072800090 | Partial_restoration | Switch Failure | Include | Include | Equipment | 24 | 2021-07-28 | 168 | keep | 0 | Jul | 2021 | 0.00011442 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-28 14:17 | 2021-07-28 16:53 | 150 | 002:36 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 80 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21072800039 | New_Event | Bad Weather | Include | Include | Weather | 156 | 2021-07-28 | 23400 | keep | 0 | Jul | 2021 | 0.015938 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
FAJARDO | 2021-07-28 14:18 | 2021-07-28 15:09 | 12 | 000:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN CORTE DE LINEA PORTAFUSIBLE | R21072800050 | New_Event | Cutout Failure | Include | Include | Equipment | 51 | 2021-07-28 | 612 | keep | 0 | Jul | 2021 | 0.00041683 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
CANOVANAS | 2021-07-28 14:32 | 2021-07-29 11:48 | 10 | 021:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | R21072800053 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1276 | 2021-07-28 | 12760 | keep | 0 | Jul | 2021 | 0.0086908 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-07-28 14:36 | 2021-07-28 17:25 | 50 | 002:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR Y 1 X 30 EN CORTE DE LINEA POR AVE | A21072800094 | New_Event |  |  | Include | Wildlife | 169 | 2021-07-28 | 8450 | keep | 0 | Jul | 2021 | 0.0057553 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-28 14:38 | 2021-07-28 15:19 | 1026 | 000:41 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR LLEVANDO LA CARGA DEL 1647-10 AVERIA EN MH-B AL MH-C CERRADO POR CONTROL | R21072800037 | Additional_clients | Switch Failure | Include | Include | Equipment | 41 | 2021-07-28 | 42066 | keep | 0 | Jul | 2021 | 0.028651 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-28 14:38 | 2021-07-28 15:19 | 61 | 000:41 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR CARGA POR EL 1646-02 AVERIA EN MH-B AL MH-C CERRADO POR CONTROL | R21072800037 | Partial_restoration | Switch Failure | Include | Include | Equipment | 41 | 2021-07-28 | 2501 | keep | 0 | Jul | 2021 | 0.0017034 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-07-28 14:41 | 2021-07-28 19:36 | 225 | 004:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | P21072800086 | New_Event | Wire Down | Include | Include | Equipment | 295 | 2021-07-28 | 66375 | keep | 0 | Jul | 2021 | 0.045208 | 0.00015325 | Sustained | FALSE | TRUE | Not_TMED_Event | 225
AGUADILLA | 2021-07-28 14:45 | 2021-07-29 14:00 | 100 | 023:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO ABIERTO | M21072800044 | New_Event | Wire Down | Include | Include | Equipment | 1395 | 2021-07-28 | 139500 | keep | 0 | Jul | 2021 | 0.095013 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-07-28 14:48 | 2021-07-29 13:14 | 35 | 022:26 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | R21072800051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1346 | 2021-07-28 | 47110 | keep | 0 | Jul | 2021 | 0.032086 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
VEGA BAJA | 2021-07-28 14:48 | 2021-07-28 17:21 | 10 | 002:33 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21072800086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 153 | 2021-07-28 | 1530 | keep | 0 | Jul | 2021 | 0.0010421 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-07-28 14:52 | 2021-07-28 16:13 | 40 | 001:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA NIDO DE PAJARO | R21072800058 | New_Event |  |  | Include | Wildlife | 81 | 2021-07-28 | 3240 | keep | 0 | Jul | 2021 | 0.0022067 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-07-28 14:53 | 2021-07-28 19:40 | 100 | 004:47 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | A21072800097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 287 | 2021-07-28 | 28700 | keep | 0 | Jul | 2021 | 0.019547 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-28 14:56 | 2021-07-28 14:58 | 450 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR Y SE CERRO POR CONTROL | B21072800000 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2021-07-28 | 900 | keep | 0 | Jul | 2021 | 0.00061299 | 0.00030649 | Momentary | FALSE | FALSE | Not_TMED_Event | 450
BAYAMON | 2021-07-28 14:58 | 2021-07-28 18:00 | 150 | 003:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO | B21072800000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 182 | 2021-07-28 | 27300 | keep | 0 | Jul | 2021 | 0.018594 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2021-07-28 14:59 | 2021-07-28 17:45 | 200 | 002:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA FUERTES LLUVIAS | P21072800079 | New_Event | Bad Weather | Include | Include | Weather | 166 | 2021-07-28 | 33200 | keep | 0 | Jul | 2021 | 0.022612 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-07-28 15:19 | 2021-07-28 15:29 | 7 | 000:10 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO VACUUM DEL MHE QUEMADO | R21072800090 | Partial_restoration | Switch Failure | Include | Include | Equipment | 10 | 2021-07-28 | 70 | keep | 0 | Jul | 2021 | 4.7677e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-07-28 15:24 | 2021-07-28 16:56 | 40 | 001:32 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21072800094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 92 | 2021-07-28 | 3680 | keep | 0 | Jul | 2021 | 0.0025064 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-07-28 15:29 | 2021-07-28 15:30 | 1026 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR SE DEJO SECCIONALIZADO DEL MH-B AL MH-C CERRADO POR CONTROL | R21072800037 | Additional_clients | Switch Failure | Include | Include | Equipment | 1 | 2021-07-28 | 1026 | keep | 0 | Jul | 2021 | 0.0006988 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-28 15:29 | 2021-07-28 15:30 | 61 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR CARGA POR EL 1646-02 AVERIA EN MH-B AL MH-C CERRADO POR CONTROL | R21072800037 | Partial_restoration | Switch Failure | Include | Include | Equipment | 1 | 2021-07-28 | 61 | keep | 0 | Jul | 2021 | 4.1547e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-28 15:30 | 2021-07-28 15:32 | 7 | 000:02 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO VACUUM DEL MHE QUEMADO | R21072800090 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 2 | 2021-07-28 | 14 | keep | 0 | Jul | 2021 | 9.5353e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-07-28 15:32 | 2021-07-28 15:46 | 1026 | 000:14 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR AVERIA DEL MH-B AL MH-C CERRADO POR CONTROL | R21072800037 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 14 | 2021-07-28 | 14364 | keep | 0 | Jul | 2021 | 0.0097833 | 0.0006988 | Sustained | FALSE | FALSE | Not_TMED_Event | 1026
SAN JUAN | 2021-07-28 15:32 | 2021-07-28 15:46 | 61 | 000:14 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR CARGA POR EL 1646-02 AVERIA EN MH-B AL MH-C CERRADO POR CONTROL | R21072800037 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 14 | 2021-07-28 | 854 | keep | 0 | Jul | 2021 | 0.00058166 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2021-07-28 15:36 | 2021-07-28 15:48 | 1399 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21072800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-07-28 | 16788 | keep | 0 | Jul | 2021 | 0.011434 | 0.00095285 | Sustained | FALSE | TRUE | Not_TMED_Event | 1399
BAYAMON | 2021-07-28 15:36 | 2021-07-28 15:48 | 302 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21072800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-07-28 | 3624 | keep | 0 | Jul | 2021 | 0.0024683 | 0.00020569 | Sustained | FALSE | TRUE | Not_TMED_Event | 302
BAYAMON | 2021-07-28 15:36 | 2021-07-28 15:48 | 1048 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA | B21072800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-07-28 | 12576 | keep | 0 | Jul | 2021 | 0.0085655 | 0.00071379 | Sustained | FALSE | TRUE | Not_TMED_Event | 1048
BAYAMON | 2021-07-28 15:36 | 2021-07-28 15:48 | 573 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 LLEVA CARGA DEL 1704-05 | B21072800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-07-28 | 6876 | keep | 0 | Jul | 2021 | 0.0046832 | 0.00039027 | Sustained | FALSE | TRUE | Not_TMED_Event | 573
BAYAMON | 2021-07-28 15:36 | 2021-07-28 15:48 | 1313 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 CARGA POR 1704-04 | B21072800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-07-28 | 15756 | keep | 0 | Jul | 2021 | 0.010731 | 0.00089428 | Sustained | FALSE | TRUE | Not_TMED_Event | 1313
BAYAMON | 2021-07-28 15:36 | 2021-07-28 15:58 | 1715 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21072800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2021-07-28 | 37730 | keep | 0 | Jul | 2021 | 0.025698 | 0.0011681 | Sustained | FALSE | TRUE | Not_TMED_Event | 1715
BAYAMON | 2021-07-28 15:36 | 2021-07-28 15:58 | 1498 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 LLEVANDO LA CARGA DEL 1708-02 | B21072800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2021-07-28 | 32956 | keep | 0 | Jul | 2021 | 0.022446 | 0.0010203 | Sustained | FALSE | TRUE | Not_TMED_Event | 1498
BAYAMON | 2021-07-28 15:36 | 2021-07-28 15:58 | 1221 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21072800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2021-07-28 | 26862 | keep | 0 | Jul | 2021 | 0.018296 | 0.00083162 | Sustained | FALSE | TRUE | Not_TMED_Event | 1221
BAYAMON | 2021-07-28 15:36 | 2021-07-28 15:58 | 1100 | 000:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B21072800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 22 | 2021-07-28 | 24200 | keep | 0 | Jul | 2021 | 0.016483 | 0.0007492 | Sustained | FALSE | TRUE | Not_TMED_Event | 1100
MAYAGÃœEZ | 2021-07-28 15:40 | 2021-07-29 15:41 | 22 | 024:01 | P | DESGANCHE | 1 X 20 Y 1 X 30 EN TRANSFORMADOR | M21072800053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1441 | 2021-07-28 | 31702 | keep | 0 | Jul | 2021 | 0.021592 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
SAN JUAN | 2021-07-28 15:46 | 2021-07-28 16:08 | 7 | 000:22 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO VACUUM DEL MHE QUEMADO | R21072800090 | Partial_restoration | Switch Failure | Include | Include | Equipment | 22 | 2021-07-28 | 154 | keep | 0 | Jul | 2021 | 0.00010489 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-28 15:50 | 2021-07-29 15:17 | 8 | 023:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21072800107 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1407 | 2021-07-28 | 11256 | keep | 0 | Jul | 2021 | 0.0076664 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2021-07-28 15:51 | 2021-07-28 16:40 | 150 | 000:49 | P | DESGANCHE | 2 X 200 EN CORTE DE LINEA | A21072800104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 49 | 2021-07-28 | 7350 | keep | 0 | Jul | 2021 | 0.0050061 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
GUAYAMA | 2021-07-28 15:52 | 2021-07-28 18:20 | 10 | 002:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | P21072800087 | New_Event | Wire Down | Include | Include | Equipment | 148 | 2021-07-28 | 1480 | keep | 0 | Jul | 2021 | 0.001008 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-07-28 16:00 | 2021-07-28 20:13 | 60 | 004:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REEMPLAZO SU-6 IMPACTADO POR AUTO | S21072800000 | New_Event |  |  | Include | Wildlife | 253 | 2021-07-28 | 15180 | keep | 0 | Jul | 2021 | 0.010339 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-07-28 16:05 | 2021-07-28 16:20 | 8 | 000:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | M21072800000 | New_Event | Wire Down | Include | Include | Equipment | 15 | 2021-07-28 | 120 | keep | 0 | Jul | 2021 | 8.1731e-05 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-07-28 16:08 | 2021-07-28 16:14 | 1026 | 000:06 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR AVERIA EN MH-B AL MH-C CERRADO POR CONTROL | R21072800037 | Additional_clients | Switch Failure | Include | Include | Equipment | 6 | 2021-07-28 | 6156 | keep | 0 | Jul | 2021 | 0.0041928 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-28 16:08 | 2021-07-28 16:14 | 61 | 000:06 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR CARGA POR EL 1646-02 AVERIA EN MH-B AL MH-C CERRADO POR CONTROL | R21072800037 | Partial_restoration | Switch Failure | Include | Include | Equipment | 6 | 2021-07-28 | 366 | keep | 0 | Jul | 2021 | 0.00024928 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-07-28 16:09 | 2021-07-30 14:37 | 1 | 046:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 20 EN TRANSFORMADOR SE REEMPLAZARON | R21072800064 | New_Event | Cutout Failure | Include | Include | Equipment | 2788 | 2021-07-28 | 2788 | keep | 0 | Jul | 2021 | 0.0018989 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-07-28 16:09 | 2021-07-28 19:54 | 25 | 003:45 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | A21072800105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2021-07-28 | 5625 | keep | 0 | Jul | 2021 | 0.0038312 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-07-28 16:12 | 2021-07-29 14:54 | 1 | 022:42 | P | DESGANCHE | 2 X 15 EN TRANSFORMADOR | M21072800056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1362 | 2021-07-28 | 1362 | keep | 0 | Jul | 2021 | 0.00092765 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-07-28 16:14 | 2021-07-28 17:22 | 7 | 001:08 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO VACUUM DEL MHE QUEMADO | R21072800090 | Partial_restoration | Switch Failure | Include | Include | Equipment | 68 | 2021-07-28 | 476 | keep | 0 | Jul | 2021 | 0.0003242 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-28 16:20 | 2021-07-28 16:40 | 50 | 000:20 | P | OTRAS CAUSAS | SE ABRIO CORTE DE LINEA PARA REPARAR CONDICION DE TRANSFORMADOR ZAFADO Y COLGANDO DE UN SOLO TORNILLO | M21072800000 | New_Event | Other Causes | Include | Include | Other | 20 | 2021-07-28 | 1000 | keep | 0 | Jul | 2021 | 0.0006811 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-28 16:28 | 2021-07-28 18:49 | 80 | 002:21 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE SECCIONALIZO CONDUCTOR DEL SUELO PENDIENTE A LEVANTAR MAÃ‘ANA | C21072800067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2021-07-28 | 11280 | keep | 0 | Jul | 2021 | 0.0076828 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-07-28 16:41 | 2021-07-30 11:13 | 5 | 042:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 15 EN MONTURA DE TRANSFORMADOR Y 2 X 25 EN RISER SE RETIRO GLOBO METALICO | S21072800080 | New_Event |  |  | Include | Wildlife | 2552 | 2021-07-28 | 12760 | keep | 0 | Jul | 2021 | 0.0086908 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-07-28 16:51 | 2021-07-28 20:24 | 1 | 003:33 | P | PARARRAYOS DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PARARAYO | B21072800000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 213 | 2021-07-28 | 213 | keep | 0 | Jul | 2021 | 0.00014507 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-07-28 17:00 | 2021-07-28 18:00 | 20 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | M21072800000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2021-07-28 | 1200 | keep | 0 | Jul | 2021 | 0.00081731 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-07-28 17:04 | 2021-07-28 21:59 | 5 | 004:55 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | P21072800093 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 295 | 2021-07-28 | 1475 | keep | 0 | Jul | 2021 | 0.0010046 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2021-07-28 17:14 | 2021-07-28 17:15 | 4882 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M21072800066 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-28 | 4882 | keep | 0 | Jul | 2021 | 0.0033251 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
AGUADILLA | 2021-07-28 17:15 | 2021-07-28 20:44 | 100 | 003:29 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21072800069 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 209 | 2021-07-28 | 20900 | keep | 0 | Jul | 2021 | 0.014235 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-07-28 17:16 | 2021-07-29 11:38 | 6 | 018:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21072800070 | New_Event | Bad Weather | Include | Include | Weather | 1102 | 2021-07-28 | 6612 | keep | 0 | Jul | 2021 | 0.0045034 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-07-28 17:22 | 2021-07-28 17:23 | 1026 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR AVERIA DEL MH-B AL MH-C CERRADO POR CONTROL | R21072800037 | Additional_clients | Switch Failure | Include | Include | Equipment | 1 | 2021-07-28 | 1026 | keep | 0 | Jul | 2021 | 0.0006988 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-28 17:22 | 2021-07-28 17:23 | 61 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR CARGA POR EL 1646-02 AVERIA EN MH-B AL MH-C CERRADO POR CONTROL | R21072800037 | Partial_restoration | Switch Failure | Include | Include | Equipment | 1 | 2021-07-28 | 61 | keep | 0 | Jul | 2021 | 4.1547e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-28 17:23 | 2021-07-28 18:25 | 7 | 001:02 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO VACUUM DEL MHE QUEMADO | R21072800090 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 62 | 2021-07-28 | 434 | keep | 0 | Jul | 2021 | 0.0002956 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-07-28 17:27 | 2021-07-28 18:25 | 40 | 000:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA SE RETIRO GLOBO SOBRE LINEA | S21072800059 | New_Event |  |  | Include | Wildlife | 58 | 2021-07-28 | 2320 | keep | 0 | Jul | 2021 | 0.0015801 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-07-28 17:45 | 2021-07-28 19:41 | 150 | 001:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21072800071 | New_Event | Bad Weather | Include | Include | Weather | 116 | 2021-07-28 | 17400 | keep | 0 | Jul | 2021 | 0.011851 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-07-28 17:46 | 2021-07-28 18:19 | 70 | 000:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIAS | C21072800076 | New_Event | Bad Weather | Include | Include | Weather | 33 | 2021-07-28 | 2310 | keep | 0 | Jul | 2021 | 0.0015733 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
PONCE | 2021-07-28 17:48 | 2021-07-28 17:49 | 2446 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21072800102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-28 | 2446 | keep | 0 | Jul | 2021 | 0.001666 | 0.001666 | Momentary | FALSE | FALSE | Not_TMED_Event | 2446
PONCE | 2021-07-28 17:48 | 2021-07-28 22:46 | 100 | 004:58 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | P21072800095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 298 | 2021-07-28 | 29800 | keep | 0 | Jul | 2021 | 0.020297 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-07-28 17:48 | 2021-07-28 21:27 | 40 | 003:39 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | A21072800112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 219 | 2021-07-28 | 8760 | keep | 0 | Jul | 2021 | 0.0059664 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2021-07-28 17:53 | 2021-07-28 21:10 | 80 | 003:17 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21072800073 | New_Event | Bad Weather | Include | Include | Weather | 197 | 2021-07-28 | 15760 | keep | 0 | Jul | 2021 | 0.010734 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-07-28 17:53 | 2021-07-28 18:04 | 15 | 000:11 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR MAL TIEMPO | A21072800000 | New_Event | Bad Weather | Include | Include | Weather | 11 | 2021-07-28 | 165 | keep | 0 | Jul | 2021 | 0.00011238 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-07-28 17:53 | 2021-07-28 19:14 | 8 | 001:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | A21072800013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 81 | 2021-07-28 | 648 | keep | 0 | Jul | 2021 | 0.00044135 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-07-28 17:55 | 2021-07-28 18:56 | 3654 | 001:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | A21072800113 | New_Event | Cutout Failure | Include | Include | Equipment | 61 | 2021-07-28 | 222894 | keep | 0 | Jul | 2021 | 0.15181 | 0.0024887 | Sustained | FALSE | FALSE | Not_TMED_Event | 3654
BAYAMON | 2021-07-28 18:00 | 2021-07-28 18:57 | 450 | 000:57 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE ABIERTO | B21072800000 | Additional_clients | Wire Down | Include | Include | Equipment | 57 | 2021-07-28 | 25650 | keep | 0 | Jul | 2021 | 0.01747 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-07-28 18:02 | 2021-07-28 18:03 | 4381 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR CON EL RECIERRE EN OFF SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR | M21072800076 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-07-28 | 4381 | keep | 0 | Jul | 2021 | 0.0029839 | 0.0029839 | Momentary | FALSE | TRUE | Not_TMED_Event | 4381
MAYAGÃœEZ | 2021-07-28 18:03 | 2021-07-28 21:23 | 75 | 003:20 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M21072800083 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 200 | 2021-07-28 | 15000 | keep | 0 | Jul | 2021 | 0.010216 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
ARECIBO | 2021-07-28 18:03 | 2021-07-29 13:38 | 12 | 019:35 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | A21072800115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1175 | 2021-07-28 | 14100 | keep | 0 | Jul | 2021 | 0.0096034 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-07-28 18:17 | 2021-07-28 18:18 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S21072800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-28 | 3718 | keep | 0 | Jul | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
AGUADILLA | 2021-07-28 18:21 | 2021-07-29 11:45 | 3 | 017:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO PARTIDO Y SE REALIZO DESGANCHE | M21072800078 | New_Event | Wire Down | Include | Include | Equipment | 1044 | 2021-07-28 | 3132 | keep | 0 | Jul | 2021 | 0.0021332 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-07-28 18:25 | 2021-07-28 18:26 | 1026 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR SE DEJO SECCIONALIZADO DEL MH-B AL MH-C CERRADO POR CONTROL | R21072800037 | Additional_clients | Switch Failure | Include | Include | Equipment | 1 | 2021-07-28 | 1026 | keep | 0 | Jul | 2021 | 0.0006988 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-28 18:25 | 2021-07-28 18:26 | 61 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR CARGA POR EL 1646-02 AVERIA EN MH-B AL MH-C CERRADO POR CONTROL | R21072800037 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-07-28 | 61 | keep | 0 | Jul | 2021 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
SAN JUAN | 2021-07-28 18:26 | 2021-07-28 19:41 | 7 | 001:15 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO VACUUM DEL MHE QUEMADO | R21072800090 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 75 | 2021-07-28 | 525 | keep | 0 | Jul | 2021 | 0.00035758 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-07-28 18:30 | 2021-07-28 19:51 | 20 | 001:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21072700080 | New_Event | Secondary Wire Down | Include | Include | Equipment | 81 | 2021-07-28 | 1620 | keep | 0 | Jul | 2021 | 0.0011034 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-07-28 18:47 | 2021-07-28 18:48 | 2000 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR DEL 1619-02 LLEVANDO 2000 CLIENTES DEL 1336-06 | R21070800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-28 | 2000 | keep | 0 | Jul | 2021 | 0.0013622 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
CAGUAS | 2021-07-28 18:49 | 2021-07-29 18:05 | 40 | 023:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHO Y LEVANTO CONDUCTOR | C21072800064 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1396 | 2021-07-28 | 55840 | keep | 0 | Jul | 2021 | 0.038032 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-07-28 18:59 | 2021-07-29 11:46 | 40 | 016:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO CONDUCTOR Y DESGANCHE | B21072800134 | New_Event | Wire Down | Include | Include | Equipment | 1007 | 2021-07-28 | 40280 | keep | 0 | Jul | 2021 | 0.027435 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-07-28 19:15 | 2021-07-29 09:57 | 7 | 014:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO BAJANTE SECUNDARIO | R21072800075 | New_Event | Secondary Wire Down | Include | Include | Equipment | 882 | 2021-07-28 | 6174 | keep | 0 | Jul | 2021 | 0.0042051 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2021-07-28 19:17 | 2021-07-28 21:30 | 300 | 002:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA | B21072800139 | New_Event | Cutout Failure | Include | Include | Equipment | 133 | 2021-07-28 | 39900 | keep | 0 | Jul | 2021 | 0.027176 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2021-07-28 19:30 | 2021-07-29 18:11 | 115 | 022:41 | P | NO SE REPORTO CAUSA | 1 RBA DE 30 AMP EN EL SU - 3 NO CAUSA | C21072800078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1361 | 2021-07-28 | 156515 | keep | 0 | Jul | 2021 | 0.1066 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
SAN JUAN | 2021-07-28 19:41 | 2021-07-28 19:42 | 1026 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR SE DEJO SECCIONALIZADO DEL MH-B AL MH-C CERRADO POR CONTROL | R21072800037 | Additional_clients | Switch Failure | Include | Include | Equipment | 1 | 2021-07-28 | 1026 | keep | 0 | Jul | 2021 | 0.0006988 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-28 19:41 | 2021-07-28 19:42 | 61 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR CARGA POR EL 1646-02 AVERIA EN MH-B AL MH-C CERRADO POR CONTROL | R21072800037 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-07-28 | 61 | keep | 0 | Jul | 2021 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
SAN JUAN | 2021-07-28 19:42 | 2021-07-28 21:03 | 7 | 001:21 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO VACUUM DEL MHE QUEMADO | R21072800090 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 81 | 2021-07-28 | 567 | keep | 0 | Jul | 2021 | 0.00038618 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2021-07-28 19:50 | 2021-07-29 09:21 | 40 | 013:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C21072800081 | New_Event |  |  | Include | Wildlife | 811 | 2021-07-28 | 32440 | keep | 0 | Jul | 2021 | 0.022095 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-07-28 20:09 | 2021-07-28 21:20 | 3433 | 001:11 | P | PROTECCION DEFECTUOSA | SUBESTACION ACTIVO LOCK OUT ERRONEAMENTE CUANDO SE INSTALO PORTATIL #22 NO SE RETIRO PEINE DIFERENCIAL SE DESABILITO DIFERENCIAL DE BARRA Y SE CERRO INTERRUPTOR PORTATIL LLEVA 80% 1204-02 Y 40% DEL 1204-03 | S21072800000 | New_Event | Protection Miscoordination | Include | Include | Other | 71 | 2021-07-28 | 243743 | keep | 0 | Jul | 2021 | 0.16601 | 0.0023382 | Sustained | FALSE | FALSE | Not_TMED_Event | 3433
SAN JUAN | 2021-07-28 20:09 | 2021-07-28 21:20 | 600 | 001:11 | P | PROTECCION DEFECTUOSA | SUBESTACION ACTIVO LOCK OUT ERRONEAMENTE CUANDO SE INSTALO PORTATIL #22 NO SE RETIRO PEINE DIFERENCIAL SE DESABILITO DIFERENCIAL DE BARRA Y SE CERRO INTERRUPTOR PORTATIL LLEVA 80% 1204-02 Y 40% DEL 1204-03 | S21072800000 | New_Event | Protection Miscoordination | Include | Include | Other | 71 | 2021-07-28 | 42600 | keep | 0 | Jul | 2021 | 0.029015 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
FAJARDO | 2021-07-28 20:59 | 2021-07-29 09:22 | 20 | 012:23 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | R21072800085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 743 | 2021-07-28 | 14860 | keep | 0 | Jul | 2021 | 0.010121 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-07-28 21:03 | 2021-07-28 21:04 | 1026 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR SE DEJO SECCIONALIZADO DEL MH-B AL MH-C CERRADO POR CONTROL | R21072800037 | Additional_clients | Switch Failure | Include | Include | Equipment | 1 | 2021-07-28 | 1026 | keep | 0 | Jul | 2021 | 0.0006988 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-07-28 21:03 | 2021-07-28 21:04 | 61 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR CARGA POR EL 1646-02 AVERIA EN MH-B AL MH-C CERRADO POR CONTROL | R21072800037 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-07-28 | 61 | keep | 0 | Jul | 2021 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
SAN JUAN | 2021-07-28 21:04 | 2021-07-29 21:05 | 7 | 024:01 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO VACUUM DEL MHE QUEMADO | R21072800090 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1441 | 2021-07-28 | 10087 | keep | 0 | Jul | 2021 | 0.0068702 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2021-07-28 21:41 | 2021-07-28 21:53 | 693 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2800 | M21072800107 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-07-28 | 8316 | keep | 0 | Jul | 2021 | 0.005664 | 0.000472 | Sustained | FALSE | TRUE | Not_TMED_Event | 693
AGUADILLA | 2021-07-28 21:41 | 2021-07-28 21:53 | 47 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2800 | M21072800107 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-07-28 | 564 | keep | 0 | Jul | 2021 | 0.00038414 | 3.2011e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 47
AGUADILLA | 2021-07-28 21:41 | 2021-07-28 21:53 | 1256 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2800 | M21072800107 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-07-28 | 15072 | keep | 0 | Jul | 2021 | 0.010265 | 0.00085546 | Sustained | FALSE | TRUE | Not_TMED_Event | 1256
AGUADILLA | 2021-07-28 21:41 | 2021-07-28 21:53 | 558 | 000:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2800 | M21072800107 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2021-07-28 | 6696 | keep | 0 | Jul | 2021 | 0.0045606 | 0.00038005 | Sustained | FALSE | TRUE | Not_TMED_Event | 558
FAJARDO | 2021-07-28 21:43 | 2021-07-29 10:52 | 150 | 013:09 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 Y 1 X 80 EN CORTES DE LINEA REMPLAZO 6 DISCOS | R21072800089 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 789 | 2021-07-28 | 118350 | keep | 0 | Jul | 2021 | 0.080608 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CANOVANAS | 2021-07-28 22:21 | 2021-07-29 12:02 | 80 | 013:41 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTES DE LINEA DESGANCHO E INSTALO AISLADOR | R21072800092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 821 | 2021-07-28 | 65680 | keep | 0 | Jul | 2021 | 0.044734 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-07-28 22:22 | 2021-07-29 10:56 | 5 | 012:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO BAJANTE SECUNDARIO | C21072800090 | New_Event | Secondary Wire Down | Include | Include | Equipment | 754 | 2021-07-28 | 3770 | keep | 0 | Jul | 2021 | 0.0025677 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-07-28 22:45 | 2021-07-28 22:46 | 2486 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21072800091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-28 | 2486 | keep | 0 | Jul | 2021 | 0.0016932 | 0.0016932 | Momentary | FALSE | FALSE | Not_TMED_Event | 2486
PONCE | 2021-07-28 23:34 | 2021-07-28 23:35 | 752 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21072800106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-28 | 752 | keep | 0 | Jul | 2021 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
CAGUAS | 2021-07-28 23:56 | 2021-07-28 23:57 | 853 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRO CERRADO POR CONTROL | C21072800092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-28 | 853 | keep | 0 | Jul | 2021 | 0.00058097 | 0.00058097 | Momentary | FALSE | FALSE | Not_TMED_Event | 853
CAGUAS | 2021-07-29 01:13 | 2021-07-29 01:14 | 2417 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECERRO INTERRUPTOR | C21072900001 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-29 | 2417 | keep | 0 | Jul | 2021 | 0.0016462 | 0.0016462 | Momentary | FALSE | FALSE | Not_TMED_Event | 2417
CAGUAS | 2021-07-29 01:14 | 2021-07-29 10:00 | 250 | 008:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 Y 1 X 80 EN CORTES DE LINEA MAL TIEMPO | C21072900002 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 526 | 2021-07-29 | 131500 | keep | 0 | Jul | 2021 | 0.089564 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
MAYAGÃœEZ | 2021-07-29 01:56 | 2021-07-29 01:57 | 2073 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M21072900000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-29 | 2073 | keep | 0 | Jul | 2021 | 0.0014119 | 0.0014119 | Momentary | FALSE | FALSE | Not_TMED_Event | 2073
MAYAGÃœEZ | 2021-07-29 02:35 | 2021-07-29 11:27 | 100 | 008:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR FUERTES LLUVIAS | M21072900002 | New_Event | Bad Weather | Include | Include | Weather | 532 | 2021-07-29 | 53200 | keep | 0 | Jul | 2021 | 0.036234 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-07-29 03:42 | 2021-07-29 10:49 | 30 | 007:07 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21072900005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 427 | 2021-07-29 | 12810 | keep | 0 | Jul | 2021 | 0.0087248 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-07-29 04:02 | 2021-07-29 11:15 | 200 | 007:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA POR MAL TIEMPO | M21072900004 | New_Event | Bad Weather | Include | Include | Weather | 433 | 2021-07-29 | 86600 | keep | 0 | Jul | 2021 | 0.058983 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-07-29 04:07 | 2021-07-29 09:50 | 50 | 005:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21072900002 | New_Event | Bad Weather | Include | Include | Weather | 343 | 2021-07-29 | 17150 | keep | 0 | Jul | 2021 | 0.011681 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-29 04:34 | 2021-07-29 20:38 | 65 | 016:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE LINEA Y SE REEMPLAZO CAJA PRIMARIA | S21072900008 | New_Event | Cutout Failure | Include | Include | Equipment | 964 | 2021-07-29 | 62660 | keep | 0 | Jul | 2021 | 0.042677 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BAYAMON | 2021-07-29 05:25 | 2021-07-29 08:41 | 3597 | 003:16 | T | EQUIPO DE CONTROL DEFECTUOSO | SE TRANSFIRIO LA CARGA AL 1719-16 NO CERRO POR BOBINA DE CLOSE QUEMADA | B21072900003 | New_Event | Defective Control Device | Include | Include | Equipment | 196 | 2021-07-29 | 705012 | keep | 0 | Jul | 2021 | 0.48018 | 0.0024499 | Sustained | FALSE | FALSE | Not_TMED_Event | 3597
CAGUAS | 2021-07-29 06:00 | 2021-07-29 13:29 | 40 | 007:29 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21072900006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 449 | 2021-07-29 | 17960 | keep | 0 | Jul | 2021 | 0.012232 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-29 06:09 | 2021-07-29 06:11 | 320 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21072900025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-29 | 640 | keep | 0 | Jul | 2021 | 0.0004359 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
CAGUAS | 2021-07-29 06:13 | 2021-07-29 06:14 | 1702 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21072900008 | New_Event |  |  | Include | Wildlife | 1 | 2021-07-29 | 1702 | keep | 0 | Jul | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2021-07-29 06:14 | 2021-07-30 12:53 | 8 | 030:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | ABRIO TRANSFORMADOR PARA REMPLAZAR PEDESTAL Y BARRAS SECUNDARIAS PARTIDO POR CAMION | C21072900076 | 1st_after_momentary |  |  | Include | Wildlife | 1839 | 2021-07-29 | 14712 | keep | 0 | Jul | 2021 | 0.01002 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2021-07-29 06:34 | 2021-07-29 08:02 | 1841 | 001:28 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR SITUACION PELIGROSA LINEA PRIMARIA ROTA | A21072900003 | New_Event | Wire Down | Include | Include | Equipment | 88 | 2021-07-29 | 162008 | keep | 0 | Jul | 2021 | 0.11034 | 0.0012539 | Sustained | FALSE | TRUE | Not_TMED_Event | 1841
MAYAGÃœEZ | 2021-07-29 06:35 | 2021-07-30 12:00 | 9 | 029:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | M21072900104 | New_Event | Bad Weather | Include | Include | Weather | 1765 | 2021-07-29 | 15885 | keep | 0 | Jul | 2021 | 0.010819 | 6.1299e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 9
CANOVANAS | 2021-07-29 06:36 | 2021-07-29 12:05 | 40 | 005:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA AVERIADA NO FUNDIO | R21072900010 | New_Event | Cutout Failure | Include | Include | Equipment | 329 | 2021-07-29 | 13160 | keep | 0 | Jul | 2021 | 0.0089632 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-07-29 06:40 | 2021-07-29 13:33 | 15 | 006:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21072900053 | New_Event | Secondary Wire Down | Include | Include | Equipment | 413 | 2021-07-29 | 6195 | keep | 0 | Jul | 2021 | 0.0042194 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-07-29 07:01 | 2021-07-29 14:35 | 10 | 007:34 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21072900012 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 454 | 2021-07-29 | 4540 | keep | 0 | Jul | 2021 | 0.0030922 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-29 07:04 | 2021-07-29 07:05 | 3798 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21072900071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-29 | 3798 | keep | 0 | Jul | 2021 | 0.0025868 | 0.0025868 | Momentary | FALSE | FALSE | Not_TMED_Event | 3798
SAN JUAN | 2021-07-29 07:18 | 2021-07-29 07:19 | 3046 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21072900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-29 | 3046 | keep | 0 | Jul | 2021 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
MAYAGÃœEZ | 2021-07-29 07:23 | 2021-07-30 17:30 | 12 | 034:07 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR LA MISMA CAPACIDAD TRANSFORMADOR NUEVO HOWARD INDUSTRIES, SERIE # HI1628711018, 37.5KVA, 4.16KV / 120-240V | M21072900011 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2047 | 2021-07-29 | 24564 | keep | 0 | Jul | 2021 | 0.01673 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-07-29 07:46 | 2021-07-29 20:46 | 60 | 013:00 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN RISER 1 X 50 EN SU-5 SE REMPLAZO PARARAYO | B21072900093 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 780 | 2021-07-29 | 46800 | keep | 0 | Jul | 2021 | 0.031875 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-07-29 07:46 | 2021-07-29 07:47 | 4641 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | M21072900000 | New_Event |  |  | Include | Wildlife | 1 | 2021-07-29 | 4641 | keep | 0 | Jul | 2021 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2021-07-29 07:47 | 2021-07-29 14:15 | 70 | 006:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA POR AVE | M21072900014 | 1st_after_momentary |  |  | Include | Wildlife | 388 | 2021-07-29 | 27160 | keep | 0 | Jul | 2021 | 0.018499 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
VEGA BAJA | 2021-07-29 08:00 | 2021-07-30 09:37 | 1 | 025:37 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR 50 KVA X 50KVA | B21072900173 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1537 | 2021-07-29 | 1537 | keep | 0 | Jul | 2021 | 0.0010468 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-07-29 08:02 | 2021-07-29 11:47 | 25 | 003:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21072900011 | New_Event | Bad Weather | Include | Include | Weather | 225 | 2021-07-29 | 5625 | keep | 0 | Jul | 2021 | 0.0038312 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
UTUADO | 2021-07-29 08:02 | 2021-07-29 12:00 | 200 | 003:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | A21072900015 | Partial_restoration | Wire Down | Include | Include | Equipment | 238 | 2021-07-29 | 47600 | keep | 0 | Jul | 2021 | 0.03242 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
FAJARDO | 2021-07-29 08:07 | 2021-07-29 08:53 | 30 | 000:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | R21072900018 | New_Event | Bad Weather | Include | Include | Weather | 46 | 2021-07-29 | 1380 | keep | 0 | Jul | 2021 | 0.00093991 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-07-29 08:11 | 2021-07-29 19:36 | 80 | 011:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PARTIDA Y PUENTE ABIERTO | M21072900016 | New_Event | Wire Down | Include | Include | Equipment | 685 | 2021-07-29 | 54800 | keep | 0 | Jul | 2021 | 0.037324 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CANOVANAS | 2021-07-29 08:19 | 2021-07-29 12:52 | 30 | 004:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | R21072900020 | New_Event |  |  | Include | Wildlife | 273 | 2021-07-29 | 8190 | keep | 0 | Jul | 2021 | 0.0055782 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-07-29 08:30 | 2021-07-29 08:36 | 64 | 000:06 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA PODER ABRIR MACHETES SOLIDOS Y SECCIONALIZAR AVERIA | M21072900021 | New_Event | Wire Down | Include | Include | Equipment | 6 | 2021-07-29 | 384 | keep | 0 | Jul | 2021 | 0.00026154 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
CANOVANAS | 2021-07-29 08:31 | 2021-07-29 10:35 | 60 | 002:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | R21072900030 | New_Event |  |  | Include | Wildlife | 124 | 2021-07-29 | 7440 | keep | 0 | Jul | 2021 | 0.0050674 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-07-29 08:33 | 2021-07-29 10:35 | 5 | 002:02 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21072900132 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2021-07-29 | 610 | keep | 0 | Jul | 2021 | 0.00041547 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-07-29 08:38 | 2021-07-29 08:39 | 108 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M21072900000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-07-29 | 108 | keep | 0 | Jul | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
MAYAGÃœEZ | 2021-07-29 08:38 | 2021-07-29 08:39 | 2174 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 7802-3 EL CUAL ESTA LLEVANDO LA CARGA DEL 7802-01 PARA ABRIR MACHETES SOLIDOS Y SECCIONALIZAR AVERIA | M21072900021 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-29 | 2174 | keep | 0 | Jul | 2021 | 0.0014807 | 0.0014807 | Momentary | FALSE | FALSE | Not_TMED_Event | 2174
BAYAMON | 2021-07-29 08:39 | 2021-07-29 08:40 | 492 | 000:01 | T | EQUIPO DE CONTROL DEFECTUOSO | SE ABRIO INTERRUPTOR PARA HACER OPERACIONES EN EL SISTEMA Y TRANFERIRLE EL 1719-15 POR BOBINA DE CLOSE DEL 1719-15 QUEMADA | B21072900148 | New_Event | Defective Control Device | Include | Include | Equipment | 1 | 2021-07-29 | 492 | keep | 0 | Jul | 2021 | 0.0003351 | 0.0003351 | Momentary | FALSE | FALSE | Not_TMED_Event | 492
MAYAGÃœEZ | 2021-07-29 08:39 | 2021-07-29 16:43 | 100 | 008:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA | M21072900052 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 484 | 2021-07-29 | 48400 | keep | 0 | Jul | 2021 | 0.032965 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-07-29 08:39 | 2021-07-29 16:17 | 1320 | 007:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTES ABIERTOS | M21072900021 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 458 | 2021-07-29 | 604560 | keep | 0 | Jul | 2021 | 0.41176 | 0.00089905 | Sustained | FALSE | FALSE | Not_TMED_Event | 1320
BAYAMON | 2021-07-29 08:41 | 2021-07-29 12:42 | 1100 | 004:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO EN SALIDA DEL ALIMENTADOR | B21072900003 | New_Event | Wire Down | Include | Include | Equipment | 241 | 2021-07-29 | 265100 | keep | 0 | Jul | 2021 | 0.18056 | 0.0007492 | Sustained | FALSE | FALSE | Not_TMED_Event | 1100
BAYAMON | 2021-07-29 09:08 | 2021-07-29 11:01 | 20 | 001:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | S21072900021 | New_Event | Cutout Failure | Include | Include | Equipment | 113 | 2021-07-29 | 2260 | keep | 0 | Jul | 2021 | 0.0015393 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-07-29 09:13 | 2021-07-29 09:14 | 2617 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21072900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-29 | 2617 | keep | 0 | Jul | 2021 | 0.0017824 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
VEGA BAJA | 2021-07-29 09:32 | 2021-07-29 18:45 | 20 | 009:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE SECUNDARIA | B21072900158 | New_Event | Secondary Wire Down | Include | Include | Equipment | 553 | 2021-07-29 | 11060 | keep | 0 | Jul | 2021 | 0.0075329 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-07-29 09:33 | 2021-07-31 17:41 | 200 | 056:08 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL AEREO | P21072900043 | New_Event | UG Cable Fault | Include | Include | Equipment | 3368 | 2021-07-29 | 673600 | keep | 0 | Jul | 2021 | 0.45879 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-07-29 09:41 | 2021-07-31 17:25 | 10 | 055:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO TRANSFORMADOR Y SE CERRO BAJANTE DE LINEA A CAJA | S21072900025 | New_Event | Wire Down | Include | Include | Equipment | 3344 | 2021-07-29 | 33440 | keep | 0 | Jul | 2021 | 0.022776 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
FAJARDO | 2021-07-29 09:55 | 2021-07-29 09:56 | 1394 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21072900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-29 | 1394 | keep | 0 | Jul | 2021 | 0.00094945 | 0.00094945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1394
MAYAGÃœEZ | 2021-07-29 09:58 | 2021-07-29 14:52 | 30 | 004:54 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | M21072900037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 294 | 2021-07-29 | 8820 | keep | 0 | Jul | 2021 | 0.0060073 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-07-29 10:08 | 2021-07-29 13:53 | 1 | 003:45 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | A21072900032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2021-07-29 | 225 | keep | 0 | Jul | 2021 | 0.00015325 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-07-29 10:24 | 2021-07-29 13:00 | 50 | 002:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO NEUTRAL PRIMARIO PARTIDO | M21072900000 | New_Event | Wire Down | Include | Include | Equipment | 156 | 2021-07-29 | 7800 | keep | 0 | Jul | 2021 | 0.0053125 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-07-29 10:28 | 2021-07-29 14:30 | 10 | 004:02 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR Y SE REALIZO DESGANCHE SE REEMPLAZO 150' DE SECUNDARIA Y DOS TOMAS | A21072800048 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 242 | 2021-07-29 | 2420 | keep | 0 | Jul | 2021 | 0.0016483 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-07-29 10:54 | 2021-07-29 11:34 | 15 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21072900179 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2021-07-29 | 600 | keep | 0 | Jul | 2021 | 0.00040866 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-07-29 11:27 | 2021-07-30 12:57 | 10 | 025:30 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA X 37.5 KVA | C21072900036 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1530 | 2021-07-29 | 15300 | keep | 0 | Jul | 2021 | 0.010421 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-07-29 11:31 | 2021-07-29 13:46 | 50 | 002:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21072900060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2021-07-29 | 6750 | keep | 0 | Jul | 2021 | 0.0045974 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BARRANQUITAS | 2021-07-29 11:31 | 2021-07-29 13:21 | 40 | 001:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA PERSONAL CONTRATISTA DESGANCHANDO | C21072900037 | New_Event |  |  | Include | Wildlife | 110 | 2021-07-29 | 4400 | keep | 0 | Jul | 2021 | 0.0029968 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-07-29 11:40 | 2021-07-29 17:35 | 90 | 005:55 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | M21072900050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 355 | 2021-07-29 | 31950 | keep | 0 | Jul | 2021 | 0.021761 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
ARECIBO | 2021-07-29 11:40 | 2021-07-29 15:20 | 100 | 003:40 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21072900038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2021-07-29 | 22000 | keep | 0 | Jul | 2021 | 0.014984 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-29 11:56 | 2021-07-29 15:17 | 60 | 003:21 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S21072900038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 201 | 2021-07-29 | 12060 | keep | 0 | Jul | 2021 | 0.008214 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-07-29 12:14 | 2021-07-29 17:16 | 100 | 005:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE DE LINEA SE REMPLAZO 2 PORTAFISIBLES | A21072900041 | New_Event | Cutout Failure | Include | Include | Equipment | 302 | 2021-07-29 | 30200 | keep | 0 | Jul | 2021 | 0.020569 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-07-29 12:23 | 2021-07-29 17:05 | 7 | 004:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR TOMA CRUZADA | C21072900041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 282 | 2021-07-29 | 1974 | keep | 0 | Jul | 2021 | 0.0013445 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-07-29 12:31 | 2021-07-29 12:33 | 60 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR SCADA | S21072900041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-29 | 120 | keep | 0 | Jul | 2021 | 8.1731e-05 | 4.0866e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2021-07-29 12:38 | 2021-07-29 17:36 | 10 | 004:58 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21072900203 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 298 | 2021-07-29 | 2980 | keep | 0 | Jul | 2021 | 0.0020297 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-07-29 12:52 | 2021-07-29 21:00 | 20 | 008:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN CORTE DE LINEA SE REMPLAZO CAJA | P21072900020 | New_Event | Wire Down | Include | Include | Equipment | 488 | 2021-07-29 | 9760 | keep | 0 | Jul | 2021 | 0.0066475 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
UTUADO | 2021-07-29 12:56 | 2021-07-29 14:25 | 1 | 001:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR WR5903852 | A21072900000 | New_Event | Wire Down | Include | Include | Equipment | 89 | 2021-07-29 | 89 | keep | 0 | Jul | 2021 | 6.0617e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-07-29 13:09 | 2021-07-29 13:10 | 218 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR 1113-04 | S21072900050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-29 | 218 | keep | 0 | Jul | 2021 | 0.00014848 | 0.00014848 | Momentary | FALSE | FALSE | Not_TMED_Event | 218
SAN JUAN | 2021-07-29 13:09 | 2021-07-29 13:10 | 1526 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR 1113-04 | S21072900050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-29 | 1526 | keep | 0 | Jul | 2021 | 0.0010394 | 0.0010394 | Momentary | FALSE | FALSE | Not_TMED_Event | 1526
SAN JUAN | 2021-07-29 13:09 | 2021-07-29 13:10 | 553 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA CARGA 1110-01 Y 1110-03 | S21072900050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-29 | 553 | keep | 0 | Jul | 2021 | 0.00037665 | 0.00037665 | Momentary | FALSE | FALSE | Not_TMED_Event | 553
ARECIBO | 2021-07-29 13:15 | 2021-07-29 16:46 | 25 | 003:31 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR POSTE PRIMARIO AVERIADO POR UNO DE 40' DE METAL | A21072900047 | New_Event | Defective Pole | Include | Include | Equipment | 211 | 2021-07-29 | 5275 | keep | 0 | Jul | 2021 | 0.0035928 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
VEGA BAJA | 2021-07-29 13:15 | 2021-07-29 15:41 | 60 | 002:26 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21072900205 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2021-07-29 | 8760 | keep | 0 | Jul | 2021 | 0.0059664 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
YAUCO | 2021-07-29 13:23 | 2021-07-29 18:45 | 50 | 005:22 | P | DESGANCHE | 1 X DE 50 EN CORTE DE LINEA DESGANCHE | P21072900021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 322 | 2021-07-29 | 16100 | keep | 0 | Jul | 2021 | 0.010966 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-29 13:24 | 2021-07-29 19:32 | 70 | 006:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA REMPLAZO CAJA PRIMARIA | M21072900062 | New_Event | Cutout Failure | Include | Include | Equipment | 368 | 2021-07-29 | 25760 | keep | 0 | Jul | 2021 | 0.017545 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
AGUADILLA | 2021-07-29 13:24 | 2021-07-29 17:30 | 1 | 004:06 | P | NO SE REPORTO CAUSA | 1 X 40 EN RAISER | M21072900061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 246 | 2021-07-29 | 246 | keep | 0 | Jul | 2021 | 0.00016755 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-07-29 13:37 | 2021-07-29 14:58 | 1 | 001:21 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | B21072900207 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2021-07-29 | 81 | keep | 0 | Jul | 2021 | 5.5169e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-07-29 13:50 | 2021-07-29 17:54 | 75 | 004:04 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA DESGANCHE | P21072900002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 244 | 2021-07-29 | 18300 | keep | 0 | Jul | 2021 | 0.012464 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
MAYAGÃœEZ | 2021-07-29 13:55 | 2021-07-29 16:55 | 70 | 003:00 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | M21072900071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2021-07-29 | 12600 | keep | 0 | Jul | 2021 | 0.0085818 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
SAN JUAN | 2021-07-29 13:58 | 2021-07-29 16:39 | 10 | 002:41 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S21072900059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 161 | 2021-07-29 | 1610 | keep | 0 | Jul | 2021 | 0.0010966 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-29 14:00 | 2021-07-29 19:00 | 40 | 005:00 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA ES NECESARIO REALIZAR DESGANCHE DE ARBOL | S21072900060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 300 | 2021-07-29 | 12000 | keep | 0 | Jul | 2021 | 0.0081731 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-07-29 14:08 | 2021-07-29 16:30 | 150 | 002:22 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | P21072900023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2021-07-29 | 21300 | keep | 0 | Jul | 2021 | 0.014507 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-07-29 14:24 | 2021-07-29 22:03 | 45 | 007:39 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | S21072900066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 459 | 2021-07-29 | 20655 | keep | 0 | Jul | 2021 | 0.014068 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
UTUADO | 2021-07-29 14:57 | 2021-07-29 18:56 | 12 | 003:59 | P | DESGANCHE | 1 X 15 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21072900053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2021-07-29 | 2868 | keep | 0 | Jul | 2021 | 0.0019534 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
GUAYAMA | 2021-07-29 15:00 | 2021-07-29 17:20 | 50 | 002:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR | P21072900023 | New_Event | Wire Down | Include | Include | Equipment | 140 | 2021-07-29 | 7000 | keep | 0 | Jul | 2021 | 0.0047677 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-29 15:00 | 2021-07-29 20:13 | 200 | 005:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 100 EN CORTE DE LINEA REPARAR LINEA ROTA | M21072900083 | New_Event | Wire Down | Include | Include | Equipment | 313 | 2021-07-29 | 62600 | keep | 0 | Jul | 2021 | 0.042637 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-07-29 15:09 | 2021-07-29 17:56 | 25 | 002:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO DE LINEA A CAJA Y SE REALIZO DESGANCHE | S21072900068 | New_Event | Wire Down | Include | Include | Equipment | 167 | 2021-07-29 | 4175 | keep | 0 | Jul | 2021 | 0.0028436 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-07-29 15:11 | 2021-07-29 19:41 | 50 | 004:30 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21072900215 | New_Event | Vegetation Contact | Include | Include | Vegetation | 270 | 2021-07-29 | 13500 | keep | 0 | Jul | 2021 | 0.0091948 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-29 15:16 | 2021-07-29 17:01 | 100 | 001:45 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | M21072900084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2021-07-29 | 10500 | keep | 0 | Jul | 2021 | 0.0071515 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-07-29 15:20 | 2021-07-29 17:24 | 1340 | 002:04 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE REMOBIO GLOBO EN SOBRE LINEAS | P21072900039 | New_Event |  |  | Include | Wildlife | 124 | 2021-07-29 | 166160 | keep | 0 | Jul | 2021 | 0.11317 | 0.00091267 | Sustained | FALSE | TRUE | Not_TMED_Event | 1340
AGUADILLA | 2021-07-29 15:30 | 2021-07-29 23:35 | 50 | 008:05 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M21072900088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 485 | 2021-07-29 | 24250 | keep | 0 | Jul | 2021 | 0.016517 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-07-29 16:00 | 2021-07-30 12:15 | 12 | 020:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA PARTIDA | A21072900059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1215 | 2021-07-29 | 14580 | keep | 0 | Jul | 2021 | 0.0099304 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
HUMACAO | 2021-07-29 16:20 | 2021-07-29 18:35 | 6 | 002:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR REMPLAZO SECUNDARIA AVERIADA POR DIGGER | C21072900060 | New_Event |  |  | Include | Wildlife | 135 | 2021-07-29 | 810 | keep | 0 | Jul | 2021 | 0.00055169 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-07-29 16:22 | 2021-07-30 14:53 | 100 | 022:31 | P | DESGANCHE | 1 X 140 Y 1 X 100 EN CORTES DE LINEA SE REALIZO DESGANCHE | M21072900150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1351 | 2021-07-29 | 135100 | keep | 0 | Jul | 2021 | 0.092016 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-07-29 16:26 | 2021-07-29 19:33 | 10 | 003:07 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO ENCONTRARON CAUSA | A21072900061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 187 | 2021-07-29 | 1870 | keep | 0 | Jul | 2021 | 0.0012736 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-29 16:31 | 2021-07-29 17:09 | 12 | 000:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21072900224 | New_Event | Secondary Wire Down | Include | Include | Equipment | 38 | 2021-07-29 | 456 | keep | 0 | Jul | 2021 | 0.00031058 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-07-29 16:31 | 2021-07-31 16:15 | 15 | 047:44 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR 25KVA | B21072900224 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2864 | 2021-07-29 | 42960 | keep | 0 | Jul | 2021 | 0.02926 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-07-29 16:39 | 2021-07-29 19:30 | 200 | 002:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO | M21072900107 | New_Event | Wire Down | Include | Include | Equipment | 171 | 2021-07-29 | 34200 | keep | 0 | Jul | 2021 | 0.023293 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
UTUADO | 2021-07-29 16:45 | 2021-07-30 13:47 | 20 | 021:02 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | A21072900062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1262 | 2021-07-29 | 25240 | keep | 0 | Jul | 2021 | 0.017191 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-07-29 16:53 | 2021-07-29 18:03 | 115 | 001:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21072900063 | New_Event | Bad Weather | Include | Include | Weather | 70 | 2021-07-29 | 8050 | keep | 0 | Jul | 2021 | 0.0054828 | 7.8326e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 115
SAN JUAN | 2021-07-29 17:04 | 2021-07-29 17:43 | 10 | 000:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO T-36B PARA REEMPLAZAR BARRA EN PEDESTAL | S21072900074 | New_Event | Secondary Wire Down | Include | Include | Equipment | 39 | 2021-07-29 | 390 | keep | 0 | Jul | 2021 | 0.00026563 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-29 17:20 | 2021-07-29 20:44 | 75 | 003:24 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | B21072900232 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 204 | 2021-07-29 | 15300 | keep | 0 | Jul | 2021 | 0.010421 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
VEGA BAJA | 2021-07-29 17:20 | 2021-07-29 19:33 | 20 | 002:13 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50 X 50 CON PROBLEMAS DE VOLTAJE | B21072900234 | New_Event | Service Transformer Failure | Include | Include | Equipment | 133 | 2021-07-29 | 2660 | keep | 0 | Jul | 2021 | 0.0018117 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-07-29 17:39 | 2021-07-29 19:43 | 6 | 002:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIAS | R21072900090 | New_Event | Bad Weather | Include | Include | Weather | 124 | 2021-07-29 | 744 | keep | 0 | Jul | 2021 | 0.00050674 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2021-07-29 17:49 | 2021-07-30 14:31 | 50 | 020:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE | A21072900067 | New_Event | Wire Down | Include | Include | Equipment | 1242 | 2021-07-29 | 62100 | keep | 0 | Jul | 2021 | 0.042296 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-07-29 17:56 | 2021-07-29 20:16 | 100 | 002:20 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | M21072900122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2021-07-29 | 14000 | keep | 0 | Jul | 2021 | 0.0095353 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-29 18:04 | 2021-07-30 15:42 | 40 | 021:38 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21072900097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1298 | 2021-07-29 | 51920 | keep | 0 | Jul | 2021 | 0.035362 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
AGUADILLA | 2021-07-29 18:49 | 2021-07-30 16:20 | 15 | 021:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTES SECUNDARIOS EN TRANSFORMADOR | M21072900128 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1291 | 2021-07-29 | 19365 | keep | 0 | Jul | 2021 | 0.013189 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-07-29 19:16 | 2021-07-29 19:19 | 1715 | 000:03 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL CARGA POR EL 1708-03 | B21072900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-07-29 | 5145 | keep | 0 | Jul | 2021 | 0.0035042 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2021-07-29 19:16 | 2021-07-29 19:19 | 1498 | 000:03 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL LLEVA EL 1708-02 | B21072900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-07-29 | 4494 | keep | 0 | Jul | 2021 | 0.0030608 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2021-07-29 19:44 | 2021-07-29 19:45 | 1715 | 000:01 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL CARGA POR 1708-03 | B21072900000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-29 | 1715 | keep | 0 | Jul | 2021 | 0.0011681 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2021-07-29 19:44 | 2021-07-29 19:45 | 1498 | 000:01 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL LLEVA EL 1708-02 | B21072900000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-29 | 1498 | keep | 0 | Jul | 2021 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
ARECIBO | 2021-07-29 19:46 | 2021-07-29 21:17 | 300 | 001:31 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA NO ENCONTRARON CAUSA | A21072900080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 91 | 2021-07-29 | 27300 | keep | 0 | Jul | 2021 | 0.018594 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
ARECIBO | 2021-07-29 19:47 | 2021-07-29 23:30 | 300 | 003:43 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A21072900082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 223 | 2021-07-29 | 66900 | keep | 0 | Jul | 2021 | 0.045565 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-07-29 20:09 | 2021-07-29 20:59 | 80 | 000:50 | P | SOBRECARGA | 1 X 100 EN CORTE DE LINEA POR CARGA | M21072900136 | New_Event | Trip Due To Overload | Include | Include | Other | 50 | 2021-07-29 | 4000 | keep | 0 | Jul | 2021 | 0.0027244 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-07-29 20:25 | 2021-07-29 20:26 | 25 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN CORTE DE LINEA SE REMPLAZO CAJA | P21072900004 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-29 | 25 | keep | 0 | Jul | 2021 | 1.7027e-05 | 1.7027e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-07-29 20:31 | 2021-07-29 20:32 | 1715 | 000:01 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL CARGA POR LE 1708-03 | B21072900000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-29 | 1715 | keep | 0 | Jul | 2021 | 0.0011681 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2021-07-29 20:31 | 2021-07-29 20:32 | 1498 | 000:01 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL LLEVA EL 1708-02 | B21072900000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-29 | 1498 | keep | 0 | Jul | 2021 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2021-07-29 20:31 | 2021-07-30 18:53 | 25 | 022:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO EN LINEA MONOFASICA | B21072900250 | New_Event | Wire Down | Include | Include | Equipment | 1342 | 2021-07-29 | 33550 | keep | 0 | Jul | 2021 | 0.022851 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CANOVANAS | 2021-07-29 20:39 | 2021-07-30 08:44 | 40 | 012:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA NO FUNDIO | R21072900093 | New_Event | Wire Down | Include | Include | Equipment | 725 | 2021-07-29 | 29000 | keep | 0 | Jul | 2021 | 0.019752 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-29 21:23 | 2021-07-30 09:55 | 1 | 012:32 | P | DESGANCHE | 1 X 100 EN CONVERTIDOR Y DESGANCHE | S21072900116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 752 | 2021-07-29 | 752 | keep | 0 | Jul | 2021 | 0.00051218 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-07-29 21:31 | 2021-07-29 22:55 | 50 | 001:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 SE REEMPLAZO CAJA PRIMARIA | B21072900267 | New_Event | Cutout Failure | Include | Include | Equipment | 84 | 2021-07-29 | 4200 | keep | 0 | Jul | 2021 | 0.0028606 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-07-29 21:46 | 2021-07-30 07:01 | 300 | 009:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA FUERTES VIENTOS | P21073000004 | New_Event | Bad Weather | Include | Include | Weather | 555 | 2021-07-29 | 166500 | keep | 0 | Jul | 2021 | 0.1134 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
CAGUAS | 2021-07-29 21:54 | 2021-07-30 11:35 | 11 | 013:41 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO CAUSA | C21072900081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 821 | 2021-07-29 | 9031 | keep | 0 | Jul | 2021 | 0.006151 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2021-07-29 21:57 | 2021-07-30 15:45 | 8 | 017:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21072900143 | New_Event | Bad Weather | Include | Include | Weather | 1068 | 2021-07-29 | 8544 | keep | 0 | Jul | 2021 | 0.0058193 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-07-29 22:08 | 2021-07-29 22:15 | 1498 | 000:07 | T | DESGANCHE | SE SECCIONALIZO ALIMENTADOR Y SE CERRO INTERRUPTOR LUEGO SE CERRARON MACHETES DE AMARRE CONTRA EL BREAKER 1708-02 EN LA CALLE DAKAR DE LA URBANIZACION FOREST VIEW | B21072900000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 7 | 2021-07-29 | 10486 | keep | 0 | Jul | 2021 | 0.007142 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
AGUADILLA | 2021-07-29 22:21 | 2021-07-30 11:40 | 100 | 013:19 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | M21072900146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 799 | 2021-07-29 | 79900 | keep | 0 | Jul | 2021 | 0.05442 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-29 22:28 | 2021-07-30 11:50 | 40 | 013:22 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | S21007290012 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 802 | 2021-07-29 | 32080 | keep | 0 | Jul | 2021 | 0.02185 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-07-29 22:30 | 2021-07-30 11:27 | 35 | 012:57 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | B21072900301 | New_Event | Vegetation Contact | Include | Include | Vegetation | 777 | 2021-07-29 | 27195 | keep | 0 | Jul | 2021 | 0.018522 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-07-29 22:32 | 2021-07-30 10:21 | 45 | 011:49 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21072900302 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 709 | 2021-07-29 | 31905 | keep | 0 | Jul | 2021 | 0.02173 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BAYAMON | 2021-07-29 22:55 | 2021-07-29 22:56 | 5961 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | B21072900000 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2021-07-29 | 5961 | keep | 0 | Jul | 2021 | 0.00406 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-07-29 22:55 | 2021-07-30 11:28 | 70 | 012:33 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO AISLADOR PARTIDO | A21072900093 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 753 | 2021-07-29 | 52710 | keep | 0 | Jul | 2021 | 0.035901 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BAYAMON | 2021-07-29 22:56 | 2021-07-30 09:23 | 50 | 010:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 SE REEMPLAZO CAJA PRIMARIA | B21072900267 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 627 | 2021-07-29 | 31350 | keep | 0 | Jul | 2021 | 0.021352 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-07-29 22:58 | 2021-07-30 13:55 | 10 | 014:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTE Y TRAMO SECUNDARIO | C21072900082 | New_Event | Secondary Wire Down | Include | Include | Equipment | 897 | 2021-07-29 | 8970 | keep | 0 | Jul | 2021 | 0.0061094 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-07-29 23:02 | 2021-07-30 19:47 | 10 | 020:45 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA X 50 KVA | C21072900083 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1245 | 2021-07-29 | 12450 | keep | 0 | Jul | 2021 | 0.0084796 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-07-29 23:07 | 2021-07-30 13:14 | 40 | 014:07 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21072900084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 847 | 2021-07-29 | 33880 | keep | 0 | Jul | 2021 | 0.023076 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-07-29 23:17 | 2021-07-30 09:30 | 30 | 010:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | A21072900094 | New_Event | Bad Weather | Include | Include | Weather | 613 | 2021-07-29 | 18390 | keep | 0 | Jul | 2021 | 0.012525 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BARRANQUITAS | 2021-07-30 00:30 | 2021-07-30 03:31 | 3296 | 003:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C21073000007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 181 | 2021-07-30 | 596576 | keep | 0 | Jul | 2021 | 0.40633 | 0.0022449 | Sustained | FALSE | FALSE | Not_TMED_Event | 3296
MAYAGÃœEZ | 2021-07-30 00:36 | 2021-07-30 10:00 | 110 | 009:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21073000002 | New_Event | Bad Weather | Include | Include | Weather | 564 | 2021-07-30 | 62040 | keep | 0 | Jul | 2021 | 0.042255 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
ARECIBO | 2021-07-30 03:02 | 2021-07-30 11:00 | 12 | 007:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | A21073000003 | New_Event | Secondary Wire Down | Include | Include | Equipment | 478 | 2021-07-30 | 5736 | keep | 0 | Jul | 2021 | 0.0039068 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-07-30 03:57 | 2021-07-30 11:22 | 23 | 007:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REMPLAZO FUSIBLES POR BARRA EN EL T - 6 | C21073000008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 445 | 2021-07-30 | 10235 | keep | 0 | Jul | 2021 | 0.006971 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
PONCE | 2021-07-30 04:16 | 2021-07-30 04:17 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P2107300009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-30 | 3744 | keep | 0 | Jul | 2021 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2021-07-30 04:16 | 2021-07-30 04:17 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR 5004-06 | P21073000009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-30 | 3114 | keep | 0 | Jul | 2021 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
CAGUAS | 2021-07-30 05:07 | 2021-07-30 05:08 | 1403 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C21073000007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-30 | 1403 | keep | 0 | Jul | 2021 | 0.00095558 | 0.00095558 | Momentary | FALSE | FALSE | Not_TMED_Event | 1403
PONCE | 2021-07-30 05:37 | 2021-07-30 05:38 | 2163 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21073000010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-30 | 2163 | keep | 0 | Jul | 2021 | 0.0014732 | 0.0014732 | Momentary | FALSE | FALSE | Not_TMED_Event | 2163
PONCE | 2021-07-30 05:45 | 2021-07-30 05:46 | 2113 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P21073000011 | New_Event |  |  | Include | Wildlife | 1 | 2021-07-30 | 2113 | keep | 0 | Jul | 2021 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
PONCE | 2021-07-30 05:46 | 2021-07-30 09:42 | 80 | 003:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO FASE PRIMARIA | P21073000015 | 1st_after_momentary |  |  | Include | Wildlife | 236 | 2021-07-30 | 18880 | keep | 0 | Jul | 2021 | 0.012859 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BARRANQUITAS | 2021-07-30 06:04 | 2021-07-30 06:06 | 3296 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C21073000010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-30 | 6592 | keep | 0 | Jul | 2021 | 0.0044898 | 0.0022449 | Momentary | FALSE | FALSE | Not_TMED_Event | 3296
CANOVANAS | 2021-07-30 06:41 | 2021-07-30 15:06 | 100 | 008:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE CRITICO Y SE LEVANTO CONDUCTOR DEL SUELO | R21073000003 | New_Event | Wire Down | Include | Include | Equipment | 505 | 2021-07-30 | 50500 | keep | 0 | Jul | 2021 | 0.034395 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BARRANQUITAS | 2021-07-30 07:04 | 2021-08-01 12:06 | 50 | 053:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 50 EN CORTE DE LINEA SE REPARO BAJANTE SECUNDARIO | C21073000015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 3182 | 2021-07-30 | 159100 | keep | 0 | Jul | 2021 | 0.10836 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-07-30 07:11 | 2021-07-30 11:00 | 20 | 003:49 | P | DESGANCHE | 1 X 25 EN RAISER POR DESGANCHE | A21073000005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2021-07-30 | 4580 | keep | 0 | Jul | 2021 | 0.0031194 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2021-07-30 07:18 | 2021-07-30 17:50 | 12 | 010:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTES Y LINEA SECUNDARIA EN TRANSFORMADOR | M21073000006 | New_Event | Secondary Wire Down | Include | Include | Equipment | 632 | 2021-07-30 | 7584 | keep | 0 | Jul | 2021 | 0.0051654 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
HUMACAO | 2021-07-30 07:34 | 2021-07-30 10:01 | 40 | 002:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA REMPLAZO CAJA AVERIADA | C21073000016 | New_Event | Cutout Failure | Include | Include | Equipment | 147 | 2021-07-30 | 5880 | keep | 0 | Jul | 2021 | 0.0040048 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-07-30 07:51 | 2021-07-30 11:40 | 1185 | 003:49 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR SE REPARO BAJANTE PRIMARIO | M21073000008 | New_Event | Wire Down | Include | Include | Equipment | 229 | 2021-07-30 | 271365 | keep | 0 | Jul | 2021 | 0.18483 | 0.0008071 | Sustained | FALSE | FALSE | Not_TMED_Event | 1185
GUAYAMA | 2021-07-30 07:52 | 2021-07-30 10:03 | 150 | 002:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA FUERTES VIENTOS | P21073000013 | New_Event | Bad Weather | Include | Include | Weather | 131 | 2021-07-30 | 19650 | keep | 0 | Jul | 2021 | 0.013384 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
VEGA BAJA | 2021-07-30 07:55 | 2021-07-30 16:49 | 50 | 008:54 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZO DE POSTE EN MALAS CONDICIONES | B21073000013 | New_Event | Defective Pole | Include | Include | Equipment | 534 | 2021-07-30 | 26700 | keep | 0 | Jul | 2021 | 0.018185 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-07-30 08:20 | 2021-07-30 10:40 | 100 | 002:20 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA POR DESGANCHE | A21073000007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2021-07-30 | 14000 | keep | 0 | Jul | 2021 | 0.0095353 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-30 08:28 | 2021-07-30 08:29 | 2147 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21073000019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-30 | 2147 | keep | 0 | Jul | 2021 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
SAN JUAN | 2021-07-30 08:47 | 2021-07-30 08:48 | 893 | 000:01 | T | ERROR HUMANO | PERSONAL DE SUBESTACIONES REALIZANDO TRABAJOS DISPARO INTERRUPTOR POR ERROR | S21073000000 | New_Event | Human Error | Include | Include | Other | 1 | 2021-07-30 | 893 | keep | 0 | Jul | 2021 | 0.00060822 | 0.00060822 | Momentary | FALSE | FALSE | Not_TMED_Event | 893
GUAYAMA | 2021-07-30 09:07 | 2021-07-30 14:55 | 75 | 005:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | P21073000022 | New_Event | Wire Down | Include | Include | Equipment | 348 | 2021-07-30 | 26100 | keep | 0 | Jul | 2021 | 0.017777 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-07-30 09:22 | 2021-07-30 11:58 | 10 | 002:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | B21073000028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 156 | 2021-07-30 | 1560 | keep | 0 | Jul | 2021 | 0.0010625 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-07-30 09:28 | 2021-07-31 12:57 | 8 | 027:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21073000025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1649 | 2021-07-30 | 13192 | keep | 0 | Jul | 2021 | 0.008985 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-07-30 09:28 | 2021-07-30 21:05 | 100 | 011:37 | P | ESTRUCTURA AVERIADA | 2 X 65 EN CORTE DE LINEA SE RELOCALIZO LINEA PRIMARIA A OTRO POSTE EXISTENTE POR POSTE PRIMARIO PARTIDO | M21073000024 | New_Event | Defective Pole | Include | Include | Equipment | 697 | 2021-07-30 | 69700 | keep | 0 | Jul | 2021 | 0.047472 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-07-30 09:36 | 2021-08-01 12:44 | 65 | 051:08 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S21073000010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3068 | 2021-07-30 | 199420 | keep | 0 | Jul | 2021 | 0.13582 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
YAUCO | 2021-07-30 09:51 | 2021-07-30 13:05 | 80 | 003:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE CERRO CORTE DE LINEA | P21073000027 | New_Event | Wire Down | Include | Include | Equipment | 194 | 2021-07-30 | 15520 | keep | 0 | Jul | 2021 | 0.010571 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CANOVANAS | 2021-07-30 10:00 | 2021-07-30 16:55 | 25 | 006:55 | P | DESGANCHE | 1 X 10 Y 1 X 15 EN TRANSFORMADORES | R21073000011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 415 | 2021-07-30 | 10375 | keep | 0 | Jul | 2021 | 0.0070664 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2021-07-30 10:03 | 2021-07-30 16:57 | 12 | 006:54 | P | OTRAS CAUSAS | SE ABRIO TRANSFORMADOR PARA PASARLO A OTRO POSTE POR RELOCALIZACION DE POSTE Y LINEA | A21073000000 | New_Event | Other Causes | Include | Include | Other | 414 | 2021-07-30 | 4968 | keep | 0 | Jul | 2021 | 0.0033837 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
CANOVANAS | 2021-07-30 10:11 | 2021-07-30 14:22 | 1 | 004:11 | P | OTRAS CAUSAS | 1 X 25 EN TRANSFORMADOR PROBLEMA DEL CLIENTE | R21073000013 | New_Event | Other Causes | Include | Include | Other | 251 | 2021-07-30 | 251 | keep | 0 | Jul | 2021 | 0.00017095 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-07-30 10:11 | 2021-07-30 12:57 | 15 | 002:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B21073000035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 166 | 2021-07-30 | 2490 | keep | 0 | Jul | 2021 | 0.0016959 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-07-30 10:12 | 2021-07-30 13:10 | 25 | 002:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A21073000011 | New_Event | Bad Weather | Include | Include | Weather | 178 | 2021-07-30 | 4450 | keep | 0 | Jul | 2021 | 0.0030309 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-07-30 10:19 | 2021-07-30 14:30 | 10 | 004:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21073000037 | New_Event | Secondary Wire Down | Include | Include | Equipment | 251 | 2021-07-30 | 2510 | keep | 0 | Jul | 2021 | 0.0017095 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-30 10:21 | 2021-07-30 12:10 | 40 | 001:49 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21073000038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2021-07-30 | 4360 | keep | 0 | Jul | 2021 | 0.0029696 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-07-30 10:24 | 2021-07-30 17:19 | 40 | 006:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21073000032 | New_Event | Bad Weather | Include | Include | Weather | 415 | 2021-07-30 | 16600 | keep | 0 | Jul | 2021 | 0.011306 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-07-30 10:34 | 2021-07-30 15:25 | 12 | 004:51 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR ESCAPE DE ACEITE DE 50KVA X 50 KVA | A21073000000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 291 | 2021-07-30 | 3492 | keep | 0 | Jul | 2021 | 0.0023784 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-07-30 10:40 | 2021-07-31 14:56 | 75 | 028:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA | M21073000030 | New_Event | Bad Weather | Include | Include | Weather | 1696 | 2021-07-30 | 127200 | keep | 0 | Jul | 2021 | 0.086635 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
MAYAGÃœEZ | 2021-07-30 11:30 | 2021-07-30 14:44 | 200 | 003:14 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO AVERIADO POR POSTE DE 45' DE METAL | M21073000000 | New_Event | Defective Pole | Include | Include | Equipment | 194 | 2021-07-30 | 38800 | keep | 0 | Jul | 2021 | 0.026427 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-07-30 11:30 | 2021-07-30 16:20 | 30 | 004:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR NEUTRAL PRIMARIO ROTO | M21073000101 | New_Event | Wire Down | Include | Include | Equipment | 290 | 2021-07-30 | 8700 | keep | 0 | Jul | 2021 | 0.0059255 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-07-30 11:46 | 2021-07-30 17:10 | 1 | 005:24 | P | OTRAS CAUSAS | 1 X 10 EN TRANSFORMADOR PROBLEMA DEL CLIENTE | R21073000025 | New_Event | Other Causes | Include | Include | Other | 324 | 2021-07-30 | 324 | keep | 0 | Jul | 2021 | 0.00022067 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-07-30 12:06 | 2021-07-30 13:42 | 18 | 001:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE LINEA A CAJA Y DESGANCHE | B21073000054 | New_Event | Wire Down | Include | Include | Equipment | 96 | 2021-07-30 | 1728 | keep | 0 | Jul | 2021 | 0.0011769 | 1.226e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 18
ARECIBO | 2021-07-30 12:12 | 2021-07-30 15:33 | 35 | 003:21 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA | A21073000017 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 201 | 2021-07-30 | 7035 | keep | 0 | Jul | 2021 | 0.0047915 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
CAGUAS | 2021-07-30 12:21 | 2021-07-31 11:07 | 35 | 022:46 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO CAUSA | C21073000035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1366 | 2021-07-30 | 47810 | keep | 0 | Jul | 2021 | 0.032563 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-07-30 12:21 | 2021-07-30 19:00 | 15 | 006:39 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA X 50 KVA | A21073000018 | New_Event | Service Transformer Failure | Include | Include | Equipment | 399 | 2021-07-30 | 5985 | keep | 0 | Jul | 2021 | 0.0040764 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-07-30 12:28 | 2021-07-31 10:01 | 10 | 021:33 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | S21073000020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1293 | 2021-07-30 | 12930 | keep | 0 | Jul | 2021 | 0.0088066 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-30 12:37 | 2021-07-30 15:16 | 50 | 002:39 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21073000059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 159 | 2021-07-30 | 7950 | keep | 0 | Jul | 2021 | 0.0054147 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-07-30 12:49 | 2021-07-30 15:25 | 8 | 002:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR AVE CRUZO FASES | A21073000021 | New_Event |  |  | Include | Wildlife | 156 | 2021-07-30 | 1248 | keep | 0 | Jul | 2021 | 0.00085001 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2021-07-30 12:50 | 2021-07-30 18:36 | 80 | 005:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA LINEAS PRIMARIAS ARRIADAS | P21073000053 | New_Event | Wire Down | Include | Include | Equipment | 346 | 2021-07-30 | 27680 | keep | 0 | Jul | 2021 | 0.018853 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
YAUCO | 2021-07-30 13:05 | 2021-07-30 13:31 | 2440 | 000:26 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR A PETICION SUP LUIS LEON SE ENCONTRO LINEA PRIMARIA ENERGIZADA EN EL SUELO SE ABRIO CORTE DE LINEA Y SE COLOCO INTERRUPTOR EN SERVICIO | P21073000039 | New_Event | Wire Down | Include | Include | Equipment | 26 | 2021-07-30 | 63440 | keep | 0 | Jul | 2021 | 0.043209 | 0.0016619 | Sustained | FALSE | TRUE | Not_TMED_Event | 2440
MAYAGÃœEZ | 2021-07-30 13:05 | 2021-07-30 16:54 | 7 | 003:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 5 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21073000042 | New_Event | Bad Weather | Include | Include | Weather | 229 | 2021-07-30 | 1603 | keep | 0 | Jul | 2021 | 0.0010918 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-07-30 13:07 | 2021-07-30 13:10 | 1399 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1704-02 | B21073000061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-07-30 | 4197 | keep | 0 | Jul | 2021 | 0.0028586 | 0.00095285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1399
BAYAMON | 2021-07-30 13:07 | 2021-07-30 13:10 | 302 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA ESTA TRANSFERIDA AL 1704-01 | B21073000061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-07-30 | 906 | keep | 0 | Jul | 2021 | 0.00061707 | 0.00020569 | Momentary | FALSE | FALSE | Not_TMED_Event | 302
CAGUAS | 2021-07-30 13:14 | 2021-07-30 19:29 | 50 | 006:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21073000037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 375 | 2021-07-30 | 18750 | keep | 0 | Jul | 2021 | 0.012771 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-30 13:20 | 2021-07-30 18:41 | 40 | 005:21 | P | NO SE REPORTO CAUSA | 2 X 20 EN CORTE DE LINEA | S21073000025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 321 | 2021-07-30 | 12840 | keep | 0 | Jul | 2021 | 0.0087453 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
YAUCO | 2021-07-30 13:31 | 2021-07-30 17:50 | 80 | 004:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA Y SE CERRO CORTE DE LINEA | P21073000027 | Partial_restoration | Wire Down | Include | Include | Equipment | 259 | 2021-07-30 | 20720 | keep | 0 | Jul | 2021 | 0.014112 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
PONCE | 2021-07-30 13:43 | 2021-07-30 15:38 | 50 | 001:55 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | P21073000040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2021-07-30 | 5750 | keep | 0 | Jul | 2021 | 0.0039163 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-07-30 13:45 | 2021-07-30 17:00 | 300 | 003:15 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE | M21073000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2021-07-30 | 58500 | keep | 0 | Jul | 2021 | 0.039844 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
BAYAMON | 2021-07-30 14:14 | 2021-07-30 18:02 | 2 | 003:48 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA X 50 KVA | B21073000028 | New_Event | Service Transformer Failure | Include | Include | Equipment | 228 | 2021-07-30 | 456 | keep | 0 | Jul | 2021 | 0.00031058 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2021-07-30 14:21 | 2021-07-30 16:58 | 10 | 002:37 | P | NO SE REPORTO CAUSA | 1 X 10 EN RISER | B21073000066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 157 | 2021-07-30 | 1570 | keep | 0 | Jul | 2021 | 0.0010693 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-30 14:30 | 2021-07-30 23:20 | 40 | 008:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21073000053 | New_Event | Bad Weather | Include | Include | Weather | 530 | 2021-07-30 | 21200 | keep | 0 | Jul | 2021 | 0.014439 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-07-30 14:39 | 2021-07-30 15:20 | 8 | 000:41 | P | TRANSFORMADOR AVERIADO | SE ABRIO TRANSFORMADOR Y SE REPARARON LOS BUSHING PRIMARIOS | A21073000025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 41 | 2021-07-30 | 328 | keep | 0 | Jul | 2021 | 0.0002234 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2021-07-30 14:46 | 2021-07-30 16:13 | 5 | 001:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | R21073000036 | New_Event | Cutout Failure | Include | Include | Equipment | 87 | 2021-07-30 | 435 | keep | 0 | Jul | 2021 | 0.00029628 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
CANOVANAS | 2021-07-30 14:48 | 2021-07-30 15:29 | 33 | 000:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | R21073000037 | New_Event |  |  | Include | Wildlife | 41 | 2021-07-30 | 1353 | keep | 0 | Jul | 2021 | 0.00092152 | 2.2476e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 33
MAYAGÃœEZ | 2021-07-30 14:50 | 2021-07-30 21:44 | 175 | 006:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21073000063 | New_Event | Bad Weather | Include | Include | Weather | 414 | 2021-07-30 | 72450 | keep | 0 | Jul | 2021 | 0.049345 | 0.00011919 | Sustained | FALSE | TRUE | Not_TMED_Event | 175
HUMACAO | 2021-07-30 15:14 | 2021-07-30 18:51 | 50 | 003:37 | P | NO SE REPORTO CAUSA | 1 X 125 SMU 20 EN SU - 11 NO CAUSA | C21073000039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 217 | 2021-07-30 | 10850 | keep | 0 | Jul | 2021 | 0.0073899 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-07-30 15:16 | 2021-07-30 18:02 | 55 | 002:46 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | S21073000032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 166 | 2021-07-30 | 9130 | keep | 0 | Jul | 2021 | 0.0062184 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
SAN JUAN | 2021-07-30 15:28 | 2021-07-30 21:13 | 1422 | 005:45 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERRADO AVERIADO Y SE CERRARON MACHETES EN SU-LOS TECATOS CONTRA 1336-08 30% DE LA CARGA POR EL 1336-08 | S21073000101 | New_Event | UG Cable Fault | Include | Include | Equipment | 345 | 2021-07-30 | 490590 | keep | 0 | Jul | 2021 | 0.33414 | 0.00096852 | Sustained | FALSE | FALSE | Not_TMED_Event | 1422
SAN JUAN | 2021-07-30 15:28 | 2021-07-30 15:48 | 5290 | 000:20 | T | CABLE SOTERRADO AVERIADO | SE ABRIO N/O EN SU LOS TECATOS Y SE CERRO POR SCADA LLEVANDO 30% DEL 1204-04 | S21073000000 | New_Event | UG Cable Fault | Include | Include | Equipment | 20 | 2021-07-30 | 105800 | keep | 0 | Jul | 2021 | 0.07206 | 0.003603 | Sustained | FALSE | FALSE | Not_TMED_Event | 5290
UTUADO | 2021-07-30 15:29 | 2021-07-30 16:34 | 30 | 001:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | A21073000028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 65 | 2021-07-30 | 1950 | keep | 0 | Jul | 2021 | 0.0013281 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BARRANQUITAS | 2021-07-30 15:32 | 2021-07-30 18:03 | 10 | 002:31 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHO | C21073000046 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 151 | 2021-07-30 | 1510 | keep | 0 | Jul | 2021 | 0.0010285 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-07-30 15:34 | 2021-07-30 15:36 | 976 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C21073000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-07-30 | 1952 | keep | 0 | Jul | 2021 | 0.0013295 | 0.00066475 | Momentary | FALSE | FALSE | Not_TMED_Event | 976
ARECIBO | 2021-07-30 15:38 | 2021-07-30 16:00 | 10 | 000:22 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR ESCAPE DE ACEITE DE 37.5 KVA X 37.5 KVA | A21073000029 | New_Event | Service Transformer Failure | Include | Include | Equipment | 22 | 2021-07-30 | 220 | keep | 0 | Jul | 2021 | 0.00014984 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-30 16:36 | 2021-07-31 10:45 | 30 | 018:09 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | M21073000086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1089 | 2021-07-30 | 32670 | keep | 0 | Jul | 2021 | 0.022251 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
VEGA BAJA | 2021-07-30 16:46 | 2021-07-30 16:47 | 2216 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO Y SE CERRO POR CONTROL | B21073000071 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-30 | 2216 | keep | 0 | Jul | 2021 | 0.0015093 | 0.0015093 | Momentary | FALSE | FALSE | Not_TMED_Event | 2216
VEGA BAJA | 2021-07-30 16:47 | 2021-07-30 20:07 | 8 | 003:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21073000060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 200 | 2021-07-30 | 1600 | keep | 0 | Jul | 2021 | 0.0010898 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2021-07-30 16:54 | 2021-07-30 18:51 | 130 | 001:57 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 40 Y 1 X 65 EN SU-S CONTAMINADOS SE LIMPIARON | R21073000049 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 117 | 2021-07-30 | 15210 | keep | 0 | Jul | 2021 | 0.010359 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
YAUCO | 2021-07-30 16:54 | 2021-07-30 23:33 | 10 | 006:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO A CAJA EN TRANSFORMADOR | P21073000064 | New_Event | Wire Down | Include | Include | Equipment | 399 | 2021-07-30 | 3990 | keep | 0 | Jul | 2021 | 0.0027176 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-07-30 17:01 | 2021-07-30 17:02 | 281 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M21073000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-30 | 281 | keep | 0 | Jul | 2021 | 0.00019139 | 0.00019139 | Momentary | FALSE | TRUE | Not_TMED_Event | 281
MAYAGÃœEZ | 2021-07-30 17:01 | 2021-07-30 17:02 | 1252 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M21073000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-30 | 1252 | keep | 0 | Jul | 2021 | 0.00085273 | 0.00085273 | Momentary | FALSE | TRUE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2021-07-30 17:01 | 2021-07-30 17:02 | 595 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M21073000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-30 | 595 | keep | 0 | Jul | 2021 | 0.00040525 | 0.00040525 | Momentary | FALSE | TRUE | Not_TMED_Event | 595
MAYAGÃœEZ | 2021-07-30 17:01 | 2021-07-30 17:02 | 51 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M21073000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-30 | 51 | keep | 0 | Jul | 2021 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 51
MAYAGÃœEZ | 2021-07-30 17:01 | 2021-07-30 17:02 | 721 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 8100 | M21073000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-07-30 | 721 | keep | 0 | Jul | 2021 | 0.00049107 | 0.00049107 | Momentary | FALSE | TRUE | Not_TMED_Event | 721
MAYAGÃœEZ | 2021-07-30 17:11 | 2021-07-30 17:12 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 6007-05 | M21073000089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-30 | 393 | keep | 0 | Jul | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2021-07-30 17:11 | 2021-07-30 17:12 | 4 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6007-04 QUE ESTA LLEVANDO LA CARGA DEL 6007-05 | M21073000089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-30 | 4 | keep | 0 | Jul | 2021 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2021-07-30 17:13 | 2021-07-31 14:02 | 95 | 020:49 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | R21073000058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1249 | 2021-07-30 | 118655 | keep | 0 | Jul | 2021 | 0.080815 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
PONCE | 2021-07-30 17:14 | 2021-07-30 19:57 | 6 | 002:43 | P | DESGANCHE | SE CERRO CAJA PRIMARIA EN TRANSFORMADOR ABIERTA AL CAER RAMA | P21073000069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2021-07-30 | 978 | keep | 0 | Jul | 2021 | 0.00066611 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-07-30 17:18 | 2021-07-30 17:19 | 3295 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21073000072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-30 | 3295 | keep | 0 | Jul | 2021 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
ARECIBO | 2021-07-30 17:21 | 2021-07-30 18:33 | 10 | 001:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | A21073000000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 72 | 2021-07-30 | 720 | keep | 0 | Jul | 2021 | 0.00049039 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-07-30 17:39 | 2021-07-31 09:57 | 90 | 016:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 Y 1 X 50 EN CORTES DE LINEAS SE REPARO CONDUCTOR ROTO Y REEMPLAZO AISLADOR ROTO | C21073000059 | New_Event | Wire Down | Include | Include | Equipment | 978 | 2021-07-30 | 88020 | keep | 0 | Jul | 2021 | 0.05995 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
CAGUAS | 2021-07-30 17:48 | 2021-07-31 10:22 | 11 | 016:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21073100061 | New_Event | Bad Weather | Include | Include | Weather | 994 | 2021-07-30 | 10934 | keep | 0 | Jul | 2021 | 0.0074471 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2021-07-30 18:15 | 2021-07-30 19:25 | 15 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21073000039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2021-07-30 | 1050 | keep | 0 | Jul | 2021 | 0.00071515 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
AGUADILLA | 2021-07-30 18:42 | 2021-07-30 21:40 | 80 | 002:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21073000097 | New_Event | Bad Weather | Include | Include | Weather | 178 | 2021-07-30 | 14240 | keep | 0 | Jul | 2021 | 0.0096988 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CANOVANAS | 2021-07-30 18:52 | 2021-07-30 22:33 | 858 | 003:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO SE CERRO MACHETES | R21073000000 | New_Event | Wire Down | Include | Include | Equipment | 221 | 2021-07-30 | 189618 | keep | 0 | Jul | 2021 | 0.12915 | 0.00058438 | Sustained | FALSE | FALSE | Not_TMED_Event | 858
ARECIBO | 2021-07-30 18:53 | 2021-07-30 20:29 | 60 | 001:36 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | A21073000033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2021-07-30 | 5760 | keep | 0 | Jul | 2021 | 0.0039231 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-07-30 18:56 | 2021-07-30 18:57 | 492 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21073000073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-30 | 492 | keep | 0 | Jul | 2021 | 0.0003351 | 0.0003351 | Momentary | FALSE | FALSE | Not_TMED_Event | 492
SAN JUAN | 2021-07-30 19:23 | 2021-07-30 21:25 | 4481 | 002:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE REMPLAZO AISLADOR DEFECTUOSO Y SE CERRO POR SCADA PARTE 2,000 POR EL 1619-02 | S21073000000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 122 | 2021-07-30 | 546682 | keep | 0 | Jul | 2021 | 0.37234 | 0.003052 | Sustained | FALSE | FALSE | Not_TMED_Event | 4481
SAN JUAN | 2021-07-30 19:23 | 2021-07-30 19:24 | 2000 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DEL 1619-02 LLEVANDO 2,000 CLIENTES DEL 1336-06 | R21073000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-30 | 2000 | keep | 0 | Jul | 2021 | 0.0013622 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
HUMACAO | 2021-07-30 19:46 | 2021-07-31 15:52 | 10 | 020:06 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR AVERIADO DE 50KVA X 50KVA | C21073000071 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1206 | 2021-07-30 | 12060 | keep | 0 | Jul | 2021 | 0.008214 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-07-30 20:04 | 2021-07-30 21:53 | 3838 | 001:49 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO INTERRUPTOR SE SECCIONALIZO POSTE PRIMARIO IMPACTADO CERRADO POR CONTROL | R21073000123 | New_Event |  |  | Include | Wildlife | 109 | 2021-07-30 | 418342 | keep | 0 | Jul | 2021 | 0.28493 | 0.002614 | Sustained | FALSE | FALSE | Not_TMED_Event | 3838
VEGA BAJA | 2021-07-30 20:22 | 2021-07-31 11:51 | 30 | 015:29 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21073000078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 929 | 2021-07-30 | 27870 | keep | 0 | Jul | 2021 | 0.018982 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-07-30 20:27 | 2021-07-31 17:11 | 1 | 020:44 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU-1 | S21073000188 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1244 | 2021-07-30 | 1244 | keep | 0 | Jul | 2021 | 0.00084728 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2021-07-30 20:34 | 2021-07-31 00:21 | 150 | 003:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO A CAJA EN CORTE DE LINEA | P21073000078 | New_Event | Wire Down | Include | Include | Equipment | 227 | 2021-07-30 | 34050 | keep | 0 | Jul | 2021 | 0.023191 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-07-30 20:35 | 2021-07-31 09:27 | 100 | 012:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA SE RETIRO RATON DE SU-1 | B21073000081 | New_Event |  |  | Include | Wildlife | 772 | 2021-07-30 | 77200 | keep | 0 | Jul | 2021 | 0.052581 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-07-30 20:35 | 2021-07-31 09:48 | 60 | 013:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21073000081 | New_Event | Bad Weather | Include | Include | Weather | 793 | 2021-07-30 | 47580 | keep | 0 | Jul | 2021 | 0.032407 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
FAJARDO | 2021-07-30 20:51 | 2021-07-31 11:12 | 40 | 014:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | R21073000148 | New_Event | Bad Weather | Include | Include | Weather | 861 | 2021-07-30 | 34440 | keep | 0 | Jul | 2021 | 0.023457 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-30 21:06 | 2021-07-31 09:32 | 64 | 012:26 | P | DESGANCHE | 1 X 140 EN CONVERTIDOR Y 1 X 40 EN OTRO CORTE DE LINEA SE REALIZO DESGANCHE | B21073000088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 746 | 2021-07-30 | 47744 | keep | 0 | Jul | 2021 | 0.032518 | 4.359e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 64
FAJARDO | 2021-07-30 21:08 | 2021-07-31 11:01 | 150 | 013:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN CORTE DE LINEA REMPLAZO 2 CAJAS QUEMADAS Y PIN POLE TOP | R21073000156 | New_Event | Cutout Failure | Include | Include | Equipment | 833 | 2021-07-30 | 124950 | keep | 0 | Jul | 2021 | 0.085103 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CANOVANAS | 2021-07-30 21:10 | 2021-07-31 11:09 | 40 | 013:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA AVERIADA NO FUNDIO | R21073000157 | New_Event | Cutout Failure | Include | Include | Equipment | 839 | 2021-07-30 | 33560 | keep | 0 | Jul | 2021 | 0.022858 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-07-30 21:42 | 2021-07-31 20:16 | 10 | 022:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO TRANSFORMADOR Y SE CERRO PUENTE DE LINEA A CAJA | S21073000199 | New_Event | Wire Down | Include | Include | Equipment | 1354 | 2021-07-30 | 13540 | keep | 0 | Jul | 2021 | 0.009222 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CANOVANAS | 2021-07-30 21:53 | 2021-07-31 09:52 | 28 | 011:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | PUENTE ABIERTO EN EL TRONCAL SE SECCIONALIZO AISLADORES ROTOS Y PUENTES ABIERTOS | R21073000123 | Partial_restoration |  |  | Include | Wildlife | 719 | 2021-07-30 | 20132 | keep | 0 | Jul | 2021 | 0.013712 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-07-30 22:25 | 2021-07-30 22:26 | 3296 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C21073000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-30 | 3296 | keep | 0 | Jul | 2021 | 0.0022449 | 0.0022449 | Momentary | FALSE | FALSE | Not_TMED_Event | 3296
UTUADO | 2021-07-30 22:49 | 2021-07-30 22:51 | 3316 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR SE CERRO INTERRUPTOR LINEA PRIMARIA PARTIDA | A21073000036 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2021-07-30 | 6632 | keep | 0 | Jul | 2021 | 0.004517 | 0.0022585 | Momentary | FALSE | TRUE | Not_TMED_Event | 3316
UTUADO | 2021-07-30 22:51 | 2021-07-31 01:24 | 200 | 002:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA PARTIDA SE ABRIO CORTE DE LINEA PARA SECCIONALIZAR | A21073000037 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 153 | 2021-07-30 | 30600 | keep | 0 | Jul | 2021 | 0.020842 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-07-30 23:04 | 2021-07-31 11:33 | 150 | 012:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPORTA PUENTE ABIERTO DE LINEA TRONCAL | S21073002060 | New_Event | Wire Down | Include | Include | Equipment | 749 | 2021-07-30 | 112350 | keep | 0 | Jul | 2021 | 0.076521 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-07-30 23:22 | 2021-07-30 23:23 | 1590 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR | C21073000092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-30 | 1590 | keep | 0 | Jul | 2021 | 0.0010829 | 0.0010829 | Momentary | FALSE | FALSE | Not_TMED_Event | 1590
CAGUAS | 2021-07-30 23:23 | 2021-07-31 10:08 | 150 | 010:45 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA | C21073000094 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 645 | 2021-07-30 | 96750 | keep | 0 | Jul | 2021 | 0.065896 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
HUMACAO | 2021-07-30 23:30 | 2021-07-31 10:32 | 300 | 011:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 SALIDA CONVERTIDOR REMPLAZO CAJA QUEMADA | C21073000093 | New_Event | Cutout Failure | Include | Include | Equipment | 662 | 2021-07-30 | 198600 | keep | 0 | Jul | 2021 | 0.13527 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
ARECIBO | 2021-07-31 00:13 | 2021-07-31 11:25 | 150 | 011:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21073100004 | New_Event | Wire Down | Include | Include | Equipment | 672 | 2021-07-31 | 100800 | keep | 0 | Jul | 2021 | 0.068654 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
HUMACAO | 2021-07-31 00:17 | 2021-07-31 14:30 | 45 | 014:13 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA REEMPLAZO AISLADOR Y REPARO CONDUCTOR ROTO | C21073100002 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 853 | 2021-07-31 | 38385 | keep | 0 | Jul | 2021 | 0.026144 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
FAJARDO | 2021-07-31 00:41 | 2021-07-31 09:10 | 60 | 008:29 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21073100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 509 | 2021-07-31 | 30540 | keep | 0 | Jul | 2021 | 0.020801 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
UTUADO | 2021-07-31 01:24 | 2021-07-31 02:08 | 900 | 000:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO LINEA PRIMARIA PARTIDA SE CERRO CORTE DE LINEA | A21073000037 | New_Event | Wire Down | Include | Include | Equipment | 44 | 2021-07-31 | 39600 | keep | 0 | Jul | 2021 | 0.026971 | 0.00061299 | Sustained | FALSE | TRUE | Not_TMED_Event | 900
UTUADO | 2021-07-31 02:08 | 2021-07-31 13:00 | 200 | 010:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | A21073100005 | Partial_restoration | Wire Down | Include | Include | Equipment | 652 | 2021-07-31 | 130400 | keep | 0 | Jul | 2021 | 0.088815 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-07-31 02:34 | 2021-07-31 15:28 | 10 | 012:54 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21073100006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 774 | 2021-07-31 | 7740 | keep | 0 | Jul | 2021 | 0.0052717 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
PONCE | 2021-07-31 03:11 | 2021-07-31 03:12 | 1478 | 000:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | RECIERRE DE INTERRUPTOR | P21073100002 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2021-07-31 | 1478 | keep | 0 | Jul | 2021 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
PONCE | 2021-07-31 03:12 | 2021-07-31 19:10 | 300 | 015:58 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REMPLAZO CAJA EN SU-4 | P21073100089 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 958 | 2021-07-31 | 287400 | keep | 0 | Jul | 2021 | 0.19575 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
GUAYAMA | 2021-07-31 03:56 | 2021-07-31 09:03 | 125 | 005:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA FUERTES LLUVIAS | P21073100005 | New_Event | Bad Weather | Include | Include | Weather | 307 | 2021-07-31 | 38375 | keep | 0 | Jul | 2021 | 0.026137 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
PONCE | 2021-07-31 04:19 | 2021-07-31 04:20 | 1952 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRPTOR | P21073100009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-31 | 1952 | keep | 0 | Jul | 2021 | 0.0013295 | 0.0013295 | Momentary | FALSE | FALSE | Not_TMED_Event | 1952
BAYAMON | 2021-07-31 04:39 | 2021-07-31 12:24 | 50 | 007:45 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21073100004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 465 | 2021-07-31 | 23250 | keep | 0 | Jul | 2021 | 0.015835 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-07-31 04:45 | 2021-07-31 04:46 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21073100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-31 | 641 | keep | 0 | Jul | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-07-31 04:46 | 2021-07-31 04:51 | 1681 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO CARGA POR EL 1303-04 | S21073100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-07-31 | 8405 | keep | 0 | Jul | 2021 | 0.0057246 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-07-31 04:46 | 2021-07-31 04:51 | 1598 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO CARGA POR EL 1303-04 | S21073100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-07-31 | 7990 | keep | 0 | Jul | 2021 | 0.005442 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2021-07-31 04:47 | 2021-07-31 04:48 | 225 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR SCADA CARGA POR EL 1908-03 | S21073100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-31 | 225 | keep | 0 | Jul | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-07-31 04:47 | 2021-07-31 04:48 | 3957 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVANDO CARGA DEL 1303-04 | S21073100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-31 | 3957 | keep | 0 | Jul | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
BAYAMON | 2021-07-31 05:30 | 2021-07-31 08:08 | 3798 | 002:38 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO Y SE CERRO POR SCADA | B21073100005 | New_Event | Wire Down | Include | Include | Equipment | 158 | 2021-07-31 | 600084 | keep | 0 | Jul | 2021 | 0.40871 | 0.0025868 | Sustained | FALSE | FALSE | Not_TMED_Event | 3798
PONCE | 2021-07-31 05:56 | 2021-07-31 05:57 | 2113 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DE INTERRUPTOR | P21073100012 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2021-07-31 | 2113 | keep | 0 | Jul | 2021 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
PONCE | 2021-07-31 05:57 | 2021-07-31 16:28 | 1100 | 010:31 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZARON TRES MACHETES DE 900 AMPERES AVERIADOS | P21073100014 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 631 | 2021-07-31 | 694100 | keep | 0 | Jul | 2021 | 0.47275 | 0.0007492 | Sustained | FALSE | FALSE | Not_TMED_Event | 1100
SAN JUAN | 2021-07-31 05:58 | 2021-07-31 17:01 | 80 | 011:03 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA Y 1 X 100 EN CORTE DE LINEA | S21073100010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 663 | 2021-07-31 | 53040 | keep | 0 | Jul | 2021 | 0.036125 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-07-31 07:04 | 2021-07-31 16:23 | 20 | 009:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21073100013 | New_Event | Bad Weather | Include | Include | Weather | 559 | 2021-07-31 | 11180 | keep | 0 | Jul | 2021 | 0.0076146 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-07-31 07:06 | 2021-07-31 07:07 | 5062 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21073100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-31 | 5062 | keep | 0 | Jul | 2021 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
CAGUAS | 2021-07-31 07:27 | 2021-07-31 11:12 | 120 | 003:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA REMPLAZO CAJA AVERIADA | C21073100016 | New_Event | Cutout Failure | Include | Include | Equipment | 225 | 2021-07-31 | 27000 | keep | 0 | Jul | 2021 | 0.01839 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
BARRANQUITAS | 2021-07-31 07:29 | 2021-07-31 12:21 | 95 | 004:52 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C21073100017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 292 | 2021-07-31 | 27740 | keep | 0 | Jul | 2021 | 0.018894 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
CAGUAS | 2021-07-31 07:35 | 2021-07-31 15:32 | 15 | 007:57 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C21073100020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 477 | 2021-07-31 | 7155 | keep | 0 | Jul | 2021 | 0.0048732 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-07-31 07:45 | 2021-07-31 15:36 | 10 | 007:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | R21073100015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 471 | 2021-07-31 | 4710 | keep | 0 | Jul | 2021 | 0.003208 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-07-31 07:49 | 2021-07-31 13:42 | 25 | 005:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE CERRO PUENTE | S21073100012 | New_Event | Wire Down | Include | Include | Equipment | 353 | 2021-07-31 | 8825 | keep | 0 | Jul | 2021 | 0.0060107 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
VEGA BAJA | 2021-07-31 07:59 | 2021-07-31 10:41 | 1 | 002:42 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | B21073100025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2021-07-31 | 162 | keep | 0 | Jul | 2021 | 0.00011034 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-07-31 08:02 | 2021-07-31 21:39 | 500 | 013:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO Y SE CERRO CORTE DE LINEA | M21073100009 | New_Event | Wire Down | Include | Include | Equipment | 817 | 2021-07-31 | 408500 | keep | 0 | Jul | 2021 | 0.27823 | 0.00034055 | Sustained | FALSE | TRUE | Not_TMED_Event | 500
BAYAMON | 2021-07-31 08:08 | 2021-07-31 08:12 | 2300 | 000:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO Y AMARRO PARTE CONTRA 1718-02 | B21073100005 | Partial_restoration | Wire Down | Include | Include | Equipment | 4 | 2021-07-31 | 9200 | keep | 0 | Jul | 2021 | 0.0062661 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-07-31 08:10 | 2021-07-31 12:20 | 60 | 004:10 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21073100028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 250 | 2021-07-31 | 15000 | keep | 0 | Jul | 2021 | 0.010216 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-07-31 08:12 | 2021-07-31 15:46 | 380 | 007:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y SE NORMALIZO LAS CARGAS | B21073100005 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 454 | 2021-07-31 | 172520 | keep | 0 | Jul | 2021 | 0.1175 | 0.00025882 | Sustained | FALSE | FALSE | Not_TMED_Event | 380
ARECIBO | 2021-07-31 08:45 | 2021-07-31 11:00 | 2 | 002:15 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO DOS TRANSFORMADORES QUEMADOS UNO 25 KVA Y UNO 15 KVA POR 25 Y 15 KVA RESPECTIVAMENTE. | A21073100017 | New_Event | Service Transformer Failure | Include | Include | Equipment | 135 | 2021-07-31 | 270 | keep | 0 | Jul | 2021 | 0.0001839 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2021-07-31 08:46 | 2021-07-31 08:53 | 4381 | 000:07 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO SE REPORTA LA CAUSA | M21073100015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2021-07-31 | 30667 | keep | 0 | Jul | 2021 | 0.020887 | 0.0029839 | Sustained | FALSE | FALSE | Not_TMED_Event | 4381
PONCE | 2021-07-31 08:56 | 2021-07-31 10:43 | 100 | 001:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | P21070310002 | New_Event | Cutout Failure | Include | Include | Equipment | 107 | 2021-07-31 | 10700 | keep | 0 | Jul | 2021 | 0.0072877 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-31 08:59 | 2021-07-31 16:12 | 95 | 007:13 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 40 EN CORTES DE LINEAS | R21073100031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 433 | 2021-07-31 | 41135 | keep | 0 | Jul | 2021 | 0.028017 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
PONCE | 2021-07-31 09:14 | 2021-07-31 11:39 | 15 | 002:25 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | P21073100028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 145 | 2021-07-31 | 2175 | keep | 0 | Jul | 2021 | 0.0014814 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CAGUAS | 2021-07-31 09:25 | 2021-07-31 14:52 | 90 | 005:27 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C21073100045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 327 | 2021-07-31 | 29430 | keep | 0 | Jul | 2021 | 0.020045 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
BAYAMON | 2021-07-31 09:46 | 2021-07-31 14:17 | 25 | 004:31 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21073100045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 271 | 2021-07-31 | 6775 | keep | 0 | Jul | 2021 | 0.0046144 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-07-31 09:51 | 2021-08-02 16:31 | 30 | 054:40 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | B21073100048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3280 | 2021-07-31 | 98400 | keep | 0 | Jul | 2021 | 0.06702 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-07-31 09:51 | 2021-08-01 09:45 | 50 | 023:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO BAJANTE DE LINEA A CAJA | C21073100050 | New_Event | Wire Down | Include | Include | Equipment | 1434 | 2021-07-31 | 71700 | keep | 0 | Jul | 2021 | 0.048835 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-07-31 09:52 | 2021-07-31 13:21 | 100 | 003:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | REMPLAZO AISLADORES QUEMADOS Y CERRO PUENTES | R21073000123 | Additional_clients |  |  | Include | Wildlife | 209 | 2021-07-31 | 20900 | keep | 0 | Jul | 2021 | 0.014235 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-07-31 09:55 | 2021-07-31 15:15 | 60 | 005:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21073100026 | New_Event | Wire Down | Include | Include | Equipment | 320 | 2021-07-31 | 19200 | keep | 0 | Jul | 2021 | 0.013077 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-07-31 09:59 | 2021-07-31 16:22 | 50 | 006:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B21073100051 | New_Event | Cutout Failure | Include | Include | Equipment | 383 | 2021-07-31 | 19150 | keep | 0 | Jul | 2021 | 0.013043 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-31 10:39 | 2021-07-31 18:09 | 75 | 007:30 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21073100040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 450 | 2021-07-31 | 33750 | keep | 0 | Jul | 2021 | 0.022987 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
YAUCO | 2021-07-31 10:47 | 2021-07-31 16:46 | 125 | 005:59 | P | ESTRUCTURA AVERIADA | 1 X 80 EN CORTE DE LINEA POSTE PRIMARIO PARTIDO SE ABRIO PUENTES PARA SECCIONALIZAR AVERIA | P21073100042 | New_Event | Defective Pole | Include | Include | Equipment | 359 | 2021-07-31 | 44875 | keep | 0 | Jul | 2021 | 0.030564 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
BARRANQUITAS | 2021-07-31 10:54 | 2021-07-31 10:55 | 3296 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C21073100007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-31 | 3296 | keep | 0 | Jul | 2021 | 0.0022449 | 0.0022449 | Momentary | FALSE | FALSE | Not_TMED_Event | 3296
SAN JUAN | 2021-07-31 10:56 | 2021-07-31 15:29 | 50 | 004:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE LEVANTO AEREO PROVISIONAL DEL SUELO | S21073100043 | New_Event | Wire Down | Include | Include | Equipment | 273 | 2021-07-31 | 13650 | keep | 0 | Jul | 2021 | 0.009297 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-31 11:33 | 2021-07-31 12:14 | 790 | 000:41 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA DAR PUENTE ABIERTO EN LINEA TRONCAL | S21073100049 | Additional_clients | Wire Down | Include | Include | Equipment | 41 | 2021-07-31 | 32390 | keep | 0 | Jul | 2021 | 0.022061 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
PONCE | 2021-07-31 12:01 | 2021-07-31 14:06 | 125 | 002:05 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | P21073100048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2021-07-31 | 15625 | keep | 0 | Jul | 2021 | 0.010642 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
UTUADO | 2021-07-31 12:05 | 2021-07-31 16:50 | 10 | 004:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO ABIERTO | A21073100037 | New_Event | Wire Down | Include | Include | Equipment | 285 | 2021-07-31 | 2850 | keep | 0 | Jul | 2021 | 0.0019411 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-07-31 12:11 | 2021-07-31 13:56 | 1 | 001:45 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR | R21073100044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2021-07-31 | 105 | keep | 0 | Jul | 2021 | 7.1515e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-07-31 12:17 | 2021-07-31 17:09 | 30 | 004:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21073100064 | New_Event | Bad Weather | Include | Include | Weather | 292 | 2021-07-31 | 8760 | keep | 0 | Jul | 2021 | 0.0059664 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-07-31 12:19 | 2021-07-31 12:20 | 2435 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21073100066 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-07-31 | 2435 | keep | 0 | Jul | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
CAGUAS | 2021-07-31 12:20 | 2021-07-31 18:45 | 40 | 006:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA AVERIADA | C21073100069 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 385 | 2021-07-31 | 15400 | keep | 0 | Jul | 2021 | 0.010489 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2021-07-31 12:21 | 2021-07-31 12:24 | 31 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE DORADO TC | B21073100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-07-31 | 93 | keep | 0 | Jul | 2021 | 6.3342e-05 | 2.1114e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 31
BAYAMON | 2021-07-31 12:21 | 2021-07-31 12:24 | 1859 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE DORADO TC | B21073100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-07-31 | 5577 | keep | 0 | Jul | 2021 | 0.0037985 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2021-07-31 12:21 | 2021-07-31 12:24 | 7 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE DORADO TC | B21073100000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-07-31 | 21 | keep | 0 | Jul | 2021 | 1.4303e-05 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2021-07-31 13:00 | 2021-07-31 16:10 | 250 | 003:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA CERRAR PUENTES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR AVERIA DE LINEA PRIMARIA ROTA | A21073100005 | New_Event | Wire Down | Include | Include | Equipment | 190 | 2021-07-31 | 47500 | keep | 0 | Jul | 2021 | 0.032352 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
UTUADO | 2021-07-31 13:01 | 2021-07-31 18:44 | 50 | 005:43 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21073100041 | New_Event | Bad Weather | Include | Include | Weather | 343 | 2021-07-31 | 17150 | keep | 0 | Jul | 2021 | 0.011681 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-31 13:19 | 2021-07-31 22:39 | 20 | 009:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21073100067 | New_Event | Secondary Wire Down | Include | Include | Equipment | 560 | 2021-07-31 | 11200 | keep | 0 | Jul | 2021 | 0.0076283 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2021-07-31 13:20 | 2021-07-31 16:20 | 50 | 003:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21073100044 | New_Event | Bad Weather | Include | Include | Weather | 180 | 2021-07-31 | 9000 | keep | 0 | Jul | 2021 | 0.0061299 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-07-31 13:21 | 2021-07-31 17:41 | 10 | 004:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR MOLES EN PEDESTAL | B21073100075 | New_Event | Secondary Wire Down | Include | Include | Equipment | 260 | 2021-07-31 | 2600 | keep | 0 | Jul | 2021 | 0.0017708 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-07-31 13:27 | 2021-07-31 13:28 | 3838 | 000:01 | T | DESGANCHE | RECIERRE | R21073100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-31 | 3838 | keep | 0 | Jul | 2021 | 0.002614 | 0.002614 | Momentary | FALSE | FALSE | Not_TMED_Event | 3838
CANOVANAS | 2021-07-31 13:28 | 2021-07-31 16:29 | 15 | 003:01 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | R21073100074 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 181 | 2021-07-31 | 2715 | keep | 0 | Jul | 2021 | 0.0018492 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
VEGA BAJA | 2021-07-31 13:32 | 2021-07-31 16:05 | 15 | 002:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21073100077 | New_Event | Secondary Wire Down | Include | Include | Equipment | 153 | 2021-07-31 | 2295 | keep | 0 | Jul | 2021 | 0.0015631 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2021-07-31 14:16 | 2021-07-31 15:12 | 543 | 000:56 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR Y SE REPARO ALAMBRE PARTIDO EN TRONCAL DEL ALIMENTADOR | M21073100068 | New_Event | Wire Down | Include | Include | Equipment | 56 | 2021-07-31 | 30408 | keep | 0 | Jul | 2021 | 0.020711 | 0.00036983 | Sustained | FALSE | FALSE | Not_TMED_Event | 543
SAN JUAN | 2021-07-31 14:27 | 2021-08-01 15:19 | 10 | 024:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21073100058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1492 | 2021-07-31 | 14920 | keep | 0 | Jul | 2021 | 0.010162 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-07-31 14:35 | 2021-07-31 17:44 | 80 | 003:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA | R21073100050 | New_Event | Cutout Failure | Include | Include | Equipment | 189 | 2021-07-31 | 15120 | keep | 0 | Jul | 2021 | 0.010298 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-07-31 14:40 | 2021-07-31 14:41 | 3597 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21073100081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-31 | 3597 | keep | 0 | Jul | 2021 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2021-07-31 14:41 | 2021-08-01 13:15 | 100 | 022:34 | P | PARARRAYOS DEFECTUOSO | 2 X 50 EN CORTE DE LINEA SE REMPLAZO PARARRAYO | B21073100111 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1354 | 2021-07-31 | 135400 | keep | 0 | Jul | 2021 | 0.09222 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-07-31 14:56 | 2021-08-01 14:30 | 1 | 023:34 | P | NO SE REPORTO CAUSA | 3 X 30 EN RISER | S21073100074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1414 | 2021-07-31 | 1414 | keep | 0 | Jul | 2021 | 0.00096307 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-07-31 15:10 | 2021-08-01 13:46 | 25 | 022:36 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21073100077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1356 | 2021-07-31 | 33900 | keep | 0 | Jul | 2021 | 0.023089 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
GUAYAMA | 2021-07-31 15:11 | 2021-07-31 16:24 | 80 | 001:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA LINEAS PRIMARIAS ARRIADAS | P21073100085 | New_Event | Wire Down | Include | Include | Equipment | 73 | 2021-07-31 | 5840 | keep | 0 | Jul | 2021 | 0.0039776 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-07-31 15:13 | 2021-07-31 16:55 | 100 | 001:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21073100053 | New_Event | Bad Weather | Include | Include | Weather | 102 | 2021-07-31 | 10200 | keep | 0 | Jul | 2021 | 0.0069472 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-07-31 15:21 | 2021-07-31 19:16 | 300 | 003:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PARTIDA Y SE CERRO CORTE DE LINEA | M21073000069 | New_Event | Wire Down | Include | Include | Equipment | 235 | 2021-07-31 | 70500 | keep | 0 | Jul | 2021 | 0.048017 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
CAGUAS | 2021-07-31 15:30 | 2021-07-31 18:12 | 8 | 002:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BARRA DE PEDESTAL | C21073000036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 162 | 2021-07-31 | 1296 | keep | 0 | Jul | 2021 | 0.0008827 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-07-31 15:42 | 2021-07-31 18:07 | 1 | 002:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONEXIONES EN RISER MONTURA DE A.A.A | M21073100003 | New_Event | Wire Down | Include | Include | Equipment | 145 | 2021-07-31 | 145 | keep | 0 | Jul | 2021 | 9.8759e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-07-31 15:52 | 2021-07-31 17:13 | 40 | 001:21 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21073100082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2021-07-31 | 3240 | keep | 0 | Jul | 2021 | 0.0022067 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-31 15:53 | 2021-07-31 16:23 | 380 | 000:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y SE NORMALIZO LAS CARGAS | B21073100005 | New_Event | Wire Down | Include | Include | Equipment | 30 | 2021-07-31 | 11400 | keep | 0 | Jul | 2021 | 0.0077645 | 0.00025882 | Sustained | FALSE | FALSE | Not_TMED_Event | 380
UTUADO | 2021-07-31 15:56 | 2021-07-31 18:09 | 654 | 002:13 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA SECCIONALIZAR LINEA PRIMARIA ROTA Y SE CERRO EL INTERRUPTOR | A21073100065 | New_Event | Wire Down | Include | Include | Equipment | 133 | 2021-07-31 | 86982 | keep | 0 | Jul | 2021 | 0.059243 | 0.00044544 | Sustained | FALSE | TRUE | Not_TMED_Event | 654
SAN JUAN | 2021-07-31 16:07 | 2021-07-31 17:48 | 10 | 001:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21073100024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 101 | 2021-07-31 | 1010 | keep | 0 | Jul | 2021 | 0.00068791 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-07-31 16:09 | 2021-07-31 16:29 | 1 | 000:20 | P | NO SE REPORTO CAUSA | 2 X 20 EN CORTE DE LINEA | R21073100076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2021-07-31 | 20 | keep | 0 | Jul | 2021 | 1.3622e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
AGUADILLA | 2021-07-31 16:20 | 2021-07-31 16:49 | 15 | 000:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | M21073100046 | New_Event | Secondary Wire Down | Include | Include | Equipment | 29 | 2021-07-31 | 435 | keep | 0 | Jul | 2021 | 0.00029628 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2021-07-31 16:24 | 2021-07-31 18:22 | 80 | 001:58 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21073100071 | New_Event | Bad Weather | Include | Include | Weather | 118 | 2021-07-31 | 9440 | keep | 0 | Jul | 2021 | 0.0064295 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
YAUCO | 2021-07-31 16:46 | 2021-07-31 21:43 | 30 | 004:57 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO | P21073100104 | Partial_restoration | Defective Pole | Include | Include | Equipment | 297 | 2021-07-31 | 8910 | keep | 0 | Jul | 2021 | 0.0060686 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2021-07-31 16:50 | 2021-08-01 12:01 | 15 | 019:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABREN CAJAS EN TRANSFORMADOR PARA REMPLAZAR LINEA SECUNDARIA | P21073100103 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1151 | 2021-07-31 | 17265 | keep | 0 | Jul | 2021 | 0.011759 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
VEGA BAJA | 2021-07-31 17:01 | 2021-07-31 18:51 | 60 | 001:50 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21073100096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 110 | 2021-07-31 | 6600 | keep | 0 | Jul | 2021 | 0.0044952 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-07-31 17:06 | 2021-07-31 17:07 | 3070 | 000:01 | T | DESGANCHE | RECERRO | B21073100082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-07-31 | 3070 | keep | 0 | Jul | 2021 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
SAN JUAN | 2021-07-31 17:07 | 2021-07-31 20:54 | 80 | 003:47 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA NECESITA REALIZARSE DESGANCHE MASIVO EN EL AREA | S21073100093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2021-07-31 | 18160 | keep | 0 | Jul | 2021 | 0.012369 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-07-31 17:07 | 2021-08-01 12:28 | 36 | 019:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21073100107 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1161 | 2021-07-31 | 41796 | keep | 0 | Jul | 2021 | 0.028467 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
ARECIBO | 2021-07-31 17:18 | 2021-07-31 20:32 | 10 | 003:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO ABIERTO | A21073100078 | New_Event | Wire Down | Include | Include | Equipment | 194 | 2021-07-31 | 1940 | keep | 0 | Jul | 2021 | 0.0013213 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-07-31 17:32 | 2021-08-01 11:57 | 20 | 018:25 | P | HERRAJE ROTO O PODRIDO | 1 X 40 EN CORTE DE LINEA REMPLAZO CRUCETA PARTIDA | C21073100084 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 1105 | 2021-07-31 | 22100 | keep | 0 | Jul | 2021 | 0.015052 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
UTUADO | 2021-07-31 18:09 | 2021-07-31 21:50 | 150 | 003:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA SE CERRO CORTE DE LINEA | A21073100085 | Partial_restoration | Wire Down | Include | Include | Equipment | 221 | 2021-07-31 | 33150 | keep | 0 | Jul | 2021 | 0.022578 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-07-31 18:43 | 2021-07-31 19:20 | 25 | 000:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES | M21073000102 | New_Event | Secondary Wire Down | Include | Include | Equipment | 37 | 2021-07-31 | 925 | keep | 0 | Jul | 2021 | 0.00063001 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2021-07-31 19:11 | 2021-07-31 21:23 | 90 | 002:12 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR | R21073100081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2021-07-31 | 11880 | keep | 0 | Jul | 2021 | 0.0080914 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
CANOVANAS | 2021-07-31 19:29 | 2021-07-31 19:30 | 7621 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | R21073100000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-07-31 | 7621 | keep | 0 | Jul | 2021 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
CANOVANAS | 2021-07-31 19:30 | 2021-07-31 23:53 | 5253 | 004:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO PUENTE ABIERTO Y MACHETE AVERIADO Y SE CERRO N/O CON EL 1646-03 EN AVE. MONSERRATE ESQ. FIDALGO DIAZ SU-1H | R21073100114 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 263 | 2021-07-31 | 1381539 | keep | 0 | Jul | 2021 | 0.94096 | 0.0035778 | Sustained | FALSE | FALSE | Not_TMED_Event | 5253
BAYAMON | 2021-07-31 19:33 | 2021-07-31 19:34 | 2234 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21073100108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-31 | 2234 | keep | 0 | Jul | 2021 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
MAYAGÃœEZ | 2021-07-31 19:37 | 2021-08-01 09:15 | 120 | 013:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA SE RETIRO GLOBO METALICO CRUZANDO LAS LINEAS | M21073100095 | New_Event |  |  | Include | Wildlife | 818 | 2021-07-31 | 98160 | keep | 0 | Jul | 2021 | 0.066856 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
ARECIBO | 2021-07-31 19:44 | 2021-08-01 10:03 | 15 | 014:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE A TRANSFORMADOR | A21073100089 | New_Event | Wire Down | Include | Include | Equipment | 859 | 2021-07-31 | 12885 | keep | 0 | Jul | 2021 | 0.0087759 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-07-31 19:46 | 2021-07-31 19:47 | 186 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21073100110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-07-31 | 186 | keep | 0 | Jul | 2021 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BARRANQUITAS | 2021-07-31 19:54 | 2021-08-01 13:51 | 20 | 017:57 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21073100087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1077 | 2021-07-31 | 21540 | keep | 0 | Jul | 2021 | 0.014671 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
AGUADILLA | 2021-07-31 19:59 | 2021-07-31 23:01 | 300 | 003:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21073100098 | New_Event | Bad Weather | Include | Include | Weather | 182 | 2021-07-31 | 54600 | keep | 0 | Jul | 2021 | 0.037188 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
ARECIBO | 2021-07-31 21:05 | 2021-08-01 09:49 | 5 | 012:44 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA | A21007310092 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 764 | 2021-07-31 | 3820 | keep | 0 | Jul | 2021 | 0.0026018 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-07-31 21:07 | 2021-08-01 09:49 | 3 | 012:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA PARTIDA | A21073100093 | New_Event | Secondary Wire Down | Include | Include | Equipment | 762 | 2021-07-31 | 2286 | keep | 0 | Jul | 2021 | 0.001557 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
CANOVANAS | 2021-07-31 21:23 | 2021-08-01 12:06 | 50 | 014:43 | P | HERRAJE ROTO O PODRIDO | 1 X 30 Y 1 X 20 EN CORTES DE LINEA REMPLAZO CRUCETA Y 4 DISCOS | R21073100122 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 883 | 2021-07-31 | 44150 | keep | 0 | Jul | 2021 | 0.03007 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-07-31 21:24 | 2021-08-01 09:59 | 8 | 012:35 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | C21073100089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 755 | 2021-07-31 | 6040 | keep | 0 | Jul | 2021 | 0.0041138 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-07-31 21:53 | 2021-08-01 09:57 | 60 | 012:04 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21073100126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 724 | 2021-07-31 | 43440 | keep | 0 | Jul | 2021 | 0.029587 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-07-31 22:39 | 2021-08-01 15:28 | 9 | 016:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN TRANSFORMADOR SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | M21073100118 | New_Event | Wire Down | Include | Include | Equipment | 1009 | 2021-07-31 | 9081 | keep | 0 | Jul | 2021 | 0.006185 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2021-07-31 22:59 | 2021-08-01 18:11 | 80 | 019:12 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | M21073100121 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1152 | 2021-07-31 | 92160 | keep | 0 | Jul | 2021 | 0.06277 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-07-31 23:02 | 2021-08-01 10:15 | 40 | 011:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21073100122 | New_Event | Bad Weather | Include | Include | Weather | 673 | 2021-07-31 | 26920 | keep | 0 | Jul | 2021 | 0.018335 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-07-31 23:06 | 2021-08-01 11:41 | 60 | 012:35 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTO DE LINEA | B21073100133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 755 | 2021-07-31 | 45300 | keep | 0 | Jul | 2021 | 0.030854 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CANOVANAS | 2021-07-31 23:53 | 2021-07-31 23:56 | 7621 | 000:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR PUENTE ABIERTO Y MACHETE AVERIADO | R21073100114 | Additional_clients | Wire Down | Include | Include | Equipment | 3 | 2021-07-31 | 22863 | keep | 0 | Jul | 2021 | 0.015572 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-08-01 00:42 | 2021-08-01 10:34 | 40 | 009:52 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21080100020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 592 | 2021-08-01 | 23680 | keep | 0 | Aug | 2021 | 0.016128 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-08-01 00:57 | 2021-08-01 09:42 | 10 | 008:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR REPARO SECUNDARIA | R21080100021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 525 | 2021-08-01 | 5250 | keep | 0 | Aug | 2021 | 0.0035758 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-01 01:28 | 2021-08-01 08:45 | 150 | 007:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21080100003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 437 | 2021-08-01 | 65550 | keep | 0 | Aug | 2021 | 0.044646 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-08-01 03:10 | 2021-08-01 19:19 | 70 | 016:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA REPAR LINEA PRIMARIA PARTIDA | A21080100004 | New_Event | Wire Down | Include | Include | Equipment | 969 | 2021-08-01 | 67830 | keep | 0 | Aug | 2021 | 0.046199 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
ARECIBO | 2021-08-01 03:23 | 2021-08-01 03:24 | 2791 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A21080100006 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-01 | 2791 | keep | 0 | Aug | 2021 | 0.0019009 | 0.0019009 | Momentary | FALSE | TRUE | Not_TMED_Event | 2791
ARECIBO | 2021-08-01 03:23 | 2021-08-01 03:24 | 1464 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A21080100006 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-01 | 1464 | keep | 0 | Aug | 2021 | 0.00099712 | 0.00099712 | Momentary | FALSE | TRUE | Not_TMED_Event | 1464
ARECIBO | 2021-08-01 03:23 | 2021-08-01 03:24 | 759 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A21080100006 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-01 | 759 | keep | 0 | Aug | 2021 | 0.00051695 | 0.00051695 | Momentary | FALSE | TRUE | Not_TMED_Event | 759
ARECIBO | 2021-08-01 03:23 | 2021-08-01 03:24 | 1500 | 000:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A21080100006 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-01 | 1500 | keep | 0 | Aug | 2021 | 0.0010216 | 0.0010216 | Momentary | FALSE | TRUE | Not_TMED_Event | 1500
BAYAMON | 2021-08-01 04:53 | 2021-08-01 04:54 | 1070 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21080100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-01 | 1070 | keep | 0 | Aug | 2021 | 0.00072877 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2021-08-01 05:48 | 2021-08-01 11:24 | 20 | 005:36 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE AVERIADO | B21080100000 | New_Event | Defective Pole | Include | Include | Equipment | 336 | 2021-08-01 | 6720 | keep | 0 | Aug | 2021 | 0.004577 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-08-01 06:00 | 2021-08-01 16:31 | 50 | 010:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA Y SE CERRO CORTE DE LINEA | A21080100000 | New_Event | Cutout Failure | Include | Include | Equipment | 631 | 2021-08-01 | 31550 | keep | 0 | Aug | 2021 | 0.021489 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-08-01 07:00 | 2021-08-01 07:01 | 752 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21080100002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-01 | 752 | keep | 0 | Aug | 2021 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
PONCE | 2021-08-01 07:00 | 2021-08-01 07:01 | 2696 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR 5011-04 | P21080100002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-01 | 2696 | keep | 0 | Aug | 2021 | 0.0018362 | 0.0018362 | Momentary | FALSE | FALSE | Not_TMED_Event | 2696
MAYAGÃœEZ | 2021-08-01 07:03 | 2021-08-01 07:04 | 1417 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR RECIERRE EN OFF NO SE REPORTO CAUSA | M21080100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-01 | 1417 | keep | 0 | Aug | 2021 | 0.00096511 | 0.00096511 | Momentary | FALSE | FALSE | Not_TMED_Event | 1417
FAJARDO | 2021-08-01 07:07 | 2021-08-01 09:39 | 65 | 002:32 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21080100023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2021-08-01 | 9880 | keep | 0 | Aug | 2021 | 0.0067292 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
CANOVANAS | 2021-08-01 07:24 | 2021-08-01 12:23 | 50 | 004:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R21080100026 | New_Event |  |  | Include | Wildlife | 299 | 2021-08-01 | 14950 | keep | 0 | Aug | 2021 | 0.010182 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-08-01 07:44 | 2021-08-01 07:45 | 1026 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21080100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-01 | 1026 | keep | 0 | Aug | 2021 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
SAN JUAN | 2021-08-01 07:59 | 2021-08-01 11:53 | 50 | 003:54 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21080100003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 234 | 2021-08-01 | 11700 | keep | 0 | Aug | 2021 | 0.0079688 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-01 08:17 | 2021-08-01 08:18 | 1533 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 1709-05 | S21080100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-01 | 1533 | keep | 0 | Aug | 2021 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
BAYAMON | 2021-08-01 08:17 | 2021-08-01 08:18 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1709-03 | S21080100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-01 | 2364 | keep | 0 | Aug | 2021 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
CANOVANAS | 2021-08-01 08:18 | 2021-08-01 16:29 | 45 | 008:11 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR | R21080100043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 491 | 2021-08-01 | 22095 | keep | 0 | Aug | 2021 | 0.015049 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
SAN JUAN | 2021-08-01 08:30 | 2021-08-01 14:58 | 2 | 006:28 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO MACHETE PARA SECCIONALIZAR TRAMO Y REEMPLAZAR MACHETES QUEMADOS | R21080100034 | New_Event | Switch Failure | Include | Include | Equipment | 388 | 2021-08-01 | 776 | keep | 0 | Aug | 2021 | 0.00052853 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2021-08-01 08:54 | 2021-08-01 12:05 | 7 | 003:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21080100002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 191 | 2021-08-01 | 1337 | keep | 0 | Aug | 2021 | 0.00091062 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-08-01 09:04 | 2021-08-01 10:11 | 10 | 001:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21073100071 | New_Event | Secondary Wire Down | Include | Include | Equipment | 67 | 2021-08-01 | 670 | keep | 0 | Aug | 2021 | 0.00045633 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-01 09:07 | 2021-08-01 13:54 | 15 | 004:47 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERAS | A21080100011 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 287 | 2021-08-01 | 4305 | keep | 0 | Aug | 2021 | 0.0029321 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-08-01 09:14 | 2021-08-01 10:46 | 36 | 001:32 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21080100015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 92 | 2021-08-01 | 3312 | keep | 0 | Aug | 2021 | 0.0022558 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
PONCE | 2021-08-01 09:24 | 2021-08-01 13:36 | 20 | 004:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA | P21080100103 | New_Event | Cutout Failure | Include | Include | Equipment | 252 | 2021-08-01 | 5040 | keep | 0 | Aug | 2021 | 0.0034327 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-08-01 09:36 | 2021-08-01 09:37 | 4085 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21080100037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-01 | 4085 | keep | 0 | Aug | 2021 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
ARECIBO | 2021-08-01 09:51 | 2021-08-01 10:46 | 60 | 000:55 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21080100014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2021-08-01 | 3300 | keep | 0 | Aug | 2021 | 0.0022476 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-08-01 09:55 | 2021-08-01 12:30 | 300 | 002:35 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21080100013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2021-08-01 | 46500 | keep | 0 | Aug | 2021 | 0.031671 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
CANOVANAS | 2021-08-01 10:13 | 2021-08-01 11:11 | 40 | 000:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA | R21080100038 | New_Event | Wire Down | Include | Include | Equipment | 58 | 2021-08-01 | 2320 | keep | 0 | Aug | 2021 | 0.0015801 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-08-01 10:16 | 2021-08-01 13:50 | 25 | 003:34 | P | SECUNDARIA/DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO ENREDADERAS | A21080100016 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 214 | 2021-08-01 | 5350 | keep | 0 | Aug | 2021 | 0.0036439 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-08-01 10:16 | 2021-08-01 14:34 | 100 | 004:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA POR AVE | A21080100016 | New_Event |  |  | Include | Wildlife | 258 | 2021-08-01 | 25800 | keep | 0 | Aug | 2021 | 0.017572 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-08-01 10:20 | 2021-08-01 14:11 | 15 | 003:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA | A21080100018 | New_Event | Bad Weather | Include | Include | Weather | 231 | 2021-08-01 | 3465 | keep | 0 | Aug | 2021 | 0.00236 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-08-01 10:37 | 2021-08-01 12:40 | 7 | 002:03 | P | SECUNDARIA/DESGANCHE | 2 X 25 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | M21080100018 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 123 | 2021-08-01 | 861 | keep | 0 | Aug | 2021 | 0.00058642 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
VEGA BAJA | 2021-08-01 11:29 | 2021-08-01 11:30 | 4702 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21080100019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-01 | 4702 | keep | 0 | Aug | 2021 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
CAGUAS | 2021-08-01 11:35 | 2021-08-01 15:15 | 50 | 003:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN RISER REMPLAZO CAJA QUEMADA | C21080100012 | New_Event | Cutout Failure | Include | Include | Equipment | 220 | 2021-08-01 | 11000 | keep | 0 | Aug | 2021 | 0.007492 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-08-01 11:36 | 2021-08-01 16:37 | 1 | 005:01 | P | NO SE REPORTO CAUSA | 3 X 80 EN SU-212 | B21080100021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 301 | 2021-08-01 | 301 | keep | 0 | Aug | 2021 | 0.00020501 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-08-01 11:44 | 2021-08-01 18:30 | 60 | 006:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA | A21080100021 | New_Event | Wire Down | Include | Include | Equipment | 406 | 2021-08-01 | 24360 | keep | 0 | Aug | 2021 | 0.016591 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-08-01 11:49 | 2021-08-01 13:58 | 12 | 002:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21080100022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 129 | 2021-08-01 | 1548 | keep | 0 | Aug | 2021 | 0.0010543 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-08-01 12:24 | 2021-08-01 14:39 | 1 | 002:15 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21080100026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 135 | 2021-08-01 | 135 | keep | 0 | Aug | 2021 | 9.1948e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-08-01 12:24 | 2021-08-01 15:20 | 1 | 002:56 | P | NO SE REPORTO CAUSA | 1 X 10 EN CORTE DE LINEA | C21080100014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 176 | 2021-08-01 | 176 | keep | 0 | Aug | 2021 | 0.00011987 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-08-01 12:37 | 2021-08-01 21:28 | 55 | 008:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21080100032 | New_Event | Bad Weather | Include | Include | Weather | 531 | 2021-08-01 | 29205 | keep | 0 | Aug | 2021 | 0.019891 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
BAYAMON | 2021-08-01 12:54 | 2021-08-01 19:26 | 15 | 006:32 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B21080100029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 392 | 2021-08-01 | 5880 | keep | 0 | Aug | 2021 | 0.0040048 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-08-01 13:07 | 2021-08-01 16:23 | 101 | 003:16 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | P21080100009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2021-08-01 | 19796 | keep | 0 | Aug | 2021 | 0.013483 | 6.8791e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 101
SAN JUAN | 2021-08-01 13:25 | 2021-08-01 16:44 | 10 | 003:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21080100012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 199 | 2021-08-01 | 1990 | keep | 0 | Aug | 2021 | 0.0013554 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-08-01 13:29 | 2021-08-01 16:47 | 30 | 003:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA REPARO BAJANTE DE LINEA A CAJA | C21080100018 | New_Event | Wire Down | Include | Include | Equipment | 198 | 2021-08-01 | 5940 | keep | 0 | Aug | 2021 | 0.0040457 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
AGUADILLA | 2021-08-01 13:35 | 2021-08-01 21:29 | 200 | 007:54 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21080100039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 474 | 2021-08-01 | 94800 | keep | 0 | Aug | 2021 | 0.064568 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
GUAYAMA | 2021-08-01 13:40 | 2021-08-01 14:45 | 38 | 001:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA LEVANTAR LINEA PRIMARIA DEL SUELO | P21080100005 | New_Event | Wire Down | Include | Include | Equipment | 65 | 2021-08-01 | 2470 | keep | 0 | Aug | 2021 | 0.0016823 | 2.5882e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 38
UTUADO | 2021-08-01 13:44 | 2021-08-01 16:32 | 40 | 002:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | A21080100026 | New_Event | Bad Weather | Include | Include | Weather | 168 | 2021-08-01 | 6720 | keep | 0 | Aug | 2021 | 0.004577 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-01 13:46 | 2021-08-01 18:48 | 300 | 005:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO ABIERTO | M21080100044 | New_Event | Wire Down | Include | Include | Equipment | 302 | 2021-08-01 | 90600 | keep | 0 | Aug | 2021 | 0.061707 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-08-01 13:59 | 2021-08-01 19:45 | 5 | 005:46 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR CAUSA DESGANCHE | M21080100050 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 346 | 2021-08-01 | 1730 | keep | 0 | Aug | 2021 | 0.0011783 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-08-01 14:14 | 2021-08-01 17:07 | 60 | 002:53 | P | DESGANCHE | 1 X 60 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21080100015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2021-08-01 | 10380 | keep | 0 | Aug | 2021 | 0.0070698 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
PONCE | 2021-08-01 14:20 | 2021-08-01 14:21 | 2696 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21070200706 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-01 | 2696 | keep | 0 | Aug | 2021 | 0.0018362 | 0.0018362 | Momentary | FALSE | FALSE | Not_TMED_Event | 2696
CANOVANAS | 2021-08-01 14:42 | 2021-08-01 17:37 | 50 | 002:55 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21080100045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2021-08-01 | 8750 | keep | 0 | Aug | 2021 | 0.0059596 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-01 14:45 | 2021-08-01 15:23 | 600 | 000:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR PUENTE PRIMARIO ABIERTO | M21080100013 | New_Event | Wire Down | Include | Include | Equipment | 38 | 2021-08-01 | 22800 | keep | 0 | Aug | 2021 | 0.015529 | 0.00040866 | Sustained | FALSE | TRUE | Not_TMED_Event | 600
AGUADILLA | 2021-08-01 14:54 | 2021-08-01 20:17 | 60 | 005:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE SEPARO LINEAS CRUZADAS | M21080100054 | New_Event | Wire Down | Include | Include | Equipment | 323 | 2021-08-01 | 19380 | keep | 0 | Aug | 2021 | 0.0132 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-08-01 15:00 | 2021-08-01 21:15 | 300 | 006:15 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR POSTE PRIMARIO PARTIDO EN EL FID:1000131579 POSTE DE METAL DE 45' | M21080100057 | New_Event | Defective Pole | Include | Include | Equipment | 375 | 2021-08-01 | 112500 | keep | 0 | Aug | 2021 | 0.076623 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
ARECIBO | 2021-08-01 15:04 | 2021-08-01 16:59 | 100 | 001:55 | P | DESGANCHE | 1 X 65 ENCORTE DE LINEA | A21080100029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2021-08-01 | 11500 | keep | 0 | Aug | 2021 | 0.0078326 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-08-01 15:55 | 2021-08-01 18:19 | 50 | 002:24 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S21080100018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2021-08-01 | 7200 | keep | 0 | Aug | 2021 | 0.0049039 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-01 15:58 | 2021-08-01 18:19 | 200 | 002:21 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA REQUIERE DESGANCHE | M21080100063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2021-08-01 | 28200 | keep | 0 | Aug | 2021 | 0.019207 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BARRANQUITAS | 2021-08-01 16:10 | 2021-08-01 18:18 | 30 | 002:08 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | C21080100030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 128 | 2021-08-01 | 3840 | keep | 0 | Aug | 2021 | 0.0026154 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-08-01 16:20 | 2021-08-01 19:14 | 10 | 002:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21080100010 | New_Event | Secondary Wire Down | Include | Include | Equipment | 174 | 2021-08-01 | 1740 | keep | 0 | Aug | 2021 | 0.0011851 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-08-01 16:33 | 2021-08-01 17:14 | 10 | 000:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTE SECUNDARIO | C21080100032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 41 | 2021-08-01 | 410 | keep | 0 | Aug | 2021 | 0.00027925 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-08-01 16:39 | 2021-08-02 09:38 | 6 | 016:59 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR | C21080100031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1019 | 2021-08-01 | 6114 | keep | 0 | Aug | 2021 | 0.0041642 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2021-08-01 16:44 | 2021-08-01 19:24 | 25 | 002:40 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | C21080100033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2021-08-01 | 4000 | keep | 0 | Aug | 2021 | 0.0027244 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CANOVANAS | 2021-08-01 16:50 | 2021-08-01 16:51 | 2708 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21080100048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-01 | 2708 | keep | 0 | Aug | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
PONCE | 2021-08-01 16:56 | 2021-08-01 16:57 | 4035 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P210801000XX | New_Event |  |  | Include | Wildlife | 1 | 2021-08-01 | 4035 | keep | 0 | Aug | 2021 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
PONCE | 2021-08-01 16:57 | 2021-08-01 19:44 | 80 | 002:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA, AVE CRUZO FASE. | P21080100017 | 1st_after_momentary |  |  | Include | Wildlife | 167 | 2021-08-01 | 13360 | keep | 0 | Aug | 2021 | 0.0090994 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-01 17:03 | 2021-08-01 19:25 | 75 | 002:22 | P | OTRAS CAUSAS | SE ABRIO DEL SU-2 @ RISER PARA BALANCEAR LAS CARGAS | B21080100033 | New_Event | Other Causes | Include | Include | Other | 142 | 2021-08-01 | 10650 | keep | 0 | Aug | 2021 | 0.0072537 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
PONCE | 2021-08-01 17:41 | 2021-08-01 21:10 | 11 | 003:29 | P | TRANSFORMADOR AVERIADO | SE REPARO BUSHING PRIMARIO EN TRANSFORMADOR | P21080100018 | New_Event | Service Transformer Failure | Include | Include | Equipment | 209 | 2021-08-01 | 2299 | keep | 0 | Aug | 2021 | 0.0015658 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
ARECIBO | 2021-08-01 17:53 | 2021-08-01 18:31 | 50 | 000:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE EN CORTE DE LINEA | A21080100033 | New_Event | Wire Down | Include | Include | Equipment | 38 | 2021-08-01 | 1900 | keep | 0 | Aug | 2021 | 0.0012941 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-01 18:01 | 2021-08-01 18:28 | 5 | 000:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REPARO BAJANTE Y SE REEMPLAZO CAJA EN TRANSFORMADOR | A21080100036 | New_Event | Cutout Failure | Include | Include | Equipment | 27 | 2021-08-01 | 135 | keep | 0 | Aug | 2021 | 9.1948e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2021-08-01 18:14 | 2021-08-02 09:11 | 60 | 014:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA CRUCE CON NEUTRAL | R21080100050 | New_Event | Wire Down | Include | Include | Equipment | 897 | 2021-08-01 | 53820 | keep | 0 | Aug | 2021 | 0.036657 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-08-01 18:35 | 2021-08-02 19:33 | 15 | 024:58 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR DE 75KVA X 75KVA | R21080100036 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1498 | 2021-08-01 | 22470 | keep | 0 | Aug | 2021 | 0.015304 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-08-01 19:07 | 2021-08-02 22:19 | 20 | 027:12 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 25 KVA X 25 KVA | M21080100076 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1632 | 2021-08-01 | 32640 | keep | 0 | Aug | 2021 | 0.022231 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-08-01 19:15 | 2021-08-01 20:19 | 100 | 001:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M21080100078 | New_Event |  |  | Include | Wildlife | 64 | 2021-08-01 | 6400 | keep | 0 | Aug | 2021 | 0.004359 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-08-01 19:18 | 2021-08-02 11:48 | 12 | 016:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA PARTIDA Y SE REALIZO DESGANCHE | A21080100039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 990 | 2021-08-01 | 11880 | keep | 0 | Aug | 2021 | 0.0080914 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-08-01 19:26 | 2021-08-02 12:19 | 20 | 016:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | M21080100079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1013 | 2021-08-01 | 20260 | keep | 0 | Aug | 2021 | 0.013799 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-08-01 19:27 | 2021-08-02 14:29 | 35 | 019:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | B21080100046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1142 | 2021-08-01 | 39970 | keep | 0 | Aug | 2021 | 0.027223 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
PONCE | 2021-08-01 19:30 | 2021-08-01 21:26 | 11 | 001:56 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 50KVA A 4.16KV POR UNO DE IGUAL CAPACIDAD | P21080100021 | New_Event | Service Transformer Failure | Include | Include | Equipment | 116 | 2021-08-01 | 1276 | keep | 0 | Aug | 2021 | 0.00086908 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CANOVANAS | 2021-08-01 19:42 | 2021-08-01 21:03 | 5 | 001:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN RISER REEMPLAZO PORTAFUSIBLE | R21080100055 | New_Event | Cutout Failure | Include | Include | Equipment | 81 | 2021-08-01 | 405 | keep | 0 | Aug | 2021 | 0.00027584 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-08-01 19:54 | 2021-08-01 20:53 | 75 | 000:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN RISER Y SE REMPLAZO CAJA PRIMARIA QUEMADA | B21080100033 | New_Event | Cutout Failure | Include | Include | Equipment | 59 | 2021-08-01 | 4425 | keep | 0 | Aug | 2021 | 0.0030138 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2021-08-01 20:00 | 2021-08-02 09:00 | 10 | 013:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA AVE CRUZO LINEAS | A21080200776 | New_Event |  |  | Include | Wildlife | 780 | 2021-08-01 | 7800 | keep | 0 | Aug | 2021 | 0.0053125 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
SAN JUAN | 2021-08-01 20:05 | 2021-08-01 21:45 | 110 | 001:40 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | R21080100056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 100 | 2021-08-01 | 11000 | keep | 0 | Aug | 2021 | 0.007492 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
AGUADILLA | 2021-08-01 20:21 | 2021-08-02 18:20 | 50 | 021:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M21080100085 | New_Event | Wire Down | Include | Include | Equipment | 1319 | 2021-08-01 | 65950 | keep | 0 | Aug | 2021 | 0.044918 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-08-01 20:49 | 2021-08-02 19:00 | 50 | 022:11 | P | DESCONECTIVO DEFECTUOSO | SE REPARARON CONEXIONES EN MACHETES SOLIDOS | A21080100042 | New_Event | Switch Failure | Include | Include | Equipment | 1331 | 2021-08-01 | 66550 | keep | 0 | Aug | 2021 | 0.045327 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-08-01 20:58 | 2021-08-01 23:33 | 100 | 002:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO PROTAFUSIBLE AVERIADO | A21080100046 | New_Event | Cutout Failure | Include | Include | Equipment | 155 | 2021-08-01 | 15500 | keep | 0 | Aug | 2021 | 0.010557 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-08-01 21:15 | 2021-08-02 10:54 | 3 | 013:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA SULFATADA | C21080100039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 819 | 2021-08-01 | 2457 | keep | 0 | Aug | 2021 | 0.0016735 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
AGUADILLA | 2021-08-01 21:50 | 2021-08-02 16:35 | 60 | 018:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | M21080100087 | New_Event | Wire Down | Include | Include | Equipment | 1125 | 2021-08-01 | 67500 | keep | 0 | Aug | 2021 | 0.045974 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-08-01 21:51 | 2021-08-03 18:20 | 1 | 044:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO | A21080100049 | New_Event | Bad Weather | Include | Include | Weather | 2669 | 2021-08-01 | 2669 | keep | 0 | Aug | 2021 | 0.0018178 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2021-08-01 21:59 | 2021-08-02 12:17 | 50 | 014:18 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA SE PATRULLO | C21080100054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 858 | 2021-08-01 | 42900 | keep | 0 | Aug | 2021 | 0.029219 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-08-01 22:14 | 2021-08-12 11:55 | 45 | 253:41 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21081100121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15221 | 2021-08-01 | 684945 | keep | 0 | Aug | 2021 | 0.46651 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
AGUADILLA | 2021-08-01 22:19 | 2021-08-02 19:20 | 15 | 021:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTES SECUNDARIOS EN TRANSFORMADOR | M21080100088 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1261 | 2021-08-01 | 18915 | keep | 0 | Aug | 2021 | 0.012883 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-08-01 22:40 | 2021-08-02 13:10 | 10 | 014:30 | P | PROTECCION DEFECTUOSA | SE ABRIO TRANSFORMADOR Y SE CERRO BAJANTE SECUNDARIO Y NEUTRAL | B21080100049 | New_Event | Protection Miscoordination | Include | Include | Other | 870 | 2021-08-01 | 8700 | keep | 0 | Aug | 2021 | 0.0059255 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-02 00:26 | 2021-08-02 17:45 | 10 | 017:19 | P | HERRAJE ROTO O PODRIDO | SE REPARO TORNILLO PARTIDO DE LA CRUCETA DEL TRANSFORMADOR | A21080200001 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 1039 | 2021-08-02 | 10390 | keep | 0 | Aug | 2021 | 0.0070766 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-08-02 00:34 | 2021-08-02 00:37 | 824 | 000:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA CARGA 95% POR EL 1119-04 | S21080200000 | New_Event | Cutout Failure | Include | Include | Equipment | 3 | 2021-08-02 | 2472 | keep | 0 | Aug | 2021 | 0.0016837 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
BAYAMON | 2021-08-02 00:34 | 2021-08-02 00:37 | 2720 | 000:03 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA LLEVA 95% 1115-05 | S21080200000 | New_Event | Cutout Failure | Include | Include | Equipment | 3 | 2021-08-02 | 8160 | keep | 0 | Aug | 2021 | 0.0055577 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
BAYAMON | 2021-08-02 00:37 | 2021-08-02 13:44 | 55 | 013:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON TRES CAJAS PRIMARIAS | S21080200001 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 787 | 2021-08-02 | 43285 | keep | 0 | Aug | 2021 | 0.029481 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CAGUAS | 2021-08-02 00:51 | 2021-08-02 09:48 | 300 | 008:57 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21080200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 537 | 2021-08-02 | 161100 | keep | 0 | Aug | 2021 | 0.10972 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
SAN JUAN | 2021-08-02 03:11 | 2021-08-02 05:23 | 892 | 002:12 | T | NO SE REPORTO CAUSA | SE PATRULLO NO SE ENCONTRO CONDICION Y SE CERRO POR SCADA | S21080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 132 | 2021-08-02 | 117744 | keep | 0 | Aug | 2021 | 0.080195 | 0.00060754 | Sustained | FALSE | FALSE | Not_TMED_Event | 892
MAYAGÃœEZ | 2021-08-02 03:47 | 2021-08-02 17:30 | 300 | 013:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON CAJAS EN CONVERTIDOR | M21080200002 | New_Event | Cutout Failure | Include | Include | Equipment | 823 | 2021-08-02 | 246900 | keep | 0 | Aug | 2021 | 0.16816 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2021-08-02 04:26 | 2021-08-02 04:27 | 418 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21080200000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-02 | 418 | keep | 0 | Aug | 2021 | 0.0002847 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
BAYAMON | 2021-08-02 04:27 | 2021-08-02 07:48 | 20 | 003:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE SAFADO | S21080200000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 201 | 2021-08-02 | 4020 | keep | 0 | Aug | 2021 | 0.002738 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-08-02 05:53 | 2021-08-02 09:41 | 31 | 003:48 | T | PROTECCION DEFECTUOSA | SE TRANSFIRIO LA CARGA AL 9206-11 POR RELE AVERIADO | B21080200003 | New_Event | Protection Miscoordination | Include | Include | Other | 228 | 2021-08-02 | 7068 | keep | 0 | Aug | 2021 | 0.004814 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
VEGA BAJA | 2021-08-02 05:53 | 2021-08-02 09:52 | 1859 | 003:59 | T | PROTECCION DEFECTUOSA | SE TRANSFIRIO LA CARGA AL 1718-04 Y LLEVA LA CARGA DEL BREAKER 9207-09 | B21080200003 | New_Event | Protection Miscoordination | Include | Include | Other | 239 | 2021-08-02 | 444301 | keep | 0 | Aug | 2021 | 0.30261 | 0.0012662 | Sustained | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2021-08-02 05:53 | 2021-08-02 09:52 | 7 | 003:59 | T | PROTECCION DEFECTUOSA | SE TRANSFIRIO LA CARGA AL 1718-04 Y LLEVA LA CARGA POR BREAKER 9207-08 | B21080200003 | New_Event | Protection Miscoordination | Include | Include | Other | 239 | 2021-08-02 | 1673 | keep | 0 | Aug | 2021 | 0.0011395 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-08-02 05:55 | 2021-08-02 14:10 | 20 | 008:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | CAJA PRIMARIA QUEMADA SE COLOCO PUENTE PRIMARIO EN EL POSTE EXISTE UN PANAL DE AVEJAS Y NO SE PUEDE CAMBIAR LA CAJA PRIMARIA POR AHORA | A21080200003 | New_Event | Cutout Failure | Include | Include | Equipment | 495 | 2021-08-02 | 9900 | keep | 0 | Aug | 2021 | 0.0067428 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2021-08-02 06:06 | 2021-08-02 11:45 | 80 | 005:39 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21080200005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 339 | 2021-08-02 | 27120 | keep | 0 | Aug | 2021 | 0.018471 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-08-02 06:09 | 2021-08-02 09:58 | 76 | 003:49 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21080200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2021-08-02 | 17404 | keep | 0 | Aug | 2021 | 0.011854 | 5.1763e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 76
YAUCO | 2021-08-02 06:49 | 2021-08-02 06:50 | 1475 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTOR | P21080200002 | New_Event |  |  | Include | Wildlife | 1 | 2021-08-02 | 1475 | keep | 0 | Aug | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
MAYAGÃœEZ | 2021-08-02 06:49 | 2021-08-02 06:50 | 4641 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M21080200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-02 | 4641 | keep | 0 | Aug | 2021 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
YAUCO | 2021-08-02 06:50 | 2021-08-02 10:39 | 50 | 003:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZA FASE PRIMARIA | P21080200003 | 1st_after_momentary |  |  | Include | Wildlife | 229 | 2021-08-02 | 11450 | keep | 0 | Aug | 2021 | 0.0077985 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-02 06:50 | 2021-08-02 11:30 | 50 | 004:40 | P | DESGANCHE | 1 X 50 EN CORTE DE LINE SE RETIRO RAMA | M21080200742 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 280 | 2021-08-02 | 14000 | keep | 0 | Aug | 2021 | 0.0095353 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-08-02 06:53 | 2021-08-02 19:40 | 65 | 012:47 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN CORTE DE LINEA CONSTRUYO PROVISIONAL DE AEREO EXISTENTE @ T-7 | C21080200003 | New_Event | UG Cable Fault | Include | Include | Equipment | 767 | 2021-08-02 | 49855 | keep | 0 | Aug | 2021 | 0.033956 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BAYAMON | 2021-08-02 07:48 | 2021-08-02 07:49 | 418 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21080200000 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2021-08-02 | 418 | keep | 0 | Aug | 2021 | 0.0002847 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-02 07:49 | 2021-08-02 12:34 | 20 | 004:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE SAFADO | S21080200000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 285 | 2021-08-02 | 5700 | keep | 0 | Aug | 2021 | 0.0038822 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2021-08-02 07:58 | 2021-08-02 12:21 | 100 | 004:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 Y 1 X 10 EN CORTE DE LINEA Y TRANSFORMADOR SE LEVANTO CONDUCTOR DEL SUELO | C21080200007 | New_Event | Wire Down | Include | Include | Equipment | 263 | 2021-08-02 | 26300 | keep | 0 | Aug | 2021 | 0.017913 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-08-02 08:10 | 2021-08-03 13:15 | 18 | 029:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN CORTE DE LINEA | A21080200027 | New_Event | Cutout Failure | Include | Include | Equipment | 1745 | 2021-08-02 | 31410 | keep | 0 | Aug | 2021 | 0.021393 | 1.226e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 18
ARECIBO | 2021-08-02 08:26 | 2021-08-02 14:15 | 80 | 005:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | A21080200478 | New_Event | Bad Weather | Include | Include | Weather | 349 | 2021-08-02 | 27920 | keep | 0 | Aug | 2021 | 0.019016 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-08-02 08:27 | 2021-08-02 11:50 | 5 | 003:23 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE RETIRO ENREDADERA | M21080200695 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 203 | 2021-08-02 | 1015 | keep | 0 | Aug | 2021 | 0.00069131 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2021-08-02 08:31 | 2021-08-02 20:10 | 64 | 011:39 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA POR DESGANCHE | P21080200533 | New_Event | Vegetation Contact | Include | Include | Vegetation | 699 | 2021-08-02 | 44736 | keep | 0 | Aug | 2021 | 0.030469 | 4.359e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 64
UTUADO | 2021-08-02 08:36 | 2021-08-02 15:49 | 15 | 007:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA POR MAL TIEMPO | A21080200710 | New_Event | Bad Weather | Include | Include | Weather | 433 | 2021-08-02 | 6495 | keep | 0 | Aug | 2021 | 0.0044237 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
ARECIBO | 2021-08-02 08:51 | 2021-08-02 15:10 | 20 | 006:19 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA POR DESGANCHE | A21080200775 | New_Event | Vegetation Contact | Include | Include | Vegetation | 379 | 2021-08-02 | 7580 | keep | 0 | Aug | 2021 | 0.0051627 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
FAJARDO | 2021-08-02 08:59 | 2021-08-02 10:27 | 4 | 001:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE DESCRUZO SECUNDARIA | R21070200444 | New_Event | Secondary Wire Down | Include | Include | Equipment | 88 | 2021-08-02 | 352 | keep | 0 | Aug | 2021 | 0.00023975 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-08-02 09:06 | 2021-08-03 15:59 | 12 | 030:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | B21080200106 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1853 | 2021-08-02 | 22236 | keep | 0 | Aug | 2021 | 0.015145 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-08-02 09:21 | 2021-08-04 19:00 | 35 | 057:39 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA DESGANCHE | M21080201180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3459 | 2021-08-02 | 121065 | keep | 0 | Aug | 2021 | 0.082457 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-08-02 09:52 | 2021-08-04 15:56 | 12 | 054:04 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA POR 50 KVA | B21080201178 | New_Event | Service Transformer Failure | Include | Include | Equipment | 3244 | 2021-08-02 | 38928 | keep | 0 | Aug | 2021 | 0.026514 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2021-08-02 10:00 | 2021-08-02 10:40 | 450 | 000:40 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE RETIRO RAMA | M21080201198 | New_Event | Vegetation Contact | Include | Include | Vegetation | 40 | 2021-08-02 | 18000 | keep | 0 | Aug | 2021 | 0.01226 | 0.00030649 | Sustained | FALSE | TRUE | Not_TMED_Event | 450
MAYAGÃœEZ | 2021-08-02 10:07 | 2021-08-02 17:30 | 12 | 007:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA | M21080201195 | New_Event | Secondary Wire Down | Include | Include | Equipment | 443 | 2021-08-02 | 5316 | keep | 0 | Aug | 2021 | 0.0036207 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-08-02 10:08 | 2021-08-02 14:12 | 100 | 004:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA REPARO CONDUCTOR ROTO | C21080200965 | New_Event | Wire Down | Include | Include | Equipment | 244 | 2021-08-02 | 24400 | keep | 0 | Aug | 2021 | 0.016619 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-08-02 10:10 | 2021-08-02 16:54 | 35 | 006:44 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | C21080200966 | New_Event | Vegetation Contact | Include | Include | Vegetation | 404 | 2021-08-02 | 14140 | keep | 0 | Aug | 2021 | 0.0096307 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-08-02 10:22 | 2021-08-02 10:23 | 34 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA LLEVANDO 1512-05 Y 1910-02 | S21080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 34 | keep | 0 | Aug | 2021 | 2.3157e-05 | 2.3157e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 34
BAYAMON | 2021-08-02 10:22 | 2021-08-02 10:23 | 19 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA CARGA POR EL 1512-04 | S21080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 19 | keep | 0 | Aug | 2021 | 1.2941e-05 | 1.2941e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 19
CAGUAS | 2021-08-02 10:38 | 2021-08-02 16:55 | 95 | 006:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 Y 1 X 50 EN CORTE DE LINEA REPARO CONDUCTOR ROTO Y DESGANCHO | C21080200967 | New_Event | Wire Down | Include | Include | Equipment | 377 | 2021-08-02 | 35815 | keep | 0 | Aug | 2021 | 0.024393 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
SAN JUAN | 2021-08-02 10:59 | 2021-08-03 14:07 | 40 | 027:08 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21080200999 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1628 | 2021-08-02 | 65120 | keep | 0 | Aug | 2021 | 0.044353 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-08-02 10:59 | 2021-08-02 11:37 | 1 | 000:38 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S21080200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 38 | 2021-08-02 | 38 | keep | 0 | Aug | 2021 | 2.5882e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-08-02 11:01 | 2021-08-02 18:00 | 120 | 006:59 | P | DESCONECTIVO DEFECTUOSO | SE MOVIO N/O PARA TRANSFERIR PARTE DE LA CARGA AL 6008-04 POR MACHETES QUERMADOS SE DEJO ASI EL N/O | M21080201201 | New_Event | Switch Failure | Include | Include | Equipment | 419 | 2021-08-02 | 50280 | keep | 0 | Aug | 2021 | 0.034245 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
GUAYAMA | 2021-08-02 11:03 | 2021-08-02 14:23 | 15 | 003:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA DE TRANSFORMADOR | P21070200690 | New_Event | Cutout Failure | Include | Include | Equipment | 200 | 2021-08-02 | 3000 | keep | 0 | Aug | 2021 | 0.0020433 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-08-02 11:08 | 2021-08-02 12:30 | 10 | 001:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21080201086 | New_Event | Secondary Wire Down | Include | Include | Equipment | 82 | 2021-08-02 | 820 | keep | 0 | Aug | 2021 | 0.0005585 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-08-02 11:12 | 2021-08-02 16:25 | 12 | 005:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA AVERIADA | C21080200975 | New_Event | Secondary Wire Down | Include | Include | Equipment | 313 | 2021-08-02 | 3756 | keep | 0 | Aug | 2021 | 0.0025582 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-08-02 11:24 | 2021-08-02 11:25 | 2163 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21080200693 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 2163 | keep | 0 | Aug | 2021 | 0.0014732 | 0.0014732 | Momentary | FALSE | FALSE | Not_TMED_Event | 2163
VEGA BAJA | 2021-08-02 11:24 | 2021-08-02 16:05 | 10 | 004:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21080201092 | New_Event | Secondary Wire Down | Include | Include | Equipment | 281 | 2021-08-02 | 2810 | keep | 0 | Aug | 2021 | 0.0019139 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-08-02 11:30 | 2021-08-02 19:15 | 150 | 007:45 | P | OTRAS CAUSAS | SE ABRIO CORTE DE LINEA PARA RELOCALIZAR LINEAS PRIMARIAS CASO WR4214888 AUT POR OMAR ORTIZ | M21080200000 | New_Event | Other Causes | Include | Include | Other | 465 | 2021-08-02 | 69750 | keep | 0 | Aug | 2021 | 0.047506 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-08-02 11:43 | 2021-08-02 17:19 | 80 | 005:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN RISER SE RETIRO GALLINA DE PALO | B21080201093 | New_Event |  |  | Include | Wildlife | 336 | 2021-08-02 | 26880 | keep | 0 | Aug | 2021 | 0.018308 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-08-02 11:44 | 2021-08-02 16:47 | 114 | 005:03 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO PUENTES Y SE CERRO CORTE DE LINEA PARA SECCIONALIZAR POSTE SECUNDARIO PARTIDO | B21080201094 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 303 | 2021-08-02 | 34542 | keep | 0 | Aug | 2021 | 0.023526 | 7.7645e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 114
PONCE | 2021-08-02 11:47 | 2021-08-04 14:00 | 15 | 050:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | P21080200696 | New_Event | Secondary Wire Down | Include | Include | Equipment | 3013 | 2021-08-02 | 45195 | keep | 0 | Aug | 2021 | 0.030782 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-08-02 11:50 | 2021-08-02 16:25 | 10 | 004:35 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTE SECUNDARIA Y SE RETIRO ENREDADERA | B21080201095 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 275 | 2021-08-02 | 2750 | keep | 0 | Aug | 2021 | 0.001873 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-08-02 11:50 | 2021-08-02 17:27 | 10 | 005:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA AVERIADA | C21080200981 | New_Event | Secondary Wire Down | Include | Include | Equipment | 337 | 2021-08-02 | 3370 | keep | 0 | Aug | 2021 | 0.0022953 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-08-02 11:52 | 2021-08-02 16:23 | 8 | 004:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA AVERIADA | C21080200982 | New_Event | Secondary Wire Down | Include | Include | Equipment | 271 | 2021-08-02 | 2168 | keep | 0 | Aug | 2021 | 0.0014766 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-08-02 11:54 | 2021-08-02 11:55 | 1297 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1904-06 LLEVANDO LA CARGA DEL 1901-02 Y 1901-03 | S21080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 1297 | keep | 0 | Aug | 2021 | 0.00088338 | 0.00088338 | Momentary | FALSE | FALSE | Not_TMED_Event | 1297
BAYAMON | 2021-08-02 11:54 | 2021-08-02 11:55 | 451 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1904-06 LLEVANDO LA CARGA DEL 1901-02 Y 1901-03 | S21080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 451 | keep | 0 | Aug | 2021 | 0.00030717 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
SAN JUAN | 2021-08-02 11:55 | 2021-08-02 11:56 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR EL 1206-03 | S21080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 10211 | keep | 0 | Aug | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-08-02 11:55 | 2021-08-02 11:56 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 1204-05 | S21080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 4133 | keep | 0 | Aug | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
AGUADILLA | 2021-08-02 12:01 | 2021-08-03 09:40 | 1 | 021:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21080201216 | New_Event | Bad Weather | Include | Include | Weather | 1299 | 2021-08-02 | 1299 | keep | 0 | Aug | 2021 | 0.00088474 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-08-02 12:03 | 2021-08-02 12:04 | 3434 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE LLEVA 80% DEL 1204-02 Y 40% DEL 1204-03 ATRAVEZ DE LA PORTATIL | S21080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 3434 | keep | 0 | Aug | 2021 | 0.0023389 | 0.0023389 | Momentary | FALSE | FALSE | Not_TMED_Event | 3434
SAN JUAN | 2021-08-02 12:03 | 2021-08-02 12:04 | 553 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE 40% DE LA CARGA POR 1204-02 | S21080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 553 | keep | 0 | Aug | 2021 | 0.00037665 | 0.00037665 | Momentary | FALSE | FALSE | Not_TMED_Event | 553
SAN JUAN | 2021-08-02 12:07 | 2021-08-02 12:08 | 84 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA CARGA POR EL 1529-15 | S21080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 84 | keep | 0 | Aug | 2021 | 5.7212e-05 | 5.7212e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 84
BAYAMON | 2021-08-02 12:07 | 2021-08-02 12:08 | 1802 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA LLEVA 30% 1346-02 | S21080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 1802 | keep | 0 | Aug | 2021 | 0.0012273 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
SAN JUAN | 2021-08-02 12:08 | 2021-08-02 20:55 | 291 | 008:47 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 CARGA POR 1531-02 | S21080201047 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 527 | 2021-08-02 | 153357 | keep | 0 | Aug | 2021 | 0.10445 | 0.0001982 | Sustained | FALSE | TRUE | Not_TMED_Event | 291
SAN JUAN | 2021-08-02 12:08 | 2021-08-02 20:55 | 164 | 008:47 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 CARGA POR 1531 02 | S21080201047 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 527 | 2021-08-02 | 86428 | keep | 0 | Aug | 2021 | 0.058866 | 0.0001117 | Sustained | FALSE | TRUE | Not_TMED_Event | 164
BAYAMON | 2021-08-02 12:08 | 2021-08-02 20:55 | 427 | 008:47 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S21080201047 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 527 | 2021-08-02 | 225029 | keep | 0 | Aug | 2021 | 0.15327 | 0.00029083 | Sustained | FALSE | TRUE | Not_TMED_Event | 427
BAYAMON | 2021-08-02 12:08 | 2021-08-02 20:55 | 716 | 008:47 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 LLEVANDO 1342-05 Y 1421-02 | S21080201047 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 527 | 2021-08-02 | 377332 | keep | 0 | Aug | 2021 | 0.257 | 0.00048766 | Sustained | FALSE | TRUE | Not_TMED_Event | 716
BAYAMON | 2021-08-02 12:08 | 2021-08-02 20:55 | 867 | 008:47 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S21080201047 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 527 | 2021-08-02 | 456909 | keep | 0 | Aug | 2021 | 0.3112 | 0.00059051 | Sustained | FALSE | TRUE | Not_TMED_Event | 867
BAYAMON | 2021-08-02 12:08 | 2021-08-02 20:55 | 353 | 008:47 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S21080201047 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 527 | 2021-08-02 | 186031 | keep | 0 | Aug | 2021 | 0.1267 | 0.00024043 | Sustained | FALSE | TRUE | Not_TMED_Event | 353
SAN JUAN | 2021-08-02 12:12 | 2021-08-03 10:15 | 50 | 022:03 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21080201034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1323 | 2021-08-02 | 66150 | keep | 0 | Aug | 2021 | 0.045054 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-08-02 12:14 | 2021-08-02 12:15 | 641 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | S21080200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-02 | 641 | keep | 0 | Aug | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-08-02 12:15 | 2021-08-02 12:45 | 500 | 000:30 | P | DESGANCHE | SE LEVANTO CONDUCTOR, SE REALIZO DESGANCHE Y SE CERRARON MACHETES | S21080201180 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 30 | 2021-08-02 | 15000 | keep | 0 | Aug | 2021 | 0.010216 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CAGUAS | 2021-08-02 12:29 | 2021-08-03 12:12 | 64 | 023:43 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE CRITICO | C21070200986 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1423 | 2021-08-02 | 91072 | keep | 0 | Aug | 2021 | 0.062029 | 4.359e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 64
MAYAGÃœEZ | 2021-08-02 12:31 | 2021-08-02 12:32 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21080200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-02 | 1617 | keep | 0 | Aug | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | TRUE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-08-02 12:31 | 2021-08-02 12:32 | 1017 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21080200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-02 | 1017 | keep | 0 | Aug | 2021 | 0.00069267 | 0.00069267 | Momentary | FALSE | TRUE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-08-02 12:31 | 2021-08-02 12:32 | 828 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21080200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-02 | 828 | keep | 0 | Aug | 2021 | 0.00056395 | 0.00056395 | Momentary | FALSE | TRUE | Not_TMED_Event | 828
MAYAGÃœEZ | 2021-08-02 12:31 | 2021-08-02 12:32 | 863 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21080200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-02 | 863 | keep | 0 | Aug | 2021 | 0.00058779 | 0.00058779 | Momentary | FALSE | TRUE | Not_TMED_Event | 863
MAYAGÃœEZ | 2021-08-02 12:31 | 2021-08-02 12:32 | 309 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21080200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-02 | 309 | keep | 0 | Aug | 2021 | 0.00021046 | 0.00021046 | Momentary | FALSE | TRUE | Not_TMED_Event | 309
MAYAGÃœEZ | 2021-08-02 12:31 | 2021-08-02 12:32 | 176 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21080200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-02 | 176 | keep | 0 | Aug | 2021 | 0.00011987 | 0.00011987 | Momentary | FALSE | TRUE | Not_TMED_Event | 176
BAYAMON | 2021-08-02 12:34 | 2021-08-02 12:35 | 418 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21080200000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-02 | 418 | keep | 0 | Aug | 2021 | 0.0002847 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
BAYAMON | 2021-08-02 12:35 | 2021-08-02 12:46 | 20 | 000:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE SAFADO | S21080200000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 11 | 2021-08-02 | 220 | keep | 0 | Aug | 2021 | 0.00014984 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-08-02 12:45 | 2021-08-02 12:46 | 641 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | S21080200000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-02 | 641 | keep | 0 | Aug | 2021 | 0.00043658 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-08-02 12:46 | 2021-08-02 12:48 | 500 | 000:02 | P | DESGANCHE | SE LEVANTO CONDUCTOR, SE REALIZO DESGANCHE Y SE CERRARON MACHETES | S21080201180 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-08-02 | 1000 | keep | 0 | Aug | 2021 | 0.0006811 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2021-08-02 12:48 | 2021-08-02 12:49 | 641 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | S21080200000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-02 | 641 | keep | 0 | Aug | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-08-02 12:49 | 2021-08-02 18:49 | 500 | 006:00 | P | DESGANCHE | SE LEVANTO CONDUCTOR, SE REALIZO DESGANCHE Y SE CERRARON MACHETES | S21080201180 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 360 | 2021-08-02 | 180000 | keep | 0 | Aug | 2021 | 0.1226 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2021-08-02 12:49 | 2021-08-02 12:50 | 2135 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | S21080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 2135 | keep | 0 | Aug | 2021 | 0.0014541 | 0.0014541 | Momentary | FALSE | FALSE | Not_TMED_Event | 2135
SAN JUAN | 2021-08-02 12:52 | 2021-08-02 12:53 | 1681 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR 1303-04 | S21080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 1681 | keep | 0 | Aug | 2021 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-08-02 12:52 | 2021-08-02 12:53 | 1598 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR 1303-04 | S21080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 1598 | keep | 0 | Aug | 2021 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2021-08-02 12:52 | 2021-08-02 12:53 | 3957 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 1303-04 | S21080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 3957 | keep | 0 | Aug | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
BAYAMON | 2021-08-02 13:08 | 2021-08-02 21:40 | 5 | 008:32 | P | TRANSFORMADOR AVERIADO | 1 X 15 EN RISER SE REEMPLAZO T-79 DE 75KVA POR 100KVA S21080201108 | B21080201108 | New_Event | Service Transformer Failure | Include | Include | Equipment | 512 | 2021-08-02 | 2560 | keep | 0 | Aug | 2021 | 0.0017436 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-08-02 13:11 | 2021-08-02 13:12 | 1026 | 000:01 | T | DESGANCHE | RECIERRE | R21080200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-02 | 1026 | keep | 0 | Aug | 2021 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
SAN JUAN | 2021-08-02 13:12 | 2021-08-02 19:34 | 121 | 006:22 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21080200489 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 382 | 2021-08-02 | 46222 | keep | 0 | Aug | 2021 | 0.031482 | 8.2413e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 121
SAN JUAN | 2021-08-02 13:14 | 2021-08-02 15:17 | 5062 | 002:03 | T | DESGANCHE | SE RETIRO ARBOL SOBRE LINEAS Y CERRO INTERRUPTOR | R21080200459 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2021-08-02 | 622626 | keep | 0 | Aug | 2021 | 0.42407 | 0.0034477 | Sustained | FALSE | TRUE | Not_TMED_Event | 5062
SAN JUAN | 2021-08-02 13:21 | 2021-08-02 13:22 | 1681 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR 1303-04 | S21080200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 1681 | keep | 0 | Aug | 2021 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-08-02 13:21 | 2021-08-02 13:22 | 1598 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR 1303-04 | S21080200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 1598 | keep | 0 | Aug | 2021 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
BAYAMON | 2021-08-02 13:21 | 2021-08-02 13:22 | 1533 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE LLEVA EL 1709-05 | S21080200000 | New_Event |  |  | Include | Wildlife | 1 | 2021-08-02 | 1533 | keep | 0 | Aug | 2021 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
BAYAMON | 2021-08-02 13:21 | 2021-08-02 13:22 | 1533 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE LLEVA EL 1709-05 | S21080200000 | New_Event |  |  | Include | Wildlife | 1 | 2021-08-02 | 1533 | keep | 0 | Aug | 2021 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
FAJARDO | 2021-08-02 13:29 | 2021-08-02 14:42 | 50 | 001:13 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21080200470 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2021-08-02 | 3650 | keep | 0 | Aug | 2021 | 0.002486 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-02 13:36 | 2021-08-02 13:37 | 2530 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 2530 | keep | 0 | Aug | 2021 | 0.0017232 | 0.0017232 | Momentary | FALSE | FALSE | Not_TMED_Event | 2530
UTUADO | 2021-08-02 13:51 | 2021-08-02 13:52 | 1054 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21080200795 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 1054 | keep | 0 | Aug | 2021 | 0.00071787 | 0.00071787 | Momentary | FALSE | FALSE | Not_TMED_Event | 1054
SAN JUAN | 2021-08-02 14:15 | 2021-08-02 15:15 | 780 | 001:00 | P | DESGANCHE | SE CERRO POR SCADA SE REALIZO DESGANCHE PRIMARIO CARGA POR 1206-04 | S21080201115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2021-08-02 | 46800 | keep | 0 | Aug | 2021 | 0.031875 | 0.00053125 | Sustained | FALSE | FALSE | Not_TMED_Event | 780
SAN JUAN | 2021-08-02 14:15 | 2021-08-02 15:15 | 1900 | 001:00 | T | DESGANCHE | SE CERRO POR SCADA SE REALIZO DESGANCHE PRIMARIO CARGA POR 1206-04 | S21080201115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2021-08-02 | 114000 | keep | 0 | Aug | 2021 | 0.077645 | 0.0012941 | Sustained | FALSE | FALSE | Not_TMED_Event | 1900
SAN JUAN | 2021-08-02 14:15 | 2021-08-02 15:15 | 1799 | 001:00 | T | DESGANCHE | SE CERRO POR SCADA SE REALIZO DESGANCHE PRIMARIO LLEVA PARTE 1204-03 1204-04 Y 1303-02 | S21080201115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2021-08-02 | 107940 | keep | 0 | Aug | 2021 | 0.073517 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2021-08-02 14:15 | 2021-08-02 15:15 | 300 | 001:00 | P | DESGANCHE | SE CERRO POR SCADA SE REALIZO DESGANCHE PRIMARIO CARGA POR 1206-04 | S21080201115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2021-08-02 | 18000 | keep | 0 | Aug | 2021 | 0.01226 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BARRANQUITAS | 2021-08-02 14:17 | 2021-08-02 14:18 | 2192 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 2192 | keep | 0 | Aug | 2021 | 0.001493 | 0.001493 | Momentary | FALSE | FALSE | Not_TMED_Event | 2192
PONCE | 2021-08-02 14:20 | 2021-08-02 14:21 | 752 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21070200706 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 752 | keep | 0 | Aug | 2021 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
AGUADILLA | 2021-08-02 14:26 | 2021-08-02 23:50 | 60 | 009:24 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | M21080201252 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 564 | 2021-08-02 | 33840 | keep | 0 | Aug | 2021 | 0.023048 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
PONCE | 2021-08-02 14:30 | 2021-08-02 17:43 | 12 | 003:13 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR DE 25KVA A 2.4KV AVERIADO. SE REMPLAZO POR UNO DE 37.5KVA A 2.4KV EATON/COOPER | P21080200741 | New_Event | Service Transformer Failure | Include | Include | Equipment | 193 | 2021-08-02 | 2316 | keep | 0 | Aug | 2021 | 0.0015774 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2021-08-02 14:40 | 2021-08-02 17:30 | 5 | 002:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR POR MAL TIEMPO | A21080200799 | New_Event | Bad Weather | Include | Include | Weather | 170 | 2021-08-02 | 850 | keep | 0 | Aug | 2021 | 0.00057893 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2021-08-02 14:41 | 2021-08-02 19:00 | 300 | 004:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE DESGANCHO Y SE RETEZO LINEA PRIMARIA | M21080201261 | New_Event | Wire Down | Include | Include | Equipment | 259 | 2021-08-02 | 77700 | keep | 0 | Aug | 2021 | 0.052921 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
UTUADO | 2021-08-02 14:43 | 2021-08-02 16:45 | 10 | 002:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A21080200800 | New_Event | Wire Down | Include | Include | Equipment | 122 | 2021-08-02 | 1220 | keep | 0 | Aug | 2021 | 0.00083094 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-02 14:44 | 2021-08-02 17:40 | 8 | 002:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR POR MAL TIEMPO | A21080200801 | New_Event | Bad Weather | Include | Include | Weather | 176 | 2021-08-02 | 1408 | keep | 0 | Aug | 2021 | 0.00095898 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2021-08-02 14:47 | 2021-08-02 20:51 | 25 | 006:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21080200803 | New_Event | Bad Weather | Include | Include | Weather | 364 | 2021-08-02 | 9100 | keep | 0 | Aug | 2021 | 0.006198 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BARRANQUITAS | 2021-08-02 14:58 | 2021-08-02 17:06 | 120 | 002:08 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21080201000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2021-08-02 | 15360 | keep | 0 | Aug | 2021 | 0.010462 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
PONCE | 2021-08-02 14:59 | 2021-08-02 15:00 | 2163 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21080200708 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 2163 | keep | 0 | Aug | 2021 | 0.0014732 | 0.0014732 | Momentary | FALSE | FALSE | Not_TMED_Event | 2163
SAN JUAN | 2021-08-02 15:00 | 2021-08-02 18:13 | 95 | 003:13 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21080200549 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2021-08-02 | 18335 | keep | 0 | Aug | 2021 | 0.012488 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
ARECIBO | 2021-08-02 15:15 | 2021-08-02 18:10 | 45 | 002:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LA LINEA | A21080200810 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2021-08-02 | 7875 | keep | 0 | Aug | 2021 | 0.0053636 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
MAYAGÃœEZ | 2021-08-02 15:17 | 2021-08-02 17:35 | 30 | 002:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | M21080201273 | New_Event | Bad Weather | Include | Include | Weather | 138 | 2021-08-02 | 4140 | keep | 0 | Aug | 2021 | 0.0028197 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-08-02 15:21 | 2021-08-02 17:40 | 100 | 002:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | A21080200814 | New_Event | Bad Weather | Include | Include | Weather | 139 | 2021-08-02 | 13900 | keep | 0 | Aug | 2021 | 0.0094672 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-08-02 15:29 | 2021-08-02 18:20 | 50 | 002:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | M21080201275 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2021-08-02 | 8550 | keep | 0 | Aug | 2021 | 0.0058234 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-08-02 15:38 | 2021-08-02 17:24 | 40 | 001:46 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA SECCIONALIZAR POSTE ROTO ABRIENDO PUENTE POR DERRUMBE DE TERRENO | R21080200507 | New_Event | Defective Pole | Include | Include | Equipment | 106 | 2021-08-02 | 4240 | keep | 0 | Aug | 2021 | 0.0028878 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-02 15:40 | 2021-08-02 21:50 | 50 | 006:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | M21080201279 | New_Event | Bad Weather | Include | Include | Weather | 370 | 2021-08-02 | 18500 | keep | 0 | Aug | 2021 | 0.0126 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-08-02 15:41 | 2021-08-02 17:24 | 10 | 001:43 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REPARO BUSHING SECUNDARIO EN TRANSFORMADOR | R21080200531 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 103 | 2021-08-02 | 1030 | keep | 0 | Aug | 2021 | 0.00070153 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-08-02 15:44 | 2021-08-03 12:20 | 50 | 020:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21080201281 | New_Event | Bad Weather | Include | Include | Weather | 1236 | 2021-08-02 | 61800 | keep | 0 | Aug | 2021 | 0.042092 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-08-02 15:51 | 2021-08-02 15:52 | 449 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210802000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 449 | keep | 0 | Aug | 2021 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
PONCE | 2021-08-02 15:59 | 2021-08-02 16:00 | 1952 | 000:01 | T | DESGANCHE | RECIERRE | P21080200710 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-02 | 1952 | keep | 0 | Aug | 2021 | 0.0013295 | 0.0013295 | Momentary | FALSE | FALSE | Not_TMED_Event | 1952
PONCE | 2021-08-02 16:00 | 2021-08-02 18:04 | 200 | 002:04 | P | DESGANCHE | 2 X 140 EN CORTE DE LINEA POR DESGANCHE | P21080200716 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 124 | 2021-08-02 | 24800 | keep | 0 | Aug | 2021 | 0.016891 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-08-02 16:11 | 2021-08-02 18:43 | 95 | 002:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AUTO IMPACTO POSTE CRUZANDO LINEAS | C21080201021 | New_Event |  |  | Include | Wildlife | 152 | 2021-08-02 | 14440 | keep | 0 | Aug | 2021 | 0.009835 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
MAYAGÃœEZ | 2021-08-02 16:30 | 2021-08-03 11:12 | 12 | 018:42 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | M2108021293 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1122 | 2021-08-02 | 13464 | keep | 0 | Aug | 2021 | 0.0091703 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
UTUADO | 2021-08-02 16:39 | 2021-08-03 11:30 | 10 | 018:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21020800832 | New_Event | Bad Weather | Include | Include | Weather | 1131 | 2021-08-02 | 11310 | keep | 0 | Aug | 2021 | 0.0077032 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-08-02 16:39 | 2021-08-02 17:35 | 500 | 000:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ENCONTRO PUENTE ABIERTO EN TRONCAL | B21080201131 | New_Event | Wire Down | Include | Include | Equipment | 56 | 2021-08-02 | 28000 | keep | 0 | Aug | 2021 | 0.019071 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2021-08-02 16:47 | 2021-08-03 17:42 | 24 | 024:55 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REMPLAZO POSTE Y 100 PIES DE SECUNDARIA QUEMADA | B21080201172 | Partial_restoration | Secondary Defective Pole | Include | Include | Equipment | 1495 | 2021-08-02 | 35880 | keep | 0 | Aug | 2021 | 0.024438 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-02 16:48 | 2021-08-02 17:31 | 10 | 000:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21080201123 | New_Event | Secondary Wire Down | Include | Include | Equipment | 43 | 2021-08-02 | 430 | keep | 0 | Aug | 2021 | 0.00029287 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-08-02 16:54 | 2021-08-03 16:49 | 50 | 023:55 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA Y 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21080201204 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1435 | 2021-08-02 | 71750 | keep | 0 | Aug | 2021 | 0.048869 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-02 17:00 | 2021-08-02 21:50 | 60 | 004:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | M21080201303 | New_Event | Bad Weather | Include | Include | Weather | 290 | 2021-08-02 | 17400 | keep | 0 | Aug | 2021 | 0.011851 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
UTUADO | 2021-08-02 17:02 | 2021-08-03 16:55 | 10 | 023:53 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA X 25 KVA | A21080200836 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1433 | 2021-08-02 | 14330 | keep | 0 | Aug | 2021 | 0.0097601 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-08-02 17:35 | 2021-08-02 19:30 | 75 | 001:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | M21080201312 | New_Event | Bad Weather | Include | Include | Weather | 115 | 2021-08-02 | 8625 | keep | 0 | Aug | 2021 | 0.0058744 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-08-02 17:35 | 2021-08-02 21:43 | 2000 | 004:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIERON MACHETES Y SE CERRO PUENTE ABIERTO EN TRONCAL | B21080201131 | Additional_clients | Wire Down | Include | Include | Equipment | 248 | 2021-08-02 | 496000 | keep | 0 | Aug | 2021 | 0.33782 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-08-02 17:39 | 2021-08-02 18:47 | 100 | 001:08 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21080201027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2021-08-02 | 6800 | keep | 0 | Aug | 2021 | 0.0046314 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-08-02 17:46 | 2021-08-02 22:30 | 30 | 004:44 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A21080200844 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 284 | 2021-08-02 | 8520 | keep | 0 | Aug | 2021 | 0.0058029 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
VEGA BAJA | 2021-08-02 17:53 | 2021-08-03 14:30 | 12 | 020:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE LEVANTO APROXIMADAMENTE 500 PIES DE ALAMBRE PRIMARIO QUE FUE ROBADO | B21080201142 | New_Event |  |  | Include | Wildlife | 1237 | 2021-08-02 | 14844 | keep | 0 | Aug | 2021 | 0.01011 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-08-02 18:11 | 2021-08-02 18:12 | 2450 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DSIPARO NO RECERRO | C21080201029 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-08-02 | 2450 | keep | 0 | Aug | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2021-08-02 18:12 | 2021-08-03 17:16 | 98 | 023:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21080201038 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1384 | 2021-08-02 | 135632 | keep | 0 | Aug | 2021 | 0.092378 | 6.6747e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 98
UTUADO | 2021-08-02 18:12 | 2021-08-03 10:05 | 40 | 015:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21080200849 | New_Event | Bad Weather | Include | Include | Weather | 953 | 2021-08-02 | 38120 | keep | 0 | Aug | 2021 | 0.025963 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-08-02 18:14 | 2021-08-02 19:03 | 9 | 000:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA ABIERTA | R21080200528 | New_Event | Secondary Wire Down | Include | Include | Equipment | 49 | 2021-08-02 | 441 | keep | 0 | Aug | 2021 | 0.00030036 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2021-08-02 18:22 | 2021-08-02 19:16 | 11 | 000:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR TOMA AVERIADA | R21080200541 | New_Event | Secondary Wire Down | Include | Include | Equipment | 54 | 2021-08-02 | 594 | keep | 0 | Aug | 2021 | 0.00040457 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2021-08-02 18:27 | 2021-08-02 18:28 | 3434 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE LLEVA 80% DEL 1204-02 Y 40% DEL 1204-03 ATRAVEZ DE LA PORTATIL | S21080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 3434 | keep | 0 | Aug | 2021 | 0.0023389 | 0.0023389 | Momentary | FALSE | FALSE | Not_TMED_Event | 3434
SAN JUAN | 2021-08-02 18:27 | 2021-08-02 18:28 | 553 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE 40% DE LA CARGA POR 1204-02 | S21080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 553 | keep | 0 | Aug | 2021 | 0.00037665 | 0.00037665 | Momentary | FALSE | FALSE | Not_TMED_Event | 553
YAUCO | 2021-08-02 18:52 | 2021-08-03 11:46 | 50 | 016:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21080200727 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1014 | 2021-08-02 | 50700 | keep | 0 | Aug | 2021 | 0.034532 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-08-02 19:01 | 2021-08-02 21:06 | 110 | 002:05 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21080200557 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2021-08-02 | 13750 | keep | 0 | Aug | 2021 | 0.0093651 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
SAN JUAN | 2021-08-02 19:10 | 2021-08-03 10:35 | 70 | 015:25 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | S21080201234 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 925 | 2021-08-02 | 64750 | keep | 0 | Aug | 2021 | 0.044101 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
SAN JUAN | 2021-08-02 19:17 | 2021-08-02 19:20 | 36 | 000:03 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR 1620 04 | S21080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-08-02 | 108 | keep | 0 | Aug | 2021 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-08-02 19:17 | 2021-08-02 19:20 | 172 | 000:03 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA 1620 01 | S21080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-08-02 | 516 | keep | 0 | Aug | 2021 | 0.00035145 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
HUMACAO | 2021-08-02 19:20 | 2021-08-02 19:21 | 1891 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 PUENTE ABIERTO | C21080201045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-02 | 1891 | keep | 0 | Aug | 2021 | 0.001288 | 0.001288 | Momentary | FALSE | TRUE | Not_TMED_Event | 1891
HUMACAO | 2021-08-02 19:20 | 2021-08-02 19:21 | 1250 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 PUENTE ABIERTO | C21080201045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-02 | 1250 | keep | 0 | Aug | 2021 | 0.00085137 | 0.00085137 | Momentary | FALSE | TRUE | Not_TMED_Event | 1250
HUMACAO | 2021-08-02 19:20 | 2021-08-02 19:21 | 2141 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 PUENTE ABIERTO | C21080201045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-02 | 2141 | keep | 0 | Aug | 2021 | 0.0014582 | 0.0014582 | Momentary | FALSE | TRUE | Not_TMED_Event | 2141
HUMACAO | 2021-08-02 19:20 | 2021-08-02 19:21 | 1827 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 PUENTE ABIERTO | C21080201045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-02 | 1827 | keep | 0 | Aug | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | TRUE | Not_TMED_Event | 1827
SAN JUAN | 2021-08-02 19:31 | 2021-08-03 16:56 | 150 | 021:25 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE DE RAMAS | S21080201234 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1285 | 2021-08-02 | 192750 | keep | 0 | Aug | 2021 | 0.13128 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
VEGA BAJA | 2021-08-02 19:32 | 2021-08-02 21:30 | 35 | 001:58 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE NECESITA DESGANCHE | B21080201166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2021-08-02 | 4130 | keep | 0 | Aug | 2021 | 0.0028129 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-08-02 19:34 | 2021-08-02 23:37 | 200 | 004:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21080200862 | New_Event | Bad Weather | Include | Include | Weather | 243 | 2021-08-02 | 48600 | keep | 0 | Aug | 2021 | 0.033101 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
PONCE | 2021-08-02 19:45 | 2021-08-03 15:50 | 15 | 020:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | P21080200730 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1205 | 2021-08-02 | 18075 | keep | 0 | Aug | 2021 | 0.012311 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-08-02 19:57 | 2021-08-03 11:17 | 40 | 015:20 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21080201240 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 920 | 2021-08-02 | 36800 | keep | 0 | Aug | 2021 | 0.025064 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-08-02 19:58 | 2021-08-03 19:07 | 15 | 023:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA REPARO CONDUCTOR ROTO | R21080200565 | New_Event | Wire Down | Include | Include | Equipment | 1389 | 2021-08-02 | 20835 | keep | 0 | Aug | 2021 | 0.014191 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-08-02 20:00 | 2021-08-03 15:56 | 20 | 019:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B21080201171 | New_Event | Cutout Failure | Include | Include | Equipment | 1196 | 2021-08-02 | 23920 | keep | 0 | Aug | 2021 | 0.016292 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
GUAYAMA | 2021-08-02 20:29 | 2021-08-02 22:32 | 100 | 002:03 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA. NO SE REPORTO LA CAUSA | P21080200735 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 123 | 2021-08-02 | 12300 | keep | 0 | Aug | 2021 | 0.0083775 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-08-02 20:31 | 2021-08-03 10:42 | 430 | 014:11 | P | DESGANCHE | 1 X 140 EN SALIDA DEL CONVERTIDOR SE REALIZO DESGANCHE CRITICO | C21080200049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 851 | 2021-08-02 | 365930 | keep | 0 | Aug | 2021 | 0.24923 | 0.00029287 | Sustained | FALSE | FALSE | Not_TMED_Event | 430
HUMACAO | 2021-08-02 20:44 | 2021-08-03 17:53 | 130 | 021:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA REEMPLAZO PORTAFUSIBLE | C21080201055 | New_Event | Cutout Failure | Include | Include | Equipment | 1269 | 2021-08-02 | 164970 | keep | 0 | Aug | 2021 | 0.11236 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
BARRANQUITAS | 2021-08-02 21:23 | 2021-08-02 21:24 | 1604 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 1604 | keep | 0 | Aug | 2021 | 0.0010925 | 0.0010925 | Momentary | FALSE | FALSE | Not_TMED_Event | 1604
AGUADILLA | 2021-08-02 21:40 | 2021-08-03 11:39 | 14 | 013:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21080201332 | New_Event | Bad Weather | Include | Include | Weather | 839 | 2021-08-02 | 11746 | keep | 0 | Aug | 2021 | 0.0080001 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CANOVANAS | 2021-08-02 22:24 | 2021-08-02 22:25 | 2708 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21080200570 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-02 | 2708 | keep | 0 | Aug | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
HUMACAO | 2021-08-02 22:30 | 2021-08-02 22:53 | 12 | 000:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR REEMPLAZO PORTAFUSIBLE | C21080201045 | New_Event | Cutout Failure | Include | Include | Equipment | 23 | 2021-08-02 | 276 | keep | 0 | Aug | 2021 | 0.00018798 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-08-02 22:35 | 2021-08-03 17:16 | 80 | 018:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21080201071 | New_Event | Bad Weather | Include | Include | Weather | 1121 | 2021-08-02 | 89680 | keep | 0 | Aug | 2021 | 0.061081 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-08-02 22:53 | 2021-08-03 16:40 | 60 | 017:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON CAJAS PRIMARIAS QUEMADAS | M21080201334 | New_Event | Cutout Failure | Include | Include | Equipment | 1067 | 2021-08-02 | 64020 | keep | 0 | Aug | 2021 | 0.043604 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-08-02 23:17 | 2021-08-03 11:08 | 70 | 011:51 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21080201200 | New_Event | Vegetation Contact | Include | Include | Vegetation | 711 | 2021-08-02 | 49770 | keep | 0 | Aug | 2021 | 0.033898 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
GUAYAMA | 2021-08-03 00:28 | 2021-08-03 07:03 | 100 | 006:35 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | P21080300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 395 | 2021-08-03 | 39500 | keep | 0 | Aug | 2021 | 0.026903 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-08-03 00:54 | 2021-08-03 00:55 | 2113 | 000:01 | T | CABLE SOTERRADO AVERIADO | AVERIA SOTERRADA | P21080300003 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2021-08-03 | 2113 | keep | 0 | Aug | 2021 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
BAYAMON | 2021-08-03 00:56 | 2021-08-04 22:00 | 20 | 045:04 | P | CABLE SOTERRADO AVERIADO | SE INSTALO AEREO PROVISIONAL DE OTRO AEREO PROVISIONAL EXISTENTE HACIA EL T-32 POR CONDUCTOR PRIMARIO SOTERRADO DEFECTUOSO | B21080300278 | New_Event | UG Cable Fault | Include | Include | Equipment | 2704 | 2021-08-03 | 54080 | keep | 0 | Aug | 2021 | 0.036834 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-08-03 02:29 | 2021-08-03 11:20 | 25 | 008:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | A21080300006 | New_Event | Cutout Failure | Include | Include | Equipment | 531 | 2021-08-03 | 13275 | keep | 0 | Aug | 2021 | 0.0090415 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
VEGA BAJA | 2021-08-03 04:17 | 2021-08-03 04:18 | 1284 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21080300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-03 | 1284 | keep | 0 | Aug | 2021 | 0.00087453 | 0.00087453 | Momentary | FALSE | FALSE | Not_TMED_Event | 1284
MAYAGÃœEZ | 2021-08-03 05:13 | 2021-08-03 09:24 | 10 | 004:11 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | M21080300004 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 251 | 2021-08-03 | 2510 | keep | 0 | Aug | 2021 | 0.0017095 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
PONCE | 2021-08-03 05:39 | 2021-08-03 06:04 | 1268 | 000:25 | P | CABLE SOTERRADO AVERIADO | MANIOBRAS PARA RESTABLECER BREAKER | P21080300010 | New_Event | UG Cable Fault | Include | Include | Equipment | 25 | 2021-08-03 | 31700 | keep | 0 | Aug | 2021 | 0.021591 | 0.00086363 | Sustained | FALSE | FALSE | Not_TMED_Event | 1268
BAYAMON | 2021-08-03 05:51 | 2021-08-03 05:52 | 2735 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21080300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-03 | 2735 | keep | 0 | Aug | 2021 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
PONCE | 2021-08-03 06:03 | 2021-08-03 06:04 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | NO SE REPORTO CAUSAS | P21080300019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-03 | 3718 | keep | 0 | Aug | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
PONCE | 2021-08-03 06:04 | 2021-08-03 16:26 | 3 | 010:22 | P | CABLE SOTERRADO AVERIADO | RISER ABIERTO HACIA MH-11 AVERIA DE MH-11 A MH01 | P21080300015 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 622 | 2021-08-03 | 1866 | keep | 0 | Aug | 2021 | 0.0012709 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-08-03 06:06 | 2021-08-03 09:55 | 200 | 003:49 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE RETIRO RAMA | A21080300012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2021-08-03 | 45800 | keep | 0 | Aug | 2021 | 0.031194 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-08-03 06:12 | 2021-08-03 06:13 | 3046 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | R21080300002 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-08-03 | 3046 | keep | 0 | Aug | 2021 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2021-08-03 06:13 | 2021-08-03 18:15 | 65 | 012:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA REEMPLAZO AISLADOR ROTO | R21080300018 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 722 | 2021-08-03 | 46930 | keep | 0 | Aug | 2021 | 0.031964 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BAYAMON | 2021-08-03 06:29 | 2021-08-03 09:37 | 2234 | 003:08 | T | NO SE REPORTO CAUSA | SE PATRULLO NO SE VIO CONDICION Y SE CERRO POR SCADA | B21080300010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 188 | 2021-08-03 | 419992 | keep | 0 | Aug | 2021 | 0.28605 | 0.0015216 | Sustained | FALSE | FALSE | Not_TMED_Event | 2234
FAJARDO | 2021-08-03 06:34 | 2021-08-03 09:19 | 100 | 002:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | R21080300004 | New_Event |  |  | Include | Wildlife | 165 | 2021-08-03 | 16500 | keep | 0 | Aug | 2021 | 0.011238 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-08-03 06:36 | 2021-08-04 19:40 | 50 | 037:04 | P | DESGANCHE | SE RETIRARON BAMBUAS SOBRE LAS LINEAS PRIMARIAS | A21080300013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2224 | 2021-08-03 | 111200 | keep | 0 | Aug | 2021 | 0.075738 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-03 06:49 | 2021-08-03 09:50 | 100 | 003:01 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PARARRAYO CRUZADO | A21080300015 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 181 | 2021-08-03 | 18100 | keep | 0 | Aug | 2021 | 0.012328 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-08-03 06:58 | 2021-08-03 11:50 | 50 | 004:52 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21080300016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 292 | 2021-08-03 | 14600 | keep | 0 | Aug | 2021 | 0.009944 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-08-03 07:03 | 2021-08-03 11:57 | 52 | 004:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIAS | C21080300013 | New_Event | Bad Weather | Include | Include | Weather | 294 | 2021-08-03 | 15288 | keep | 0 | Aug | 2021 | 0.010413 | 3.5417e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 52
BAYAMON | 2021-08-03 07:03 | 2021-08-03 18:08 | 15 | 011:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | B21080300013 | New_Event | Cutout Failure | Include | Include | Equipment | 665 | 2021-08-03 | 9975 | keep | 0 | Aug | 2021 | 0.0067939 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CANOVANAS | 2021-08-03 07:11 | 2021-08-03 09:37 | 60 | 002:26 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 50 Y 1 X 30 EN RISER Y SU SE REEMPLAZO STRESSCONE | R21080300006 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 146 | 2021-08-03 | 8760 | keep | 0 | Aug | 2021 | 0.0059664 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-08-03 07:29 | 2021-08-03 09:15 | 100 | 001:46 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21080300007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2021-08-03 | 10600 | keep | 0 | Aug | 2021 | 0.0072196 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-08-03 07:35 | 2021-08-03 08:06 | 3387 | 000:31 | S | ANIMAL U OBJETO EXTRAÃ‘O | SUB. SE FUE A LOCK-OUT POR PALOMA QUE CRUZO MEDICION EN EL LADO DE LA BARRA SE REMONTO LOCK-OUT Y SE ENERGIZO Y NORMALIZO CARGAS AUTORIZADO POR LUIS MIRANDA Y LUIS CENTENO | B21080300018 | New_Event |  |  | Include | Wildlife | 31 | 2021-08-03 | 104997 | keep | 0 | Aug | 2021 | 0.071513 | 0.0023069 | Sustained | FALSE | FALSE | Not_TMED_Event | 3387
VEGA BAJA | 2021-08-03 07:35 | 2021-08-03 08:06 | 4702 | 000:31 | S | ANIMAL U OBJETO EXTRAÃ‘O | SUB. SE FUE A LOCK-OUT POR PALOMA QUE CRUZO MEDICION EN EL LADO DE LA BARRA SE REMONTO LOCK-OUT Y SE ENERGIZO Y NORMALIZO CARGAS AUTORIZADO POR LUIS MIRANDA Y LUIS CENTENO | B21080300018 | New_Event |  |  | Include | Wildlife | 31 | 2021-08-03 | 145762 | keep | 0 | Aug | 2021 | 0.099278 | 0.0032025 | Sustained | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2021-08-03 07:35 | 2021-08-03 08:06 | 377 | 000:31 | S | ANIMAL U OBJETO EXTRAÃ‘O | SUB. SE FUE A LOCK-OUT POR PALOMA QUE CRUZO MEDICION EN EL LADO DE LA BARRA SE REMONTO LOCK-OUT Y SE ENERGIZO Y NORMALIZO CARGAS AUTORIZADO POR LUIS MIRANDA Y LUIS CENTENO | B21080300018 | New_Event |  |  | Include | Wildlife | 31 | 2021-08-03 | 11687 | keep | 0 | Aug | 2021 | 0.00796 | 0.00025677 | Sustained | FALSE | FALSE | Not_TMED_Event | 377
CAGUAS | 2021-08-03 07:46 | 2021-08-03 18:36 | 5 | 010:50 | P | NO SE REPORTO CAUSA | 2 X 50 EN RISER | C21080300015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 650 | 2021-08-03 | 3250 | keep | 0 | Aug | 2021 | 0.0022136 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-08-03 07:51 | 2021-08-03 13:30 | 40 | 005:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DE AISLADORES | A21080300019 | New_Event | Wire Down | Include | Include | Equipment | 339 | 2021-08-03 | 13560 | keep | 0 | Aug | 2021 | 0.0092357 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-08-03 07:53 | 2021-08-03 08:49 | 2725 | 000:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEAS 8500 Y 4800 | C21080300019 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 56 | 2021-08-03 | 152600 | keep | 0 | Aug | 2021 | 0.10394 | 0.001856 | Sustained | FALSE | TRUE | Not_TMED_Event | 2725
BARRANQUITAS | 2021-08-03 07:53 | 2021-08-03 08:49 | 1834 | 000:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEAS 8500 Y 4800 | C21080300019 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 56 | 2021-08-03 | 102704 | keep | 0 | Aug | 2021 | 0.069951 | 0.0012491 | Sustained | FALSE | TRUE | Not_TMED_Event | 1834
BARRANQUITAS | 2021-08-03 07:53 | 2021-08-03 08:49 | 1437 | 000:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEAS 8500 Y 4800 | C21080300019 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 56 | 2021-08-03 | 80472 | keep | 0 | Aug | 2021 | 0.054809 | 0.00097873 | Sustained | FALSE | TRUE | Not_TMED_Event | 1437
BARRANQUITAS | 2021-08-03 07:53 | 2021-08-03 08:49 | 2565 | 000:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEAS 8500 Y 4800 | C21080300020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 56 | 2021-08-03 | 143640 | keep | 0 | Aug | 2021 | 0.097833 | 0.001747 | Sustained | FALSE | TRUE | Not_TMED_Event | 2565
BARRANQUITAS | 2021-08-03 07:53 | 2021-08-03 08:49 | 3565 | 000:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEAS 8500 Y 4800 | C21080300020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 56 | 2021-08-03 | 199640 | keep | 0 | Aug | 2021 | 0.13597 | 0.0024281 | Sustained | FALSE | TRUE | Not_TMED_Event | 3565
PONCE | 2021-08-03 07:54 | 2021-08-03 08:50 | 2751 | 000:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 | P21080300059 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 56 | 2021-08-03 | 154056 | keep | 0 | Aug | 2021 | 0.10493 | 0.0018737 | Sustained | FALSE | TRUE | Not_TMED_Event | 2751
PONCE | 2021-08-03 07:54 | 2021-08-03 08:50 | 576 | 000:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 | P21080300059 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 56 | 2021-08-03 | 32256 | keep | 0 | Aug | 2021 | 0.021969 | 0.00039231 | Sustained | FALSE | TRUE | Not_TMED_Event | 576
PONCE | 2021-08-03 07:54 | 2021-08-03 08:50 | 2584 | 000:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 | P21080300059 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 56 | 2021-08-03 | 144704 | keep | 0 | Aug | 2021 | 0.098557 | 0.00176 | Sustained | FALSE | TRUE | Not_TMED_Event | 2584
PONCE | 2021-08-03 07:54 | 2021-08-03 08:50 | 1606 | 000:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 | P21080300059 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 56 | 2021-08-03 | 89936 | keep | 0 | Aug | 2021 | 0.061255 | 0.0010938 | Sustained | FALSE | TRUE | Not_TMED_Event | 1606
PONCE | 2021-08-03 07:54 | 2021-08-03 08:50 | 29 | 000:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 | P21080300059 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 56 | 2021-08-03 | 1624 | keep | 0 | Aug | 2021 | 0.0011061 | 1.9752e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 29
PONCE | 2021-08-03 07:54 | 2021-08-03 08:50 | 4035 | 000:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 | P21080300060 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 56 | 2021-08-03 | 225960 | keep | 0 | Aug | 2021 | 0.1539 | 0.0027482 | Sustained | FALSE | TRUE | Not_TMED_Event | 4035
PONCE | 2021-08-03 07:54 | 2021-08-03 08:50 | 3718 | 000:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4800 | P21080300060 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 56 | 2021-08-03 | 208208 | keep | 0 | Aug | 2021 | 0.14181 | 0.0025323 | Sustained | FALSE | TRUE | Not_TMED_Event | 3718
BARRANQUITAS | 2021-08-03 08:01 | 2021-08-03 13:07 | 90 | 005:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIAS | C21080300021 | New_Event | Bad Weather | Include | Include | Weather | 306 | 2021-08-03 | 27540 | keep | 0 | Aug | 2021 | 0.018757 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
ARECIBO | 2021-08-03 08:08 | 2021-08-03 15:40 | 4 | 007:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21080300021 | New_Event | Bad Weather | Include | Include | Weather | 452 | 2021-08-03 | 1808 | keep | 0 | Aug | 2021 | 0.0012314 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-08-03 08:10 | 2021-08-03 20:58 | 50 | 012:48 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21080300031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 768 | 2021-08-03 | 38400 | keep | 0 | Aug | 2021 | 0.026154 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-08-03 08:38 | 2021-08-03 08:39 | 36 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21080300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-03 | 36 | keep | 0 | Aug | 2021 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-08-03 08:38 | 2021-08-03 08:39 | 172 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21080300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-03 | 172 | keep | 0 | Aug | 2021 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
BARRANQUITAS | 2021-08-03 08:42 | 2021-08-03 14:18 | 130 | 005:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA AVERIADA | C21080300031 | New_Event | Cutout Failure | Include | Include | Equipment | 336 | 2021-08-03 | 43680 | keep | 0 | Aug | 2021 | 0.02975 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
CAGUAS | 2021-08-03 08:44 | 2021-08-03 18:45 | 10 | 010:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA AVERIADA | C21080300022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 601 | 2021-08-03 | 6010 | keep | 0 | Aug | 2021 | 0.0040934 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-08-03 08:46 | 2021-08-03 16:36 | 50 | 007:50 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21080300032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 470 | 2021-08-03 | 23500 | keep | 0 | Aug | 2021 | 0.016006 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-08-03 09:00 | 2021-08-03 10:43 | 120 | 001:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 N CORTE DE LINEA CRUCE CON AVE | R21080300015 | New_Event |  |  | Include | Wildlife | 103 | 2021-08-03 | 12360 | keep | 0 | Aug | 2021 | 0.0084183 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
ARECIBO | 2021-08-03 09:14 | 2021-08-03 17:00 | 8 | 007:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21080300035 | New_Event | Bad Weather | Include | Include | Weather | 466 | 2021-08-03 | 3728 | keep | 0 | Aug | 2021 | 0.0025391 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-08-03 09:19 | 2021-08-03 20:44 | 10 | 011:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 75 KVA X 75 KVA | M21080300019 | New_Event | Service Transformer Failure | Include | Include | Equipment | 685 | 2021-08-03 | 6850 | keep | 0 | Aug | 2021 | 0.0046655 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2021-08-03 09:21 | 2021-08-03 10:26 | 100 | 001:05 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA CAUSADO POR DESGANCHE | P21080300067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 65 | 2021-08-03 | 6500 | keep | 0 | Aug | 2021 | 0.0044271 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-08-03 09:27 | 2021-08-03 14:58 | 150 | 005:31 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | M21080300021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 331 | 2021-08-03 | 49650 | keep | 0 | Aug | 2021 | 0.033816 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
PONCE | 2021-08-03 09:47 | 2021-08-03 11:31 | 80 | 001:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA POR CONTACTO DE AVE | P21080300073 | New_Event |  |  | Include | Wildlife | 104 | 2021-08-03 | 8320 | keep | 0 | Aug | 2021 | 0.0056667 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-08-03 09:52 | 2021-08-03 13:10 | 1891 | 003:18 | S | LINEA DE TRANSMISION 38KV | AVERIA EN LA LINEA 3700 | C21080300062 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 198 | 2021-08-03 | 374418 | keep | 0 | Aug | 2021 | 0.25501 | 0.001288 | Sustained | FALSE | TRUE | Not_TMED_Event | 1891
HUMACAO | 2021-08-03 09:52 | 2021-08-03 13:10 | 1250 | 003:18 | S | LINEA DE TRANSMISION 38KV | AVERIA EN LA LINEA 3700 | C21080300062 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 198 | 2021-08-03 | 247500 | keep | 0 | Aug | 2021 | 0.16857 | 0.00085137 | Sustained | FALSE | TRUE | Not_TMED_Event | 1250
HUMACAO | 2021-08-03 09:52 | 2021-08-03 13:10 | 2141 | 003:18 | S | LINEA DE TRANSMISION 38KV | AVERIA EN LA LINEA 3700 | C21080300062 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 198 | 2021-08-03 | 423918 | keep | 0 | Aug | 2021 | 0.28873 | 0.0014582 | Sustained | FALSE | TRUE | Not_TMED_Event | 2141
HUMACAO | 2021-08-03 09:52 | 2021-08-03 13:10 | 1827 | 003:18 | S | LINEA DE TRANSMISION 38KV | AVERIA EN LA LINEA 3700 | C21080300062 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 198 | 2021-08-03 | 361746 | keep | 0 | Aug | 2021 | 0.24638 | 0.0012444 | Sustained | FALSE | TRUE | Not_TMED_Event | 1827
BARRANQUITAS | 2021-08-03 09:53 | 2021-08-03 09:55 | 1 | 000:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | LINEA SECUNDARIA SULFATADA SE REPARO WR 5882476 | C21080300000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2 | 2021-08-03 | 2 | keep | 0 | Aug | 2021 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | TRUE | Not_TMED_Event | 1
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 386 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BANCO 115 KVA JOBOS TC | P21080300136 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 52882 | keep | 0 | Aug | 2021 | 0.036018 | 0.0002629 | Sustained | FALSE | FALSE | Not_TMED_Event | 386
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 610 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BANCO 115 KVA JOBOS TC | P21080300136 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 83570 | keep | 0 | Aug | 2021 | 0.056919 | 0.00041547 | Sustained | FALSE | FALSE | Not_TMED_Event | 610
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 1785 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BANCO 115 KVA JOBOS TC | P21080300136 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 244545 | keep | 0 | Aug | 2021 | 0.16656 | 0.0012158 | Sustained | FALSE | FALSE | Not_TMED_Event | 1785
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 1233 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BANCO 115 KVA JOBOS TC | P21080300136 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 168921 | keep | 0 | Aug | 2021 | 0.11505 | 0.00083979 | Sustained | FALSE | FALSE | Not_TMED_Event | 1233
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 584 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KVA JOBOS TC | P21080300138 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 80008 | keep | 0 | Aug | 2021 | 0.054493 | 0.00039776 | Sustained | FALSE | FALSE | Not_TMED_Event | 584
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 1658 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KVA JOBOS TC | P21080300138 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 227146 | keep | 0 | Aug | 2021 | 0.15471 | 0.0011293 | Sustained | FALSE | FALSE | Not_TMED_Event | 1658
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 630 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KVA JOBOS TC | P21080300138 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 86310 | keep | 0 | Aug | 2021 | 0.058785 | 0.00042909 | Sustained | FALSE | FALSE | Not_TMED_Event | 630
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 4132 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115 KVA JOBOS TC | P21080300142 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 566084 | keep | 0 | Aug | 2021 | 0.38556 | 0.0028143 | Sustained | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 4279 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115 KVA JOBOS TC | P21080300142 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 586223 | keep | 0 | Aug | 2021 | 0.39927 | 0.0029144 | Sustained | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 1945 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115 KVA JOBOS TC | P21080300142 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 266465 | keep | 0 | Aug | 2021 | 0.18149 | 0.0013247 | Sustained | FALSE | FALSE | Not_TMED_Event | 1945
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 1173 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115 KVA JOBOS TC | P21080300104 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 160701 | keep | 0 | Aug | 2021 | 0.10945 | 0.00079892 | Sustained | FALSE | FALSE | Not_TMED_Event | 1173
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 215 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115 KVA JOBOS TC | P21080300104 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 29455 | keep | 0 | Aug | 2021 | 0.020062 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 464 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115 KVA JOBOS TC | P21080300104 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 63568 | keep | 0 | Aug | 2021 | 0.043296 | 0.00031603 | Sustained | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 2100 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KVA JOBOS TC | P21080300133 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 287700 | keep | 0 | Aug | 2021 | 0.19595 | 0.0014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 922 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KVA JOBOS TC | P21080300133 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 126314 | keep | 0 | Aug | 2021 | 0.086032 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 1676 | 002:17 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KVA JOBOS TC | P21080300133 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 229612 | keep | 0 | Aug | 2021 | 0.15639 | 0.0011415 | Sustained | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 2844 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KVA JOBOS TC | P21080300133 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 389628 | keep | 0 | Aug | 2021 | 0.26537 | 0.001937 | Sustained | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 2775 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BANCO DE 115KVA JOBOS TC | P21080300092 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 380175 | keep | 0 | Aug | 2021 | 0.25894 | 0.00189 | Sustained | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 1457 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BANCO DE 115KVA JOBOS TC | P21080300092 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 199609 | keep | 0 | Aug | 2021 | 0.13595 | 0.00099236 | Sustained | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 1086 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BANCO DE 115KVA JOBOS TC | P21080300092 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 148782 | keep | 0 | Aug | 2021 | 0.10133 | 0.00073967 | Sustained | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 2134 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BANCO DE 115KVA JOBOS TC | P21080300092 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 292358 | keep | 0 | Aug | 2021 | 0.19912 | 0.0014535 | Sustained | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 1464 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KVA JOBOS TC | P21080300132 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 200568 | keep | 0 | Aug | 2021 | 0.13661 | 0.00099712 | Sustained | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 1833 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KVA JOBOS TC | P21080300132 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 251121 | keep | 0 | Aug | 2021 | 0.17104 | 0.0012484 | Sustained | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 1565 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KVA JOBOS TC | P21080300132 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 214405 | keep | 0 | Aug | 2021 | 0.14603 | 0.0010659 | Sustained | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2021-08-03 09:58 | 2021-08-03 12:15 | 977 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KVA JOBOS TC | P21080300132 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 133849 | keep | 0 | Aug | 2021 | 0.091164 | 0.00066543 | Sustained | FALSE | FALSE | Not_TMED_Event | 977
PONCE | 2021-08-03 09:58 | 2021-08-03 12:15 | 1093 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KVA JOBOS TC | P21080300118 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 149741 | keep | 0 | Aug | 2021 | 0.10199 | 0.00074444 | Sustained | FALSE | FALSE | Not_TMED_Event | 1093
PONCE | 2021-08-03 09:58 | 2021-08-03 12:15 | 1067 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KVA JOBOS TC | P21080300118 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 146179 | keep | 0 | Aug | 2021 | 0.099562 | 0.00072673 | Sustained | FALSE | FALSE | Not_TMED_Event | 1067
PONCE | 2021-08-03 09:58 | 2021-08-03 12:15 | 836 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KVA JOBOS TC | P21080300118 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 114532 | keep | 0 | Aug | 2021 | 0.078007 | 0.0005694 | Sustained | FALSE | FALSE | Not_TMED_Event | 836
PONCE | 2021-08-03 09:58 | 2021-08-03 12:15 | 1339 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KVA JOBOS TC | P21080300118 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 183443 | keep | 0 | Aug | 2021 | 0.12494 | 0.00091199 | Sustained | FALSE | FALSE | Not_TMED_Event | 1339
PONCE | 2021-08-03 09:58 | 2021-08-03 12:15 | 1295 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KVA JOBOS TC | P21080300118 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 177415 | keep | 0 | Aug | 2021 | 0.12084 | 0.00088202 | Sustained | FALSE | FALSE | Not_TMED_Event | 1295
PONCE | 2021-08-03 09:58 | 2021-08-03 12:15 | 978 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KVA JOBOS TC | P21080300147 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 133986 | keep | 0 | Aug | 2021 | 0.091257 | 0.00066611 | Sustained | FALSE | FALSE | Not_TMED_Event | 978
PONCE | 2021-08-03 09:58 | 2021-08-03 12:15 | 1730 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KVA JOBOS TC | P21080300147 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 237010 | keep | 0 | Aug | 2021 | 0.16143 | 0.0011783 | Sustained | FALSE | FALSE | Not_TMED_Event | 1730
PONCE | 2021-08-03 09:58 | 2021-08-03 12:15 | 1320 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KVA JOBOS TC | P21080300145 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 180840 | keep | 0 | Aug | 2021 | 0.12317 | 0.00089905 | Sustained | FALSE | FALSE | Not_TMED_Event | 1320
PONCE | 2021-08-03 09:58 | 2021-08-03 12:15 | 274 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KVA JOBOS TC | P21080300145 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 37538 | keep | 0 | Aug | 2021 | 0.025567 | 0.00018662 | Sustained | FALSE | FALSE | Not_TMED_Event | 274
PONCE | 2021-08-03 09:58 | 2021-08-03 12:15 | 891 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KVA JOBOS TC | P21080300148 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 122067 | keep | 0 | Aug | 2021 | 0.083139 | 0.00060686 | Sustained | FALSE | FALSE | Not_TMED_Event | 891
PONCE | 2021-08-03 09:58 | 2021-08-03 12:15 | 527 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KVA JOBOS TC | P21080300148 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 72199 | keep | 0 | Aug | 2021 | 0.049174 | 0.00035894 | Sustained | FALSE | FALSE | Not_TMED_Event | 527
PONCE | 2021-08-03 09:58 | 2021-08-03 12:15 | 542 | 002:17 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BANCO 115KVA JOBOS TC | P21080300148 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 137 | 2021-08-03 | 74254 | keep | 0 | Aug | 2021 | 0.050574 | 0.00036915 | Sustained | FALSE | FALSE | Not_TMED_Event | 542
ARECIBO | 2021-08-03 10:00 | 2021-08-03 18:42 | 100 | 008:42 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR POSTE PRIMARIO | A21080300000 | New_Event | Defective Pole | Include | Include | Equipment | 522 | 2021-08-03 | 52200 | keep | 0 | Aug | 2021 | 0.035553 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-08-03 10:02 | 2021-08-03 20:50 | 40 | 010:48 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21080300072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 648 | 2021-08-03 | 25920 | keep | 0 | Aug | 2021 | 0.017654 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-08-03 10:04 | 2021-08-04 07:10 | 50 | 021:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X DE 100 EN CORTE DE LINEA AVE CRUZO LINEAS | P21080300093 | New_Event |  |  | Include | Wildlife | 1266 | 2021-08-03 | 63300 | keep | 0 | Aug | 2021 | 0.043113 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-08-03 10:07 | 2021-08-03 17:49 | 12 | 007:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO 100 PIES DE SECUNDARIA | B21080300073 | New_Event | Secondary Wire Down | Include | Include | Equipment | 462 | 2021-08-03 | 5544 | keep | 0 | Aug | 2021 | 0.003776 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-08-03 10:09 | 2021-08-03 16:29 | 11 | 006:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON LAS DOS BARRAS EN PEDESTAL | C21080300050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 380 | 2021-08-03 | 4180 | keep | 0 | Aug | 2021 | 0.002847 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2021-08-03 10:18 | 2021-08-05 16:20 | 1 | 054:02 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21080300069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3242 | 2021-08-03 | 3242 | keep | 0 | Aug | 2021 | 0.0022081 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-08-03 10:25 | 2021-08-03 15:34 | 100 | 005:09 | P | ESTRUCTURA AVERIADA | SE PASARON LINEAS PRIMARIAS A POSTE PRIMARIO NUEVO | M210803000 | New_Event | Defective Pole | Include | Include | Equipment | 309 | 2021-08-03 | 30900 | keep | 0 | Aug | 2021 | 0.021046 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-08-03 10:37 | 2021-08-03 12:07 | 1 | 001:30 | P | OTRAS CAUSAS | 2 X 25 Y 2 X 20 EN TRANSFORMADORES PROBLEMA DEL CLIENTE | R21080300024 | New_Event | Other Causes | Include | Include | Other | 90 | 2021-08-03 | 90 | keep | 0 | Aug | 2021 | 6.1299e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-08-03 11:00 | 2021-08-03 18:28 | 70 | 007:28 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21080300025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 448 | 2021-08-03 | 31360 | keep | 0 | Aug | 2021 | 0.021359 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-08-03 11:10 | 2021-08-03 12:30 | 15 | 001:20 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 50 KVA X 50 KVA | M21080300028 | New_Event | Service Transformer Failure | Include | Include | Equipment | 80 | 2021-08-03 | 1200 | keep | 0 | Aug | 2021 | 0.00081731 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-08-03 11:25 | 2021-08-03 19:46 | 11 | 008:21 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA X 37.5KVA | C21080300074 | New_Event | Service Transformer Failure | Include | Include | Equipment | 501 | 2021-08-03 | 5511 | keep | 0 | Aug | 2021 | 0.0037535 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2021-08-03 11:48 | 2021-08-03 19:02 | 25 | 007:14 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA PRINCIPAL Y 1 X 40 EN CORTE DE LINEA INTERMEDIO SE REALIZO DESGANCHE PRIMARIO | B21080300098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 434 | 2021-08-03 | 10850 | keep | 0 | Aug | 2021 | 0.0073899 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-08-03 11:51 | 2021-08-03 11:52 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21080300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-03 | 393 | keep | 0 | Aug | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2021-08-03 12:04 | 2021-08-03 12:05 | 6285 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21080300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-03 | 6285 | keep | 0 | Aug | 2021 | 0.0042807 | 0.0042807 | Momentary | FALSE | FALSE | Not_TMED_Event | 6285
VEGA BAJA | 2021-08-03 12:04 | 2021-08-03 16:36 | 10 | 004:32 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | B21080300102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 272 | 2021-08-03 | 2720 | keep | 0 | Aug | 2021 | 0.0018526 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
VEGA BAJA | 2021-08-03 12:04 | 2021-08-03 18:55 | 20 | 006:51 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | B21080300103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 411 | 2021-08-03 | 8220 | keep | 0 | Aug | 2021 | 0.0055986 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
VEGA BAJA | 2021-08-03 12:08 | 2021-08-03 13:58 | 1310 | 001:50 | T | DESGANCHE | SE CERRO POR SCADA SE RETIRO RAMA CRUZANDO LINEAS | B21080300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2021-08-03 | 144100 | keep | 0 | Aug | 2021 | 0.098146 | 0.00089224 | Sustained | FALSE | TRUE | Not_TMED_Event | 1310
UTUADO | 2021-08-03 12:14 | 2021-08-03 18:40 | 25 | 006:26 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | A21080300066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 386 | 2021-08-03 | 9650 | keep | 0 | Aug | 2021 | 0.0065726 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CAGUAS | 2021-08-03 12:16 | 2021-08-03 16:38 | 9 | 004:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR REPARO SECUNDARIA AVERIADA | C21080300086 | New_Event | Secondary Wire Down | Include | Include | Equipment | 262 | 2021-08-03 | 2358 | keep | 0 | Aug | 2021 | 0.001606 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2021-08-03 12:20 | 2021-08-03 15:30 | 25 | 003:10 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | M21080300043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2021-08-03 | 4750 | keep | 0 | Aug | 2021 | 0.0032352 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-08-03 12:20 | 2021-08-03 13:47 | 3 | 001:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA DE TRANSFORMADOR AVERIADA | M21080201332 | New_Event | Cutout Failure | Include | Include | Equipment | 87 | 2021-08-03 | 261 | keep | 0 | Aug | 2021 | 0.00017777 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2021-08-03 12:28 | 2021-08-03 13:47 | 1905 | 001:19 | T | DESGANCHE | SE REMOVIO ARBOL SOBRE LINEAS | P21080300230 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2021-08-03 | 150495 | keep | 0 | Aug | 2021 | 0.1025 | 0.0012975 | Sustained | FALSE | TRUE | Not_TMED_Event | 1905
BAYAMON | 2021-08-03 12:28 | 2021-08-04 00:34 | 1800 | 012:06 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO ALIMENTADOR LEVANTANDO 3 FASES DE TRONCAL Y REMPLAZANDO MACHETE QUEMADO EN CARRETERA 854 SECTOR MEDIA LUNA | B21080300282 | New_Event | Wire Down | Include | Include | Equipment | 726 | 2021-08-03 | 1306800 | keep | 0 | Aug | 2021 | 0.89006 | 0.001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 1800
BAYAMON | 2021-08-03 12:28 | 2021-08-03 17:03 | 2324 | 004:35 | S | PROTECCION DEFECTUOSA | DISPARO DE SUBESTACION POR AVERIA EN ALIMENTADOR 02 QUE INTERRUPTOR NO DETECTO SE SECCIONALIZO Y SE DIO SERVICIO A SUBESTACION PERSONAL DE SUBESTACIONES REPARO INTERRUPTOR | B21080300116 | New_Event | Protection Miscoordination | Include | Include | Other | 275 | 2021-08-03 | 639100 | keep | 0 | Aug | 2021 | 0.43529 | 0.0015829 | Sustained | FALSE | FALSE | Not_TMED_Event | 2324
VEGA BAJA | 2021-08-03 12:28 | 2021-08-03 17:03 | 1570 | 004:35 | S | PROTECCION DEFECTUOSA | DISPARO DE SUBESTACION POR AVERIA EN ALIMENTADOR 02 QUE INTERRUPTOR NO DETECTO SE SECCIONALIZO Y SE DIO SERVICIO A SUBESTACION PERSONAL DE SUBESTACIONES REPARO INTERRUPTOR | B21080300116 | New_Event | Protection Miscoordination | Include | Include | Other | 275 | 2021-08-03 | 431750 | keep | 0 | Aug | 2021 | 0.29406 | 0.0010693 | Sustained | FALSE | FALSE | Not_TMED_Event | 1570
SAN JUAN | 2021-08-03 12:36 | 2021-08-03 16:49 | 150 | 004:13 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA | S21080300090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 253 | 2021-08-03 | 37950 | keep | 0 | Aug | 2021 | 0.025848 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
FAJARDO | 2021-08-03 12:37 | 2021-08-03 13:35 | 1 | 000:58 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21080300030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2021-08-03 | 58 | keep | 0 | Aug | 2021 | 3.9504e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
AGUADILLA | 2021-08-03 12:41 | 2021-08-03 12:43 | 569 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21080300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-08-03 | 1138 | keep | 0 | Aug | 2021 | 0.00077509 | 0.00038754 | Momentary | FALSE | TRUE | Not_TMED_Event | 569
AGUADILLA | 2021-08-03 12:41 | 2021-08-03 12:43 | 1245 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21080300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-08-03 | 2490 | keep | 0 | Aug | 2021 | 0.0016959 | 0.00084796 | Momentary | FALSE | TRUE | Not_TMED_Event | 1245
AGUADILLA | 2021-08-03 12:41 | 2021-08-03 12:43 | 1155 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21080300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-08-03 | 2310 | keep | 0 | Aug | 2021 | 0.0015733 | 0.00078667 | Momentary | FALSE | TRUE | Not_TMED_Event | 1155
AGUADILLA | 2021-08-03 12:41 | 2021-08-03 12:43 | 867 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21080300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-08-03 | 1734 | keep | 0 | Aug | 2021 | 0.001181 | 0.00059051 | Momentary | FALSE | TRUE | Not_TMED_Event | 867
AGUADILLA | 2021-08-03 12:41 | 2021-08-03 12:43 | 257 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21080300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-08-03 | 514 | keep | 0 | Aug | 2021 | 0.00035008 | 0.00017504 | Momentary | FALSE | TRUE | Not_TMED_Event | 257
AGUADILLA | 2021-08-03 12:41 | 2021-08-03 12:43 | 1336 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21080300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-08-03 | 2672 | keep | 0 | Aug | 2021 | 0.0018199 | 0.00090994 | Momentary | FALSE | TRUE | Not_TMED_Event | 1336
AGUADILLA | 2021-08-03 12:41 | 2021-08-03 12:43 | 3315 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21080300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-08-03 | 6630 | keep | 0 | Aug | 2021 | 0.0045157 | 0.0022578 | Momentary | FALSE | TRUE | Not_TMED_Event | 3315
AGUADILLA | 2021-08-03 12:41 | 2021-08-03 12:43 | 1718 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2500 | M21080300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-08-03 | 3436 | keep | 0 | Aug | 2021 | 0.0023402 | 0.0011701 | Momentary | FALSE | TRUE | Not_TMED_Event | 1718
AGUADILLA | 2021-08-03 12:46 | 2021-08-03 15:53 | 569 | 003:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21080300064 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 187 | 2021-08-03 | 106403 | keep | 0 | Aug | 2021 | 0.072471 | 0.00038754 | Sustained | FALSE | TRUE | Not_TMED_Event | 569
AGUADILLA | 2021-08-03 12:46 | 2021-08-03 15:53 | 1245 | 003:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21080300064 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 187 | 2021-08-03 | 232815 | keep | 0 | Aug | 2021 | 0.15857 | 0.00084796 | Sustained | FALSE | TRUE | Not_TMED_Event | 1245
AGUADILLA | 2021-08-03 12:46 | 2021-08-03 15:53 | 1155 | 003:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21080300064 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 187 | 2021-08-03 | 215985 | keep | 0 | Aug | 2021 | 0.14711 | 0.00078667 | Sustained | FALSE | TRUE | Not_TMED_Event | 1155
AGUADILLA | 2021-08-03 12:46 | 2021-08-03 19:23 | 867 | 006:37 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21080300064 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 397 | 2021-08-03 | 344199 | keep | 0 | Aug | 2021 | 0.23443 | 0.00059051 | Sustained | FALSE | TRUE | Not_TMED_Event | 867
AGUADILLA | 2021-08-03 12:46 | 2021-08-03 19:23 | 257 | 006:37 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21080300064 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 397 | 2021-08-03 | 102029 | keep | 0 | Aug | 2021 | 0.069491 | 0.00017504 | Sustained | FALSE | TRUE | Not_TMED_Event | 257
AGUADILLA | 2021-08-03 12:46 | 2021-08-03 19:23 | 1336 | 006:37 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21080300064 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 397 | 2021-08-03 | 530392 | keep | 0 | Aug | 2021 | 0.36125 | 0.00090994 | Sustained | FALSE | TRUE | Not_TMED_Event | 1336
AGUADILLA | 2021-08-03 12:46 | 2021-08-03 15:53 | 3315 | 003:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21080300064 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 187 | 2021-08-03 | 619905 | keep | 0 | Aug | 2021 | 0.42221 | 0.0022578 | Sustained | FALSE | TRUE | Not_TMED_Event | 3315
AGUADILLA | 2021-08-03 12:46 | 2021-08-03 15:53 | 1718 | 003:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21080300064 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 187 | 2021-08-03 | 321266 | keep | 0 | Aug | 2021 | 0.21881 | 0.0011701 | Sustained | FALSE | TRUE | Not_TMED_Event | 1718
BAYAMON | 2021-08-03 13:21 | 2021-08-03 15:59 | 1 | 002:38 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B21080300169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 158 | 2021-08-03 | 158 | keep | 0 | Aug | 2021 | 0.00010761 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-08-03 13:37 | 2021-08-03 17:00 | 10 | 003:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21080300076 | New_Event | Bad Weather | Include | Include | Weather | 203 | 2021-08-03 | 2030 | keep | 0 | Aug | 2021 | 0.0013826 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
SAN JUAN | 2021-08-03 13:40 | 2021-08-03 17:30 | 40 | 003:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21080300108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 230 | 2021-08-03 | 9200 | keep | 0 | Aug | 2021 | 0.0062661 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-08-03 13:41 | 2021-08-03 17:23 | 50 | 003:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN RISER POR CONTACTO DE AVE | P21080300235 | New_Event |  |  | Include | Wildlife | 222 | 2021-08-03 | 11100 | keep | 0 | Aug | 2021 | 0.0075602 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-08-03 13:45 | 2021-08-03 15:00 | 10 | 001:15 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21080300004 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 75 | 2021-08-03 | 750 | keep | 0 | Aug | 2021 | 0.00051082 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-08-03 13:49 | 2021-08-03 18:50 | 35 | 005:01 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE PRIMARIO | B21080300183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 301 | 2021-08-03 | 10535 | keep | 0 | Aug | 2021 | 0.0071753 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
SAN JUAN | 2021-08-03 13:56 | 2021-08-04 10:26 | 70 | 020:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | R21080300031 | New_Event | Cutout Failure | Include | Include | Equipment | 1230 | 2021-08-03 | 86100 | keep | 0 | Aug | 2021 | 0.058642 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BARRANQUITAS | 2021-08-03 14:29 | 2021-08-03 22:00 | 50 | 007:31 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C21080300107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 451 | 2021-08-03 | 22550 | keep | 0 | Aug | 2021 | 0.015359 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-03 14:29 | 2021-08-03 20:40 | 1 | 006:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | A21080300079 | New_Event | Bad Weather | Include | Include | Weather | 371 | 2021-08-03 | 371 | keep | 0 | Aug | 2021 | 0.00025269 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-08-03 14:33 | 2021-08-03 17:30 | 10 | 002:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21080201248 | New_Event | Secondary Wire Down | Include | Include | Equipment | 177 | 2021-08-03 | 1770 | keep | 0 | Aug | 2021 | 0.0012055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-08-03 14:36 | 2021-08-03 14:40 | 1891 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | C21080300108 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-08-03 | 7564 | keep | 0 | Aug | 2021 | 0.0051518 | 0.001288 | Momentary | FALSE | TRUE | Not_TMED_Event | 1891
HUMACAO | 2021-08-03 14:36 | 2021-08-03 14:40 | 1250 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | C21080300108 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-08-03 | 5000 | keep | 0 | Aug | 2021 | 0.0034055 | 0.00085137 | Momentary | FALSE | TRUE | Not_TMED_Event | 1250
HUMACAO | 2021-08-03 14:36 | 2021-08-03 14:40 | 2141 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | C21080300108 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-08-03 | 8564 | keep | 0 | Aug | 2021 | 0.0058329 | 0.0014582 | Momentary | FALSE | TRUE | Not_TMED_Event | 2141
HUMACAO | 2021-08-03 14:36 | 2021-08-03 14:40 | 1827 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | C21080300108 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-08-03 | 7308 | keep | 0 | Aug | 2021 | 0.0049774 | 0.0012444 | Momentary | FALSE | TRUE | Not_TMED_Event | 1827
AGUADILLA | 2021-08-03 14:36 | 2021-08-03 16:59 | 1827 | 002:23 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR POR CAJAS PRIMARIAS QUEMADAS | M21080300097 | New_Event | Cutout Failure | Include | Include | Equipment | 143 | 2021-08-03 | 261261 | keep | 0 | Aug | 2021 | 0.17794 | 0.0012444 | Sustained | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2021-08-03 14:36 | 2021-08-03 19:13 | 1047 | 004:37 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR 7011-01 EL CUAL ESTA LLEVANDO LA CARGA DEL 7011-02 EL CUAL TENIA CAJAS PRIMARIAS QUEMADAS | M21080300097 | New_Event | Cutout Failure | Include | Include | Equipment | 277 | 2021-08-03 | 290019 | keep | 0 | Aug | 2021 | 0.19753 | 0.00071311 | Sustained | FALSE | FALSE | Not_TMED_Event | 1047
AGUADILLA | 2021-08-03 15:05 | 2021-08-03 22:09 | 20 | 007:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21080300119 | New_Event | Bad Weather | Include | Include | Weather | 424 | 2021-08-03 | 8480 | keep | 0 | Aug | 2021 | 0.0057757 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-08-03 15:07 | 2021-08-03 15:08 | 1467 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21080300111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-03 | 1467 | keep | 0 | Aug | 2021 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
PONCE | 2021-08-03 15:07 | 2021-08-03 19:48 | 100 | 004:41 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P21080300246 | New_Event | Vegetation Contact | Include | Include | Vegetation | 281 | 2021-08-03 | 28100 | keep | 0 | Aug | 2021 | 0.019139 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-08-03 15:18 | 2021-08-03 19:43 | 10 | 004:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE EN TRANSFORMADOR | A21080300083 | New_Event | Wire Down | Include | Include | Equipment | 265 | 2021-08-03 | 2650 | keep | 0 | Aug | 2021 | 0.0018049 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-08-03 15:25 | 2021-08-05 15:26 | 10 | 048:01 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR | S21080300157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2881 | 2021-08-03 | 28810 | keep | 0 | Aug | 2021 | 0.019622 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-08-03 15:31 | 2021-08-04 12:35 | 50 | 021:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO | M21080300133 | New_Event | Wire Down | Include | Include | Equipment | 1264 | 2021-08-03 | 63200 | keep | 0 | Aug | 2021 | 0.043045 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-08-03 15:34 | 2021-08-03 15:38 | 2234 | 000:04 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | B21080300218 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-08-03 | 8936 | keep | 0 | Aug | 2021 | 0.0060863 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
CANOVANAS | 2021-08-03 15:37 | 2021-08-03 15:38 | 4188 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21080300039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-03 | 4188 | keep | 0 | Aug | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
BARRANQUITAS | 2021-08-03 15:39 | 2021-08-04 10:46 | 14 | 019:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | C21080300117 | New_Event | Cutout Failure | Include | Include | Equipment | 1147 | 2021-08-03 | 16058 | keep | 0 | Aug | 2021 | 0.010937 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2021-08-03 15:57 | 2021-08-03 17:30 | 12 | 001:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21080300088 | New_Event | Bad Weather | Include | Include | Weather | 93 | 2021-08-03 | 1116 | keep | 0 | Aug | 2021 | 0.0007601 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2021-08-03 16:04 | 2021-08-03 17:45 | 9 | 001:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21080300091 | New_Event | Bad Weather | Include | Include | Weather | 101 | 2021-08-03 | 909 | keep | 0 | Aug | 2021 | 0.00061912 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2021-08-03 16:08 | 2021-08-03 19:00 | 80 | 002:52 | P | ESTRUCTURA AVERIADA | 1 X 80 EN CORTE DE LINEA SE ABRIO PUENTES PARA SECCIONALIZAR POSTE PRIMARIO AVERIADO | A21080300092 | New_Event | Defective Pole | Include | Include | Equipment | 172 | 2021-08-03 | 13760 | keep | 0 | Aug | 2021 | 0.0093719 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-08-03 16:10 | 2021-08-03 19:42 | 60 | 003:32 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO PALMA SOBRE LINEA | C21080300119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2021-08-03 | 12720 | keep | 0 | Aug | 2021 | 0.0086635 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-08-03 16:11 | 2021-08-03 18:36 | 1 | 002:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | 3 X 50 EN CORTE DE LINEA REEMPLAZO AISLADOR | C21080300120 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 145 | 2021-08-03 | 145 | keep | 0 | Aug | 2021 | 9.8759e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-08-03 16:20 | 2021-08-04 09:10 | 12 | 016:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21080300136 | New_Event | Bad Weather | Include | Include | Weather | 1010 | 2021-08-03 | 12120 | keep | 0 | Aug | 2021 | 0.0082549 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-08-03 16:20 | 2021-08-03 19:30 | 30 | 003:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | A21080300097 | New_Event | Bad Weather | Include | Include | Weather | 190 | 2021-08-03 | 5700 | keep | 0 | Aug | 2021 | 0.0038822 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
YAUCO | 2021-08-03 16:22 | 2021-08-03 19:44 | 30 | 003:22 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | P21080300263 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2021-08-03 | 6060 | keep | 0 | Aug | 2021 | 0.0041274 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-08-03 16:26 | 2021-08-03 16:33 | 2113 | 000:07 | T | CABLE SOTERRADO AVERIADO | PERSONAL REALIZANDO PRUEBA A SISTEMA SOTERRADO OCASIONARON DISPARO DE INTERRUPTOR SE LE DIO PRUEBA LUEGO DE VERIFICAR PERSONAL FUERA DE LINEA Y QUEDO EN SERVICIO | P21080300267 | New_Event | UG Cable Fault | Include | Include | Equipment | 7 | 2021-08-03 | 14791 | keep | 0 | Aug | 2021 | 0.010074 | 0.0014392 | Sustained | FALSE | TRUE | Not_TMED_Event | 2113
ARECIBO | 2021-08-03 16:35 | 2021-08-03 18:40 | 40 | 002:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | A21080300101 | New_Event | Bad Weather | Include | Include | Weather | 125 | 2021-08-03 | 5000 | keep | 0 | Aug | 2021 | 0.0034055 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-08-03 16:37 | 2021-08-04 10:38 | 159 | 018:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA CRUCE POR AVE | C21080300125 | New_Event |  |  | Include | Wildlife | 1081 | 2021-08-03 | 171879 | keep | 0 | Aug | 2021 | 0.11707 | 0.00010829 | Sustained | FALSE | TRUE | Not_TMED_Event | 159
PONCE | 2021-08-03 16:44 | 2021-08-03 16:45 | 2113 | 000:01 | T | CABLE SOTERRADO AVERIADO | PERSONAL REALIZANDO PRUEBA A SISTEMA SOTERRADO OCASIONARON DISPARO DE INTERRUPTOR SE LE DIO PRUEBA LUEGO DE VERIFICAR PERSONAL FUERA DE LINEA Y QUEDO EN SERVICIO | P21080300275 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1 | 2021-08-03 | 2113 | keep | 0 | Aug | 2021 | 0.0014392 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-08-03 16:44 | 2021-08-03 19:10 | 100 | 002:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | A21080300102 | New_Event | Bad Weather | Include | Include | Weather | 146 | 2021-08-03 | 14600 | keep | 0 | Aug | 2021 | 0.009944 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-08-03 16:50 | 2021-08-04 00:55 | 14 | 008:05 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE POSTE SECUNDARIO | M21080300000 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 485 | 2021-08-03 | 6790 | keep | 0 | Aug | 2021 | 0.0046246 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
GUAYAMA | 2021-08-03 17:05 | 2021-08-03 17:47 | 2100 | 000:42 | S | LINEA DE TRANSMISION 38KV | CCE ABRIO 3700 | P210803000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 42 | 2021-08-03 | 88200 | keep | 0 | Aug | 2021 | 0.060073 | 0.0014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2021-08-03 17:05 | 2021-08-03 17:47 | 922 | 000:42 | S | LINEA DE TRANSMISION 38KV | CCE ABRIO 3700 | P210803000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 42 | 2021-08-03 | 38724 | keep | 0 | Aug | 2021 | 0.026375 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2021-08-03 17:05 | 2021-08-03 17:47 | 1676 | 000:42 | T | LINEA DE TRANSMISION 38KV | CCE ABRIO 3700 | P210803000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 42 | 2021-08-03 | 70392 | keep | 0 | Aug | 2021 | 0.047944 | 0.0011415 | Sustained | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2021-08-03 17:05 | 2021-08-03 17:47 | 2844 | 000:42 | S | LINEA DE TRANSMISION 38KV | CCE ABRIO 3700 | P210803000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 42 | 2021-08-03 | 119448 | keep | 0 | Aug | 2021 | 0.081355 | 0.001937 | Sustained | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2021-08-03 17:05 | 2021-08-03 17:47 | 2775 | 000:42 | S | LINEA DE TRANSMISION 38KV | CCE ABRIO 3700 | P210803000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 42 | 2021-08-03 | 116550 | keep | 0 | Aug | 2021 | 0.079382 | 0.00189 | Sustained | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2021-08-03 17:05 | 2021-08-03 17:47 | 1457 | 000:42 | S | LINEA DE TRANSMISION 38KV | CCE ABRIO 3700 | P210803000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 42 | 2021-08-03 | 61194 | keep | 0 | Aug | 2021 | 0.041679 | 0.00099236 | Sustained | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2021-08-03 17:05 | 2021-08-03 17:47 | 1086 | 000:42 | S | LINEA DE TRANSMISION 38KV | CCE ABRIO 3700 | P210803000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 42 | 2021-08-03 | 45612 | keep | 0 | Aug | 2021 | 0.031066 | 0.00073967 | Sustained | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2021-08-03 17:05 | 2021-08-03 17:47 | 2134 | 000:42 | S | LINEA DE TRANSMISION 38KV | CCE ABRIO 3700 | P210803000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 42 | 2021-08-03 | 89628 | keep | 0 | Aug | 2021 | 0.061045 | 0.0014535 | Sustained | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2021-08-03 17:05 | 2021-08-03 17:47 | 1464 | 000:42 | S | LINEA DE TRANSMISION 38KV | CCE ABRIO 3700 | P210803000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 42 | 2021-08-03 | 61488 | keep | 0 | Aug | 2021 | 0.041879 | 0.00099712 | Sustained | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2021-08-03 17:05 | 2021-08-03 17:47 | 1833 | 000:42 | S | LINEA DE TRANSMISION 38KV | CCE ABRIO 3700 | P210803000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 42 | 2021-08-03 | 76986 | keep | 0 | Aug | 2021 | 0.052435 | 0.0012484 | Sustained | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2021-08-03 17:05 | 2021-08-03 17:47 | 1565 | 000:42 | S | LINEA DE TRANSMISION 38KV | CCE ABRIO 3700 | P210803000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 42 | 2021-08-03 | 65730 | keep | 0 | Aug | 2021 | 0.044768 | 0.0010659 | Sustained | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2021-08-03 17:05 | 2021-08-03 17:47 | 977 | 000:42 | S | LINEA DE TRANSMISION 38KV | CCE ABRIO 3700 | P210803000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 42 | 2021-08-03 | 41034 | keep | 0 | Aug | 2021 | 0.027948 | 0.00066543 | Sustained | FALSE | FALSE | Not_TMED_Event | 977
BAYAMON | 2021-08-03 17:35 | 2021-08-03 18:02 | 20 | 000:27 | P | DESGANCHE | 1 X 40 EN RISER SE RETIRO ENREDADERA | S21080300132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 27 | 2021-08-03 | 540 | keep | 0 | Aug | 2021 | 0.00036779 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-08-03 17:42 | 2021-08-03 19:12 | 40 | 001:30 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA PRINCIPAL Y 1 X 80 EN CORTE DE LINEA INTERMEDIO | B21080300242 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 90 | 2021-08-03 | 3600 | keep | 0 | Aug | 2021 | 0.0024519 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-08-03 18:08 | 2021-08-04 11:07 | 50 | 016:59 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | B21080300249 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1019 | 2021-08-03 | 50950 | keep | 0 | Aug | 2021 | 0.034702 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-08-03 18:09 | 2021-08-04 14:52 | 20 | 020:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR | C21080300132 | New_Event |  |  | Include | Wildlife | 1243 | 2021-08-03 | 24860 | keep | 0 | Aug | 2021 | 0.016932 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-08-03 18:10 | 2021-08-04 17:08 | 1 | 022:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON 2 CAJAS PRIMARIAS | B21080300250 | New_Event | Cutout Failure | Include | Include | Equipment | 1378 | 2021-08-03 | 1378 | keep | 0 | Aug | 2021 | 0.00093855 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-08-03 18:15 | 2021-08-04 12:00 | 10 | 017:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA X 50 KVA | A21080300112 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1065 | 2021-08-03 | 10650 | keep | 0 | Aug | 2021 | 0.0072537 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-03 18:22 | 2021-08-03 20:20 | 100 | 001:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | A21080300118 | New_Event | Bad Weather | Include | Include | Weather | 118 | 2021-08-03 | 11800 | keep | 0 | Aug | 2021 | 0.0080369 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-08-03 18:27 | 2021-08-04 10:09 | 76 | 015:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21080300135 | New_Event | Bad Weather | Include | Include | Weather | 942 | 2021-08-03 | 71592 | keep | 0 | Aug | 2021 | 0.048761 | 5.1763e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 76
VEGA BAJA | 2021-08-03 18:28 | 2021-08-03 18:29 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21080300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-03 | 1310 | keep | 0 | Aug | 2021 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
ARECIBO | 2021-08-03 18:36 | 2021-08-04 10:00 | 8 | 015:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21080300117 | New_Event | Bad Weather | Include | Include | Weather | 924 | 2021-08-03 | 7392 | keep | 0 | Aug | 2021 | 0.0050347 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-08-03 18:48 | 2021-08-03 21:21 | 10 | 002:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA Y REALIZAR DESGANCHE | S21080300027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 153 | 2021-08-03 | 1530 | keep | 0 | Aug | 2021 | 0.0010421 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-08-03 19:03 | 2021-08-03 19:04 | 1428 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21080300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-03 | 1428 | keep | 0 | Aug | 2021 | 0.0009726 | 0.0009726 | Momentary | FALSE | FALSE | Not_TMED_Event | 1428
MAYAGÃœEZ | 2021-08-03 19:13 | 2021-08-03 20:10 | 70 | 000:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | M21080300200 | New_Event | Bad Weather | Include | Include | Weather | 57 | 2021-08-03 | 3990 | keep | 0 | Aug | 2021 | 0.0027176 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
AGUADILLA | 2021-08-03 19:13 | 2021-08-03 19:18 | 1827 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR AL OPERAR MACHETES SOLIDOS | M21080300202 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-08-03 | 9135 | keep | 0 | Aug | 2021 | 0.0062218 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2021-08-03 19:13 | 2021-08-03 19:18 | 1047 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR AL OPERAR MACHETES SOLIDOS | M21080300202 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-08-03 | 5235 | keep | 0 | Aug | 2021 | 0.0035655 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
MAYAGÃœEZ | 2021-08-03 19:32 | 2021-08-03 19:37 | 6285 | 000:05 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR PARA PODER OPERAR MACHETES SOLIDOS ABIERTOS POR AVERIA DE OVERHEAD DE LINEA 2500 SOBRE DISTRIBUCION | M21080300210 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-08-03 | 31425 | keep | 0 | Aug | 2021 | 0.021403 | 0.0042807 | Momentary | FALSE | TRUE | Not_TMED_Event | 6285
BAYAMON | 2021-08-03 19:35 | 2021-08-03 20:03 | 34 | 000:28 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR 1512-04 PARA REEMPLAZAR MACHETE QUEMADO LLEVANDO LA CARGA DEL 1512-05 Y 1910-02 | S21080300000 | New_Event | Switch Failure | Include | Include | Equipment | 28 | 2021-08-03 | 952 | keep | 0 | Aug | 2021 | 0.0006484 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
BAYAMON | 2021-08-03 19:35 | 2021-08-03 20:03 | 19 | 000:28 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA REEMPLAZAR MACHETE QUEMADO CARGA POR EL 1512-04 | S21080300000 | New_Event | Switch Failure | Include | Include | Equipment | 28 | 2021-08-03 | 532 | keep | 0 | Aug | 2021 | 0.00036234 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
MAYAGÃœEZ | 2021-08-03 19:37 | 2021-08-03 20:30 | 100 | 000:53 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21080300162 | New_Event | Bad Weather | Include | Include | Weather | 53 | 2021-08-03 | 5300 | keep | 0 | Aug | 2021 | 0.0036098 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
YAUCO | 2021-08-03 19:38 | 2021-08-03 20:55 | 40 | 001:17 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA POR DESGANCHE | P21080300300 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2021-08-03 | 3080 | keep | 0 | Aug | 2021 | 0.0020978 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-08-03 19:40 | 2021-08-03 22:16 | 30 | 002:36 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE DE ENREDADERA | B21080300267 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2021-08-03 | 4680 | keep | 0 | Aug | 2021 | 0.0031875 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
VEGA BAJA | 2021-08-03 19:41 | 2021-08-03 19:42 | 1570 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B32108030000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-03 | 1570 | keep | 0 | Aug | 2021 | 0.0010693 | 0.0010693 | Momentary | FALSE | FALSE | Not_TMED_Event | 1570
ARECIBO | 2021-08-03 19:46 | 2021-08-03 21:19 | 200 | 001:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ABIERTO | A21080300129 | New_Event | Wire Down | Include | Include | Equipment | 93 | 2021-08-03 | 18600 | keep | 0 | Aug | 2021 | 0.012668 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2021-08-03 20:00 | 2021-08-03 20:01 | 1570 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B32108030000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-03 | 1570 | keep | 0 | Aug | 2021 | 0.0010693 | 0.0010693 | Momentary | FALSE | FALSE | Not_TMED_Event | 1570
CANOVANAS | 2021-08-03 20:03 | 2021-08-04 12:18 | 20 | 016:15 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REMPLAZO TERMINACION QUEMADA EN RISER | R21080300050 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 975 | 2021-08-03 | 19500 | keep | 0 | Aug | 2021 | 0.013281 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-08-03 20:26 | 2021-08-04 10:26 | 100 | 014:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | R21080300051 | New_Event |  |  | Include | Wildlife | 840 | 2021-08-03 | 84000 | keep | 0 | Aug | 2021 | 0.057212 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-08-03 20:26 | 2021-08-04 12:47 | 50 | 016:21 | P | ESTRUCTURA AVERIADA | 2 X 40 EN CORTE DE LINEA POSTE PRIMARIO PARTIDO SE SECCIONALISO Y QUEDARON 4 CLIENTES SIN SERVICIO | P21080300303 | New_Event | Defective Pole | Include | Include | Equipment | 981 | 2021-08-03 | 49050 | keep | 0 | Aug | 2021 | 0.033408 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-03 20:44 | 2021-08-03 20:45 | 1145 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21080300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-03 | 1145 | keep | 0 | Aug | 2021 | 0.00077985 | 0.00077985 | Momentary | FALSE | FALSE | Not_TMED_Event | 1145
MAYAGÃœEZ | 2021-08-03 20:44 | 2021-08-03 20:45 | 528 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M21080300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-03 | 528 | keep | 0 | Aug | 2021 | 0.00035962 | 0.00035962 | Momentary | FALSE | TRUE | Not_TMED_Event | 528
MAYAGÃœEZ | 2021-08-03 20:44 | 2021-08-03 20:45 | 4664 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M21080300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-03 | 4664 | keep | 0 | Aug | 2021 | 0.0031766 | 0.0031766 | Momentary | FALSE | TRUE | Not_TMED_Event | 4664
MAYAGÃœEZ | 2021-08-03 20:44 | 2021-08-03 20:45 | 2067 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M21080300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-03 | 2067 | keep | 0 | Aug | 2021 | 0.0014078 | 0.0014078 | Momentary | FALSE | TRUE | Not_TMED_Event | 2067
MAYAGÃœEZ | 2021-08-03 20:44 | 2021-08-04 00:02 | 220 | 003:18 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21080300218 | New_Event | Bad Weather | Include | Include | Weather | 198 | 2021-08-03 | 43560 | keep | 0 | Aug | 2021 | 0.029669 | 0.00014984 | Sustained | FALSE | TRUE | Not_TMED_Event | 220
MAYAGÃœEZ | 2021-08-03 20:44 | 2021-08-03 20:45 | 1352 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M21080300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-03 | 1352 | keep | 0 | Aug | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | TRUE | Not_TMED_Event | 1352
YAUCO | 2021-08-03 20:45 | 2021-08-04 00:42 | 770 | 003:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ABIERTO EN SALIDA DE ALIMENTADOR | P21080300304 | New_Event | Wire Down | Include | Include | Equipment | 237 | 2021-08-03 | 182490 | keep | 0 | Aug | 2021 | 0.12429 | 0.00052444 | Sustained | FALSE | FALSE | Not_TMED_Event | 770
MAYAGÃœEZ | 2021-08-03 20:45 | 2021-08-05 18:50 | 10 | 046:05 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 75 KVA X LO MISMO | M21080300019 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2765 | 2021-08-03 | 27650 | keep | 0 | Aug | 2021 | 0.018832 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-08-03 21:18 | 2021-08-03 21:19 | 1570 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B32108030000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-03 | 1570 | keep | 0 | Aug | 2021 | 0.0010693 | 0.0010693 | Momentary | FALSE | FALSE | Not_TMED_Event | 1570
ARECIBO | 2021-08-03 21:19 | 2021-08-03 21:30 | 2366 | 000:11 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR A PETICION SUP. CARLOS SOTO PARA CERRAR PUENTE PRIMARIO | A21080300138 | Additional_clients | Wire Down | Include | Include | Equipment | 11 | 2021-08-03 | 26026 | keep | 0 | Aug | 2021 | 0.017726 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-08-03 21:50 | 2021-08-04 14:09 | 110 | 016:19 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN CORTE DE LINEA | R21080300056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 979 | 2021-08-03 | 107690 | keep | 0 | Aug | 2021 | 0.073347 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
VEGA BAJA | 2021-08-03 22:09 | 2021-08-03 22:10 | 1570 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21080300000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-03 | 1570 | keep | 0 | Aug | 2021 | 0.0010693 | 0.0010693 | Momentary | FALSE | FALSE | Not_TMED_Event | 1570
SAN JUAN | 2021-08-03 22:13 | 2021-08-04 19:27 | 80 | 021:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE LEVANTO CONDUCTOR | S21080300155 | New_Event | Wire Down | Include | Include | Equipment | 1274 | 2021-08-03 | 101920 | keep | 0 | Aug | 2021 | 0.069417 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-08-03 22:13 | 2021-08-04 05:07 | 40 | 006:54 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE SECCIONALIZO CONDUCTOR ROTO POR ARBOL CAIDO | S21080300155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 414 | 2021-08-03 | 16560 | keep | 0 | Aug | 2021 | 0.011279 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-03 22:42 | 2021-08-04 11:00 | 8 | 012:18 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | M21080300230 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 738 | 2021-08-03 | 5904 | keep | 0 | Aug | 2021 | 0.0040212 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-08-03 23:00 | 2021-08-04 18:40 | 50 | 019:40 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21080300152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1180 | 2021-08-03 | 59000 | keep | 0 | Aug | 2021 | 0.040185 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-08-03 23:02 | 2021-08-04 20:08 | 7 | 021:06 | P | DESGANCHE | DESGANCHO REMPLAZO CAJA DE TRANSFORMADOR Y BAJANTE SECUNDARIO | C21080300149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1266 | 2021-08-03 | 8862 | keep | 0 | Aug | 2021 | 0.0060359 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2021-08-03 23:44 | 2021-08-04 09:08 | 18 | 009:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21080300152 | New_Event | Bad Weather | Include | Include | Weather | 564 | 2021-08-03 | 10152 | keep | 0 | Aug | 2021 | 0.0069145 | 1.226e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 18
VEGA BAJA | 2021-08-03 23:56 | 2021-08-03 23:57 | 3076 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21080300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-03 | 3076 | keep | 0 | Aug | 2021 | 0.002095 | 0.002095 | Momentary | FALSE | FALSE | Not_TMED_Event | 3076
BAYAMON | 2021-08-04 00:34 | 2021-08-04 02:53 | 34 | 002:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRARON PUENTES PRIMARIOS Y SE LEVANTO CONDUCTOR PRIMARIO | B21080300282 | Partial_restoration | Wire Down | Include | Include | Equipment | 139 | 2021-08-04 | 4726 | keep | 0 | Aug | 2021 | 0.0032189 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2021-08-04 00:42 | 2021-08-04 01:24 | 2309 | 000:42 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE PRIMARIO EN SALIDA DE ALIMENTADOR | P21080400001 | Additional_clients | Wire Down | Include | Include | Equipment | 42 | 2021-08-04 | 96978 | keep | 0 | Aug | 2021 | 0.066051 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-08-04 00:46 | 2021-08-04 11:34 | 72 | 010:48 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO PIN POLE TOP | C21080400001 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 648 | 2021-08-04 | 46656 | keep | 0 | Aug | 2021 | 0.031777 | 4.9039e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 72
FAJARDO | 2021-08-04 01:31 | 2021-08-04 01:32 | 1463 | 000:01 | T | TRANSFORMADOR AVERIADO | RECIERRE | R21080400001 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1 | 2021-08-04 | 1463 | keep | 0 | Aug | 2021 | 0.00099644 | 0.00099644 | Momentary | FALSE | FALSE | Not_TMED_Event | 1463
FAJARDO | 2021-08-04 01:32 | 2021-08-04 12:32 | 30 | 011:00 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 75KVA X 75KVA | R21080400002 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 660 | 2021-08-04 | 19800 | keep | 0 | Aug | 2021 | 0.013486 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2021-08-04 03:12 | 2021-08-04 10:35 | 15 | 007:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21080400001 | New_Event | Bad Weather | Include | Include | Weather | 443 | 2021-08-04 | 6645 | keep | 0 | Aug | 2021 | 0.0045259 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-08-04 03:25 | 2021-08-04 03:26 | 4641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-04 | 4641 | keep | 0 | Aug | 2021 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
PONCE | 2021-08-04 03:52 | 2021-08-04 05:53 | 2113 | 002:01 | T | CABLE SOTERRADO AVERIADO | DISPARO INTERRUPTOR SE ABRIO RISER EN PONCE BY PASS | P21080400003 | New_Event | UG Cable Fault | Include | Include | Equipment | 121 | 2021-08-04 | 255673 | keep | 0 | Aug | 2021 | 0.17414 | 0.0014392 | Sustained | FALSE | FALSE | Not_TMED_Event | 2113
ARECIBO | 2021-08-04 04:29 | 2021-08-04 04:30 | 5042 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21080400002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-04 | 5042 | keep | 0 | Aug | 2021 | 0.0034341 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
HUMACAO | 2021-08-04 04:42 | 2021-08-04 13:20 | 25 | 008:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | C21080400003 | New_Event | Wire Down | Include | Include | Equipment | 518 | 2021-08-04 | 12950 | keep | 0 | Aug | 2021 | 0.0088202 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
VEGA BAJA | 2021-08-04 04:55 | 2021-08-04 07:38 | 3332 | 002:43 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZARON DISCOS PARTIDOS Y SE CERRO POR SCADA | B21080400003 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 163 | 2021-08-04 | 543116 | keep | 0 | Aug | 2021 | 0.36991 | 0.0022694 | Sustained | FALSE | FALSE | Not_TMED_Event | 3332
SAN JUAN | 2021-08-04 05:19 | 2021-08-04 10:36 | 6 | 005:17 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR SE INSPECCIONO | R21080400003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 317 | 2021-08-04 | 1902 | keep | 0 | Aug | 2021 | 0.0012954 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-08-04 05:41 | 2021-08-04 05:42 | 2000 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE CARGA POR INTERRUPTOR SPARE 1619-02 | R21080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-04 | 2000 | keep | 0 | Aug | 2021 | 0.0013622 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
PONCE | 2021-08-04 05:53 | 2021-08-05 18:39 | 5 | 036:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO AVERIA SOTERRADA Y SE CERRO RAISER HACIA EL SOETRRADO | P21080400009 | New_Event | Wire Down | Include | Include | Equipment | 2206 | 2021-08-04 | 11030 | keep | 0 | Aug | 2021 | 0.0075125 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-08-04 06:16 | 2021-08-04 14:04 | 15 | 007:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR POR PORTA FUSIBLE QUEMADO | P21080400005 | New_Event | Cutout Failure | Include | Include | Equipment | 468 | 2021-08-04 | 7020 | keep | 0 | Aug | 2021 | 0.0047813 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-08-04 06:28 | 2021-08-04 11:45 | 3 | 005:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA Y BAJANTE DEL TRANSFORMADOR | A21080400006 | New_Event | Cutout Failure | Include | Include | Equipment | 317 | 2021-08-04 | 951 | keep | 0 | Aug | 2021 | 0.00064772 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2021-08-04 06:28 | 2021-08-04 11:00 | 10 | 004:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21080400016 | New_Event | Bad Weather | Include | Include | Weather | 272 | 2021-08-04 | 2720 | keep | 0 | Aug | 2021 | 0.0018526 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
AGUADILLA | 2021-08-04 06:31 | 2021-08-04 17:18 | 30 | 010:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR MAL TIEMPO | M21080400009 | New_Event | Bad Weather | Include | Include | Weather | 647 | 2021-08-04 | 19410 | keep | 0 | Aug | 2021 | 0.01322 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-08-04 06:31 | 2021-08-04 11:45 | 1 | 005:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M21080400003 | New_Event | Bad Weather | Include | Include | Weather | 314 | 2021-08-04 | 314 | keep | 0 | Aug | 2021 | 0.00021386 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-08-04 07:04 | 2021-08-04 12:25 | 40 | 005:21 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | S21080400013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 321 | 2021-08-04 | 12840 | keep | 0 | Aug | 2021 | 0.0087453 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
GUAYAMA | 2021-08-04 07:10 | 2021-08-04 07:11 | 1173 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210804000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-04 | 1173 | keep | 0 | Aug | 2021 | 0.00079892 | 0.00079892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1173
BAYAMON | 2021-08-04 07:20 | 2021-08-04 07:22 | 37 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4400 | S21080400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-08-04 | 74 | keep | 0 | Aug | 2021 | 5.0401e-05 | 2.5201e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 37
BAYAMON | 2021-08-04 07:20 | 2021-08-04 07:22 | 7 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4400 | S21080400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-08-04 | 14 | keep | 0 | Aug | 2021 | 9.5353e-06 | 4.7677e-06 | Momentary | FALSE | TRUE | Not_TMED_Event | 7
BAYAMON | 2021-08-04 07:20 | 2021-08-04 07:22 | 2 | 000:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4400 | S21080400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-08-04 | 4 | keep | 0 | Aug | 2021 | 2.7244e-06 | 1.3622e-06 | Momentary | FALSE | TRUE | Not_TMED_Event | 2
BARRANQUITAS | 2021-08-04 07:22 | 2021-08-04 14:57 | 40 | 007:35 | P | HERRAJE ROTO O PODRIDO | 1 X 40 EN CORTE DE LINEA REMPLAZO CRUCETA PODRIDA | C21080400005 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 455 | 2021-08-04 | 18200 | keep | 0 | Aug | 2021 | 0.012396 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-04 07:27 | 2021-08-04 07:28 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-04 | 1097 | keep | 0 | Aug | 2021 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
BAYAMON | 2021-08-04 07:48 | 2021-08-04 12:17 | 36 | 004:29 | P | NO SE REPORTO CAUSA | 2 X 40 EN CORTE DE LINEA | B21080400013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 269 | 2021-08-04 | 9684 | keep | 0 | Aug | 2021 | 0.0065957 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
MAYAGÃœEZ | 2021-08-04 08:05 | 2021-08-04 13:15 | 75 | 005:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21080400006 | New_Event | Bad Weather | Include | Include | Weather | 310 | 2021-08-04 | 23250 | keep | 0 | Aug | 2021 | 0.015835 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
SAN JUAN | 2021-08-04 08:06 | 2021-08-04 18:40 | 10 | 010:34 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21080400020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 634 | 2021-08-04 | 6340 | keep | 0 | Aug | 2021 | 0.0043181 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-08-04 08:08 | 2021-08-04 14:46 | 80 | 006:38 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21080400007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 398 | 2021-08-04 | 31840 | keep | 0 | Aug | 2021 | 0.021686 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-04 08:12 | 2021-08-04 09:27 | 6 | 001:15 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21080400059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 75 | 2021-08-04 | 450 | keep | 0 | Aug | 2021 | 0.00030649 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-08-04 08:13 | 2021-08-04 09:20 | 12 | 001:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21080400009 | New_Event | Bad Weather | Include | Include | Weather | 67 | 2021-08-04 | 804 | keep | 0 | Aug | 2021 | 0.0005476 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-08-04 08:14 | 2021-08-04 10:45 | 200 | 002:31 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M21080400010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2021-08-04 | 30200 | keep | 0 | Aug | 2021 | 0.020569 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
AGUADILLA | 2021-08-04 08:14 | 2021-08-04 12:00 | 4 | 003:46 | P | OTRAS CAUSAS | 1 X 80 EN CORTE DE LINEA SE SECCIONALIZO AVERIA EN COMPANIA BIO MEDICAL QUE TIENE CT AVERIADO | M21080400012 | New_Event | Other Causes | Include | Include | Other | 226 | 2021-08-04 | 904 | keep | 0 | Aug | 2021 | 0.00061571 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
PONCE | 2021-08-04 08:24 | 2021-08-04 08:25 | 1979 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE DE PORTATIL EN 5018 | P210804000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-04 | 1979 | keep | 0 | Aug | 2021 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2021-08-04 08:24 | 2021-08-04 08:25 | 3114 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE DE PORTATIL EN 5018 | P210804000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-04 | 3114 | keep | 0 | Aug | 2021 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
PONCE | 2021-08-04 08:24 | 2021-08-04 08:25 | 5069 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE DE SUB ESTACION PORTATIL 5018 | P210804000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-04 | 5069 | keep | 0 | Aug | 2021 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2021-08-04 08:24 | 2021-08-04 08:25 | 5063 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE DE SUB ESTACION PORTATIL 5018 | P210804000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-04 | 5063 | keep | 0 | Aug | 2021 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
BAYAMON | 2021-08-04 08:25 | 2021-08-04 14:35 | 20 | 006:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA RELAMPAGOS | B21080400016 | New_Event | Bad Weather | Include | Include | Weather | 370 | 2021-08-04 | 7400 | keep | 0 | Aug | 2021 | 0.0050401 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-08-04 08:25 | 2021-08-04 17:59 | 15 | 009:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIARON 2 CAJAS PRIMARIAS DE RISER QUEMADAS Y 1 POR 100 | P21080400016 | New_Event | Cutout Failure | Include | Include | Equipment | 574 | 2021-08-04 | 8610 | keep | 0 | Aug | 2021 | 0.0058642 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-08-04 08:33 | 2021-08-04 12:18 | 16 | 003:45 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REEMPLAZO TERMINACION QUEMADA DE RISER A SU7 | R21080400012 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 225 | 2021-08-04 | 3600 | keep | 0 | Aug | 2021 | 0.0024519 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
ARECIBO | 2021-08-04 08:34 | 2021-08-04 11:45 | 7 | 003:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DEL TRANSFORMADOR PARA REPARAR LINEAS | A21080400014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 191 | 2021-08-04 | 1337 | keep | 0 | Aug | 2021 | 0.00091062 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
BAYAMON | 2021-08-04 08:43 | 2021-08-04 15:35 | 30 | 006:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO DE LINEA A CAJA EN CORTE DE LINEA | B21080400019 | New_Event | Wire Down | Include | Include | Equipment | 412 | 2021-08-04 | 12360 | keep | 0 | Aug | 2021 | 0.0084183 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-08-04 08:44 | 2021-08-04 08:45 | 1588 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA CARGA DEL 1711-03 | B21080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-04 | 1588 | keep | 0 | Aug | 2021 | 0.0010816 | 0.0010816 | Momentary | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2021-08-04 08:44 | 2021-08-04 08:45 | 13 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA TRANSFERIDA AL 1711-01 | B21080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-04 | 13 | keep | 0 | Aug | 2021 | 8.8542e-06 | 8.8542e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 13
FAJARDO | 2021-08-04 08:46 | 2021-08-04 11:59 | 50 | 003:13 | P | DESGANCHE | 1 X 30 Y 1 X 10 EN CORTE DE LINEA Y TRANSFORMADOR | R21080400013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2021-08-04 | 9650 | keep | 0 | Aug | 2021 | 0.0065726 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-08-04 08:47 | 2021-08-04 18:01 | 1 | 009:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | C21080400015 | New_Event |  |  | Include | Wildlife | 554 | 2021-08-04 | 554 | keep | 0 | Aug | 2021 | 0.00037733 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-08-04 08:51 | 2021-08-04 14:35 | 1 | 005:44 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA Y 1 X 20 EN MONTURA TRANSFORMADOR | R21080400014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 344 | 2021-08-04 | 344 | keep | 0 | Aug | 2021 | 0.0002343 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-08-04 09:00 | 2021-08-04 15:09 | 50 | 006:09 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21080400029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 369 | 2021-08-04 | 18450 | keep | 0 | Aug | 2021 | 0.012566 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-08-04 09:10 | 2021-08-04 15:53 | 110 | 006:43 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA REEMPLAZO PARARRAYO | R21080400016 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 403 | 2021-08-04 | 44330 | keep | 0 | Aug | 2021 | 0.030193 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
HUMACAO | 2021-08-04 09:18 | 2021-08-04 09:19 | 551 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-04 | 551 | keep | 0 | Aug | 2021 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
HUMACAO | 2021-08-04 09:36 | 2021-08-04 18:01 | 6 | 008:25 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C21080400025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 505 | 2021-08-04 | 3030 | keep | 0 | Aug | 2021 | 0.0020637 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2021-08-04 09:37 | 2021-08-04 18:15 | 40 | 008:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | A21080400024 | New_Event | Wire Down | Include | Include | Equipment | 518 | 2021-08-04 | 20720 | keep | 0 | Aug | 2021 | 0.014112 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-04 09:43 | 2021-08-04 20:53 | 12 | 011:10 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PODRIDO DE 45' X 45' MADERA C4 FID19518097 | M21080400026 | New_Event | Defective Pole | Include | Include | Equipment | 670 | 2021-08-04 | 8040 | keep | 0 | Aug | 2021 | 0.005476 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-08-04 09:49 | 2021-08-04 09:50 | 2000 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL INTERRUPTOR SPARE 1619-02 | R21080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-04 | 2000 | keep | 0 | Aug | 2021 | 0.0013622 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
CANOVANAS | 2021-08-04 09:50 | 2021-08-04 13:53 | 6 | 004:03 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR | R21080400022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2021-08-04 | 1458 | keep | 0 | Aug | 2021 | 0.00099304 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2021-08-04 09:56 | 2021-08-04 12:08 | 27 | 002:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR CONECTORES EN SECUNDARIA | C21080300146 | New_Event | Secondary Wire Down | Include | Include | Equipment | 132 | 2021-08-04 | 3564 | keep | 0 | Aug | 2021 | 0.0024274 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
ARECIBO | 2021-08-04 09:57 | 2021-08-04 14:00 | 15 | 004:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA A TRANSFORMADOR | A21080400033 | New_Event | Cutout Failure | Include | Include | Equipment | 243 | 2021-08-04 | 3645 | keep | 0 | Aug | 2021 | 0.0024826 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-08-04 10:03 | 2021-08-04 16:02 | 1 | 005:59 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | B21080400024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 359 | 2021-08-04 | 359 | keep | 0 | Aug | 2021 | 0.00024451 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-08-04 10:07 | 2021-08-04 10:47 | 17 | 000:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN RISER SE REEMPLAZO CAJA PRIMARIA | R21080400024 | New_Event | Cutout Failure | Include | Include | Equipment | 40 | 2021-08-04 | 680 | keep | 0 | Aug | 2021 | 0.00046314 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
AGUADILLA | 2021-08-04 10:21 | 2021-08-04 10:22 | 3041 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | M21080400000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-04 | 3041 | keep | 0 | Aug | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2021-08-04 10:22 | 2021-08-04 17:55 | 1 | 007:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO NEUTRAL PARTIDO | M21080400100 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 453 | 2021-08-04 | 453 | keep | 0 | Aug | 2021 | 0.00030854 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-08-04 10:41 | 2021-08-04 13:16 | 30 | 002:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | R21080400026 | New_Event |  |  | Include | Wildlife | 155 | 2021-08-04 | 4650 | keep | 0 | Aug | 2021 | 0.0031671 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
AGUADILLA | 2021-08-04 10:46 | 2021-08-04 16:50 | 15 | 006:04 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.05KVA X 37.5KVA HOWARD 4160/7200 120/240 | M21080400021 | New_Event | Service Transformer Failure | Include | Include | Equipment | 364 | 2021-08-04 | 5460 | keep | 0 | Aug | 2021 | 0.0037188 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-08-04 11:10 | 2021-08-04 11:44 | 10 | 000:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR Y REPARARON SECUNDARIA | C21080300046 | New_Event | Secondary Wire Down | Include | Include | Equipment | 34 | 2021-08-04 | 340 | keep | 0 | Aug | 2021 | 0.00023157 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-08-04 11:17 | 2021-08-04 11:18 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-04 | 393 | keep | 0 | Aug | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
ARECIBO | 2021-08-04 11:27 | 2021-08-04 20:00 | 35 | 008:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA DEFECTUOSA | A21080400047 | New_Event | Cutout Failure | Include | Include | Equipment | 513 | 2021-08-04 | 17955 | keep | 0 | Aug | 2021 | 0.012229 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
HUMACAO | 2021-08-04 11:33 | 2021-08-04 16:37 | 10 | 005:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR REMPLAZO PORTAFUSIBLE | C21080400041 | New_Event | Cutout Failure | Include | Include | Equipment | 304 | 2021-08-04 | 3040 | keep | 0 | Aug | 2021 | 0.0020705 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-08-04 11:36 | 2021-08-04 11:37 | 3046 | 000:01 | T | DESGANCHE | RECIERRE | R21080400032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-04 | 3046 | keep | 0 | Aug | 2021 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2021-08-04 11:37 | 2021-08-04 16:22 | 230 | 004:45 | P | DESGANCHE | 1 X 80 Y 2 X 40 EN CORTES DE LINEAS | R21080400034 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 285 | 2021-08-04 | 65550 | keep | 0 | Aug | 2021 | 0.044646 | 0.00015665 | Sustained | FALSE | TRUE | Not_TMED_Event | 230
UTUADO | 2021-08-04 11:39 | 2021-08-04 15:37 | 5 | 003:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA PARTIDA | A21080400049 | New_Event | Bad Weather | Include | Include | Weather | 238 | 2021-08-04 | 1190 | keep | 0 | Aug | 2021 | 0.0008105 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
PONCE | 2021-08-04 11:44 | 2021-08-04 15:45 | 50 | 004:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | P21080400028 | New_Event | Wire Down | Include | Include | Equipment | 241 | 2021-08-04 | 12050 | keep | 0 | Aug | 2021 | 0.0082072 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-04 12:00 | 2021-08-04 13:05 | 1 | 001:05 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMA | M21080400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 65 | 2021-08-04 | 65 | keep | 0 | Aug | 2021 | 4.4271e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-08-04 12:00 | 2021-08-04 13:05 | 40 | 001:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21080400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 65 | 2021-08-04 | 2600 | keep | 0 | Aug | 2021 | 0.0017708 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
AGUADILLA | 2021-08-04 12:07 | 2021-08-04 12:08 | 4882 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-04 | 4882 | keep | 0 | Aug | 2021 | 0.0033251 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
ARECIBO | 2021-08-04 12:11 | 2021-08-04 18:02 | 12 | 005:51 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 50KVA X 50 KVA | A21080400053 | New_Event | Service Transformer Failure | Include | Include | Equipment | 351 | 2021-08-04 | 4212 | keep | 0 | Aug | 2021 | 0.0028688 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-08-04 12:24 | 2021-08-04 16:02 | 15 | 003:38 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 10 EN RISER PROVISIONAL @ T-116 REPARO TERMINACION EN RISER DEL PROVISIONAL | R21080300028 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 218 | 2021-08-04 | 3270 | keep | 0 | Aug | 2021 | 0.0022272 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-08-04 12:25 | 2021-08-04 12:26 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-04 | 870 | keep | 0 | Aug | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2021-08-04 12:26 | 2021-08-04 15:00 | 40 | 002:34 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | S21080400013 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 154 | 2021-08-04 | 6160 | keep | 0 | Aug | 2021 | 0.0041955 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-08-04 12:29 | 2021-08-04 12:30 | 2466 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S21080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-04 | 2466 | keep | 0 | Aug | 2021 | 0.0016796 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
BAYAMON | 2021-08-04 12:32 | 2021-08-04 12:35 | 1935 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE GUARAGUAO | B21080400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-08-04 | 5805 | keep | 0 | Aug | 2021 | 0.0039538 | 0.0013179 | Momentary | FALSE | FALSE | Not_TMED_Event | 1935
BAYAMON | 2021-08-04 12:32 | 2021-08-04 12:35 | 3 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE GUARAGUAO LLEVANDO CARGA DEL 1707-03 | S21080400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-08-04 | 9 | keep | 0 | Aug | 2021 | 6.1299e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-08-04 12:32 | 2021-08-04 12:35 | 61 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE GUARAGUAO CARGA TRANSFERIDA AL 1707-02 | S21080400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-08-04 | 183 | keep | 0 | Aug | 2021 | 0.00012464 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2021-08-04 12:32 | 2021-08-04 12:35 | 1501 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE GUARAGUAO | S21080400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-08-04 | 4503 | keep | 0 | Aug | 2021 | 0.003067 | 0.0010223 | Momentary | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2021-08-04 12:32 | 2021-08-04 12:35 | 546 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE GUARAGUAO | S21080400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-08-04 | 1638 | keep | 0 | Aug | 2021 | 0.0011156 | 0.00037188 | Momentary | FALSE | FALSE | Not_TMED_Event | 546
BAYAMON | 2021-08-04 12:32 | 2021-08-04 12:35 | 959 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE GUARAGUAO | S21080400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-08-04 | 2877 | keep | 0 | Aug | 2021 | 0.0019595 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2021-08-04 12:32 | 2021-08-04 12:48 | 15 | 000:16 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | S21080400047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 16 | 2021-08-04 | 240 | keep | 0 | Aug | 2021 | 0.00016346 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-08-04 12:32 | 2021-08-04 12:35 | 1297 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE GUARAGUAO | S21080400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-08-04 | 3891 | keep | 0 | Aug | 2021 | 0.0026501 | 0.00088338 | Momentary | FALSE | FALSE | Not_TMED_Event | 1297
BAYAMON | 2021-08-04 12:32 | 2021-08-04 12:35 | 451 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE GUARAGUAO | S21080400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-08-04 | 1353 | keep | 0 | Aug | 2021 | 0.00092152 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
BAYAMON | 2021-08-04 12:32 | 2021-08-04 12:35 | 1264 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE GUARAGUAO | S21080400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-08-04 | 3792 | keep | 0 | Aug | 2021 | 0.0025827 | 0.0008609 | Momentary | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2021-08-04 12:32 | 2021-08-04 12:35 | 620 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE GUARAGUAO | S21080400000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-08-04 | 1860 | keep | 0 | Aug | 2021 | 0.0012668 | 0.00042228 | Momentary | FALSE | FALSE | Not_TMED_Event | 620
BAYAMON | 2021-08-04 12:35 | 2021-08-05 17:45 | 10 | 029:10 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B21080400086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1750 | 2021-08-04 | 17500 | keep | 0 | Aug | 2021 | 0.011919 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-08-04 12:35 | 2021-08-04 12:36 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-04 | 222 | keep | 0 | Aug | 2021 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2021-08-04 12:42 | 2021-08-04 12:43 | 2402 | 000:01 | T | DESGANCHE | RECIERRE | C21080400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-04 | 2402 | keep | 0 | Aug | 2021 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
CAGUAS | 2021-08-04 12:43 | 2021-08-05 11:23 | 3 | 022:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA NEUTRAL SECUNDARIO | C21080400049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1360 | 2021-08-04 | 4080 | keep | 0 | Aug | 2021 | 0.0027789 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
PONCE | 2021-08-04 12:47 | 2021-08-04 18:06 | 4 | 005:19 | P | ESTRUCTURA AVERIADA | 2 X 40 EN CORTE DE LINEA POSTE PRIMARIO PARTIDO SE SECCIONALISO Y QUEDARON 4 CLIENTES SIN SERVICIO | P21080300303 | Partial_restoration | Defective Pole | Include | Include | Equipment | 319 | 2021-08-04 | 1276 | keep | 0 | Aug | 2021 | 0.00086908 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-04 12:48 | 2021-08-04 12:49 | 1297 | 000:01 | T | DESGANCHE | DISPARO 1904-06 QUE LLEVA 1901-02 Y SE CERRO POR SCADA | S21080400000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-04 | 1297 | keep | 0 | Aug | 2021 | 0.00088338 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-04 12:48 | 2021-08-04 12:49 | 451 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1904-06 QUE LLEVA 1901-03 Y SE CERRO POR SCADA | S21080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-04 | 451 | keep | 0 | Aug | 2021 | 0.00030717 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
BAYAMON | 2021-08-04 12:49 | 2021-08-04 17:59 | 15 | 005:10 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | S21080400047 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 310 | 2021-08-04 | 4650 | keep | 0 | Aug | 2021 | 0.0031671 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
SAN JUAN | 2021-08-04 12:59 | 2021-08-04 13:00 | 1051 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21080400048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-04 | 1051 | keep | 0 | Aug | 2021 | 0.00071583 | 0.00071583 | Momentary | FALSE | FALSE | Not_TMED_Event | 1051
VEGA BAJA | 2021-08-04 13:00 | 2021-08-04 13:01 | 6 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-04 | 6 | keep | 0 | Aug | 2021 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-08-04 13:03 | 2021-08-04 18:31 | 40 | 005:28 | P | DESGANCHE | 3 X 140 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21080400060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 328 | 2021-08-04 | 13120 | keep | 0 | Aug | 2021 | 0.008936 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-08-04 13:08 | 2021-08-04 13:50 | 12 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA PARTIDA | A21080400007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2021-08-04 | 504 | keep | 0 | Aug | 2021 | 0.00034327 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
AGUADILLA | 2021-08-04 13:22 | 2021-08-04 17:00 | 60 | 003:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CORTE DE LINEA Y SE REPARO 200 PIES DE SECUNDARIA | M21080400054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 218 | 2021-08-04 | 13080 | keep | 0 | Aug | 2021 | 0.0089087 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-08-04 13:23 | 2021-08-04 16:20 | 200 | 002:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21080400062 | New_Event | Bad Weather | Include | Include | Weather | 177 | 2021-08-04 | 35400 | keep | 0 | Aug | 2021 | 0.024111 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
FAJARDO | 2021-08-04 13:28 | 2021-08-04 17:07 | 1 | 003:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA | R21080400054 | New_Event | Cutout Failure | Include | Include | Equipment | 219 | 2021-08-04 | 219 | keep | 0 | Aug | 2021 | 0.00014916 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
VEGA BAJA | 2021-08-04 13:30 | 2021-08-05 15:02 | 12 | 025:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21080400045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1532 | 2021-08-04 | 18384 | keep | 0 | Aug | 2021 | 0.012521 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-08-04 13:34 | 2021-08-04 18:01 | 55 | 004:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA REMPLAZO CAJA QUEMADA | C21080400057 | New_Event | Cutout Failure | Include | Include | Equipment | 267 | 2021-08-04 | 14685 | keep | 0 | Aug | 2021 | 0.010002 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
VEGA BAJA | 2021-08-04 13:48 | 2021-08-04 19:35 | 30 | 005:47 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21080400050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 347 | 2021-08-04 | 10410 | keep | 0 | Aug | 2021 | 0.0070902 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-08-04 13:49 | 2021-08-05 11:31 | 15 | 021:42 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | B21080400051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1302 | 2021-08-04 | 19530 | keep | 0 | Aug | 2021 | 0.013302 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
SAN JUAN | 2021-08-04 13:54 | 2021-08-04 13:58 | 1587 | 000:04 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA 30% POR 1424-08 | S21080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-08-04 | 6348 | keep | 0 | Aug | 2021 | 0.0043236 | 0.0010809 | Momentary | FALSE | FALSE | Not_TMED_Event | 1587
SAN JUAN | 2021-08-04 13:54 | 2021-08-04 13:58 | 1000 | 000:04 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA 80% POR 1424-08 | S21080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-08-04 | 4000 | keep | 0 | Aug | 2021 | 0.0027244 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2021-08-04 13:54 | 2021-08-04 13:58 | 278 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA CARGA POR 1424-08 | S21080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-08-04 | 1112 | keep | 0 | Aug | 2021 | 0.00075738 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2021-08-04 13:54 | 2021-08-04 13:58 | 9 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA LLEVA 1348-07, 80% 1348-06 Y 30% 1336-08 | S21080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-08-04 | 36 | keep | 0 | Aug | 2021 | 2.4519e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2021-08-04 13:54 | 2021-08-05 10:13 | 7 | 020:19 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21080400056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1219 | 2021-08-04 | 8533 | keep | 0 | Aug | 2021 | 0.0058118 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
BAYAMON | 2021-08-04 13:55 | 2021-08-04 19:25 | 40 | 005:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | S21080400073 | New_Event | Cutout Failure | Include | Include | Equipment | 330 | 2021-08-04 | 13200 | keep | 0 | Aug | 2021 | 0.0089905 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-04 13:55 | 2021-08-04 18:30 | 6 | 004:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO | M21080400057 | New_Event | Bad Weather | Include | Include | Weather | 275 | 2021-08-04 | 1650 | keep | 0 | Aug | 2021 | 0.0011238 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-08-04 13:59 | 2021-08-04 15:41 | 1587 | 001:42 | P | NO SE REPORTO CAUSA | DISPARO 1424-08 Y SE PATRULLO SIN ENCONTRAR CAUSA APARENTE 30% POR 1424-08 | S21080400078 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 102 | 2021-08-04 | 161874 | keep | 0 | Aug | 2021 | 0.11025 | 0.0010809 | Sustained | FALSE | FALSE | Not_TMED_Event | 1587
SAN JUAN | 2021-08-04 13:59 | 2021-08-04 15:41 | 1000 | 001:42 | P | NO SE REPORTO CAUSA | DISPARO 1424-08 Y SE PATRULLO SIN ENCONTRAR CAUSA APARENTE 80% POR 1424-08 | S21080400078 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 102 | 2021-08-04 | 102000 | keep | 0 | Aug | 2021 | 0.069472 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2021-08-04 13:59 | 2021-08-04 15:41 | 278 | 001:42 | T | NO SE REPORTO CAUSA | DISPARO 1424-08 Y SE PATRULLO SIN ENCONTRAR CAUSA APARENTE CARGA POR 1424-08 | S21080400078 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 102 | 2021-08-04 | 28356 | keep | 0 | Aug | 2021 | 0.019313 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2021-08-04 13:59 | 2021-08-04 15:41 | 9 | 001:42 | T | NO SE REPORTO CAUSA | DISPARO 1424-08 Y SE PATRULLO SIN ENCONTRAR CAUSA APARENTE LLEVANDO LA CARGA DEL 1348-07, 80% 1348-06 Y 30% DEL 1336-08 | S21080400078 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 102 | 2021-08-04 | 918 | keep | 0 | Aug | 2021 | 0.00062525 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2021-08-04 14:00 | 2021-08-04 19:40 | 10 | 005:40 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN RISER MAL TIEMPO | M21080400119 | New_Event | Bad Weather | Include | Include | Weather | 340 | 2021-08-04 | 3400 | keep | 0 | Aug | 2021 | 0.0023157 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-08-04 14:03 | 2021-08-04 15:38 | 2203 | 001:35 | T | DESGANCHE | SE RETIRO ARBOL SOBRE LINEAS | S21080400076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2021-08-04 | 209285 | keep | 0 | Aug | 2021 | 0.14254 | 0.0015005 | Sustained | FALSE | TRUE | Not_TMED_Event | 2203
CANOVANAS | 2021-08-04 14:07 | 2021-08-04 15:32 | 12 | 001:25 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | R21080400057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 85 | 2021-08-04 | 1020 | keep | 0 | Aug | 2021 | 0.00069472 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-08-04 14:14 | 2021-08-04 14:16 | 761 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-04 | 1522 | keep | 0 | Aug | 2021 | 0.0010366 | 0.00051831 | Momentary | FALSE | FALSE | Not_TMED_Event | 761
BARRANQUITAS | 2021-08-04 14:31 | 2021-08-04 17:46 | 50 | 003:15 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO CAUSA | C21080400063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 195 | 2021-08-04 | 9750 | keep | 0 | Aug | 2021 | 0.0066407 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-04 14:34 | 2021-08-04 17:20 | 3522 | 002:46 | T | DESGANCHE | SE SECCIONALIZO ABRIENDO MACHETES PARA REALIZAR DESGANCHE | M21080400061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2021-08-04 | 584652 | keep | 0 | Aug | 2021 | 0.3982 | 0.0023988 | Sustained | FALSE | FALSE | Not_TMED_Event | 3522
CAGUAS | 2021-08-04 14:38 | 2021-08-05 13:51 | 100 | 023:13 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE CRITICO | C21080400064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1393 | 2021-08-04 | 139300 | keep | 0 | Aug | 2021 | 0.094877 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-08-04 14:39 | 2021-08-04 17:33 | 1 | 002:54 | P | NO SE REPORTO CAUSA | 1 X 15 EN RISER NO CAUSA | C21080400065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2021-08-04 | 174 | keep | 0 | Aug | 2021 | 0.00011851 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-08-04 14:57 | 2021-08-04 18:15 | 125 | 003:18 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21080400090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2021-08-04 | 24750 | keep | 0 | Aug | 2021 | 0.016857 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
BAYAMON | 2021-08-04 15:04 | 2021-08-04 18:08 | 12 | 003:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA Y BAJANTE SECUNDARIO | B21080400052 | New_Event | Cutout Failure | Include | Include | Equipment | 184 | 2021-08-04 | 2208 | keep | 0 | Aug | 2021 | 0.0015039 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2021-08-04 15:04 | 2021-08-04 16:13 | 65 | 001:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA REEMPLAZO PORTAFUSIBLE | R21080400066 | New_Event | Cutout Failure | Include | Include | Equipment | 69 | 2021-08-04 | 4485 | keep | 0 | Aug | 2021 | 0.0030547 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BAYAMON | 2021-08-04 15:07 | 2021-08-04 19:10 | 50 | 004:03 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21080400053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2021-08-04 | 12150 | keep | 0 | Aug | 2021 | 0.0082753 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-04 15:19 | 2021-08-04 20:15 | 9 | 004:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | M21080400082 | New_Event | Bad Weather | Include | Include | Weather | 296 | 2021-08-04 | 2664 | keep | 0 | Aug | 2021 | 0.0018144 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2021-08-04 15:25 | 2021-08-04 15:50 | 100 | 000:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR PUENTE PRIMARIO | P21080400047 | New_Event | Wire Down | Include | Include | Equipment | 25 | 2021-08-04 | 2500 | keep | 0 | Aug | 2021 | 0.0017027 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-08-04 15:31 | 2021-08-04 17:05 | 1746 | 001:34 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE AREA SOTERRADA Y SE CERRO EL INTERRUPTOR. ENTRO EL 20% DEL INTERRUPTOR(350 CLIENTES) | P21080400038 | New_Event | Wire Down | Include | Include | Equipment | 94 | 2021-08-04 | 164124 | keep | 0 | Aug | 2021 | 0.11178 | 0.0011892 | Sustained | FALSE | FALSE | Not_TMED_Event | 1746
PONCE | 2021-08-04 15:33 | 2021-08-04 15:34 | 3718 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P21080400039 | New_Event |  |  | Include | Wildlife | 1 | 2021-08-04 | 3718 | keep | 0 | Aug | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
PONCE | 2021-08-04 15:34 | 2021-08-05 09:57 | 80 | 018:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA, AVE CRUZO FASE | P21080400090 | 1st_after_momentary |  |  | Include | Wildlife | 1103 | 2021-08-04 | 88240 | keep | 0 | Aug | 2021 | 0.0601 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-08-04 15:44 | 2021-08-04 18:32 | 200 | 002:48 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 200 EN CORTE DE LINEA POR MAL TIEMPO | P21080400042 | New_Event | Bad Weather | Include | Include | Weather | 168 | 2021-08-04 | 33600 | keep | 0 | Aug | 2021 | 0.022885 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
HUMACAO | 2021-08-04 15:46 | 2021-08-04 19:03 | 75 | 003:17 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | C21080400073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2021-08-04 | 14775 | keep | 0 | Aug | 2021 | 0.010063 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
ARECIBO | 2021-08-04 15:59 | 2021-08-04 17:42 | 20 | 001:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR MAL TIEMPO | A21080400109 | New_Event | Bad Weather | Include | Include | Weather | 103 | 2021-08-04 | 2060 | keep | 0 | Aug | 2021 | 0.0014031 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-08-04 16:03 | 2021-08-04 18:41 | 4035 | 002:38 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON 3 CAJAS PRIMARIAS QUEMADAS | P210804000XX | New_Event | Cutout Failure | Include | Include | Equipment | 158 | 2021-08-04 | 637530 | keep | 0 | Aug | 2021 | 0.43422 | 0.0027482 | Sustained | FALSE | FALSE | Not_TMED_Event | 4035
SAN JUAN | 2021-08-04 16:06 | 2021-08-04 16:07 | 686 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-04 | 686 | keep | 0 | Aug | 2021 | 0.00046723 | 0.00046723 | Momentary | FALSE | FALSE | Not_TMED_Event | 686
AGUADILLA | 2021-08-04 16:06 | 2021-08-05 08:39 | 80 | 016:33 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M21080400092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 993 | 2021-08-04 | 79440 | keep | 0 | Aug | 2021 | 0.054106 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-08-04 16:07 | 2021-08-05 15:31 | 33 | 023:24 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21080400076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1404 | 2021-08-04 | 46332 | keep | 0 | Aug | 2021 | 0.031557 | 2.2476e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 33
PONCE | 2021-08-04 16:09 | 2021-08-05 21:00 | 2 | 028:51 | P | ESTRUCTURA AVERIADA | SE CAMBIARON 2 POSTES PARTIDOS | P21080400048 | New_Event | Defective Pole | Include | Include | Equipment | 1731 | 2021-08-04 | 3462 | keep | 0 | Aug | 2021 | 0.002358 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2021-08-04 16:14 | 2021-08-05 16:50 | 30 | 024:36 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21080400125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1476 | 2021-08-04 | 44280 | keep | 0 | Aug | 2021 | 0.030159 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-08-04 16:15 | 2021-08-04 18:30 | 100 | 002:15 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR MAL TIEMPO | A21080400111 | New_Event | Bad Weather | Include | Include | Weather | 135 | 2021-08-04 | 13500 | keep | 0 | Aug | 2021 | 0.0091948 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-08-04 16:21 | 2021-08-04 17:25 | 100 | 001:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21080400094 | New_Event | Bad Weather | Include | Include | Weather | 64 | 2021-08-04 | 6400 | keep | 0 | Aug | 2021 | 0.004359 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-08-04 16:24 | 2021-08-04 19:03 | 200 | 002:39 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 , 2 X 40, 2 X 50 Y 2 X 30 EN DISTINTOS CORTES DE LINEAS. FUERTES LLUVIAS Y TRUENOS | S21080400129 | New_Event | Bad Weather | Include | Include | Weather | 159 | 2021-08-04 | 31800 | keep | 0 | Aug | 2021 | 0.021659 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-08-04 16:27 | 2021-08-04 23:08 | 100 | 006:41 | P | NO SE REPORTO CAUSA | 2 X 100 Y 2 X 80 EN CORTES DE LINEA | S21080400132 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 401 | 2021-08-04 | 40100 | keep | 0 | Aug | 2021 | 0.027312 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-08-04 16:30 | 2021-08-04 18:08 | 25 | 001:38 | P | DESGANCHE | SE ABRIO CORTE DE LINEA MONOFASICO POR ARBOL HACIENDO CONTACTO EN FUEGO | B21080400052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 98 | 2021-08-04 | 2450 | keep | 0 | Aug | 2021 | 0.0016687 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-08-04 16:32 | 2021-08-04 20:38 | 50 | 004:06 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21080400135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2021-08-04 | 12300 | keep | 0 | Aug | 2021 | 0.0083775 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-04 16:36 | 2021-08-04 19:00 | 80 | 002:24 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DEGANCHE | M21080400078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2021-08-04 | 11520 | keep | 0 | Aug | 2021 | 0.0078462 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-08-04 16:36 | 2021-08-04 16:37 | 40 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR DECARGAS ELECTRICAS | A21080400097 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-08-04 | 40 | keep | 0 | Aug | 2021 | 2.7244e-05 | 2.7244e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-04 17:00 | 2021-08-04 18:40 | 6 | 001:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO | M21080400101 | New_Event | Bad Weather | Include | Include | Weather | 100 | 2021-08-04 | 600 | keep | 0 | Aug | 2021 | 0.00040866 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-08-04 17:03 | 2021-08-04 17:04 | 2402 | 000:01 | T | DESGANCHE | RECIERRE | B21080400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-04 | 2402 | keep | 0 | Aug | 2021 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2021-08-04 17:04 | 2021-08-05 14:21 | 50 | 021:17 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21080400195 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1277 | 2021-08-04 | 63850 | keep | 0 | Aug | 2021 | 0.043488 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-08-04 17:05 | 2021-08-04 18:43 | 1376 | 001:38 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRE PULL BOX EN MH-80 PARA SECCIONALIZAR AVERIA Y SE CERRO RAISER DE ENTRADA DEL SOTERRADO | P21080400067 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 98 | 2021-08-04 | 134848 | keep | 0 | Aug | 2021 | 0.091844 | 0.00093719 | Sustained | FALSE | FALSE | Not_TMED_Event | 1376
VEGA BAJA | 2021-08-04 17:07 | 2021-08-04 19:30 | 15 | 002:23 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | B21080400067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2021-08-04 | 2145 | keep | 0 | Aug | 2021 | 0.0014609 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
FAJARDO | 2021-08-04 17:11 | 2021-08-04 17:37 | 1 | 000:26 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R21080400077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 26 | 2021-08-04 | 26 | keep | 0 | Aug | 2021 | 1.7708e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-08-04 17:20 | 2021-08-04 20:55 | 12 | 003:35 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE RETIRO RAMAS | M21080400108 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 215 | 2021-08-04 | 2580 | keep | 0 | Aug | 2021 | 0.0017572 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-08-04 17:25 | 2021-08-04 20:15 | 55 | 002:50 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21080400078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2021-08-04 | 9350 | keep | 0 | Aug | 2021 | 0.0063682 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
AGUADILLA | 2021-08-04 17:34 | 2021-08-08 15:10 | 2 | 093:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA DE 100 AMP X CAJA DE 100 AMP | M21080400107 | New_Event | Cutout Failure | Include | Include | Equipment | 5616 | 2021-08-04 | 11232 | keep | 0 | Aug | 2021 | 0.0076501 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2021-08-04 17:47 | 2021-08-04 19:44 | 30 | 001:57 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO CAUSA | C21080400082 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 117 | 2021-08-04 | 3510 | keep | 0 | Aug | 2021 | 0.0023906 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-04 17:52 | 2021-08-04 20:15 | 1 | 002:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 10 EN BANCO DE TRANSFORMADORES SE REMPLAZARON CAJAS PRIMARIAS EN MAL ESTADO Y PARARRAYOS | B21080400059 | New_Event | Cutout Failure | Include | Include | Equipment | 143 | 2021-08-04 | 143 | keep | 0 | Aug | 2021 | 9.7397e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-08-04 17:53 | 2021-08-06 14:15 | 1 | 044:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO TOMA AVERIADA DEL CLIENTE | P21080400073 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2662 | 2021-08-04 | 2662 | keep | 0 | Aug | 2021 | 0.0018131 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-08-04 18:03 | 2021-08-04 18:44 | 8 | 000:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN BANCO DE TRANSFORMADOR REEMPLAZO PORTAFUSIBLE | R21080400083 | New_Event | Cutout Failure | Include | Include | Equipment | 41 | 2021-08-04 | 328 | keep | 0 | Aug | 2021 | 0.0002234 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-08-04 18:13 | 2021-08-05 19:00 | 7 | 024:47 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN TRANFORMADOR REMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA X 37.5 KVA Y PARARRAYO | C21080400083 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1487 | 2021-08-04 | 10409 | keep | 0 | Aug | 2021 | 0.0070895 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-08-04 18:15 | 2021-08-05 14:55 | 15 | 020:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA AVERIADA | M21080400113 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1240 | 2021-08-04 | 18600 | keep | 0 | Aug | 2021 | 0.012668 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-08-04 18:19 | 2021-08-05 17:38 | 12 | 023:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | S21080400161 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1399 | 2021-08-04 | 16788 | keep | 0 | Aug | 2021 | 0.011434 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
CAGUAS | 2021-08-04 18:31 | 2021-08-05 16:25 | 10 | 021:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA AVERIADA Y BAJANTE SECUNDARIO | C21080400085 | New_Event | Cutout Failure | Include | Include | Equipment | 1314 | 2021-08-04 | 13140 | keep | 0 | Aug | 2021 | 0.0089496 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-08-04 18:43 | 2021-08-09 16:25 | 10 | 117:42 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE REMPLAZARON TRES EMPALMES EN PULLBOX #8 MH 79A ESTAN SIN SERVICIO DESDE EL 8/04 CERRARON EL EVENTO DE ESE DIA. | P21080600004 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 7062 | 2021-08-04 | 70620 | keep | 0 | Aug | 2021 | 0.048099 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-08-04 18:43 | 2021-08-04 19:30 | 20 | 000:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | B21080400078 | New_Event |  |  | Include | Wildlife | 47 | 2021-08-04 | 940 | keep | 0 | Aug | 2021 | 0.00064023 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-08-04 18:48 | 2021-08-04 20:38 | 60 | 001:50 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | S21080400165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 110 | 2021-08-04 | 6600 | keep | 0 | Aug | 2021 | 0.0044952 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-08-04 19:05 | 2021-08-04 20:45 | 40 | 001:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A21080400129 | New_Event | Bad Weather | Include | Include | Weather | 100 | 2021-08-04 | 4000 | keep | 0 | Aug | 2021 | 0.0027244 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-08-04 19:06 | 2021-08-05 11:14 | 50 | 016:08 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21080400079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 968 | 2021-08-04 | 48400 | keep | 0 | Aug | 2021 | 0.032965 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-04 19:10 | 2021-08-04 21:00 | 50 | 001:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | A21080400131 | New_Event | Bad Weather | Include | Include | Weather | 110 | 2021-08-04 | 5500 | keep | 0 | Aug | 2021 | 0.003746 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-08-04 20:05 | 2021-08-04 20:49 | 110 | 000:44 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | R21080400104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 44 | 2021-08-04 | 4840 | keep | 0 | Aug | 2021 | 0.0032965 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
MAYAGÃœEZ | 2021-08-04 20:22 | 2021-08-05 10:54 | 7 | 014:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | M21080400127 | New_Event | Wire Down | Include | Include | Equipment | 872 | 2021-08-04 | 6104 | keep | 0 | Aug | 2021 | 0.0041574 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-08-04 20:55 | 2021-08-04 21:11 | 3522 | 000:16 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE RETIRO RAMA CRUZANDO LINEAS PRIMARIAS | M21080400128 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 16 | 2021-08-04 | 56352 | keep | 0 | Aug | 2021 | 0.038381 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CANOVANAS | 2021-08-04 21:02 | 2021-08-04 23:29 | 40 | 002:27 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21080400111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2021-08-04 | 5880 | keep | 0 | Aug | 2021 | 0.0040048 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-04 21:11 | 2021-08-05 11:27 | 12 | 014:16 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE RETIRO RAMAS | M21080400108 | Partial_restoration | Secondary Vegetation | Include | Include | Vegetation | 856 | 2021-08-04 | 10272 | keep | 0 | Aug | 2021 | 0.0069962 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-08-04 21:40 | 2021-08-05 17:47 | 5 | 020:07 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRAYO AVERIADO | R21080400112 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1207 | 2021-08-04 | 6035 | keep | 0 | Aug | 2021 | 0.0041104 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2021-08-04 22:02 | 2021-08-04 22:03 | 215 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21080400009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-04 | 215 | keep | 0 | Aug | 2021 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
HUMACAO | 2021-08-04 22:49 | 2021-08-04 22:50 | 776 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO | C21080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-04 | 776 | keep | 0 | Aug | 2021 | 0.00052853 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
HUMACAO | 2021-08-04 23:25 | 2021-08-05 09:38 | 90 | 010:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIAS | C21080400089 | New_Event | Bad Weather | Include | Include | Weather | 613 | 2021-08-04 | 55170 | keep | 0 | Aug | 2021 | 0.037576 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
MAYAGÃœEZ | 2021-08-05 00:30 | 2021-08-05 12:12 | 10 | 011:42 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21080500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 702 | 2021-08-05 | 7020 | keep | 0 | Aug | 2021 | 0.0047813 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CANOVANAS | 2021-08-05 01:34 | 2021-08-05 01:35 | 539 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21080500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-05 | 539 | keep | 0 | Aug | 2021 | 0.00036711 | 0.00036711 | Momentary | FALSE | FALSE | Not_TMED_Event | 539
SAN JUAN | 2021-08-05 02:49 | 2021-08-05 19:28 | 45 | 016:39 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21080500004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 999 | 2021-08-05 | 44955 | keep | 0 | Aug | 2021 | 0.030619 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
SAN JUAN | 2021-08-05 03:14 | 2021-08-05 11:27 | 60 | 008:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 Y 1 X 40 EN AEREOS PROVISIONALES CRUCE POR RATA | R21080500002 | New_Event |  |  | Include | Wildlife | 493 | 2021-08-05 | 29580 | keep | 0 | Aug | 2021 | 0.020147 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-08-05 03:54 | 2021-08-05 10:20 | 50 | 006:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO UNA CAJA AVERIADA EN CORTE DE LINEA POR UNA CAJA DE 100AMP MARCA HUMBLE | M21080500002 | New_Event | Cutout Failure | Include | Include | Equipment | 386 | 2021-08-05 | 19300 | keep | 0 | Aug | 2021 | 0.013145 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-08-05 03:58 | 2021-08-05 13:00 | 75 | 009:02 | P | DESGANCHE | 1 X 100 Y 1 X 50 EN CORTES DE LINEAS | B21080500003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 542 | 2021-08-05 | 40650 | keep | 0 | Aug | 2021 | 0.027687 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
PONCE | 2021-08-05 06:08 | 2021-08-05 17:13 | 80 | 011:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 POR 80 EN CORTE DE LINEA POR CAJA PRIMARIA QUEMADA | P21080500004 | New_Event | Cutout Failure | Include | Include | Equipment | 665 | 2021-08-05 | 53200 | keep | 0 | Aug | 2021 | 0.036234 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-08-05 06:50 | 2021-08-05 15:35 | 100 | 008:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA POR GLOBO DE HELIO CUZANDO FASES | P21080500005 | New_Event |  |  | Include | Wildlife | 525 | 2021-08-05 | 52500 | keep | 0 | Aug | 2021 | 0.035758 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-08-05 07:11 | 2021-08-05 14:21 | 20 | 007:10 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE LEVANTARON DOS FASES PRIMARIAS DEL SUELO | S21080500013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 430 | 2021-08-05 | 8600 | keep | 0 | Aug | 2021 | 0.0058574 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-08-05 07:21 | 2021-08-05 09:55 | 20 | 002:34 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A21080500002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2021-08-05 | 3080 | keep | 0 | Aug | 2021 | 0.0020978 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-08-05 07:29 | 2021-08-05 20:56 | 40 | 013:27 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO | S21080500010 | New_Event | Defective Pole | Include | Include | Equipment | 807 | 2021-08-05 | 32280 | keep | 0 | Aug | 2021 | 0.021986 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-08-05 07:31 | 2021-08-05 07:32 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21080500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-05 | 2203 | keep | 0 | Aug | 2021 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
BAYAMON | 2021-08-05 07:33 | 2021-08-05 09:40 | 824 | 002:07 | P | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR 95% POR EL 1119-04 | S21080500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 127 | 2021-08-05 | 104648 | keep | 0 | Aug | 2021 | 0.071275 | 0.00056122 | Sustained | FALSE | FALSE | Not_TMED_Event | 824
BAYAMON | 2021-08-05 07:33 | 2021-08-05 09:40 | 2720 | 002:07 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR SE ELIMINO PUENTE DE ENCIMA DE PARARRAYO Y SE CERRO POR CONTROL LLEVA 95% 1115-05 | S21080500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 127 | 2021-08-05 | 345440 | keep | 0 | Aug | 2021 | 0.23528 | 0.0018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 2720
BAYAMON | 2021-08-05 07:46 | 2021-08-05 14:14 | 8 | 006:28 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA PRINCIPAL AFUERA Y 1 X 30 EN RISER DEL CLIENTE | B21080500030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 388 | 2021-08-05 | 3104 | keep | 0 | Aug | 2021 | 0.0021141 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
BAYAMON | 2021-08-05 07:58 | 2021-08-05 15:30 | 15 | 007:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21080500026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 452 | 2021-08-05 | 6780 | keep | 0 | Aug | 2021 | 0.0046178 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-08-05 08:01 | 2021-08-05 12:40 | 1 | 004:39 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMA | A21080500005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 279 | 2021-08-05 | 279 | keep | 0 | Aug | 2021 | 0.00019003 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-08-05 08:04 | 2021-08-05 11:30 | 1 | 003:26 | P | DESGANCHE | 1 X 50 EN RISER SE RETIRO ENREDADERA | A21080500004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2021-08-05 | 206 | keep | 0 | Aug | 2021 | 0.00014031 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-08-05 08:07 | 2021-08-05 14:23 | 1 | 006:16 | P | OTRAS CAUSAS | 1 X 40 EN RISER CONTAMINACION EN EL TRANSCLOSURE | R21080500005 | New_Event | Other Causes | Include | Include | Other | 376 | 2021-08-05 | 376 | keep | 0 | Aug | 2021 | 0.00025609 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-08-05 08:08 | 2021-08-05 13:30 | 25 | 005:22 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 Y 1 X 10 EN DIFERENTES TRANSFORMADORES DESCARGAS ELECTRICAS | A21080500005 | New_Event | Bad Weather | Include | Include | Weather | 322 | 2021-08-05 | 8050 | keep | 0 | Aug | 2021 | 0.0054828 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2021-08-05 08:09 | 2021-08-05 10:08 | 1 | 001:59 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 20 EN BANCO DE TRANSFORMADORES LLUVIAS | C21080500004 | New_Event | Bad Weather | Include | Include | Weather | 119 | 2021-08-05 | 119 | keep | 0 | Aug | 2021 | 8.105e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2021-08-05 08:26 | 2021-08-05 08:27 | 1352 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO INTERRUPTOR CON CARGA DE 5602-01 SE ABRIO MACHETES EN AREA DE MALECON Y SE REALIZO PRUEBA QUEDANDO EN SERVICIO | P21072400066 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-08-05 | 1352 | keep | 0 | Aug | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
YAUCO | 2021-08-05 08:26 | 2021-08-05 08:27 | 3973 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO INTERRUPTOR CON CARGA DE 5602-01 SE ABRIO MACHETES EN AREA DE MALECON Y SE REALIZO PRUEBA QUEDANDO EN SERVICIO | P21072400066 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-08-05 | 3973 | keep | 0 | Aug | 2021 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2021-08-05 08:27 | 2021-08-05 12:01 | 250 | 003:34 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO INTERRUPTOR CON CARGA DE 5602-01 SE ABRIO MACHETES EN AREA DE MALECON Y SE REALIZO PRUEBA QUEDANDO EN SERVICIO | P21072400066 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 214 | 2021-08-05 | 53500 | keep | 0 | Aug | 2021 | 0.036439 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2021-08-05 08:36 | 2021-08-05 09:06 | 14 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA REPARAR SECUNDARIA | R21080300025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 30 | 2021-08-05 | 420 | keep | 0 | Aug | 2021 | 0.00028606 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
YAUCO | 2021-08-05 08:43 | 2021-08-05 08:44 | 2340 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | P21080500013 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-08-05 | 2340 | keep | 0 | Aug | 2021 | 0.0015938 | 0.0015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 2340
CAGUAS | 2021-08-05 08:49 | 2021-08-05 16:14 | 1 | 007:25 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO CAUSA | C21080500008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 445 | 2021-08-05 | 445 | keep | 0 | Aug | 2021 | 0.00030309 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-08-05 08:49 | 2021-08-05 13:36 | 200 | 004:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 Y 1 X 65 EN CORTES DE LINEA CRUCE POR AVE | C21080500007 | New_Event |  |  | Include | Wildlife | 287 | 2021-08-05 | 57400 | keep | 0 | Aug | 2021 | 0.039095 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
UTUADO | 2021-08-05 08:57 | 2021-08-06 18:15 | 5 | 033:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21080500009 | New_Event | Bad Weather | Include | Include | Weather | 1998 | 2021-08-05 | 9990 | keep | 0 | Aug | 2021 | 0.0068041 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2021-08-05 09:03 | 2021-08-05 12:30 | 40 | 003:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21080500010 | New_Event | Bad Weather | Include | Include | Weather | 207 | 2021-08-05 | 8280 | keep | 0 | Aug | 2021 | 0.0056395 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-08-05 09:10 | 2021-08-05 15:48 | 30 | 006:38 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LA LINEA | A21080500025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 398 | 2021-08-05 | 11940 | keep | 0 | Aug | 2021 | 0.0081323 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-08-05 09:10 | 2021-08-05 14:10 | 12 | 005:00 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A21080500011 | New_Event | Bad Weather | Include | Include | Weather | 300 | 2021-08-05 | 3600 | keep | 0 | Aug | 2021 | 0.0024519 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2021-08-05 09:14 | 2021-08-05 14:56 | 1 | 005:42 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA Y NO SE REPORTO CAUSA | P21080500016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 342 | 2021-08-05 | 342 | keep | 0 | Aug | 2021 | 0.00023293 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-08-05 09:17 | 2021-08-06 09:25 | 25 | 024:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN RISER CRUCE POR AVE | C21080500009 | New_Event |  |  | Include | Wildlife | 1448 | 2021-08-05 | 36200 | keep | 0 | Aug | 2021 | 0.024656 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-08-05 09:18 | 2021-08-05 11:31 | 20 | 002:13 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | B21080500016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 133 | 2021-08-05 | 2660 | keep | 0 | Aug | 2021 | 0.0018117 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-08-05 09:26 | 2021-08-05 15:48 | 65 | 006:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | A21080500012 | New_Event | Cutout Failure | Include | Include | Equipment | 382 | 2021-08-05 | 24830 | keep | 0 | Aug | 2021 | 0.016912 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
ARECIBO | 2021-08-05 09:29 | 2021-08-05 12:00 | 8 | 002:31 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | A21080500014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2021-08-05 | 1208 | keep | 0 | Aug | 2021 | 0.00082276 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-08-05 09:30 | 2021-08-05 14:44 | 1 | 005:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN RISER SE REEMPLAZO CAJA PRIMARIA | R21080300020 | New_Event | Cutout Failure | Include | Include | Equipment | 314 | 2021-08-05 | 314 | keep | 0 | Aug | 2021 | 0.00021386 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-08-05 09:41 | 2021-08-05 09:42 | 4641 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M21080500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-05 | 4641 | keep | 0 | Aug | 2021 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2021-08-05 09:42 | 2021-08-05 14:20 | 130 | 004:38 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | M21080500015 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 278 | 2021-08-05 | 36140 | keep | 0 | Aug | 2021 | 0.024615 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
BAYAMON | 2021-08-05 09:51 | 2021-08-05 13:06 | 824 | 003:15 | P | NO SE REPORTO CAUSA | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR CONTROL 95% POR EL 1909-04 | S21080500000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 195 | 2021-08-05 | 160680 | keep | 0 | Aug | 2021 | 0.10944 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-05 09:51 | 2021-08-05 13:06 | 2720 | 003:15 | T | NO SE REPORTO CAUSA | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR CONTROL LLEVA 95% 1115-05 | S21080500000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 195 | 2021-08-05 | 530400 | keep | 0 | Aug | 2021 | 0.36125 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-08-05 10:08 | 2021-08-05 13:25 | 1 | 003:17 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE | A21080400117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2021-08-05 | 197 | keep | 0 | Aug | 2021 | 0.00013418 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-08-05 10:12 | 2021-08-05 10:14 | 1812 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B21080500021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-05 | 3624 | keep | 0 | Aug | 2021 | 0.0024683 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
ARECIBO | 2021-08-05 10:15 | 2021-08-05 13:50 | 10 | 003:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BARRAS SECUNDARIAS | A21080500024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 215 | 2021-08-05 | 2150 | keep | 0 | Aug | 2021 | 0.0014644 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-05 10:16 | 2021-08-05 16:38 | 10 | 006:22 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PRIMARIO PARTIDO | A21080500022 | New_Event | Defective Pole | Include | Include | Equipment | 382 | 2021-08-05 | 3820 | keep | 0 | Aug | 2021 | 0.0026018 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-05 10:45 | 2021-08-05 14:00 | 10 | 003:15 | P | TRANSFORMADOR AVERIADO | SE REPARO BUCHING SECUNDARIO DE TRANSFORMADOR | A21080400122 | New_Event | Service Transformer Failure | Include | Include | Equipment | 195 | 2021-08-05 | 1950 | keep | 0 | Aug | 2021 | 0.0013281 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-05 11:00 | 2021-08-05 17:03 | 100 | 006:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | A21080500029 | New_Event | Wire Down | Include | Include | Equipment | 363 | 2021-08-05 | 36300 | keep | 0 | Aug | 2021 | 0.024724 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-08-05 11:00 | 2021-08-05 12:00 | 80 | 001:00 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | A21080400078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2021-08-05 | 4800 | keep | 0 | Aug | 2021 | 0.0032693 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-05 11:01 | 2021-08-05 15:13 | 25 | 004:12 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REPARO AISLADOR Y SE REPUSO 1 X 50 EN CORTE DE LINEA | B21080500030 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 252 | 2021-08-05 | 6300 | keep | 0 | Aug | 2021 | 0.0042909 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CAGUAS | 2021-08-05 11:21 | 2021-08-05 18:08 | 40 | 006:47 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21080500021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 407 | 2021-08-05 | 16280 | keep | 0 | Aug | 2021 | 0.011088 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-08-05 11:25 | 2021-08-05 14:54 | 8 | 003:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE HACIA TRANSFORMADOR | C21080500022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 209 | 2021-08-05 | 1672 | keep | 0 | Aug | 2021 | 0.0011388 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2021-08-05 11:25 | 2021-08-06 12:45 | 20 | 025:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | M21080500032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1520 | 2021-08-05 | 30400 | keep | 0 | Aug | 2021 | 0.020705 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2021-08-05 11:34 | 2021-08-05 11:48 | 2340 | 000:14 | T | PARARRAYOS DEFECTUOSO | SE ABRE INTERRUPTOR DE EMERGENCIA, PARARRAYO ARQUEANDO EN TRONCAL DEL ALIMENTADOR | P21080500025 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 14 | 2021-08-05 | 32760 | keep | 0 | Aug | 2021 | 0.022313 | 0.0015938 | Sustained | FALSE | FALSE | Not_TMED_Event | 2340
AGUADILLA | 2021-08-05 11:43 | 2021-08-05 21:16 | 15 | 009:33 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PRIMARIO Y SECUNDARIO | M21080500024 | New_Event | Defective Pole | Include | Include | Equipment | 573 | 2021-08-05 | 8595 | keep | 0 | Aug | 2021 | 0.005854 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-08-05 11:50 | 2021-08-05 15:34 | 35 | 003:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | P210805000XX | New_Event | Wire Down | Include | Include | Equipment | 224 | 2021-08-05 | 7840 | keep | 0 | Aug | 2021 | 0.0053398 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
YAUCO | 2021-08-05 12:01 | 2021-08-05 18:14 | 50 | 006:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 POR 65 EN CORTE DE LINEA POR CONTACTO DE AVE | P21080500027 | New_Event |  |  | Include | Wildlife | 373 | 2021-08-05 | 18650 | keep | 0 | Aug | 2021 | 0.012702 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-08-05 12:11 | 2021-08-05 15:20 | 43 | 003:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR CULEBRA Y DESGANCHE | R21080500017 | New_Event |  |  | Include | Wildlife | 189 | 2021-08-05 | 8127 | keep | 0 | Aug | 2021 | 0.0055353 | 2.9287e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 43
CAGUAS | 2021-08-05 12:12 | 2021-08-06 16:41 | 69 | 028:29 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 40 EN SU-15 SE RAPARO TERMINACION EN PULL BOX HACIA T-9 | C21080500027 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1709 | 2021-08-05 | 117921 | keep | 0 | Aug | 2021 | 0.080315 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
SAN JUAN | 2021-08-05 12:15 | 2021-08-06 14:04 | 15 | 025:49 | P | ESTRUCTURA AVERIADA | SE LEVANTO CONDUCTOR PRIMARIO Y SE REALIZO DESGANCHE | S21080500155 | New_Event | Defective Pole | Include | Include | Equipment | 1549 | 2021-08-05 | 23235 | keep | 0 | Aug | 2021 | 0.015825 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2021-08-05 12:41 | 2021-08-05 19:42 | 80 | 007:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA Y SE REALIZO DESGANCHE | A21080500042 | New_Event | Wire Down | Include | Include | Equipment | 421 | 2021-08-05 | 33680 | keep | 0 | Aug | 2021 | 0.022939 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-08-05 12:50 | 2021-08-05 12:51 | 2067 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21080500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-05 | 2067 | keep | 0 | Aug | 2021 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
BAYAMON | 2021-08-05 13:06 | 2021-08-05 15:31 | 500 | 002:25 | P | CABLE SOTERRADO AVERIADO | SE CERRO DE VACUUM SWITCH A MH 8 | S21080500000 | New_Event | UG Cable Fault | Include | Include | Equipment | 145 | 2021-08-05 | 72500 | keep | 0 | Aug | 2021 | 0.049379 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CAGUAS | 2021-08-05 14:11 | 2021-08-05 15:35 | 7 | 001:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTE SECUNDARIO | C21080200992 | New_Event | Secondary Wire Down | Include | Include | Equipment | 84 | 2021-08-05 | 588 | keep | 0 | Aug | 2021 | 0.00040048 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2021-08-05 14:22 | 2021-08-05 16:20 | 50 | 001:58 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21080500046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 118 | 2021-08-05 | 5900 | keep | 0 | Aug | 2021 | 0.0040185 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-08-05 14:29 | 2021-08-05 16:32 | 238 | 002:03 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | R21080500024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2021-08-05 | 29274 | keep | 0 | Aug | 2021 | 0.019938 | 0.0001621 | Sustained | FALSE | TRUE | Not_TMED_Event | 238
VEGA BAJA | 2021-08-05 14:29 | 2021-08-05 15:25 | 2216 | 000:56 | T | DESGANCHE | SE SECCIONALIZO ALIMENTADOR | B21080500047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2021-08-05 | 124096 | keep | 0 | Aug | 2021 | 0.084521 | 0.0015093 | Sustained | FALSE | FALSE | Not_TMED_Event | 2216
BAYAMON | 2021-08-05 15:03 | 2021-08-05 20:48 | 15 | 005:45 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN RISER SE REMPLAZO TRAMO SOTERRADO | B21080500057 | New_Event | UG Cable Fault | Include | Include | Equipment | 345 | 2021-08-05 | 5175 | keep | 0 | Aug | 2021 | 0.0035247 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-08-05 15:07 | 2021-08-05 16:39 | 1 | 001:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA Y REGULAR VOLTAJE | C21080500049 | New_Event | Wire Down | Include | Include | Equipment | 92 | 2021-08-05 | 92 | keep | 0 | Aug | 2021 | 6.2661e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-08-05 15:10 | 2021-08-05 21:27 | 50 | 006:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | SMU DE 40 EN SU-3 POR CONTACTO ANIMAL | P21080500052 | New_Event |  |  | Include | Wildlife | 377 | 2021-08-05 | 18850 | keep | 0 | Aug | 2021 | 0.012839 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-08-05 15:21 | 2021-08-05 15:22 | 50 | 000:01 | P | NO SE REPORTO CAUSA | 1 X 100 EN SWITCH UNIT Y 1 X 100 EN EL RISER | S21080500110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-05 | 50 | keep | 0 | Aug | 2021 | 3.4055e-05 | 3.4055e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-08-05 15:25 | 2021-08-05 19:10 | 1100 | 003:45 | P | DESGANCHE | SE REALIZO DESGANCHE | B21080500047 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 225 | 2021-08-05 | 247500 | keep | 0 | Aug | 2021 | 0.16857 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-05 15:26 | 2021-08-05 15:31 | 353 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S21080500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-08-05 | 1765 | keep | 0 | Aug | 2021 | 0.0012021 | 0.00024043 | Momentary | FALSE | FALSE | Not_TMED_Event | 353
GUAYAMA | 2021-08-05 15:27 | 2021-08-05 17:08 | 50 | 001:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X EN CORTE DE LINEA POR AVE | P21080500044 | New_Event |  |  | Include | Wildlife | 101 | 2021-08-05 | 5050 | keep | 0 | Aug | 2021 | 0.0034395 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-08-05 15:29 | 2021-08-05 15:31 | 2450 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO NO RECERRO | C21080500051 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2021-08-05 | 4900 | keep | 0 | Aug | 2021 | 0.0033374 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
MAYAGÃœEZ | 2021-08-05 15:44 | 2021-08-05 20:00 | 65 | 004:16 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA POR DESGANCHE | M21080500060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 256 | 2021-08-05 | 16640 | keep | 0 | Aug | 2021 | 0.011333 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
PONCE | 2021-08-05 15:48 | 2021-08-05 20:36 | 200 | 004:48 | P | SOBRECARGA | 1 X 200 EN CORTE DE LINEA POR CARGA | P21080500065 | New_Event | Trip Due To Overload | Include | Include | Other | 288 | 2021-08-05 | 57600 | keep | 0 | Aug | 2021 | 0.039231 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-08-05 15:51 | 2021-08-05 19:00 | 100 | 003:09 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | M21080500065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 189 | 2021-08-05 | 18900 | keep | 0 | Aug | 2021 | 0.012873 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-08-05 15:59 | 2021-08-06 20:38 | 30 | 028:39 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21080500223 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1719 | 2021-08-05 | 51570 | keep | 0 | Aug | 2021 | 0.035124 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-08-05 16:03 | 2021-08-06 09:50 | 40 | 017:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASES | M21080500070 | New_Event |  |  | Include | Wildlife | 1067 | 2021-08-05 | 42680 | keep | 0 | Aug | 2021 | 0.029069 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-05 16:04 | 2021-08-05 18:45 | 125 | 002:41 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | M21080500071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2021-08-05 | 20125 | keep | 0 | Aug | 2021 | 0.013707 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
BAYAMON | 2021-08-05 16:18 | 2021-08-05 18:26 | 500 | 002:08 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | B21080500062 | New_Event | Wire Down | Include | Include | Equipment | 128 | 2021-08-05 | 64000 | keep | 0 | Aug | 2021 | 0.04359 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
HUMACAO | 2021-08-05 16:24 | 2021-08-05 16:26 | 2450 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO NO RECERRO | C21080500057 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 2 | 2021-08-05 | 4900 | keep | 0 | Aug | 2021 | 0.0033374 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2021-08-05 16:26 | 2021-08-05 16:57 | 150 | 000:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE DE LINEA REMPLAZO CAJA AVERIADA | C21080500052 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 31 | 2021-08-05 | 4650 | keep | 0 | Aug | 2021 | 0.0031671 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
UTUADO | 2021-08-05 16:30 | 2021-08-06 13:33 | 40 | 021:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21080500062 | New_Event | Bad Weather | Include | Include | Weather | 1263 | 2021-08-05 | 50520 | keep | 0 | Aug | 2021 | 0.034409 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-05 16:37 | 2021-08-06 10:25 | 25 | 017:48 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | M21080500095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1068 | 2021-08-05 | 26700 | keep | 0 | Aug | 2021 | 0.018185 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
HUMACAO | 2021-08-05 16:57 | 2021-08-05 17:01 | 2450 | 000:04 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO NO RECERRO | C21080500060 | Additional_clients | Cutout Failure | Include | Include | Equipment | 4 | 2021-08-05 | 9800 | keep | 0 | Aug | 2021 | 0.0066747 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-08-05 17:01 | 2021-08-05 18:18 | 150 | 001:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE DE LINEA REMPLAZO CAJA AVERIADA | C21080500052 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 77 | 2021-08-05 | 11550 | keep | 0 | Aug | 2021 | 0.0078667 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
FAJARDO | 2021-08-05 17:05 | 2021-08-05 17:59 | 229 | 000:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | R21080500029 | New_Event |  |  | Include | Wildlife | 54 | 2021-08-05 | 12366 | keep | 0 | Aug | 2021 | 0.0084224 | 0.00015597 | Sustained | FALSE | TRUE | Not_TMED_Event | 229
SAN JUAN | 2021-08-05 17:09 | 2021-08-05 17:11 | 837 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA 1401 07 | S21080500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-05 | 1674 | keep | 0 | Aug | 2021 | 0.0011402 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2021-08-05 17:09 | 2021-08-05 17:11 | 908 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA 1401 06 | S21080500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-05 | 1816 | keep | 0 | Aug | 2021 | 0.0012369 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
BAYAMON | 2021-08-05 17:15 | 2021-08-05 17:18 | 514 | 000:03 | T | DESGANCHE | SE CERRO POR SCADA CARGA POR 1520 05 | S21080500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-08-05 | 1542 | keep | 0 | Aug | 2021 | 0.0010502 | 0.00035008 | Momentary | FALSE | FALSE | Not_TMED_Event | 514
BAYAMON | 2021-08-05 17:15 | 2021-08-05 17:18 | 752 | 000:03 | T | DESGANCHE | SE CERRO POR SCADA CARGA POR 1520 05 | S21080500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-08-05 | 2256 | keep | 0 | Aug | 2021 | 0.0015366 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
BAYAMON | 2021-08-05 17:15 | 2021-08-05 17:18 | 68 | 000:03 | T | DESGANCHE | SE CERRO POR SCADA LLEVA 1520 01 Y 1520 04 | S21080500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-08-05 | 204 | keep | 0 | Aug | 2021 | 0.00013894 | 4.6314e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 68
BAYAMON | 2021-08-05 17:22 | 2021-08-05 17:24 | 514 | 000:02 | T | DESGANCHE | SE CERRO POR SCADA CARGA POR 1520 05 | S21080500000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-08-05 | 1028 | keep | 0 | Aug | 2021 | 0.00070017 | 0.00035008 | Momentary | FALSE | FALSE | Not_TMED_Event | 514
BAYAMON | 2021-08-05 17:22 | 2021-08-05 17:24 | 752 | 000:02 | T | DESGANCHE | SE CERRO POR SCADA CARGA POR 1520 05 | S21080500000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-08-05 | 1504 | keep | 0 | Aug | 2021 | 0.0010244 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
BAYAMON | 2021-08-05 17:22 | 2021-08-05 17:24 | 68 | 000:02 | T | DESGANCHE | SE CERRO POR SCADA LLEVA 1520 01 Y 1520 04 | S21080500000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-08-05 | 136 | keep | 0 | Aug | 2021 | 9.2629e-05 | 4.6314e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 68
CANOVANAS | 2021-08-05 17:32 | 2021-08-05 22:59 | 40 | 005:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA REPARO CONDUCTOR | R21080500037 | New_Event | Wire Down | Include | Include | Equipment | 327 | 2021-08-05 | 13080 | keep | 0 | Aug | 2021 | 0.0089087 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
GUAYAMA | 2021-08-05 17:39 | 2021-08-05 17:40 | 215 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21080500060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-05 | 215 | keep | 0 | Aug | 2021 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
BAYAMON | 2021-08-05 17:40 | 2021-08-05 19:41 | 514 | 002:01 | T | DESGANCHE | SE CERRO INTERRUPTOR ABRIENDO AMARRE CONTRA 1520 04 EN BARRA DE INSPECCION CARGA POR 1520 05 | S21080500000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 121 | 2021-08-05 | 62194 | keep | 0 | Aug | 2021 | 0.04236 | 0.00035008 | Sustained | FALSE | FALSE | Not_TMED_Event | 514
BAYAMON | 2021-08-05 17:40 | 2021-08-05 21:30 | 752 | 003:50 | T | DESGANCHE | SE CERRO AMARRE DE 1520-04 EN BARRA DE INSPECCION CONTRA 1520-05 SE REALIZO DESGANCHE DE ENREDADERA | S21080500000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 230 | 2021-08-05 | 172960 | keep | 0 | Aug | 2021 | 0.1178 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
BAYAMON | 2021-08-05 17:40 | 2021-08-05 19:41 | 68 | 002:01 | T | DESGANCHE | SE CERRO INTERRUPTOR ABRIENDO AMARRE CONTRA 1520 04 EN BARRA DE INSPECCION LLEVA CARGA 1520 01 | S21080500000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 121 | 2021-08-05 | 8228 | keep | 0 | Aug | 2021 | 0.0056041 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
BARRANQUITAS | 2021-08-05 17:51 | 2021-08-05 20:20 | 40 | 002:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA LEVANTO CONDUCTOR | C21080500062 | New_Event | Wire Down | Include | Include | Equipment | 149 | 2021-08-05 | 5960 | keep | 0 | Aug | 2021 | 0.0040593 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
FAJARDO | 2021-08-05 18:04 | 2021-08-05 18:16 | 8 | 000:12 | P | OTRAS CAUSAS | 1 X 20 EN CORTE DE LINEA FUSIBLE FUNDIDO | R21080500039 | New_Event | Other Causes | Include | Include | Other | 12 | 2021-08-05 | 96 | keep | 0 | Aug | 2021 | 6.5385e-05 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
BAYAMON | 2021-08-05 18:26 | 2021-08-05 19:21 | 1501 | 000:55 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE ABIERTO | B21080500088 | Additional_clients | Wire Down | Include | Include | Equipment | 55 | 2021-08-05 | 82555 | keep | 0 | Aug | 2021 | 0.056228 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-08-05 18:50 | 2021-08-05 21:01 | 50 | 002:11 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO AISLADOR ROTO | A21080500056 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 131 | 2021-08-05 | 6550 | keep | 0 | Aug | 2021 | 0.0044612 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-08-05 18:51 | 2021-08-05 21:14 | 8 | 002:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A21080500008 | New_Event | Bad Weather | Include | Include | Weather | 143 | 2021-08-05 | 1144 | keep | 0 | Aug | 2021 | 0.00077917 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-08-05 18:55 | 2021-08-06 19:58 | 58 | 025:03 | P | CABLE SOTERRADO AVERIADO | 1 X 65 EN RISER, 1 X 40 EN AEREO PROVISIONAL Y 1 X 25 EN SU-2 AVERIA NUEVA DEL T-5 AL T-6 | C21080500067 | New_Event | UG Cable Fault | Include | Include | Equipment | 1503 | 2021-08-05 | 87174 | keep | 0 | Aug | 2021 | 0.059374 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
BAYAMON | 2021-08-05 18:58 | 2021-08-06 10:34 | 25 | 015:36 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21080500092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 936 | 2021-08-05 | 23400 | keep | 0 | Aug | 2021 | 0.015938 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
VEGA BAJA | 2021-08-05 18:59 | 2021-08-05 19:39 | 40 | 000:40 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21080500095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 40 | 2021-08-05 | 1600 | keep | 0 | Aug | 2021 | 0.0010898 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-05 19:14 | 2021-08-05 22:33 | 150 | 003:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 Y 1 X 100 EN CORTE DE LINEA REMPLAZO CAJA QUEMADA | M21080500110 | New_Event | Cutout Failure | Include | Include | Equipment | 199 | 2021-08-05 | 29850 | keep | 0 | Aug | 2021 | 0.020331 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-08-05 19:16 | 2021-08-05 23:37 | 548 | 004:21 | T | BREAKER DEFECTUOSO O NO OPERA | SE REMPLAZO AISLADOR QUEMADO Y SE TRANSFIRIO LA CARGA AL 3007-03 YA QUE EL 3602-03 PROBO MALO SIN CARGA | C21080500069 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 261 | 2021-08-05 | 143028 | keep | 0 | Aug | 2021 | 0.097416 | 0.00037324 | Sustained | FALSE | FALSE | Not_TMED_Event | 548
MAYAGÃœEZ | 2021-08-05 19:33 | 2021-08-06 11:10 | 50 | 015:37 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO RAMA | M21080400113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 937 | 2021-08-05 | 46850 | keep | 0 | Aug | 2021 | 0.031909 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-08-05 19:43 | 2021-08-07 11:56 | 30 | 040:13 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO CORTE DE LINEA PARA REPARAR CONDUCTOR A PUNTO DE CAER POR AISLADOR SAFADO | C21080500075 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 2413 | 2021-08-05 | 72390 | keep | 0 | Aug | 2021 | 0.049304 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-08-05 19:51 | 2021-08-05 19:53 | 824 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 95% POR EL 1909-04 | S21080500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-05 | 1648 | keep | 0 | Aug | 2021 | 0.0011224 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
BAYAMON | 2021-08-05 19:51 | 2021-08-05 19:53 | 2720 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA 95% 1115-05 | S21080500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-05 | 5440 | keep | 0 | Aug | 2021 | 0.0037052 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
GUAYAMA | 2021-08-05 19:56 | 2021-08-06 11:04 | 15 | 015:08 | P | TRANSFORMADOR AVERIADO | SE FIJO BAJANTE EN XMR SAFADO | P21080500073 | New_Event | Service Transformer Failure | Include | Include | Equipment | 908 | 2021-08-05 | 13620 | keep | 0 | Aug | 2021 | 0.0092765 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-08-05 20:05 | 2021-08-05 20:06 | 824 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 95% POR EL 1909-04 | S21080500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-05 | 824 | keep | 0 | Aug | 2021 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
BAYAMON | 2021-08-05 20:05 | 2021-08-05 20:06 | 2720 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA 95% 1115-05 | S21080500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-05 | 2720 | keep | 0 | Aug | 2021 | 0.0018526 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
ARECIBO | 2021-08-05 20:32 | 2021-08-06 11:53 | 150 | 015:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | A21080500092 | New_Event | Cutout Failure | Include | Include | Equipment | 921 | 2021-08-05 | 138150 | keep | 0 | Aug | 2021 | 0.094093 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-08-05 20:43 | 2021-08-06 10:06 | 115 | 013:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE REMPLAZO UNA CAJA DE POLIMERO DE 100AMP EN FID31140478 | A21080500093 | New_Event | Cutout Failure | Include | Include | Equipment | 803 | 2021-08-05 | 92345 | keep | 0 | Aug | 2021 | 0.062896 | 7.8326e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 115
MAYAGÃœEZ | 2021-08-05 20:56 | 2021-08-05 22:01 | 40 | 001:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | M21080500120 | New_Event | Bad Weather | Include | Include | Weather | 65 | 2021-08-05 | 2600 | keep | 0 | Aug | 2021 | 0.0017708 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-05 21:11 | 2021-08-05 23:09 | 8 | 001:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN RISER | M21080500123 | New_Event | Bad Weather | Include | Include | Weather | 118 | 2021-08-05 | 944 | keep | 0 | Aug | 2021 | 0.00064295 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-08-05 21:16 | 2021-08-06 12:35 | 40 | 015:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN RISER DESCARGAS ELECTRICAS | M21080500124 | New_Event | Bad Weather | Include | Include | Weather | 919 | 2021-08-05 | 36760 | keep | 0 | Aug | 2021 | 0.025037 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-08-05 21:18 | 2021-08-06 10:48 | 100 | 013:30 | P | ESTRUCTURA AVERIADA | 1 X 65 EN CORTE DE LINEA SE ENDEREZO POSTE Y SE REINSTALO TENSOR PARTIDO QUE CAUSABA CRUCE DE LINEAS | A21080500100 | New_Event | Defective Pole | Include | Include | Equipment | 810 | 2021-08-05 | 81000 | keep | 0 | Aug | 2021 | 0.055169 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-08-05 21:33 | 2021-08-06 12:05 | 50 | 014:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 AMP EN CORTE DE LINEA AVE CRUZO LINEAS | P21080500076 | New_Event |  |  | Include | Wildlife | 872 | 2021-08-05 | 43600 | keep | 0 | Aug | 2021 | 0.029696 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-08-05 21:40 | 2021-08-06 12:31 | 50 | 014:51 | P | DESGANCHE | 1 X 30 Y 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21080500105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 891 | 2021-08-05 | 44550 | keep | 0 | Aug | 2021 | 0.030343 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-08-05 22:08 | 2021-08-06 15:20 | 1 | 017:12 | P | OTRAS CAUSAS | TIENE CONTADOR DANADO | P21080500077 | New_Event | Other Causes | Include | Include | Other | 1032 | 2021-08-05 | 1032 | keep | 0 | Aug | 2021 | 0.00070289 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-08-05 22:24 | 2021-08-06 10:00 | 250 | 011:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C21080500082 | New_Event | Cutout Failure | Include | Include | Equipment | 696 | 2021-08-05 | 174000 | keep | 0 | Aug | 2021 | 0.11851 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
SAN JUAN | 2021-08-05 22:36 | 2021-08-05 22:39 | 5400 | 000:03 | P | DESGANCHE | SE CERRO POR SCADA CARGA POR 1620 04 | S21080500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-08-05 | 16200 | keep | 0 | Aug | 2021 | 0.011034 | 0.0036779 | Momentary | FALSE | FALSE | Not_TMED_Event | 5400
SAN JUAN | 2021-08-05 22:36 | 2021-08-05 22:39 | 340 | 000:03 | P | DESGANCHE | SE CERRO POR SCADA CARGA POR 1620 04 | S21080500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-08-05 | 1020 | keep | 0 | Aug | 2021 | 0.00069472 | 0.00023157 | Momentary | FALSE | FALSE | Not_TMED_Event | 340
SAN JUAN | 2021-08-05 22:36 | 2021-08-05 22:39 | 36 | 000:03 | T | DESGANCHE | SE CERRO POR SCADA CARGA POR 1620 04 | S21080500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-08-05 | 108 | keep | 0 | Aug | 2021 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-08-05 22:36 | 2021-08-05 22:39 | 172 | 000:03 | T | DESGANCHE | SE CERRO POR SCADA LLEVA 1620 01 PARTE 1336 10 Y 1336 07 | S21080500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-08-05 | 516 | keep | 0 | Aug | 2021 | 0.00035145 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2021-08-05 22:39 | 2021-08-05 22:41 | 12 | 000:02 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR SE REALIZO DESGANCHE | S21080500287 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-08-05 | 24 | keep | 0 | Aug | 2021 | 1.6346e-05 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-08-05 22:41 | 2021-08-05 22:42 | 5400 | 000:01 | P | DESGANCHE | SE CERRO POR SCADA CARGA POR 1620 04 | S21080500000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-05 | 5400 | keep | 0 | Aug | 2021 | 0.0036779 | 0.0036779 | Momentary | FALSE | FALSE | Not_TMED_Event | 5400
SAN JUAN | 2021-08-05 22:41 | 2021-08-05 22:42 | 340 | 000:01 | P | DESGANCHE | SE CERRO POR SCADA CARGA POR 1620 04 | S21080500000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-05 | 340 | keep | 0 | Aug | 2021 | 0.00023157 | 0.00023157 | Momentary | FALSE | FALSE | Not_TMED_Event | 340
SAN JUAN | 2021-08-05 22:41 | 2021-08-05 22:42 | 36 | 000:01 | T | DESGANCHE | SE CERRO POR SCADA CARGA POR 1620 04 | S21080500000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-05 | 36 | keep | 0 | Aug | 2021 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-08-05 22:41 | 2021-08-05 22:42 | 172 | 000:01 | T | DESGANCHE | SE CERRO POR SCADA LLEVACARGA 1620 01 Y PARTE 1336 07 1336 10 | S21080500000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-05 | 172 | keep | 0 | Aug | 2021 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2021-08-05 22:42 | 2021-08-06 19:55 | 12 | 021:13 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR SE REALIZO DESGANCHE | S21080500287 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1273 | 2021-08-05 | 15276 | keep | 0 | Aug | 2021 | 0.010404 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-08-05 22:53 | 2021-08-06 10:30 | 150 | 011:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21080500129 | New_Event | Bad Weather | Include | Include | Weather | 697 | 2021-08-05 | 104550 | keep | 0 | Aug | 2021 | 0.071209 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
VEGA BAJA | 2021-08-05 23:13 | 2021-08-06 13:45 | 30 | 014:32 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | B21080600040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 872 | 2021-08-05 | 26160 | keep | 0 | Aug | 2021 | 0.017817 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-08-05 23:27 | 2021-08-06 09:10 | 150 | 009:43 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M21080500130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 583 | 2021-08-05 | 87450 | keep | 0 | Aug | 2021 | 0.059562 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
VEGA BAJA | 2021-08-05 23:43 | 2021-08-06 09:52 | 15 | 010:09 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | B21080500112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 609 | 2021-08-05 | 9135 | keep | 0 | Aug | 2021 | 0.0062218 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-08-06 00:15 | 2021-08-06 09:59 | 100 | 009:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 Y 1 X 65 EN CORTE DE LINEA CRUCE CON CULEBRA | R21080600002 | New_Event |  |  | Include | Wildlife | 584 | 2021-08-06 | 58400 | keep | 0 | Aug | 2021 | 0.039776 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-08-06 02:46 | 2021-08-06 10:27 | 397 | 007:41 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUA | C21080600001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 461 | 2021-08-06 | 183017 | keep | 0 | Aug | 2021 | 0.12465 | 0.00027039 | Sustained | FALSE | TRUE | Not_TMED_Event | 397
HUMACAO | 2021-08-06 05:08 | 2021-08-06 11:35 | 17 | 006:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO SECUNDARIA Y SE LEVANTO NEUTRAL PRIMARIO | C21080600003 | New_Event | Wire Down | Include | Include | Equipment | 387 | 2021-08-06 | 6579 | keep | 0 | Aug | 2021 | 0.0044809 | 1.1579e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 17
ARECIBO | 2021-08-06 06:28 | 2021-08-06 16:55 | 6 | 010:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | A21080600003 | New_Event | Bad Weather | Include | Include | Weather | 627 | 2021-08-06 | 3762 | keep | 0 | Aug | 2021 | 0.0025623 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2021-08-06 06:35 | 2021-08-06 13:35 | 60 | 007:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21080600005 | New_Event |  |  | Include | Wildlife | 420 | 2021-08-06 | 25200 | keep | 0 | Aug | 2021 | 0.017164 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-08-06 06:36 | 2021-08-06 12:35 | 16 | 005:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | C21080600006 | New_Event |  |  | Include | Wildlife | 359 | 2021-08-06 | 5744 | keep | 0 | Aug | 2021 | 0.0039122 | 1.0898e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 16
SAN JUAN | 2021-08-06 06:37 | 2021-08-06 06:38 | 761 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | S21080600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-06 | 761 | keep | 0 | Aug | 2021 | 0.00051831 | 0.00051831 | Momentary | FALSE | FALSE | Not_TMED_Event | 761
CAGUAS | 2021-08-06 06:37 | 2021-08-07 13:20 | 11 | 030:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO T-16 PARA REEMPLAZAR DOS PEDESTALES Y BARRAS AVERIADAS | C21080600007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1843 | 2021-08-06 | 20273 | keep | 0 | Aug | 2021 | 0.013808 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CANOVANAS | 2021-08-06 06:40 | 2021-08-06 06:41 | 4085 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | R21080600006 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-06 | 4085 | keep | 0 | Aug | 2021 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
SAN JUAN | 2021-08-06 06:41 | 2021-08-06 16:08 | 1 | 009:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA NO FUNDIO | R21080600029 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 567 | 2021-08-06 | 567 | keep | 0 | Aug | 2021 | 0.00038618 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CANOVANAS | 2021-08-06 07:01 | 2021-08-06 11:15 | 100 | 004:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21080600008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 254 | 2021-08-06 | 25400 | keep | 0 | Aug | 2021 | 0.0173 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-08-06 07:06 | 2021-08-06 07:08 | 3896 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C21080600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-06 | 7792 | keep | 0 | Aug | 2021 | 0.0053071 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
UTUADO | 2021-08-06 07:24 | 2021-08-06 13:20 | 50 | 005:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21080600006 | New_Event | Bad Weather | Include | Include | Weather | 356 | 2021-08-06 | 17800 | keep | 0 | Aug | 2021 | 0.012123 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-06 07:26 | 2021-08-06 15:00 | 12 | 007:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21080600007 | New_Event | Bad Weather | Include | Include | Weather | 454 | 2021-08-06 | 5448 | keep | 0 | Aug | 2021 | 0.0037106 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-08-06 07:37 | 2021-08-06 19:12 | 30 | 011:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21080600014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 695 | 2021-08-06 | 20850 | keep | 0 | Aug | 2021 | 0.014201 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-08-06 07:39 | 2021-08-06 07:40 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 99% 1909-09 | S21080600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-06 | 222 | keep | 0 | Aug | 2021 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2021-08-06 07:39 | 2021-08-06 07:40 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE 99% POR EL 1907-03 | S21080600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-06 | 222 | keep | 0 | Aug | 2021 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
SAN JUAN | 2021-08-06 08:00 | 2021-08-06 17:03 | 25 | 009:03 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21080600020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 543 | 2021-08-06 | 13575 | keep | 0 | Aug | 2021 | 0.0092459 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-08-06 08:09 | 2021-08-06 14:40 | 25 | 006:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 50 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA | B21080600007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 391 | 2021-08-06 | 9775 | keep | 0 | Aug | 2021 | 0.0066577 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-08-06 08:18 | 2021-08-06 12:06 | 30 | 003:48 | P | NO SE REPORTO CAUSA | 1 X 20 Y 1 X 40 EN CORTE DE LINEA | B21080600009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 228 | 2021-08-06 | 6840 | keep | 0 | Aug | 2021 | 0.0046587 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-08-06 08:21 | 2021-08-07 09:44 | 10 | 025:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21080600009 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1523 | 2021-08-06 | 15230 | keep | 0 | Aug | 2021 | 0.010373 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-08-06 08:24 | 2021-08-06 11:43 | 40 | 003:19 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | A21080600011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2021-08-06 | 7960 | keep | 0 | Aug | 2021 | 0.0054215 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-08-06 08:29 | 2021-08-06 11:47 | 15 | 003:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA LINEAS CRUZADAS | A21080600012 | New_Event | Wire Down | Include | Include | Equipment | 198 | 2021-08-06 | 2970 | keep | 0 | Aug | 2021 | 0.0020229 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-08-06 08:30 | 2021-08-06 22:38 | 50 | 014:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA Y SE CERRO CORTE DE LINEA | M21080600008 | New_Event | Wire Down | Include | Include | Equipment | 848 | 2021-08-06 | 42400 | keep | 0 | Aug | 2021 | 0.028878 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-06 08:34 | 2021-08-06 16:45 | 50 | 008:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | A21080600013 | New_Event | Bad Weather | Include | Include | Weather | 491 | 2021-08-06 | 24550 | keep | 0 | Aug | 2021 | 0.016721 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-08-06 08:43 | 2021-08-06 11:02 | 173 | 002:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C21080600159 | New_Event |  |  | Include | Wildlife | 139 | 2021-08-06 | 24047 | keep | 0 | Aug | 2021 | 0.016378 | 0.00011783 | Sustained | FALSE | TRUE | Not_TMED_Event | 173
MAYAGÃœEZ | 2021-08-06 08:49 | 2021-08-06 14:33 | 6 | 005:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR POR MAL TIEMPO | M21080600012 | New_Event | Bad Weather | Include | Include | Weather | 344 | 2021-08-06 | 2064 | keep | 0 | Aug | 2021 | 0.0014058 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2021-08-06 08:59 | 2021-08-06 17:51 | 20 | 008:52 | P | DESGANCHE | SE REALIZO DESGANCHE MASIVO | M21080600013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 532 | 2021-08-06 | 10640 | keep | 0 | Aug | 2021 | 0.0072469 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-08-06 09:11 | 2021-08-06 11:29 | 10 | 002:18 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21080600015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 138 | 2021-08-06 | 1380 | keep | 0 | Aug | 2021 | 0.00093991 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-08-06 09:19 | 2021-08-06 10:35 | 25 | 001:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | M21080600015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2021-08-06 | 1900 | keep | 0 | Aug | 2021 | 0.0012941 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CANOVANAS | 2021-08-06 09:24 | 2021-08-06 10:57 | 1 | 001:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE HACIA CAJA PRIMARIA | R21080600014 | New_Event | Wire Down | Include | Include | Equipment | 93 | 2021-08-06 | 93 | keep | 0 | Aug | 2021 | 6.3342e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2021-08-06 09:36 | 2021-08-06 17:35 | 40 | 007:59 | P | ESTRUCTURA AVERIADA | SE CAMBIO POSTE PRIMARIO DE EMERGENCIA | P21080600008 | New_Event | Defective Pole | Include | Include | Equipment | 479 | 2021-08-06 | 19160 | keep | 0 | Aug | 2021 | 0.01305 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2021-08-06 09:51 | 2021-08-06 12:22 | 99 | 002:31 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO CORNER BRAKET | R21080600017 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 151 | 2021-08-06 | 14949 | keep | 0 | Aug | 2021 | 0.010182 | 6.7428e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 99
YAUCO | 2021-08-06 09:52 | 2021-08-06 09:53 | 1352 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P210806000XX | New_Event |  |  | Include | Wildlife | 1 | 2021-08-06 | 1352 | keep | 0 | Aug | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
YAUCO | 2021-08-06 09:52 | 2021-08-06 09:53 | 3973 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210806000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-06 | 3973 | keep | 0 | Aug | 2021 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2021-08-06 09:53 | 2021-08-06 18:25 | 20 | 008:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA POR CONTACTO DE AVE | P21080600018 | New_Event |  |  | Include | Wildlife | 512 | 2021-08-06 | 10240 | keep | 0 | Aug | 2021 | 0.0069744 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
VEGA BAJA | 2021-08-06 10:06 | 2021-08-06 11:15 | 35 | 001:09 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | B21080600006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 69 | 2021-08-06 | 2415 | keep | 0 | Aug | 2021 | 0.0016448 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
HUMACAO | 2021-08-06 10:22 | 2021-08-06 16:52 | 7 | 006:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21080600019 | New_Event | Bad Weather | Include | Include | Weather | 390 | 2021-08-06 | 2730 | keep | 0 | Aug | 2021 | 0.0018594 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
BAYAMON | 2021-08-06 10:24 | 2021-08-06 10:25 | 748 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21080600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-06 | 748 | keep | 0 | Aug | 2021 | 0.00050946 | 0.00050946 | Momentary | FALSE | FALSE | Not_TMED_Event | 748
MAYAGÃœEZ | 2021-08-06 10:34 | 2021-08-06 10:35 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21080600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-06 | 393 | keep | 0 | Aug | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
BAYAMON | 2021-08-06 10:38 | 2021-08-06 14:14 | 12 | 003:36 | P | TRANSFORMADOR AVERIADO | 1 X 20 EN TRANSFORMADOR Y SE REEMPLAZO TRANSFORMADOR 37KVA AVERIADO POR 37KVA | S21080600016 | New_Event | Service Transformer Failure | Include | Include | Equipment | 216 | 2021-08-06 | 2592 | keep | 0 | Aug | 2021 | 0.0017654 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-08-06 10:44 | 2021-08-06 22:41 | 3 | 011:57 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PARTIDO Y SE CERRO MONTURA DE TRANSFORMADOR | M21080600035 | New_Event | Defective Pole | Include | Include | Equipment | 717 | 2021-08-06 | 2151 | keep | 0 | Aug | 2021 | 0.001465 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2021-08-06 10:53 | 2021-08-06 10:54 | 1526 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7800 | B21080600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-06 | 1526 | keep | 0 | Aug | 2021 | 0.0010394 | 0.0010394 | Momentary | FALSE | TRUE | Not_TMED_Event | 1526
VEGA BAJA | 2021-08-06 10:53 | 2021-08-06 10:54 | 308 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 | B21080600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-06 | 308 | keep | 0 | Aug | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | TRUE | Not_TMED_Event | 308
VEGA BAJA | 2021-08-06 10:53 | 2021-08-06 10:54 | 1397 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 | B21080600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-06 | 1397 | keep | 0 | Aug | 2021 | 0.00095149 | 0.00095149 | Momentary | FALSE | TRUE | Not_TMED_Event | 1397
VEGA BAJA | 2021-08-06 10:53 | 2021-08-06 10:54 | 2926 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 17200 | B21080600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-06 | 2926 | keep | 0 | Aug | 2021 | 0.0019929 | 0.0019929 | Momentary | FALSE | TRUE | Not_TMED_Event | 2926
MAYAGÃœEZ | 2021-08-06 10:58 | 2021-08-06 11:15 | 4 | 000:17 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR POR DESGANCHE | M21080600030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 17 | 2021-08-06 | 68 | keep | 0 | Aug | 2021 | 4.6314e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-08-06 11:03 | 2021-08-06 15:02 | 300 | 003:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA Y SE REALIZO DESGANCHE | M21080600031 | New_Event | Wire Down | Include | Include | Equipment | 239 | 2021-08-06 | 71700 | keep | 0 | Aug | 2021 | 0.048835 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
AGUADILLA | 2021-08-06 11:04 | 2021-08-08 10:57 | 1 | 047:53 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 20 EN SU-2 MAL TIEMPO DESCARGAS ELECTRICAS | M21080600032 | New_Event | Bad Weather | Include | Include | Weather | 2873 | 2021-08-06 | 2873 | keep | 0 | Aug | 2021 | 0.0019568 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-08-06 11:04 | 2021-08-06 14:30 | 75 | 003:26 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | A21080600046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2021-08-06 | 15450 | keep | 0 | Aug | 2021 | 0.010523 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
MAYAGÃœEZ | 2021-08-06 11:06 | 2021-08-06 11:07 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21080600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-06 | 393 | keep | 0 | Aug | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
UTUADO | 2021-08-06 11:14 | 2021-08-06 17:55 | 12 | 006:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO NEUTRAL SECUNDARIO | A21080600033 | New_Event | Secondary Wire Down | Include | Include | Equipment | 401 | 2021-08-06 | 4812 | keep | 0 | Aug | 2021 | 0.0032774 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-08-06 11:14 | 2021-08-06 15:40 | 10 | 004:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21080600034 | New_Event | Bad Weather | Include | Include | Weather | 266 | 2021-08-06 | 2660 | keep | 0 | Aug | 2021 | 0.0018117 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-08-06 11:17 | 2021-08-06 14:05 | 15 | 002:48 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 65 EN CORTE DE LINEA | S21080600069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 168 | 2021-08-06 | 2520 | keep | 0 | Aug | 2021 | 0.0017164 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CAGUAS | 2021-08-06 11:28 | 2021-08-06 15:38 | 90 | 004:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C21080600237 | New_Event |  |  | Include | Wildlife | 250 | 2021-08-06 | 22500 | keep | 0 | Aug | 2021 | 0.015325 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
CAGUAS | 2021-08-06 11:28 | 2021-08-06 13:50 | 157 | 002:22 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE PALMA | C21080600238 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2021-08-06 | 22294 | keep | 0 | Aug | 2021 | 0.015184 | 0.00010693 | Sustained | FALSE | TRUE | Not_TMED_Event | 157
BAYAMON | 2021-08-06 11:42 | 2021-08-06 16:48 | 8 | 005:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO BAJANTE Y SECUNDARIA | S21080600081 | New_Event | Secondary Wire Down | Include | Include | Equipment | 306 | 2021-08-06 | 2448 | keep | 0 | Aug | 2021 | 0.0016673 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-08-06 11:54 | 2021-08-06 14:06 | 1 | 002:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO TOMA Y SE REALIZO DESGANCHE | S21080400042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 132 | 2021-08-06 | 132 | keep | 0 | Aug | 2021 | 8.9905e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-08-06 11:57 | 2021-08-06 11:59 | 2106 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | R21080600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-06 | 4212 | keep | 0 | Aug | 2021 | 0.0028688 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
CANOVANAS | 2021-08-06 11:59 | 2021-08-06 20:05 | 100 | 008:06 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | R21080600039 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 486 | 2021-08-06 | 48600 | keep | 0 | Aug | 2021 | 0.033101 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-08-06 12:03 | 2021-08-06 16:26 | 15 | 004:23 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 37KVA X 37KVA | B21080600042 | New_Event | Service Transformer Failure | Include | Include | Equipment | 263 | 2021-08-06 | 3945 | keep | 0 | Aug | 2021 | 0.0026869 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-08-06 12:06 | 2021-08-06 14:37 | 150 | 002:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | M21080600043 | New_Event | Bad Weather | Include | Include | Weather | 151 | 2021-08-06 | 22650 | keep | 0 | Aug | 2021 | 0.015427 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-08-06 12:23 | 2021-08-06 17:44 | 570 | 005:21 | T | NO SE REPORTO CAUSA | SE REEMPLAZO FUSIBLE DE ALTA TRANSFORMADOR 125 EN SLOW SE LE HIZO PRUEBA A TRANSFORMADOR Y SE LE INSTALO TIERRAS A SUBESTACION CARGA POR 1338 02 | S21080600074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 321 | 2021-08-06 | 182970 | keep | 0 | Aug | 2021 | 0.12462 | 0.00038822 | Sustained | FALSE | FALSE | Not_TMED_Event | 570
SAN JUAN | 2021-08-06 12:23 | 2021-08-06 17:44 | 155 | 005:21 | T | NO SE REPORTO CAUSA | SE REEMPLAZO FUSIBLE DE ALTA TRANSFORMADOR 125 E SLOW SE LE HIZO PRUEBA A TRANSFORMADOR Y SE LE INSTALO TIERRAS A SUBESTACION CARGA POR 1338 02 | S21080600074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 321 | 2021-08-06 | 49755 | keep | 0 | Aug | 2021 | 0.033888 | 0.00010557 | Sustained | FALSE | FALSE | Not_TMED_Event | 155
SAN JUAN | 2021-08-06 12:23 | 2021-08-06 17:44 | 255 | 005:21 | S | NO SE REPORTO CAUSA | SE REEMPLAZO FUSIBLE DE ALTA TRANSFORMADOR 125 E SLOW SE LE HIZO PRUEBA A TRANSFORMADOR Y SE LE INSTALO TIERRAS A SUBESTACION ALIMENTADOR 1338 02 LLEVA CARGA 1328 05 1328 02 1422 05 Y PARTE DE 1422 03 | S21080600074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 321 | 2021-08-06 | 81855 | keep | 0 | Aug | 2021 | 0.055751 | 0.00017368 | Sustained | FALSE | FALSE | Not_TMED_Event | 255
SAN JUAN | 2021-08-06 12:23 | 2021-08-06 17:44 | 928 | 005:21 | S | NO SE REPORTO CAUSA | SE REEMPLAZO FUSIBLE DE ALTA TRANSFORMADOR 125 E SLOW SE LE HIZO PRUEBA A TRANSFORMADOR Y SE LE INSTALO TIERRAS A SUBESTACION ALIMENTADOR 1338 02 LLEVA CARGA 1328 05 1328 02 1422 05 Y PARTE DE 1422 03 | S21080600074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 321 | 2021-08-06 | 297888 | keep | 0 | Aug | 2021 | 0.20289 | 0.00063206 | Sustained | FALSE | FALSE | Not_TMED_Event | 928
SAN JUAN | 2021-08-06 12:23 | 2021-08-06 17:44 | 200 | 005:21 | S | NO SE REPORTO CAUSA | SE REEMPLAZO FUSIBLE DE ALTA TRANSFORMADOR 125 E SLOW SE LE HIZO PRUEBA A TRANSFORMADOR Y SE LE INSTALO TIERRAS A SUBESTACION ALIMENTADOR 1338 02 LLEVA CARGA 1328 05 1328 02 1422 05 Y PARTE DE 1422 03 | S21080600074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 321 | 2021-08-06 | 64200 | keep | 0 | Aug | 2021 | 0.043726 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-08-06 12:23 | 2021-08-06 17:44 | 185 | 005:21 | S | NO SE REPORTO CAUSA | SE REEMPLAZO FUSIBLE DE ALTA TRANSFORMADOR 125 E SLOW SE LE HIZO PRUEBA A TRANSFORMADOR Y SE LE INSTALO TIERRAS A SUBESTACION ALIMENTADOR 1338 02 LLEVA CARGA 1328 05 1328 02 1422 05 Y PARTE DE 1422 03 | S21080600074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 321 | 2021-08-06 | 59385 | keep | 0 | Aug | 2021 | 0.040447 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
SAN JUAN | 2021-08-06 12:23 | 2021-08-06 17:44 | 73 | 005:21 | S | NO SE REPORTO CAUSA | SE REEMPLAZO FUSIBLE DE ALTA TRANSFORMADOR 125 E SLOW SE LE HIZO PRUEBA A TRANSFORMADOR Y SE LE INSTALO TIERRAS A SUBESTACION ALIMENTADOR 1338 02 LLEVA CARGA 1328 05 1328 02 1422 05 Y PARTE DE 1422 03 | S21080600074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 321 | 2021-08-06 | 23433 | keep | 0 | Aug | 2021 | 0.01596 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
SAN JUAN | 2021-08-06 12:23 | 2021-08-06 17:44 | 186 | 005:21 | P | NO SE REPORTO CAUSA | SE REEMPLAZO FUSIBLE DE ALTA TRANSFORMADOR 125 E SLOW SE LE HIZO PRUEBA A TRANSFORMADOR Y SE LE INSTALO TIERRAS A SUBESTACION CARGA POR 1338 02 | S21080600074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 321 | 2021-08-06 | 59706 | keep | 0 | Aug | 2021 | 0.040665 | 0.00012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 186
SAN JUAN | 2021-08-06 12:23 | 2021-08-06 17:44 | 637 | 005:21 | T | NO SE REPORTO CAUSA | SE REMPLAZO FUSIBLE DE ALTA TRANSFORMADOR 125 E SLOW SE LE HIZO PRUEBA A TRANSFORMADOR Y SE LE INSTALO TIERRAS A SUBESTACION CARGA POR 1338 02 | S21080600074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 321 | 2021-08-06 | 204477 | keep | 0 | Aug | 2021 | 0.13927 | 0.00043386 | Sustained | FALSE | FALSE | Not_TMED_Event | 637
BAYAMON | 2021-08-06 12:26 | 2021-08-07 00:24 | 20 | 011:58 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN RISER SE SECCIONALIZO TRAMO SOTERRADO AVERIADO | B21080600040 | New_Event | UG Cable Fault | Include | Include | Equipment | 718 | 2021-08-06 | 14360 | keep | 0 | Aug | 2021 | 0.0097805 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-08-06 12:41 | 2021-08-09 17:30 | 20 | 076:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA Y SE CERRO CORTE DE LINEA | M21080600048 | New_Event | Wire Down | Include | Include | Equipment | 4609 | 2021-08-06 | 92180 | keep | 0 | Aug | 2021 | 0.062783 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-08-06 12:53 | 2021-08-06 13:57 | 20 | 001:04 | P | DESGANCHE | SE REPARO SECUNDARIA Y SE REALIZO DESGANCHE SECUNDARIO WR - 5893564 | S21080600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2021-08-06 | 1280 | keep | 0 | Aug | 2021 | 0.0008718 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-08-06 12:53 | 2021-08-06 17:04 | 20 | 004:11 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO ENREDADERA | C21080600773 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2021-08-06 | 5020 | keep | 0 | Aug | 2021 | 0.0034191 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
FAJARDO | 2021-08-06 12:58 | 2021-08-06 14:52 | 20 | 001:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA REMPLAZO CAJA QUEMADA | R21080600024 | New_Event | Cutout Failure | Include | Include | Equipment | 114 | 2021-08-06 | 2280 | keep | 0 | Aug | 2021 | 0.0015529 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-08-06 12:59 | 2021-08-06 14:28 | 10 | 001:29 | P | NO SE REPORTO CAUSA | 1 X 10 EN CORTE DE LINEA | B21080600042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 89 | 2021-08-06 | 890 | keep | 0 | Aug | 2021 | 0.00060617 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
SAN JUAN | 2021-08-06 13:12 | 2021-08-07 10:53 | 21 | 021:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA | S21080600103 | New_Event | Wire Down | Include | Include | Equipment | 1301 | 2021-08-06 | 27321 | keep | 0 | Aug | 2021 | 0.018608 | 1.4303e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 21
YAUCO | 2021-08-06 13:20 | 2021-08-06 21:30 | 10 | 008:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE HIZO DESGANCHE Y SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | P21080600022 | New_Event | Wire Down | Include | Include | Equipment | 490 | 2021-08-06 | 4900 | keep | 0 | Aug | 2021 | 0.0033374 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-08-06 13:31 | 2021-08-06 17:34 | 75 | 004:03 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21080600044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 243 | 2021-08-06 | 18225 | keep | 0 | Aug | 2021 | 0.012413 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
VEGA BAJA | 2021-08-06 13:31 | 2021-08-06 19:20 | 15 | 005:49 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR 50KVA | B21080600036 | New_Event | Service Transformer Failure | Include | Include | Equipment | 349 | 2021-08-06 | 5235 | keep | 0 | Aug | 2021 | 0.0035655 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-08-06 13:59 | 2021-08-06 14:04 | 2435 | 000:05 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1909-08 | S21080600000 | New_Event |  |  | Include | Wildlife | 5 | 2021-08-06 | 12175 | keep | 0 | Aug | 2021 | 0.0082923 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-08-06 13:59 | 2021-08-06 14:04 | 2956 | 000:05 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO INTERRUPTOR SE CERRO POR SCADA LLEVA 1907-05 | S21080600000 | New_Event |  |  | Include | Wildlife | 5 | 2021-08-06 | 14780 | keep | 0 | Aug | 2021 | 0.010067 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
ARECIBO | 2021-08-06 14:04 | 2021-08-06 15:30 | 10 | 001:26 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21080600046 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 86 | 2021-08-06 | 860 | keep | 0 | Aug | 2021 | 0.00058574 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-08-06 14:07 | 2021-08-06 16:30 | 25 | 002:23 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50 KVA X 50 KVA | C21080600958 | New_Event | Service Transformer Failure | Include | Include | Equipment | 143 | 2021-08-06 | 3575 | keep | 0 | Aug | 2021 | 0.0024349 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-08-06 14:13 | 2021-08-07 11:15 | 1 | 021:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21080600057 | New_Event | Bad Weather | Include | Include | Weather | 1262 | 2021-08-06 | 1262 | keep | 0 | Aug | 2021 | 0.00085954 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2021-08-06 14:22 | 2021-08-06 17:00 | 1 | 002:38 | P | OTRAS CAUSAS | DEFECTO INTERIOR | P21080600026 | New_Event | Other Causes | Include | Include | Other | 158 | 2021-08-06 | 158 | keep | 0 | Aug | 2021 | 0.00010761 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2021-08-06 14:43 | 2021-08-07 14:00 | 10 | 023:17 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | P21080600028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1397 | 2021-08-06 | 13970 | keep | 0 | Aug | 2021 | 0.0095149 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
GUAYAMA | 2021-08-06 14:44 | 2021-08-06 17:05 | 30 | 002:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR POR CONTACTO DE AVE | P21080600029 | New_Event |  |  | Include | Wildlife | 141 | 2021-08-06 | 4230 | keep | 0 | Aug | 2021 | 0.002881 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
FAJARDO | 2021-08-06 14:45 | 2021-08-06 15:27 | 100 | 000:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | R21080600030 | New_Event |  |  | Include | Wildlife | 42 | 2021-08-06 | 4200 | keep | 0 | Aug | 2021 | 0.0028606 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-08-06 14:56 | 2021-08-06 15:56 | 50 | 001:00 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21080600007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2021-08-06 | 3000 | keep | 0 | Aug | 2021 | 0.0020433 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-08-06 14:57 | 2021-08-06 15:53 | 11 | 000:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21080600432 | New_Event | Secondary Wire Down | Include | Include | Equipment | 56 | 2021-08-06 | 616 | keep | 0 | Aug | 2021 | 0.00041955 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
PONCE | 2021-08-06 15:05 | 2021-08-06 17:20 | 50 | 002:15 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE REPORTO CAUSA | P21080600032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 135 | 2021-08-06 | 6750 | keep | 0 | Aug | 2021 | 0.0045974 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-08-06 15:30 | 2021-08-06 17:57 | 85 | 002:27 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21080600031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2021-08-06 | 12495 | keep | 0 | Aug | 2021 | 0.0085103 | 5.7893e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 85
ARECIBO | 2021-08-06 15:30 | 2021-08-06 17:00 | 20 | 001:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON LIQUEO DE ACEITE DE 50 KVA, COOPER, 2055099535, 2400/ 120/240V. FID-33978655 | A21080600053 | New_Event | Service Transformer Failure | Include | Include | Equipment | 90 | 2021-08-06 | 1800 | keep | 0 | Aug | 2021 | 0.001226 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-08-06 15:46 | 2021-08-06 18:02 | 26 | 002:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA Y 1 X 20 EN RISER CRUCE POR AVE | C21080600967 | New_Event |  |  | Include | Wildlife | 136 | 2021-08-06 | 3536 | keep | 0 | Aug | 2021 | 0.0024084 | 1.7708e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 26
CAGUAS | 2021-08-06 15:46 | 2021-08-07 11:20 | 125 | 019:34 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTES DE LINEAS | C21080600968 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1174 | 2021-08-06 | 146750 | keep | 0 | Aug | 2021 | 0.099951 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
AGUADILLA | 2021-08-06 15:46 | 2021-08-06 16:50 | 569 | 001:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21080600081 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 64 | 2021-08-06 | 36416 | keep | 0 | Aug | 2021 | 0.024803 | 0.00038754 | Sustained | FALSE | TRUE | Not_TMED_Event | 569
AGUADILLA | 2021-08-06 15:46 | 2021-08-06 16:50 | 1245 | 001:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21080600081 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 64 | 2021-08-06 | 79680 | keep | 0 | Aug | 2021 | 0.05427 | 0.00084796 | Sustained | FALSE | TRUE | Not_TMED_Event | 1245
AGUADILLA | 2021-08-06 15:46 | 2021-08-06 16:50 | 1155 | 001:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21080600081 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 64 | 2021-08-06 | 73920 | keep | 0 | Aug | 2021 | 0.050347 | 0.00078667 | Sustained | FALSE | TRUE | Not_TMED_Event | 1155
AGUADILLA | 2021-08-06 15:46 | 2021-08-06 16:50 | 867 | 001:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21080600079 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 64 | 2021-08-06 | 55488 | keep | 0 | Aug | 2021 | 0.037793 | 0.00059051 | Sustained | FALSE | TRUE | Not_TMED_Event | 867
AGUADILLA | 2021-08-06 15:46 | 2021-08-06 16:50 | 257 | 001:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21080600079 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 64 | 2021-08-06 | 16448 | keep | 0 | Aug | 2021 | 0.011203 | 0.00017504 | Sustained | FALSE | TRUE | Not_TMED_Event | 257
AGUADILLA | 2021-08-06 15:46 | 2021-08-06 16:50 | 1336 | 001:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21080600079 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 64 | 2021-08-06 | 85504 | keep | 0 | Aug | 2021 | 0.058236 | 0.00090994 | Sustained | FALSE | TRUE | Not_TMED_Event | 1336
AGUADILLA | 2021-08-06 15:46 | 2021-08-06 16:50 | 3315 | 001:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21080600080 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 64 | 2021-08-06 | 212160 | keep | 0 | Aug | 2021 | 0.1445 | 0.0022578 | Sustained | FALSE | TRUE | Not_TMED_Event | 3315
AGUADILLA | 2021-08-06 15:46 | 2021-08-06 16:50 | 1718 | 001:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21080600080 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 64 | 2021-08-06 | 109952 | keep | 0 | Aug | 2021 | 0.074888 | 0.0011701 | Sustained | FALSE | TRUE | Not_TMED_Event | 1718
ARECIBO | 2021-08-06 15:47 | 2021-08-06 21:15 | 1644 | 005:28 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR. SE REPARO PUENTE PRIMARIO ABIERTO | A21080600000 | New_Event | Wire Down | Include | Include | Equipment | 328 | 2021-08-06 | 539232 | keep | 0 | Aug | 2021 | 0.36727 | 0.0011197 | Sustained | FALSE | FALSE | Not_TMED_Event | 1644
MAYAGÃœEZ | 2021-08-06 15:58 | 2021-08-06 17:20 | 3 | 001:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21080500058 | New_Event | Bad Weather | Include | Include | Weather | 82 | 2021-08-06 | 246 | keep | 0 | Aug | 2021 | 0.00016755 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
ARECIBO | 2021-08-06 16:00 | 2021-08-06 18:58 | 80 | 002:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | A21080600058 | New_Event | Bad Weather | Include | Include | Weather | 178 | 2021-08-06 | 14240 | keep | 0 | Aug | 2021 | 0.0096988 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-08-06 16:15 | 2021-08-06 17:45 | 528 | 001:30 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE PATRULLO Y NO SE DETECTO LA CAUSA | M21080600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 90 | 2021-08-06 | 47520 | keep | 0 | Aug | 2021 | 0.032366 | 0.00035962 | Sustained | FALSE | FALSE | Not_TMED_Event | 528
MAYAGÃœEZ | 2021-08-06 16:26 | 2021-08-06 17:20 | 2073 | 000:54 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO PARA RETIRAR ARBOL SOBRE LINEA PRIMARIA | M21080600098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2021-08-06 | 111942 | keep | 0 | Aug | 2021 | 0.076243 | 0.0014119 | Sustained | FALSE | TRUE | Not_TMED_Event | 2073
BAYAMON | 2021-08-06 16:49 | 2021-08-06 16:50 | 1362 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21080600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-06 | 1362 | keep | 0 | Aug | 2021 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
BAYAMON | 2021-08-06 16:50 | 2021-08-07 10:00 | 2 | 017:10 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | B21080600370 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1030 | 2021-08-06 | 2060 | keep | 0 | Aug | 2021 | 0.0014031 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2021-08-06 17:20 | 2021-08-06 22:04 | 200 | 004:44 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO PARA RETIRAR ARBOL SOBRE LINEA PRIMARIA | M21080600098 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 284 | 2021-08-06 | 56800 | keep | 0 | Aug | 2021 | 0.038686 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-06 17:21 | 2021-08-06 19:05 | 2435 | 001:44 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1909-08 | S21080600000 | Partial_restoration |  |  | Include | Wildlife | 104 | 2021-08-06 | 253240 | keep | 0 | Aug | 2021 | 0.17248 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-06 17:21 | 2021-08-06 19:05 | 2956 | 001:44 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO LLEVA 1907-05 | S21080600000 | Partial_restoration |  |  | Include | Wildlife | 104 | 2021-08-06 | 307424 | keep | 0 | Aug | 2021 | 0.20939 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-06 17:21 | 2021-08-06 20:20 | 25 | 002:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA DE 100 AMP | M21080500124 | New_Event | Cutout Failure | Include | Include | Equipment | 179 | 2021-08-06 | 4475 | keep | 0 | Aug | 2021 | 0.0030479 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-08-06 17:30 | 2021-08-07 11:40 | 20 | 018:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M21080600126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1090 | 2021-08-06 | 21800 | keep | 0 | Aug | 2021 | 0.014848 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-08-06 17:37 | 2021-08-07 12:15 | 3 | 018:38 | P | CABLE SOTERRADO AVERIADO | EN AVERIA SOTERRADA DEL RISER DE SALIDA DEL 1106-01 SE DEJO FUERA ESTA AREA SE ABRIO EN EL SU-32 Y SE CERRO N/O EN SU-36 | R21080600044 | New_Event | UG Cable Fault | Include | Include | Equipment | 1118 | 2021-08-06 | 3354 | keep | 0 | Aug | 2021 | 0.0022844 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-08-06 18:03 | 2021-08-07 11:46 | 30 | 017:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA SE RETIRO RATA CARGA POR EL 1909-08 | S21080600156 | New_Event |  |  | Include | Wildlife | 1063 | 2021-08-06 | 31890 | keep | 0 | Aug | 2021 | 0.02172 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-08-06 18:19 | 2021-08-06 20:42 | 150 | 002:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | S21080600159 | New_Event | Cutout Failure | Include | Include | Equipment | 143 | 2021-08-06 | 21450 | keep | 0 | Aug | 2021 | 0.014609 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-08-06 18:27 | 2021-08-06 18:28 | 3 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21080600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-06 | 3 | keep | 0 | Aug | 2021 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2021-08-06 18:30 | 2021-08-06 18:31 | 652 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 38KV 7800 | B21080600368 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-06 | 652 | keep | 0 | Aug | 2021 | 0.00044407 | 0.00044407 | Momentary | FALSE | TRUE | Not_TMED_Event | 652
VEGA BAJA | 2021-08-06 18:30 | 2021-08-06 18:31 | 2704 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 38KV | B21080600368 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-06 | 2704 | keep | 0 | Aug | 2021 | 0.0018417 | 0.0018417 | Momentary | FALSE | TRUE | Not_TMED_Event | 2704
VEGA BAJA | 2021-08-06 18:31 | 2021-08-06 19:26 | 15 | 000:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21080600321 | New_Event | Secondary Wire Down | Include | Include | Equipment | 55 | 2021-08-06 | 825 | keep | 0 | Aug | 2021 | 0.0005619 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-08-06 18:40 | 2021-08-06 23:41 | 40 | 005:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | M21080600136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 301 | 2021-08-06 | 12040 | keep | 0 | Aug | 2021 | 0.0082004 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-08-06 18:48 | 2021-08-07 12:00 | 25 | 017:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO PRIMARIA Y SE CERRO CORTE DE LINEA | C21080600074 | New_Event | Wire Down | Include | Include | Equipment | 1032 | 2021-08-06 | 25800 | keep | 0 | Aug | 2021 | 0.017572 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-08-06 18:54 | 2021-08-06 18:55 | 3438 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21080600369 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-06 | 3438 | keep | 0 | Aug | 2021 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
MAYAGÃœEZ | 2021-08-06 18:57 | 2021-08-06 19:50 | 150 | 000:53 | P | DESGANCHE | SE TERMINO ABRIO CORTE DE LINEA PARA RETIRAR BAMBUAS SOBRE LINEA PRIMARIA | M21080600058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 53 | 2021-08-06 | 7950 | keep | 0 | Aug | 2021 | 0.0054147 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-08-06 19:03 | 2021-08-06 19:04 | 3300 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE LLEVA PARTE DE 1204-03 | S21080600000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-06 | 3300 | keep | 0 | Aug | 2021 | 0.0022476 | 0.0022476 | Momentary | FALSE | FALSE | Not_TMED_Event | 3300
SAN JUAN | 2021-08-06 19:03 | 2021-08-06 19:04 | 530 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE PARTE CARGA POR 1204-02 | S21080600000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-06 | 530 | keep | 0 | Aug | 2021 | 0.00036098 | 0.00036098 | Momentary | FALSE | FALSE | Not_TMED_Event | 530
SAN JUAN | 2021-08-06 19:15 | 2021-08-06 19:16 | 3300 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE LLEVA PARTE CARGA 1204-03 | S21080600000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-08-06 | 3300 | keep | 0 | Aug | 2021 | 0.0022476 | 0.0022476 | Momentary | FALSE | FALSE | Not_TMED_Event | 3300
SAN JUAN | 2021-08-06 19:15 | 2021-08-06 19:16 | 530 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE PARTE CARGA POR 1204-02 | S21080600000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-08-06 | 530 | keep | 0 | Aug | 2021 | 0.00036098 | 0.00036098 | Momentary | FALSE | FALSE | Not_TMED_Event | 530
CANOVANAS | 2021-08-06 19:15 | 2021-08-06 21:30 | 80 | 002:15 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R21080600050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2021-08-06 | 10800 | keep | 0 | Aug | 2021 | 0.0073558 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-06 19:26 | 2021-08-06 19:27 | 1715 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL CARGA TRANSFERIDA AL 1707-03 | B21080600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-06 | 1715 | keep | 0 | Aug | 2021 | 0.0011681 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2021-08-06 19:26 | 2021-08-06 19:27 | 1498 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA CARGA DEL 1707-02 | B21080600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-06 | 1498 | keep | 0 | Aug | 2021 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
AGUADILLA | 2021-08-06 19:28 | 2021-08-08 15:37 | 12 | 044:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA ROTA | M21080600148 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2649 | 2021-08-06 | 31788 | keep | 0 | Aug | 2021 | 0.021651 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
SAN JUAN | 2021-08-06 19:35 | 2021-08-06 19:36 | 3300 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE LLEVA PARTE CARGA 1204-03 | S21080600000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-08-06 | 3300 | keep | 0 | Aug | 2021 | 0.0022476 | 0.0022476 | Momentary | FALSE | FALSE | Not_TMED_Event | 3300
SAN JUAN | 2021-08-06 19:35 | 2021-08-06 19:36 | 530 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE PARTE CARGA POR 1204-02 | S21080600000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1 | 2021-08-06 | 530 | keep | 0 | Aug | 2021 | 0.00036098 | 0.00036098 | Momentary | FALSE | FALSE | Not_TMED_Event | 530
ARECIBO | 2021-08-06 19:46 | 2021-08-06 20:45 | 300 | 000:59 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA POR DESGANCHE | A21080600088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2021-08-06 | 17700 | keep | 0 | Aug | 2021 | 0.012055 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
SAN JUAN | 2021-08-06 19:51 | 2021-08-06 23:22 | 3300 | 003:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO Y PARARRAYO AVERIADO LLEVA PARTE CARGA 1204-03 | S21080600000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 211 | 2021-08-06 | 696300 | keep | 0 | Aug | 2021 | 0.47425 | 0.0022476 | Sustained | FALSE | FALSE | Not_TMED_Event | 3300
SAN JUAN | 2021-08-06 19:51 | 2021-08-06 23:22 | 530 | 003:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO Y PARARRAYO AVERIADO PARTE POR 1204-02 | S21080600000 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 211 | 2021-08-06 | 111830 | keep | 0 | Aug | 2021 | 0.076167 | 0.00036098 | Sustained | FALSE | FALSE | Not_TMED_Event | 530
GUAYAMA | 2021-08-06 20:30 | 2021-08-06 23:00 | 200 | 002:30 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE REMOVIO BAMBUS | P21080600051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2021-08-06 | 30000 | keep | 0 | Aug | 2021 | 0.020433 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CANOVANAS | 2021-08-06 20:48 | 2021-08-07 10:06 | 6 | 013:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R21080600052 | New_Event |  |  | Include | Wildlife | 798 | 2021-08-06 | 4788 | keep | 0 | Aug | 2021 | 0.0032611 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-08-06 21:01 | 2021-08-06 21:02 | 1715 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL CARGA TRANSFERIDA AL 1707-03 | B21080600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-06 | 1715 | keep | 0 | Aug | 2021 | 0.0011681 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2021-08-06 21:01 | 2021-08-06 21:02 | 1498 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA CARGA DEL 1707-02 | B21080600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-06 | 1498 | keep | 0 | Aug | 2021 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
ARECIBO | 2021-08-06 21:07 | 2021-08-07 00:33 | 250 | 003:26 | P | SOBRECARGA | 1 X 200 EN CONVERTIDOR | A21080600101 | New_Event | Trip Due To Overload | Include | Include | Other | 206 | 2021-08-06 | 51500 | keep | 0 | Aug | 2021 | 0.035076 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
MAYAGÃœEZ | 2021-08-06 21:35 | 2021-08-06 21:36 | 1417 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR POR DESCARGAS ELECTRICAS | M21080600158 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-08-06 | 1417 | keep | 0 | Aug | 2021 | 0.00096511 | 0.00096511 | Momentary | FALSE | FALSE | Not_TMED_Event | 1417
MAYAGÃœEZ | 2021-08-06 21:50 | 2021-08-07 11:00 | 25 | 013:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21080600159 | New_Event | Bad Weather | Include | Include | Weather | 790 | 2021-08-06 | 19750 | keep | 0 | Aug | 2021 | 0.013452 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-08-06 22:26 | 2021-08-07 18:33 | 20 | 020:07 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVISIONAL HACIA T-6 | B21080600381 | New_Event | UG Cable Fault | Include | Include | Equipment | 1207 | 2021-08-06 | 24140 | keep | 0 | Aug | 2021 | 0.016442 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-08-06 22:36 | 2021-08-07 09:59 | 60 | 011:23 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21080600382 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 683 | 2021-08-06 | 40980 | keep | 0 | Aug | 2021 | 0.027911 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-08-06 22:55 | 2021-08-07 12:25 | 60 | 013:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21080600113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 810 | 2021-08-06 | 48600 | keep | 0 | Aug | 2021 | 0.033101 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-08-06 23:40 | 2021-08-07 12:01 | 19 | 012:21 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S21080600210 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 741 | 2021-08-06 | 14079 | keep | 0 | Aug | 2021 | 0.0095891 | 1.2941e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 19
SAN JUAN | 2021-08-07 00:22 | 2021-08-07 00:23 | 2640 | 000:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE LLEVA PARTE CARGA 1204 03 LLEVA 80% DE SU CARGA | S21080700000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-08-07 | 2640 | keep | 0 | Aug | 2021 | 0.0017981 | 0.0017981 | Momentary | FALSE | FALSE | Not_TMED_Event | 2640
SAN JUAN | 2021-08-07 00:22 | 2021-08-07 00:23 | 530 | 000:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE PARTE CARGA POR 1204 02 | S21080700000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-08-07 | 530 | keep | 0 | Aug | 2021 | 0.00036098 | 0.00036098 | Momentary | FALSE | FALSE | Not_TMED_Event | 530
SAN JUAN | 2021-08-07 00:23 | 2021-08-08 18:16 | 12 | 041:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR Y SE REEMPLAZO CAJA PRIMARIA | S21080700022 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 2513 | 2021-08-07 | 30156 | keep | 0 | Aug | 2021 | 0.020539 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-08-07 00:24 | 2021-08-07 00:25 | 5809 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE | B21080700000 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1 | 2021-08-07 | 5809 | keep | 0 | Aug | 2021 | 0.0039565 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-07 00:25 | 2021-08-07 13:19 | 25 | 012:54 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO DEL T-8 AL T-9 | B21080600040 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 774 | 2021-08-07 | 19350 | keep | 0 | Aug | 2021 | 0.013179 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-08-07 00:39 | 2021-08-09 17:40 | 50 | 065:01 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU-10 | S21080700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3901 | 2021-08-07 | 195050 | keep | 0 | Aug | 2021 | 0.13285 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-08-07 01:03 | 2021-08-07 01:04 | 2234 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | B21080700000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-08-07 | 2234 | keep | 0 | Aug | 2021 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2021-08-07 01:04 | 2021-08-07 17:14 | 12 | 016:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA EN TRANSFORMADOR | B21080700039 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 970 | 2021-08-07 | 11640 | keep | 0 | Aug | 2021 | 0.007928 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-08-07 02:13 | 2021-08-07 11:35 | 1 | 009:22 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO PARARRAYO | B21080700003 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 562 | 2021-08-07 | 562 | keep | 0 | Aug | 2021 | 0.00038278 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-08-07 02:19 | 2021-08-07 02:20 | 519 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21080700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-07 | 519 | keep | 0 | Aug | 2021 | 0.00035349 | 0.00035349 | Momentary | FALSE | FALSE | Not_TMED_Event | 519
CANOVANAS | 2021-08-07 03:29 | 2021-08-07 09:32 | 169 | 006:03 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE DESGANCHO | R21080700002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 363 | 2021-08-07 | 61347 | keep | 0 | Aug | 2021 | 0.041783 | 0.00011511 | Sustained | FALSE | TRUE | Not_TMED_Event | 169
CAGUAS | 2021-08-07 06:35 | 2021-08-07 12:32 | 108 | 005:57 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA REEMPLAZO PARARRAYO | C21080700003 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 357 | 2021-08-07 | 38556 | keep | 0 | Aug | 2021 | 0.02626 | 7.3558e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 108
CAGUAS | 2021-08-07 06:56 | 2021-08-07 14:51 | 100 | 007:55 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTES DE LINEA | C21080700004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 475 | 2021-08-07 | 47500 | keep | 0 | Aug | 2021 | 0.032352 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-08-07 07:14 | 2021-08-07 13:14 | 40 | 006:00 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21080700007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 360 | 2021-08-07 | 14400 | keep | 0 | Aug | 2021 | 0.0098078 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-08-07 07:19 | 2021-08-07 12:50 | 60 | 005:31 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21080700002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 331 | 2021-08-07 | 19860 | keep | 0 | Aug | 2021 | 0.013527 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-08-07 07:36 | 2021-08-07 14:34 | 50 | 006:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA RETEZO CONDUCTORES | C21080700008 | New_Event |  |  | Include | Wildlife | 418 | 2021-08-07 | 20900 | keep | 0 | Aug | 2021 | 0.014235 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-07 07:37 | 2021-08-07 07:38 | 2402 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21080700009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-07 | 2402 | keep | 0 | Aug | 2021 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2021-08-07 07:38 | 2021-08-07 13:12 | 5 | 005:34 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B21080600361 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 334 | 2021-08-07 | 1670 | keep | 0 | Aug | 2021 | 0.0011374 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-08-07 07:54 | 2021-08-07 07:55 | 2190 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21080700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-07 | 2190 | keep | 0 | Aug | 2021 | 0.0014916 | 0.0014916 | Momentary | FALSE | FALSE | Not_TMED_Event | 2190
CANOVANAS | 2021-08-07 07:56 | 2021-08-07 07:57 | 2708 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | R21080700003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-07 | 2708 | keep | 0 | Aug | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
SAN JUAN | 2021-08-07 08:03 | 2021-08-07 08:04 | 5062 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | R21080700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-07 | 5062 | keep | 0 | Aug | 2021 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
SAN JUAN | 2021-08-07 08:06 | 2021-08-07 08:07 | 2000 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR CARGA POR SPARE 1619-02 | R21080700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-07 | 2000 | keep | 0 | Aug | 2021 | 0.0013622 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
SAN JUAN | 2021-08-07 08:07 | 2021-08-07 14:26 | 29 | 006:19 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO PENCA DE LA LINEA | R21080700004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 379 | 2021-08-07 | 10991 | keep | 0 | Aug | 2021 | 0.0074859 | 1.9752e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 29
BAYAMON | 2021-08-07 08:33 | 2021-08-07 15:33 | 8 | 007:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21080700011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 420 | 2021-08-07 | 3360 | keep | 0 | Aug | 2021 | 0.0022885 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-08-07 08:33 | 2021-08-07 08:34 | 1514 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9100 | B21080700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-07 | 1514 | keep | 0 | Aug | 2021 | 0.0010312 | 0.0010312 | Momentary | FALSE | TRUE | Not_TMED_Event | 1514
BAYAMON | 2021-08-07 08:33 | 2021-08-07 08:34 | 1105 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA | B21080700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-07 | 1105 | keep | 0 | Aug | 2021 | 0.00075261 | 0.00075261 | Momentary | FALSE | TRUE | Not_TMED_Event | 1105
VEGA BAJA | 2021-08-07 08:39 | 2021-08-07 13:15 | 30 | 004:36 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU-7 | B21080700013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 276 | 2021-08-07 | 8280 | keep | 0 | Aug | 2021 | 0.0056395 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-08-07 08:49 | 2021-08-07 10:36 | 12 | 001:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | R21080600054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 107 | 2021-08-07 | 1284 | keep | 0 | Aug | 2021 | 0.00087453 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-08-07 08:53 | 2021-08-07 08:54 | 1879 | 000:01 | T | SECUNDARIA/ESTRUCTURA AVERIADA | DISPARO DE INTERRUPTOR SE CERRO SCADA | C21080700014 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 1 | 2021-08-07 | 1879 | keep | 0 | Aug | 2021 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
ARECIBO | 2021-08-07 09:10 | 2021-08-07 14:18 | 125 | 005:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 50 EN CORTE DE LINEA SE REEMPLAZO AISLADOR ROTO | A21080700008 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 308 | 2021-08-07 | 38500 | keep | 0 | Aug | 2021 | 0.026222 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
SAN JUAN | 2021-08-07 09:17 | 2021-08-07 15:00 | 65 | 005:43 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | S21080700019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 343 | 2021-08-07 | 22295 | keep | 0 | Aug | 2021 | 0.015185 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
AGUADILLA | 2021-08-07 09:30 | 2021-08-07 16:00 | 20 | 006:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR NEUTRAL PRIMARIO Y REALIZAR DESGANCHE | M21080700031 | New_Event | Wire Down | Include | Include | Equipment | 390 | 2021-08-07 | 7800 | keep | 0 | Aug | 2021 | 0.0053125 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
FAJARDO | 2021-08-07 09:34 | 2021-08-07 11:30 | 12 | 001:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 10 EN TRANSFORMADOR SE RETEZO LINEA SECUNDARIA Y SE REPARO NEUTRAL | R21080700006 | New_Event | Secondary Wire Down | Include | Include | Equipment | 116 | 2021-08-07 | 1392 | keep | 0 | Aug | 2021 | 0.00094808 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
PONCE | 2021-08-07 09:47 | 2021-08-07 18:30 | 10 | 008:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR | P21080700006 | New_Event |  |  | Include | Wildlife | 523 | 2021-08-07 | 5230 | keep | 0 | Aug | 2021 | 0.0035621 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-07 09:48 | 2021-08-07 10:40 | 86 | 000:52 | P | OTRAS CAUSAS | SE ABRIO CORTE DE LINEA PARA PASARLO A OTRA FASE POR DESBALANCE EN LA LINEA SE PASO DE FASE C @ FASE A DE HIZO H/C A GIS UPDATES | A21080700010 | New_Event | Other Causes | Include | Include | Other | 52 | 2021-08-07 | 4472 | keep | 0 | Aug | 2021 | 0.0030459 | 5.8574e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 86
HUMACAO | 2021-08-07 10:42 | 2021-08-07 20:02 | 30 | 009:20 | P | SECUNDARIA/ESTRUCTURA AVERIADA | 1 X 30 EN CORTE DE LINEA REMPLAZO POSTE SECUNDARIO Y RETEZO LINEA PRIMARIA | C21080700023 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 560 | 2021-08-07 | 16800 | keep | 0 | Aug | 2021 | 0.011442 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-08-07 10:45 | 2021-08-09 10:51 | 20 | 048:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 20 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A21080700015 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 2886 | 2021-08-07 | 57720 | keep | 0 | Aug | 2021 | 0.039313 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
HUMACAO | 2021-08-07 10:50 | 2021-08-07 12:13 | 11 | 001:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | C21080700024 | New_Event |  |  | Include | Wildlife | 83 | 2021-08-07 | 913 | keep | 0 | Aug | 2021 | 0.00062184 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2021-08-07 10:55 | 2021-08-07 14:19 | 637 | 003:24 | T | HERRAJE ROTO O PODRIDO | SE ABRIO INTERRUPTOR PARA REMPLAZAR CRUCETAS PARTIDAS AUTORIZADO POR EL ING. CHRISTIAN FELICIANO | M21080700016 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 204 | 2021-08-07 | 129948 | keep | 0 | Aug | 2021 | 0.088507 | 0.00043386 | Sustained | FALSE | FALSE | Not_TMED_Event | 637
GUAYAMA | 2021-08-07 11:02 | 2021-08-07 14:47 | 8 | 003:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR REMPLAZO CAJA | P21080700008 | New_Event | Cutout Failure | Include | Include | Equipment | 225 | 2021-08-07 | 1800 | keep | 0 | Aug | 2021 | 0.001226 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-08-07 11:18 | 2021-08-07 11:19 | 6285 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21080700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-07 | 6285 | keep | 0 | Aug | 2021 | 0.0042807 | 0.0042807 | Momentary | FALSE | FALSE | Not_TMED_Event | 6285
PONCE | 2021-08-07 11:22 | 2021-08-07 11:23 | 3718 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | P210807000XX | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-08-07 | 3718 | keep | 0 | Aug | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
PONCE | 2021-08-07 11:23 | 2021-08-07 13:35 | 72 | 002:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA REMPLAZO CAJA | P21080700009 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 132 | 2021-08-07 | 9504 | keep | 0 | Aug | 2021 | 0.0064731 | 4.9039e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 72
MAYAGÃœEZ | 2021-08-07 11:25 | 2021-08-07 13:18 | 15 | 001:53 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZAR POSTE SECUNDARIO DE 35' DE METAL | M21080700018 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 113 | 2021-08-07 | 1695 | keep | 0 | Aug | 2021 | 0.0011545 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-08-07 11:26 | 2021-08-07 17:12 | 12 | 005:46 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA X 25 KVA | C21080700025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 346 | 2021-08-07 | 4152 | keep | 0 | Aug | 2021 | 0.0028279 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-08-07 11:55 | 2021-08-07 14:45 | 150 | 002:50 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21080700023 | New_Event | Bad Weather | Include | Include | Weather | 170 | 2021-08-07 | 25500 | keep | 0 | Aug | 2021 | 0.017368 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-08-07 11:56 | 2021-08-07 11:57 | 1533 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA EL 1709-05 | S21080700025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-07 | 1533 | keep | 0 | Aug | 2021 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
BAYAMON | 2021-08-07 11:56 | 2021-08-07 11:57 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR 1709-03 | S21080700025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-07 | 2364 | keep | 0 | Aug | 2021 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
BAYAMON | 2021-08-07 11:57 | 2021-08-07 18:34 | 60 | 006:37 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21080700042 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 397 | 2021-08-07 | 23820 | keep | 0 | Aug | 2021 | 0.016224 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-08-07 12:23 | 2021-08-07 13:10 | 10 | 000:47 | P | DESGANCHE | 1 X 20 EN CORTES DE LINEA | S21080900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 47 | 2021-08-07 | 470 | keep | 0 | Aug | 2021 | 0.00032011 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-08-07 12:29 | 2021-08-08 11:26 | 12 | 022:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA Y SE REPARO BAJANTE PRIMARIO DE REALIZO DESGANCHE | A21080700023 | New_Event | Wire Down | Include | Include | Equipment | 1377 | 2021-08-07 | 16524 | keep | 0 | Aug | 2021 | 0.011254 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
CAGUAS | 2021-08-07 12:41 | 2021-08-07 14:42 | 7 | 002:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | C21080700028 | New_Event |  |  | Include | Wildlife | 121 | 2021-08-07 | 847 | keep | 0 | Aug | 2021 | 0.00057689 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-08-07 12:42 | 2021-08-07 12:43 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21080700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-07 | 393 | keep | 0 | Aug | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2021-08-07 12:42 | 2021-08-07 12:43 | 4 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6007-04 QUE LLEVA LA CARGA DEL 6007-05 | M21080700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-07 | 4 | keep | 0 | Aug | 2021 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-08-07 12:43 | 2021-08-07 14:38 | 4 | 001:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | M21080700028 | New_Event |  |  | Include | Wildlife | 115 | 2021-08-07 | 460 | keep | 0 | Aug | 2021 | 0.0003133 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
ARECIBO | 2021-08-07 13:10 | 2021-08-07 17:52 | 75 | 004:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO A CORTE DE LINEA | A21080700019 | New_Event | Wire Down | Include | Include | Equipment | 282 | 2021-08-07 | 21150 | keep | 0 | Aug | 2021 | 0.014405 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
CAGUAS | 2021-08-07 13:13 | 2021-08-07 17:11 | 150 | 003:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21080700030 | New_Event |  |  | Include | Wildlife | 238 | 2021-08-07 | 35700 | keep | 0 | Aug | 2021 | 0.024315 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-08-07 13:15 | 2021-08-07 16:45 | 8 | 003:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21080600043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 210 | 2021-08-07 | 1680 | keep | 0 | Aug | 2021 | 0.0011442 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2021-08-07 13:32 | 2021-08-07 14:50 | 5 | 001:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA AVERIADA Y PARARRAYO | R21080700008 | New_Event | Cutout Failure | Include | Include | Equipment | 78 | 2021-08-07 | 390 | keep | 0 | Aug | 2021 | 0.00026563 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2021-08-07 13:35 | 2021-08-07 14:35 | 163 | 001:00 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | R21080700009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2021-08-07 | 9780 | keep | 0 | Aug | 2021 | 0.0066611 | 0.00011102 | Sustained | FALSE | TRUE | Not_TMED_Event | 163
MAYAGÃœEZ | 2021-08-07 13:40 | 2021-08-07 15:25 | 100 | 001:45 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE AVERIADO | M21080700033 | New_Event | Switch Failure | Include | Include | Equipment | 105 | 2021-08-07 | 10500 | keep | 0 | Aug | 2021 | 0.0071515 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2021-08-07 13:50 | 2021-08-07 14:10 | 40 | 000:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRE CORTE DE LINEA PARA ENDEREZAR CAJA PRIMARIA | P21080700013 | New_Event | Cutout Failure | Include | Include | Equipment | 20 | 2021-08-07 | 800 | keep | 0 | Aug | 2021 | 0.00054488 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-08-07 13:55 | 2021-08-07 15:52 | 5 | 001:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR TOMA | C21080700032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 117 | 2021-08-07 | 585 | keep | 0 | Aug | 2021 | 0.00039844 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-08-07 14:15 | 2021-08-10 13:26 | 15 | 071:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO NEUTRAL SECUNDARIO | B21080700031 | New_Event | Wire Down | Include | Include | Equipment | 4271 | 2021-08-07 | 64065 | keep | 0 | Aug | 2021 | 0.043634 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-08-07 14:20 | 2021-08-07 19:40 | 40 | 005:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO Y SE REPARO BAJANTE DE TRANSFORMADOR | M21080700035 | New_Event | Wire Down | Include | Include | Equipment | 320 | 2021-08-07 | 12800 | keep | 0 | Aug | 2021 | 0.008718 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-08-07 14:24 | 2021-08-07 17:34 | 25 | 003:10 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21080700033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 190 | 2021-08-07 | 4750 | keep | 0 | Aug | 2021 | 0.0032352 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
HUMACAO | 2021-08-07 14:35 | 2021-08-07 14:37 | 2450 | 000:02 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO NO RECERRO | C21080700034 | New_Event |  |  | Include | Wildlife | 2 | 2021-08-07 | 4900 | keep | 0 | Aug | 2021 | 0.0033374 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2021-08-07 14:37 | 2021-08-07 15:58 | 40 | 001:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C21080700036 | 1st_after_momentary |  |  | Include | Wildlife | 81 | 2021-08-07 | 3240 | keep | 0 | Aug | 2021 | 0.0022067 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-07 14:37 | 2021-08-07 14:38 | 1097 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS | M21080700038 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-08-07 | 1097 | keep | 0 | Aug | 2021 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
BAYAMON | 2021-08-07 14:50 | 2021-08-07 18:50 | 30 | 004:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE SUBIO PRIMARIA | B21080600974 | New_Event | Wire Down | Include | Include | Equipment | 240 | 2021-08-07 | 7200 | keep | 0 | Aug | 2021 | 0.0049039 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-08-07 14:57 | 2021-08-08 09:59 | 80 | 019:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21080700028 | New_Event | Bad Weather | Include | Include | Weather | 1142 | 2021-08-07 | 91360 | keep | 0 | Aug | 2021 | 0.062225 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-08-07 14:59 | 2021-08-08 10:04 | 60 | 019:05 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSO | M21080700040 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1145 | 2021-08-07 | 68700 | keep | 0 | Aug | 2021 | 0.046791 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
PONCE | 2021-08-07 15:04 | 2021-08-07 17:18 | 66 | 002:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | P21080700015 | New_Event | Bad Weather | Include | Include | Weather | 134 | 2021-08-07 | 8844 | keep | 0 | Aug | 2021 | 0.0060236 | 4.4952e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 66
MAYAGÃœEZ | 2021-08-07 15:17 | 2021-08-07 17:15 | 60 | 001:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | M21080700043 | New_Event | Cutout Failure | Include | Include | Equipment | 118 | 2021-08-07 | 7080 | keep | 0 | Aug | 2021 | 0.0048222 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-08-07 15:18 | 2021-08-07 17:23 | 40 | 002:05 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C21080700037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 125 | 2021-08-07 | 5000 | keep | 0 | Aug | 2021 | 0.0034055 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-08-07 15:35 | 2021-08-07 16:10 | 1 | 000:35 | P | NO SE REPORTO CAUSA | 1 X 10 EN BANCO DE TRANSFORMADORES | B21080600405 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 35 | 2021-08-07 | 35 | keep | 0 | Aug | 2021 | 2.3838e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-08-07 15:47 | 2021-08-07 19:50 | 80 | 004:03 | P | DESGANCHE | 1 X 30 Y 1 X 40 EN CORTES DE LINEA | C21080700042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2021-08-07 | 19440 | keep | 0 | Aug | 2021 | 0.01324 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-08-07 15:51 | 2021-08-07 19:25 | 100 | 003:34 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN CORTE DE LINEA REMPLAZO 2 PARARRAYOS | C21080700043 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 214 | 2021-08-07 | 21400 | keep | 0 | Aug | 2021 | 0.014575 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-08-07 15:55 | 2021-08-07 18:16 | 80 | 002:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA REMPLAZO PORTAFUSIBLE QUEMADO | C21080700047 | New_Event | Cutout Failure | Include | Include | Equipment | 141 | 2021-08-07 | 11280 | keep | 0 | Aug | 2021 | 0.0076828 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-08-07 15:58 | 2021-08-08 13:11 | 5 | 021:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M21080700047 | New_Event | Wire Down | Include | Include | Equipment | 1273 | 2021-08-07 | 6365 | keep | 0 | Aug | 2021 | 0.0043352 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-08-07 16:10 | 2021-08-07 17:45 | 60 | 001:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21080700051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2021-08-07 | 5700 | keep | 0 | Aug | 2021 | 0.0038822 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
GUAYAMA | 2021-08-07 16:20 | 2021-08-07 16:21 | 215 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210807000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-07 | 215 | keep | 0 | Aug | 2021 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
GUAYAMA | 2021-08-07 16:28 | 2021-08-07 16:29 | 4132 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21080700018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-07 | 4132 | keep | 0 | Aug | 2021 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
CANOVANAS | 2021-08-07 16:29 | 2021-08-07 16:30 | 2708 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | R21080700014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-07 | 2708 | keep | 0 | Aug | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
UTUADO | 2021-08-07 16:29 | 2021-08-08 11:50 | 20 | 019:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21080700032 | New_Event | Bad Weather | Include | Include | Weather | 1161 | 2021-08-07 | 23220 | keep | 0 | Aug | 2021 | 0.015815 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BARRANQUITAS | 2021-08-07 16:33 | 2021-08-07 18:47 | 40 | 002:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21080700050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2021-08-07 | 5360 | keep | 0 | Aug | 2021 | 0.0036507 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-08-07 17:14 | 2021-08-07 17:16 | 2234 | 000:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO Y SE CERRO POR SCADA | B21080700045 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2021-08-07 | 4468 | keep | 0 | Aug | 2021 | 0.0030431 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2021-08-07 17:16 | 2021-08-07 18:27 | 12 | 001:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA EN TRANSFORMADOR | B21080700039 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 71 | 2021-08-07 | 852 | keep | 0 | Aug | 2021 | 0.00058029 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2021-08-07 17:34 | 2021-08-07 18:29 | 36 | 000:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO SPACER | B21080600364 | New_Event | Wire Down | Include | Include | Equipment | 55 | 2021-08-07 | 1980 | keep | 0 | Aug | 2021 | 0.0013486 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
MAYAGÃœEZ | 2021-08-07 17:38 | 2021-08-07 17:39 | 4641 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DEL INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS | M21080700000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-08-07 | 4641 | keep | 0 | Aug | 2021 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
PONCE | 2021-08-07 17:55 | 2021-08-07 17:56 | 1478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21080700021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-07 | 1478 | keep | 0 | Aug | 2021 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
AGUADILLA | 2021-08-07 18:12 | 2021-08-08 18:32 | 6 | 024:20 | P | SECUNDARIA/DESGANCHE | SE REPARO LINEA SECUNDARIA PARTIDA REQUIERE DESGANCHE | M21080700053 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1460 | 2021-08-07 | 8760 | keep | 0 | Aug | 2021 | 0.0059664 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
BAYAMON | 2021-08-07 18:31 | 2021-08-07 19:38 | 30 | 001:07 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21080600365 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2021-08-07 | 2010 | keep | 0 | Aug | 2021 | 0.001369 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-08-07 18:40 | 2021-08-07 22:19 | 45 | 003:39 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | M21080700057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2021-08-07 | 9855 | keep | 0 | Aug | 2021 | 0.0067122 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
FAJARDO | 2021-08-07 18:50 | 2021-08-08 08:48 | 1 | 013:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | R21080700016 | New_Event | Bad Weather | Include | Include | Weather | 838 | 2021-08-07 | 838 | keep | 0 | Aug | 2021 | 0.00057076 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
FAJARDO | 2021-08-07 18:55 | 2021-08-08 10:03 | 25 | 015:08 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R21080800017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 908 | 2021-08-07 | 22700 | keep | 0 | Aug | 2021 | 0.015461 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
VEGA BAJA | 2021-08-07 19:06 | 2021-08-08 16:57 | 60 | 021:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B21080800049 | New_Event | Cutout Failure | Include | Include | Equipment | 1311 | 2021-08-07 | 78660 | keep | 0 | Aug | 2021 | 0.053575 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
PONCE | 2021-08-07 19:20 | 2021-08-07 19:21 | 2446 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21080700024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-07 | 2446 | keep | 0 | Aug | 2021 | 0.001666 | 0.001666 | Momentary | FALSE | FALSE | Not_TMED_Event | 2446
BAYAMON | 2021-08-07 19:21 | 2021-08-07 19:22 | 1715 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1708-03 Y SE CERRO POR SCADA LLEVA 1708-02 | B21080700050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-07 | 1715 | keep | 0 | Aug | 2021 | 0.0011681 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2021-08-07 19:21 | 2021-08-07 19:22 | 1498 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1708-03 Y SE CERRO POR SCADA LLEVA 1708-02 | B21080700050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-07 | 1498 | keep | 0 | Aug | 2021 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2021-08-07 20:51 | 2021-08-08 14:36 | 200 | 017:45 | P | NO SE REPORTO CAUSA | 1 X 200 EN CONVERTIDOR | B21080700055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1065 | 2021-08-07 | 213000 | keep | 0 | Aug | 2021 | 0.14507 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-08-07 21:39 | 2021-08-08 10:08 | 30 | 012:29 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21080700063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 749 | 2021-08-07 | 22470 | keep | 0 | Aug | 2021 | 0.015304 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
VEGA BAJA | 2021-08-07 21:53 | 2021-08-08 12:27 | 10 | 014:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA | B21080700067 | New_Event | Cutout Failure | Include | Include | Equipment | 874 | 2021-08-07 | 8740 | keep | 0 | Aug | 2021 | 0.0059528 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-08-07 22:04 | 2021-08-08 09:13 | 9 | 011:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO PORTAFUISBLE DEFECTUOSO Y CERRO FUSIBLE, NO FUNDIO. | R21080700020 | New_Event | Cutout Failure | Include | Include | Equipment | 669 | 2021-08-07 | 6021 | keep | 0 | Aug | 2021 | 0.0041009 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
HUMACAO | 2021-08-07 22:04 | 2021-08-08 09:56 | 15 | 011:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE CAJA A LINEA | C21080700064 | New_Event | Wire Down | Include | Include | Equipment | 712 | 2021-08-07 | 10680 | keep | 0 | Aug | 2021 | 0.0072741 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BARRANQUITAS | 2021-08-07 23:46 | 2021-08-08 11:12 | 14 | 011:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO SECUNDARIA | C21080700066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 686 | 2021-08-07 | 9604 | keep | 0 | Aug | 2021 | 0.0065412 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2021-08-07 23:52 | 2021-08-08 04:02 | 560 | 004:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO 1529-15 LLEVANDO 30% DEL 1346-02 SE SECCIONALIZO ABRIENDO MACHETES POR CONDUCTOR EN EL SUELO, PUENTE ABIERTO Y MACHETE QUEMADO EN DISTINTOS PUNTOS. | S21080700077 | New_Event | Wire Down | Include | Include | Equipment | 250 | 2021-08-07 | 140000 | keep | 0 | Aug | 2021 | 0.095353 | 0.00038141 | Sustained | FALSE | FALSE | Not_TMED_Event | 560
BAYAMON | 2021-08-07 23:52 | 2021-08-08 04:02 | 1802 | 004:10 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO 1529-15 LLEVANDO 30% 1346-02 SE SECCIONALIZO ABRIENDO MACHETES POR CONDUCTOR EN EL SUELO, PUENTE ABIERTO Y MACHETE QUEMADO EN DISTINTOS PUNTOS. SOLO ENTRO UN 30% DEL 1529-15 | S21080700077 | New_Event | Wire Down | Include | Include | Equipment | 250 | 2021-08-07 | 450500 | keep | 0 | Aug | 2021 | 0.30683 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
SAN JUAN | 2021-08-07 23:54 | 2021-08-08 02:02 | 1058 | 002:08 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3200 20% DEL 1336-08 A TRAVES DE PORTATIL #8 | S21080800011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 128 | 2021-08-07 | 135424 | keep | 0 | Aug | 2021 | 0.092237 | 0.0007206 | Sustained | FALSE | TRUE | Not_TMED_Event | 1058
SAN JUAN | 2021-08-07 23:54 | 2021-08-08 02:02 | 250 | 002:08 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3200 CARGA A TRAVES DE PORTATIL #8 VENEZUELA 13KV 1348-00 | S21080800011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 128 | 2021-08-07 | 32000 | keep | 0 | Aug | 2021 | 0.021795 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
SAN JUAN | 2021-08-07 23:54 | 2021-08-08 02:02 | 1290 | 002:08 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3200 CARGA A TRAVES DE PORTATIL #8 | S21080800011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 128 | 2021-08-07 | 165120 | keep | 0 | Aug | 2021 | 0.11246 | 0.00087861 | Sustained | FALSE | TRUE | Not_TMED_Event | 1290
BAYAMON | 2021-08-07 23:54 | 2021-08-07 23:57 | 946 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO 1525-05 LLEVANDO LA CARGA DEL 1525-02 | S21080700078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-08-07 | 2838 | keep | 0 | Aug | 2021 | 0.0019329 | 0.00064432 | Momentary | FALSE | FALSE | Not_TMED_Event | 946
BAYAMON | 2021-08-07 23:54 | 2021-08-07 23:57 | 937 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO 1525-05 LLEVANDO LA CARGA DEL 1525-02 | S21080700078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-08-07 | 2811 | keep | 0 | Aug | 2021 | 0.0019146 | 0.00063819 | Momentary | FALSE | FALSE | Not_TMED_Event | 937
BAYAMON | 2021-08-07 23:54 | 2021-08-07 23:55 | 1420 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1530-06 LLEVANDO EL 1526-02 | S21080700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-07 | 1420 | keep | 0 | Aug | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-08-07 23:54 | 2021-08-07 23:55 | 437 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1530-06 LLEVANDO EL 1526-02 | S21080700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-07 | 437 | keep | 0 | Aug | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2021-08-08 00:07 | 2021-08-08 08:58 | 40 | 008:51 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21080800014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 531 | 2021-08-08 | 21240 | keep | 0 | Aug | 2021 | 0.014466 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-08-08 01:04 | 2021-08-08 01:05 | 6197 | 000:01 | T | DESGANCHE | RECIERRE | C21080800001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-08 | 6197 | keep | 0 | Aug | 2021 | 0.0042207 | 0.0042207 | Momentary | FALSE | FALSE | Not_TMED_Event | 6197
CAGUAS | 2021-08-08 01:05 | 2021-08-08 10:28 | 179 | 009:23 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO ENREDADERA | C21080800008 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 563 | 2021-08-08 | 100777 | keep | 0 | Aug | 2021 | 0.068639 | 0.00012192 | Sustained | FALSE | TRUE | Not_TMED_Event | 179
BAYAMON | 2021-08-08 01:59 | 2021-08-08 02:00 | 1533 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA EL 1709-05 | S21080800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-08 | 1533 | keep | 0 | Aug | 2021 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
BAYAMON | 2021-08-08 01:59 | 2021-08-08 02:00 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR 1709-03 | S21080800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-08 | 2364 | keep | 0 | Aug | 2021 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
PONCE | 2021-08-08 02:10 | 2021-08-08 13:30 | 115 | 011:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | POSTE PARTIDO POR ACCIDENTE DE AUTO | P21080800004 | New_Event |  |  | Include | Wildlife | 680 | 2021-08-08 | 78200 | keep | 0 | Aug | 2021 | 0.053262 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
ARECIBO | 2021-08-08 02:53 | 2021-08-08 15:10 | 70 | 012:17 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21080800002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 737 | 2021-08-08 | 51590 | keep | 0 | Aug | 2021 | 0.035138 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BAYAMON | 2021-08-08 03:11 | 2021-08-09 12:41 | 100 | 033:30 | P | DESGANCHE | 3 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA Y DESGANCHE 1711-05 CARGA POR EL 1711-02 | B21080800004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2010 | 2021-08-08 | 201000 | keep | 0 | Aug | 2021 | 0.1369 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-08-08 03:31 | 2021-08-08 03:32 | 1228 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21080800002 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-08-08 | 1228 | keep | 0 | Aug | 2021 | 0.00083639 | 0.00083639 | Momentary | FALSE | FALSE | Not_TMED_Event | 1228
CAGUAS | 2021-08-08 03:32 | 2021-08-08 10:54 | 48 | 007:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C21080800007 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 442 | 2021-08-08 | 21216 | keep | 0 | Aug | 2021 | 0.01445 | 3.2693e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 48
BAYAMON | 2021-08-08 04:02 | 2021-08-08 12:37 | 40 | 008:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO MACHETE QUEMADO Y SE CERRARON MACHETES PREVIAMENTE ABIERTOS | S21080800019 | Partial_restoration | Wire Down | Include | Include | Equipment | 515 | 2021-08-08 | 20600 | keep | 0 | Aug | 2021 | 0.014031 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-08 04:02 | 2021-08-08 12:31 | 80 | 008:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y SE CERRARON MACHETES | S21080800000 | New_Event | Wire Down | Include | Include | Equipment | 509 | 2021-08-08 | 40720 | keep | 0 | Aug | 2021 | 0.027734 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-08-08 04:02 | 2021-08-08 10:16 | 150 | 006:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO Y SE CERRARON MACHETES PREVIAMENTE ABIERTOS | S21080800019 | New_Event | Wire Down | Include | Include | Equipment | 374 | 2021-08-08 | 56100 | keep | 0 | Aug | 2021 | 0.038209 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2021-08-08 04:09 | 2021-08-08 11:14 | 50 | 007:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21080800003 | New_Event | Bad Weather | Include | Include | Weather | 425 | 2021-08-08 | 21250 | keep | 0 | Aug | 2021 | 0.014473 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-08 05:28 | 2021-08-08 10:35 | 150 | 005:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 140 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A21080800005 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 307 | 2021-08-08 | 46050 | keep | 0 | Aug | 2021 | 0.031364 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-08-08 06:11 | 2021-08-08 09:46 | 1 | 003:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 30 EN CORTE DE LINEA CRUCE POR AVE | C21080800004 | New_Event |  |  | Include | Wildlife | 215 | 2021-08-08 | 215 | keep | 0 | Aug | 2021 | 0.00014644 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-08-08 06:24 | 2021-08-08 06:25 | 888 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M21080800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 888 | keep | 0 | Aug | 2021 | 0.00060481 | 0.00060481 | Momentary | FALSE | TRUE | Not_TMED_Event | 888
MAYAGÃœEZ | 2021-08-08 06:24 | 2021-08-08 06:25 | 393 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M21080800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 393 | keep | 0 | Aug | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | TRUE | Not_TMED_Event | 393
MAYAGÃœEZ | 2021-08-08 06:24 | 2021-08-08 06:25 | 4 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M21080800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 4 | keep | 0 | Aug | 2021 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | TRUE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-08-08 06:24 | 2021-08-08 06:25 | 372 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M21080800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 372 | keep | 0 | Aug | 2021 | 0.00025337 | 0.00025337 | Momentary | FALSE | TRUE | Not_TMED_Event | 372
MAYAGÃœEZ | 2021-08-08 06:24 | 2021-08-08 06:25 | 2530 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M21080800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 2530 | keep | 0 | Aug | 2021 | 0.0017232 | 0.0017232 | Momentary | FALSE | TRUE | Not_TMED_Event | 2530
MAYAGÃœEZ | 2021-08-08 06:24 | 2021-08-08 06:25 | 199 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M21080800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 199 | keep | 0 | Aug | 2021 | 0.00013554 | 0.00013554 | Momentary | FALSE | TRUE | Not_TMED_Event | 199
MAYAGÃœEZ | 2021-08-08 06:24 | 2021-08-08 06:25 | 312 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M21080800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 312 | keep | 0 | Aug | 2021 | 0.0002125 | 0.0002125 | Momentary | FALSE | TRUE | Not_TMED_Event | 312
MAYAGÃœEZ | 2021-08-08 06:24 | 2021-08-08 06:25 | 4641 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M21080800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 4641 | keep | 0 | Aug | 2021 | 0.003161 | 0.003161 | Momentary | FALSE | TRUE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2021-08-08 06:25 | 2021-08-08 06:40 | 667 | 000:15 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 6008-04 SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR LLEVA LA CARGA DEL 6003-03 | M21080800002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2021-08-08 | 10005 | keep | 0 | Aug | 2021 | 0.0068144 | 0.00045429 | Sustained | FALSE | TRUE | Not_TMED_Event | 667
MAYAGÃœEZ | 2021-08-08 06:25 | 2021-08-08 06:40 | 2530 | 000:15 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR | M21080800002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2021-08-08 | 37950 | keep | 0 | Aug | 2021 | 0.025848 | 0.0017232 | Sustained | FALSE | TRUE | Not_TMED_Event | 2530
VEGA BAJA | 2021-08-08 06:35 | 2021-08-08 10:37 | 80 | 004:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21080800007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2021-08-08 | 19360 | keep | 0 | Aug | 2021 | 0.013186 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-08-08 06:40 | 2021-08-09 10:17 | 1 | 027:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21080800069 | New_Event | Bad Weather | Include | Include | Weather | 1657 | 2021-08-08 | 1657 | keep | 0 | Aug | 2021 | 0.0011286 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-08-08 07:01 | 2021-08-08 15:00 | 12 | 007:59 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | A21080800000 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 479 | 2021-08-08 | 5748 | keep | 0 | Aug | 2021 | 0.0039149 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
FAJARDO | 2021-08-08 07:09 | 2021-08-08 08:47 | 40 | 001:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 Y 1 X 20 EN CORTES DE LINEAS Y 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R21080800001 | New_Event |  |  | Include | Wildlife | 98 | 2021-08-08 | 3920 | keep | 0 | Aug | 2021 | 0.0026699 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-08-08 07:14 | 2021-08-10 11:22 | 40 | 052:08 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU 1 | B21081000012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3128 | 2021-08-08 | 125120 | keep | 0 | Aug | 2021 | 0.085219 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2021-08-08 07:20 | 2021-08-08 15:10 | 50 | 007:50 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | P21080800020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 470 | 2021-08-08 | 23500 | keep | 0 | Aug | 2021 | 0.016006 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-08-08 07:42 | 2021-08-08 10:04 | 55 | 002:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | R21080800002 | New_Event |  |  | Include | Wildlife | 142 | 2021-08-08 | 7810 | keep | 0 | Aug | 2021 | 0.0053194 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
CAGUAS | 2021-08-08 07:42 | 2021-08-08 07:43 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21080800005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-08 | 1702 | keep | 0 | Aug | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
BAYAMON | 2021-08-08 07:51 | 2021-08-08 18:53 | 60 | 011:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA SECA EN PULL BOX | B21080800010 | New_Event | Cutout Failure | Include | Include | Equipment | 662 | 2021-08-08 | 39720 | keep | 0 | Aug | 2021 | 0.027053 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-08-08 08:19 | 2021-08-08 13:04 | 2558 | 004:45 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADORES ROTOS Y SE REPARO LINEA ZAFADA DE AISLADORES EN VARIOS POSTES DEL TRONCAL DEL ALIMENTADOR Y SE CERRO EL INTERRUPTOR | A21080800000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 285 | 2021-08-08 | 729030 | keep | 0 | Aug | 2021 | 0.49654 | 0.0017422 | Sustained | FALSE | TRUE | Not_TMED_Event | 2558
BAYAMON | 2021-08-08 08:26 | 2021-08-08 14:36 | 20 | 006:10 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50KVA AVERIADO POR UNO DE IGUAL CAPACIDAD | B21080700027 | New_Event | Service Transformer Failure | Include | Include | Equipment | 370 | 2021-08-08 | 7400 | keep | 0 | Aug | 2021 | 0.0050401 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-08-08 08:28 | 2021-08-08 08:29 | 3332 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO | B21080800014 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-08-08 | 3332 | keep | 0 | Aug | 2021 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
VEGA BAJA | 2021-08-08 08:29 | 2021-08-08 10:47 | 50 | 002:18 | P | CABLE SOTERRADO AVERIADO | 1 X 30 EN PROVISIONAL AEREO, SE SECCIONALIZO AVERIA | B21080800008 | New_Event | UG Cable Fault | Include | Include | Equipment | 138 | 2021-08-08 | 6900 | keep | 0 | Aug | 2021 | 0.0046996 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2021-08-08 08:49 | 2021-08-08 10:50 | 12 | 002:01 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | R21080800004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 121 | 2021-08-08 | 1452 | keep | 0 | Aug | 2021 | 0.00098895 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2021-08-08 08:49 | 2021-08-08 15:38 | 4 | 006:49 | P | TRANSFORMADOR AVERIADO | 1 X 15 EN TRANSFORMADOR REEMPLAZO TRANSFORMADOR AVERIADO DE 15 KVA X 15 KVA | R21080800004 | New_Event | Service Transformer Failure | Include | Include | Equipment | 409 | 2021-08-08 | 1636 | keep | 0 | Aug | 2021 | 0.0011143 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-08-08 08:53 | 2021-08-08 12:50 | 80 | 003:57 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A21080800019 | New_Event |  |  | Include | Wildlife | 237 | 2021-08-08 | 18960 | keep | 0 | Aug | 2021 | 0.012914 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
VEGA BAJA | 2021-08-08 08:58 | 2021-08-08 12:21 | 25 | 003:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE CAJA A LINEA | B21080800019 | New_Event | Wire Down | Include | Include | Equipment | 203 | 2021-08-08 | 5075 | keep | 0 | Aug | 2021 | 0.0034566 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-08-08 09:01 | 2021-08-08 09:02 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21080800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-08 | 3941 | keep | 0 | Aug | 2021 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
SAN JUAN | 2021-08-08 09:19 | 2021-08-08 12:00 | 90 | 002:41 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21080600006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2021-08-08 | 14490 | keep | 0 | Aug | 2021 | 0.0098691 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
CAGUAS | 2021-08-08 09:48 | 2021-08-08 14:06 | 503 | 004:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 200 EN CORTE DE LINEA SE LEVANTO NEUTRAL PRIMARIO | C21080800009 | New_Event | Wire Down | Include | Include | Equipment | 258 | 2021-08-08 | 129774 | keep | 0 | Aug | 2021 | 0.088388 | 0.00034259 | Sustained | FALSE | TRUE | Not_TMED_Event | 503
MAYAGÃœEZ | 2021-08-08 10:22 | 2021-08-08 13:13 | 20 | 002:51 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21080800012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2021-08-08 | 3420 | keep | 0 | Aug | 2021 | 0.0023293 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
VEGA BAJA | 2021-08-08 10:34 | 2021-08-09 14:50 | 10 | 028:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA AVERIADA | B21080800066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1696 | 2021-08-08 | 16960 | keep | 0 | Aug | 2021 | 0.011551 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-08-08 10:35 | 2021-08-08 10:59 | 10 | 000:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21080800030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 24 | 2021-08-08 | 240 | keep | 0 | Aug | 2021 | 0.00016346 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-08-08 10:39 | 2021-08-08 10:40 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21080800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-08 | 2354 | keep | 0 | Aug | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
HUMACAO | 2021-08-08 10:42 | 2021-08-08 10:43 | 3701 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE RIO BLANCO A NAGUABO | C21080800011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 3701 | keep | 0 | Aug | 2021 | 0.0025207 | 0.0025207 | Momentary | FALSE | TRUE | Not_TMED_Event | 3701
HUMACAO | 2021-08-08 10:42 | 2021-08-08 10:43 | 989 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE RIO BLANCO A NAGUABO | C21080800011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 989 | keep | 0 | Aug | 2021 | 0.0006736 | 0.0006736 | Momentary | FALSE | TRUE | Not_TMED_Event | 989
HUMACAO | 2021-08-08 10:42 | 2021-08-08 10:43 | 1467 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE RIO BLANCO A NAGUABO | C21080800011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 1467 | keep | 0 | Aug | 2021 | 0.00099917 | 0.00099917 | Momentary | FALSE | TRUE | Not_TMED_Event | 1467
MAYAGÃœEZ | 2021-08-08 10:49 | 2021-08-08 13:10 | 60 | 002:21 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21080800014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2021-08-08 | 8460 | keep | 0 | Aug | 2021 | 0.0057621 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-08-08 10:52 | 2021-08-08 12:54 | 100 | 002:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21080800012 | New_Event | Bad Weather | Include | Include | Weather | 122 | 2021-08-08 | 12200 | keep | 0 | Aug | 2021 | 0.0083094 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-08-08 10:58 | 2021-08-08 14:37 | 98 | 003:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C21080800013 | New_Event | Bad Weather | Include | Include | Weather | 219 | 2021-08-08 | 21462 | keep | 0 | Aug | 2021 | 0.014618 | 6.6747e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 98
SAN JUAN | 2021-08-08 11:03 | 2021-08-08 11:04 | 1452 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21080800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-08 | 1452 | keep | 0 | Aug | 2021 | 0.00098895 | 0.00098895 | Momentary | FALSE | FALSE | Not_TMED_Event | 1452
SAN JUAN | 2021-08-08 11:03 | 2021-08-08 11:10 | 5620 | 000:07 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 90% POR EL 1620-04 | S21080800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2021-08-08 | 39340 | keep | 0 | Aug | 2021 | 0.026794 | 0.0038278 | Sustained | FALSE | FALSE | Not_TMED_Event | 5620
SAN JUAN | 2021-08-08 11:03 | 2021-08-08 11:10 | 343 | 000:07 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 85% POR EL 1620-04 | S21080800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2021-08-08 | 2401 | keep | 0 | Aug | 2021 | 0.0016353 | 0.00023362 | Sustained | FALSE | FALSE | Not_TMED_Event | 343
SAN JUAN | 2021-08-08 11:03 | 2021-08-08 11:10 | 36 | 000:07 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1620-04 | S21080800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2021-08-08 | 252 | keep | 0 | Aug | 2021 | 0.00017164 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-08-08 11:03 | 2021-08-08 11:10 | 172 | 000:07 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 1620-01, 85% 1336-10 Y 90% 1336-07 | S21080800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2021-08-08 | 1204 | keep | 0 | Aug | 2021 | 0.00082004 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
HUMACAO | 2021-08-08 11:03 | 2021-08-08 13:00 | 5 | 001:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21080700060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 117 | 2021-08-08 | 585 | keep | 0 | Aug | 2021 | 0.00039844 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-08-08 11:04 | 2021-08-08 11:05 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1206-03 | S21080800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-08 | 10211 | keep | 0 | Aug | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-08-08 11:04 | 2021-08-08 11:05 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 1204-05 | S21080800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-08 | 4133 | keep | 0 | Aug | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-08-08 11:05 | 2021-08-08 11:07 | 247 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO | R21080600048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-08 | 494 | keep | 0 | Aug | 2021 | 0.00033646 | 0.00016823 | Momentary | FALSE | FALSE | Not_TMED_Event | 247
CAGUAS | 2021-08-08 11:07 | 2021-08-08 14:45 | 363 | 003:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE CERRO PUENTE DE LINEA A LINEA | C21080800015 | New_Event | Wire Down | Include | Include | Equipment | 218 | 2021-08-08 | 79134 | keep | 0 | Aug | 2021 | 0.053898 | 0.00024724 | Sustained | FALSE | TRUE | Not_TMED_Event | 363
CANOVANAS | 2021-08-08 11:10 | 2021-08-08 18:07 | 30 | 006:57 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHO Y LEVANTO CONDUCTOR | R21080800014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 417 | 2021-08-08 | 12510 | keep | 0 | Aug | 2021 | 0.0085205 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-08-08 11:13 | 2021-08-08 11:14 | 2782 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21080800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-08 | 2782 | keep | 0 | Aug | 2021 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
BAYAMON | 2021-08-08 11:15 | 2021-08-08 11:16 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1105-02 | S21080800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-08 | 641 | keep | 0 | Aug | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
BAYAMON | 2021-08-08 11:15 | 2021-08-08 11:16 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVANDO EL 1105-01 Y 1133-04 | S21080800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-08 | 308 | keep | 0 | Aug | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2021-08-08 11:15 | 2021-08-08 11:16 | 333 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1105-02 | S21080800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-08 | 333 | keep | 0 | Aug | 2021 | 0.0002268 | 0.0002268 | Momentary | FALSE | FALSE | Not_TMED_Event | 333
CAGUAS | 2021-08-08 11:17 | 2021-08-08 13:57 | 157 | 002:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 Y 1 X 40 EN CORTES DE LINEA MAL TIEMPO | C21080800020 | New_Event | Bad Weather | Include | Include | Weather | 160 | 2021-08-08 | 25120 | keep | 0 | Aug | 2021 | 0.017109 | 0.00010693 | Sustained | FALSE | TRUE | Not_TMED_Event | 157
SAN JUAN | 2021-08-08 11:18 | 2021-08-08 11:19 | 225 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1908-03 | S21080800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-08 | 225 | keep | 0 | Aug | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
BAYAMON | 2021-08-08 11:18 | 2021-08-08 13:30 | 842 | 002:12 | T | DESGANCHE | SE SECCIONALIZO Y SE CERRO POR SCADA | S21080800059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2021-08-08 | 111144 | keep | 0 | Aug | 2021 | 0.0757 | 0.00057348 | Sustained | FALSE | FALSE | Not_TMED_Event | 842
BAYAMON | 2021-08-08 11:18 | 2021-08-08 11:19 | 1310 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR Y SE CERRO POR CONTROL | S21080800057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-08 | 1310 | keep | 0 | Aug | 2021 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
SAN JUAN | 2021-08-08 11:18 | 2021-08-08 11:19 | 3957 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 1303-04 | S21080800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-08 | 3957 | keep | 0 | Aug | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
BAYAMON | 2021-08-08 11:19 | 2021-08-08 11:20 | 959 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA TRANSMISION 3400 | S21080800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 959 | keep | 0 | Aug | 2021 | 0.00065317 | 0.00065317 | Momentary | FALSE | TRUE | Not_TMED_Event | 959
BAYAMON | 2021-08-08 11:19 | 2021-08-08 11:20 | 1297 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA TRANSMISION 3400 | S21080800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 1297 | keep | 0 | Aug | 2021 | 0.00088338 | 0.00088338 | Momentary | FALSE | TRUE | Not_TMED_Event | 1297
BAYAMON | 2021-08-08 11:19 | 2021-08-08 11:20 | 451 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA TRANSMISION 3400 | S21080800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 451 | keep | 0 | Aug | 2021 | 0.00030717 | 0.00030717 | Momentary | FALSE | TRUE | Not_TMED_Event | 451
BAYAMON | 2021-08-08 11:19 | 2021-08-08 11:20 | 1264 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA TRANSMISION 3400 | S21080800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 1264 | keep | 0 | Aug | 2021 | 0.0008609 | 0.0008609 | Momentary | FALSE | TRUE | Not_TMED_Event | 1264
BAYAMON | 2021-08-08 11:19 | 2021-08-08 11:20 | 620 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA TRANSMISION 3400 | S21080800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 620 | keep | 0 | Aug | 2021 | 0.00042228 | 0.00042228 | Momentary | FALSE | TRUE | Not_TMED_Event | 620
BAYAMON | 2021-08-08 11:19 | 2021-08-08 18:43 | 30 | 007:24 | P | DESGANCHE | SE REALIZO DESGANCHE MASIVO Y SE CERRO CORTE DE LINEA | S21080800079 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 444 | 2021-08-08 | 13320 | keep | 0 | Aug | 2021 | 0.0090722 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-08-08 11:26 | 2021-08-08 13:40 | 12 | 002:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR AVE CRUZO FASE A TIERRA | A21080800065 | New_Event |  |  | Include | Wildlife | 134 | 2021-08-08 | 1608 | keep | 0 | Aug | 2021 | 0.0010952 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-08-08 11:27 | 2021-08-08 11:30 | 186 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21080800033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-08-08 | 558 | keep | 0 | Aug | 2021 | 0.00038005 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
CANOVANAS | 2021-08-08 11:28 | 2021-08-08 14:29 | 65 | 003:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21080800015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2021-08-08 | 11765 | keep | 0 | Aug | 2021 | 0.0080131 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BAYAMON | 2021-08-08 11:29 | 2021-08-08 12:36 | 50 | 001:07 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21080800034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2021-08-08 | 3350 | keep | 0 | Aug | 2021 | 0.0022817 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-08-08 11:30 | 2021-08-08 16:08 | 35 | 004:38 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21080800066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 278 | 2021-08-08 | 9730 | keep | 0 | Aug | 2021 | 0.0066271 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
SAN JUAN | 2021-08-08 11:33 | 2021-08-08 13:31 | 130 | 001:58 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21080800018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2021-08-08 | 15340 | keep | 0 | Aug | 2021 | 0.010448 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
CAGUAS | 2021-08-08 11:33 | 2021-08-08 15:15 | 588 | 003:42 | P | DESGANCHE | 2 X 140 EN CORTE DE LINEA SE RETIRO BAMBUAS DE LA LINEA | C21080800022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2021-08-08 | 130536 | keep | 0 | Aug | 2021 | 0.088907 | 0.00040048 | Sustained | FALSE | TRUE | Not_TMED_Event | 588
MAYAGÃœEZ | 2021-08-08 11:35 | 2021-08-08 15:39 | 3 | 004:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21080800018 | New_Event | Bad Weather | Include | Include | Weather | 244 | 2021-08-08 | 732 | keep | 0 | Aug | 2021 | 0.00049856 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
CANOVANAS | 2021-08-08 11:38 | 2021-08-08 12:25 | 150 | 000:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO | R21080800020 | New_Event | Bad Weather | Include | Include | Weather | 47 | 2021-08-08 | 7050 | keep | 0 | Aug | 2021 | 0.0048017 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-08-08 11:40 | 2021-08-08 14:40 | 25 | 003:00 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | C21080800027 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 180 | 2021-08-08 | 4500 | keep | 0 | Aug | 2021 | 0.0030649 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2021-08-08 11:43 | 2021-08-08 11:44 | 1922 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P210808000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 1922 | keep | 0 | Aug | 2021 | 0.0013091 | 0.0013091 | Momentary | FALSE | TRUE | Not_TMED_Event | 1922
PONCE | 2021-08-08 11:43 | 2021-08-08 11:44 | 2235 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P210808000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 2235 | keep | 0 | Aug | 2021 | 0.0015222 | 0.0015222 | Momentary | FALSE | TRUE | Not_TMED_Event | 2235
PONCE | 2021-08-08 11:43 | 2021-08-08 11:44 | 713 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P210808000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 713 | keep | 0 | Aug | 2021 | 0.00048562 | 0.00048562 | Momentary | FALSE | TRUE | Not_TMED_Event | 713
PONCE | 2021-08-08 11:43 | 2021-08-08 11:44 | 1067 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P210808000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 1067 | keep | 0 | Aug | 2021 | 0.00072673 | 0.00072673 | Momentary | FALSE | TRUE | Not_TMED_Event | 1067
PONCE | 2021-08-08 11:43 | 2021-08-08 11:44 | 1293 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P210808000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 1293 | keep | 0 | Aug | 2021 | 0.00088066 | 0.00088066 | Momentary | FALSE | TRUE | Not_TMED_Event | 1293
PONCE | 2021-08-08 11:43 | 2021-08-08 11:44 | 426 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P210808000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 426 | keep | 0 | Aug | 2021 | 0.00029015 | 0.00029015 | Momentary | FALSE | TRUE | Not_TMED_Event | 426
PONCE | 2021-08-08 11:43 | 2021-08-08 11:44 | 1556 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | P210808000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 1556 | keep | 0 | Aug | 2021 | 0.0010598 | 0.0010598 | Momentary | FALSE | TRUE | Not_TMED_Event | 1556
BAYAMON | 2021-08-08 11:52 | 2021-08-08 18:00 | 40 | 006:08 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21080800016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 368 | 2021-08-08 | 14720 | keep | 0 | Aug | 2021 | 0.010026 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-08-08 11:55 | 2021-08-08 12:00 | 18 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | P020808000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-08-08 | 90 | keep | 0 | Aug | 2021 | 6.1299e-05 | 1.226e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2021-08-08 11:56 | 2021-08-08 14:31 | 135 | 002:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE Y REEMPLAZO TERMINACION EN EL T - 24 | R21080800021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2021-08-08 | 20925 | keep | 0 | Aug | 2021 | 0.014252 | 9.1948e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 135
CANOVANAS | 2021-08-08 12:01 | 2021-08-08 16:01 | 40 | 004:00 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR | R21080800023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2021-08-08 | 9600 | keep | 0 | Aug | 2021 | 0.0065385 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-08 12:06 | 2021-08-08 20:10 | 20 | 008:04 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21080800019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 484 | 2021-08-08 | 9680 | keep | 0 | Aug | 2021 | 0.006593 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
HUMACAO | 2021-08-08 12:08 | 2021-08-08 16:49 | 11 | 004:41 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA | C21080800034 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 281 | 2021-08-08 | 3091 | keep | 0 | Aug | 2021 | 0.0021053 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2021-08-08 12:13 | 2021-08-08 12:14 | 2999 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR RECIERRE EN OFF NO SE REPORTO CAUSA | M21080800019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-08 | 2999 | keep | 0 | Aug | 2021 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
ARECIBO | 2021-08-08 12:16 | 2021-08-08 16:10 | 80 | 003:54 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21080800044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 234 | 2021-08-08 | 18720 | keep | 0 | Aug | 2021 | 0.01275 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-08-08 12:22 | 2021-08-08 14:00 | 6 | 001:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR NEUTRAL SECUNDARIO | C21080400042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 98 | 2021-08-08 | 588 | keep | 0 | Aug | 2021 | 0.00040048 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-08-08 12:25 | 2021-08-08 18:29 | 24 | 006:04 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C21080800038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 364 | 2021-08-08 | 8736 | keep | 0 | Aug | 2021 | 0.00595 | 1.6346e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 24
CAGUAS | 2021-08-08 12:25 | 2021-08-08 17:00 | 56 | 004:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C21080800039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2021-08-08 | 15400 | keep | 0 | Aug | 2021 | 0.010489 | 3.8141e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 56
UTUADO | 2021-08-08 12:28 | 2021-08-09 15:15 | 25 | 026:47 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO ARBOL | A21080800046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1607 | 2021-08-08 | 40175 | keep | 0 | Aug | 2021 | 0.027363 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
VEGA BAJA | 2021-08-08 12:28 | 2021-08-09 09:10 | 10 | 020:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21080800067 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1242 | 2021-08-08 | 12420 | keep | 0 | Aug | 2021 | 0.0084592 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-08 12:30 | 2021-08-09 12:00 | 1 | 023:30 | P | DESGANCHE | 1 X 10 EN CORTE DE LINEA SE RETIRO RAMA | A21080800047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1410 | 2021-08-08 | 1410 | keep | 0 | Aug | 2021 | 0.00096034 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BARRANQUITAS | 2021-08-08 12:32 | 2021-08-08 15:25 | 78 | 002:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | C21080800044 | New_Event | Bad Weather | Include | Include | Weather | 173 | 2021-08-08 | 13494 | keep | 0 | Aug | 2021 | 0.0091907 | 5.3125e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 78
ARECIBO | 2021-08-08 12:34 | 2021-08-08 12:35 | 2228 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR 8007-04 QUE LLEVA LA CARGA DEL 8007-03 | A21080800049 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-08-08 | 2228 | keep | 0 | Aug | 2021 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2021-08-08 12:34 | 2021-08-08 12:35 | 438 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 8007-04 | A21080800049 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-08-08 | 438 | keep | 0 | Aug | 2021 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
ARECIBO | 2021-08-08 12:35 | 2021-08-08 16:20 | 35 | 003:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A21080800073 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 225 | 2021-08-08 | 7875 | keep | 0 | Aug | 2021 | 0.0053636 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-08-08 12:35 | 2021-08-08 12:36 | 2201 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21080800050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-08 | 2201 | keep | 0 | Aug | 2021 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
AGUADILLA | 2021-08-08 12:37 | 2021-08-08 19:50 | 1 | 007:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA DE 100 AMP X CAJA DE 100 AMP | M21080800021 | New_Event | Cutout Failure | Include | Include | Equipment | 433 | 2021-08-08 | 433 | keep | 0 | Aug | 2021 | 0.00029491 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-08-08 12:45 | 2021-08-08 18:25 | 30 | 005:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21080800055 | New_Event | Bad Weather | Include | Include | Weather | 340 | 2021-08-08 | 10200 | keep | 0 | Aug | 2021 | 0.0069472 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-08-08 12:46 | 2021-08-08 19:00 | 100 | 006:14 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21080800057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 374 | 2021-08-08 | 37400 | keep | 0 | Aug | 2021 | 0.025473 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-08-08 12:50 | 2021-08-08 12:51 | 2952 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21080800024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-08 | 2952 | keep | 0 | Aug | 2021 | 0.0020106 | 0.0020106 | Momentary | FALSE | FALSE | Not_TMED_Event | 2952
MAYAGÃœEZ | 2021-08-08 13:01 | 2021-08-08 15:30 | 30 | 002:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21080800027 | New_Event | Bad Weather | Include | Include | Weather | 149 | 2021-08-08 | 4470 | keep | 0 | Aug | 2021 | 0.0030445 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-08-08 13:04 | 2021-08-08 15:06 | 37 | 002:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C21080800053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2021-08-08 | 4514 | keep | 0 | Aug | 2021 | 0.0030745 | 2.5201e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 37
HUMACAO | 2021-08-08 13:09 | 2021-08-08 13:28 | 296 | 000:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21080800014 | New_Event | Bad Weather | Include | Include | Weather | 19 | 2021-08-08 | 5624 | keep | 0 | Aug | 2021 | 0.0038305 | 0.0002016 | Sustained | FALSE | TRUE | Not_TMED_Event | 296
ARECIBO | 2021-08-08 13:10 | 2021-08-09 14:35 | 10 | 025:25 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMA | A21080800061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1525 | 2021-08-08 | 15250 | keep | 0 | Aug | 2021 | 0.010387 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-08-08 13:13 | 2021-08-08 16:34 | 100 | 003:21 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZE DESGANCHE PRIMARIO | M21080800028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2021-08-08 | 20100 | keep | 0 | Aug | 2021 | 0.01369 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-08-08 13:26 | 2021-08-08 18:10 | 1 | 004:44 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21080800066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 284 | 2021-08-08 | 284 | keep | 0 | Aug | 2021 | 0.00019343 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-08-08 13:29 | 2021-08-08 14:30 | 46 | 001:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21080800058 | New_Event | Bad Weather | Include | Include | Weather | 61 | 2021-08-08 | 2806 | keep | 0 | Aug | 2021 | 0.0019112 | 3.133e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 46
BAYAMON | 2021-08-08 13:30 | 2021-08-08 14:22 | 350 | 000:52 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETES | S21080800107 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 52 | 2021-08-08 | 18200 | keep | 0 | Aug | 2021 | 0.012396 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-08-08 13:59 | 2021-08-08 17:45 | 100 | 003:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21080800034 | New_Event | Bad Weather | Include | Include | Weather | 226 | 2021-08-08 | 22600 | keep | 0 | Aug | 2021 | 0.015393 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-08-08 14:00 | 2021-08-09 15:45 | 20 | 025:45 | P | DESGANCHE | SE RETIRO ARBOL SOBRE LINEA Y SE CERRO CORTE DE LINEA | A21080800076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1545 | 2021-08-08 | 30900 | keep | 0 | Aug | 2021 | 0.021046 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-08-08 14:05 | 2021-08-08 19:27 | 20 | 005:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE A TRANSFORMADOR | M21080700035 | New_Event | Wire Down | Include | Include | Equipment | 322 | 2021-08-08 | 6440 | keep | 0 | Aug | 2021 | 0.0043863 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-08-08 14:07 | 2021-08-08 14:29 | 5 | 000:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA LEVANTAR LINEA SECUNDARIA | C21080800057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 22 | 2021-08-08 | 110 | keep | 0 | Aug | 2021 | 7.492e-05 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
ARECIBO | 2021-08-08 14:07 | 2021-08-08 19:45 | 30 | 005:38 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBÃšS SOBRE LAS LINEAS | A21080800071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 338 | 2021-08-08 | 10140 | keep | 0 | Aug | 2021 | 0.0069063 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-08-08 14:10 | 2021-08-08 17:00 | 30 | 002:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21080800036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2021-08-08 | 5100 | keep | 0 | Aug | 2021 | 0.0034736 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-08-08 14:14 | 2021-08-08 19:25 | 10 | 005:11 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA X 50 KVA | R21080800032 | New_Event | Service Transformer Failure | Include | Include | Equipment | 311 | 2021-08-08 | 3110 | keep | 0 | Aug | 2021 | 0.0021182 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-08-08 14:15 | 2021-08-08 14:16 | 667 | 000:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M21080800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 667 | keep | 0 | Aug | 2021 | 0.00045429 | 0.00045429 | Momentary | FALSE | TRUE | Not_TMED_Event | 667
BAYAMON | 2021-08-08 14:22 | 2021-08-08 20:18 | 750 | 005:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA | S21080800107 | New_Event | Wire Down | Include | Include | Equipment | 356 | 2021-08-08 | 267000 | keep | 0 | Aug | 2021 | 0.18185 | 0.00051082 | Sustained | FALSE | TRUE | Not_TMED_Event | 750
CAGUAS | 2021-08-08 14:25 | 2021-08-08 19:40 | 45 | 005:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO ARBOL DE LA LINEA | C21080800067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 315 | 2021-08-08 | 14175 | keep | 0 | Aug | 2021 | 0.0096545 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
HUMACAO | 2021-08-08 14:38 | 2021-08-08 16:08 | 17 | 001:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA CRUCE POR PALOMA | C21080800069 | New_Event |  |  | Include | Wildlife | 90 | 2021-08-08 | 1530 | keep | 0 | Aug | 2021 | 0.0010421 | 1.1579e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 17
BAYAMON | 2021-08-08 15:11 | 2021-08-09 16:25 | 100 | 025:14 | P | DESGANCHE | 3 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA Y DESGANCHE LLEVA CARGA DEL 1711-05 | B21080800004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1514 | 2021-08-08 | 151400 | keep | 0 | Aug | 2021 | 0.10312 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-08-08 15:14 | 2021-08-08 16:10 | 45 | 000:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE | P21080800026 | New_Event |  |  | Include | Wildlife | 56 | 2021-08-08 | 2520 | keep | 0 | Aug | 2021 | 0.0017164 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
ARECIBO | 2021-08-08 15:15 | 2021-08-08 17:30 | 70 | 002:15 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO BAMBÃšS SOBRE LAS LINEAS | A21080800078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2021-08-08 | 9450 | keep | 0 | Aug | 2021 | 0.0064364 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
ARECIBO | 2021-08-08 15:23 | 2021-08-09 01:50 | 50 | 010:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | A21080800081 | New_Event | Wire Down | Include | Include | Equipment | 627 | 2021-08-08 | 31350 | keep | 0 | Aug | 2021 | 0.021352 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-08 16:01 | 2021-08-08 19:44 | 60 | 003:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA Y AISLADOR | B21080800043 | New_Event | Cutout Failure | Include | Include | Equipment | 223 | 2021-08-08 | 13380 | keep | 0 | Aug | 2021 | 0.0091131 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-08-08 16:16 | 2021-08-08 22:25 | 150 | 006:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA Y 1 X 30 EN TRANSFORMADOR SE LEVANTO CONDUCTOR Y SE REALIZO DESGANCHE MASIVO | B21080800044 | New_Event | Wire Down | Include | Include | Equipment | 369 | 2021-08-08 | 55350 | keep | 0 | Aug | 2021 | 0.037699 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
YAUCO | 2021-08-08 16:16 | 2021-08-08 17:40 | 82 | 001:24 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | P21080800028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2021-08-08 | 6888 | keep | 0 | Aug | 2021 | 0.0046914 | 5.585e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 82
FAJARDO | 2021-08-08 16:19 | 2021-08-08 16:49 | 80 | 000:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | R21080890003 | New_Event |  |  | Include | Wildlife | 30 | 2021-08-08 | 2400 | keep | 0 | Aug | 2021 | 0.0016346 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-08-08 16:21 | 2021-08-09 11:06 | 9 | 018:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | C21080800077 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1125 | 2021-08-08 | 10125 | keep | 0 | Aug | 2021 | 0.0068961 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-08-08 16:39 | 2021-08-08 17:00 | 100 | 000:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 65 EN CORTE DE LINEA SE RETIRO GLOBO | B21080800046 | New_Event |  |  | Include | Wildlife | 21 | 2021-08-08 | 2100 | keep | 0 | Aug | 2021 | 0.0014303 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-08-08 16:56 | 2021-08-09 10:22 | 20 | 017:26 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A21080800082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1046 | 2021-08-08 | 20920 | keep | 0 | Aug | 2021 | 0.014249 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-08-08 17:07 | 2021-08-09 08:49 | 1 | 015:42 | P | NO SE REPORTO CAUSA | 2 X 10 EN TRANSFORMADOR NO SE REPORTO CAUSA | P21080800031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 942 | 2021-08-08 | 942 | keep | 0 | Aug | 2021 | 0.00064159 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2021-08-08 17:31 | 2021-08-08 18:08 | 8 | 000:37 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA X 37.5 KVA | R21080800039 | New_Event | Service Transformer Failure | Include | Include | Equipment | 37 | 2021-08-08 | 296 | keep | 0 | Aug | 2021 | 0.0002016 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-08-08 17:38 | 2021-08-09 12:45 | 15 | 019:07 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 25 KVA X 25 KVA | A21080900020 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1147 | 2021-08-08 | 17205 | keep | 0 | Aug | 2021 | 0.011718 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-08-08 18:08 | 2021-08-08 20:45 | 50 | 002:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21080800088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2021-08-08 | 7850 | keep | 0 | Aug | 2021 | 0.0053466 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-08 18:11 | 2021-08-08 23:57 | 125 | 005:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA REAPRO LINEA PARTIDA | M21080800051 | New_Event | Wire Down | Include | Include | Equipment | 346 | 2021-08-08 | 43250 | keep | 0 | Aug | 2021 | 0.029457 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
AGUADILLA | 2021-08-08 18:21 | 2021-08-09 09:55 | 150 | 015:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21080800052 | New_Event | Bad Weather | Include | Include | Weather | 934 | 2021-08-08 | 140100 | keep | 0 | Aug | 2021 | 0.095421 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BARRANQUITAS | 2021-08-08 18:21 | 2021-08-08 18:22 | 2635 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 6500 DE BARRANQUITAS A TORO NEGRO | C21080800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 2635 | keep | 0 | Aug | 2021 | 0.0017947 | 0.0017947 | Momentary | FALSE | TRUE | Not_TMED_Event | 2635
BARRANQUITAS | 2021-08-08 18:21 | 2021-08-08 18:22 | 2280 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 6500 DE BARRANQUITAS A TORO NEGRO | C21080800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 2280 | keep | 0 | Aug | 2021 | 0.0015529 | 0.0015529 | Momentary | FALSE | TRUE | Not_TMED_Event | 2280
BARRANQUITAS | 2021-08-08 18:21 | 2021-08-08 18:22 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 6500 DE BARRANQUITAS A TORO NEGRO | C21080800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-08 | 1617 | keep | 0 | Aug | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | TRUE | Not_TMED_Event | 1617
SAN JUAN | 2021-08-08 19:09 | 2021-08-09 14:08 | 31 | 018:59 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 100 KVA X 100 KVA | R21080800041 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1139 | 2021-08-08 | 35309 | keep | 0 | Aug | 2021 | 0.024049 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
MAYAGÃœEZ | 2021-08-08 19:24 | 2021-08-09 14:30 | 50 | 019:06 | P | DESGANCHE | SE RELES RECLOSER SE ACTIVO SE RETIRO RAMAS SOBRE LAS LINEAS | M21080800060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1146 | 2021-08-08 | 57300 | keep | 0 | Aug | 2021 | 0.039027 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-08-08 19:43 | 2021-08-08 21:09 | 8 | 001:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA REPARAR SECUNDARIA | C21080800078 | New_Event | Secondary Wire Down | Include | Include | Equipment | 86 | 2021-08-08 | 688 | keep | 0 | Aug | 2021 | 0.00046859 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-08-08 20:16 | 2021-08-08 20:17 | 859 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA 20%CARGA POR EL 1303-02 | S21080800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-08 | 859 | keep | 0 | Aug | 2021 | 0.00058506 | 0.00058506 | Momentary | FALSE | FALSE | Not_TMED_Event | 859
SAN JUAN | 2021-08-08 20:16 | 2021-08-08 20:17 | 2435 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA LLEVA 60% 1346-05 Y 20% 1204-02 | S21080800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-08 | 2435 | keep | 0 | Aug | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2021-08-08 20:16 | 2021-08-08 20:17 | 553 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA 60% CARGA POR EL 1303-02 | S21080800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-08 | 553 | keep | 0 | Aug | 2021 | 0.00037665 | 0.00037665 | Momentary | FALSE | FALSE | Not_TMED_Event | 553
SAN JUAN | 2021-08-08 20:17 | 2021-08-09 00:01 | 800 | 003:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETE DE SALIDA DE LA FASE AFECTADA Y SE REEMPLAZO DISCO, GRAPA Y SE INSTALO PUENTE PORTATIL | S21080800134 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 224 | 2021-08-08 | 179200 | keep | 0 | Aug | 2021 | 0.12205 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
BAYAMON | 2021-08-08 20:17 | 2021-08-08 21:26 | 60 | 001:09 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21080800058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 69 | 2021-08-08 | 4140 | keep | 0 | Aug | 2021 | 0.0028197 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
PONCE | 2021-08-08 20:18 | 2021-08-08 23:32 | 1730 | 003:14 | T | ESTRUCTURA AVERIADA | DISPARO DE INTERRUPTOR POR POSTE EN LLAMAS | P21080800036 | New_Event | Defective Pole | Include | Include | Equipment | 194 | 2021-08-08 | 335620 | keep | 0 | Aug | 2021 | 0.22859 | 0.0011783 | Sustained | FALSE | FALSE | Not_TMED_Event | 1730
BAYAMON | 2021-08-08 20:49 | 2021-08-09 13:16 | 15 | 016:27 | P | NO SE REPORTO CAUSA | 2 X 15 EN TRANSFORMADOR | B21080800061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 987 | 2021-08-08 | 14805 | keep | 0 | Aug | 2021 | 0.010084 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-08-08 20:57 | 2021-08-08 22:14 | 500 | 001:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA | A21080800095 | New_Event | Bad Weather | Include | Include | Weather | 77 | 2021-08-08 | 38500 | keep | 0 | Aug | 2021 | 0.026222 | 0.00034055 | Sustained | FALSE | TRUE | Not_TMED_Event | 500
ARECIBO | 2021-08-08 21:08 | 2021-08-09 15:50 | 12 | 018:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN TRANSFORMADOR SE REPARO BAJANTE PARTIDO | A21080800097 | New_Event | Wire Down | Include | Include | Equipment | 1122 | 2021-08-08 | 13464 | keep | 0 | Aug | 2021 | 0.0091703 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2021-08-08 21:18 | 2021-08-09 15:05 | 35 | 017:47 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | P21080800037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1067 | 2021-08-08 | 37345 | keep | 0 | Aug | 2021 | 0.025436 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
CAGUAS | 2021-08-08 21:25 | 2021-08-09 11:08 | 11 | 013:43 | P | DESGANCHE | 1 X 20 EN BANCO DE TRANSFORMADOR | C21080800087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 823 | 2021-08-08 | 9053 | keep | 0 | Aug | 2021 | 0.006166 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
VEGA BAJA | 2021-08-08 22:47 | 2021-08-09 17:08 | 3 | 018:21 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL AEREO DE T-19 A T-20 | B21080800008 | New_Event | UG Cable Fault | Include | Include | Equipment | 1101 | 2021-08-08 | 3303 | keep | 0 | Aug | 2021 | 0.0022497 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-08-08 23:17 | 2021-08-09 15:11 | 390 | 015:54 | P | DESGANCHE | 2 X 100 Y 1 X 50 EN CORTES DE LINEA SE DESGANCHO Y SE INSTALO RIGIDO | R21080800048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 954 | 2021-08-08 | 372060 | keep | 0 | Aug | 2021 | 0.25341 | 0.00026563 | Sustained | FALSE | TRUE | Not_TMED_Event | 390
CANOVANAS | 2021-08-08 23:29 | 2021-08-09 15:43 | 35 | 016:14 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA X 50 KVA | R21080800049 | New_Event | Service Transformer Failure | Include | Include | Equipment | 974 | 2021-08-08 | 34090 | keep | 0 | Aug | 2021 | 0.023219 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
FAJARDO | 2021-08-08 23:31 | 2021-08-09 09:19 | 11 | 009:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN RISER CRUCE POR RATA | R21080800050 | New_Event |  |  | Include | Wildlife | 588 | 2021-08-08 | 6468 | keep | 0 | Aug | 2021 | 0.0044053 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
PONCE | 2021-08-08 23:32 | 2021-08-08 23:35 | 1093 | 000:03 | S | LINEA DE TRANSMISION 38KV | CENTRO DE CONTROL ENERGETICO ABRIO LINEA 200 POR POSTE EN LLAMAS | P210808000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-08-08 | 3279 | keep | 0 | Aug | 2021 | 0.0022333 | 0.00074444 | Momentary | FALSE | TRUE | Not_TMED_Event | 1093
PONCE | 2021-08-08 23:32 | 2021-08-08 23:35 | 1067 | 000:03 | S | LINEA DE TRANSMISION 38KV | CENTRO DE CONTROL ENERGETICO ABRIO LINEA 200 POR POSTE EN LLAMAS | P210808000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-08-08 | 3201 | keep | 0 | Aug | 2021 | 0.0021802 | 0.00072673 | Momentary | FALSE | TRUE | Not_TMED_Event | 1067
PONCE | 2021-08-08 23:32 | 2021-08-08 23:35 | 836 | 000:03 | S | LINEA DE TRANSMISION 38KV | CENTRO DE CONTROL ENERGETICO ABRIO LINEA 200 POR POSTE EN LLAMAS | P210808000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-08-08 | 2508 | keep | 0 | Aug | 2021 | 0.0017082 | 0.0005694 | Momentary | FALSE | TRUE | Not_TMED_Event | 836
PONCE | 2021-08-08 23:32 | 2021-08-08 23:35 | 1339 | 000:03 | S | LINEA DE TRANSMISION 38KV | CENTRO DE CONTROL ENERGETICO ABRIO LINEA 200 POR POSTE EN LLAMAS | P210808000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-08-08 | 4017 | keep | 0 | Aug | 2021 | 0.002736 | 0.00091199 | Momentary | FALSE | TRUE | Not_TMED_Event | 1339
PONCE | 2021-08-08 23:32 | 2021-08-08 23:35 | 1295 | 000:03 | S | LINEA DE TRANSMISION 38KV | CENTRO DE CONTROL ENERGETICO ABRIO LINEA 200 POR POSTE EN LLAMAS | P210808000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-08-08 | 3885 | keep | 0 | Aug | 2021 | 0.0026461 | 0.00088202 | Momentary | FALSE | TRUE | Not_TMED_Event | 1295
PONCE | 2021-08-08 23:32 | 2021-08-08 23:35 | 978 | 000:03 | S | LINEA DE TRANSMISION 38KV | CENTRO DE CONTROL ENERGETICO ABRIO LINEA 200 POR POSTE EN LLAMAS | P210808000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-08-08 | 2934 | keep | 0 | Aug | 2021 | 0.0019983 | 0.00066611 | Momentary | FALSE | TRUE | Not_TMED_Event | 978
PONCE | 2021-08-08 23:32 | 2021-08-08 23:35 | 1730 | 000:03 | S | LINEA DE TRANSMISION 38KV | CENTRO DE CONTROL ENERGETICO ABRIO LINEA 200 POR POSTE EN LLAMAS | P210808000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-08-08 | 5190 | keep | 0 | Aug | 2021 | 0.0035349 | 0.0011783 | Momentary | FALSE | TRUE | Not_TMED_Event | 1730
PONCE | 2021-08-08 23:35 | 2021-08-09 07:28 | 1730 | 007:53 | T | ESTRUCTURA AVERIADA | SE CAMBIO POSTE QUEMADO DE MADERA INSTALANDO UNO DE METAL 40 PIES DENTRO DE UNA FINCA | P21080800036 | Partial_restoration | Defective Pole | Include | Include | Equipment | 473 | 2021-08-08 | 818290 | keep | 0 | Aug | 2021 | 0.55733 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-08-08 23:35 | 2021-08-09 09:45 | 891 | 010:10 | S | ESTRUCTURA AVERIADA | SE CAMBIO POSTE QUEMADO INSTALANDO UNO DE METAL 40 PIES | P21080800014 | New_Event | Defective Pole | Include | Include | Equipment | 610 | 2021-08-08 | 543510 | keep | 0 | Aug | 2021 | 0.37018 | 0.00060686 | Sustained | FALSE | FALSE | Not_TMED_Event | 891
PONCE | 2021-08-08 23:35 | 2021-08-09 09:45 | 527 | 010:10 | S | ESTRUCTURA AVERIADA | SE CAMBIO POSTE QUEMADO INSTALANDO UNO DE METAL 40 PIES | P21080800014 | New_Event | Defective Pole | Include | Include | Equipment | 610 | 2021-08-08 | 321470 | keep | 0 | Aug | 2021 | 0.21895 | 0.00035894 | Sustained | FALSE | FALSE | Not_TMED_Event | 527
PONCE | 2021-08-08 23:35 | 2021-08-09 09:45 | 542 | 010:10 | S | ESTRUCTURA AVERIADA | SE CAMBIO POSTE QUEMADO INSTALANDO UNO DE METAL 40 PIES | P21080800014 | New_Event | Defective Pole | Include | Include | Equipment | 610 | 2021-08-08 | 330620 | keep | 0 | Aug | 2021 | 0.22518 | 0.00036915 | Sustained | FALSE | FALSE | Not_TMED_Event | 542
BAYAMON | 2021-08-08 23:48 | 2021-08-09 10:36 | 12 | 010:48 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21080800067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 648 | 2021-08-08 | 7776 | keep | 0 | Aug | 2021 | 0.0052962 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-08-08 23:51 | 2021-08-09 16:12 | 1 | 016:21 | P | NO SE REPORTO CAUSA | 1 X 10 EN BANCO DE TRANSFORMADORES | B21080800069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 981 | 2021-08-08 | 981 | keep | 0 | Aug | 2021 | 0.00066815 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-08-09 00:57 | 2021-08-09 11:53 | 35 | 010:56 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21080900001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 656 | 2021-08-09 | 22960 | keep | 0 | Aug | 2021 | 0.015638 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
HUMACAO | 2021-08-09 01:22 | 2021-08-09 12:40 | 55 | 011:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | C21080900002 | New_Event |  |  | Include | Wildlife | 678 | 2021-08-09 | 37290 | keep | 0 | Aug | 2021 | 0.025398 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
BAYAMON | 2021-08-09 01:52 | 2021-08-10 09:15 | 25 | 031:23 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21080900002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1883 | 2021-08-09 | 47075 | keep | 0 | Aug | 2021 | 0.032063 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-08-09 02:14 | 2021-08-09 02:15 | 726 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1303-03 LLEVANDO LA CARGA DEL 1346-04 | S21080900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-09 | 726 | keep | 0 | Aug | 2021 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-08-09 02:14 | 2021-08-09 02:15 | 3932 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1303-03 LLEVANDO LA CARGA DEL 1346-04 | S21080900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-09 | 3932 | keep | 0 | Aug | 2021 | 0.0026781 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
CAGUAS | 2021-08-09 03:25 | 2021-08-09 10:06 | 70 | 006:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21080900007 | New_Event | Bad Weather | Include | Include | Weather | 401 | 2021-08-09 | 28070 | keep | 0 | Aug | 2021 | 0.019118 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
VEGA BAJA | 2021-08-09 03:26 | 2021-08-09 11:26 | 60 | 008:00 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21080900004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 480 | 2021-08-09 | 28800 | keep | 0 | Aug | 2021 | 0.019616 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-08-09 04:42 | 2021-08-09 13:30 | 60 | 008:48 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO PM-13 QUEMADO SE CERRO RISER | A21080800004 | New_Event | Service Transformer Failure | Include | Include | Equipment | 528 | 2021-08-09 | 31680 | keep | 0 | Aug | 2021 | 0.021577 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2021-08-09 04:45 | 2021-08-09 04:46 | 1284 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21080900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-09 | 1284 | keep | 0 | Aug | 2021 | 0.00087453 | 0.00087453 | Momentary | FALSE | FALSE | Not_TMED_Event | 1284
CANOVANAS | 2021-08-09 04:56 | 2021-08-09 09:08 | 3 | 004:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA CONDUCTOR AVERIADO | R21080900005 | New_Event | Wire Down | Include | Include | Equipment | 252 | 2021-08-09 | 756 | keep | 0 | Aug | 2021 | 0.00051491 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
HUMACAO | 2021-08-09 05:47 | 2021-08-09 10:32 | 60 | 004:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21080900010 | New_Event | Bad Weather | Include | Include | Weather | 285 | 2021-08-09 | 17100 | keep | 0 | Aug | 2021 | 0.011647 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-08-09 06:22 | 2021-08-09 06:23 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21080900002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-09 | 870 | keep | 0 | Aug | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
PONCE | 2021-08-09 06:38 | 2021-08-09 09:40 | 10 | 003:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZARON CONEXIONES SULFATADAS EN SECUNDARIA | P21080900015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 182 | 2021-08-09 | 1820 | keep | 0 | Aug | 2021 | 0.0012396 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-08-09 06:46 | 2021-08-09 11:33 | 1 | 004:47 | P | NO SE REPORTO CAUSA | 2 X 25 EN RISER | R21080900008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 287 | 2021-08-09 | 287 | keep | 0 | Aug | 2021 | 0.00019547 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-08-09 06:52 | 2021-08-09 13:50 | 55 | 006:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21080900014 | New_Event | Bad Weather | Include | Include | Weather | 418 | 2021-08-09 | 22990 | keep | 0 | Aug | 2021 | 0.015658 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
SAN JUAN | 2021-08-09 06:59 | 2021-08-10 15:56 | 15 | 032:57 | P | NO SE REPORTO CAUSA | 2 X 10 EN TRANSFORMADOR | S21080900006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1977 | 2021-08-09 | 29655 | keep | 0 | Aug | 2021 | 0.020198 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-08-09 07:54 | 2021-08-09 15:55 | 8 | 008:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE EN TRANSFORMADOR | A21080900007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 481 | 2021-08-09 | 3848 | keep | 0 | Aug | 2021 | 0.0026209 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-08-09 08:13 | 2021-08-09 12:00 | 12 | 003:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B21080900014 | New_Event | Cutout Failure | Include | Include | Equipment | 227 | 2021-08-09 | 2724 | keep | 0 | Aug | 2021 | 0.0018553 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-08-09 08:17 | 2021-08-10 09:57 | 60 | 025:40 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21080900112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1540 | 2021-08-09 | 92400 | keep | 0 | Aug | 2021 | 0.062933 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-08-09 08:21 | 2021-08-09 08:57 | 50 | 000:36 | P | NO SE REPORTO CAUSA | 1 X 80 1 X 50 Y 1 X 40 EN CORTE DE LINEA CARGA POR EL 1206-03 | S21080900007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 36 | 2021-08-09 | 1800 | keep | 0 | Aug | 2021 | 0.001226 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-08-09 08:24 | 2021-08-09 11:55 | 40 | 003:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21080900013 | New_Event | Bad Weather | Include | Include | Weather | 211 | 2021-08-09 | 8440 | keep | 0 | Aug | 2021 | 0.0057484 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-08-09 08:30 | 2021-08-09 10:53 | 812 | 002:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REEMPLAZO DE PUENTE PORTATIL LLEVANDO UN 60% DE LA CARGA DEL 1346-05 Y UN 20% DEL 1204-02 | S21080900027 | New_Event | Wire Down | Include | Include | Equipment | 143 | 2021-08-09 | 116116 | keep | 0 | Aug | 2021 | 0.079086 | 0.00055305 | Sustained | FALSE | FALSE | Not_TMED_Event | 812
SAN JUAN | 2021-08-09 08:30 | 2021-08-09 10:53 | 183 | 002:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REEMPLAZO DE PUENTE PORTATIL 60% DE LA CARGA POR EL 1303-02 | S21080900027 | New_Event | Wire Down | Include | Include | Equipment | 143 | 2021-08-09 | 26169 | keep | 0 | Aug | 2021 | 0.017824 | 0.00012464 | Sustained | FALSE | FALSE | Not_TMED_Event | 183
CANOVANAS | 2021-08-09 08:32 | 2021-08-09 08:33 | 1648 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR | R21080900014 | New_Event |  |  | Include | Wildlife | 1 | 2021-08-09 | 1648 | keep | 0 | Aug | 2021 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2021-08-09 08:33 | 2021-08-09 10:46 | 55 | 002:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R21080900018 | 1st_after_momentary |  |  | Include | Wildlife | 133 | 2021-08-09 | 7315 | keep | 0 | Aug | 2021 | 0.0049822 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
ARECIBO | 2021-08-09 08:40 | 2021-08-09 11:24 | 8 | 002:44 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE 50 KVA X 50 KVA | A21080900024 | New_Event | Service Transformer Failure | Include | Include | Equipment | 164 | 2021-08-09 | 1312 | keep | 0 | Aug | 2021 | 0.0008936 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2021-08-09 08:44 | 2021-08-09 16:05 | 1 | 007:21 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | A21080900016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 441 | 2021-08-09 | 441 | keep | 0 | Aug | 2021 | 0.00030036 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-08-09 08:57 | 2021-08-09 08:58 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1206-03 | S21080900000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-09 | 10211 | keep | 0 | Aug | 2021 | 0.0069547 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-08-09 08:57 | 2021-08-09 08:58 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA EL 1204-05 | S21080900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-09 | 4133 | keep | 0 | Aug | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-08-09 08:58 | 2021-08-10 11:28 | 50 | 026:30 | P | NO SE REPORTO CAUSA | 1 X 80 1 X 50 Y 1 X 40 EN CORTE DE LINEA CARGA POR EL 1206-03 | S21080900007 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1590 | 2021-08-09 | 79500 | keep | 0 | Aug | 2021 | 0.054147 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BARRANQUITAS | 2021-08-09 08:59 | 2021-08-09 12:28 | 90 | 003:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21080900032 | New_Event | Bad Weather | Include | Include | Weather | 209 | 2021-08-09 | 18810 | keep | 0 | Aug | 2021 | 0.012811 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
PONCE | 2021-08-09 09:00 | 2021-08-10 12:53 | 10 | 027:53 | P | TRANSFORMADOR AVERIADO | SE REMPLASO XMR AVERIADO | P21080900030 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1673 | 2021-08-09 | 16730 | keep | 0 | Aug | 2021 | 0.011395 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-08-09 09:01 | 2021-08-09 22:31 | 10 | 013:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA QUEMADA | B21080900012 | New_Event | Cutout Failure | Include | Include | Equipment | 810 | 2021-08-09 | 8100 | keep | 0 | Aug | 2021 | 0.0055169 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-09 09:02 | 2021-08-09 14:10 | 20 | 005:08 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMA | A21080900018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 308 | 2021-08-09 | 6160 | keep | 0 | Aug | 2021 | 0.0041955 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
HUMACAO | 2021-08-09 09:29 | 2021-08-09 16:56 | 30 | 007:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 30 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA | C21080900034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 447 | 2021-08-09 | 13410 | keep | 0 | Aug | 2021 | 0.0091335 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-08-09 09:30 | 2021-08-09 12:01 | 80 | 002:31 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL CAIDO SOBRE LAS LINEAS | M21080900035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2021-08-09 | 12080 | keep | 0 | Aug | 2021 | 0.0082276 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CANOVANAS | 2021-08-09 09:33 | 2021-08-09 16:41 | 35 | 007:08 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | R21080900021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 428 | 2021-08-09 | 14980 | keep | 0 | Aug | 2021 | 0.010203 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-08-09 09:52 | 2021-08-09 15:12 | 25 | 005:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | B21080900029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 320 | 2021-08-09 | 8000 | keep | 0 | Aug | 2021 | 0.0054488 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-08-09 09:52 | 2021-08-09 13:37 | 1 | 003:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA PARTIDA SE ABRIO INTERRUPTOR PARA REPARAR | A21080900026 | New_Event | Wire Down | Include | Include | Equipment | 225 | 2021-08-09 | 225 | keep | 0 | Aug | 2021 | 0.00015325 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-08-09 10:00 | 2021-08-09 11:02 | 12 | 001:02 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR | C21080900036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2021-08-09 | 744 | keep | 0 | Aug | 2021 | 0.00050674 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2021-08-09 10:00 | 2021-08-09 11:00 | 200 | 001:00 | P | ESTRUCTURA AVERIADA | SE ABRIO MACHETES PARA ABRIR PUENTES Y REMPLAZAR POSTE PRIMARIO PARTIDO | M21080900031 | New_Event | Defective Pole | Include | Include | Equipment | 60 | 2021-08-09 | 12000 | keep | 0 | Aug | 2021 | 0.0081731 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2021-08-09 10:15 | 2021-08-09 12:21 | 80 | 002:06 | P | NO SE REPORTO CAUSA | 3 X 100 EN RISER @ LINEA AEREA | C21080900039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2021-08-09 | 10080 | keep | 0 | Aug | 2021 | 0.0068654 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-09 10:22 | 2021-08-10 13:29 | 22 | 027:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | B21080900159 | New_Event | Wire Down | Include | Include | Equipment | 1627 | 2021-08-09 | 35794 | keep | 0 | Aug | 2021 | 0.024379 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
AGUADILLA | 2021-08-09 10:48 | 2021-08-09 11:45 | 16 | 000:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M21080800049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 57 | 2021-08-09 | 912 | keep | 0 | Aug | 2021 | 0.00062116 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2021-08-09 10:56 | 2021-08-10 14:36 | 45 | 027:40 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21080900042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1660 | 2021-08-09 | 74700 | keep | 0 | Aug | 2021 | 0.050878 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
AGUADILLA | 2021-08-09 11:00 | 2021-08-09 20:05 | 50 | 009:05 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO SE ABRIO MACHETES PARA CERRAR PUENTES | M21080900031 | Partial_restoration | Defective Pole | Include | Include | Equipment | 545 | 2021-08-09 | 27250 | keep | 0 | Aug | 2021 | 0.01856 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-09 11:10 | 2021-08-09 18:00 | 11 | 006:50 | P | ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZAR POSTE SECUNDARIO | M21080600156 | New_Event | Defective Pole | Include | Include | Equipment | 410 | 2021-08-09 | 4510 | keep | 0 | Aug | 2021 | 0.0030717 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
ARECIBO | 2021-08-09 11:17 | 2021-08-09 17:10 | 5 | 005:53 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | A21080900035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 353 | 2021-08-09 | 1765 | keep | 0 | Aug | 2021 | 0.0012021 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-08-09 11:24 | 2021-08-09 11:25 | 812 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REEMPLAZO DE PUENTE PORTATIL 20% DE LA CARGA POR EL 1303-02 | S21080900027 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-09 | 812 | keep | 0 | Aug | 2021 | 0.00055305 | 0.00055305 | Momentary | FALSE | FALSE | Not_TMED_Event | 812
SAN JUAN | 2021-08-09 11:44 | 2021-08-09 11:45 | 641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21080900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-09 | 641 | keep | 0 | Aug | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
FAJARDO | 2021-08-09 11:54 | 2021-08-09 15:44 | 31 | 003:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | R21080900027 | New_Event | Cutout Failure | Include | Include | Equipment | 230 | 2021-08-09 | 7130 | keep | 0 | Aug | 2021 | 0.0048562 | 2.1114e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 31
ARECIBO | 2021-08-09 11:55 | 2021-08-09 12:40 | 6 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS EN TRANSFORMADOR | A21080900041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2021-08-09 | 270 | keep | 0 | Aug | 2021 | 0.0001839 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-08-09 12:05 | 2021-08-09 12:40 | 1 | 000:35 | P | NO SE REPORTO CAUSA | 3 X 15 EN BANCO DE TRANSFORMADOR | C21080900053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 35 | 2021-08-09 | 35 | keep | 0 | Aug | 2021 | 2.3838e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-08-09 12:05 | 2021-08-09 17:41 | 10 | 005:36 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA X 25 KVA | C21080900052 | New_Event | Service Transformer Failure | Include | Include | Equipment | 336 | 2021-08-09 | 3360 | keep | 0 | Aug | 2021 | 0.0022885 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-08-09 12:07 | 2021-08-09 13:50 | 10 | 001:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | C21080900055 | New_Event | Secondary Wire Down | Include | Include | Equipment | 103 | 2021-08-09 | 1030 | keep | 0 | Aug | 2021 | 0.00070153 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-08-09 12:34 | 2021-08-09 15:30 | 50 | 002:56 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21080900055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2021-08-09 | 8800 | keep | 0 | Aug | 2021 | 0.0059936 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-09 12:41 | 2021-08-09 18:41 | 1976 | 006:00 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO Y SE CERRARON MACHETES DE AMARRE CONTRA 1711-02 | B21080900050 | New_Event | Switch Failure | Include | Include | Equipment | 360 | 2021-08-09 | 711360 | keep | 0 | Aug | 2021 | 0.4845 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
YAUCO | 2021-08-09 12:51 | 2021-08-09 16:10 | 12 | 003:19 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REPARAR POSTE PARTIDO EN LA PERILLA | P21080900041 | New_Event | Defective Pole | Include | Include | Equipment | 199 | 2021-08-09 | 2388 | keep | 0 | Aug | 2021 | 0.0016265 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-08-09 12:58 | 2021-08-09 14:50 | 10 | 001:52 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR SE RETIRO BAMBÃšS SOBRE LAS LINEAS | M21080900058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2021-08-09 | 1120 | keep | 0 | Aug | 2021 | 0.00076283 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BAYAMON | 2021-08-09 13:00 | 2021-08-12 12:31 | 12 | 071:31 | P | SECUNDARIA/DESGANCHE | SE REPARARON LINEAS SECUNDARIAS Y SE REALIZO DESGANCHE | B21080900056 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 4291 | 2021-08-09 | 51492 | keep | 0 | Aug | 2021 | 0.035071 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-08-09 13:00 | 2021-08-09 13:01 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21080900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-09 | 393 | keep | 0 | Aug | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2021-08-09 13:00 | 2021-08-09 13:01 | 4 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21080900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-09 | 4 | keep | 0 | Aug | 2021 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2021-08-09 13:06 | 2021-08-09 16:25 | 80 | 003:19 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | C21080900060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2021-08-09 | 15920 | keep | 0 | Aug | 2021 | 0.010843 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-09 13:09 | 2021-08-10 13:05 | 30 | 023:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA Y SE REEMPLAZO CAJA PRIMARIA QUEMADA | S21080900053 | New_Event | Cutout Failure | Include | Include | Equipment | 1436 | 2021-08-09 | 43080 | keep | 0 | Aug | 2021 | 0.029342 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-08-09 13:09 | 2021-08-10 11:39 | 360 | 022:30 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE Y SE CERRO PUENTE ABIERTO CARGA POR 1907-03 | S21080900054 | New_Event | Switch Failure | Include | Include | Equipment | 1350 | 2021-08-09 | 486000 | keep | 0 | Aug | 2021 | 0.33101 | 0.00024519 | Sustained | FALSE | FALSE | Not_TMED_Event | 360
AGUADILLA | 2021-08-09 13:16 | 2021-08-09 23:24 | 100 | 010:08 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | M21080900061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 608 | 2021-08-09 | 60800 | keep | 0 | Aug | 2021 | 0.041411 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-08-09 13:37 | 2021-08-09 13:55 | 199 | 000:18 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA SE CERRO INTERRUPTOR | A21080900050 | New_Event | Wire Down | Include | Include | Equipment | 18 | 2021-08-09 | 3582 | keep | 0 | Aug | 2021 | 0.0024397 | 0.00013554 | Sustained | FALSE | TRUE | Not_TMED_Event | 199
MAYAGÃœEZ | 2021-08-09 13:38 | 2021-08-09 13:41 | 393 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON EL RECIERRE EN OFF SE VERIFICO PERSONAL FUERA DE LAS LINEAS Y SE CERRO EL INTERRUPTOR | M21080900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-08-09 | 1179 | keep | 0 | Aug | 2021 | 0.00080301 | 0.00026767 | Momentary | FALSE | TRUE | Not_TMED_Event | 393
MAYAGÃœEZ | 2021-08-09 13:38 | 2021-08-09 13:41 | 4 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 6007-04 CON EL RECIERRE EN OFF SE VERIFICO PERSONAL FUERA DE LAS LINEAS Y SE CERRO EL INTERRUPTOR LLEVA LA CARGA DEL 6007-05 | M21080900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-08-09 | 12 | keep | 0 | Aug | 2021 | 8.1731e-06 | 2.7244e-06 | Momentary | FALSE | TRUE | Not_TMED_Event | 4
SAN JUAN | 2021-08-09 13:50 | 2021-08-09 14:40 | 15 | 000:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE CERRO PUENTE SAFADO DE LINEA A CAJA | S21080900074 | New_Event | Secondary Wire Down | Include | Include | Equipment | 50 | 2021-08-09 | 750 | keep | 0 | Aug | 2021 | 0.00051082 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-08-09 13:52 | 2021-08-09 15:21 | 393 | 001:29 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6007-05 | M21080900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 89 | 2021-08-09 | 34977 | keep | 0 | Aug | 2021 | 0.023823 | 0.00026767 | Sustained | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2021-08-09 13:52 | 2021-08-09 15:21 | 4 | 001:29 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR 6007-04 EL CUAL LLEVA LA CARGA DEL 6007-05 NO SE REPORTO CAUSA | M21080900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 89 | 2021-08-09 | 356 | keep | 0 | Aug | 2021 | 0.00024247 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2021-08-09 13:55 | 2021-08-09 17:55 | 40 | 004:00 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21080900061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2021-08-09 | 9600 | keep | 0 | Aug | 2021 | 0.0065385 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-08-09 13:58 | 2021-08-10 13:01 | 12 | 023:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | B21080900077 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1383 | 2021-08-09 | 16596 | keep | 0 | Aug | 2021 | 0.011303 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2021-08-09 14:10 | 2021-08-09 16:24 | 26 | 002:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 40 EN CORTE DE LINEA CRUCE POR AVE | R21080900043 | New_Event |  |  | Include | Wildlife | 134 | 2021-08-09 | 3484 | keep | 0 | Aug | 2021 | 0.0023729 | 1.7708e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 26
HUMACAO | 2021-08-09 14:15 | 2021-08-09 15:17 | 1 | 001:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO | C21080900062 | New_Event | Bad Weather | Include | Include | Weather | 62 | 2021-08-09 | 62 | keep | 0 | Aug | 2021 | 4.2228e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-08-09 14:35 | 2021-08-09 16:00 | 6 | 001:25 | P | ESTRUCTURA AVERIADA | POSTE PARTIDO SE TRANSFIRIO TRANSFORMADOR A POSTE NUEVO | A21080400043 | New_Event | Defective Pole | Include | Include | Equipment | 85 | 2021-08-09 | 510 | keep | 0 | Aug | 2021 | 0.00034736 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2021-08-09 14:35 | 2021-08-09 18:20 | 16 | 003:45 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B21080900090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 225 | 2021-08-09 | 3600 | keep | 0 | Aug | 2021 | 0.0024519 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
FAJARDO | 2021-08-09 14:37 | 2021-08-09 18:13 | 107 | 003:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | R21080900046 | New_Event | Cutout Failure | Include | Include | Equipment | 216 | 2021-08-09 | 23112 | keep | 0 | Aug | 2021 | 0.015741 | 7.2877e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 107
BAYAMON | 2021-08-09 14:38 | 2021-08-09 15:03 | 25 | 000:25 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21080900078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 25 | 2021-08-09 | 625 | keep | 0 | Aug | 2021 | 0.00042568 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-08-09 14:47 | 2021-08-09 19:30 | 100 | 004:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21080900080 | New_Event | Bad Weather | Include | Include | Weather | 283 | 2021-08-09 | 28300 | keep | 0 | Aug | 2021 | 0.019275 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-08-09 15:15 | 2021-08-09 15:21 | 393 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6007-05 | M21080900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2021-08-09 | 2358 | keep | 0 | Aug | 2021 | 0.001606 | 0.00026767 | Sustained | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2021-08-09 15:15 | 2021-08-09 15:21 | 4 | 000:06 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR 6007-04 EL CUAL LLEVA LA CARGA DEL 6007-05 NO SE REPORTO CAUSA | M21080900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2021-08-09 | 24 | keep | 0 | Aug | 2021 | 1.6346e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2021-08-09 15:22 | 2021-08-09 18:57 | 200 | 003:35 | P | DESGANCHE | 2 X 50 Y 1 X 80 EN CORTES DE LINEA | C21080900067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2021-08-09 | 43000 | keep | 0 | Aug | 2021 | 0.029287 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-08-09 15:25 | 2021-08-09 19:30 | 125 | 004:05 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | A21080900057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2021-08-09 | 30625 | keep | 0 | Aug | 2021 | 0.020859 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
MAYAGÃœEZ | 2021-08-09 15:26 | 2021-08-09 17:18 | 50 | 001:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21080900090 | New_Event | Bad Weather | Include | Include | Weather | 112 | 2021-08-09 | 5600 | keep | 0 | Aug | 2021 | 0.0038141 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-08-09 15:28 | 2021-08-09 18:40 | 50 | 003:12 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21080900091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2021-08-09 | 9600 | keep | 0 | Aug | 2021 | 0.0065385 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-09 15:35 | 2021-08-09 15:48 | 393 | 000:13 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6007-05 | M21080900000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 13 | 2021-08-09 | 5109 | keep | 0 | Aug | 2021 | 0.0034797 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-09 15:35 | 2021-08-09 15:48 | 4 | 000:13 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR 6007-04 EL CUAL LLEVA LA CARGA DEL 6007-05 NO SE REPORTO CAUSA | M21080900000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 13 | 2021-08-09 | 52 | keep | 0 | Aug | 2021 | 3.5417e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-09 15:38 | 2021-08-09 21:13 | 80 | 005:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBÃšS SOBRE LAS LINEAS | M21080090092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 335 | 2021-08-09 | 26800 | keep | 0 | Aug | 2021 | 0.018253 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-08-09 15:48 | 2021-08-10 12:21 | 10 | 020:33 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REEMPLAZO BARRA EN PEDESTAL | C21080900075 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 1233 | 2021-08-09 | 12330 | keep | 0 | Aug | 2021 | 0.0083979 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-08-09 15:51 | 2021-08-09 18:45 | 20 | 002:54 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21080900093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2021-08-09 | 3480 | keep | 0 | Aug | 2021 | 0.0023702 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-08-09 15:54 | 2021-08-09 19:30 | 80 | 003:36 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | R21080900050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 216 | 2021-08-09 | 17280 | keep | 0 | Aug | 2021 | 0.011769 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-09 16:00 | 2021-08-09 20:56 | 30 | 004:56 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | B21080900099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 296 | 2021-08-09 | 8880 | keep | 0 | Aug | 2021 | 0.0060481 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-08-09 16:10 | 2021-08-09 18:00 | 76 | 001:50 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | P21080900070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 110 | 2021-08-09 | 8360 | keep | 0 | Aug | 2021 | 0.005694 | 5.1763e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 76
BAYAMON | 2021-08-09 16:25 | 2021-08-09 18:03 | 723 | 001:38 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO Y SE CERRO POR SCADA LLEVA CARGA DEL 1711-05 | B21080900050 | New_Event | Switch Failure | Include | Include | Equipment | 98 | 2021-08-09 | 70854 | keep | 0 | Aug | 2021 | 0.048258 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
CAGUAS | 2021-08-09 16:30 | 2021-08-09 17:08 | 6 | 000:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTE SECUNDARIO Y REPARAR LINEA SECUNDARIA | C21080900008 | New_Event | Secondary Wire Down | Include | Include | Equipment | 38 | 2021-08-09 | 228 | keep | 0 | Aug | 2021 | 0.00015529 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
ARECIBO | 2021-08-09 16:30 | 2021-08-09 18:00 | 100 | 001:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO Y SE CERRO CORTE DE LINEA | A21080900061 | New_Event | Wire Down | Include | Include | Equipment | 90 | 2021-08-09 | 9000 | keep | 0 | Aug | 2021 | 0.0061299 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-08-09 16:40 | 2021-08-09 17:51 | 65 | 001:11 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21080900086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2021-08-09 | 4615 | keep | 0 | Aug | 2021 | 0.0031433 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
MAYAGÃœEZ | 2021-08-09 16:45 | 2021-08-09 20:33 | 667 | 003:48 | T | DESCONECTIVO DEFECTUOSO | DISPARO DEL INTERRUPTOR SE RETIRO RAMAS SOBRE LAS LINEAS SE PASO SU CARGA POR EL 6008-05 YA QUE TIENE MACHETES DE BARRA QUEMADOS | M21080900103 | New_Event | Switch Failure | Include | Include | Equipment | 228 | 2021-08-09 | 152076 | keep | 0 | Aug | 2021 | 0.10358 | 0.00045429 | Sustained | FALSE | TRUE | Not_TMED_Event | 667
MAYAGÃœEZ | 2021-08-09 16:45 | 2021-08-09 20:33 | 2530 | 003:48 | T | DESCONECTIVO DEFECTUOSO | DISPARO DEL INTERRUPTOR SE RETIRO RAMAS SOBRE LAS LINEAS SE PASO SU CARGA POR EL 6008-05 YA QUE TIENE MACHETES DE BARRA QUEMADOS | M21080900103 | New_Event | Switch Failure | Include | Include | Equipment | 228 | 2021-08-09 | 576840 | keep | 0 | Aug | 2021 | 0.39288 | 0.0017232 | Sustained | FALSE | TRUE | Not_TMED_Event | 2530
MAYAGÃœEZ | 2021-08-09 16:45 | 2021-08-09 16:46 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21080900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-09 | 312 | keep | 0 | Aug | 2021 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
HUMACAO | 2021-08-09 17:00 | 2021-08-09 17:50 | 8 | 000:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR REPARO SECUNDARIA | C21080900091 | New_Event | Secondary Wire Down | Include | Include | Equipment | 50 | 2021-08-09 | 400 | keep | 0 | Aug | 2021 | 0.00027244 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2021-08-09 17:02 | 2021-08-09 18:57 | 170 | 001:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | P21080900078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2021-08-09 | 19550 | keep | 0 | Aug | 2021 | 0.013315 | 0.00011579 | Sustained | FALSE | TRUE | Not_TMED_Event | 170
ARECIBO | 2021-08-09 17:03 | 2021-08-09 18:30 | 30 | 001:27 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A21080900065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2021-08-09 | 2610 | keep | 0 | Aug | 2021 | 0.0017777 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-08-09 17:13 | 2021-08-09 18:07 | 20 | 000:54 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | A21080900067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2021-08-09 | 1080 | keep | 0 | Aug | 2021 | 0.00073558 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-08-09 18:03 | 2021-08-10 11:45 | 100 | 017:42 | P | DESGANCHE | 3 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA Y DESGANCHE LLEVA CARGA DEL 1711-05 | B21080800004 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1062 | 2021-08-09 | 106200 | keep | 0 | Aug | 2021 | 0.072332 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-09 18:07 | 2021-08-10 17:37 | 8 | 023:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTE | B21080900141 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1410 | 2021-08-09 | 11280 | keep | 0 | Aug | 2021 | 0.0076828 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-08-09 18:13 | 2021-08-09 19:15 | 2147 | 001:02 | T | DESGANCHE | SE REALIZO DESGANCHE DE BAMBUA Y SE CERRO POR SCADA | B21080900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2021-08-09 | 133114 | keep | 0 | Aug | 2021 | 0.090663 | 0.0014623 | Sustained | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2021-08-09 18:41 | 2021-08-10 15:53 | 100 | 021:12 | P | DESGANCHE | 3 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA Y DESGANCHE 1711-05 CARGA POR EL 1711-02 | B21080800004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1272 | 2021-08-09 | 127200 | keep | 0 | Aug | 2021 | 0.086635 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
GUAYAMA | 2021-08-09 18:44 | 2021-08-10 07:09 | 138 | 012:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | P21080900085 | New_Event |  |  | Include | Wildlife | 745 | 2021-08-09 | 102810 | keep | 0 | Aug | 2021 | 0.070023 | 9.3991e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 138
BAYAMON | 2021-08-09 18:46 | 2021-08-09 18:47 | 76 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA MIRAMAR | S21080900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-08-09 | 76 | keep | 0 | Aug | 2021 | 5.1763e-05 | 5.1763e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 76
BAYAMON | 2021-08-09 18:46 | 2021-08-09 18:47 | 626 | 000:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA MIRAMAR | S21080900000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2021-08-09 | 626 | keep | 0 | Aug | 2021 | 0.00042637 | 0.00042637 | Momentary | FALSE | FALSE | Not_TMED_Event | 626
MAYAGÃœEZ | 2021-08-09 19:26 | 2021-08-09 19:27 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21080900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-09 | 990 | keep | 0 | Aug | 2021 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
PONCE | 2021-08-09 19:30 | 2021-08-10 11:39 | 75 | 016:09 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | P21080900091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 969 | 2021-08-09 | 72675 | keep | 0 | Aug | 2021 | 0.049499 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
MAYAGÃœEZ | 2021-08-09 19:41 | 2021-08-09 19:42 | 312 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21080900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-09 | 312 | keep | 0 | Aug | 2021 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
BAYAMON | 2021-08-09 20:03 | 2021-08-09 20:21 | 1715 | 000:18 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA TRANSFERIDA AL 1708-03 | B210809000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 18 | 2021-08-09 | 30870 | keep | 0 | Aug | 2021 | 0.021025 | 0.0011681 | Sustained | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2021-08-09 20:03 | 2021-08-09 20:21 | 1498 | 000:18 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA CARGA DEL 1708-02 | B210809000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 18 | 2021-08-09 | 26964 | keep | 0 | Aug | 2021 | 0.018365 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
AGUADILLA | 2021-08-09 20:05 | 2021-08-09 21:40 | 200 | 001:35 | P | ESTRUCTURA AVERIADA | SE ABRIO MACHETES PARA CERRAR PUENTES LUEGO DE REMPLAZAR POSTE PRIMARIO PARTIDO | M21080900031 | Additional_clients | Defective Pole | Include | Include | Equipment | 95 | 2021-08-09 | 19000 | keep | 0 | Aug | 2021 | 0.012941 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-09 20:31 | 2021-08-09 20:34 | 1715 | 000:03 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA TRANSFERIDA AL 1708-03 | B210809000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-08-09 | 5145 | keep | 0 | Aug | 2021 | 0.0035042 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-09 20:31 | 2021-08-09 20:34 | 1498 | 000:03 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA CARGA DEL 1708-02 | B210809000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-08-09 | 4494 | keep | 0 | Aug | 2021 | 0.0030608 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-09 20:51 | 2021-08-10 18:53 | 10 | 022:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | B21080900189 | New_Event | Cutout Failure | Include | Include | Equipment | 1322 | 2021-08-09 | 13220 | keep | 0 | Aug | 2021 | 0.0090041 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-08-09 21:05 | 2021-08-09 21:20 | 1715 | 000:15 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA TRANFERIDA AL 1708-03 | B210809000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 15 | 2021-08-09 | 25725 | keep | 0 | Aug | 2021 | 0.017521 | 0.0011681 | Sustained | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2021-08-09 21:05 | 2021-08-09 21:20 | 1498 | 000:15 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA CARGA DEL 1708-02 | B210809000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 15 | 2021-08-09 | 22470 | keep | 0 | Aug | 2021 | 0.015304 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
CAGUAS | 2021-08-09 21:09 | 2021-08-10 11:18 | 80 | 014:09 | P | DESGANCHE | 2 X 40 Y 2 X 65 EN CORTE DE LINEAS | C21080900119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 849 | 2021-08-09 | 67920 | keep | 0 | Aug | 2021 | 0.04626 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-08-09 21:11 | 2021-08-09 23:40 | 300 | 002:29 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA POR DESGANCHE | A21080900090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2021-08-09 | 44700 | keep | 0 | Aug | 2021 | 0.030445 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-08-09 21:25 | 2021-08-10 10:00 | 1 | 012:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21080900161 | New_Event | Vegetation Contact | Include | Include | Vegetation | 755 | 2021-08-09 | 755 | keep | 0 | Aug | 2021 | 0.00051423 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CANOVANAS | 2021-08-09 21:32 | 2021-08-09 22:14 | 100 | 000:42 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21080900067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 42 | 2021-08-09 | 4200 | keep | 0 | Aug | 2021 | 0.0028606 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-08-09 21:57 | 2021-08-10 | 125 | 002:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA POR PAJARO QUE CRUZO LINEAS | A21080900101 | New_Event |  |  | Include | Wildlife | 123 | 2021-08-09 | 15375 | keep | 0 | Aug | 2021 | 0.010472 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
MAYAGÃœEZ | 2021-08-09 22:15 | 2021-08-10 10:10 | 10 | 011:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | CAJA QUEMADA EN TRANSFORMADOR SE ABRIO CORTE DE LINEA PARA REMPLAZO DE LA MISMA POR PERSONAL DE LORD ELECTRIC | M21080900167 | New_Event | Cutout Failure | Include | Include | Equipment | 715 | 2021-08-09 | 7150 | keep | 0 | Aug | 2021 | 0.0048698 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BAYAMON | 2021-08-09 22:17 | 2021-08-09 22:18 | 1715 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1708-03 CARGA TRANSFERIDA AL 1708-03 | B21080900000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-09 | 1715 | keep | 0 | Aug | 2021 | 0.0011681 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-09 22:17 | 2021-08-09 22:18 | 1498 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1708-03 LLEVANDO LA CARGA DEL 1708-02 | B21080900000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-09 | 1498 | keep | 0 | Aug | 2021 | 0.0010203 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-08-09 23:19 | 2021-08-10 14:10 | 65 | 014:51 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | P21080900106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 891 | 2021-08-09 | 57915 | keep | 0 | Aug | 2021 | 0.039446 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
CANOVANAS | 2021-08-09 23:36 | 2021-08-10 10:20 | 90 | 010:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA QUEMADA | R21080900079 | New_Event | Cutout Failure | Include | Include | Equipment | 644 | 2021-08-09 | 57960 | keep | 0 | Aug | 2021 | 0.039476 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
HUMACAO | 2021-08-10 00:24 | 2021-08-10 00:25 | 1835 | 000:01 | T | DESGANCHE | RECIERRE | C21081000002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-10 | 1835 | keep | 0 | Aug | 2021 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
HUMACAO | 2021-08-10 00:25 | 2021-08-11 16:06 | 150 | 039:41 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C21081100332 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2381 | 2021-08-10 | 357150 | keep | 0 | Aug | 2021 | 0.24325 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
HUMACAO | 2021-08-10 01:28 | 2021-08-10 01:29 | 3 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C21081000000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-08-10 | 3 | keep | 0 | Aug | 2021 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2021-08-10 01:31 | 2021-08-10 01:32 | 2704 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21081000001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 2704 | keep | 0 | Aug | 2021 | 0.0018417 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
CAGUAS | 2021-08-10 01:34 | 2021-08-10 15:20 | 245 | 013:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C21081000054 | New_Event | Cutout Failure | Include | Include | Equipment | 826 | 2021-08-10 | 202370 | keep | 0 | Aug | 2021 | 0.13783 | 0.00016687 | Sustained | FALSE | TRUE | Not_TMED_Event | 245
HUMACAO | 2021-08-10 01:37 | 2021-08-10 01:38 | 3701 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5400 | C21081000012 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-10 | 3701 | keep | 0 | Aug | 2021 | 0.0025207 | 0.0025207 | Momentary | FALSE | TRUE | Not_TMED_Event | 3701
HUMACAO | 2021-08-10 01:37 | 2021-08-10 01:38 | 989 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5400 | C21081000012 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-10 | 989 | keep | 0 | Aug | 2021 | 0.0006736 | 0.0006736 | Momentary | FALSE | TRUE | Not_TMED_Event | 989
HUMACAO | 2021-08-10 01:37 | 2021-08-10 01:38 | 1467 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5400 | C21081000012 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-10 | 1467 | keep | 0 | Aug | 2021 | 0.00099917 | 0.00099917 | Momentary | FALSE | TRUE | Not_TMED_Event | 1467
HUMACAO | 2021-08-10 02:56 | 2021-08-10 10:53 | 300 | 007:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 Y 2 X 100 EN CORTES DE LINEAS MAL TIEMPO | C21081000006 | New_Event | Bad Weather | Include | Include | Weather | 477 | 2021-08-10 | 143100 | keep | 0 | Aug | 2021 | 0.097465 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
UTUADO | 2021-08-10 04:00 | 2021-08-10 12:24 | 100 | 008:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | A21081000005 | New_Event | Cutout Failure | Include | Include | Equipment | 504 | 2021-08-10 | 50400 | keep | 0 | Aug | 2021 | 0.034327 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BARRANQUITAS | 2021-08-10 04:02 | 2021-08-10 04:03 | 2410 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE EVENTO ATMOSFERICO | C21081000000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-08-10 | 2410 | keep | 0 | Aug | 2021 | 0.0016414 | 0.0016414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2410
BARRANQUITAS | 2021-08-10 04:02 | 2021-08-10 04:04 | 2826 | 000:02 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL EVENTO ATMOSFERICO | C21081000000 | New_Event | Bad Weather | Include | Include | Weather | 2 | 2021-08-10 | 5652 | keep | 0 | Aug | 2021 | 0.0038496 | 0.0019248 | Momentary | FALSE | FALSE | Not_TMED_Event | 2826
CANOVANAS | 2021-08-10 04:30 | 2021-08-10 09:18 | 90 | 004:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | R21081000001 | New_Event | Bad Weather | Include | Include | Weather | 288 | 2021-08-10 | 25920 | keep | 0 | Aug | 2021 | 0.017654 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
CAGUAS | 2021-08-10 05:36 | 2021-08-10 05:37 | 853 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C21081000000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-08-10 | 853 | keep | 0 | Aug | 2021 | 0.00058097 | 0.00058097 | Momentary | FALSE | FALSE | Not_TMED_Event | 853
CAGUAS | 2021-08-10 05:37 | 2021-08-10 13:49 | 65 | 008:12 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21081000013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 492 | 2021-08-10 | 31980 | keep | 0 | Aug | 2021 | 0.021781 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
ARECIBO | 2021-08-10 06:15 | 2021-08-10 09:45 | 60 | 003:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21081000008 | New_Event | Bad Weather | Include | Include | Weather | 210 | 2021-08-10 | 12600 | keep | 0 | Aug | 2021 | 0.0085818 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-08-10 06:22 | 2021-08-10 10:35 | 100 | 004:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | A21081000009 | New_Event | Bad Weather | Include | Include | Weather | 253 | 2021-08-10 | 25300 | keep | 0 | Aug | 2021 | 0.017232 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-08-10 06:36 | 2021-08-10 12:15 | 40 | 005:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | A21081000010 | New_Event | Bad Weather | Include | Include | Weather | 339 | 2021-08-10 | 13560 | keep | 0 | Aug | 2021 | 0.0092357 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-08-10 06:41 | 2021-08-10 09:35 | 100 | 002:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | A21081000011 | New_Event | Bad Weather | Include | Include | Weather | 174 | 2021-08-10 | 17400 | keep | 0 | Aug | 2021 | 0.011851 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-08-10 06:48 | 2021-08-10 06:49 | 635 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | R21081000000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-08-10 | 635 | keep | 0 | Aug | 2021 | 0.0004325 | 0.0004325 | Momentary | FALSE | FALSE | Not_TMED_Event | 635
CANOVANAS | 2021-08-10 06:49 | 2021-08-10 07:21 | 335 | 000:32 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZARON AISLADORES ROTOS Y MACHETES QUEMADOS | R21081000013 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 32 | 2021-08-10 | 10720 | keep | 0 | Aug | 2021 | 0.0073013 | 0.00022817 | Sustained | FALSE | FALSE | Not_TMED_Event | 335
BAYAMON | 2021-08-10 06:53 | 2021-08-10 06:55 | 1983 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1801-02 | B21081000008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-10 | 3966 | keep | 0 | Aug | 2021 | 0.0027012 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-08-10 06:53 | 2021-08-10 06:55 | 2720 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA PARTE DE LA CARGA POR EL 1801-02 | B21081000008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-10 | 5440 | keep | 0 | Aug | 2021 | 0.0037052 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
BAYAMON | 2021-08-10 06:53 | 2021-08-10 06:55 | 186 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1711-04 Y PARTE DEL 1717-01 | B21081000008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-10 | 372 | keep | 0 | Aug | 2021 | 0.00025337 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
MAYAGÃœEZ | 2021-08-10 07:00 | 2021-08-10 11:23 | 100 | 004:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21081000027 | New_Event | Bad Weather | Include | Include | Weather | 263 | 2021-08-10 | 26300 | keep | 0 | Aug | 2021 | 0.017913 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-08-10 07:02 | 2021-08-10 07:04 | 1983 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1801-02 | B21081000010 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-10 | 3966 | keep | 0 | Aug | 2021 | 0.0027012 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-08-10 07:02 | 2021-08-10 07:04 | 2720 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA PARTE DE LA CARGA POR EL 1801-02 | B21081000010 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-10 | 5440 | keep | 0 | Aug | 2021 | 0.0037052 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
BAYAMON | 2021-08-10 07:02 | 2021-08-10 07:04 | 186 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1711-04 Y PARTE DEL 1717-01 | B21081000010 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-10 | 372 | keep | 0 | Aug | 2021 | 0.00025337 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2021-08-10 07:04 | 2021-08-10 19:35 | 36 | 012:31 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21081000138 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 751 | 2021-08-10 | 27036 | keep | 0 | Aug | 2021 | 0.018414 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
CANOVANAS | 2021-08-10 07:21 | 2021-08-10 07:22 | 635 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | R21081000000 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-08-10 | 635 | keep | 0 | Aug | 2021 | 0.0004325 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-08-10 07:21 | 2021-08-10 12:50 | 60 | 005:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | A21081000013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 329 | 2021-08-10 | 19740 | keep | 0 | Aug | 2021 | 0.013445 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CANOVANAS | 2021-08-10 07:22 | 2021-08-10 07:29 | 335 | 000:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZARON AISLADORES ROTOS Y MACHETES QUEMADOS | R21081000013 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 7 | 2021-08-10 | 2345 | keep | 0 | Aug | 2021 | 0.0015972 | 0.00022817 | Sustained | FALSE | FALSE | Not_TMED_Event | 335
CANOVANAS | 2021-08-10 07:29 | 2021-08-10 07:30 | 635 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | R21081000000 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-08-10 | 635 | keep | 0 | Aug | 2021 | 0.0004325 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-08-10 07:30 | 2021-08-10 08:33 | 635 | 001:03 | T | AISLADOR ROTO, PARTIDO O SAFADO | SECCIONALIZARON AISLADOR ROTO Y MACHETES QUEMADOS | R21081000013 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 63 | 2021-08-10 | 40005 | keep | 0 | Aug | 2021 | 0.027247 | 0.0004325 | Sustained | FALSE | FALSE | Not_TMED_Event | 635
SAN JUAN | 2021-08-10 07:34 | 2021-08-10 07:35 | 3046 | 000:01 | T | DESGANCHE | RECIERRE | R21081000010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-10 | 3046 | keep | 0 | Aug | 2021 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2021-08-10 07:35 | 2021-08-10 19:05 | 40 | 011:30 | P | DESGANCHE | 1 X 30 EN RISER Y 1 X 40 EN CORTE DE LINEA | R21081000120 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 690 | 2021-08-10 | 27600 | keep | 0 | Aug | 2021 | 0.018798 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-08-10 07:36 | 2021-08-10 11:02 | 1 | 003:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN BANCO DE TRANSFORMADOR CRUCE POR AVE | C21081000020 | New_Event |  |  | Include | Wildlife | 206 | 2021-08-10 | 206 | keep | 0 | Aug | 2021 | 0.00014031 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-08-10 07:38 | 2021-08-10 17:22 | 120 | 009:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21081000021 | New_Event | Bad Weather | Include | Include | Weather | 584 | 2021-08-10 | 70080 | keep | 0 | Aug | 2021 | 0.047731 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
CAGUAS | 2021-08-10 07:56 | 2021-08-10 11:41 | 80 | 003:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21081000022 | New_Event |  |  | Include | Wildlife | 225 | 2021-08-10 | 18000 | keep | 0 | Aug | 2021 | 0.01226 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CANOVANAS | 2021-08-10 08:33 | 2021-08-10 10:05 | 335 | 001:32 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZARON AISLADORES ROTOS Y MACHETES QUEMADOS | R21081000013 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 92 | 2021-08-10 | 30820 | keep | 0 | Aug | 2021 | 0.020991 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-08-10 09:01 | 2021-08-10 11:20 | 10 | 002:19 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081000021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2021-08-10 | 1390 | keep | 0 | Aug | 2021 | 0.00094672 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
HUMACAO | 2021-08-10 09:12 | 2021-08-10 09:13 | 2354 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE MAL TIEMPO | C21081000000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-08-10 | 2354 | keep | 0 | Aug | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
HUMACAO | 2021-08-10 09:13 | 2021-08-11 09:45 | 60 | 024:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN SU-CCD5 @ T-7 MAL TIEMPO | C21081000167 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 1472 | 2021-08-10 | 88320 | keep | 0 | Aug | 2021 | 0.060154 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2021-08-10 09:44 | 2021-08-10 14:25 | 135 | 004:41 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C21081000034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 281 | 2021-08-10 | 37935 | keep | 0 | Aug | 2021 | 0.025837 | 9.1948e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 135
BARRANQUITAS | 2021-08-10 09:46 | 2021-08-10 12:16 | 3 | 002:30 | P | SECUNDARIA/DESGANCHE | SE REPARO SECUNDARIA ROTA POR ARBOL | C21081000035 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 150 | 2021-08-10 | 450 | keep | 0 | Aug | 2021 | 0.00030649 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2021-08-10 09:50 | 2021-08-10 15:11 | 20 | 005:21 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE DE 40' DE MADERA POR POSTE DE 40' GALVANIZADO NO FUNDIO FUSIBLE ALGUNO | B21081000030 | New_Event | Defective Pole | Include | Include | Equipment | 321 | 2021-08-10 | 6420 | keep | 0 | Aug | 2021 | 0.0043726 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-08-10 09:56 | 2021-08-10 11:00 | 60 | 001:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | A21081000032 | New_Event | Bad Weather | Include | Include | Weather | 64 | 2021-08-10 | 3840 | keep | 0 | Aug | 2021 | 0.0026154 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
FAJARDO | 2021-08-10 09:58 | 2021-08-10 10:50 | 65 | 000:52 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | R21081000037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 52 | 2021-08-10 | 3380 | keep | 0 | Aug | 2021 | 0.0023021 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BAYAMON | 2021-08-10 09:59 | 2021-08-10 12:50 | 15 | 002:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA RAPARAR BAJANTE SECUNDARIO | S21080900090 | New_Event | Secondary Wire Down | Include | Include | Equipment | 171 | 2021-08-10 | 2565 | keep | 0 | Aug | 2021 | 0.001747 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-08-10 10:00 | 2021-08-10 15:50 | 200 | 005:50 | P | HERRAJE ROTO O PODRIDO | REEMPLAZO DE CRUCETAS EN MALAS CONDICIONES | P210810000XX | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 350 | 2021-08-10 | 70000 | keep | 0 | Aug | 2021 | 0.047677 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2021-08-10 10:05 | 2021-08-10 11:19 | 635 | 001:14 | T | AISLADOR ROTO, PARTIDO O SAFADO | SECCIONALIZARON AISLADORES ROTOS, MACHETES QUEMADOS Y TRANSFIRIO PARTE DE LA CARGA DEL 2305-04 AL 2305-01. EL 2305-04 NO CIERRA POR SCADA, NI MANUAL ELECTRICAMENTE. | R21081000013 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 74 | 2021-08-10 | 46990 | keep | 0 | Aug | 2021 | 0.032005 | 0.0004325 | Sustained | FALSE | FALSE | Not_TMED_Event | 635
MAYAGÃœEZ | 2021-08-10 10:10 | 2021-08-10 12:53 | 160 | 002:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN TRANSFORMADOR SE CERRO CORTE DE LINEA | M21080900167 | New_Event | Cutout Failure | Include | Include | Equipment | 163 | 2021-08-10 | 26080 | keep | 0 | Aug | 2021 | 0.017763 | 0.00010898 | Sustained | FALSE | TRUE | Not_TMED_Event | 160
GUAYAMA | 2021-08-10 10:30 | 2021-08-10 16:00 | 100 | 005:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA RETESAR LINEA | P210810000XX | New_Event | Wire Down | Include | Include | Equipment | 330 | 2021-08-10 | 33000 | keep | 0 | Aug | 2021 | 0.022476 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-08-10 10:35 | 2021-08-10 14:44 | 80 | 004:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | A21081000038 | New_Event | Bad Weather | Include | Include | Weather | 249 | 2021-08-10 | 19920 | keep | 0 | Aug | 2021 | 0.013567 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-08-10 10:42 | 2021-08-10 12:20 | 180 | 001:38 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | C21081000040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 98 | 2021-08-10 | 17640 | keep | 0 | Aug | 2021 | 0.012015 | 0.0001226 | Sustained | FALSE | TRUE | Not_TMED_Event | 180
AGUADILLA | 2021-08-10 10:45 | 2021-08-10 12:50 | 100 | 002:05 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21080900039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2021-08-10 | 12500 | keep | 0 | Aug | 2021 | 0.0085137 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-08-10 10:46 | 2021-08-10 13:26 | 8 | 002:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO NEUTRAL | B21080700031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 160 | 2021-08-10 | 1280 | keep | 0 | Aug | 2021 | 0.0008718 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-08-10 10:48 | 2021-08-10 12:42 | 10 | 001:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | C21081000041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 114 | 2021-08-10 | 1140 | keep | 0 | Aug | 2021 | 0.00077645 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-08-10 10:55 | 2021-08-10 16:00 | 15 | 005:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE SECCIONALIZO TOMA AVERIADA | C21081000043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 305 | 2021-08-10 | 4575 | keep | 0 | Aug | 2021 | 0.003116 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-08-10 10:58 | 2021-08-10 10:59 | 830 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE INTERRUPTOR | A21081000042 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-10 | 830 | keep | 0 | Aug | 2021 | 0.00056531 | 0.00056531 | Momentary | FALSE | FALSE | Not_TMED_Event | 830
ARECIBO | 2021-08-10 10:59 | 2021-08-10 19:20 | 1 | 008:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RAPARO LINEA PRIMARIA | A21081000094 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 501 | 2021-08-10 | 501 | keep | 0 | Aug | 2021 | 0.00034123 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
AGUADILLA | 2021-08-10 11:00 | 2021-08-10 17:10 | 150 | 006:10 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR POSTE PRIMARIO PARTIDO | M21081000024 | New_Event | Defective Pole | Include | Include | Equipment | 370 | 2021-08-10 | 55500 | keep | 0 | Aug | 2021 | 0.037801 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-08-10 11:00 | 2021-08-10 15:30 | 10 | 004:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REMPLAZARON BAJANTES | A21081000040 | New_Event | Wire Down | Include | Include | Equipment | 270 | 2021-08-10 | 2700 | keep | 0 | Aug | 2021 | 0.001839 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-08-10 11:07 | 2021-08-11 11:08 | 30 | 024:01 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21081000107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1441 | 2021-08-10 | 43230 | keep | 0 | Aug | 2021 | 0.029444 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BARRANQUITAS | 2021-08-10 11:12 | 2021-08-10 15:42 | 46 | 004:30 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C21081000046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 270 | 2021-08-10 | 12420 | keep | 0 | Aug | 2021 | 0.0084592 | 3.133e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 46
MAYAGÃœEZ | 2021-08-10 11:15 | 2021-08-10 13:43 | 6 | 002:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | M21081000025 | New_Event | Secondary Wire Down | Include | Include | Equipment | 148 | 2021-08-10 | 888 | keep | 0 | Aug | 2021 | 0.00060481 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2021-08-10 11:19 | 2021-08-10 14:15 | 334 | 002:56 | P | AISLADOR ROTO, PARTIDO O SAFADO | REEMPLAZARON AISLADORES ROTOS, MACHETES QUEMADOS Y TRANSFIRIO LA CARGA DEL 2305-04 AL 2305-01. EL 2305-04 NO CIERRA POR SCADA, NI MANUAL ELECTRICAMENTE. | R21081000013 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 176 | 2021-08-10 | 58784 | keep | 0 | Aug | 2021 | 0.040038 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-10 11:20 | 2021-08-10 11:21 | 353 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO CON R/R OFF QUEDO EN SERVICIO | S21081000020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 353 | keep | 0 | Aug | 2021 | 0.00024043 | 0.00024043 | Momentary | FALSE | FALSE | Not_TMED_Event | 353
AGUADILLA | 2021-08-10 11:23 | 2021-08-11 12:20 | 8 | 024:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA PARTIDA | M21081000029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1497 | 2021-08-10 | 11976 | keep | 0 | Aug | 2021 | 0.0081568 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-08-10 11:24 | 2021-08-10 11:25 | 1061 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21081000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 1061 | keep | 0 | Aug | 2021 | 0.00072264 | 0.00072264 | Momentary | FALSE | FALSE | Not_TMED_Event | 1061
MAYAGÃœEZ | 2021-08-10 11:26 | 2021-08-10 14:40 | 60 | 003:14 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21081000030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2021-08-10 | 11640 | keep | 0 | Aug | 2021 | 0.007928 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-08-10 11:27 | 2021-08-10 11:28 | 15 | 000:01 | P | DESGANCHE | 1 X 10 EN TRANSFOTRMADOR Y 1 X 15 EN RISER SE REALIZO DESGANCHE | B21081000029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-10 | 15 | keep | 0 | Aug | 2021 | 1.0216e-05 | 1.0216e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-08-10 11:28 | 2021-08-10 11:29 | 10211 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR EL 1206-03 | S21081000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 10211 | keep | 0 | Aug | 2021 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-08-10 11:28 | 2021-08-10 11:29 | 4133 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1204-05 | S21081000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 4133 | keep | 0 | Aug | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-08-10 11:29 | 2021-08-10 12:44 | 50 | 001:15 | P | NO SE REPORTO CAUSA | 1 X 80 1 X 50 Y 1 X 40 EN CORTE DE LINEA CARGA POR EL 1206-03 | S21080900007 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 75 | 2021-08-10 | 3750 | keep | 0 | Aug | 2021 | 0.0025541 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-10 11:31 | 2021-08-10 11:32 | 80 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 30% DEL 1346-2 CARGA POR 1529-15 | S21081000027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 80 | keep | 0 | Aug | 2021 | 5.4488e-05 | 5.4488e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-08-10 11:31 | 2021-08-10 11:32 | 1802 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 30% DEL 1346-2 | S21081000027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 1802 | keep | 0 | Aug | 2021 | 0.0012273 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
SAN JUAN | 2021-08-10 11:38 | 2021-08-10 11:39 | 225 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR EL 1908-03 | S21081000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 225 | keep | 0 | Aug | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-08-10 11:38 | 2021-08-10 11:39 | 3957 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA EL 1303-04 | S21081000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 3957 | keep | 0 | Aug | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
PONCE | 2021-08-10 11:38 | 2021-08-10 17:17 | 1 | 005:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REMMPLAZARON CONEXIONES EN TRANSCLOUSURE DEL PEAJE EN LA PLAYA DE PONCE | P21081000015 | New_Event | Wire Down | Include | Include | Equipment | 339 | 2021-08-10 | 339 | keep | 0 | Aug | 2021 | 0.00023089 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-08-10 11:39 | 2021-08-10 11:40 | 222 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE LLEVA 1909 09 | S21081000000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2021-08-10 | 222 | keep | 0 | Aug | 2021 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2021-08-10 11:39 | 2021-08-10 11:40 | 4411 | 000:01 | P | DESCONECTIVO DEFECTUOSO | RECIERRE CARGA POR 1907 03 | S21081000000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2021-08-10 | 4411 | keep | 0 | Aug | 2021 | 0.0030043 | 0.0030043 | Momentary | FALSE | FALSE | Not_TMED_Event | 4411
BAYAMON | 2021-08-10 11:40 | 2021-08-11 10:46 | 360 | 023:06 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE Y SE CERRO PUENTE ABIERTO CARGA POR 1907-03 | S21080900054 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1386 | 2021-08-10 | 498960 | keep | 0 | Aug | 2021 | 0.33984 | 0.00024519 | Sustained | FALSE | FALSE | Not_TMED_Event | 360
FAJARDO | 2021-08-10 11:40 | 2021-08-10 12:20 | 4 | 000:40 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR CON DERRAME DE 50KVA X 50KVA | R21081000051 | New_Event | Service Transformer Failure | Include | Include | Equipment | 40 | 2021-08-10 | 160 | keep | 0 | Aug | 2021 | 0.00010898 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-08-10 11:42 | 2021-08-10 16:15 | 65 | 004:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | A21081000051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 273 | 2021-08-10 | 17745 | keep | 0 | Aug | 2021 | 0.012086 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BAYAMON | 2021-08-10 11:45 | 2021-08-10 11:48 | 723 | 000:03 | T | DESGANCHE | DISPARO INTERRUPTOR SE CERRO POR SCADA LLEVA CARGA DEL 1711-05 | B21081000045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-08-10 | 2169 | keep | 0 | Aug | 2021 | 0.0014773 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2021-08-10 11:45 | 2021-08-10 11:48 | 1976 | 000:03 | T | DESGANCHE | DISPARO INTERRUPTOR SE CERRO POR SCADA CARGA POR 1711-02 | B21081000045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-08-10 | 5928 | keep | 0 | Aug | 2021 | 0.0040375 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2021-08-10 11:48 | 2021-08-10 15:53 | 100 | 004:05 | P | DESGANCHE | 3 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA Y DESGANCHE LLEVA CARGA DEL 1711-05 | B21080800004 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 245 | 2021-08-10 | 24500 | keep | 0 | Aug | 2021 | 0.016687 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-08-10 11:49 | 2021-08-11 11:50 | 8 | 024:01 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21081000147 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1441 | 2021-08-10 | 11528 | keep | 0 | Aug | 2021 | 0.0078517 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-08-10 11:50 | 2021-08-10 17:04 | 1 | 005:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZAO CAJA PRIMARIA | B21081000048 | New_Event | Cutout Failure | Include | Include | Equipment | 314 | 2021-08-10 | 314 | keep | 0 | Aug | 2021 | 0.00021386 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-08-10 11:55 | 2021-08-10 17:09 | 40 | 005:14 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21081000031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 314 | 2021-08-10 | 12560 | keep | 0 | Aug | 2021 | 0.0085546 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
AGUADILLA | 2021-08-10 11:56 | 2021-08-11 11:30 | 60 | 023:34 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21081000034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1414 | 2021-08-10 | 84840 | keep | 0 | Aug | 2021 | 0.057784 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-08-10 12:11 | 2021-08-10 23:35 | 25 | 011:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA CARGA POR EL 1303-04 | S21081000037 | New_Event | Wire Down | Include | Include | Equipment | 684 | 2021-08-10 | 17100 | keep | 0 | Aug | 2021 | 0.011647 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
AGUADILLA | 2021-08-10 12:16 | 2021-08-10 22:28 | 5 | 010:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | M21081000040 | New_Event | Bad Weather | Include | Include | Weather | 612 | 2021-08-10 | 3060 | keep | 0 | Aug | 2021 | 0.0020842 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
BAYAMON | 2021-08-10 12:21 | 2021-08-10 18:26 | 36 | 006:05 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081000054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 365 | 2021-08-10 | 13140 | keep | 0 | Aug | 2021 | 0.0089496 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
ARECIBO | 2021-08-10 12:27 | 2021-08-10 14:36 | 2916 | 002:09 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO INTERRUPTOR AISLADORES ROTOS | A21081000053 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 129 | 2021-08-10 | 376164 | keep | 0 | Aug | 2021 | 0.2562 | 0.0019861 | Sustained | FALSE | FALSE | Not_TMED_Event | 2916
HUMACAO | 2021-08-10 12:28 | 2021-08-10 16:36 | 70 | 004:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO DISCO ROTO | C21081000059 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 248 | 2021-08-10 | 17360 | keep | 0 | Aug | 2021 | 0.011824 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
HUMACAO | 2021-08-10 12:31 | 2021-08-10 17:25 | 500 | 004:54 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C21081000060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 294 | 2021-08-10 | 147000 | keep | 0 | Aug | 2021 | 0.10012 | 0.00034055 | Sustained | FALSE | TRUE | Not_TMED_Event | 500
SAN JUAN | 2021-08-10 12:32 | 2021-08-10 17:13 | 68 | 004:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE SUBIO PRIMARIA Y SE REALIZO DESGANCHE | S21081000044 | New_Event | Wire Down | Include | Include | Equipment | 281 | 2021-08-10 | 19108 | keep | 0 | Aug | 2021 | 0.013014 | 4.6314e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 68
HUMACAO | 2021-08-10 12:33 | 2021-08-10 19:44 | 70 | 007:11 | P | CABLE SOTERRADO AVERIADO | SE CERRO N/O DEL SU-2A AL SU-3A, SE DEJO ABIERTO DEL RISER AL SU-3A PROBO MALO | C21081000062 | New_Event | UG Cable Fault | Include | Include | Equipment | 431 | 2021-08-10 | 30170 | keep | 0 | Aug | 2021 | 0.020549 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
FAJARDO | 2021-08-10 12:45 | 2021-08-10 13:56 | 110 | 001:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR IGUANA | R21081000067 | New_Event |  |  | Include | Wildlife | 71 | 2021-08-10 | 7810 | keep | 0 | Aug | 2021 | 0.0053194 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
ARECIBO | 2021-08-10 12:50 | 2021-08-10 15:00 | 150 | 002:10 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA DESGANCHE | A21081000057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2021-08-10 | 19500 | keep | 0 | Aug | 2021 | 0.013281 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
GUAYAMA | 2021-08-10 13:00 | 2021-08-10 15:15 | 50 | 002:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21081000031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2021-08-10 | 6750 | keep | 0 | Aug | 2021 | 0.0045974 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-08-10 13:00 | 2021-08-10 16:00 | 15 | 003:00 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR DE 37.5 KVA X 35.7 KVA CON PERDIDA DE ACEITE | P21081000030 | New_Event | Service Transformer Failure | Include | Include | Equipment | 180 | 2021-08-10 | 2700 | keep | 0 | Aug | 2021 | 0.001839 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2021-08-10 13:02 | 2021-08-10 13:03 | 519 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | C21081000067 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-10 | 519 | keep | 0 | Aug | 2021 | 0.00035349 | 0.00035349 | Momentary | FALSE | FALSE | Not_TMED_Event | 519
HUMACAO | 2021-08-10 13:03 | 2021-08-10 19:07 | 300 | 006:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO MACHETES PARA LEVANTAR CONDUCTORES | C21081000183 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 364 | 2021-08-10 | 109200 | keep | 0 | Aug | 2021 | 0.074376 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2021-08-10 13:05 | 2021-08-10 13:06 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1909-08 | S21081000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 2435 | keep | 0 | Aug | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-08-10 13:05 | 2021-08-10 13:06 | 2956 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE LEVA EL 1907-05 | S21081000000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-08-10 | 2956 | keep | 0 | Aug | 2021 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
ARECIBO | 2021-08-10 13:05 | 2021-08-10 19:45 | 70 | 006:40 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA PARARRAYO | A21081000061 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 400 | 2021-08-10 | 28000 | keep | 0 | Aug | 2021 | 0.019071 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BAYAMON | 2021-08-10 13:06 | 2021-08-11 08:22 | 30 | 019:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA Y SE REEMPLAZO CAJA PRIMARIA QUEMADA | S21080900053 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1156 | 2021-08-10 | 34680 | keep | 0 | Aug | 2021 | 0.02362 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-08-10 13:12 | 2021-08-10 17:39 | 74 | 004:27 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21081000062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 267 | 2021-08-10 | 19758 | keep | 0 | Aug | 2021 | 0.013457 | 5.0401e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 74
GUAYAMA | 2021-08-10 13:21 | 2021-08-10 16:55 | 50 | 003:34 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21081000033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 214 | 2021-08-10 | 10700 | keep | 0 | Aug | 2021 | 0.0072877 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-08-10 13:29 | 2021-08-10 16:10 | 125 | 002:41 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21081000077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2021-08-10 | 20125 | keep | 0 | Aug | 2021 | 0.013707 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
CAGUAS | 2021-08-10 13:29 | 2021-08-10 16:48 | 74 | 003:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE DIO LIGADURA | C21081000076 | New_Event | Wire Down | Include | Include | Equipment | 199 | 2021-08-10 | 14726 | keep | 0 | Aug | 2021 | 0.01003 | 5.0401e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 74
PONCE | 2021-08-10 13:30 | 2021-08-10 14:00 | 11 | 000:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 37.5 POR 50 KVA | P2108100040 | New_Event | Service Transformer Failure | Include | Include | Equipment | 30 | 2021-08-10 | 330 | keep | 0 | Aug | 2021 | 0.00022476 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2021-08-10 13:33 | 2021-08-11 10:25 | 15 | 020:52 | P | NO SE REPORTO CAUSA | 1 X 30 EN PROVISIONAL AEREO | B21081000094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1252 | 2021-08-10 | 18780 | keep | 0 | Aug | 2021 | 0.012791 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-08-10 13:34 | 2021-08-10 16:45 | 125 | 003:11 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21081000052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2021-08-10 | 23875 | keep | 0 | Aug | 2021 | 0.016261 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
BAYAMON | 2021-08-10 13:35 | 2021-08-11 10:25 | 30 | 020:50 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | B21081000061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1250 | 2021-08-10 | 37500 | keep | 0 | Aug | 2021 | 0.025541 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-08-10 13:46 | 2021-08-10 15:52 | 40 | 002:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO BAJANTE SAFADO A CAJA PRIMARIA. NO FUNDIO FUSIBLE | R21081000078 | New_Event | Wire Down | Include | Include | Equipment | 126 | 2021-08-10 | 5040 | keep | 0 | Aug | 2021 | 0.0034327 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-08-10 13:49 | 2021-08-10 19:01 | 50 | 005:12 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21081000084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 312 | 2021-08-10 | 15600 | keep | 0 | Aug | 2021 | 0.010625 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-08-10 13:50 | 2021-08-10 19:40 | 1 | 005:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21081000078 | New_Event | Bad Weather | Include | Include | Weather | 350 | 2021-08-10 | 350 | keep | 0 | Aug | 2021 | 0.00023838 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-08-10 13:50 | 2021-08-10 18:42 | 44 | 004:52 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR SE REEMPLAZO PARARRAYO | C21081000072 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 292 | 2021-08-10 | 12848 | keep | 0 | Aug | 2021 | 0.0087507 | 2.9968e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 44
UTUADO | 2021-08-10 13:56 | 2021-08-11 14:15 | 7 | 024:19 | P | ESTRUCTURA AVERIADA | SE CORRIGIO POSTE PARTIDO EN LA PERILLA Y SE DESGANCHO | A21081000074 | New_Event | Defective Pole | Include | Include | Equipment | 1459 | 2021-08-10 | 10213 | keep | 0 | Aug | 2021 | 0.006956 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2021-08-10 13:56 | 2021-08-10 15:15 | 40 | 001:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CONVERTIDOR MAL TIEMPO | A21081000074 | New_Event | Bad Weather | Include | Include | Weather | 79 | 2021-08-10 | 3160 | keep | 0 | Aug | 2021 | 0.0021523 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-08-10 13:57 | 2021-08-10 16:37 | 1 | 002:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21081000082 | New_Event | Bad Weather | Include | Include | Weather | 160 | 2021-08-10 | 160 | keep | 0 | Aug | 2021 | 0.00010898 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-08-10 13:58 | 2021-08-11 09:12 | 12 | 019:14 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | S21081000071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1154 | 2021-08-10 | 13848 | keep | 0 | Aug | 2021 | 0.0094318 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2021-08-10 14:07 | 2021-08-10 17:30 | 50 | 003:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21081000039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2021-08-10 | 10150 | keep | 0 | Aug | 2021 | 0.0069131 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-08-10 14:14 | 2021-08-10 16:03 | 25 | 001:49 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21081000075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2021-08-10 | 2725 | keep | 0 | Aug | 2021 | 0.001856 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-08-10 14:15 | 2021-08-10 17:49 | 40 | 003:34 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA Y SE RETIRO PENCA | S21081000076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 214 | 2021-08-10 | 8560 | keep | 0 | Aug | 2021 | 0.0058302 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-08-10 14:15 | 2021-08-11 12:38 | 1 | 022:23 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | C21081000088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1343 | 2021-08-10 | 1343 | keep | 0 | Aug | 2021 | 0.00091471 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-08-10 14:19 | 2021-08-10 20:30 | 60 | 006:11 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21081000067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 371 | 2021-08-10 | 22260 | keep | 0 | Aug | 2021 | 0.015161 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-08-10 14:30 | 2021-08-10 14:31 | 137 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21081000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 137 | keep | 0 | Aug | 2021 | 9.331e-05 | 9.331e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 137
CAGUAS | 2021-08-10 14:34 | 2021-08-10 20:48 | 1701 | 006:14 | P | AISLADOR ROTO, PARTIDO O SAFADO | SECCIONALIZO AISLADOR ROTO Y SE CERRO INTELLIRUPTER 3006-5D | C21081000093 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 374 | 2021-08-10 | 636174 | keep | 0 | Aug | 2021 | 0.4333 | 0.0011585 | Sustained | FALSE | FALSE | Not_TMED_Event | 1701
CANOVANAS | 2021-08-10 14:36 | 2021-08-10 18:24 | 60 | 003:48 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21081000098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2021-08-10 | 13680 | keep | 0 | Aug | 2021 | 0.0093174 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-08-10 14:36 | 2021-08-10 17:33 | 1416 | 002:57 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO MACHETES PARA REMPLAZAR AISLADORES AVERIADOS | A21081000082 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 177 | 2021-08-10 | 250632 | keep | 0 | Aug | 2021 | 0.1707 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-08-10 14:37 | 2021-08-10 17:13 | 162 | 002:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100, 1 X 80 Y 1 X 65 EN CORTES DE LINA MAL TIEMPO | C21081000095 | New_Event | Bad Weather | Include | Include | Weather | 156 | 2021-08-10 | 25272 | keep | 0 | Aug | 2021 | 0.017213 | 0.00011034 | Sustained | FALSE | FALSE | Not_TMED_Event | 162
ARECIBO | 2021-08-10 14:37 | 2021-08-11 12:05 | 50 | 021:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CULEBRA CRUZO LINEAS | A21081000081 | New_Event |  |  | Include | Wildlife | 1288 | 2021-08-10 | 64400 | keep | 0 | Aug | 2021 | 0.043863 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-08-10 14:38 | 2021-08-10 19:01 | 30 | 004:23 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN RISER Y 2 X 80 EN SU - 15 SE REEMPLAZO PARRARAYO AVERIADO | R21081000099 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 263 | 2021-08-10 | 7890 | keep | 0 | Aug | 2021 | 0.0053738 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-08-10 14:39 | 2021-08-10 16:57 | 200 | 002:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21081000074 | New_Event | Bad Weather | Include | Include | Weather | 138 | 2021-08-10 | 27600 | keep | 0 | Aug | 2021 | 0.018798 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
YAUCO | 2021-08-10 14:50 | 2021-08-10 14:51 | 1475 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210801000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 1475 | keep | 0 | Aug | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
PONCE | 2021-08-10 14:52 | 2021-08-10 14:53 | 85 | 000:01 | P | DESGANCHE | 1 FUSIBLE DE 40 EN C/L DESGANCHE | P21080900100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-10 | 85 | keep | 0 | Aug | 2021 | 5.7893e-05 | 5.7893e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 85
YAUCO | 2021-08-10 14:52 | 2021-08-10 14:53 | 1587 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21081000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 1587 | keep | 0 | Aug | 2021 | 0.0010809 | 0.0010809 | Momentary | FALSE | FALSE | Not_TMED_Event | 1587
CANOVANAS | 2021-08-10 15:08 | 2021-08-10 16:45 | 60 | 001:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | R21081000106 | New_Event | Bad Weather | Include | Include | Weather | 97 | 2021-08-10 | 5820 | keep | 0 | Aug | 2021 | 0.003964 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-08-10 15:13 | 2021-08-11 15:26 | 125 | 024:13 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B21081000087 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1453 | 2021-08-10 | 181625 | keep | 0 | Aug | 2021 | 0.1237 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
MAYAGÃœEZ | 2021-08-10 15:19 | 2021-08-10 17:39 | 80 | 002:20 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M21081000084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2021-08-10 | 11200 | keep | 0 | Aug | 2021 | 0.0076283 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-10 15:21 | 2021-08-10 15:22 | 1976 | 000:01 | T | DESGANCHE | DISPARO INTERRUPTOR SE CERRO POR SCADA CARGA POR 1711-02 | B21081000045 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-10 | 1976 | keep | 0 | Aug | 2021 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
MAYAGÃœEZ | 2021-08-10 15:30 | 2021-08-10 20:55 | 20 | 005:25 | P | ESTRUCTURA AVERIADA | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR POSTE PARTIDO | M21081000089 | New_Event | Defective Pole | Include | Include | Equipment | 325 | 2021-08-10 | 6500 | keep | 0 | Aug | 2021 | 0.0044271 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2021-08-10 15:31 | 2021-08-10 16:30 | 75 | 000:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 Y 1 X 50 EN CORTES DE LINEAS SE REPARO CONDUCTOR SAFADO DE AISLADOR | R21081000111 | New_Event | Wire Down | Include | Include | Equipment | 59 | 2021-08-10 | 4425 | keep | 0 | Aug | 2021 | 0.0030138 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
SAN JUAN | 2021-08-10 15:34 | 2021-08-12 03:23 | 100 | 035:49 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S21081000092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2149 | 2021-08-10 | 214900 | keep | 0 | Aug | 2021 | 0.14637 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-08-10 15:40 | 2021-08-10 19:00 | 65 | 003:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | A21081000098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2021-08-10 | 13000 | keep | 0 | Aug | 2021 | 0.0088542 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BARRANQUITAS | 2021-08-10 15:44 | 2021-08-11 15:49 | 90 | 024:05 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21081000107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1445 | 2021-08-10 | 130050 | keep | 0 | Aug | 2021 | 0.088576 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
BAYAMON | 2021-08-10 15:48 | 2021-08-11 18:25 | 30 | 026:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO Y SE CERRO CORTE DE LINEA | B21081000097 | New_Event | Wire Down | Include | Include | Equipment | 1597 | 2021-08-10 | 47910 | keep | 0 | Aug | 2021 | 0.032631 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-08-10 16:03 | 2021-08-10 16:25 | 50 | 000:22 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P21081000057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 22 | 2021-08-10 | 1100 | keep | 0 | Aug | 2021 | 0.0007492 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-10 16:10 | 2021-08-11 12:07 | 40 | 019:57 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21081000110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1197 | 2021-08-10 | 47880 | keep | 0 | Aug | 2021 | 0.032611 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-08-10 16:14 | 2021-08-10 16:16 | 3387 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B21081000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-10 | 6774 | keep | 0 | Aug | 2021 | 0.0046137 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
VEGA BAJA | 2021-08-10 16:16 | 2021-08-11 17:39 | 6 | 025:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO EN PEDESTAL | B21081000124 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1523 | 2021-08-10 | 9138 | keep | 0 | Aug | 2021 | 0.0062239 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-08-10 16:23 | 2021-08-11 10:03 | 25 | 017:40 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S21081000103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1060 | 2021-08-10 | 26500 | keep | 0 | Aug | 2021 | 0.018049 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-08-10 16:28 | 2021-08-10 16:29 | 600 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21081000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 600 | keep | 0 | Aug | 2021 | 0.00040866 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2021-08-10 16:29 | 2021-08-12 13:19 | 3 | 044:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R21081000116 | New_Event |  |  | Include | Wildlife | 2690 | 2021-08-10 | 8070 | keep | 0 | Aug | 2021 | 0.0054964 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
BAYAMON | 2021-08-10 16:29 | 2021-08-11 08:33 | 50 | 016:04 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER Y 2 X 30 EN CORTE DE LINEA | B21081000105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 964 | 2021-08-10 | 48200 | keep | 0 | Aug | 2021 | 0.032829 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-08-10 16:36 | 2021-08-11 10:15 | 12 | 017:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | C21081000114 | New_Event |  |  | Include | Wildlife | 1059 | 2021-08-10 | 12708 | keep | 0 | Aug | 2021 | 0.0086554 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-08-10 16:37 | 2021-08-10 19:20 | 30 | 002:43 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21081000110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2021-08-10 | 4890 | keep | 0 | Aug | 2021 | 0.0033306 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-08-10 16:40 | 2021-08-10 19:26 | 90 | 002:46 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R21081000119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2021-08-10 | 14940 | keep | 0 | Aug | 2021 | 0.010176 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
BAYAMON | 2021-08-10 16:43 | 2021-08-11 08:18 | 40 | 015:35 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21081000106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 935 | 2021-08-10 | 37400 | keep | 0 | Aug | 2021 | 0.025473 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-08-10 16:43 | 2021-08-11 13:04 | 60 | 020:21 | P | DESGANCHE | 3 X 40 EN CORTE DE LINEA SE RETEZO LINEA DESGANCHE MASIVO | B21081000060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1221 | 2021-08-10 | 73260 | keep | 0 | Aug | 2021 | 0.049897 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-08-10 16:44 | 2021-08-11 07:41 | 50 | 014:57 | P | NO SE REPORTO CAUSA | 1 X 50 EN SU - 3 NO CAUSA | C21081000116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 897 | 2021-08-10 | 44850 | keep | 0 | Aug | 2021 | 0.030547 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-08-10 16:45 | 2021-08-10 19:40 | 100 | 002:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA. BAJANTE CRUZANDO CON CRUCETA | P21081000065 | New_Event | Wire Down | Include | Include | Equipment | 175 | 2021-08-10 | 17500 | keep | 0 | Aug | 2021 | 0.011919 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
YAUCO | 2021-08-10 16:46 | 2021-08-10 16:47 | 1475 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210810000XX | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 1475 | keep | 0 | Aug | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
YAUCO | 2021-08-10 16:47 | 2021-08-10 18:00 | 50 | 001:13 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA Y 1 X 80 EN OTRO CORTE DE LINEA. NO SE REPORTO CAUSA | P21081000070 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 73 | 2021-08-10 | 3650 | keep | 0 | Aug | 2021 | 0.002486 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-10 16:52 | 2021-08-11 16:10 | 75 | 023:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA CAMION IMPACTO ARBOL CRUZANDO LAS LINEAS MOMENTANEAMENTE | A21081000110 | New_Event |  |  | Include | Wildlife | 1398 | 2021-08-10 | 104850 | keep | 0 | Aug | 2021 | 0.071413 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
MAYAGÃœEZ | 2021-08-10 16:53 | 2021-08-11 15:45 | 40 | 022:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO | M21081000105 | New_Event | Wire Down | Include | Include | Equipment | 1372 | 2021-08-10 | 54880 | keep | 0 | Aug | 2021 | 0.037379 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-08-10 16:57 | 2021-08-11 10:33 | 25 | 017:36 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE LEVANTO CONDUCTOR | S21081000113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1056 | 2021-08-10 | 26400 | keep | 0 | Aug | 2021 | 0.017981 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2021-08-10 16:59 | 2021-08-10 17:13 | 2484 | 000:14 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR POR CRUCE DE ALAMBRES | P210810000XX | New_Event | Wire Down | Include | Include | Equipment | 14 | 2021-08-10 | 34776 | keep | 0 | Aug | 2021 | 0.023686 | 0.0016918 | Sustained | FALSE | FALSE | Not_TMED_Event | 2484
BAYAMON | 2021-08-10 17:07 | 2021-08-11 13:49 | 40 | 020:42 | P | NO SE REPORTO CAUSA | 2 X 40 EN CORTE DE LINEA | B21081000118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1242 | 2021-08-10 | 49680 | keep | 0 | Aug | 2021 | 0.033837 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-08-10 17:16 | 2021-08-11 13:43 | 1 | 020:27 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA Y 1 X 40 EN RISER DE CLIENTE | B21081000119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1227 | 2021-08-10 | 1227 | keep | 0 | Aug | 2021 | 0.0008357 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-08-10 17:22 | 2021-08-10 17:55 | 12 | 000:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE SAFADO DE LINEA A CAJA EN TRANSFORMADOR | S21081000098 | New_Event | Wire Down | Include | Include | Equipment | 33 | 2021-08-10 | 396 | keep | 0 | Aug | 2021 | 0.00026971 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-08-10 17:25 | 2021-08-10 17:26 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6007-05 | M21081000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 393 | keep | 0 | Aug | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2021-08-10 17:25 | 2021-08-10 17:26 | 4 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR 6007-04 EL CUAL LLEVA LA CARGA DEL 6007-05 NO SE REPORTO CAUSA | M21081000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 4 | keep | 0 | Aug | 2021 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-08-10 17:33 | 2021-08-10 18:40 | 30 | 001:07 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA DESGANCHE | A21081000113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2021-08-10 | 2010 | keep | 0 | Aug | 2021 | 0.001369 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-08-10 17:37 | 2021-08-10 19:45 | 200 | 002:08 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M21081000113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2021-08-10 | 25600 | keep | 0 | Aug | 2021 | 0.017436 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-08-10 17:39 | 2021-08-10 18:35 | 10 | 000:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21081000116 | New_Event | Bad Weather | Include | Include | Weather | 56 | 2021-08-10 | 560 | keep | 0 | Aug | 2021 | 0.00038141 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-10 17:41 | 2021-08-10 17:46 | 3431 | 000:05 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DEL INTERRUPTOR RECIERRE EN OFF SE VERIFICO PERSONAL FUERA DE LAS LINEAS NO SE REPORTO CAUSA | A21081000117 | New_Event | Bad Weather | Include | Include | Weather | 5 | 2021-08-10 | 17155 | keep | 0 | Aug | 2021 | 0.011684 | 0.0023368 | Momentary | FALSE | TRUE | Not_TMED_Event | 3431
BARRANQUITAS | 2021-08-10 17:41 | 2021-08-10 19:23 | 2635 | 001:42 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6500 DE BARRANQUITAS A TORO NEGRO SE SECCIONALIZO DE OROCOVIS A TORO NEGRO | C21081000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2021-08-10 | 268770 | keep | 0 | Aug | 2021 | 0.18306 | 0.0017947 | Sustained | FALSE | TRUE | Not_TMED_Event | 2635
BARRANQUITAS | 2021-08-10 17:41 | 2021-08-10 19:23 | 2280 | 001:42 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6500 DE BARRANQUITAS A TORO NEGRO SE SECCIONALIZO DE OROCOVIS A TORO NEGRO | C21081000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2021-08-10 | 232560 | keep | 0 | Aug | 2021 | 0.1584 | 0.0015529 | Sustained | FALSE | TRUE | Not_TMED_Event | 2280
BARRANQUITAS | 2021-08-10 17:41 | 2021-08-10 19:23 | 1617 | 001:42 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6500 DE BARRANQUITAS A TORO NEGRO SE SECCIONALIZO DE OROCOVIS A TORO NEGRO | C21081000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2021-08-10 | 164934 | keep | 0 | Aug | 2021 | 0.11234 | 0.0011013 | Sustained | FALSE | TRUE | Not_TMED_Event | 1617
ARECIBO | 2021-08-10 17:46 | 2021-08-10 19:10 | 30 | 001:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | A21081000119 | Partial_restoration | Bad Weather | Include | Include | Weather | 84 | 2021-08-10 | 2520 | keep | 0 | Aug | 2021 | 0.0017164 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-10 17:57 | 2021-08-11 17:39 | 1 | 023:42 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | B21081000125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1422 | 2021-08-10 | 1422 | keep | 0 | Aug | 2021 | 0.00096852 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-08-10 17:59 | 2021-08-11 11:45 | 50 | 017:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO Y SE CERRO CORTE DE LINEA | M21081000115 | New_Event | Wire Down | Include | Include | Equipment | 1066 | 2021-08-10 | 53300 | keep | 0 | Aug | 2021 | 0.036302 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-10 18:08 | 2021-08-10 21:10 | 60 | 003:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | A21081000125 | New_Event | Bad Weather | Include | Include | Weather | 182 | 2021-08-10 | 10920 | keep | 0 | Aug | 2021 | 0.0074376 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
PONCE | 2021-08-10 18:17 | 2021-08-10 18:18 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210810000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 3744 | keep | 0 | Aug | 2021 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2021-08-10 18:17 | 2021-08-10 18:18 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 5004-06 | P210810000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 3114 | keep | 0 | Aug | 2021 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
MAYAGÃœEZ | 2021-08-10 18:17 | 2021-08-11 09:28 | 5 | 015:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | M21081000120 | New_Event | Bad Weather | Include | Include | Weather | 911 | 2021-08-10 | 4555 | keep | 0 | Aug | 2021 | 0.0031024 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
VEGA BAJA | 2021-08-10 18:20 | 2021-08-11 13:54 | 25 | 019:34 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21081000129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1174 | 2021-08-10 | 29350 | keep | 0 | Aug | 2021 | 0.01999 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
VEGA BAJA | 2021-08-10 18:22 | 2021-08-11 09:03 | 1 | 014:41 | P | NO SE REPORTO CAUSA | 2 X 25 EN MONTURA DE TRANSFORMADORES DEL CLIENTE | B21081000130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 881 | 2021-08-10 | 881 | keep | 0 | Aug | 2021 | 0.00060005 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-08-10 18:26 | 2021-08-11 19:51 | 185 | 025:25 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA DESGANCHO Y LEVANTO CONDUCTORES | R21081000129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1525 | 2021-08-10 | 282125 | keep | 0 | Aug | 2021 | 0.19215 | 0.000126 | Sustained | FALSE | TRUE | Not_TMED_Event | 185
ARECIBO | 2021-08-10 18:46 | 2021-08-11 11:00 | 20 | 016:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21081000132 | New_Event | Bad Weather | Include | Include | Weather | 974 | 2021-08-10 | 19480 | keep | 0 | Aug | 2021 | 0.013268 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
HUMACAO | 2021-08-10 19:02 | 2021-08-11 08:59 | 55 | 013:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21081000147 | New_Event | Bad Weather | Include | Include | Weather | 837 | 2021-08-10 | 46035 | keep | 0 | Aug | 2021 | 0.031354 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
BAYAMON | 2021-08-10 19:04 | 2021-08-11 09:54 | 89 | 014:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO INTERRUPTOR PARA REEMPLAZO DE CAJA PRIMARIA QUEMADA A PETICION DE BENGIE FEBRES 75% DE LA CARGA POR EL 1011-05 | S21081000133 | New_Event | Cutout Failure | Include | Include | Equipment | 890 | 2021-08-10 | 79210 | keep | 0 | Aug | 2021 | 0.05395 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
BAYAMON | 2021-08-10 19:04 | 2021-08-11 09:16 | 50 | 014:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEPLAZO CAJA PRIMARIA QUEMADA LLEVA 75% DEL 1011-02 | S21081000133 | New_Event | Cutout Failure | Include | Include | Equipment | 852 | 2021-08-10 | 42600 | keep | 0 | Aug | 2021 | 0.029015 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2021-08-10 19:04 | 2021-08-11 06:20 | 30 | 011:16 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CARGA ESTA POR EL 1711-02 | B21081000058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 676 | 2021-08-10 | 20280 | keep | 0 | Aug | 2021 | 0.013813 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-08-10 19:05 | 2021-08-10 19:06 | 3046 | 000:01 | T | DESGANCHE | RECIERRE | R21081000135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-10 | 3046 | keep | 0 | Aug | 2021 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2021-08-10 19:06 | 2021-08-11 08:57 | 40 | 013:51 | P | DESGANCHE | 1 X 30 EN RISER Y 1 X 40 EN CORTE DE LINEA | R21081000120 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 831 | 2021-08-10 | 33240 | keep | 0 | Aug | 2021 | 0.02264 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-08-10 19:07 | 2021-08-10 19:08 | 519 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO INTERRUPTOR | C21081000151 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2021-08-10 | 519 | keep | 0 | Aug | 2021 | 0.00035349 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-08-10 19:08 | 2021-08-11 10:54 | 300 | 015:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO MACHETES PARA LEVANTAR CONDUCTORES | C21081000183 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 946 | 2021-08-10 | 283800 | keep | 0 | Aug | 2021 | 0.19329 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
FAJARDO | 2021-08-10 19:12 | 2021-08-11 06:24 | 30 | 011:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | R21081000136 | New_Event | Bad Weather | Include | Include | Weather | 672 | 2021-08-10 | 20160 | keep | 0 | Aug | 2021 | 0.013731 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
HUMACAO | 2021-08-10 19:24 | 2021-08-11 11:27 | 11 | 016:03 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR | C21081000157 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 963 | 2021-08-10 | 10593 | keep | 0 | Aug | 2021 | 0.0072148 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
HUMACAO | 2021-08-10 19:25 | 2021-08-11 09:44 | 95 | 014:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21081000159 | New_Event | Bad Weather | Include | Include | Weather | 859 | 2021-08-10 | 81605 | keep | 0 | Aug | 2021 | 0.055581 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
MAYAGÃœEZ | 2021-08-10 19:26 | 2021-08-11 17:12 | 60 | 021:46 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21081100122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1306 | 2021-08-10 | 78360 | keep | 0 | Aug | 2021 | 0.053371 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-08-10 19:27 | 2021-08-11 09:04 | 40 | 013:37 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | S21081000136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 817 | 2021-08-10 | 32680 | keep | 0 | Aug | 2021 | 0.022258 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-08-10 19:27 | 2021-08-11 08:51 | 40 | 013:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN CORTE DE LINEA MAL TIEMPO | R21081000138 | New_Event | Bad Weather | Include | Include | Weather | 804 | 2021-08-10 | 32160 | keep | 0 | Aug | 2021 | 0.021904 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-08-10 19:31 | 2021-08-10 21:13 | 40 | 001:42 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21081000162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2021-08-10 | 4080 | keep | 0 | Aug | 2021 | 0.0027789 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-08-10 19:34 | 2021-08-10 21:21 | 40 | 001:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | R21081000141 | New_Event | Bad Weather | Include | Include | Weather | 107 | 2021-08-10 | 4280 | keep | 0 | Aug | 2021 | 0.0029151 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
AGUADILLA | 2021-08-10 19:40 | 2021-08-11 11:20 | 30 | 015:40 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | M21081000124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 940 | 2021-08-10 | 28200 | keep | 0 | Aug | 2021 | 0.019207 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-08-10 20:01 | 2021-08-11 13:11 | 70 | 017:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CAMION CRUZO LINEAS | A21081000144 | New_Event |  |  | Include | Wildlife | 1030 | 2021-08-10 | 72100 | keep | 0 | Aug | 2021 | 0.049107 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BARRANQUITAS | 2021-08-10 20:03 | 2021-08-11 01:26 | 1 | 005:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA LEVANTO CONDUCTOR | C21081000170 | New_Event | Wire Down | Include | Include | Equipment | 323 | 2021-08-10 | 323 | keep | 0 | Aug | 2021 | 0.00021999 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-08-10 20:06 | 2021-08-11 08:54 | 60 | 012:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21081000171 | New_Event | Bad Weather | Include | Include | Weather | 768 | 2021-08-10 | 46080 | keep | 0 | Aug | 2021 | 0.031385 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
FAJARDO | 2021-08-10 20:20 | 2021-08-10 22:14 | 100 | 001:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 Y 1 X 40 EN CORTES DE LINEA LLUVIAS | R21081000142 | New_Event | Bad Weather | Include | Include | Weather | 114 | 2021-08-10 | 11400 | keep | 0 | Aug | 2021 | 0.0077645 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-08-10 20:26 | 2021-08-10 20:54 | 80 | 000:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | A21081000147 | New_Event | Bad Weather | Include | Include | Weather | 28 | 2021-08-10 | 2240 | keep | 0 | Aug | 2021 | 0.0015257 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-08-10 20:29 | 2021-08-11 10:52 | 65 | 014:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21081000177 | New_Event | Bad Weather | Include | Include | Weather | 863 | 2021-08-10 | 56095 | keep | 0 | Aug | 2021 | 0.038206 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
HUMACAO | 2021-08-10 20:31 | 2021-08-11 01:30 | 65 | 004:59 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA REMPLAZO DISCOS PARTIDOS | C21081000179 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 299 | 2021-08-10 | 19435 | keep | 0 | Aug | 2021 | 0.013237 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
CAGUAS | 2021-08-10 20:45 | 2021-08-11 17:00 | 150 | 020:15 | P | DESGANCHE | 3 X 80 EN CORTE DE LINEA | C21081000187 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1215 | 2021-08-10 | 182250 | keep | 0 | Aug | 2021 | 0.12413 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-08-10 20:48 | 2021-08-10 20:52 | 3005 | 000:04 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO INTERRUPTOR CERRADO POR CONTROL | C21081000192 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 4 | 2021-08-10 | 12020 | keep | 0 | Aug | 2021 | 0.0081868 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-08-10 20:52 | 2021-08-11 10:36 | 1701 | 013:44 | P | AISLADOR ROTO, PARTIDO O SAFADO | SECCIONALIZO AISLADOR ROTO Y SE CERRO INTELLIRUPTER 3006-5D | C21081000093 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 824 | 2021-08-10 | 1401624 | keep | 0 | Aug | 2021 | 0.95464 | 0.0011585 | Sustained | FALSE | FALSE | Not_TMED_Event | 1701
CANOVANAS | 2021-08-10 21:00 | 2021-08-11 10:27 | 60 | 013:27 | P | DESGANCHE | 1 X 30 Y 1 X 50 EN CORTES DE LINEA | R21081000153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 807 | 2021-08-10 | 48420 | keep | 0 | Aug | 2021 | 0.032979 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-08-10 21:02 | 2021-08-11 14:05 | 100 | 017:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN CORTE DE LINEA | M21081000010 | New_Event | Cutout Failure | Include | Include | Equipment | 1023 | 2021-08-10 | 102300 | keep | 0 | Aug | 2021 | 0.069676 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-08-10 21:13 | 2021-08-10 21:14 | 1565 | 000:01 | T | DESGANCHE | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C21081000208 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-10 | 1565 | keep | 0 | Aug | 2021 | 0.0010659 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-08-10 21:14 | 2021-08-11 16:40 | 40 | 019:26 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21081000162 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1166 | 2021-08-10 | 46640 | keep | 0 | Aug | 2021 | 0.031766 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-08-10 21:16 | 2021-08-11 10:08 | 60 | 012:52 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | R21081000086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 772 | 2021-08-10 | 46320 | keep | 0 | Aug | 2021 | 0.031548 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-08-10 21:37 | 2021-08-10 21:38 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21081000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 990 | keep | 0 | Aug | 2021 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
BARRANQUITAS | 2021-08-10 21:44 | 2021-08-11 16:46 | 140 | 019:02 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA NO CAUSA | C21081000218 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1142 | 2021-08-10 | 159880 | keep | 0 | Aug | 2021 | 0.10889 | 9.5353e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 140
BAYAMON | 2021-08-10 22:00 | 2021-08-10 22:01 | 1210 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21081000156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 1210 | keep | 0 | Aug | 2021 | 0.00082413 | 0.00082413 | Momentary | FALSE | FALSE | Not_TMED_Event | 1210
BAYAMON | 2021-08-10 22:00 | 2021-08-11 07:37 | 50 | 009:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | B21081000155 | New_Event | Bad Weather | Include | Include | Weather | 577 | 2021-08-10 | 28850 | keep | 0 | Aug | 2021 | 0.01965 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-08-10 22:11 | 2021-08-11 14:54 | 8 | 016:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21081000223 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1003 | 2021-08-10 | 8024 | keep | 0 | Aug | 2021 | 0.0054651 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2021-08-10 22:17 | 2021-08-10 22:18 | 1093 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21081000092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 1093 | keep | 0 | Aug | 2021 | 0.00074444 | 0.00074444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1093
PONCE | 2021-08-10 22:21 | 2021-08-10 22:22 | 1730 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21081000093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 1730 | keep | 0 | Aug | 2021 | 0.0011783 | 0.0011783 | Momentary | FALSE | FALSE | Not_TMED_Event | 1730
SAN JUAN | 2021-08-10 22:31 | 2021-08-10 22:32 | 225 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR EL 1908-03 | S21081000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 225 | keep | 0 | Aug | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2021-08-10 22:31 | 2021-08-10 22:32 | 3957 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA EL 1303-04 | S21081000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 3957 | keep | 0 | Aug | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
SAN JUAN | 2021-08-10 22:34 | 2021-08-11 07:54 | 30 | 009:20 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21081000160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 560 | 2021-08-10 | 16800 | keep | 0 | Aug | 2021 | 0.011442 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-08-10 22:51 | 2021-08-11 12:17 | 150 | 013:26 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | R21081000161 | New_Event | Vegetation Contact | Include | Include | Vegetation | 806 | 2021-08-10 | 120900 | keep | 0 | Aug | 2021 | 0.082344 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
PONCE | 2021-08-10 22:52 | 2021-08-10 22:53 | 1979 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE | P21081000096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 1979 | keep | 0 | Aug | 2021 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2021-08-10 22:52 | 2021-08-10 22:53 | 5069 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE | P21081000096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 5069 | keep | 0 | Aug | 2021 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2021-08-10 22:52 | 2021-08-10 22:53 | 5063 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE | P21081000096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 5063 | keep | 0 | Aug | 2021 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
YAUCO | 2021-08-10 22:53 | 2021-08-11 10:30 | 84 | 011:37 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P21081000095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 697 | 2021-08-10 | 58548 | keep | 0 | Aug | 2021 | 0.039877 | 5.7212e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 84
CANOVANAS | 2021-08-10 23:18 | 2021-08-10 23:38 | 100 | 000:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIAS | R21081000144 | New_Event | Bad Weather | Include | Include | Weather | 20 | 2021-08-10 | 2000 | keep | 0 | Aug | 2021 | 0.0013622 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
GUAYAMA | 2021-08-10 23:19 | 2021-08-11 07:57 | 80 | 008:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA POR LINEAS ARREADAS | P21081000102 | New_Event | Wire Down | Include | Include | Equipment | 518 | 2021-08-10 | 41440 | keep | 0 | Aug | 2021 | 0.028225 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BARRANQUITAS | 2021-08-10 23:29 | 2021-08-11 08:19 | 90 | 008:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C21081000246 | New_Event | Bad Weather | Include | Include | Weather | 530 | 2021-08-10 | 47700 | keep | 0 | Aug | 2021 | 0.032488 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
SAN JUAN | 2021-08-10 23:35 | 2021-08-10 23:36 | 1681 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR CARGA POR 1303-04 | S21081000000 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2021-08-10 | 1681 | keep | 0 | Aug | 2021 | 0.0011449 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-08-10 23:35 | 2021-08-10 23:36 | 1598 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CARGA POR EL 1303-04 | S21081000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 1598 | keep | 0 | Aug | 2021 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2021-08-10 23:36 | 2021-08-11 11:57 | 25 | 012:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA CARGA POR EL 1303-04 | S21081000037 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 741 | 2021-08-10 | 18525 | keep | 0 | Aug | 2021 | 0.012617 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-08-10 23:59 | 2021-08-11 | 271 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21081000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-10 | 271 | keep | 0 | Aug | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
HUMACAO | 2021-08-11 | 2021-08-11 07:33 | 60 | 007:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN RISER MAL TIEMPO | C21081100152 | New_Event | Bad Weather | Include | Include | Weather | 453 | 2021-08-11 | 27180 | keep | 0 | Aug | 2021 | 0.018512 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
BARRANQUITAS | 2021-08-11 00:07 | 2021-08-11 09:26 | 110 | 009:19 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 50 EN CORTE DE LINEA REEMPLAZO AISLADOR ROTO | C21081100002 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 559 | 2021-08-11 | 61490 | keep | 0 | Aug | 2021 | 0.041881 | 7.492e-05 | Sustained | FALSE | TRUE | TMED_Event | 110
YAUCO | 2021-08-11 00:08 | 2021-08-12 21:15 | 591 | 045:07 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR POR LINEA PRIMARIA EN EL SUELO. SE ABREN PUENTES PARA SECCIONALIZAR AVERIA | P21081100175 | New_Event | Wire Down | Include | Include | Equipment | 2707 | 2021-08-11 | 1599837 | keep | 0 | Aug | 2021 | 1.0896 | 0.00040253 | Sustained | FALSE | TRUE | TMED_Event | 591
BARRANQUITAS | 2021-08-11 00:09 | 2021-08-11 11:06 | 130 | 010:57 | P | DESGANCHE | 1 X 40 Y 2 X 50 EN CORTES DE LINEAS | C21081100004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 657 | 2021-08-11 | 85410 | keep | 0 | Aug | 2021 | 0.058172 | 8.8542e-05 | Sustained | FALSE | TRUE | TMED_Event | 130
PONCE | 2021-08-11 00:15 | 2021-08-11 00:16 | 4035 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210811000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-11 | 4035 | keep | 0 | Aug | 2021 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | TMED_Event | 4035
CAGUAS | 2021-08-11 00:18 | 2021-08-11 15:42 | 150 | 015:24 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C21081100007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 924 | 2021-08-11 | 138600 | keep | 0 | Aug | 2021 | 0.0944 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
CAGUAS | 2021-08-11 00:18 | 2021-08-11 11:30 | 100 | 011:12 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21081100008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 672 | 2021-08-11 | 67200 | keep | 0 | Aug | 2021 | 0.04577 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
CAGUAS | 2021-08-11 00:19 | 2021-08-11 13:42 | 100 | 013:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21081100009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 803 | 2021-08-11 | 80300 | keep | 0 | Aug | 2021 | 0.054692 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
PONCE | 2021-08-11 00:19 | 2021-08-11 00:20 | 4035 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | P210811000XX | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-11 | 4035 | keep | 0 | Aug | 2021 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | TMED_Event | 4035
CAGUAS | 2021-08-11 00:20 | 2021-08-11 00:21 | 4390 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO INTERRUPTOR | C21081100010 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-11 | 4390 | keep | 0 | Aug | 2021 | 0.00299 | 0.00299 | Momentary | FALSE | FALSE | TMED_Event | 4390
PONCE | 2021-08-11 00:20 | 2021-08-11 14:03 | 50 | 013:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE EN CORTE DE LINEAS | P2108110083 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 823 | 2021-08-11 | 41150 | keep | 0 | Aug | 2021 | 0.028027 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
YAUCO | 2021-08-11 00:20 | 2021-08-11 00:21 | 1924 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P210811000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-11 | 1924 | keep | 0 | Aug | 2021 | 0.0013104 | 0.0013104 | Momentary | FALSE | TRUE | TMED_Event | 1924
YAUCO | 2021-08-11 00:20 | 2021-08-11 00:21 | 968 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P210811000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-11 | 968 | keep | 0 | Aug | 2021 | 0.0006593 | 0.0006593 | Momentary | FALSE | TRUE | TMED_Event | 968
YAUCO | 2021-08-11 00:20 | 2021-08-11 00:21 | 680 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P210811000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-11 | 680 | keep | 0 | Aug | 2021 | 0.00046314 | 0.00046314 | Momentary | FALSE | TRUE | TMED_Event | 680
YAUCO | 2021-08-11 00:20 | 2021-08-11 00:21 | 2246 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P210811000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-11 | 2246 | keep | 0 | Aug | 2021 | 0.0015297 | 0.0015297 | Momentary | FALSE | TRUE | TMED_Event | 2246
YAUCO | 2021-08-11 00:20 | 2021-08-11 00:21 | 1569 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P210811000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-11 | 1569 | keep | 0 | Aug | 2021 | 0.0010686 | 0.0010686 | Momentary | FALSE | TRUE | TMED_Event | 1569
YAUCO | 2021-08-11 00:20 | 2021-08-11 00:21 | 2309 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P210811000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-11 | 2309 | keep | 0 | Aug | 2021 | 0.0015726 | 0.0015726 | Momentary | FALSE | TRUE | TMED_Event | 2309
YAUCO | 2021-08-11 00:20 | 2021-08-11 00:21 | 2179 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P210811000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-11 | 2179 | keep | 0 | Aug | 2021 | 0.0014841 | 0.0014841 | Momentary | FALSE | TRUE | TMED_Event | 2179
YAUCO | 2021-08-11 00:20 | 2021-08-11 00:21 | 2440 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P210811000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-11 | 2440 | keep | 0 | Aug | 2021 | 0.0016619 | 0.0016619 | Momentary | FALSE | TRUE | TMED_Event | 2440
YAUCO | 2021-08-11 00:20 | 2021-08-11 00:21 | 1352 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P210811000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-11 | 1352 | keep | 0 | Aug | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | TRUE | TMED_Event | 1352
YAUCO | 2021-08-11 00:20 | 2021-08-11 00:21 | 3973 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P210811000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-11 | 3973 | keep | 0 | Aug | 2021 | 0.002706 | 0.002706 | Momentary | FALSE | TRUE | TMED_Event | 3973
YAUCO | 2021-08-11 00:20 | 2021-08-11 00:21 | 2484 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 700 | P210811000XX | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-11 | 2484 | keep | 0 | Aug | 2021 | 0.0016918 | 0.0016918 | Momentary | FALSE | TRUE | TMED_Event | 2484
CAGUAS | 2021-08-11 00:21 | 2021-08-11 07:49 | 4000 | 007:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 Y 2 X 50 EN CORTES DE LINEA DESGANCHARON REMPLAZO AISLADORES Y CAJA | C21081100017 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 448 | 2021-08-11 | 1792000 | keep | 0 | Aug | 2021 | 1.2205 | 0.0027244 | Sustained | FALSE | TRUE | TMED_Event | 4000
YAUCO | 2021-08-11 00:21 | 2021-08-11 08:51 | 40 | 008:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21081000098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 510 | 2021-08-11 | 20400 | keep | 0 | Aug | 2021 | 0.013894 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
MAYAGÃœEZ | 2021-08-11 00:32 | 2021-08-11 00:33 | 108 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M21081100002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-11 | 108 | keep | 0 | Aug | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | TMED_Event | 108
MAYAGÃœEZ | 2021-08-11 00:34 | 2021-08-11 09:35 | 50 | 009:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21081100003 | New_Event | Bad Weather | Include | Include | Weather | 541 | 2021-08-11 | 27050 | keep | 0 | Aug | 2021 | 0.018424 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
CAGUAS | 2021-08-11 00:47 | 2021-08-11 00:48 | 2900 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C21081100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-11 | 2900 | keep | 0 | Aug | 2021 | 0.0019752 | 0.0019752 | Momentary | FALSE | FALSE | TMED_Event | 2900
CAGUAS | 2021-08-11 00:48 | 2021-08-11 00:53 | 2900 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C21081100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-08-11 | 14500 | keep | 0 | Aug | 2021 | 0.0098759 | 0.0019752 | Momentary | FALSE | FALSE | TMED_Event | 2900
SAN JUAN | 2021-08-11 00:59 | 2021-08-11 16:06 | 100 | 015:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA EN TRANSFPORMADOR | S21081100002 | New_Event | Wire Down | Include | Include | Equipment | 907 | 2021-08-11 | 90700 | keep | 0 | Aug | 2021 | 0.061775 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
MAYAGÃœEZ | 2021-08-11 00:59 | 2021-08-11 17:12 | 80 | 016:13 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21081100011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 973 | 2021-08-11 | 77840 | keep | 0 | Aug | 2021 | 0.053016 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
MAYAGÃœEZ | 2021-08-11 00:59 | 2021-08-11 01:03 | 721 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | M21081100012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-08-11 | 2884 | keep | 0 | Aug | 2021 | 0.0019643 | 0.00049107 | Momentary | FALSE | FALSE | TMED_Event | 721
PONCE | 2021-08-11 01:00 | 2021-08-11 11:02 | 40 | 010:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | P21081100018 | New_Event | Bad Weather | Include | Include | Weather | 602 | 2021-08-11 | 24080 | keep | 0 | Aug | 2021 | 0.016401 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
MAYAGÃœEZ | 2021-08-11 01:04 | 2021-08-11 15:15 | 75 | 014:11 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21081100014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 851 | 2021-08-11 | 63825 | keep | 0 | Aug | 2021 | 0.043471 | 5.1082e-05 | Sustained | FALSE | TRUE | TMED_Event | 75
CAGUAS | 2021-08-11 01:08 | 2021-08-11 19:30 | 30 | 018:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21081100028 | New_Event | Bad Weather | Include | Include | Weather | 1102 | 2021-08-11 | 33060 | keep | 0 | Aug | 2021 | 0.022517 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
MAYAGÃœEZ | 2021-08-11 01:08 | 2021-08-11 11:21 | 1 | 010:13 | P | OTRAS CAUSAS | VERIFICO CLIENTE TIENE SERVICIO | M21081100018 | New_Event | Other Causes | Include | Include | Other | 613 | 2021-08-11 | 613 | keep | 0 | Aug | 2021 | 0.00041751 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
PONCE | 2021-08-11 01:17 | 2021-08-12 18:38 | 50 | 041:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE DESENREDO LINEA PRIMARIA | P21081100009 | New_Event | Wire Down | Include | Include | Equipment | 2481 | 2021-08-11 | 124050 | keep | 0 | Aug | 2021 | 0.08449 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
BAYAMON | 2021-08-11 01:18 | 2021-08-13 19:01 | 50 | 065:43 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO CRUCETA Y PARARRAYO | S21081100325 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 3943 | 2021-08-11 | 197150 | keep | 0 | Aug | 2021 | 0.13428 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
MAYAGÃœEZ | 2021-08-11 01:18 | 2021-08-11 01:21 | 411 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | M21081100022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-08-11 | 1233 | keep | 0 | Aug | 2021 | 0.00083979 | 0.00027993 | Momentary | FALSE | FALSE | TMED_Event | 411
MAYAGÃœEZ | 2021-08-11 01:18 | 2021-08-11 01:21 | 721 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | M21081100021 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-08-11 | 2163 | keep | 0 | Aug | 2021 | 0.0014732 | 0.00049107 | Momentary | FALSE | FALSE | TMED_Event | 721
MAYAGÃœEZ | 2021-08-11 01:19 | 2021-08-11 01:20 | 2999 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M21081100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-11 | 2999 | keep | 0 | Aug | 2021 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | TMED_Event | 2999
BARRANQUITAS | 2021-08-11 01:26 | 2021-08-11 10:06 | 1246 | 008:40 | T | DESGANCHE | RETIRO RAMAS SOBRE LINEAS Y CERRO INTERRUPTOR QUE NO CERRABA POR SCADA | C21081100031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 520 | 2021-08-11 | 647920 | keep | 0 | Aug | 2021 | 0.4413 | 0.00084864 | Sustained | FALSE | TRUE | TMED_Event | 1246
HUMACAO | 2021-08-11 01:30 | 2021-08-11 01:31 | 1250 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO INTERRUPTOR | C21081100034 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-08-11 | 1250 | keep | 0 | Aug | 2021 | 0.00085137 | 0 | Momentary | FALSE | FALSE | TMED_Event | 0
HUMACAO | 2021-08-11 01:31 | 2021-08-12 13:47 | 65 | 036:16 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA REMPLAZO DISCOS PARTIDOS | C21081000179 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 2176 | 2021-08-11 | 141440 | keep | 0 | Aug | 2021 | 0.096334 | 4.4271e-05 | Sustained | FALSE | TRUE | TMED_Event | 65
MAYAGÃœEZ | 2021-08-11 01:31 | 2021-08-12 22:25 | 281 | 044:54 | S | LINEA DE TRANSMISION 38KV | EN SERVICIO LINEA 8100. SUBESTACION 6305 EN SERVICIO TOTAL | M21081100024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2694 | 2021-08-11 | 757014 | keep | 0 | Aug | 2021 | 0.5156 | 0.00019139 | Sustained | FALSE | TRUE | TMED_Event | 281
MAYAGÃœEZ | 2021-08-11 01:31 | 2021-08-12 22:25 | 1252 | 044:54 | S | LINEA DE TRANSMISION 38KV | EN SERVICIO LINEA 8100. SUBESTACION 6305 EN SERVICIO TOTAL | M21081100024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2694 | 2021-08-11 | 3372888 | keep | 0 | Aug | 2021 | 2.2973 | 0.00085273 | Sustained | FALSE | TRUE | TMED_Event | 1252
MAYAGÃœEZ | 2021-08-11 01:31 | 2021-08-12 22:16 | 595 | 044:45 | S | LINEA DE TRANSMISION 38KV | ENERGIZADA LINEA 8100. SUBESTACION 7902 EN SERVICIO TOTAL | M21081100025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2685 | 2021-08-11 | 1597575 | keep | 0 | Aug | 2021 | 1.0881 | 0.00040525 | Sustained | FALSE | TRUE | TMED_Event | 595
MAYAGÃœEZ | 2021-08-11 01:31 | 2021-08-12 22:16 | 51 | 044:45 | S | LINEA DE TRANSMISION 38KV | ENERGIZADA LINEA 8100. SUBESTACION 7902 EN SERVICIO TOTAL | M21081100025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2685 | 2021-08-11 | 136935 | keep | 0 | Aug | 2021 | 0.093266 | 3.4736e-05 | Sustained | FALSE | TRUE | TMED_Event | 51
MAYAGÃœEZ | 2021-08-11 01:31 | 2021-08-12 22:16 | 721 | 044:45 | S | LINEA DE TRANSMISION 38KV | ENERGIZADA LINEA 8100. SUBESTACION 7902 EN SERVICIO TOTAL | M21081100025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2685 | 2021-08-11 | 1935885 | keep | 0 | Aug | 2021 | 1.3185 | 0.00049107 | Sustained | FALSE | TRUE | TMED_Event | 721
UTUADO | 2021-08-11 01:31 | 2021-08-11 13:20 | 1382 | 011:49 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | A21081100004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 709 | 2021-08-11 | 979838 | keep | 0 | Aug | 2021 | 0.66736 | 0.00094127 | Sustained | FALSE | TRUE | TMED_Event | 1382
UTUADO | 2021-08-11 01:31 | 2021-08-11 13:20 | 654 | 011:49 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | A21081100004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 709 | 2021-08-11 | 463686 | keep | 0 | Aug | 2021 | 0.31581 | 0.00044544 | Sustained | FALSE | TRUE | TMED_Event | 654
UTUADO | 2021-08-11 01:37 | 2021-08-11 10:20 | 20 | 008:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21081100005 | New_Event | Bad Weather | Include | Include | Weather | 523 | 2021-08-11 | 10460 | keep | 0 | Aug | 2021 | 0.0071243 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
MAYAGÃœEZ | 2021-08-11 01:44 | 2021-08-11 01:45 | 108 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M21081100000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-11 | 108 | keep | 0 | Aug | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | TMED_Event | 108
YAUCO | 2021-08-11 01:45 | 2021-08-11 01:46 | 2484 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P21081100011 | New_Event |  |  | Include | Wildlife | 1 | 2021-08-11 | 2484 | keep | 0 | Aug | 2021 | 0.0016918 | 0.0016918 | Momentary | FALSE | FALSE | TMED_Event | 2484
MAYAGÃœEZ | 2021-08-11 01:45 | 2021-08-11 10:51 | 50 | 009:06 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21081100092 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 546 | 2021-08-11 | 27300 | keep | 0 | Aug | 2021 | 0.018594 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
YAUCO | 2021-08-11 01:46 | 2021-08-11 18:37 | 60 | 016:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | P21081100046 | 1st_after_momentary |  |  | Include | Wildlife | 1011 | 2021-08-11 | 60660 | keep | 0 | Aug | 2021 | 0.041315 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
MAYAGÃœEZ | 2021-08-11 01:54 | 2021-08-11 11:49 | 1666 | 009:55 | T | MAL TIEMPO/RAYOS/WET ASH | SE CERRO INTERRUPTOR MANUAL NO HAY RTU | M21081100029 | New_Event | Bad Weather | Include | Include | Weather | 595 | 2021-08-11 | 991270 | keep | 0 | Aug | 2021 | 0.67515 | 0.0011347 | Sustained | FALSE | FALSE | TMED_Event | 1666
SAN JUAN | 2021-08-11 01:57 | 2021-08-11 01:58 | 686 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S21081100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-11 | 686 | keep | 0 | Aug | 2021 | 0.00046723 | 0.00046723 | Momentary | FALSE | FALSE | TMED_Event | 686
MAYAGÃœEZ | 2021-08-11 01:58 | 2021-08-11 19:00 | 200 | 017:02 | P | ESTRUCTURA AVERIADA | 2 X 65 EN CORTE DE LINEA SE REMPLAZO CRUZETAS PARTIDAS | M21081100030 | New_Event | Defective Pole | Include | Include | Equipment | 1022 | 2021-08-11 | 204400 | keep | 0 | Aug | 2021 | 0.13922 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
MAYAGÃœEZ | 2021-08-11 02:11 | 2021-08-11 12:36 | 2999 | 010:25 | T | DESGANCHE | DISPARO INTERRUPTOR SE RETIRARON BAMBUAS | M21081100034 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 625 | 2021-08-11 | 1874375 | keep | 0 | Aug | 2021 | 1.2766 | 0.0020426 | Sustained | FALSE | FALSE | TMED_Event | 2999
MAYAGÃœEZ | 2021-08-11 02:11 | 2021-08-11 12:36 | 1597 | 010:25 | T | DESGANCHE | INTERRUPTOR AMARRADO CON EL 6406-02 | M21081100034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 625 | 2021-08-11 | 998125 | keep | 0 | Aug | 2021 | 0.67982 | 0.0010877 | Sustained | FALSE | FALSE | TMED_Event | 1597
MAYAGÃœEZ | 2021-08-11 02:21 | 2021-08-11 09:10 | 80 | 006:49 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M21081100037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 409 | 2021-08-11 | 32720 | keep | 0 | Aug | 2021 | 0.022285 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
PONCE | 2021-08-11 02:24 | 2021-08-11 02:25 | 752 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21081100013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-11 | 752 | keep | 0 | Aug | 2021 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | TMED_Event | 752
MAYAGÃœEZ | 2021-08-11 02:32 | 2021-08-11 02:37 | 4381 | 000:05 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR | M21081100041 | New_Event | Bad Weather | Include | Include | Weather | 5 | 2021-08-11 | 21905 | keep | 0 | Aug | 2021 | 0.014919 | 0.0029839 | Momentary | FALSE | FALSE | TMED_Event | 4381
MAYAGÃœEZ | 2021-08-11 02:33 | 2021-08-11 02:34 | 1266 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M21081100042 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-08-11 | 1266 | keep | 0 | Aug | 2021 | 0.00086227 | 0.00086227 | Momentary | FALSE | FALSE | TMED_Event | 1266
MAYAGÃœEZ | 2021-08-11 02:34 | 2021-08-11 18:18 | 50 | 015:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21081100106 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 944 | 2021-08-11 | 47200 | keep | 0 | Aug | 2021 | 0.032148 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
MAYAGÃœEZ | 2021-08-11 02:36 | 2021-08-11 15:26 | 50 | 012:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR FUERTES VIENTOS | M21081100044 | New_Event | Bad Weather | Include | Include | Weather | 770 | 2021-08-11 | 38500 | keep | 0 | Aug | 2021 | 0.026222 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
MAYAGÃœEZ | 2021-08-11 02:37 | 2021-08-11 11:00 | 30 | 008:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21081100045 | New_Event | Bad Weather | Include | Include | Weather | 503 | 2021-08-11 | 15090 | keep | 0 | Aug | 2021 | 0.010278 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
MAYAGÃœEZ | 2021-08-11 02:37 | 2021-08-11 11:58 | 50 | 009:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | M21081100141 | Partial_restoration | Bad Weather | Include | Include | Weather | 561 | 2021-08-11 | 28050 | keep | 0 | Aug | 2021 | 0.019105 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
MAYAGÃœEZ | 2021-08-11 02:44 | 2021-08-11 11:45 | 200 | 009:01 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | M21081100048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 541 | 2021-08-11 | 108200 | keep | 0 | Aug | 2021 | 0.073695 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
BAYAMON | 2021-08-11 02:46 | 2021-08-11 09:24 | 40 | 006:38 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21081100004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 398 | 2021-08-11 | 15920 | keep | 0 | Aug | 2021 | 0.010843 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
PONCE | 2021-08-11 02:48 | 2021-08-11 02:50 | 2163 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR | P21081100015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-11 | 4326 | keep | 0 | Aug | 2021 | 0.0029464 | 0.0014732 | Momentary | FALSE | FALSE | TMED_Event | 2163
MAYAGÃœEZ | 2021-08-11 02:49 | 2021-08-11 09:40 | 80 | 006:51 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | M21081100049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 411 | 2021-08-11 | 32880 | keep | 0 | Aug | 2021 | 0.022394 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
MAYAGÃœEZ | 2021-08-11 03:20 | 2021-08-11 10:05 | 125 | 006:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | M21081100055 | New_Event | Bad Weather | Include | Include | Weather | 405 | 2021-08-11 | 50625 | keep | 0 | Aug | 2021 | 0.03448 | 8.5137e-05 | Sustained | FALSE | TRUE | TMED_Event | 125
PONCE | 2021-08-11 03:41 | 2021-08-11 11:09 | 100 | 007:28 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA DESGANCHE | P21081100016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 448 | 2021-08-11 | 44800 | keep | 0 | Aug | 2021 | 0.030513 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
SAN JUAN | 2021-08-11 04:50 | 2021-08-11 15:27 | 55 | 010:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO | S21081100009 | New_Event | Wire Down | Include | Include | Equipment | 637 | 2021-08-11 | 35035 | keep | 0 | Aug | 2021 | 0.023862 | 3.746e-05 | Sustained | FALSE | FALSE | TMED_Event | 55
CANOVANAS | 2021-08-11 04:58 | 2021-08-11 09:07 | 80 | 004:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | R21081100006 | New_Event | Bad Weather | Include | Include | Weather | 249 | 2021-08-11 | 19920 | keep | 0 | Aug | 2021 | 0.013567 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
SAN JUAN | 2021-08-11 05:11 | 2021-08-11 05:12 | 225 | 000:01 | T | ESTRUCTURA AVERIADA | RECIERRE CARGA POR EL 1908-03 | S21081100000 | New_Event | Defective Pole | Include | Include | Equipment | 1 | 2021-08-11 | 225 | keep | 0 | Aug | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | TMED_Event | 225
SAN JUAN | 2021-08-11 05:11 | 2021-08-11 05:12 | 3957 | 000:01 | T | ESTRUCTURA AVERIADA | RECERRO LLEVANDO 1303-04 | S21081100000 | New_Event | Defective Pole | Include | Include | Equipment | 1 | 2021-08-11 | 3957 | keep | 0 | Aug | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | TMED_Event | 3957
CANOVANAS | 2021-08-11 05:18 | 2021-08-11 08:45 | 100 | 003:27 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA Y 1 X 10 EN BANCO DE TRANSFORMADORES | R21081100007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2021-08-11 | 20700 | keep | 0 | Aug | 2021 | 0.014099 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
PONCE | 2021-08-11 06:01 | 2021-08-11 11:55 | 75 | 005:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEAS CRUZADAS | P21081100027 | New_Event | Wire Down | Include | Include | Equipment | 354 | 2021-08-11 | 26550 | keep | 0 | Aug | 2021 | 0.018083 | 5.1082e-05 | Sustained | FALSE | TRUE | TMED_Event | 75
GUAYAMA | 2021-08-11 06:06 | 2021-08-11 12:40 | 250 | 006:34 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | P21081100030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 394 | 2021-08-11 | 98500 | keep | 0 | Aug | 2021 | 0.067088 | 0.00017027 | Sustained | FALSE | TRUE | TMED_Event | 250
UTUADO | 2021-08-11 06:11 | 2021-08-11 20:09 | 60 | 013:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21081100282 | New_Event | Bad Weather | Include | Include | Weather | 838 | 2021-08-11 | 50280 | keep | 0 | Aug | 2021 | 0.034245 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
BAYAMON | 2021-08-11 06:20 | 2021-08-11 06:23 | 723 | 000:03 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LEVA LA CARGA DEL 1711-05 | B21081100011 | New_Event | Cutout Failure | Include | Include | Equipment | 3 | 2021-08-11 | 2169 | keep | 0 | Aug | 2021 | 0.0014773 | 0.00049243 | Momentary | FALSE | FALSE | TMED_Event | 723
BAYAMON | 2021-08-11 06:20 | 2021-08-11 06:23 | 1976 | 000:03 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE DISPARO EL INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1711-02 | B21081100011 | New_Event | Cutout Failure | Include | Include | Equipment | 3 | 2021-08-11 | 5928 | keep | 0 | Aug | 2021 | 0.0040375 | 0.0013458 | Momentary | FALSE | FALSE | TMED_Event | 1976
UTUADO | 2021-08-11 06:22 | 2021-08-11 16:45 | 40 | 010:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A21081100025 | New_Event | Cutout Failure | Include | Include | Equipment | 623 | 2021-08-11 | 24920 | keep | 0 | Aug | 2021 | 0.016973 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
BAYAMON | 2021-08-11 06:23 | 2021-08-11 17:50 | 1 | 011:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON CAJAS PRIMARIAS EN RISER LLEVA CARGA DEL 1711-05 | B21081100035 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 687 | 2021-08-11 | 687 | keep | 0 | Aug | 2021 | 0.00046791 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2021-08-11 06:23 | 2021-08-11 09:52 | 30 | 003:29 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CARGA ESTA POR EL 1711-02 | B21081000058 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 209 | 2021-08-11 | 6270 | keep | 0 | Aug | 2021 | 0.0042705 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
ARECIBO | 2021-08-11 06:25 | 2021-08-11 09:44 | 75 | 003:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A21081100028 | New_Event | Wire Down | Include | Include | Equipment | 199 | 2021-08-11 | 14925 | keep | 0 | Aug | 2021 | 0.010165 | 5.1082e-05 | Sustained | FALSE | TRUE | TMED_Event | 75
MAYAGÃœEZ | 2021-08-11 06:27 | 2021-08-11 11:00 | 150 | 004:33 | P | DESGANCHE | 1 X 150 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21081100084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 273 | 2021-08-11 | 40950 | keep | 0 | Aug | 2021 | 0.027891 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
SAN JUAN | 2021-08-11 06:33 | 2021-08-11 06:36 | 1615 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S21081100014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-08-11 | 4845 | keep | 0 | Aug | 2021 | 0.0032999 | 0.0011 | Momentary | FALSE | FALSE | TMED_Event | 1615
CAGUAS | 2021-08-11 06:40 | 2021-08-11 11:43 | 160 | 005:03 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA REPARO CONDUCTOR ROTO POR BAMBUAS Y SE REALIZO DESGANCHE | C21081100080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 303 | 2021-08-11 | 48480 | keep | 0 | Aug | 2021 | 0.03302 | 0.00010898 | Sustained | FALSE | TRUE | TMED_Event | 160
UTUADO | 2021-08-11 06:42 | 2021-08-11 13:04 | 100 | 006:22 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21081100032 | New_Event | Bad Weather | Include | Include | Weather | 382 | 2021-08-11 | 38200 | keep | 0 | Aug | 2021 | 0.026018 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
ARECIBO | 2021-08-11 06:45 | 2021-08-11 11:20 | 150 | 004:35 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21081100034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2021-08-11 | 41250 | keep | 0 | Aug | 2021 | 0.028095 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
UTUADO | 2021-08-11 06:49 | 2021-08-11 15:00 | 30 | 008:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A21081100035 | New_Event | Cutout Failure | Include | Include | Equipment | 491 | 2021-08-11 | 14730 | keep | 0 | Aug | 2021 | 0.010033 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
YAUCO | 2021-08-11 06:51 | 2021-08-11 16:00 | 65 | 009:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | P21081100040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 549 | 2021-08-11 | 35685 | keep | 0 | Aug | 2021 | 0.024305 | 4.4271e-05 | Sustained | FALSE | TRUE | TMED_Event | 65
ARECIBO | 2021-08-11 06:52 | 2021-08-11 15:30 | 20 | 008:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21081100036 | New_Event | Wire Down | Include | Include | Equipment | 518 | 2021-08-11 | 10360 | keep | 0 | Aug | 2021 | 0.0070561 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
CAGUAS | 2021-08-11 07:00 | 2021-08-11 14:44 | 80 | 007:44 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | C21081100038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 464 | 2021-08-11 | 37120 | keep | 0 | Aug | 2021 | 0.025282 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
YAUCO | 2021-08-11 07:04 | 2021-08-11 12:28 | 85 | 005:24 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | P21081100047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 324 | 2021-08-11 | 27540 | keep | 0 | Aug | 2021 | 0.018757 | 5.7893e-05 | Sustained | FALSE | TRUE | TMED_Event | 85
UTUADO | 2021-08-11 07:15 | 2021-08-11 12:55 | 80 | 005:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21081100043 | New_Event | Bad Weather | Include | Include | Weather | 340 | 2021-08-11 | 27200 | keep | 0 | Aug | 2021 | 0.018526 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
CAGUAS | 2021-08-11 07:24 | 2021-08-11 18:18 | 80 | 010:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA REMPLAZO CAJA AVERIADA | C21081100100 | New_Event | Cutout Failure | Include | Include | Equipment | 654 | 2021-08-11 | 52320 | keep | 0 | Aug | 2021 | 0.035635 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
MAYAGÃœEZ | 2021-08-11 07:25 | 2021-08-11 18:35 | 20 | 011:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21081100108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 670 | 2021-08-11 | 13400 | keep | 0 | Aug | 2021 | 0.0091267 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
CANOVANAS | 2021-08-11 07:26 | 2021-08-11 13:49 | 6 | 006:23 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE | R21081100023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 383 | 2021-08-11 | 2298 | keep | 0 | Aug | 2021 | 0.0015652 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
MAYAGÃœEZ | 2021-08-11 07:39 | 2021-08-11 09:50 | 45 | 002:11 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M21081100117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2021-08-11 | 5895 | keep | 0 | Aug | 2021 | 0.0040151 | 3.0649e-05 | Sustained | FALSE | TRUE | TMED_Event | 45
BAYAMON | 2021-08-11 07:40 | 2021-08-11 14:44 | 10 | 007:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA | B21081100026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 424 | 2021-08-11 | 4240 | keep | 0 | Aug | 2021 | 0.0028878 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
CAGUAS | 2021-08-11 07:41 | 2021-08-11 07:51 | 1879 | 000:10 | T | NO SE REPORTO CAUSA | DISPARO RR/OFF | C21081100114 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 10 | 2021-08-11 | 18790 | keep | 0 | Aug | 2021 | 0.012798 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
CAGUAS | 2021-08-11 07:49 | 2021-08-11 07:53 | 4390 | 000:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR ROTO EN EL SUELO | C21081100118 | New_Event | Wire Down | Include | Include | Equipment | 4 | 2021-08-11 | 17560 | keep | 0 | Aug | 2021 | 0.01196 | 0.00299 | Momentary | FALSE | FALSE | TMED_Event | 4390
CAGUAS | 2021-08-11 07:51 | 2021-08-11 16:31 | 50 | 008:40 | P | NO SE REPORTO CAUSA | 1 X 50 EN SU - 3 NO CAUSA | C21081000116 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 520 | 2021-08-11 | 26000 | keep | 0 | Aug | 2021 | 0.017708 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
CAGUAS | 2021-08-11 07:53 | 2021-08-11 19:06 | 4000 | 011:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 Y 2 X 50 EN CORTES DE LINEA DESGANCHARON REMPLAZO AISLADORES Y CAJA | C21081100017 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 673 | 2021-08-11 | 2692000 | keep | 0 | Aug | 2021 | 1.8335 | 0.0027244 | Sustained | FALSE | TRUE | TMED_Event | 4000
MAYAGÃœEZ | 2021-08-11 07:53 | 2021-08-11 19:53 | 75 | 012:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR FUERTES VIENTOS | M21081100123 | New_Event | Bad Weather | Include | Include | Weather | 720 | 2021-08-11 | 54000 | keep | 0 | Aug | 2021 | 0.036779 | 5.1082e-05 | Sustained | FALSE | TRUE | TMED_Event | 75
UTUADO | 2021-08-11 07:56 | 2021-08-11 12:35 | 25 | 004:39 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21081100069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 279 | 2021-08-11 | 6975 | keep | 0 | Aug | 2021 | 0.0047506 | 1.7027e-05 | Sustained | FALSE | TRUE | TMED_Event | 25
FAJARDO | 2021-08-11 08:08 | 2021-08-11 09:23 | 15 | 001:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | R21081100025 | New_Event |  |  | Include | Wildlife | 75 | 2021-08-11 | 1125 | keep | 0 | Aug | 2021 | 0.00076623 | 1.0216e-05 | Sustained | FALSE | TRUE | TMED_Event | 15
VEGA BAJA | 2021-08-11 08:09 | 2021-08-11 14:28 | 8 | 006:19 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21081100032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 379 | 2021-08-11 | 3032 | keep | 0 | Aug | 2021 | 0.0020651 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
BAYAMON | 2021-08-11 08:16 | 2021-08-11 19:31 | 200 | 011:15 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA Y 1 X 140 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081100033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 675 | 2021-08-11 | 135000 | keep | 0 | Aug | 2021 | 0.091948 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
MAYAGÃœEZ | 2021-08-11 08:16 | 2021-08-11 22:42 | 40 | 014:26 | P | DESGANCHE | SE REALIZO DESGANCHE MASIVO | M21081100146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 866 | 2021-08-11 | 34640 | keep | 0 | Aug | 2021 | 0.023593 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
BARRANQUITAS | 2021-08-11 08:19 | 2021-08-11 12:18 | 70 | 003:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21081100063 | Partial_restoration | Bad Weather | Include | Include | Weather | 239 | 2021-08-11 | 16730 | keep | 0 | Aug | 2021 | 0.011395 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
CANOVANAS | 2021-08-11 08:20 | 2021-08-11 11:25 | 80 | 003:05 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA REEMPLAZO 2 AISLADORES | R21081100027 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 185 | 2021-08-11 | 14800 | keep | 0 | Aug | 2021 | 0.01008 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
CAGUAS | 2021-08-11 08:22 | 2021-08-11 17:51 | 7 | 009:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21081100140 | New_Event | Secondary Wire Down | Include | Include | Equipment | 569 | 2021-08-11 | 3983 | keep | 0 | Aug | 2021 | 0.0027128 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
UTUADO | 2021-08-11 08:31 | 2021-08-11 11:03 | 40 | 002:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21081100089 | New_Event | Bad Weather | Include | Include | Weather | 152 | 2021-08-11 | 6080 | keep | 0 | Aug | 2021 | 0.0041411 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
MAYAGÃœEZ | 2021-08-11 08:35 | 2021-08-11 16:21 | 100 | 007:46 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZE DESGANCHE | M21081100163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 466 | 2021-08-11 | 46600 | keep | 0 | Aug | 2021 | 0.031739 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
CAGUAS | 2021-08-11 08:36 | 2021-08-11 08:37 | 1590 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21081100152 | New_Event |  |  | Include | Wildlife | 1 | 2021-08-11 | 1590 | keep | 0 | Aug | 2021 | 0.0010829 | 0.0010829 | Momentary | FALSE | FALSE | TMED_Event | 1590
UTUADO | 2021-08-11 08:36 | 2021-08-13 11:15 | 50 | 050:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21081100098 | New_Event | Bad Weather | Include | Include | Weather | 3039 | 2021-08-11 | 151950 | keep | 0 | Aug | 2021 | 0.10349 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
CAGUAS | 2021-08-11 08:37 | 2021-08-11 14:59 | 10 | 006:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN SU - 3 CRUCE POR GATO | C21081100156 | 1st_after_momentary |  |  | Include | Wildlife | 382 | 2021-08-11 | 3820 | keep | 0 | Aug | 2021 | 0.0026018 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
VEGA BAJA | 2021-08-11 08:44 | 2021-08-11 09:54 | 7 | 001:10 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21081100037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 70 | 2021-08-11 | 490 | keep | 0 | Aug | 2021 | 0.00033374 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
BAYAMON | 2021-08-11 08:47 | 2021-08-11 11:28 | 1 | 002:41 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | B21081100038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 161 | 2021-08-11 | 161 | keep | 0 | Aug | 2021 | 0.00010966 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
FAJARDO | 2021-08-11 08:55 | 2021-08-11 11:21 | 40 | 002:26 | P | AISLADOR ROTO, PARTIDO O SAFADO | ABRIO CORTE DE LINEA PARA REEMPLAZAR PIN POLE TOP 2 DISCOS Y RETEZAR LAS LINEAS | R21081100032 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 146 | 2021-08-11 | 5840 | keep | 0 | Aug | 2021 | 0.0039776 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
MAYAGÃœEZ | 2021-08-11 08:57 | 2021-08-11 20:46 | 20 | 011:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR FUERTES VIENTOS | M21081100172 | New_Event | Bad Weather | Include | Include | Weather | 709 | 2021-08-11 | 14180 | keep | 0 | Aug | 2021 | 0.0096579 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
GUAYAMA | 2021-08-11 08:59 | 2021-08-11 16:50 | 50 | 007:51 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | P21081100067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 471 | 2021-08-11 | 23550 | keep | 0 | Aug | 2021 | 0.01604 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
PONCE | 2021-08-11 09:00 | 2021-08-11 14:27 | 50 | 005:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | P21081100050 | New_Event |  |  | Include | Wildlife | 327 | 2021-08-11 | 16350 | keep | 0 | Aug | 2021 | 0.011136 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
BAYAMON | 2021-08-11 09:01 | 2021-08-11 18:53 | 30 | 009:52 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PARTIDO | B21081100040 | New_Event | Defective Pole | Include | Include | Equipment | 592 | 2021-08-11 | 17760 | keep | 0 | Aug | 2021 | 0.012096 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
BAYAMON | 2021-08-11 09:02 | 2021-08-12 12:03 | 25 | 027:01 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21081100057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1621 | 2021-08-11 | 40525 | keep | 0 | Aug | 2021 | 0.027601 | 1.7027e-05 | Sustained | FALSE | TRUE | TMED_Event | 25
CAGUAS | 2021-08-11 09:03 | 2021-08-11 18:45 | 40 | 009:42 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA REMPLAZO AISLADORES | C21081100168 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 582 | 2021-08-11 | 23280 | keep | 0 | Aug | 2021 | 0.015856 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
BAYAMON | 2021-08-11 09:03 | 2021-08-11 14:47 | 150 | 005:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES PARA CERRAR PUENTE ABIERTO | B21081100041 | New_Event | Wire Down | Include | Include | Equipment | 344 | 2021-08-11 | 51600 | keep | 0 | Aug | 2021 | 0.035145 | 0.00010216 | Sustained | FALSE | FALSE | TMED_Event | 150
BAYAMON | 2021-08-11 09:07 | 2021-08-11 16:22 | 35 | 007:15 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081100042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 435 | 2021-08-11 | 15225 | keep | 0 | Aug | 2021 | 0.01037 | 2.3838e-05 | Sustained | FALSE | TRUE | TMED_Event | 35
PONCE | 2021-08-11 09:11 | 2021-08-11 10:04 | 200 | 000:53 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA POR DESGANCHE | P21081100070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 53 | 2021-08-11 | 10600 | keep | 0 | Aug | 2021 | 0.0072196 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
UTUADO | 2021-08-11 09:12 | 2021-08-11 16:44 | 60 | 007:32 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21081100111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 452 | 2021-08-11 | 27120 | keep | 0 | Aug | 2021 | 0.018471 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
BAYAMON | 2021-08-11 09:16 | 2021-08-11 09:54 | 719 | 000:38 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO INTERRUPTOR PARA REEMPLAZO DE CAJA PRIMARIA QUEMADA A PETICION DE BENGIE FEBRES 75% DE LA CARGA POR EL 1011-05 | S21081100043 | Additional_clients | Cutout Failure | Include | Include | Equipment | 38 | 2021-08-11 | 27322 | keep | 0 | Aug | 2021 | 0.018609 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
BAYAMON | 2021-08-11 09:18 | 2021-08-11 10:49 | 20 | 001:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVERIA POR AVE EN EL TENDIDO ELECTRICO PRIMARIO | B21081100044 | New_Event |  |  | Include | Wildlife | 91 | 2021-08-11 | 1820 | keep | 0 | Aug | 2021 | 0.0012396 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
HUMACAO | 2021-08-11 09:23 | 2021-08-11 18:03 | 10 | 008:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21081100181 | New_Event | Bad Weather | Include | Include | Weather | 520 | 2021-08-11 | 5200 | keep | 0 | Aug | 2021 | 0.0035417 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
SAN JUAN | 2021-08-11 09:36 | 2021-08-11 09:37 | 1483 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO UN 30% DE LA CARGA POR EL 1336-08 | S21081100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-11 | 1483 | keep | 0 | Aug | 2021 | 0.0010101 | 0.0010101 | Momentary | FALSE | FALSE | TMED_Event | 1483
SAN JUAN | 2021-08-11 09:36 | 2021-08-11 09:37 | 5290 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA LA CARGA DEL 1336-09 Y UN 30% DEL 1204-04 | S21081100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-11 | 5290 | keep | 0 | Aug | 2021 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | TMED_Event | 5290
SAN JUAN | 2021-08-11 09:36 | 2021-08-11 09:37 | 207 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR EL 1336-08 | S21081100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-11 | 207 | keep | 0 | Aug | 2021 | 0.00014099 | 0.00014099 | Momentary | FALSE | FALSE | TMED_Event | 207
HUMACAO | 2021-08-11 09:37 | 2021-08-11 16:56 | 50 | 007:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21081100196 | New_Event | Vegetation Contact | Include | Include | Vegetation | 439 | 2021-08-11 | 21950 | keep | 0 | Aug | 2021 | 0.01495 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
SAN JUAN | 2021-08-11 09:40 | 2021-08-11 17:46 | 151 | 008:06 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE AVERIADO EN VIA LIBRE DE EMERGENCIA | S21081100051 | New_Event | Defective Pole | Include | Include | Equipment | 486 | 2021-08-11 | 73386 | keep | 0 | Aug | 2021 | 0.049983 | 0.00010285 | Sustained | FALSE | FALSE | TMED_Event | 151
CAGUAS | 2021-08-11 09:50 | 2021-08-11 11:05 | 1 | 001:15 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SECCIONALIZO STRESSCONE AVERIADO EN RISER @ SU-1 Y CERRO N/O EN SU-3 @ SU-2 | C21081100206 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 75 | 2021-08-11 | 75 | keep | 0 | Aug | 2021 | 5.1082e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
UTUADO | 2021-08-11 09:53 | 2021-08-11 21:25 | 20 | 011:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21081100127 | New_Event | Bad Weather | Include | Include | Weather | 692 | 2021-08-11 | 13840 | keep | 0 | Aug | 2021 | 0.0094264 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
UTUADO | 2021-08-11 10:00 | 2021-08-11 10:27 | 12 | 000:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR NEUTRAL SECUNDARIO | A21081100258 | New_Event | Secondary Wire Down | Include | Include | Equipment | 27 | 2021-08-11 | 324 | keep | 0 | Aug | 2021 | 0.00022067 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
BARRANQUITAS | 2021-08-11 10:04 | 2021-08-11 18:48 | 30 | 008:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21081100212 | New_Event | Bad Weather | Include | Include | Weather | 524 | 2021-08-11 | 15720 | keep | 0 | Aug | 2021 | 0.010707 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
BARRANQUITAS | 2021-08-11 10:06 | 2021-08-11 15:00 | 20 | 004:54 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA REMPLAZO BAJANTE | C21081100031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 294 | 2021-08-11 | 5880 | keep | 0 | Aug | 2021 | 0.0040048 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
BARRANQUITAS | 2021-08-11 10:06 | 2021-08-11 13:03 | 95 | 002:57 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR | C21081100031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2021-08-11 | 16815 | keep | 0 | Aug | 2021 | 0.011453 | 6.4704e-05 | Sustained | FALSE | TRUE | TMED_Event | 95
BAYAMON | 2021-08-11 10:13 | 2021-08-11 10:46 | 30 | 000:33 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO CORTE DE LINEA POR SEGURIDAD PARA REEMPLAZO DE MACHETE | S21080900054 | New_Event | Switch Failure | Include | Include | Equipment | 33 | 2021-08-11 | 990 | keep | 0 | Aug | 2021 | 0.00067428 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
SAN JUAN | 2021-08-11 10:15 | 2021-08-12 13:31 | 2 | 027:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | R21081100047 | New_Event | Bad Weather | Include | Include | Weather | 1636 | 2021-08-11 | 3272 | keep | 0 | Aug | 2021 | 0.0022285 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
FAJARDO | 2021-08-11 10:19 | 2021-08-11 16:14 | 40 | 005:55 | P | ESTRUCTURA AVERIADA | 1 X 25 EN CORTE DE LINEA REEMPLAZO POSTE PARTIDO | R21081100048 | New_Event | Defective Pole | Include | Include | Equipment | 355 | 2021-08-11 | 14200 | keep | 0 | Aug | 2021 | 0.0096716 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
CANOVANAS | 2021-08-11 10:25 | 2021-08-11 12:21 | 65 | 001:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | R21081100049 | New_Event | Bad Weather | Include | Include | Weather | 116 | 2021-08-11 | 7540 | keep | 0 | Aug | 2021 | 0.0051355 | 4.4271e-05 | Sustained | FALSE | TRUE | TMED_Event | 65
BAYAMON | 2021-08-11 10:29 | 2021-08-13 09:50 | 25 | 047:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S21081100081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2841 | 2021-08-11 | 71025 | keep | 0 | Aug | 2021 | 0.048375 | 1.7027e-05 | Sustained | FALSE | TRUE | TMED_Event | 25
ARECIBO | 2021-08-11 10:30 | 2021-08-11 14:25 | 15 | 003:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | A21081000050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 235 | 2021-08-11 | 3525 | keep | 0 | Aug | 2021 | 0.0024009 | 1.0216e-05 | Sustained | FALSE | TRUE | TMED_Event | 15
CAGUAS | 2021-08-11 10:36 | 2021-08-11 12:20 | 1500 | 001:44 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO MACHETES PARA SECCIONALIZAR Y REPARAR AISLADOR ROTO | C21081000093 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 104 | 2021-08-11 | 156000 | keep | 0 | Aug | 2021 | 0.10625 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
BAYAMON | 2021-08-11 10:39 | 2021-08-11 10:40 | 1180 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21081100038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-11 | 1180 | keep | 0 | Aug | 2021 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | TMED_Event | 1180
CANOVANAS | 2021-08-11 10:44 | 2021-08-11 12:32 | 20 | 001:48 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | R21081100051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2021-08-11 | 2160 | keep | 0 | Aug | 2021 | 0.0014712 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
BAYAMON | 2021-08-11 10:46 | 2021-08-11 11:37 | 222 | 000:51 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR A PETICION DE EDWARD O'NEILL POR MACHETE INOPERANTE LLEVA 99% DE LA CARGA DEL 1909-09 | S21081100000 | Additional_clients | Switch Failure | Include | Include | Equipment | 51 | 2021-08-11 | 11322 | keep | 0 | Aug | 2021 | 0.0077114 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
BAYAMON | 2021-08-11 10:46 | 2021-08-11 11:37 | 4411 | 000:51 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR A PETICION DE EDWARD O'NEILL POR MACHETE INOPERANTE CARGA ESTA POR EL 1907-03 | S21081100000 | Additional_clients | Switch Failure | Include | Include | Equipment | 51 | 2021-08-11 | 224961 | keep | 0 | Aug | 2021 | 0.15322 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
SAN JUAN | 2021-08-11 10:49 | 2021-08-11 14:47 | 100 | 003:58 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | S21081100094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 238 | 2021-08-11 | 23800 | keep | 0 | Aug | 2021 | 0.01621 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
VEGA BAJA | 2021-08-11 10:50 | 2021-08-11 19:21 | 25 | 008:31 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21081100095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 511 | 2021-08-11 | 12775 | keep | 0 | Aug | 2021 | 0.008701 | 1.7027e-05 | Sustained | FALSE | TRUE | TMED_Event | 25
HUMACAO | 2021-08-11 10:52 | 2021-08-11 10:53 | 3833 | 000:01 | T | ERROR HUMANO | SE ABRIO INTERRUPTOR POR ERROR CONFUNDIO CON EL 2602-01 | C21081100239 | New_Event | Human Error | Include | Include | Other | 1 | 2021-08-11 | 3833 | keep | 0 | Aug | 2021 | 0.0026106 | 0.0026106 | Momentary | FALSE | FALSE | TMED_Event | 3833
HUMACAO | 2021-08-11 10:53 | 2021-08-11 11:41 | 65 | 000:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21081000177 | New_Event | Bad Weather | Include | Include | Weather | 48 | 2021-08-11 | 3120 | keep | 0 | Aug | 2021 | 0.002125 | 4.4271e-05 | Sustained | FALSE | TRUE | TMED_Event | 65
HUMACAO | 2021-08-11 10:54 | 2021-08-11 10:55 | 519 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR ROTO EN EL SUELO | C21081100242 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2021-08-11 | 519 | keep | 0 | Aug | 2021 | 0.00035349 | 0 | Momentary | FALSE | FALSE | TMED_Event | 0
CAGUAS | 2021-08-11 10:54 | 2021-08-11 10:55 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21081100241 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-11 | 1702 | keep | 0 | Aug | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | TMED_Event | 1702
HUMACAO | 2021-08-11 10:55 | 2021-08-11 18:41 | 300 | 007:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO MACHETES PARA LEVANTAR CONDUCTORES | C21081000183 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 466 | 2021-08-11 | 139800 | keep | 0 | Aug | 2021 | 0.095217 | 0.00020433 | Sustained | FALSE | FALSE | TMED_Event | 300
PONCE | 2021-08-11 10:56 | 2021-08-12 13:01 | 50 | 026:05 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | P21081100096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1565 | 2021-08-11 | 78250 | keep | 0 | Aug | 2021 | 0.053296 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
MAYAGÃœEZ | 2021-08-11 10:56 | 2021-08-11 14:40 | 80 | 003:44 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21081100252 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2021-08-11 | 17920 | keep | 0 | Aug | 2021 | 0.012205 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
MAYAGÃœEZ | 2021-08-11 10:56 | 2021-08-11 19:25 | 60 | 008:29 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA POR FUERTES VIENTOS | M21081100252 | New_Event | Bad Weather | Include | Include | Weather | 509 | 2021-08-11 | 30540 | keep | 0 | Aug | 2021 | 0.020801 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
ARECIBO | 2021-08-11 10:57 | 2021-08-11 14:09 | 10 | 003:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR SE REMPLAZO CAJA TRANSFORMADOR AVERIADA | A21081100163 | New_Event | Cutout Failure | Include | Include | Equipment | 192 | 2021-08-11 | 1920 | keep | 0 | Aug | 2021 | 0.0013077 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
HUMACAO | 2021-08-11 11:02 | 2021-08-11 16:05 | 80 | 005:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C21081100245 | New_Event | Bad Weather | Include | Include | Weather | 303 | 2021-08-11 | 24240 | keep | 0 | Aug | 2021 | 0.01651 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
BAYAMON | 2021-08-11 11:06 | 2021-08-11 19:01 | 50 | 007:55 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21081100112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 475 | 2021-08-11 | 23750 | keep | 0 | Aug | 2021 | 0.016176 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
UTUADO | 2021-08-11 11:09 | 2021-08-11 19:22 | 50 | 008:13 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21081100169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 493 | 2021-08-11 | 24650 | keep | 0 | Aug | 2021 | 0.016789 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
HUMACAO | 2021-08-11 11:24 | 2021-08-11 17:25 | 10 | 006:01 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C21081100251 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 361 | 2021-08-11 | 3610 | keep | 0 | Aug | 2021 | 0.0024588 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
BAYAMON | 2021-08-11 11:37 | 2021-08-11 15:10 | 30 | 003:33 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO CORTE DE LINEA POR SEGURIDAD PARA REEMPLAZO DE MACHETE | S21080900054 | Partial_restoration | Switch Failure | Include | Include | Equipment | 213 | 2021-08-11 | 6390 | keep | 0 | Aug | 2021 | 0.0043522 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
BAYAMON | 2021-08-11 11:37 | 2021-08-11 15:10 | 360 | 003:33 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE Y SE CERRO PUENTE ABIERTO CARGA POR 1907-03 | S21080900054 | Partial_restoration | Switch Failure | Include | Include | Equipment | 213 | 2021-08-11 | 76680 | keep | 0 | Aug | 2021 | 0.052226 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
BAYAMON | 2021-08-11 11:42 | 2021-08-11 15:42 | 30 | 004:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B21081000043 | New_Event | Cutout Failure | Include | Include | Equipment | 240 | 2021-08-11 | 7200 | keep | 0 | Aug | 2021 | 0.0049039 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
AGUADILLA | 2021-08-11 12:00 | 2021-08-11 18:30 | 99 | 006:30 | T | ESTRUCTURA AVERIADA | SE ABRIO INTERRUPTOR MANUAL ELECTRICO PARA REINSTALAR POSTE AUTORIZADO POR ING LUIS FENEQUE NO ESTABA PROFUNDO | M21081100311 | New_Event | Defective Pole | Include | Include | Equipment | 390 | 2021-08-11 | 38610 | keep | 0 | Aug | 2021 | 0.026297 | 6.7428e-05 | Sustained | FALSE | FALSE | TMED_Event | 99
ARECIBO | 2021-08-11 12:02 | 2021-08-11 16:40 | 20 | 004:38 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21081100188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 278 | 2021-08-11 | 5560 | keep | 0 | Aug | 2021 | 0.0037869 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
MAYAGÃœEZ | 2021-08-11 12:04 | 2021-08-11 17:06 | 50 | 005:02 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21081100282 | New_Event | Vegetation Contact | Include | Include | Vegetation | 302 | 2021-08-11 | 15100 | keep | 0 | Aug | 2021 | 0.010285 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
HUMACAO | 2021-08-11 12:30 | 2021-08-11 14:14 | 40 | 001:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN CORTE DE LINEA RETEZO LINEA | C21081100285 | New_Event | Wire Down | Include | Include | Equipment | 104 | 2021-08-11 | 4160 | keep | 0 | Aug | 2021 | 0.0028334 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
BARRANQUITAS | 2021-08-11 12:35 | 2021-08-11 17:29 | 85 | 004:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | C21081100286 | New_Event | Bad Weather | Include | Include | Weather | 294 | 2021-08-11 | 24990 | keep | 0 | Aug | 2021 | 0.017021 | 5.7893e-05 | Sustained | FALSE | TRUE | TMED_Event | 85
CANOVANAS | 2021-08-11 12:37 | 2021-08-11 16:00 | 50 | 003:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA REPARO CONDUCTOR | R21081100059 | New_Event | Wire Down | Include | Include | Equipment | 203 | 2021-08-11 | 10150 | keep | 0 | Aug | 2021 | 0.0069131 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
GUAYAMA | 2021-08-11 12:52 | 2021-08-11 12:53 | 4279 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | P21081100119 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-08-11 | 4279 | keep | 0 | Aug | 2021 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | TMED_Event | 4279
GUAYAMA | 2021-08-11 12:53 | 2021-08-11 17:30 | 100 | 004:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON TRES CAJAS PRIMARIAS AVERIADAS | P21081100123 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 277 | 2021-08-11 | 27700 | keep | 0 | Aug | 2021 | 0.018866 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
BARRANQUITAS | 2021-08-11 12:53 | 2021-08-11 19:08 | 140 | 006:15 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C21081100290 | New_Event | Vegetation Contact | Include | Include | Vegetation | 375 | 2021-08-11 | 52500 | keep | 0 | Aug | 2021 | 0.035758 | 9.5353e-05 | Sustained | FALSE | TRUE | TMED_Event | 140
SAN JUAN | 2021-08-11 12:58 | 2021-08-12 19:26 | 53 | 030:28 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERRADO AVERIADO | S21081100044 | New_Event | UG Cable Fault | Include | Include | Equipment | 1828 | 2021-08-11 | 96884 | keep | 0 | Aug | 2021 | 0.065987 | 3.6098e-05 | Sustained | FALSE | FALSE | TMED_Event | 53
BARRANQUITAS | 2021-08-11 12:59 | 2021-08-11 17:12 | 8 | 004:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE CAJA A TRANSFORMADOR | C21081100291 | New_Event | Wire Down | Include | Include | Equipment | 253 | 2021-08-11 | 2024 | keep | 0 | Aug | 2021 | 0.0013785 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
AGUADILLA | 2021-08-11 13:00 | 2021-08-11 17:55 | 300 | 004:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 200 EN CORTE DE LINEA SE RETEZO LINEAS | M21081100303 | New_Event | Wire Down | Include | Include | Equipment | 295 | 2021-08-11 | 88500 | keep | 0 | Aug | 2021 | 0.060277 | 0.00020433 | Sustained | FALSE | TRUE | TMED_Event | 300
CAGUAS | 2021-08-11 13:02 | 2021-08-11 16:48 | 8 | 003:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 3 EN TRANSFORMADOR REPARO SECUNDARIA | C21081100293 | New_Event | Secondary Wire Down | Include | Include | Equipment | 226 | 2021-08-11 | 1808 | keep | 0 | Aug | 2021 | 0.0012314 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
VEGA BAJA | 2021-08-11 13:04 | 2021-08-11 14:03 | 12 | 000:59 | P | NO SE REPORTO CAUSA | 2 X 25 EN TRANSFORMADOR | B21081100069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 59 | 2021-08-11 | 708 | keep | 0 | Aug | 2021 | 0.00048222 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
CAGUAS | 2021-08-11 13:08 | 2021-08-11 19:05 | 5 | 005:57 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHO | C21081100294 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 357 | 2021-08-11 | 1785 | keep | 0 | Aug | 2021 | 0.0012158 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
PONCE | 2021-08-11 13:51 | 2021-08-11 17:31 | 40 | 003:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | P21081100138 | New_Event |  |  | Include | Wildlife | 220 | 2021-08-11 | 8800 | keep | 0 | Aug | 2021 | 0.0059936 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
ARECIBO | 2021-08-11 13:55 | 2021-08-11 14:10 | 9 | 000:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | A21081000118 | New_Event | Secondary Wire Down | Include | Include | Equipment | 15 | 2021-08-11 | 135 | keep | 0 | Aug | 2021 | 9.1948e-05 | 6.1299e-06 | Sustained | FALSE | FALSE | TMED_Event | 9
YAUCO | 2021-08-11 13:59 | 2021-08-11 18:07 | 50 | 004:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | P21081100134 | New_Event |  |  | Include | Wildlife | 248 | 2021-08-11 | 12400 | keep | 0 | Aug | 2021 | 0.0084456 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
HUMACAO | 2021-08-11 14:05 | 2021-08-11 15:31 | 4 | 001:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | ABRIO TRANSFORMADOR PARA LEVANTAR SECUNDARIA AVERIADA POR CAMION | C21081100311 | New_Event |  |  | Include | Wildlife | 86 | 2021-08-11 | 344 | keep | 0 | Aug | 2021 | 0.0002343 | 2.7244e-06 | Sustained | FALSE | FALSE | TMED_Event | 4
FAJARDO | 2021-08-11 14:08 | 2021-08-11 15:08 | 100 | 001:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | R21081100064 | New_Event |  |  | Include | Wildlife | 60 | 2021-08-11 | 6000 | keep | 0 | Aug | 2021 | 0.0040866 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
ARECIBO | 2021-08-11 14:12 | 2021-08-11 16:45 | 50 | 002:33 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21081100238 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2021-08-11 | 7650 | keep | 0 | Aug | 2021 | 0.0052104 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
SAN JUAN | 2021-08-11 14:20 | 2021-08-11 14:49 | 1 | 000:29 | P | NO SE REPORTO CAUSA | 1 X 15 RBA EN EL SU - 5 | R21081100094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 29 | 2021-08-11 | 29 | keep | 0 | Aug | 2021 | 1.9752e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
CAGUAS | 2021-08-11 14:31 | 2021-08-11 16:49 | 6 | 002:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21081100316 | New_Event | Secondary Wire Down | Include | Include | Equipment | 138 | 2021-08-11 | 828 | keep | 0 | Aug | 2021 | 0.00056395 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
UTUADO | 2021-08-11 14:31 | 2021-08-11 15:15 | 70 | 000:44 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21081100244 | New_Event | Vegetation Contact | Include | Include | Vegetation | 44 | 2021-08-11 | 3080 | keep | 0 | Aug | 2021 | 0.0020978 | 4.7677e-05 | Sustained | FALSE | TRUE | TMED_Event | 70
ARECIBO | 2021-08-11 14:31 | 2021-08-11 15:15 | 60 | 000:44 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21081100020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 44 | 2021-08-11 | 2640 | keep | 0 | Aug | 2021 | 0.0017981 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
CANOVANAS | 2021-08-11 14:34 | 2021-08-11 15:44 | 2106 | 001:10 | T | PARARRAYOS DEFECTUOSO | SE ELIMINO PARARRAYO AVERIADO EN TRANSFORMADOR VACANTE | R21081100000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 70 | 2021-08-11 | 147420 | keep | 0 | Aug | 2021 | 0.10041 | 0.0014344 | Sustained | FALSE | FALSE | TMED_Event | 2106
UTUADO | 2021-08-11 14:40 | 2021-08-11 17:00 | 50 | 002:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21081100246 | New_Event | Bad Weather | Include | Include | Weather | 140 | 2021-08-11 | 7000 | keep | 0 | Aug | 2021 | 0.0047677 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
UTUADO | 2021-08-11 14:51 | 2021-08-11 18:30 | 75 | 003:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21081100250 | New_Event | Bad Weather | Include | Include | Weather | 219 | 2021-08-11 | 16425 | keep | 0 | Aug | 2021 | 0.011187 | 5.1082e-05 | Sustained | FALSE | TRUE | TMED_Event | 75
CAGUAS | 2021-08-11 14:55 | 2021-08-12 12:42 | 40 | 021:47 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21081100318 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1307 | 2021-08-11 | 52280 | keep | 0 | Aug | 2021 | 0.035608 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
SAN JUAN | 2021-08-11 14:56 | 2021-08-11 20:01 | 100 | 005:05 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21081100078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 305 | 2021-08-11 | 30500 | keep | 0 | Aug | 2021 | 0.020773 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
UTUADO | 2021-08-11 14:59 | 2021-08-11 20:40 | 300 | 005:41 | P | DESGANCHE | 2 X 100 EN CONVERTIDOR SE RETIRO RAMAS SOBRE LAS LINEAS | A21081100254 | New_Event | Vegetation Contact | Include | Include | Vegetation | 341 | 2021-08-11 | 102300 | keep | 0 | Aug | 2021 | 0.069676 | 0.00020433 | Sustained | FALSE | TRUE | TMED_Event | 300
HUMACAO | 2021-08-11 15:11 | 2021-08-11 15:15 | 2126 | 000:04 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO SE VERIFICO PERSONAL FUERA | C21081100323 | New_Event | Cutout Failure | Include | Include | Equipment | 4 | 2021-08-11 | 8504 | keep | 0 | Aug | 2021 | 0.005792 | 0.001448 | Momentary | FALSE | FALSE | TMED_Event | 2126
UTUADO | 2021-08-11 15:11 | 2021-08-11 17:55 | 2 | 002:44 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | A21081100275 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 164 | 2021-08-11 | 328 | keep | 0 | Aug | 2021 | 0.0002234 | 1.3622e-06 | Sustained | FALSE | TRUE | TMED_Event | 2
HUMACAO | 2021-08-11 15:15 | 2021-08-11 18:58 | 300 | 003:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN ENTRADA DE CONVERTIDOR REMPLAZO CAJA QUEMADA | C21081100346 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 223 | 2021-08-11 | 66900 | keep | 0 | Aug | 2021 | 0.045565 | 0.00020433 | Sustained | FALSE | FALSE | TMED_Event | 300
CANOVANAS | 2021-08-11 15:31 | 2021-08-11 19:47 | 50 | 004:16 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE Y FIJO BAJANTE DE LINEA A CAJA | R21081100082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 256 | 2021-08-11 | 12800 | keep | 0 | Aug | 2021 | 0.008718 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
PONCE | 2021-08-11 15:37 | 2021-08-12 13:48 | 15 | 022:11 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR POR DESGANCHE | P21081100274 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1331 | 2021-08-11 | 19965 | keep | 0 | Aug | 2021 | 0.013598 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
ARECIBO | 2021-08-11 15:43 | 2021-08-11 18:00 | 30 | 002:17 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21081100279 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2021-08-11 | 4110 | keep | 0 | Aug | 2021 | 0.0027993 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
BAYAMON | 2021-08-11 15:47 | 2021-08-12 11:30 | 10 | 019:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | B21081100083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1183 | 2021-08-11 | 11830 | keep | 0 | Aug | 2021 | 0.0080574 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
CAGUAS | 2021-08-11 15:56 | 2021-08-12 11:33 | 6 | 019:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO Y LINEA SECUNDARIA | C21081100341 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1177 | 2021-08-11 | 7062 | keep | 0 | Aug | 2021 | 0.0048099 | 4.0866e-06 | Sustained | FALSE | TRUE | TMED_Event | 6
FAJARDO | 2021-08-11 16:01 | 2021-08-11 17:04 | 40 | 001:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | R21081100085 | New_Event | Bad Weather | Include | Include | Weather | 63 | 2021-08-11 | 2520 | keep | 0 | Aug | 2021 | 0.0017164 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
MAYAGÃœEZ | 2021-08-11 16:08 | 2021-08-12 19:09 | 40 | 027:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M21081100365 | New_Event | Wire Down | Include | Include | Equipment | 1621 | 2021-08-11 | 64840 | keep | 0 | Aug | 2021 | 0.044162 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
SAN JUAN | 2021-08-11 16:11 | 2021-08-12 01:31 | 2 | 009:20 | T | ESTRUCTURA AVERIADA | SE ABRIO ALIMENTADOR PARA TRABAJOS DE REEMPLAZO DE POSTE PARTIDO EN EL 13KV 1908-03 | S21081100229 | New_Event | Defective Pole | Include | Include | Equipment | 560 | 2021-08-11 | 1120 | keep | 0 | Aug | 2021 | 0.00076283 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
GUAYAMA | 2021-08-11 16:16 | 2021-08-11 17:50 | 60 | 001:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | P21081100158 | New_Event | Bad Weather | Include | Include | Weather | 94 | 2021-08-11 | 5640 | keep | 0 | Aug | 2021 | 0.0038414 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
ARECIBO | 2021-08-11 16:25 | 2021-08-11 18:45 | 30 | 002:20 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21081100289 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2021-08-11 | 4200 | keep | 0 | Aug | 2021 | 0.0028606 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
PONCE | 2021-08-11 16:30 | 2021-08-11 16:31 | 50 | 000:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | P21081100081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-11 | 50 | keep | 0 | Aug | 2021 | 3.4055e-05 | 3.4055e-05 | Momentary | FALSE | TRUE | TMED_Event | 50
BAYAMON | 2021-08-11 16:32 | 2021-08-11 18:00 | 6 | 001:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21081100006 | New_Event | Secondary Wire Down | Include | Include | Equipment | 88 | 2021-08-11 | 528 | keep | 0 | Aug | 2021 | 0.00035962 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
MAYAGÃœEZ | 2021-08-11 16:34 | 2021-08-11 22:37 | 20 | 006:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN CORTE DE LINEA SE REPARARON TRAMOS DE LINEA PRIMARIA Y SECUNDARIA | M21081100213 | New_Event | Wire Down | Include | Include | Equipment | 363 | 2021-08-11 | 7260 | keep | 0 | Aug | 2021 | 0.0049448 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
VEGA BAJA | 2021-08-11 16:40 | 2021-08-11 17:56 | 4 | 001:16 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21081100091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 76 | 2021-08-11 | 304 | keep | 0 | Aug | 2021 | 0.00020705 | 2.7244e-06 | Sustained | FALSE | FALSE | TMED_Event | 4
UTUADO | 2021-08-11 16:44 | 2021-08-12 12:15 | 120 | 019:31 | P | DESGANCHE | 2 X 65 SE REALISO DESGANCHE | A21081100295 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1171 | 2021-08-11 | 140520 | keep | 0 | Aug | 2021 | 0.095708 | 8.1731e-05 | Sustained | FALSE | FALSE | TMED_Event | 120
UTUADO | 2021-08-11 16:44 | 2021-08-12 14:50 | 60 | 022:06 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A21081100294 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1326 | 2021-08-11 | 79560 | keep | 0 | Aug | 2021 | 0.054188 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
PONCE | 2021-08-11 16:59 | 2021-08-11 17:00 | 50 | 000:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21081100072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-11 | 50 | keep | 0 | Aug | 2021 | 3.4055e-05 | 3.4055e-05 | Momentary | FALSE | TRUE | TMED_Event | 50
BAYAMON | 2021-08-11 17:13 | 2021-08-12 10:49 | 70 | 017:36 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | B21081100094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1056 | 2021-08-11 | 73920 | keep | 0 | Aug | 2021 | 0.050347 | 4.7677e-05 | Sustained | FALSE | TRUE | TMED_Event | 70
UTUADO | 2021-08-11 17:17 | 2021-08-11 19:25 | 225 | 002:08 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 200 EN CONVERTIDOR MAL TIEMPO DESCARGAS ELECTRICAS | A21081100310 | New_Event | Bad Weather | Include | Include | Weather | 128 | 2021-08-11 | 28800 | keep | 0 | Aug | 2021 | 0.019616 | 0.00015325 | Sustained | FALSE | FALSE | TMED_Event | 225
CAGUAS | 2021-08-11 17:32 | 2021-08-14 16:18 | 3 | 070:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA LEVANTAR SECUNDARIA | C21081100358 | New_Event | Secondary Wire Down | Include | Include | Equipment | 4246 | 2021-08-11 | 12738 | keep | 0 | Aug | 2021 | 0.0086758 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
PONCE | 2021-08-11 17:33 | 2021-08-11 17:34 | 65 | 000:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | P21081100020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-11 | 65 | keep | 0 | Aug | 2021 | 4.4271e-05 | 4.4271e-05 | Momentary | FALSE | TRUE | TMED_Event | 65
SAN JUAN | 2021-08-11 17:34 | 2021-08-12 09:38 | 125 | 016:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA PERSONA ACCIDENTALMENTE LANZO PALO DE GOLF Y CRUZO LA FASE | S21081100305 | New_Event |  |  | Include | Wildlife | 964 | 2021-08-11 | 120500 | keep | 0 | Aug | 2021 | 0.082072 | 8.5137e-05 | Sustained | FALSE | TRUE | TMED_Event | 125
ARECIBO | 2021-08-11 17:35 | 2021-08-11 17:50 | 5 | 000:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | A21081100175 | New_Event | Secondary Wire Down | Include | Include | Equipment | 15 | 2021-08-11 | 75 | keep | 0 | Aug | 2021 | 5.1082e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
CAGUAS | 2021-08-11 17:36 | 2021-08-11 18:52 | 5 | 001:16 | P | SECUNDARIA/DESGANCHE | ABRIO TRANSFORMADOR PARA DESGANCHAR Y REPARAR SECUNDARIA | C21081100357 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 76 | 2021-08-11 | 380 | keep | 0 | Aug | 2021 | 0.00025882 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
SAN JUAN | 2021-08-11 17:40 | 2021-08-12 01:13 | 3165 | 007:33 | P | ESTRUCTURA AVERIADA | SE ABRIO MACHETES PARA REEMPLAZO DE POSTE PARTIDO CARR#1 CERCA PANADERIA FRANCAISE | S21081100171 | New_Event | Defective Pole | Include | Include | Equipment | 453 | 2021-08-11 | 1433745 | keep | 0 | Aug | 2021 | 0.97652 | 0.0021557 | Sustained | FALSE | FALSE | TMED_Event | 3165
MAYAGÃœEZ | 2021-08-11 17:40 | 2021-08-11 19:00 | 15 | 001:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO FUERTES VIENTOS | M21081100375 | New_Event | Bad Weather | Include | Include | Weather | 80 | 2021-08-11 | 1200 | keep | 0 | Aug | 2021 | 0.00081731 | 1.0216e-05 | Sustained | FALSE | TRUE | TMED_Event | 15
BAYAMON | 2021-08-11 18:02 | 2021-08-11 20:26 | 6 | 002:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21081100061 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 144 | 2021-08-11 | 864 | keep | 0 | Aug | 2021 | 0.00058847 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
VEGA BAJA | 2021-08-11 18:12 | 2021-08-11 18:56 | 6 | 000:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO NEUTRAL | B21081100100 | New_Event | Secondary Wire Down | Include | Include | Equipment | 44 | 2021-08-11 | 264 | keep | 0 | Aug | 2021 | 0.00017981 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
FAJARDO | 2021-08-11 18:23 | 2021-08-12 11:02 | 62 | 016:39 | P | HERRAJE ROTO O PODRIDO | 1 X 50 EN CORTE DE LINEA Y 1 X 40 EN RISER SE REEMPLAZO CRUCETA PARTIDA 3 DISCOS Y SE CERRO PUENTE | R21081100096 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 999 | 2021-08-11 | 61938 | keep | 0 | Aug | 2021 | 0.042186 | 4.2228e-05 | Sustained | FALSE | TRUE | TMED_Event | 62
CAGUAS | 2021-08-11 18:29 | 2021-08-12 21:32 | 200 | 027:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 Y 1 X 80 EN CORTES DE LINEA LEVANTO CONDUCTOR | C21081100365 | New_Event | Wire Down | Include | Include | Equipment | 1623 | 2021-08-11 | 324600 | keep | 0 | Aug | 2021 | 0.22108 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
MAYAGÃœEZ | 2021-08-11 18:30 | 2021-08-11 19:50 | 12 | 001:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR FUERTES VIENTOS | M21081100382 | New_Event | Bad Weather | Include | Include | Weather | 80 | 2021-08-11 | 960 | keep | 0 | Aug | 2021 | 0.00065385 | 8.1731e-06 | Sustained | FALSE | TRUE | TMED_Event | 12
MAYAGÃœEZ | 2021-08-11 18:31 | 2021-08-12 12:27 | 50 | 017:56 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 25 EN CORTE DE LINEA MAL TIEMPO | M21081100383 | New_Event | Bad Weather | Include | Include | Weather | 1076 | 2021-08-11 | 53800 | keep | 0 | Aug | 2021 | 0.036643 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
MAYAGÃœEZ | 2021-08-11 18:44 | 2021-08-11 20:29 | 100 | 001:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR FUERTES VIENTOS | M21081100385 | New_Event | Bad Weather | Include | Include | Weather | 105 | 2021-08-11 | 10500 | keep | 0 | Aug | 2021 | 0.0071515 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
BAYAMON | 2021-08-11 19:06 | 2021-08-11 19:07 | 1715 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1708-03 Y SE CERRO POR SCADA CARGA TRANSFERIDA AL 1708-03 | B21081100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-11 | 1715 | keep | 0 | Aug | 2021 | 0.0011681 | 0.0011681 | Momentary | FALSE | FALSE | TMED_Event | 1715
BAYAMON | 2021-08-11 19:06 | 2021-08-11 19:07 | 1498 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1708-03 Y SE CERRO POR SCADA LLEVA 1708-02 | B21081100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-11 | 1498 | keep | 0 | Aug | 2021 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | TMED_Event | 1498
BAYAMON | 2021-08-11 19:06 | 2021-08-12 15:13 | 12 | 020:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21081100103 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1207 | 2021-08-11 | 14484 | keep | 0 | Aug | 2021 | 0.009865 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
ARECIBO | 2021-08-11 19:17 | 2021-08-11 19:55 | 100 | 000:38 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21081100348 | New_Event | Vegetation Contact | Include | Include | Vegetation | 38 | 2021-08-11 | 3800 | keep | 0 | Aug | 2021 | 0.0025882 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
BARRANQUITAS | 2021-08-11 19:28 | 2021-08-12 12:16 | 30 | 016:48 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21081100373 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1008 | 2021-08-11 | 30240 | keep | 0 | Aug | 2021 | 0.020596 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
MAYAGÃœEZ | 2021-08-11 19:34 | 2021-08-12 13:15 | 60 | 017:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE DESGANCHO Y SE REPARO LINEA PRIMARIA | M21081100389 | New_Event | Wire Down | Include | Include | Equipment | 1061 | 2021-08-11 | 63660 | keep | 0 | Aug | 2021 | 0.043359 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
CAGUAS | 2021-08-11 19:38 | 2021-08-11 19:40 | 1001 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C21081100374 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-11 | 2002 | keep | 0 | Aug | 2021 | 0.0013636 | 0.00068178 | Momentary | FALSE | FALSE | TMED_Event | 1001
CAGUAS | 2021-08-11 19:44 | 2021-08-12 11:41 | 40 | 015:57 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21081100375 | New_Event | Vegetation Contact | Include | Include | Vegetation | 957 | 2021-08-11 | 38280 | keep | 0 | Aug | 2021 | 0.026072 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
MAYAGÃœEZ | 2021-08-11 20:16 | 2021-08-12 16:29 | 40 | 020:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA | M21081100392 | New_Event | Wire Down | Include | Include | Equipment | 1213 | 2021-08-11 | 48520 | keep | 0 | Aug | 2021 | 0.033047 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
CAGUAS | 2021-08-11 20:21 | 2021-08-12 14:02 | 7 | 017:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR SECUNDARIA | C21081100379 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1061 | 2021-08-11 | 7427 | keep | 0 | Aug | 2021 | 0.0050585 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
MAYAGÃœEZ | 2021-08-11 20:56 | 2021-08-12 11:45 | 15 | 014:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | M21081100396 | New_Event | Bad Weather | Include | Include | Weather | 889 | 2021-08-11 | 13335 | keep | 0 | Aug | 2021 | 0.0090824 | 1.0216e-05 | Sustained | FALSE | TRUE | TMED_Event | 15
BAYAMON | 2021-08-11 20:57 | 2021-08-11 20:58 | 1715 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1708-03 Y SE CERRO POR SCADA CARGA TRANSFERIDA AL 1708-03 | B21081100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-11 | 1715 | keep | 0 | Aug | 2021 | 0.0011681 | 0.0011681 | Momentary | FALSE | FALSE | TMED_Event | 1715
BAYAMON | 2021-08-11 20:57 | 2021-08-11 20:58 | 1498 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1708-03 Y SE CERRO POR SCADA LLEVA 1708-02 | B21081100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-11 | 1498 | keep | 0 | Aug | 2021 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | TMED_Event | 1498
BAYAMON | 2021-08-11 21:41 | 2021-08-11 21:42 | 723 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA LLEVA 1711-05 | B21081100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-11 | 723 | keep | 0 | Aug | 2021 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | TMED_Event | 723
BAYAMON | 2021-08-11 21:41 | 2021-08-11 21:42 | 1976 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1711-02 Y SE CERRO POR SCADA LLEVA CARGA DEL 1711-05 | B21081100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-11 | 1976 | keep | 0 | Aug | 2021 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | TMED_Event | 1976
AGUADILLA | 2021-08-11 21:45 | 2021-08-12 10:35 | 200 | 012:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 200 EN CORTE DE LINEA POR LINEAS CRUZADAS | M21081100406 | New_Event | Wire Down | Include | Include | Equipment | 770 | 2021-08-11 | 154000 | keep | 0 | Aug | 2021 | 0.10489 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
CAGUAS | 2021-08-11 22:13 | 2021-08-12 09:32 | 60 | 011:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | C21081100388 | New_Event | Bad Weather | Include | Include | Weather | 679 | 2021-08-11 | 40740 | keep | 0 | Aug | 2021 | 0.027748 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
MAYAGÃœEZ | 2021-08-11 22:30 | 2021-08-12 11:40 | 25 | 013:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | M21081100416 | New_Event | Bad Weather | Include | Include | Weather | 790 | 2021-08-11 | 19750 | keep | 0 | Aug | 2021 | 0.013452 | 1.7027e-05 | Sustained | FALSE | TRUE | TMED_Event | 25
PONCE | 2021-08-11 22:57 | 2021-08-11 22:58 | 449 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210811000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-11 | 449 | keep | 0 | Aug | 2021 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | TMED_Event | 449
PONCE | 2021-08-11 23:12 | 2021-08-11 23:13 | 752 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210811000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-11 | 752 | keep | 0 | Aug | 2021 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | TMED_Event | 752
PONCE | 2021-08-11 23:12 | 2021-08-11 23:13 | 2696 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR 5011-04 | P210811000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-11 | 2696 | keep | 0 | Aug | 2021 | 0.0018362 | 0.0018362 | Momentary | FALSE | FALSE | TMED_Event | 2696
CAGUAS | 2021-08-11 23:20 | 2021-08-11 23:21 | 870 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO SE CERRO POR CONTROL | C21081100391 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-11 | 870 | keep | 0 | Aug | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | TMED_Event | 870
ARECIBO | 2021-08-11 23:35 | 2021-08-12 14:20 | 40 | 014:45 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A21081100390 | New_Event | Vegetation Contact | Include | Include | Vegetation | 885 | 2021-08-11 | 35400 | keep | 0 | Aug | 2021 | 0.024111 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
ARECIBO | 2021-08-11 23:57 | 2021-08-11 23:59 | 425 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | A21081100393 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-11 | 850 | keep | 0 | Aug | 2021 | 0.00057893 | 0.00028947 | Momentary | FALSE | FALSE | TMED_Event | 425
BAYAMON | 2021-08-12 00:16 | 2021-08-12 09:54 | 30 | 009:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA QUEMADA | B21081200001 | New_Event | Cutout Failure | Include | Include | Equipment | 578 | 2021-08-12 | 17340 | keep | 0 | Aug | 2021 | 0.01181 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-08-12 00:49 | 2021-08-12 20:59 | 60 | 020:10 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO DOS POSTES PARTIDOS | B21081200003 | New_Event | Defective Pole | Include | Include | Equipment | 1210 | 2021-08-12 | 72600 | keep | 0 | Aug | 2021 | 0.049448 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-08-12 01:12 | 2021-08-12 05:15 | 30 | 004:03 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA EN TRONCAL SE RETIRO ARBOL DE ENCIMA DE LINEAS Y SE SECCIONALIZO AVERIA DE POSTES PARTIDOS | B21081200005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2021-08-12 | 7290 | keep | 0 | Aug | 2021 | 0.0049652 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-08-12 01:22 | 2021-08-12 11:40 | 78 | 010:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | R21081200004 | New_Event |  |  | Include | Wildlife | 618 | 2021-08-12 | 48204 | keep | 0 | Aug | 2021 | 0.032832 | 5.3125e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 78
MAYAGÃœEZ | 2021-08-12 01:30 | 2021-08-14 12:40 | 60 | 059:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE | M21081200001 | New_Event | Wire Down | Include | Include | Equipment | 3550 | 2021-08-12 | 213000 | keep | 0 | Aug | 2021 | 0.14507 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2021-08-12 02:39 | 2021-08-12 10:15 | 70 | 007:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | R21081200004 | New_Event |  |  | Include | Wildlife | 456 | 2021-08-12 | 31920 | keep | 0 | Aug | 2021 | 0.021741 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
SAN JUAN | 2021-08-12 03:23 | 2021-08-12 03:24 | 386 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21081200005 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 386 | keep | 0 | Aug | 2021 | 0.0002629 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-08-12 03:24 | 2021-08-12 18:38 | 100 | 015:14 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S21081000092 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 914 | 2021-08-12 | 91400 | keep | 0 | Aug | 2021 | 0.062252 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
YAUCO | 2021-08-12 03:48 | 2021-08-12 03:49 | 1475 | 000:01 | T | RELEVO DE CARGA AUTOMATICO | RECIERRE | P210812000XX | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 1 | 2021-08-12 | 1475 | keep | 0 | Aug | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
YAUCO | 2021-08-12 03:49 | 2021-08-12 10:21 | 80 | 006:32 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA POR AVE | P21081200002 | New_Event |  |  | Include | Wildlife | 392 | 2021-08-12 | 31360 | keep | 0 | Aug | 2021 | 0.021359 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-12 05:02 | 2021-08-12 13:30 | 12 | 008:28 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR CARGA TRANSFERIDA AL 1903-05 | B21081200009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 508 | 2021-08-12 | 6096 | keep | 0 | Aug | 2021 | 0.004152 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-08-12 05:30 | 2021-08-12 05:31 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210813000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 3744 | keep | 0 | Aug | 2021 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2021-08-12 05:30 | 2021-08-12 05:31 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 5004-06 | P210813000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 3114 | keep | 0 | Aug | 2021 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
GUAYAMA | 2021-08-12 05:54 | 2021-08-12 10:35 | 5 | 004:41 | P | DESGANCHE | 1 X 5 EN TRANSFORMADOR POR DESGANCHE | P21081200003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 281 | 2021-08-12 | 1405 | keep | 0 | Aug | 2021 | 0.00095694 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-08-12 05:58 | 2021-08-12 10:35 | 20 | 004:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR FUERTES VIENTOS | M21081100012 | New_Event | Bad Weather | Include | Include | Weather | 277 | 2021-08-12 | 5540 | keep | 0 | Aug | 2021 | 0.0037733 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BARRANQUITAS | 2021-08-12 06:00 | 2021-08-12 12:39 | 10 | 006:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR REMPLAZO PORTA FUSIBLE QUEMADO | C21081200008 | New_Event | Cutout Failure | Include | Include | Equipment | 399 | 2021-08-12 | 3990 | keep | 0 | Aug | 2021 | 0.0027176 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-08-12 06:24 | 2021-08-12 16:55 | 200 | 010:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 40 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A21081200020 | New_Event | Wire Down | Include | Include | Equipment | 631 | 2021-08-12 | 126200 | keep | 0 | Aug | 2021 | 0.085954 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
HUMACAO | 2021-08-12 06:33 | 2021-08-12 11:45 | 8 | 005:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21081200004 | New_Event | Secondary Wire Down | Include | Include | Equipment | 312 | 2021-08-12 | 2496 | keep | 0 | Aug | 2021 | 0.0017 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-08-12 07:01 | 2021-08-12 16:34 | 60 | 009:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 Y 1 X 50 EN CORTES DE LINEA CRUCE POR AVE | C21081200006 | New_Event |  |  | Include | Wildlife | 573 | 2021-08-12 | 34380 | keep | 0 | Aug | 2021 | 0.023416 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BARRANQUITAS | 2021-08-12 07:03 | 2021-08-12 15:59 | 40 | 008:56 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA REMPLAZO JUEGO DE DISCOS | C21081200007 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 536 | 2021-08-12 | 21440 | keep | 0 | Aug | 2021 | 0.014603 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-08-12 07:23 | 2021-08-12 18:35 | 40 | 011:12 | P | DESGANCHE | 1 X 25 EN TRANSFORMALDOR SE RETIRO ENREDADERA | A21081200013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 672 | 2021-08-12 | 26880 | keep | 0 | Aug | 2021 | 0.018308 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2021-08-12 07:34 | 2021-08-12 10:27 | 7 | 002:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P21081200006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2021-08-12 | 1211 | keep | 0 | Aug | 2021 | 0.00082481 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
SAN JUAN | 2021-08-12 07:35 | 2021-08-12 12:36 | 7 | 005:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN RISER Y 1 X 65 EN CORTE DE LINEA CRUCE POR PALOMA | R21081200006 | New_Event |  |  | Include | Wildlife | 301 | 2021-08-12 | 2107 | keep | 0 | Aug | 2021 | 0.0014351 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
ARECIBO | 2021-08-12 07:55 | 2021-08-12 09:58 | 1 | 002:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO PARTIDO | A21081200017 | New_Event | Wire Down | Include | Include | Equipment | 123 | 2021-08-12 | 123 | keep | 0 | Aug | 2021 | 8.3775e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-08-12 07:56 | 2021-08-12 16:01 | 1 | 008:05 | P | NO SE REPORTO CAUSA | 3 X 65 EN CORTE DE LINEA | B21081200013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 485 | 2021-08-12 | 485 | keep | 0 | Aug | 2021 | 0.00033033 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-08-12 08:00 | 2021-08-12 09:31 | 1 | 001:31 | P | NO SE REPORTO CAUSA | 12 X 30 EN RISER NO SE DETECTO LA CAUSA | A21081200018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 91 | 2021-08-12 | 91 | keep | 0 | Aug | 2021 | 6.198e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-08-12 08:11 | 2021-08-12 17:33 | 150 | 009:22 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M21081200053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 562 | 2021-08-12 | 84300 | keep | 0 | Aug | 2021 | 0.057416 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-08-12 08:17 | 2021-08-12 09:51 | 30 | 001:34 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21081200021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2021-08-12 | 2820 | keep | 0 | Aug | 2021 | 0.0019207 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-08-12 08:22 | 2021-08-12 16:34 | 10 | 008:12 | P | NO SE REPORTO CAUSA | 1 X 40 EN TRANSCLOSURE | P21081200010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 492 | 2021-08-12 | 4920 | keep | 0 | Aug | 2021 | 0.003351 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-08-12 08:24 | 2021-08-12 12:33 | 45 | 004:09 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21081200026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 249 | 2021-08-12 | 11205 | keep | 0 | Aug | 2021 | 0.0076317 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
SAN JUAN | 2021-08-12 08:25 | 2021-08-12 19:22 | 15 | 010:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21081200017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 657 | 2021-08-12 | 9855 | keep | 0 | Aug | 2021 | 0.0067122 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2021-08-12 08:49 | 2021-08-12 10:41 | 40 | 001:52 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZE DESGANCHE | A21081100025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2021-08-12 | 4480 | keep | 0 | Aug | 2021 | 0.0030513 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-08-12 08:50 | 2021-08-12 09:52 | 60 | 001:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA | A21081200026 | New_Event | Wire Down | Include | Include | Equipment | 62 | 2021-08-12 | 3720 | keep | 0 | Aug | 2021 | 0.0025337 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
YAUCO | 2021-08-12 08:54 | 2021-08-12 16:13 | 125 | 007:19 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN DISTINTOS CORTES DE LINEA POR DESGANCHE | P21081200016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 439 | 2021-08-12 | 54875 | keep | 0 | Aug | 2021 | 0.037375 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
HUMACAO | 2021-08-12 08:57 | 2021-08-12 21:36 | 60 | 012:39 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA CONTRATISTA DESGANCHAR | C21081100016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 759 | 2021-08-12 | 45540 | keep | 0 | Aug | 2021 | 0.031017 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-08-12 09:16 | 2021-08-12 11:38 | 20 | 002:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | M21081200029 | New_Event | Bad Weather | Include | Include | Weather | 142 | 2021-08-12 | 2840 | keep | 0 | Aug | 2021 | 0.0019343 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
YAUCO | 2021-08-12 09:18 | 2021-08-12 18:37 | 50 | 009:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | P21081200024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 559 | 2021-08-12 | 27950 | keep | 0 | Aug | 2021 | 0.019037 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-12 09:20 | 2021-08-12 17:06 | 1 | 007:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | B21081200026 | New_Event | Cutout Failure | Include | Include | Equipment | 466 | 2021-08-12 | 466 | keep | 0 | Aug | 2021 | 0.00031739 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-08-12 09:21 | 2021-08-12 09:22 | 1420 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR 1530-06 | S21081200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 1420 | keep | 0 | Aug | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
MAYAGÃœEZ | 2021-08-12 09:29 | 2021-08-12 13:40 | 45 | 004:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR FUERTES VIENTOS | M21081200030 | New_Event | Bad Weather | Include | Include | Weather | 251 | 2021-08-12 | 11295 | keep | 0 | Aug | 2021 | 0.007693 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
MAYAGÃœEZ | 2021-08-12 09:35 | 2021-08-12 18:38 | 6 | 009:03 | P | DESGANCHE | 1 X 8 EN TRANSFORMADOR SE REALIZO DESGANCHE | M21081200031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 543 | 2021-08-12 | 3258 | keep | 0 | Aug | 2021 | 0.002219 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2021-08-12 09:36 | 2021-08-12 18:25 | 100 | 008:49 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M21081200032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 529 | 2021-08-12 | 52900 | keep | 0 | Aug | 2021 | 0.03603 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-08-12 09:38 | 2021-08-12 15:08 | 75 | 005:30 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081200030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 330 | 2021-08-12 | 24750 | keep | 0 | Aug | 2021 | 0.016857 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-08-12 09:44 | 2021-08-13 14:09 | 30 | 028:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA | B21081200025 | New_Event | Cutout Failure | Include | Include | Equipment | 1705 | 2021-08-12 | 51150 | keep | 0 | Aug | 2021 | 0.034838 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
VEGA BAJA | 2021-08-12 09:45 | 2021-08-12 17:02 | 12 | 007:17 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZO POSTE SECUNDARIO | B21081200032 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 437 | 2021-08-12 | 5244 | keep | 0 | Aug | 2021 | 0.0035717 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2021-08-12 10:02 | 2021-08-12 15:15 | 75 | 005:13 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M21081200040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 313 | 2021-08-12 | 23475 | keep | 0 | Aug | 2021 | 0.015989 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
CANOVANAS | 2021-08-12 10:16 | 2021-08-12 14:18 | 35 | 004:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | R21081200021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2021-08-12 | 8470 | keep | 0 | Aug | 2021 | 0.0057689 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
GUAYAMA | 2021-08-12 10:30 | 2021-08-12 20:20 | 200 | 009:50 | P | ESTRUCTURA AVERIADA | SE ABRE CORTE DE LINEA DE EMERGENCIA PARA REEMPLAZAR POSTE PRIMARIO PARTIDO | P21081200014 | New_Event | Defective Pole | Include | Include | Equipment | 590 | 2021-08-12 | 118000 | keep | 0 | Aug | 2021 | 0.080369 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-08-12 10:32 | 2021-08-12 17:05 | 10 | 006:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | A21081200044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 393 | 2021-08-12 | 3930 | keep | 0 | Aug | 2021 | 0.0026767 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-08-12 10:46 | 2021-08-12 18:41 | 50 | 007:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21081200036 | New_Event | Bad Weather | Include | Include | Weather | 475 | 2021-08-12 | 23750 | keep | 0 | Aug | 2021 | 0.016176 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-12 10:55 | 2021-08-12 13:40 | 100 | 002:45 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | M21081200052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2021-08-12 | 16500 | keep | 0 | Aug | 2021 | 0.011238 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BARRANQUITAS | 2021-08-12 11:13 | 2021-08-12 16:51 | 50 | 005:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21081200044 | New_Event | Bad Weather | Include | Include | Weather | 338 | 2021-08-12 | 16900 | keep | 0 | Aug | 2021 | 0.011511 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-08-12 11:37 | 2021-08-12 14:51 | 100 | 003:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | C21081200049 | New_Event |  |  | Include | Wildlife | 194 | 2021-08-12 | 19400 | keep | 0 | Aug | 2021 | 0.013213 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-08-12 11:44 | 2021-08-12 11:48 | 870 | 000:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | A SOLICITUD DEL SUPERVISOR JOSE COLON SE ABRIO EL INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR VIVO EN EL SUELO | C21081200050 | New_Event | Wire Down | Include | Include | Equipment | 4 | 2021-08-12 | 3480 | keep | 0 | Aug | 2021 | 0.0023702 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CAGUAS | 2021-08-12 11:46 | 2021-08-12 11:48 | 1001 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C21081200051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-12 | 2002 | keep | 0 | Aug | 2021 | 0.0013636 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
CAGUAS | 2021-08-12 11:48 | 2021-08-12 17:00 | 300 | 005:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y SE CERRARON MACHETES | C21081200011 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 312 | 2021-08-12 | 93600 | keep | 0 | Aug | 2021 | 0.063751 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
PONCE | 2021-08-12 11:55 | 2021-08-12 17:42 | 80 | 005:47 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA. NO SE REPORTO CAUSA. | P21081200043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 347 | 2021-08-12 | 27760 | keep | 0 | Aug | 2021 | 0.018907 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BARRANQUITAS | 2021-08-12 12:16 | 2021-08-14 17:26 | 1 | 053:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA LEVANTO CONDUCTOR | C21081000170 | New_Event | Wire Down | Include | Include | Equipment | 3190 | 2021-08-12 | 3190 | keep | 0 | Aug | 2021 | 0.0021727 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-08-12 12:27 | 2021-08-12 18:07 | 7 | 005:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21081100277 | New_Event | Secondary Wire Down | Include | Include | Equipment | 340 | 2021-08-12 | 2380 | keep | 0 | Aug | 2021 | 0.001621 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-08-12 12:55 | 2021-08-13 11:17 | 20 | 022:22 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081200054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1342 | 2021-08-12 | 26840 | keep | 0 | Aug | 2021 | 0.018281 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-08-12 12:59 | 2021-08-12 15:48 | 10 | 002:49 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21081200072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2021-08-12 | 1690 | keep | 0 | Aug | 2021 | 0.0011511 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
SAN JUAN | 2021-08-12 13:14 | 2021-08-14 15:15 | 1 | 050:01 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | R21081200026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3001 | 2021-08-12 | 3001 | keep | 0 | Aug | 2021 | 0.002044 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-08-12 13:17 | 2021-08-12 17:00 | 7 | 003:43 | P | SECUNDARIA/DESGANCHE | ABRIO TRANSFORMADOR PARA DESGANCHAR Y REPARAR SECUNDARIA | C21081200063 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 223 | 2021-08-12 | 1561 | keep | 0 | Aug | 2021 | 0.0010632 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-08-12 13:19 | 2021-08-12 18:40 | 843 | 005:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ABIERTO EN EL TRONCAL DEL 6008-05 QUE ESTA LLEVANDO LA CARGA DEL 6008-04 | M21081200075 | New_Event | Wire Down | Include | Include | Equipment | 321 | 2021-08-12 | 270603 | keep | 0 | Aug | 2021 | 0.18431 | 0.00057416 | Sustained | FALSE | FALSE | Not_TMED_Event | 843
MAYAGÃœEZ | 2021-08-12 13:19 | 2021-08-12 18:40 | 66 | 005:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE PRIMARIO ABIERTO EN EL TRONCAL DEL ALIMENTADOR | M21081200075 | New_Event | Wire Down | Include | Include | Equipment | 321 | 2021-08-12 | 21186 | keep | 0 | Aug | 2021 | 0.01443 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
UTUADO | 2021-08-12 13:45 | 2021-08-12 17:24 | 8 | 003:39 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | A21081200065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2021-08-12 | 1752 | keep | 0 | Aug | 2021 | 0.0011933 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2021-08-12 13:50 | 2021-08-12 13:51 | 64 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21081200062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 64 | keep | 0 | Aug | 2021 | 4.359e-05 | 4.359e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 64
HUMACAO | 2021-08-12 13:58 | 2021-08-12 21:37 | 6 | 007:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR BASE DE CONTADOR DE CANCHA CRUZADA | C21081200068 | New_Event | Secondary Wire Down | Include | Include | Equipment | 459 | 2021-08-12 | 2754 | keep | 0 | Aug | 2021 | 0.0018757 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-08-12 14:04 | 2021-08-12 16:30 | 18 | 002:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA AVERIADA | P21081200065 | New_Event | Secondary Wire Down | Include | Include | Equipment | 146 | 2021-08-12 | 2628 | keep | 0 | Aug | 2021 | 0.0017899 | 1.226e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 18
BAYAMON | 2021-08-12 14:10 | 2021-08-12 14:11 | 437 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA EL 1526-02 | S21081200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 437 | keep | 0 | Aug | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
UTUADO | 2021-08-12 14:26 | 2021-08-12 16:00 | 80 | 001:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA | A21081200075 | New_Event | Cutout Failure | Include | Include | Equipment | 94 | 2021-08-12 | 7520 | keep | 0 | Aug | 2021 | 0.0051218 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2021-08-12 14:27 | 2021-08-12 16:25 | 160 | 001:58 | P | DESGANCHE | 1 X 80 EN CORTE DE LINES SE RETIRO RAMA | A21081200076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2021-08-12 | 18880 | keep | 0 | Aug | 2021 | 0.012859 | 0.00010898 | Sustained | FALSE | TRUE | Not_TMED_Event | 160
BAYAMON | 2021-08-12 14:28 | 2021-08-12 14:29 | 6136 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21081200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 6136 | keep | 0 | Aug | 2021 | 0.0041792 | 0.0041792 | Momentary | FALSE | FALSE | Not_TMED_Event | 6136
CANOVANAS | 2021-08-12 14:39 | 2021-08-12 15:50 | 18 | 001:11 | P | OTRAS CAUSAS | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA REPARAR PEDESTAL Y SE DEJO SECCIONALIZADO CLIENTE CON PROA | R21081200009 | New_Event | Other Causes | Include | Include | Other | 71 | 2021-08-12 | 1278 | keep | 0 | Aug | 2021 | 0.00087044 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
PONCE | 2021-08-12 14:40 | 2021-08-14 16:41 | 5 | 050:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN RISER IGUANA CRUZA FASE | P21081200071 | New_Event |  |  | Include | Wildlife | 3001 | 2021-08-12 | 15005 | keep | 0 | Aug | 2021 | 0.01022 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-08-12 14:41 | 2021-08-12 14:43 | 1001 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | C21081200078 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-12 | 2002 | keep | 0 | Aug | 2021 | 0.0013636 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
CAGUAS | 2021-08-12 14:52 | 2021-08-12 17:58 | 40 | 003:06 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHO Y REMPLAZO DISCO | C21081200079 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 186 | 2021-08-12 | 7440 | keep | 0 | Aug | 2021 | 0.0050674 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-08-12 14:53 | 2021-08-12 18:28 | 30 | 003:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO EN CORTE DE LINEA | A21081200080 | New_Event | Wire Down | Include | Include | Equipment | 215 | 2021-08-12 | 6450 | keep | 0 | Aug | 2021 | 0.0043931 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BARRANQUITAS | 2021-08-12 14:58 | 2021-08-14 11:23 | 10 | 044:25 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR QUERMADO DE 37.5 KVA X 37.5 KVA | C21081200081 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2665 | 2021-08-12 | 26650 | keep | 0 | Aug | 2021 | 0.018151 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-12 15:00 | 2021-08-12 18:50 | 60 | 003:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO NEUTRAL PARTIDO | A21081200106 | New_Event | Wire Down | Include | Include | Equipment | 230 | 2021-08-12 | 13800 | keep | 0 | Aug | 2021 | 0.0093991 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-08-12 15:00 | 2021-08-12 17:00 | 6 | 002:00 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | A21081200082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2021-08-12 | 720 | keep | 0 | Aug | 2021 | 0.00049039 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-08-12 15:01 | 2021-08-12 16:05 | 125 | 001:04 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | A21081200084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2021-08-12 | 8000 | keep | 0 | Aug | 2021 | 0.0054488 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
MAYAGÃœEZ | 2021-08-12 15:02 | 2021-08-12 16:12 | 1 | 001:10 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21081200105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2021-08-12 | 70 | keep | 0 | Aug | 2021 | 4.7677e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-08-12 15:12 | 2021-08-12 20:56 | 80 | 005:44 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M21081200108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 344 | 2021-08-12 | 27520 | keep | 0 | Aug | 2021 | 0.018744 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-08-12 15:14 | 2021-08-12 20:53 | 80 | 005:39 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M21081200109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 339 | 2021-08-12 | 27120 | keep | 0 | Aug | 2021 | 0.018471 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-08-12 15:17 | 2021-08-12 15:19 | 3458 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON EL RECIERRE EN OFF SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR | M21081200111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-12 | 6916 | keep | 0 | Aug | 2021 | 0.0047105 | 0.0023552 | Momentary | FALSE | TRUE | Not_TMED_Event | 3458
MAYAGÃœEZ | 2021-08-12 15:27 | 2021-08-12 21:30 | 30 | 006:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081200116 | New_Event | Bad Weather | Include | Include | Weather | 363 | 2021-08-12 | 10890 | keep | 0 | Aug | 2021 | 0.0074171 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-08-12 15:27 | 2021-08-12 18:47 | 100 | 003:20 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081200116 | New_Event | Bad Weather | Include | Include | Weather | 200 | 2021-08-12 | 20000 | keep | 0 | Aug | 2021 | 0.013622 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-08-12 15:37 | 2021-08-12 19:55 | 45 | 004:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE LEVANTO NEUTRAL PRIMARIO Y SE REEMPLAZO CAJA PRIMARIA | R21081200030 | New_Event | Cutout Failure | Include | Include | Equipment | 258 | 2021-08-12 | 11610 | keep | 0 | Aug | 2021 | 0.0079075 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
MAYAGÃœEZ | 2021-08-12 15:37 | 2021-08-14 15:50 | 5 | 048:13 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR AVERIADO DE 25KVA X 25 KVA | M21081200120 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2893 | 2021-08-12 | 14465 | keep | 0 | Aug | 2021 | 0.009852 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-08-12 15:43 | 2021-08-13 10:16 | 10 | 018:33 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21081200068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1113 | 2021-08-12 | 11130 | keep | 0 | Aug | 2021 | 0.0075806 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-12 15:45 | 2021-08-12 16:50 | 12 | 001:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO EN TRANSFORMADOR | A21081200048 | New_Event | Wire Down | Include | Include | Equipment | 65 | 2021-08-12 | 780 | keep | 0 | Aug | 2021 | 0.00053125 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-08-12 15:51 | 2021-08-12 16:45 | 11 | 000:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | R21081200014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 54 | 2021-08-12 | 594 | keep | 0 | Aug | 2021 | 0.00040457 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2021-08-12 15:56 | 2021-08-13 15:00 | 200 | 023:04 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO RAMA | M21081200126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1384 | 2021-08-12 | 276800 | keep | 0 | Aug | 2021 | 0.18853 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
VEGA BAJA | 2021-08-12 16:12 | 2021-08-13 11:15 | 50 | 019:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B21081200070 | New_Event | Cutout Failure | Include | Include | Equipment | 1143 | 2021-08-12 | 57150 | keep | 0 | Aug | 2021 | 0.038925 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-12 16:16 | 2021-08-12 19:35 | 180 | 003:19 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | A21081200097 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 199 | 2021-08-12 | 35820 | keep | 0 | Aug | 2021 | 0.024397 | 0.0001226 | Sustained | FALSE | TRUE | Not_TMED_Event | 180
FAJARDO | 2021-08-12 16:18 | 2021-08-12 18:58 | 9 | 002:40 | P | SECUNDARIA/ESTRUCTURA AVERIADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO BARRA EN PEDESTAL | R21081200035 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 160 | 2021-08-12 | 1440 | keep | 0 | Aug | 2021 | 0.00098078 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2021-08-12 16:23 | 2021-08-12 22:28 | 50 | 006:05 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | M21081200133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 365 | 2021-08-12 | 18250 | keep | 0 | Aug | 2021 | 0.01243 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-12 16:33 | 2021-08-12 17:32 | 15 | 000:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21081100325 | New_Event | Secondary Wire Down | Include | Include | Equipment | 59 | 2021-08-12 | 885 | keep | 0 | Aug | 2021 | 0.00060277 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-08-12 16:35 | 2021-08-12 18:52 | 613 | 002:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R21081200037 | New_Event |  |  | Include | Wildlife | 137 | 2021-08-12 | 83981 | keep | 0 | Aug | 2021 | 0.057199 | 0.00041751 | Sustained | FALSE | TRUE | Not_TMED_Event | 613
VEGA BAJA | 2021-08-12 16:36 | 2021-08-12 18:42 | 80 | 002:06 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081200071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2021-08-12 | 10080 | keep | 0 | Aug | 2021 | 0.0068654 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
YAUCO | 2021-08-12 16:55 | 2021-08-13 18:23 | 50 | 025:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | P21081200092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1528 | 2021-08-12 | 76400 | keep | 0 | Aug | 2021 | 0.052036 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-12 17:07 | 2021-08-12 17:08 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21081200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 393 | keep | 0 | Aug | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2021-08-12 17:07 | 2021-08-12 17:08 | 4 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6007-04 QUE LLEVA LA CARGA DEL 6007-05 | M21081200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 4 | keep | 0 | Aug | 2021 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2021-08-12 17:12 | 2021-08-12 17:32 | 3 | 000:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR Y SE REEMPLAZO CONECTORES EN SECUNDARIA | R21081200031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 20 | 2021-08-12 | 60 | keep | 0 | Aug | 2021 | 4.0866e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-08-12 17:24 | 2021-08-12 17:25 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21081200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 393 | keep | 0 | Aug | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2021-08-12 17:24 | 2021-08-12 17:25 | 4 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6007-04 QUE LLEVA LA CARGA DEL 6007-05 | M21081200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 4 | keep | 0 | Aug | 2021 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-08-12 17:30 | 2021-08-12 20:44 | 20 | 003:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21081200070 | New_Event | Secondary Wire Down | Include | Include | Equipment | 194 | 2021-08-12 | 3880 | keep | 0 | Aug | 2021 | 0.0026427 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-08-12 17:33 | 2021-08-12 17:34 | 1715 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL CARGA POR 1708-03 | B21081200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 1715 | keep | 0 | Aug | 2021 | 0.0011681 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2021-08-12 17:33 | 2021-08-12 17:34 | 1498 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA CARGA DEL 1708-02 | B21081200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 1498 | keep | 0 | Aug | 2021 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
SAN JUAN | 2021-08-12 17:48 | 2021-08-12 20:52 | 20 | 003:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REEMPLAZO 25 PIES DE SECUNDARIA Y REPARARON TOMAS | R21081100087 | New_Event | Secondary Wire Down | Include | Include | Equipment | 184 | 2021-08-12 | 3680 | keep | 0 | Aug | 2021 | 0.0025064 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-08-12 17:55 | 2021-08-12 19:50 | 4 | 001:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO TRANSFORMADOR Y REEMPLAZARON PEDESTAL IMPACTADO POR DIGGER | R21081200043 | New_Event |  |  | Include | Wildlife | 115 | 2021-08-12 | 460 | keep | 0 | Aug | 2021 | 0.0003133 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-08-12 17:58 | 2021-08-12 19:08 | 10 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21081100105 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2021-08-12 | 700 | keep | 0 | Aug | 2021 | 0.00047677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-08-12 18:07 | 2021-08-12 18:08 | 1250 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21081200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 1250 | keep | 0 | Aug | 2021 | 0.00085137 | 0.00085137 | Momentary | FALSE | FALSE | Not_TMED_Event | 1250
ARECIBO | 2021-08-12 18:16 | 2021-08-13 13:56 | 25 | 019:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA POR DECARGAS ELECTRICAS | A21081200109 | New_Event | Bad Weather | Include | Include | Weather | 1180 | 2021-08-12 | 29500 | keep | 0 | Aug | 2021 | 0.020092 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CAGUAS | 2021-08-12 18:18 | 2021-08-14 13:22 | 9 | 043:04 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21081200103 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2584 | 2021-08-12 | 23256 | keep | 0 | Aug | 2021 | 0.01584 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2021-08-12 18:19 | 2021-08-12 18:20 | 4035 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P210812000XX | New_Event |  |  | Include | Wildlife | 1 | 2021-08-12 | 4035 | keep | 0 | Aug | 2021 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
PONCE | 2021-08-12 18:20 | 2021-08-12 23:26 | 99 | 005:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE. | P21081200104 | 1st_after_momentary |  |  | Include | Wildlife | 306 | 2021-08-12 | 30294 | keep | 0 | Aug | 2021 | 0.020633 | 6.7428e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 99
BARRANQUITAS | 2021-08-12 18:34 | 2021-08-13 18:20 | 55 | 023:46 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE DESGANCHO | C21081200105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1426 | 2021-08-12 | 78430 | keep | 0 | Aug | 2021 | 0.053418 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
MAYAGÃœEZ | 2021-08-12 18:40 | 2021-08-12 20:05 | 2525 | 001:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES EN EL TRONCAL DEL ALIMENTADOR 6008-05 PARA REPARAR PUENTE PRIMARIO ABIERTO QUE ESTA LLEVANDO LA CARGA DEL 6008-04 | M21081200075 | Additional_clients | Wire Down | Include | Include | Equipment | 85 | 2021-08-12 | 214625 | keep | 0 | Aug | 2021 | 0.14618 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-12 18:40 | 2021-08-12 20:05 | 195 | 001:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES EN EL TRONCAL DEL ALIMENTADOR PARA REPARAR PUENTE PRIMARIO ABIERTO | M21081200075 | Additional_clients | Wire Down | Include | Include | Equipment | 85 | 2021-08-12 | 16575 | keep | 0 | Aug | 2021 | 0.011289 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-08-12 18:52 | 2021-08-12 18:53 | 4634 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21081200106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 4634 | keep | 0 | Aug | 2021 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
CAGUAS | 2021-08-12 18:59 | 2021-08-12 19:00 | 473 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21081200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 473 | keep | 0 | Aug | 2021 | 0.00032216 | 0.00032216 | Momentary | FALSE | FALSE | Not_TMED_Event | 473
CAGUAS | 2021-08-12 19:01 | 2021-08-13 15:00 | 142 | 019:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C21081200108 | New_Event |  |  | Include | Wildlife | 1199 | 2021-08-12 | 170258 | keep | 0 | Aug | 2021 | 0.11596 | 9.6716e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 142
SAN JUAN | 2021-08-12 19:03 | 2021-08-13 10:17 | 8 | 015:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | R21081200052 | New_Event | Secondary Wire Down | Include | Include | Equipment | 914 | 2021-08-12 | 7312 | keep | 0 | Aug | 2021 | 0.0049802 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-08-12 19:06 | 2021-08-12 19:07 | 1715 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL CARGA POR 1708-03 | B21081200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 1715 | keep | 0 | Aug | 2021 | 0.0011681 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2021-08-12 19:06 | 2021-08-12 19:07 | 1498 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA CARGA DEL 1708-02 | B21081200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 1498 | keep | 0 | Aug | 2021 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
PONCE | 2021-08-12 19:09 | 2021-08-13 10:35 | 150 | 015:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE CORTE DE LINEA | P21081200107 | New_Event | Wire Down | Include | Include | Equipment | 926 | 2021-08-12 | 138900 | keep | 0 | Aug | 2021 | 0.094604 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CANOVANAS | 2021-08-12 19:16 | 2021-08-13 10:20 | 100 | 015:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA REEMPLAZO CAJA QUEMADA | R21081200053 | New_Event | Cutout Failure | Include | Include | Equipment | 904 | 2021-08-12 | 90400 | keep | 0 | Aug | 2021 | 0.061571 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-08-12 19:25 | 2021-08-13 10:36 | 12 | 015:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO CONECTORES EN SALIDA DE TRANSFORMADOR | B21081200078 | New_Event | Secondary Wire Down | Include | Include | Equipment | 911 | 2021-08-12 | 10932 | keep | 0 | Aug | 2021 | 0.0074457 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-08-12 19:52 | 2021-08-12 19:53 | 1715 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL CARGA POR 1708-03 | B21081200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 1715 | keep | 0 | Aug | 2021 | 0.0011681 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2021-08-12 19:52 | 2021-08-12 19:53 | 1498 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA CARGA DEL 1708-02 | B21081200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 1498 | keep | 0 | Aug | 2021 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
CAGUAS | 2021-08-12 19:54 | 2021-08-12 19:55 | 1843 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21081200111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 1843 | keep | 0 | Aug | 2021 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
CAGUAS | 2021-08-12 19:56 | 2021-08-13 19:34 | 215 | 023:38 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA SE RETIRO ARBOL Y SE LEVANTO LINEAS PRIMARIAS | C21081200119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1418 | 2021-08-12 | 304870 | keep | 0 | Aug | 2021 | 0.20765 | 0.00014644 | Sustained | FALSE | TRUE | Not_TMED_Event | 215
CAGUAS | 2021-08-12 19:56 | 2021-08-12 19:57 | 1843 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21081200112 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 1843 | keep | 0 | Aug | 2021 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
ARECIBO | 2021-08-12 19:57 | 2021-08-13 10:28 | 10 | 014:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR REPARAR SECUNDARIA | A21081200113 | New_Event | Secondary Wire Down | Include | Include | Equipment | 871 | 2021-08-12 | 8710 | keep | 0 | Aug | 2021 | 0.0059323 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-08-12 19:58 | 2021-08-13 09:40 | 100 | 013:42 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | M21081200203 | New_Event | Vegetation Contact | Include | Include | Vegetation | 822 | 2021-08-12 | 82200 | keep | 0 | Aug | 2021 | 0.055986 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-08-12 20:24 | 2021-08-13 09:49 | 35 | 013:25 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21081200075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 805 | 2021-08-12 | 28175 | keep | 0 | Aug | 2021 | 0.01919 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-08-12 20:28 | 2021-08-12 20:29 | 1715 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL CARGA POR 1708-03 | B21081200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 1715 | keep | 0 | Aug | 2021 | 0.0011681 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2021-08-12 20:28 | 2021-08-12 20:29 | 1498 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA CARGA DEL 1708-02 | B21081200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 1498 | keep | 0 | Aug | 2021 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
PONCE | 2021-08-12 20:46 | 2021-08-13 12:51 | 200 | 016:05 | P | DESGANCHE | 1 POR 65 EN CORTE DE LINEA POR DESGANCHE | P21081200116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 965 | 2021-08-12 | 193000 | keep | 0 | Aug | 2021 | 0.13145 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-08-12 20:46 | 2021-08-13 17:40 | 45 | 020:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21081200208 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1254 | 2021-08-12 | 56430 | keep | 0 | Aug | 2021 | 0.038434 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BAYAMON | 2021-08-12 20:52 | 2021-08-13 14:09 | 15 | 017:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21081200088 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1037 | 2021-08-12 | 15555 | keep | 0 | Aug | 2021 | 0.010594 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-08-12 20:59 | 2021-08-12 21:01 | 870 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S21081200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-12 | 1740 | keep | 0 | Aug | 2021 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2021-08-12 21:04 | 2021-08-12 21:06 | 870 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S21081200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-12 | 1740 | keep | 0 | Aug | 2021 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
YAUCO | 2021-08-12 21:15 | 2021-08-13 17:28 | 472 | 020:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PRIMARIO | P21081200122 | Partial_restoration | Wire Down | Include | Include | Equipment | 1213 | 2021-08-12 | 572536 | keep | 0 | Aug | 2021 | 0.38995 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-08-12 21:18 | 2021-08-12 21:19 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21081200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 1310 | keep | 0 | Aug | 2021 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2021-08-12 21:37 | 2021-08-12 21:38 | 1715 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL CARGA POR 1708-03 | B21081200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 1715 | keep | 0 | Aug | 2021 | 0.0011681 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2021-08-12 21:37 | 2021-08-12 21:38 | 1498 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA CARGA DEL 1708-02 | B21081200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-12 | 1498 | keep | 0 | Aug | 2021 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
AGUADILLA | 2021-08-12 21:40 | 2021-08-13 11:15 | 120 | 013:35 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | M21081200213 | New_Event | Vegetation Contact | Include | Include | Vegetation | 815 | 2021-08-12 | 97800 | keep | 0 | Aug | 2021 | 0.066611 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
BAYAMON | 2021-08-12 21:50 | 2021-08-13 12:09 | 15 | 014:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE RETIRO AVE CRUZANDO LINEAS | B21081200089 | New_Event |  |  | Include | Wildlife | 859 | 2021-08-12 | 12885 | keep | 0 | Aug | 2021 | 0.0087759 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BARRANQUITAS | 2021-08-12 23:43 | 2021-08-13 13:59 | 200 | 014:16 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE RAPARO CONDUCTOR PRIMARIO | C21081200126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 856 | 2021-08-12 | 171200 | keep | 0 | Aug | 2021 | 0.1166 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-08-12 23:52 | 2021-08-13 11:22 | 60 | 011:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | M21081200218 | New_Event | Bad Weather | Include | Include | Weather | 690 | 2021-08-12 | 41400 | keep | 0 | Aug | 2021 | 0.028197 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-08-13 01:03 | 2021-08-13 01:04 | 958 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE LLEVA CARGA DEL 3202-01 | C21081300001 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-13 | 958 | keep | 0 | Aug | 2021 | 0.00065249 | 0.00065249 | Momentary | FALSE | FALSE | Not_TMED_Event | 958
CAGUAS | 2021-08-13 01:03 | 2021-08-13 01:04 | 1725 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE CARGA POR 3201-03 | C21081300001 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-13 | 1725 | keep | 0 | Aug | 2021 | 0.0011749 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
CAGUAS | 2021-08-13 01:04 | 2021-08-13 03:52 | 211 | 002:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | C21081300011 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 168 | 2021-08-13 | 35448 | keep | 0 | Aug | 2021 | 0.024143 | 0.00014371 | Sustained | FALSE | TRUE | Not_TMED_Event | 211
CAGUAS | 2021-08-13 02:04 | 2021-08-14 13:18 | 15 | 035:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | C21081300008 | New_Event | Bad Weather | Include | Include | Weather | 2114 | 2021-08-13 | 31710 | keep | 0 | Aug | 2021 | 0.021598 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-08-13 02:16 | 2021-08-13 07:22 | 12 | 005:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO Y SE LEVANTO LINEA SECUNDARIA | B21081300002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 306 | 2021-08-13 | 3672 | keep | 0 | Aug | 2021 | 0.002501 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
VEGA BAJA | 2021-08-13 02:54 | 2021-08-13 11:11 | 12 | 008:17 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21081300005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 497 | 2021-08-13 | 5964 | keep | 0 | Aug | 2021 | 0.0040621 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-08-13 03:52 | 2021-08-13 03:54 | 958 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR DEL SUELO LLEVA CARGA DEL 3202-01 | C21081300001 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 2 | 2021-08-13 | 1916 | keep | 0 | Aug | 2021 | 0.001305 | 0.00065249 | Momentary | FALSE | FALSE | Not_TMED_Event | 958
CAGUAS | 2021-08-13 03:52 | 2021-08-13 03:54 | 1725 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR DEL SUELO CARGA POR 3201-03 | C21081300001 | Additional_clients | Wire Down | Include | Include | Equipment | 2 | 2021-08-13 | 3450 | keep | 0 | Aug | 2021 | 0.0023498 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-08-13 03:54 | 2021-08-13 14:27 | 211 | 010:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | C21081300011 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 633 | 2021-08-13 | 133563 | keep | 0 | Aug | 2021 | 0.090969 | 0.00014371 | Sustained | FALSE | TRUE | Not_TMED_Event | 211
SAN JUAN | 2021-08-13 04:02 | 2021-08-13 08:52 | 600 | 004:50 | P | AISLADOR ROTO, PARTIDO O SAFADO | 80% EN SERVICIO DEL 1206-04 SE ABRIO MACHETE EN LA CARR PR-176 KM 10.8 Y SE CERRO MACHETE EN LA CARR PR-181 FRENTE A LA ENTRADA DE ENCANTADA EN SERVICIO 60% DEL 1204-03 40% DEL 1204-04 Y 33% DEL 1303-02 | S21081300004 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 290 | 2021-08-13 | 174000 | keep | 0 | Aug | 2021 | 0.11851 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2021-08-13 04:02 | 2021-08-13 08:52 | 552 | 004:50 | P | AISLADOR ROTO, PARTIDO O SAFADO | 80% EN SERVICIO DEL 1206-04 SE ABRIO MACHETE EN LA CARR PR-176 KM 10.8 Y SE CERRO MACHETE EN LA CARR PR-181 FRENTE A LA ENTRADA DE ENCANTADA EN SERVICIO 60% DEL 1204-03, 40% DEL 1204-04 Y 33% DEL 1303-02 | S21081300004 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 290 | 2021-08-13 | 160080 | keep | 0 | Aug | 2021 | 0.10903 | 0.00037596 | Sustained | FALSE | FALSE | Not_TMED_Event | 552
SAN JUAN | 2021-08-13 04:02 | 2021-08-13 08:07 | 1440 | 004:05 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO ABRIENDO MACHETES EN LA ENTRADA HACIA COMPLEJO DE URBANIZACIONES ENCANTADA EN LA CARR PR-181 POR AISLADOR PARTIDO Y SE CERRO INTERRUPTOR POR CONTROL 80% EN SERVICIO CONTINUA FUERA 60% DEL 1204-03 40% DEL 1204-04 Y 33% DEL 1203-02 | S21081300004 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 245 | 2021-08-13 | 352800 | keep | 0 | Aug | 2021 | 0.24029 | 0.00098078 | Sustained | FALSE | FALSE | Not_TMED_Event | 1440
SAN JUAN | 2021-08-13 04:02 | 2021-08-13 08:52 | 803 | 004:50 | P | AISLADOR ROTO, PARTIDO O SAFADO | 80% EN SERVICIO DE 1206-04 SE ABRIO MACHETE EN LA CARR PR-176 KM 10.8 Y SE CERRO MACHETE EN LA CARR PR-181 FRENTE A LA ENTRADA DE ENCANTADA EN SERVICIO 60% DEL 1204-03 40% DEL 1204-04 Y 33% DEL 1303-02 | S21081300004 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 290 | 2021-08-13 | 232870 | keep | 0 | Aug | 2021 | 0.15861 | 0.00054692 | Sustained | FALSE | FALSE | Not_TMED_Event | 803
PONCE | 2021-08-13 05:30 | 2021-08-13 05:31 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210813000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-13 | 3114 | keep | 0 | Aug | 2021 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
MAYAGÃœEZ | 2021-08-13 06:22 | 2021-08-13 18:10 | 20 | 011:48 | P | PARARRAYOS DEFECTUOSO | 1 X 25 EN TRANSFORMADOR SE REMPLAZO PARARRAYO CRUZADO | M21081300007 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 708 | 2021-08-13 | 14160 | keep | 0 | Aug | 2021 | 0.0096443 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-08-13 06:40 | 2021-08-13 06:41 | 350 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 40% POR EL 1437-03 | S21081300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-13 | 350 | keep | 0 | Aug | 2021 | 0.00023838 | 0.00023838 | Momentary | FALSE | FALSE | Not_TMED_Event | 350
SAN JUAN | 2021-08-13 06:40 | 2021-08-13 06:41 | 1699 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 40 % DEL 1301-2 | S21081300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-13 | 1699 | keep | 0 | Aug | 2021 | 0.0011572 | 0.0011572 | Momentary | FALSE | FALSE | Not_TMED_Event | 1699
CAGUAS | 2021-08-13 06:43 | 2021-08-14 15:09 | 1 | 032:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | C21081300014 | New_Event |  |  | Include | Wildlife | 1946 | 2021-08-13 | 1946 | keep | 0 | Aug | 2021 | 0.0013254 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-08-13 06:53 | 2021-08-13 06:54 | 1702 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR | C21081300000 | New_Event |  |  | Include | Wildlife | 1 | 2021-08-13 | 1702 | keep | 0 | Aug | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2021-08-13 06:54 | 2021-08-13 15:18 | 60 | 008:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C21081300026 | 1st_after_momentary |  |  | Include | Wildlife | 504 | 2021-08-13 | 30240 | keep | 0 | Aug | 2021 | 0.020596 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-08-13 07:02 | 2021-08-13 16:19 | 1 | 009:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN TRANSFOMADOR DESCARGAS ELECTRICAS | M21081300009 | New_Event | Bad Weather | Include | Include | Weather | 557 | 2021-08-13 | 557 | keep | 0 | Aug | 2021 | 0.00037937 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-08-13 07:19 | 2021-08-13 07:20 | 449 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | P210813000XX | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-13 | 449 | keep | 0 | Aug | 2021 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
PONCE | 2021-08-13 07:20 | 2021-08-13 13:58 | 75 | 006:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA LINEAS CRUZADAS | P21081300012 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 398 | 2021-08-13 | 29850 | keep | 0 | Aug | 2021 | 0.020331 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
YAUCO | 2021-08-13 07:31 | 2021-08-13 13:43 | 15 | 006:12 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21081300022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 372 | 2021-08-13 | 5580 | keep | 0 | Aug | 2021 | 0.0038005 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
SAN JUAN | 2021-08-13 08:07 | 2021-08-13 08:52 | 1223 | 000:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | 80% EN SERVICIO SE ABRIO MACHETE EN LA CARR PR-176 KM 10.8 Y SE CERRO MACHETE EN LA CARR PR-181 FRENTE A LA ENTRADA DE ENCANTADA EN SERVICIO 60% DEL 1204-03 40% DEL 1204-04 Y 33% DEL 1303-02 | S21081300004 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 45 | 2021-08-13 | 55035 | keep | 0 | Aug | 2021 | 0.037484 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-13 08:24 | 2021-08-13 08:25 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 99% DEL 1909 09 | S21081300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-13 | 222 | keep | 0 | Aug | 2021 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2021-08-13 08:24 | 2021-08-13 08:25 | 4411 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR 1907 03 | S21081300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-13 | 4411 | keep | 0 | Aug | 2021 | 0.0030043 | 0.0030043 | Momentary | FALSE | FALSE | Not_TMED_Event | 4411
BAYAMON | 2021-08-13 08:25 | 2021-08-13 08:29 | 1 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR SCADA | B21081200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-08-13 | 4 | keep | 0 | Aug | 2021 | 2.7244e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-08-13 08:52 | 2021-08-13 10:57 | 599 | 002:05 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR Y SE REPARO ALAMBRE PRIMARIO EN EL TRONCAL Y SE CERRO MACHETE EN LA CARR PR-175 EN CARRAIZO ALIMENTADOR 100% EN SERVICIO | S21081300004 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 125 | 2021-08-13 | 74875 | keep | 0 | Aug | 2021 | 0.050997 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-13 09:01 | 2021-08-14 17:23 | 10 | 032:22 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO DEL T-5 A T-3 | B21081300018 | New_Event | UG Cable Fault | Include | Include | Equipment | 1942 | 2021-08-13 | 19420 | keep | 0 | Aug | 2021 | 0.013227 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-08-13 09:01 | 2021-08-13 15:52 | 50 | 006:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21081300019 | New_Event | Bad Weather | Include | Include | Weather | 411 | 2021-08-13 | 20550 | keep | 0 | Aug | 2021 | 0.013997 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-08-13 09:01 | 2021-08-13 12:13 | 50 | 003:12 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21081300015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 192 | 2021-08-13 | 9600 | keep | 0 | Aug | 2021 | 0.0065385 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-13 09:07 | 2021-08-13 18:55 | 100 | 009:48 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 140 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | M21081300025 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 588 | 2021-08-13 | 58800 | keep | 0 | Aug | 2021 | 0.040048 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-08-13 09:08 | 2021-08-13 09:52 | 20 | 000:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA, DISCOS Y AISLADORES | B21081300000 | New_Event | Cutout Failure | Include | Include | Equipment | 44 | 2021-08-13 | 880 | keep | 0 | Aug | 2021 | 0.00059936 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-08-13 09:16 | 2021-08-14 10:30 | 15 | 025:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | S21081300057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1514 | 2021-08-13 | 22710 | keep | 0 | Aug | 2021 | 0.015468 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-08-13 09:16 | 2021-08-13 11:57 | 15 | 002:41 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21081300023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 161 | 2021-08-13 | 2415 | keep | 0 | Aug | 2021 | 0.0016448 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CANOVANAS | 2021-08-13 09:16 | 2021-08-13 15:29 | 1 | 006:13 | P | OTRAS CAUSAS | 2 X 40 EN RISER Y 2 X 25 RBA EN TRANSCLOSURE P/T AVERIADO | R21081300002 | New_Event | Other Causes | Include | Include | Other | 373 | 2021-08-13 | 373 | keep | 0 | Aug | 2021 | 0.00025405 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-08-13 09:16 | 2021-08-13 19:25 | 46 | 010:09 | P | ESTRUCTURA AVERIADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO POSTE PRIMARIO Y SE LEVANTARON LINEAS PRIMARIA | C21081300022 | New_Event | Defective Pole | Include | Include | Equipment | 609 | 2021-08-13 | 28014 | keep | 0 | Aug | 2021 | 0.01908 | 3.133e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 46
CAGUAS | 2021-08-13 09:16 | 2021-08-13 11:03 | 225 | 001:47 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN CORTES DE LINEA SE RETIRO BAMBUA DE LA LINEA | C21081300025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 107 | 2021-08-13 | 24075 | keep | 0 | Aug | 2021 | 0.016397 | 0.00015325 | Sustained | FALSE | TRUE | Not_TMED_Event | 225
ARECIBO | 2021-08-13 09:16 | 2021-08-13 13:30 | 50 | 004:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN RISER SE REMPLAZO CAJA DE POLIMERO DE 100AMP EN RISER FID30223994 | A21081300004 | New_Event | Cutout Failure | Include | Include | Equipment | 254 | 2021-08-13 | 12700 | keep | 0 | Aug | 2021 | 0.0086499 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-08-13 09:16 | 2021-08-13 15:18 | 10 | 006:02 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA REQUIERE DESGANCHE | A21081300007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 362 | 2021-08-13 | 3620 | keep | 0 | Aug | 2021 | 0.0024656 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
HUMACAO | 2021-08-13 09:17 | 2021-08-13 10:37 | 1064 | 001:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DEL 2603-08E SE CERRO EN EL CAMPO | C21081300031 | New_Event |  |  | Include | Wildlife | 80 | 2021-08-13 | 85120 | keep | 0 | Aug | 2021 | 0.057975 | 0.00072469 | Sustained | FALSE | FALSE | Not_TMED_Event | 1064
CAGUAS | 2021-08-13 09:17 | 2021-08-13 09:57 | 1 | 000:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | C21081300041 | New_Event | Cutout Failure | Include | Include | Equipment | 40 | 2021-08-13 | 40 | keep | 0 | Aug | 2021 | 2.7244e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-08-13 09:17 | 2021-08-13 12:13 | 15 | 002:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21081300033 | New_Event | Bad Weather | Include | Include | Weather | 176 | 2021-08-13 | 2640 | keep | 0 | Aug | 2021 | 0.0017981 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-08-13 09:17 | 2021-08-13 11:40 | 54 | 002:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE REEMPAZO 2 CAJAS PRIMARIAS | C21081300030 | New_Event | Cutout Failure | Include | Include | Equipment | 143 | 2021-08-13 | 7722 | keep | 0 | Aug | 2021 | 0.0052594 | 3.6779e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 54
MAYAGÃœEZ | 2021-08-13 09:17 | 2021-08-13 12:39 | 25 | 003:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE SOBRE LINEA | M21081300021 | New_Event |  |  | Include | Wildlife | 202 | 2021-08-13 | 5050 | keep | 0 | Aug | 2021 | 0.0034395 | 1.7027e-05 | Sustained | TRUE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-08-13 09:17 | 2021-08-13 17:15 | 12 | 007:58 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO EN FID16433530 POSTE DE METAL 45' | A21081300008 | New_Event | Defective Pole | Include | Include | Equipment | 478 | 2021-08-13 | 5736 | keep | 0 | Aug | 2021 | 0.0039068 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-08-13 09:31 | 2021-08-13 09:40 | 1 | 000:09 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | R21081300010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2021-08-13 | 9 | keep | 0 | Aug | 2021 | 6.1299e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-08-13 09:40 | 2021-08-13 13:54 | 40 | 004:14 | P | ERROR HUMANO | 1 X 80 EN SU - 14 PERSONAL REALIZANDO OPERACIONES PARA DESCONECTE | R21081300010 | New_Event | Human Error | Include | Include | Other | 254 | 2021-08-13 | 10160 | keep | 0 | Aug | 2021 | 0.0069199 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-08-13 09:40 | 2021-08-13 11:21 | 200 | 001:41 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA NO CAUSA | R21081300010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 101 | 2021-08-13 | 20200 | keep | 0 | Aug | 2021 | 0.013758 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
VEGA BAJA | 2021-08-13 09:52 | 2021-08-13 09:53 | 3000 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO INTERRUPTOR PARA PODER ABRIR CAJA PRIMARIA DIRECTO A TRONCAL | B21081300000 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2021-08-13 | 3000 | keep | 0 | Aug | 2021 | 0.0020433 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-08-13 09:53 | 2021-08-13 19:35 | 20 | 009:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA, DISCOS Y AISLADORES | B21081300000 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 582 | 2021-08-13 | 11640 | keep | 0 | Aug | 2021 | 0.007928 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-08-13 10:20 | 2021-08-13 10:24 | 609 | 000:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETE EN LA CARR PR-176 CAMINO LOS ROMERO Y SE CERRO MACHETE EN LA CARR PR-842 ESQUINA CALLE FIDALGO DIAZ POR ALAMBRE PRIMARIO EN EL SUELO SE TRANSFIRIO 70% DE LA CARGA AL BREAKER 1908-03 | S21081300069 | New_Event | Wire Down | Include | Include | Equipment | 4 | 2021-08-13 | 2436 | keep | 0 | Aug | 2021 | 0.0016591 | 0.00041479 | Momentary | FALSE | FALSE | Not_TMED_Event | 609
SAN JUAN | 2021-08-13 10:24 | 2021-08-13 14:19 | 150 | 003:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO DEL SUELO | S21081300069 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 235 | 2021-08-13 | 35250 | keep | 0 | Aug | 2021 | 0.024009 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2021-08-13 10:29 | 2021-08-13 10:30 | 325 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21081300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-13 | 325 | keep | 0 | Aug | 2021 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
HUMACAO | 2021-08-13 10:37 | 2021-08-13 10:38 | 5630 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR | C21081300054 | New_Event |  |  | Include | Wildlife | 1 | 2021-08-13 | 5630 | keep | 0 | Aug | 2021 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2021-08-13 10:38 | 2021-08-13 14:00 | 1064 | 003:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DEL 2603-08E SE CERRO EN EL CAMPO | C21081300031 | 1st_after_momentary |  |  | Include | Wildlife | 202 | 2021-08-13 | 214928 | keep | 0 | Aug | 2021 | 0.14639 | 0.00072469 | Sustained | FALSE | FALSE | Not_TMED_Event | 1064
CAGUAS | 2021-08-13 11:27 | 2021-08-13 13:31 | 853 | 002:04 | T | CABLE SOTERRADO AVERIADO | DISPARO INTERRUPTOR SE SECCIONALIZO CABLE SOTERRADO EN RISER Y SE CERRO POR CONTROL 75% DE LA CARGA TRANSFERIDO AL 3103-02 | C21081300060 | New_Event | UG Cable Fault | Include | Include | Equipment | 124 | 2021-08-13 | 105772 | keep | 0 | Aug | 2021 | 0.072041 | 0.00058097 | Sustained | FALSE | FALSE | Not_TMED_Event | 853
SAN JUAN | 2021-08-13 12:13 | 2021-08-13 12:14 | 733 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21081300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-13 | 733 | keep | 0 | Aug | 2021 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
CAGUAS | 2021-08-13 13:31 | 2021-08-13 13:44 | 637 | 000:13 | P | CABLE SOTERRADO AVERIADO | DISPARO INTERRUPTOR SE SECCIONALIZO CABLE SOTERRADO EN RISER Y SE CERRO POR CONTROL 75% EN SERVICIO CERRANDO N/O CONTRA EL 3103-03 | C21081300060 | New_Event | UG Cable Fault | Include | Include | Equipment | 13 | 2021-08-13 | 8281 | keep | 0 | Aug | 2021 | 0.0056402 | 0.00043386 | Sustained | FALSE | FALSE | Not_TMED_Event | 637
BAYAMON | 2021-08-13 13:48 | 2021-08-13 13:50 | 353 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S21081300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-13 | 706 | keep | 0 | Aug | 2021 | 0.00048085 | 0.00024043 | Momentary | FALSE | FALSE | Not_TMED_Event | 353
BAYAMON | 2021-08-13 13:59 | 2021-08-13 14:00 | 320 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO Y SE CERRO POR CONTROL | B21081300043 | New_Event |  |  | Include | Wildlife | 1 | 2021-08-13 | 320 | keep | 0 | Aug | 2021 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
HUMACAO | 2021-08-13 14:00 | 2021-08-13 16:59 | 50 | 002:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO INTELLIRRUPTER 2603-08F CRUCE POR PALOMA CERRADO EN EL CAMPO | C21081300066 | Partial_restoration |  |  | Include | Wildlife | 179 | 2021-08-13 | 8950 | keep | 0 | Aug | 2021 | 0.0060958 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-13 14:00 | 2021-08-13 18:29 | 40 | 004:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 40 EN CORTE DE LINEA SE RETIRO AVE | B21081300044 | 1st_after_momentary |  |  | Include | Wildlife | 269 | 2021-08-13 | 10760 | keep | 0 | Aug | 2021 | 0.0073286 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-08-13 14:01 | 2021-08-13 17:18 | 49 | 003:17 | P | DESGANCHE | 3 X 30 EN CORTE DE LINEA SE RETIRO ARBOL | C21081300073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2021-08-13 | 9653 | keep | 0 | Aug | 2021 | 0.0065746 | 3.3374e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 49
SAN JUAN | 2021-08-13 14:12 | 2021-08-13 17:17 | 1 | 003:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | S21081300100 | New_Event | Cutout Failure | Include | Include | Equipment | 185 | 2021-08-13 | 185 | keep | 0 | Aug | 2021 | 0.000126 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-08-13 14:12 | 2021-08-13 14:15 | 353 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S21081300000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-08-13 | 1059 | keep | 0 | Aug | 2021 | 0.00072128 | 0.00024043 | Momentary | FALSE | FALSE | Not_TMED_Event | 353
MAYAGÃœEZ | 2021-08-13 14:31 | 2021-08-13 18:30 | 15 | 003:59 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA SOBRE LINEA | M21081300049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2021-08-13 | 3585 | keep | 0 | Aug | 2021 | 0.0024417 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
ARECIBO | 2021-08-13 14:38 | 2021-08-13 17:00 | 80 | 002:22 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA FUERTE VIENTO | A21081300021 | New_Event | Bad Weather | Include | Include | Weather | 142 | 2021-08-13 | 11360 | keep | 0 | Aug | 2021 | 0.0077372 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-08-13 14:39 | 2021-08-13 14:40 | 528 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21081300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-13 | 528 | keep | 0 | Aug | 2021 | 0.00035962 | 0.00035962 | Momentary | FALSE | FALSE | Not_TMED_Event | 528
SAN JUAN | 2021-08-13 14:41 | 2021-08-13 16:04 | 844 | 001:23 | T | NO SE REPORTO CAUSA | NO CERRO POR CONTROL PERSONAL DE SUBESTACION LO CERRO FISICAMENTE EN EL CAMPO | S21081300104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 83 | 2021-08-13 | 70052 | keep | 0 | Aug | 2021 | 0.047712 | 0.00057484 | Sustained | FALSE | FALSE | Not_TMED_Event | 844
SAN JUAN | 2021-08-13 14:57 | 2021-08-14 08:08 | 50 | 017:11 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S21081300109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1031 | 2021-08-13 | 51550 | keep | 0 | Aug | 2021 | 0.03511 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-08-13 14:58 | 2021-08-13 20:28 | 50 | 005:30 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21081300049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 330 | 2021-08-13 | 16500 | keep | 0 | Aug | 2021 | 0.011238 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-08-13 15:03 | 2021-08-13 19:17 | 50 | 004:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA QUEMADA | S21081300103 | New_Event | Cutout Failure | Include | Include | Equipment | 254 | 2021-08-13 | 12700 | keep | 0 | Aug | 2021 | 0.0086499 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2021-08-13 15:03 | 2021-08-13 17:15 | 1 | 002:12 | P | NO SE REPORTO CAUSA | 2 X 10 EN BANCO DE TRANSFORMADORES | R21081300021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 132 | 2021-08-13 | 132 | keep | 0 | Aug | 2021 | 8.9905e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-08-13 15:16 | 2021-08-13 21:08 | 150 | 005:52 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21081300027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 352 | 2021-08-13 | 52800 | keep | 0 | Aug | 2021 | 0.035962 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
HUMACAO | 2021-08-13 15:20 | 2021-08-13 17:34 | 1 | 002:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA CRUCE POR AVE | C21081300092 | New_Event |  |  | Include | Wildlife | 134 | 2021-08-13 | 134 | keep | 0 | Aug | 2021 | 9.1267e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-08-13 15:21 | 2021-08-13 17:29 | 11 | 002:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE TRANSFORMADOR | C21081300093 | New_Event | Wire Down | Include | Include | Equipment | 128 | 2021-08-13 | 1408 | keep | 0 | Aug | 2021 | 0.00095898 | 7.492e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 11
YAUCO | 2021-08-13 15:23 | 2021-08-14 13:04 | 10 | 021:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR LINEA SECUNDARIA CRUZADA | P21081300040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1301 | 2021-08-13 | 13010 | keep | 0 | Aug | 2021 | 0.0088611 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
PONCE | 2021-08-13 15:25 | 2021-08-13 16:33 | 50 | 001:08 | P | MAL TIEMPO/RAYOS/WET ASH | BAJANTE ZAFADO EN TRANFORMADOR | P21081300080 | New_Event | Bad Weather | Include | Include | Weather | 68 | 2021-08-13 | 3400 | keep | 0 | Aug | 2021 | 0.0023157 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-08-13 15:25 | 2021-08-13 17:01 | 15 | 001:36 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21081300053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2021-08-13 | 1440 | keep | 0 | Aug | 2021 | 0.00098078 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-08-13 15:32 | 2021-08-14 15:13 | 40 | 023:41 | P | DESGANCHE | 1 X 80 EN CORTE DE LNEA | S21081300163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1421 | 2021-08-13 | 56840 | keep | 0 | Aug | 2021 | 0.038713 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-13 15:34 | 2021-08-13 17:40 | 50 | 002:06 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21081300060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2021-08-13 | 6300 | keep | 0 | Aug | 2021 | 0.0042909 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-08-13 15:45 | 2021-08-13 18:40 | 122 | 002:55 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C21081300099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2021-08-13 | 21350 | keep | 0 | Aug | 2021 | 0.014541 | 8.3094e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 122
BAYAMON | 2021-08-13 15:48 | 2021-08-13 15:57 | 1715 | 000:09 | T | ERROR HUMANO | SE DISPARO INTERRUPTOR REALIZANDO OPERACIONES CERRANDO N O DEL 1707-01 CONTRA 1708-02 | B21081300000 | New_Event | Human Error | Include | Include | Other | 9 | 2021-08-13 | 15435 | keep | 0 | Aug | 2021 | 0.010513 | 0.0011681 | Sustained | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2021-08-13 15:48 | 2021-08-13 15:57 | 1498 | 000:09 | T | ERROR HUMANO | SE DISPARO INTERRUPTOR REALIZANDO OPERACIONES CERRANDO N O DEL 1708-02 CONTRA 1708-03 | B21081300000 | New_Event | Human Error | Include | Include | Other | 9 | 2021-08-13 | 13482 | keep | 0 | Aug | 2021 | 0.0091825 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2021-08-13 15:52 | 2021-08-13 15:57 | 1935 | 000:05 | T | ERROR HUMANO | SE DISPARO INTERRUPTOR REALIZANDO OPERACIONES CERRANDO N O DEL 1707-01 CONTRA 1708-02 | B21081300059 | New_Event | Human Error | Include | Include | Other | 5 | 2021-08-13 | 9675 | keep | 0 | Aug | 2021 | 0.0065896 | 0.0013179 | Momentary | FALSE | FALSE | Not_TMED_Event | 1935
MAYAGÃœEZ | 2021-08-13 15:58 | 2021-08-13 21:30 | 30 | 005:32 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMA | M21081300069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 332 | 2021-08-13 | 9960 | keep | 0 | Aug | 2021 | 0.0067837 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
AGUADILLA | 2021-08-13 16:02 | 2021-08-13 20:05 | 300 | 004:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 100 EN CONVERTIDOR SE REPARO CONECTORES QUEMADOS DE BAJANTE HACIA CONVERTIDOR | M21081300070 | New_Event | Wire Down | Include | Include | Equipment | 243 | 2021-08-13 | 72900 | keep | 0 | Aug | 2021 | 0.049652 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2021-08-13 16:07 | 2021-08-14 02:13 | 100 | 010:06 | P | ESTRUCTURA AVERIADA | 2 X 65 EN CORTE DE LINEA SE REMPLAZO 2 POSTES PARTIDOS | S21081300133 | New_Event | Defective Pole | Include | Include | Equipment | 606 | 2021-08-13 | 60600 | keep | 0 | Aug | 2021 | 0.041274 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-08-13 16:13 | 2021-08-13 18:23 | 75 | 002:10 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEADESGANCHE | P21081300048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2021-08-13 | 9750 | keep | 0 | Aug | 2021 | 0.0066407 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-08-13 16:16 | 2021-08-13 17:41 | 10 | 001:25 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21081300063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 85 | 2021-08-13 | 850 | keep | 0 | Aug | 2021 | 0.00057893 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-08-13 16:24 | 2021-08-13 17:32 | 30 | 001:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | R21081300028 | New_Event |  |  | Include | Wildlife | 68 | 2021-08-13 | 2040 | keep | 0 | Aug | 2021 | 0.0013894 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-08-13 16:29 | 2021-08-13 16:30 | 435 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21081300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-13 | 435 | keep | 0 | Aug | 2021 | 0.00029628 | 0.00029628 | Momentary | FALSE | FALSE | Not_TMED_Event | 435
MAYAGÃœEZ | 2021-08-13 16:35 | 2021-08-13 18:35 | 3 | 002:00 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M21081300084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2021-08-13 | 360 | keep | 0 | Aug | 2021 | 0.00024519 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
BAYAMON | 2021-08-13 16:40 | 2021-08-14 11:55 | 12 | 019:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADR SE REEMPLAZO CAJA PRIMARIA | S21081300147 | New_Event | Cutout Failure | Include | Include | Equipment | 1155 | 2021-08-13 | 13860 | keep | 0 | Aug | 2021 | 0.00944 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-08-13 16:52 | 2021-08-13 20:08 | 40 | 003:16 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081300067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2021-08-13 | 7840 | keep | 0 | Aug | 2021 | 0.0053398 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-08-13 16:53 | 2021-08-14 11:40 | 50 | 018:47 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | P21081300052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1127 | 2021-08-13 | 56350 | keep | 0 | Aug | 2021 | 0.03838 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-13 16:54 | 2021-08-13 16:55 | 1812 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21081300068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-13 | 1812 | keep | 0 | Aug | 2021 | 0.0012341 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
CAGUAS | 2021-08-13 17:16 | 2021-08-13 17:18 | 1001 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C21081300115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-13 | 2002 | keep | 0 | Aug | 2021 | 0.0013636 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
CAGUAS | 2021-08-13 17:17 | 2021-08-14 14:53 | 40 | 021:36 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA REMPLAZO PIN POLE TOP | C21081300114 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1296 | 2021-08-13 | 51840 | keep | 0 | Aug | 2021 | 0.035308 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-08-13 17:47 | 2021-08-13 19:26 | 81 | 001:39 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C21081300125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2021-08-13 | 8019 | keep | 0 | Aug | 2021 | 0.0054617 | 5.5169e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 81
VEGA BAJA | 2021-08-13 17:53 | 2021-08-13 22:01 | 10 | 004:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21081300080 | New_Event | Secondary Wire Down | Include | Include | Equipment | 248 | 2021-08-13 | 2480 | keep | 0 | Aug | 2021 | 0.0016891 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-08-13 18:00 | 2021-08-14 10:18 | 65 | 016:18 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | M21081300109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 978 | 2021-08-13 | 63570 | keep | 0 | Aug | 2021 | 0.043297 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BAYAMON | 2021-08-13 18:28 | 2021-08-13 19:28 | 40 | 001:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 40 EN CORTE DE LINEA SE REPARO CONDUCTOR | B21081300085 | New_Event | Wire Down | Include | Include | Equipment | 60 | 2021-08-13 | 2400 | keep | 0 | Aug | 2021 | 0.0016346 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-08-13 18:30 | 2021-08-13 19:12 | 3 | 000:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR EN FID31546738 CAJA DE POLIMERO 100AMP | A21081300022 | New_Event | Cutout Failure | Include | Include | Equipment | 42 | 2021-08-13 | 126 | keep | 0 | Aug | 2021 | 8.5818e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2021-08-13 18:33 | 2021-08-14 10:29 | 80 | 015:56 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR | C21081300134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 956 | 2021-08-13 | 76480 | keep | 0 | Aug | 2021 | 0.05209 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
VEGA BAJA | 2021-08-13 18:38 | 2021-08-13 21:14 | 15 | 002:36 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFFORMADOR | B21081300086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 156 | 2021-08-13 | 2340 | keep | 0 | Aug | 2021 | 0.0015938 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-08-13 18:47 | 2021-08-13 23:09 | 40 | 004:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA | M21081300123 | New_Event | Wire Down | Include | Include | Equipment | 262 | 2021-08-13 | 10480 | keep | 0 | Aug | 2021 | 0.0071379 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-08-13 19:19 | 2021-08-13 19:20 | 1835 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21081300148 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-13 | 1835 | keep | 0 | Aug | 2021 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
PONCE | 2021-08-13 19:30 | 2021-08-13 23:40 | 125 | 004:10 | P | DESGANCHE | 1 X 65, 1 X 50 Y 1 X 40 EN CORTE DE LINEA | P21081300059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 250 | 2021-08-13 | 31250 | keep | 0 | Aug | 2021 | 0.021284 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
HUMACAO | 2021-08-13 19:33 | 2021-08-14 10:41 | 30 | 015:08 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21081300152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 908 | 2021-08-13 | 27240 | keep | 0 | Aug | 2021 | 0.018553 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-08-13 20:03 | 2021-08-14 17:50 | 10 | 021:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21081300054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1307 | 2021-08-13 | 13070 | keep | 0 | Aug | 2021 | 0.0089019 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-08-13 20:21 | 2021-08-14 09:48 | 50 | 013:27 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO CAUSA | C21081300162 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 807 | 2021-08-13 | 40350 | keep | 0 | Aug | 2021 | 0.027482 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-08-13 20:23 | 2021-08-13 21:16 | 254 | 000:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR IGUANA | C21081300163 | New_Event |  |  | Include | Wildlife | 53 | 2021-08-13 | 13462 | keep | 0 | Aug | 2021 | 0.0091689 | 0.000173 | Sustained | FALSE | TRUE | Not_TMED_Event | 254
CAGUAS | 2021-08-13 20:30 | 2021-08-14 11:41 | 7 | 015:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO BAJANTE SECUNDARIO Y LINEA SECUNDARIA | C21081300165 | New_Event | Secondary Wire Down | Include | Include | Equipment | 911 | 2021-08-13 | 6377 | keep | 0 | Aug | 2021 | 0.0043433 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
UTUADO | 2021-08-13 20:48 | 2021-08-14 13:50 | 15 | 017:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21081300058 | New_Event | Bad Weather | Include | Include | Weather | 1022 | 2021-08-13 | 15330 | keep | 0 | Aug | 2021 | 0.010441 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-08-13 20:50 | 2021-08-14 15:13 | 50 | 018:23 | P | ESTRUCTURA AVERIADA | SE CAMBIO POSTE PRIMARIO | S21081300165 | New_Event | Defective Pole | Include | Include | Equipment | 1103 | 2021-08-13 | 55150 | keep | 0 | Aug | 2021 | 0.037562 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2021-08-13 21:51 | 2021-08-14 09:18 | 134 | 011:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN LA ENTRADA DEL CONVERTIDOR MAL TIEMPO | C21081300175 | New_Event | Bad Weather | Include | Include | Weather | 687 | 2021-08-13 | 92058 | keep | 0 | Aug | 2021 | 0.0627 | 9.1267e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 134
PONCE | 2021-08-13 22:10 | 2021-08-13 23:10 | 30 | 001:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO NETRAL COMUN | P21081300053 | New_Event | Wire Down | Include | Include | Equipment | 60 | 2021-08-13 | 1800 | keep | 0 | Aug | 2021 | 0.001226 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2021-08-13 22:19 | 2021-08-15 13:40 | 200 | 039:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA Y 1 X 25 EN TRANSFORMADOR SE REPARO LINEA PRIMARIA ZAFADA DE AISLADOR Y SE REPARO LINEA SECUNDARIA | M21081300137 | New_Event | Wire Down | Include | Include | Equipment | 2361 | 2021-08-13 | 472200 | keep | 0 | Aug | 2021 | 0.32161 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-08-13 22:24 | 2021-08-15 11:28 | 65 | 037:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE LINEA A CAJA PRIMARIA | A21081300064 | New_Event | Wire Down | Include | Include | Equipment | 2224 | 2021-08-13 | 144560 | keep | 0 | Aug | 2021 | 0.098459 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
CANOVANAS | 2021-08-13 22:54 | 2021-08-14 14:05 | 40 | 015:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO Y LEVANTO CONDUCTOR YA ESTABA SECCIONALIZADO | R21081300043 | New_Event | Wire Down | Include | Include | Equipment | 911 | 2021-08-13 | 36440 | keep | 0 | Aug | 2021 | 0.024819 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-08-13 22:56 | 2021-08-14 09:55 | 12 | 010:59 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE SECUNDARIO Y SE REPARO TOMA DE SERVICIO | B21081300013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 659 | 2021-08-13 | 7908 | keep | 0 | Aug | 2021 | 0.0053861 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-08-13 23:14 | 2021-08-14 10:16 | 40 | 011:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA PUENTE PORTATIL CRUZANDO FASE | C21081300184 | New_Event | Wire Down | Include | Include | Equipment | 662 | 2021-08-13 | 26480 | keep | 0 | Aug | 2021 | 0.018035 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-08-13 23:30 | 2021-08-14 15:42 | 10 | 016:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR SE REMPLAZO TRAMO SECUNDARIO | B21081300099 | New_Event | Secondary Wire Down | Include | Include | Equipment | 972 | 2021-08-13 | 9720 | keep | 0 | Aug | 2021 | 0.0066202 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-08-14 01:05 | 2021-08-14 12:31 | 5 | 011:26 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO CAUSA | C21081400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 686 | 2021-08-14 | 3430 | keep | 0 | Aug | 2021 | 0.0023362 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2021-08-14 01:29 | 2021-08-14 01:30 | 5630 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21081400002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-14 | 5630 | keep | 0 | Aug | 2021 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
CAGUAS | 2021-08-14 02:46 | 2021-08-14 02:47 | 2000 | 000:01 | P | NO SE REPORTO CAUSA | RECIERRE | C21081400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-14 | 2000 | keep | 0 | Aug | 2021 | 0.0013622 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
SAN JUAN | 2021-08-14 02:47 | 2021-08-14 11:51 | 30 | 009:04 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21081400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 544 | 2021-08-14 | 16320 | keep | 0 | Aug | 2021 | 0.011115 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-08-14 02:49 | 2021-08-14 13:23 | 12 | 010:34 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE SECUNDARIO Y SE REPARO SECUNDARIA EN VARIOS PUNTOS | B21081400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 634 | 2021-08-14 | 7608 | keep | 0 | Aug | 2021 | 0.0051818 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2021-08-14 02:57 | 2021-08-14 02:58 | 1827 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M21081400000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-08-14 | 1827 | keep | 0 | Aug | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2021-08-14 02:58 | 2021-08-15 12:34 | 60 | 033:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081400142 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 2016 | 2021-08-14 | 120960 | keep | 0 | Aug | 2021 | 0.082385 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-08-14 04:05 | 2021-08-14 18:40 | 125 | 014:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO | A21081400008 | New_Event | Bad Weather | Include | Include | Weather | 875 | 2021-08-14 | 109375 | keep | 0 | Aug | 2021 | 0.074495 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
CAGUAS | 2021-08-14 04:25 | 2021-08-14 04:26 | 315 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C21081400004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-14 | 315 | keep | 0 | Aug | 2021 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
ARECIBO | 2021-08-14 04:56 | 2021-08-14 04:57 | 1227 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | A21081400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-14 | 1227 | keep | 0 | Aug | 2021 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2021-08-14 04:57 | 2021-08-14 12:35 | 25 | 007:38 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21081400045 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 458 | 2021-08-14 | 11450 | keep | 0 | Aug | 2021 | 0.0077985 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CAGUAS | 2021-08-14 05:21 | 2021-08-14 11:19 | 100 | 005:58 | P | NO SE REPORTO CAUSA | 1 X 65, 2 X 40 EN CORTES DE LINEA Y 2 X 25 EN RISER NO CAUSA | C21081400007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 358 | 2021-08-14 | 35800 | keep | 0 | Aug | 2021 | 0.024383 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-08-14 05:24 | 2021-08-14 08:21 | 4188 | 002:57 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR SE SECCIONALIZO CONDUCTOR PRIMARIO EN EL SUELO CERRADO POR CONTROL | R21081400005 | New_Event | Wire Down | Include | Include | Equipment | 177 | 2021-08-14 | 741276 | keep | 0 | Aug | 2021 | 0.50488 | 0.0028524 | Sustained | FALSE | FALSE | Not_TMED_Event | 4188
BAYAMON | 2021-08-14 05:46 | 2021-08-14 05:47 | 2858 | 000:01 | T | DESGANCHE | RECERRO | B21081400005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-14 | 2858 | keep | 0 | Aug | 2021 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
BAYAMON | 2021-08-14 05:47 | 2021-08-14 13:35 | 50 | 007:48 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081400006 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 468 | 2021-08-14 | 23400 | keep | 0 | Aug | 2021 | 0.015938 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-08-14 05:52 | 2021-08-14 11:58 | 80 | 006:06 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA ELIMINO PARARRAYO | C21081400009 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 366 | 2021-08-14 | 29280 | keep | 0 | Aug | 2021 | 0.019942 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-08-14 06:15 | 2021-08-14 06:16 | 1702 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21081400010 | New_Event |  |  | Include | Wildlife | 1 | 2021-08-14 | 1702 | keep | 0 | Aug | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2021-08-14 06:16 | 2021-08-14 06:32 | 200 | 000:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 Y 1 X 65 EN CORTES DE LINEA CRUCE POR AVE | C21081400016 | 1st_after_momentary |  |  | Include | Wildlife | 16 | 2021-08-14 | 3200 | keep | 0 | Aug | 2021 | 0.0021795 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-08-14 06:19 | 2021-08-14 10:25 | 60 | 004:06 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21081400013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2021-08-14 | 14760 | keep | 0 | Aug | 2021 | 0.010053 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-08-14 06:32 | 2021-08-14 06:33 | 1702 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21081400010 | Additional_clients |  |  | Include | Wildlife | 1 | 2021-08-14 | 1702 | keep | 0 | Aug | 2021 | 0.0011592 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-08-14 06:33 | 2021-08-14 06:44 | 200 | 000:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 Y 1 X 65 EN CORTES DE LINEA CRUCE POR AVE | C21081400016 | 1st_after_momentary |  |  | Include | Wildlife | 11 | 2021-08-14 | 2200 | keep | 0 | Aug | 2021 | 0.0014984 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-08-14 06:44 | 2021-08-14 06:45 | 1702 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21081400010 | Additional_clients |  |  | Include | Wildlife | 1 | 2021-08-14 | 1702 | keep | 0 | Aug | 2021 | 0.0011592 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-08-14 06:45 | 2021-08-14 10:34 | 200 | 003:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 Y 1 X 65 EN CORTES DE LINEA CRUCE POR AVE | C21081400016 | 1st_after_momentary |  |  | Include | Wildlife | 229 | 2021-08-14 | 45800 | keep | 0 | Aug | 2021 | 0.031194 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-08-14 06:58 | 2021-08-14 13:35 | 20 | 006:37 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081400009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 397 | 2021-08-14 | 7940 | keep | 0 | Aug | 2021 | 0.0054079 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-08-14 07:16 | 2021-08-14 11:17 | 45 | 004:01 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081400010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2021-08-14 | 10845 | keep | 0 | Aug | 2021 | 0.0073865 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BAYAMON | 2021-08-14 07:37 | 2021-08-14 07:38 | 112 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE ALIMENTADOR | B21081400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-14 | 112 | keep | 0 | Aug | 2021 | 7.6283e-05 | 7.6283e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 112
BAYAMON | 2021-08-14 07:39 | 2021-08-14 14:02 | 100 | 006:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 200 EN CORTE DE LINEA SE CERRO PUENTE ABIERTO | B21081400013 | New_Event | Wire Down | Include | Include | Equipment | 383 | 2021-08-14 | 38300 | keep | 0 | Aug | 2021 | 0.026086 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-08-14 07:42 | 2021-08-14 07:43 | 5809 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE ALIMENTADOR | B21081400000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-14 | 5809 | keep | 0 | Aug | 2021 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
BAYAMON | 2021-08-14 07:43 | 2021-08-14 17:44 | 200 | 010:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | B21081400025 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 601 | 2021-08-14 | 120200 | keep | 0 | Aug | 2021 | 0.081868 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-08-14 07:45 | 2021-08-14 18:00 | 200 | 010:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 Y 1 X 40 EN CORTES DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21081400007 | New_Event | Wire Down | Include | Include | Equipment | 615 | 2021-08-14 | 123000 | keep | 0 | Aug | 2021 | 0.083775 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-08-14 08:06 | 2021-08-14 08:07 | 2107 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21081400029 | New_Event |  |  | Include | Wildlife | 1 | 2021-08-14 | 2107 | keep | 0 | Aug | 2021 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
ARECIBO | 2021-08-14 08:07 | 2021-08-14 11:20 | 25 | 003:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE CRUZO LINEAS | A21081400035 | 1st_after_momentary |  |  | Include | Wildlife | 193 | 2021-08-14 | 4825 | keep | 0 | Aug | 2021 | 0.0032863 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
HUMACAO | 2021-08-14 08:10 | 2021-08-14 11:25 | 50 | 003:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C21081400029 | New_Event |  |  | Include | Wildlife | 195 | 2021-08-14 | 9750 | keep | 0 | Aug | 2021 | 0.0066407 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-14 08:11 | 2021-08-14 11:18 | 60 | 003:07 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA | B21081400017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 187 | 2021-08-14 | 11220 | keep | 0 | Aug | 2021 | 0.0076419 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-08-14 08:14 | 2021-08-14 20:52 | 1 | 012:38 | P | NO SE REPORTO CAUSA | 2 X 40 EN SU | B21081400020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 758 | 2021-08-14 | 758 | keep | 0 | Aug | 2021 | 0.00051627 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-08-14 08:17 | 2021-08-14 09:55 | 341 | 001:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES PARA SECCIONALIZAR CONDUCTOR DE 13 KV SOBRE EL 8 KV Y PODER REPARAR | R21081300036 | New_Event | Wire Down | Include | Include | Equipment | 98 | 2021-08-14 | 33418 | keep | 0 | Aug | 2021 | 0.022761 | 0.00023225 | Sustained | FALSE | FALSE | Not_TMED_Event | 341
CANOVANAS | 2021-08-14 08:21 | 2021-08-14 11:34 | 375 | 003:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO 3 JUEGOS DE DISCO Y SE SUBIO CONDUCTOR PRIMARIO | R21081400035 | Partial_restoration | Wire Down | Include | Include | Equipment | 193 | 2021-08-14 | 72375 | keep | 0 | Aug | 2021 | 0.049294 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-14 08:22 | 2021-08-14 08:23 | 2402 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE ALIMENTADOR | B21081400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-14 | 2402 | keep | 0 | Aug | 2021 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2021-08-14 08:39 | 2021-08-14 15:44 | 12 | 007:05 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR 37.5KVA | B21081400026 | New_Event | Service Transformer Failure | Include | Include | Equipment | 425 | 2021-08-14 | 5100 | keep | 0 | Aug | 2021 | 0.0034736 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-08-14 08:53 | 2021-08-14 14:01 | 125 | 005:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 Y 1 X 40 EN CORTES DE LINEA CRUCE POR AVE | R21081400036 | New_Event |  |  | Include | Wildlife | 308 | 2021-08-14 | 38500 | keep | 0 | Aug | 2021 | 0.026222 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
SAN JUAN | 2021-08-14 08:58 | 2021-08-14 19:43 | 3 | 010:45 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIO TRANSFORMADOR PARA REEMPLAZAR POSTE SECUNDARIO POR PERSONAL DE CLARO Y BAJANTE SECUNDARIO | R21081400037 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 645 | 2021-08-14 | 1935 | keep | 0 | Aug | 2021 | 0.0013179 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-08-14 09:05 | 2021-08-15 12:24 | 1452 | 027:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21081400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1639 | 2021-08-14 | 2379828 | keep | 0 | Aug | 2021 | 1.6209 | 0.00098895 | Sustained | FALSE | TRUE | Not_TMED_Event | 1452
SAN JUAN | 2021-08-14 09:05 | 2021-08-15 12:24 | 616 | 027:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21081400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1639 | 2021-08-14 | 1009624 | keep | 0 | Aug | 2021 | 0.68765 | 0.00041955 | Sustained | FALSE | TRUE | Not_TMED_Event | 616
MAYAGÃœEZ | 2021-08-14 09:11 | 2021-08-14 17:20 | 1 | 008:09 | P | DESGANCHE | 1 X 65 EN RISER REQUIERE DESGANCHE | M21081400014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 489 | 2021-08-14 | 489 | keep | 0 | Aug | 2021 | 0.00033306 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-08-14 09:37 | 2021-08-14 16:40 | 10 | 007:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21081400042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 423 | 2021-08-14 | 4230 | keep | 0 | Aug | 2021 | 0.002881 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-08-14 09:38 | 2021-08-15 17:40 | 100 | 032:02 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081400011 | New_Event | Bad Weather | Include | Include | Weather | 1922 | 2021-08-14 | 192200 | keep | 0 | Aug | 2021 | 0.13091 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-08-14 09:43 | 2021-08-16 13:30 | 200 | 051:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO BAJANTE PRIMARIO | M21081400018 | New_Event | Wire Down | Include | Include | Equipment | 3107 | 2021-08-14 | 621400 | keep | 0 | Aug | 2021 | 0.42323 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-08-14 09:46 | 2021-08-14 11:00 | 15 | 001:14 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21081400020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2021-08-14 | 1110 | keep | 0 | Aug | 2021 | 0.00075602 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
PONCE | 2021-08-14 09:56 | 2021-08-14 18:22 | 1 | 008:26 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN MONTURA TRIFASICA BEJUCO EN LINEA SECUNDARIA | P21081400010 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 506 | 2021-08-14 | 506 | keep | 0 | Aug | 2021 | 0.00034463 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
PONCE | 2021-08-14 09:57 | 2021-08-14 11:33 | 2 | 001:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA LINEAS ARRIADAS | P21081400011 | New_Event | Wire Down | Include | Include | Equipment | 96 | 2021-08-14 | 192 | keep | 0 | Aug | 2021 | 0.00013077 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
CAGUAS | 2021-08-14 10:01 | 2021-08-14 15:43 | 40 | 005:42 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21081400046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 342 | 2021-08-14 | 13680 | keep | 0 | Aug | 2021 | 0.0093174 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
FAJARDO | 2021-08-14 10:03 | 2021-08-14 11:08 | 45 | 001:05 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | R21081400042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 65 | 2021-08-14 | 2925 | keep | 0 | Aug | 2021 | 0.0019922 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BAYAMON | 2021-08-14 10:11 | 2021-08-14 11:17 | 10 | 001:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | B21081400014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 66 | 2021-08-14 | 660 | keep | 0 | Aug | 2021 | 0.00044952 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-08-14 10:12 | 2021-08-15 13:39 | 20 | 027:27 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO PINO DE LA LINEA | C21081500031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1647 | 2021-08-14 | 32940 | keep | 0 | Aug | 2021 | 0.022435 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-08-14 10:23 | 2021-08-14 17:04 | 15 | 006:41 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | S21081400019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 401 | 2021-08-14 | 6015 | keep | 0 | Aug | 2021 | 0.0040968 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-08-14 10:25 | 2021-08-14 14:59 | 1117 | 004:34 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE RETIRO IGUANA QUEMADA DEL TRONCAL DEL ALIMENTADOR 6404-02 Y SE CERRO EL INTERRUPTOR 6404-02 QUE ESTA LLEVANDO LA CARGA DEL 6404-01 | M21081400026 | New_Event |  |  | Include | Wildlife | 274 | 2021-08-14 | 306058 | keep | 0 | Aug | 2021 | 0.20845 | 0.00076078 | Sustained | FALSE | FALSE | Not_TMED_Event | 1117
MAYAGÃœEZ | 2021-08-14 10:25 | 2021-08-14 14:59 | 1671 | 004:34 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE RETIRO IGUANA QUEMADA EN EL TRONCAL DEL ALIMENTADOR Y SE CERRO EL INTERRUPTOR | M21081400026 | New_Event |  |  | Include | Wildlife | 274 | 2021-08-14 | 457854 | keep | 0 | Aug | 2021 | 0.31184 | 0.0011381 | Sustained | FALSE | FALSE | Not_TMED_Event | 1671
ARECIBO | 2021-08-14 10:25 | 2021-08-14 14:20 | 30 | 003:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21081400044 | New_Event | Bad Weather | Include | Include | Weather | 235 | 2021-08-14 | 7050 | keep | 0 | Aug | 2021 | 0.0048017 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-08-14 10:38 | 2021-08-14 16:00 | 50 | 005:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081400038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 322 | 2021-08-14 | 16100 | keep | 0 | Aug | 2021 | 0.010966 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-08-14 10:40 | 2021-08-14 16:58 | 50 | 006:18 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | R21081400046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 378 | 2021-08-14 | 18900 | keep | 0 | Aug | 2021 | 0.012873 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
YAUCO | 2021-08-14 10:50 | 2021-08-14 13:19 | 1475 | 002:29 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO 0010 LOCKOUT TRIP SE REMOVIO IGUANA CRUZANDO PARARRAYO DE BARRA FASE C | P21081400039 | New_Event |  |  | Include | Wildlife | 149 | 2021-08-14 | 219775 | keep | 0 | Aug | 2021 | 0.14969 | 0.0010046 | Sustained | FALSE | FALSE | Not_TMED_Event | 1475
YAUCO | 2021-08-14 10:50 | 2021-08-14 13:19 | 661 | 002:29 | S | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO 0010 LOCKOUT TRIP SE REMOVIO IGUANA CRUZANDO PARARRAYO DE BARRA FASE C | P21081400039 | New_Event |  |  | Include | Wildlife | 149 | 2021-08-14 | 98489 | keep | 0 | Aug | 2021 | 0.06708 | 0.0004502 | Sustained | FALSE | FALSE | Not_TMED_Event | 661
CAGUAS | 2021-08-14 10:59 | 2021-08-14 13:18 | 60 | 002:19 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21081400054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2021-08-14 | 8340 | keep | 0 | Aug | 2021 | 0.0056803 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-08-14 11:01 | 2021-08-14 18:00 | 7 | 006:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21081400055 | New_Event | Secondary Wire Down | Include | Include | Equipment | 419 | 2021-08-14 | 2933 | keep | 0 | Aug | 2021 | 0.0019977 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2021-08-14 11:03 | 2021-08-14 14:43 | 4 | 003:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BARRAS DE PEDESTAL | C21081200101 | New_Event | Secondary Wire Down | Include | Include | Equipment | 220 | 2021-08-14 | 880 | keep | 0 | Aug | 2021 | 0.00059936 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-08-14 11:25 | 2021-08-14 15:57 | 10 | 004:32 | P | ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA RETIRAR POSTE VACANTE | S21081400031 | New_Event | Defective Pole | Include | Include | Equipment | 272 | 2021-08-14 | 2720 | keep | 0 | Aug | 2021 | 0.0018526 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-08-14 11:36 | 2021-08-14 20:41 | 20 | 009:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21081400038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 545 | 2021-08-14 | 10900 | keep | 0 | Aug | 2021 | 0.0074239 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-08-14 11:49 | 2021-08-14 16:25 | 15 | 004:36 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S21081400003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 276 | 2021-08-14 | 4140 | keep | 0 | Aug | 2021 | 0.0028197 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-08-14 11:54 | 2021-08-14 15:00 | 20 | 003:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21081400050 | New_Event | Bad Weather | Include | Include | Weather | 186 | 2021-08-14 | 3720 | keep | 0 | Aug | 2021 | 0.0025337 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-08-14 12:06 | 2021-08-14 14:21 | 75 | 002:15 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081400046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2021-08-14 | 10125 | keep | 0 | Aug | 2021 | 0.0068961 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-08-14 12:19 | 2021-08-14 17:55 | 25 | 005:36 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | S21081400043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 336 | 2021-08-14 | 8400 | keep | 0 | Aug | 2021 | 0.0057212 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-08-14 12:25 | 2021-08-15 11:07 | 1 | 022:42 | P | NO SE REPORTO CAUSA | 1 X 150 EN SU-6 | S21081400045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1362 | 2021-08-14 | 1362 | keep | 0 | Aug | 2021 | 0.00092765 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-08-14 13:05 | 2021-08-14 17:30 | 50 | 004:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | A21081400052 | New_Event | Bad Weather | Include | Include | Weather | 265 | 2021-08-14 | 13250 | keep | 0 | Aug | 2021 | 0.0090245 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-14 13:07 | 2021-08-14 18:32 | 10 | 005:25 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21081400053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 325 | 2021-08-14 | 3250 | keep | 0 | Aug | 2021 | 0.0022136 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-08-14 13:26 | 2021-08-14 15:16 | 35 | 001:50 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21081400052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 110 | 2021-08-14 | 3850 | keep | 0 | Aug | 2021 | 0.0026222 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
SAN JUAN | 2021-08-14 14:01 | 2021-08-14 14:02 | 1021 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21081400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-14 | 1021 | keep | 0 | Aug | 2021 | 0.0006954 | 0.0006954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1021
HUMACAO | 2021-08-14 14:07 | 2021-08-14 15:52 | 10 | 001:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR REMPLAZO BAJANTE SECUNDARIO | C21081400065 | New_Event | Secondary Wire Down | Include | Include | Equipment | 105 | 2021-08-14 | 1050 | keep | 0 | Aug | 2021 | 0.00071515 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-08-14 14:08 | 2021-08-14 17:48 | 80 | 003:40 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S21081400059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 220 | 2021-08-14 | 17600 | keep | 0 | Aug | 2021 | 0.011987 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
AGUADILLA | 2021-08-14 14:19 | 2021-08-14 17:26 | 150 | 003:07 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21081400061 | New_Event | Bad Weather | Include | Include | Weather | 187 | 2021-08-14 | 28050 | keep | 0 | Aug | 2021 | 0.019105 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-08-14 14:57 | 2021-08-14 16:24 | 40 | 001:27 | P | NO SE REPORTO CAUSA | 1 X 150 EN SU | B21081500102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2021-08-14 | 3480 | keep | 0 | Aug | 2021 | 0.0023702 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-14 15:05 | 2021-08-15 14:27 | 100 | 023:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M21081400079 | New_Event | Cutout Failure | Include | Include | Equipment | 1402 | 2021-08-14 | 140200 | keep | 0 | Aug | 2021 | 0.09549 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-08-14 15:17 | 2021-08-14 18:45 | 8 | 003:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REEMPLAZAR PEDESTAL | R21081100055 | New_Event | Secondary Wire Down | Include | Include | Equipment | 208 | 2021-08-14 | 1664 | keep | 0 | Aug | 2021 | 0.0011333 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-08-14 15:35 | 2021-08-14 15:36 | 3046 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | R21081400000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2021-08-14 | 3046 | keep | 0 | Aug | 2021 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
CAGUAS | 2021-08-14 15:35 | 2021-08-14 15:38 | 1001 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C21081400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-08-14 | 3003 | keep | 0 | Aug | 2021 | 0.0020453 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
SAN JUAN | 2021-08-14 15:36 | 2021-08-14 15:37 | 200 | 000:01 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO | R21081400064 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-08-14 | 200 | keep | 0 | Aug | 2021 | 0.00013622 | 0.00013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2021-08-14 15:37 | 2021-08-14 15:38 | 3046 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | R21081400000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-08-14 | 3046 | keep | 0 | Aug | 2021 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
SAN JUAN | 2021-08-14 15:38 | 2021-08-14 16:48 | 200 | 001:10 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO | R21081400064 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 70 | 2021-08-14 | 14000 | keep | 0 | Aug | 2021 | 0.0095353 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2021-08-14 15:44 | 2021-08-14 15:46 | 1001 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C21081400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-14 | 2002 | keep | 0 | Aug | 2021 | 0.0013636 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
MAYAGÃœEZ | 2021-08-14 15:50 | 2021-08-14 18:00 | 300 | 002:10 | P | TRANSFORMADOR AVERIADO | SE ABRIO CORTE DE LINEA AUTORIZADO POR ING LUIS FENEQUE PARA REMPLAZAR TRANSFORMADOR AVERIADO POR MISMA CAPACIDAD 25KVA MARCA ERM CO #SERIE 82011973250 2.4KV 240/120V | M21081400034 | Additional_clients | Service Transformer Failure | Include | Include | Equipment | 130 | 2021-08-14 | 39000 | keep | 0 | Aug | 2021 | 0.026563 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-14 15:57 | 2021-08-14 15:58 | 2402 | 000:01 | T | ESTRUCTURA AVERIADA | RECERRO | S21081400000 | Additional_clients | Defective Pole | Include | Include | Equipment | 1 | 2021-08-14 | 2402 | keep | 0 | Aug | 2021 | 0.001636 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-14 15:58 | 2021-08-15 08:51 | 40 | 016:53 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | S21081400092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1013 | 2021-08-14 | 40520 | keep | 0 | Aug | 2021 | 0.027598 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-08-14 15:58 | 2021-08-14 16:39 | 10 | 000:41 | P | ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA RETIRAR POSTE VACANTE | S21081400031 | 1st_after_momentary | Defective Pole | Include | Include | Equipment | 41 | 2021-08-14 | 410 | keep | 0 | Aug | 2021 | 0.00027925 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-08-14 16:00 | 2021-08-14 16:34 | 50 | 000:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | R21081400067 | New_Event | Bad Weather | Include | Include | Weather | 34 | 2021-08-14 | 1700 | keep | 0 | Aug | 2021 | 0.0011579 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-08-14 16:04 | 2021-08-14 18:21 | 8 | 002:17 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BARRA DE PEDESTAL | C21081400071 | New_Event | Secondary Wire Down | Include | Include | Equipment | 137 | 2021-08-14 | 1096 | keep | 0 | Aug | 2021 | 0.00074648 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-08-14 16:16 | 2021-08-14 19:15 | 12 | 002:59 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 10 EN TRANSFORMADOR MAL TIEMPO | A21081400071 | New_Event | Bad Weather | Include | Include | Weather | 179 | 2021-08-14 | 2148 | keep | 0 | Aug | 2021 | 0.001463 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2021-08-14 16:19 | 2021-08-14 17:50 | 10 | 001:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN CORTE DE LINEA MAL TIEMPO | A21081400072 | New_Event | Bad Weather | Include | Include | Weather | 91 | 2021-08-14 | 910 | keep | 0 | Aug | 2021 | 0.0006198 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
AGUADILLA | 2021-08-14 16:24 | 2021-08-15 13:56 | 30 | 021:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081400091 | New_Event | Bad Weather | Include | Include | Weather | 1292 | 2021-08-14 | 38760 | keep | 0 | Aug | 2021 | 0.026399 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
YAUCO | 2021-08-14 16:42 | 2021-08-14 19:10 | 8 | 002:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR LINEA SECUNDARIA CRUZADA | P21081400058 | New_Event | Secondary Wire Down | Include | Include | Equipment | 148 | 2021-08-14 | 1184 | keep | 0 | Aug | 2021 | 0.00080642 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
ARECIBO | 2021-08-14 16:44 | 2021-08-14 22:00 | 35 | 005:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21081400086 | New_Event | Bad Weather | Include | Include | Weather | 316 | 2021-08-14 | 11060 | keep | 0 | Aug | 2021 | 0.0075329 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
HUMACAO | 2021-08-14 16:46 | 2021-08-14 18:29 | 8 | 001:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21081400077 | New_Event | Bad Weather | Include | Include | Weather | 103 | 2021-08-14 | 824 | keep | 0 | Aug | 2021 | 0.00056122 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-08-14 16:47 | 2021-08-14 16:48 | 3387 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21081400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-14 | 3387 | keep | 0 | Aug | 2021 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
SAN JUAN | 2021-08-14 16:48 | 2021-08-14 17:07 | 3046 | 000:19 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA REEMPLAZAR MACHETE QUEMADO EN EL TRONCAL | R21081400064 | Additional_clients | Switch Failure | Include | Include | Equipment | 19 | 2021-08-14 | 57874 | keep | 0 | Aug | 2021 | 0.039418 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-08-14 16:58 | 2021-08-14 17:19 | 15 | 000:21 | P | DESGANCHE | SE REALIZO DESGANCHE | S21081400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 21 | 2021-08-14 | 315 | keep | 0 | Aug | 2021 | 0.00021455 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-08-14 17:02 | 2021-08-14 19:01 | 12 | 001:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21081400225 | New_Event | Secondary Wire Down | Include | Include | Equipment | 119 | 2021-08-14 | 1428 | keep | 0 | Aug | 2021 | 0.0009726 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2021-08-14 17:21 | 2021-08-14 18:22 | 2216 | 001:01 | T | RELEVO DE CARGA POR CONTINGENCIA | SOBRE CARGA LINEA 2200 | B21081400237 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 61 | 2021-08-14 | 135176 | keep | 0 | Aug | 2021 | 0.092068 | 0.0015093 | Sustained | FALSE | TRUE | Not_TMED_Event | 2216
CAGUAS | 2021-08-14 17:22 | 2021-08-14 18:26 | 200 | 001:04 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C21081400079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 64 | 2021-08-14 | 12800 | keep | 0 | Aug | 2021 | 0.008718 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
VEGA BAJA | 2021-08-14 17:22 | 2021-08-14 18:23 | 4027 | 001:01 | T | RELEVO DE CARGA POR CONTINGENCIA | SOBRE CARGA LINEA 2200 | B21081400238 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 61 | 2021-08-14 | 245647 | keep | 0 | Aug | 2021 | 0.16731 | 0.0027428 | Sustained | FALSE | TRUE | Not_TMED_Event | 4027
AGUADILLA | 2021-08-14 17:26 | 2021-08-15 00:20 | 200 | 006:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 Y 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21081400067 | New_Event | Wire Down | Include | Include | Equipment | 414 | 2021-08-14 | 82800 | keep | 0 | Aug | 2021 | 0.056395 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-08-14 17:30 | 2021-08-14 17:31 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21081400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-14 | 393 | keep | 0 | Aug | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2021-08-14 17:30 | 2021-08-14 17:31 | 4 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6007-04 QUE LLEVA LA CARGA DEL 6007-05 | M21081400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-14 | 4 | keep | 0 | Aug | 2021 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-08-14 17:32 | 2021-08-14 19:23 | 50 | 001:51 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21081400078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2021-08-14 | 5550 | keep | 0 | Aug | 2021 | 0.0037801 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-14 17:40 | 2021-08-14 22:00 | 60 | 004:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21081400080 | New_Event | Bad Weather | Include | Include | Weather | 260 | 2021-08-14 | 15600 | keep | 0 | Aug | 2021 | 0.010625 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-08-14 17:44 | 2021-08-16 12:34 | 10 | 042:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO BAJANTE SECUNDARIO | S21081400080 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2570 | 2021-08-14 | 25700 | keep | 0 | Aug | 2021 | 0.017504 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-08-14 17:44 | 2021-08-15 10:57 | 10 | 017:13 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M21081400106 | New_Event | Bad Weather | Include | Include | Weather | 1033 | 2021-08-14 | 10330 | keep | 0 | Aug | 2021 | 0.0070357 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-08-14 17:57 | 2021-08-14 18:37 | 1000 | 000:40 | P | DESCONECTIVO DEFECTUOSO | MACHETE QUEMADO SE ABRIO MACHETES ANTERIORES PARA REMPLAZARLOS | M21081400109 | New_Event | Switch Failure | Include | Include | Equipment | 40 | 2021-08-14 | 40000 | keep | 0 | Aug | 2021 | 0.027244 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
VEGA BAJA | 2021-08-14 17:58 | 2021-08-14 22:00 | 50 | 004:02 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21081400263 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 242 | 2021-08-14 | 12100 | keep | 0 | Aug | 2021 | 0.0082413 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-14 18:30 | 2021-08-15 16:48 | 50 | 022:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21081400113 | New_Event | Bad Weather | Include | Include | Weather | 1338 | 2021-08-14 | 66900 | keep | 0 | Aug | 2021 | 0.045565 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-14 18:37 | 2021-08-14 18:38 | 4664 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DE INTERRUPTOR | M21081400113 | Additional_clients | Switch Failure | Include | Include | Equipment | 1 | 2021-08-14 | 4664 | keep | 0 | Aug | 2021 | 0.0031766 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-14 18:38 | 2021-08-15 14:00 | 1000 | 019:22 | P | DESCONECTIVO DEFECTUOSO | MACHETE QUEMADO SE ABRIO MACHETES ANTERIORES PARA REMPLAZARLOS | M21081400109 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1162 | 2021-08-14 | 1162000 | keep | 0 | Aug | 2021 | 0.79143 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
CAGUAS | 2021-08-14 18:54 | 2021-08-15 14:39 | 50 | 019:45 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA REEMPLAZO PARARRAYO | C21081400091 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1185 | 2021-08-14 | 59250 | keep | 0 | Aug | 2021 | 0.040355 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-14 19:02 | 2021-08-15 12:36 | 2500 | 017:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO EN EL TRONCAL DEL ALIMENTADOR 6008-05 QUE ESTA LLEVANDO LA CARGA DEL 6008-04 | M21081400121 | New_Event | Wire Down | Include | Include | Equipment | 1054 | 2021-08-14 | 2635000 | keep | 0 | Aug | 2021 | 1.7947 | 0.0017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 2500
MAYAGÃœEZ | 2021-08-14 19:02 | 2021-08-15 12:36 | 150 | 017:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO 3 PUENTES PRIMARIOS EN EL TRONCAL DEL ALIMENTADOR | M21081400121 | New_Event | Wire Down | Include | Include | Equipment | 1054 | 2021-08-14 | 158100 | keep | 0 | Aug | 2021 | 0.10768 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2021-08-14 19:33 | 2021-08-14 19:49 | 1 | 000:16 | P | NO SE REPORTO CAUSA | 1 X 10 EN MONTURA DE TRANSFORMADORES | B21081400304 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 16 | 2021-08-14 | 16 | keep | 0 | Aug | 2021 | 1.0898e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-08-14 19:34 | 2021-08-15 11:05 | 20 | 015:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M21081400140 | New_Event | Secondary Wire Down | Include | Include | Equipment | 931 | 2021-08-14 | 18620 | keep | 0 | Aug | 2021 | 0.012682 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-08-14 20:05 | 2021-08-15 11:56 | 8 | 015:51 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZO DE BARRA EN PEDESTAL | C21081400099 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 951 | 2021-08-14 | 7608 | keep | 0 | Aug | 2021 | 0.0051818 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-08-14 20:38 | 2021-08-15 09:00 | 50 | 012:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | S21081400318 | New_Event | Vegetation Contact | Include | Include | Vegetation | 742 | 2021-08-14 | 37100 | keep | 0 | Aug | 2021 | 0.025269 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-14 20:45 | 2021-08-15 16:35 | 12 | 019:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B21081400319 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1190 | 2021-08-14 | 14280 | keep | 0 | Aug | 2021 | 0.009726 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-08-14 20:56 | 2021-08-15 01:30 | 190 | 004:34 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | R21081400090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 274 | 2021-08-14 | 52060 | keep | 0 | Aug | 2021 | 0.035458 | 0.00012941 | Sustained | FALSE | TRUE | Not_TMED_Event | 190
HUMACAO | 2021-08-14 21:17 | 2021-08-15 10:38 | 7 | 013:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA REEMPLAZO DE BAJANTE SECUNDARIO | C21081400106 | New_Event | Secondary Wire Down | Include | Include | Equipment | 801 | 2021-08-14 | 5607 | keep | 0 | Aug | 2021 | 0.0038189 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-08-14 21:23 | 2021-08-15 09:50 | 80 | 012:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | A21081400106 | New_Event | Bad Weather | Include | Include | Weather | 747 | 2021-08-14 | 59760 | keep | 0 | Aug | 2021 | 0.040702 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
AGUADILLA | 2021-08-14 21:35 | 2021-08-15 14:14 | 150 | 016:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21081400166 | New_Event | Bad Weather | Include | Include | Weather | 999 | 2021-08-14 | 149850 | keep | 0 | Aug | 2021 | 0.10206 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-08-14 21:46 | 2021-08-15 10:51 | 125 | 013:05 | P | DESGANCHE | 1 X 50 Y 1 X 20 EN CORTES DE LINEA SE DESGANCHO BAMBUA | C21081400110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 785 | 2021-08-14 | 98125 | keep | 0 | Aug | 2021 | 0.066832 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
BARRANQUITAS | 2021-08-14 22:04 | 2021-08-15 11:37 | 64 | 013:33 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | C21081400112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 813 | 2021-08-14 | 52032 | keep | 0 | Aug | 2021 | 0.035439 | 4.359e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 64
VEGA BAJA | 2021-08-14 22:10 | 2021-08-15 08:08 | 75 | 009:58 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21081400336 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 598 | 2021-08-14 | 44850 | keep | 0 | Aug | 2021 | 0.030547 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
AGUADILLA | 2021-08-14 22:23 | 2021-08-15 18:00 | 200 | 019:37 | P | ESTRUCTURA AVERIADA | 2 X 100 EN CORTE DE LINEA SE SECCIONALIZO POSTE PARTIDO EN LA PERILLA | M21081400171 | New_Event | Defective Pole | Include | Include | Equipment | 1177 | 2021-08-14 | 235400 | keep | 0 | Aug | 2021 | 0.16033 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-08-14 22:34 | 2021-08-15 10:30 | 150 | 011:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | A21081400112 | New_Event | Bad Weather | Include | Include | Weather | 716 | 2021-08-14 | 107400 | keep | 0 | Aug | 2021 | 0.07315 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-08-14 22:59 | 2021-08-15 09:47 | 150 | 010:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | A21081400116 | New_Event | Bad Weather | Include | Include | Weather | 648 | 2021-08-14 | 97200 | keep | 0 | Aug | 2021 | 0.066202 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-08-14 23:09 | 2021-08-15 13:35 | 28 | 014:26 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA | C21081400115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 866 | 2021-08-14 | 24248 | keep | 0 | Aug | 2021 | 0.016515 | 1.9071e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 28
SAN JUAN | 2021-08-14 23:40 | 2021-08-14 23:47 | 137 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 Y LA CERRARON PERO TIENE PUENTE ABIERTO | S21081400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-08-14 | 959 | keep | 0 | Aug | 2021 | 0.00065317 | 9.331e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 137
SAN JUAN | 2021-08-14 23:40 | 2021-08-14 23:47 | 457 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 Y LA CERRARON PERO TIENE PUENTE ABIERTO | S21081400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-08-14 | 3199 | keep | 0 | Aug | 2021 | 0.0021788 | 0.00031126 | Sustained | FALSE | TRUE | Not_TMED_Event | 457
SAN JUAN | 2021-08-14 23:40 | 2021-08-14 23:47 | 1225 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 Y LA CERRARON PERO TIENE PUENTE ABIERTO | S21081400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-08-14 | 8575 | keep | 0 | Aug | 2021 | 0.0058404 | 0.00083434 | Sustained | FALSE | TRUE | Not_TMED_Event | 1225
SAN JUAN | 2021-08-14 23:40 | 2021-08-14 23:47 | 1452 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 Y LA CERRARON PERO TIENE PUENTE ABIERTO | S21081400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-08-14 | 10164 | keep | 0 | Aug | 2021 | 0.0069227 | 0.00098895 | Sustained | FALSE | TRUE | Not_TMED_Event | 1452
SAN JUAN | 2021-08-14 23:40 | 2021-08-14 23:47 | 616 | 000:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 Y LA CERRARON PERO TIENE PUENTE ABIERTO | S21081400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2021-08-14 | 4312 | keep | 0 | Aug | 2021 | 0.0029369 | 0.00041955 | Sustained | FALSE | TRUE | Not_TMED_Event | 616
SAN JUAN | 2021-08-14 23:40 | 2021-08-15 12:24 | 3492 | 012:44 | P | LINEA DE TRANSMISION 38KV | SE REPARO PUENTE ABIERTO EN LINEA 3600 | S21081400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 764 | 2021-08-14 | 2667888 | keep | 0 | Aug | 2021 | 1.8171 | 0.0023784 | Sustained | FALSE | TRUE | Not_TMED_Event | 3492
CAGUAS | 2021-08-15 01:25 | 2021-08-15 01:26 | 1001 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C21081500000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-15 | 1001 | keep | 0 | Aug | 2021 | 0.00068178 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
CAGUAS | 2021-08-15 01:26 | 2021-08-15 13:25 | 80 | 011:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR LINEA PRIMARIA | C21081500063 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 719 | 2021-08-15 | 57520 | keep | 0 | Aug | 2021 | 0.039177 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-15 01:59 | 2021-08-15 02:00 | 1983 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1801-02 Y SE CERRO POR SCADA LLEVANDO 1711-04 | B21081500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 1983 | keep | 0 | Aug | 2021 | 0.0013506 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-08-15 01:59 | 2021-08-15 02:00 | 600 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO 1801-02 Y SE CERRO POR SCADA LLEVANDO PARTE DEL 1717-01 | B21081500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 600 | keep | 0 | Aug | 2021 | 0.00040866 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
BAYAMON | 2021-08-15 01:59 | 2021-08-15 02:00 | 186 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1801-02 Y SE CERRO POR SCADA LLEVANDO 1711-04 Y PARTE DEL 1717-01 | B21081500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 186 | keep | 0 | Aug | 2021 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
UTUADO | 2021-08-15 02:24 | 2021-08-15 02:25 | 1241 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO SE REPORTO CAUSA | A21081500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 1241 | keep | 0 | Aug | 2021 | 0.00084524 | 0.00084524 | Momentary | FALSE | FALSE | Not_TMED_Event | 1241
CANOVANAS | 2021-08-15 04:10 | 2021-08-15 04:11 | 2106 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | R21081500000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-08-15 | 2106 | keep | 0 | Aug | 2021 | 0.0014344 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
CANOVANAS | 2021-08-15 04:11 | 2021-08-15 10:30 | 50 | 006:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA Y 1 X 20 EN RISER MAL TIEMPO | R21081500006 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 379 | 2021-08-15 | 18950 | keep | 0 | Aug | 2021 | 0.012907 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-15 06:00 | 2021-08-15 14:55 | 5 | 008:55 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA PROLEC GE M20I10290 7,620/13200 | A21081500000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 535 | 2021-08-15 | 2675 | keep | 0 | Aug | 2021 | 0.0018219 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-08-15 06:20 | 2021-08-15 06:21 | 271 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21081500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 271 | keep | 0 | Aug | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
BAYAMON | 2021-08-15 06:28 | 2021-08-15 09:53 | 2234 | 003:25 | T | DESGANCHE | SE SECCIONALIZO ALIMENTADOR | B21081500018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2021-08-15 | 457970 | keep | 0 | Aug | 2021 | 0.31192 | 0.0015216 | Sustained | FALSE | FALSE | Not_TMED_Event | 2234
MAYAGÃœEZ | 2021-08-15 06:31 | 2021-08-15 06:32 | 108 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR | M21081500000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-08-15 | 108 | keep | 0 | Aug | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
HUMACAO | 2021-08-15 06:45 | 2021-08-15 06:46 | 2450 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C21081500015 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-08-15 | 2450 | keep | 0 | Aug | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2021-08-15 06:46 | 2021-08-15 11:53 | 333 | 005:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21081500033 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 307 | 2021-08-15 | 102231 | keep | 0 | Aug | 2021 | 0.069629 | 0.0002268 | Sustained | FALSE | TRUE | Not_TMED_Event | 333
YAUCO | 2021-08-15 07:17 | 2021-08-15 11:41 | 45 | 004:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 30 EN CORTE DE LINEA POR IGUANA | P21081500005 | New_Event |  |  | Include | Wildlife | 264 | 2021-08-15 | 11880 | keep | 0 | Aug | 2021 | 0.0080914 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BAYAMON | 2021-08-15 07:31 | 2021-08-15 07:32 | 5961 | 000:01 | T | DESGANCHE | RECERRO | B21081500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-15 | 5961 | keep | 0 | Aug | 2021 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2021-08-15 07:32 | 2021-08-15 19:05 | 60 | 011:33 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21081500123 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 693 | 2021-08-15 | 41580 | keep | 0 | Aug | 2021 | 0.02832 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
PONCE | 2021-08-15 07:34 | 2021-08-15 13:13 | 50 | 005:39 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21081500004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 339 | 2021-08-15 | 16950 | keep | 0 | Aug | 2021 | 0.011545 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-08-15 07:43 | 2021-08-15 07:44 | 215 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210815000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 215 | keep | 0 | Aug | 2021 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
BARRANQUITAS | 2021-08-15 07:58 | 2021-08-15 07:59 | 2635 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6500 DE BARRANQUITAS A TORO NEGRO | C21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 2635 | keep | 0 | Aug | 2021 | 0.0017947 | 0.0017947 | Momentary | FALSE | TRUE | Not_TMED_Event | 2635
BARRANQUITAS | 2021-08-15 07:58 | 2021-08-15 07:59 | 2280 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6500 DE BARRANQUITAS A TORO NEGRO | C21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 2280 | keep | 0 | Aug | 2021 | 0.0015529 | 0.0015529 | Momentary | FALSE | TRUE | Not_TMED_Event | 2280
BARRANQUITAS | 2021-08-15 07:58 | 2021-08-15 07:59 | 1617 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6500 DE BARRANQUITAS A TORO NEGRO | C21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 1617 | keep | 0 | Aug | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | TRUE | Not_TMED_Event | 1617
CAGUAS | 2021-08-15 08:22 | 2021-08-15 10:46 | 12 | 002:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA MAL TIEMPO | C21081500002 | New_Event | Bad Weather | Include | Include | Weather | 144 | 2021-08-15 | 1728 | keep | 0 | Aug | 2021 | 0.0011769 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
BAYAMON | 2021-08-15 08:27 | 2021-08-15 08:28 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21081500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 1310 | keep | 0 | Aug | 2021 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2021-08-15 08:38 | 2021-08-15 09:35 | 641 | 000:57 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1105-02 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1105-01, 1133-04 | S21081500065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2021-08-15 | 36537 | keep | 0 | Aug | 2021 | 0.024885 | 0.00043658 | Sustained | FALSE | FALSE | Not_TMED_Event | 641
BAYAMON | 2021-08-15 08:38 | 2021-08-15 09:35 | 308 | 000:57 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1105-02 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1105-01, 1133-04 | S21081500065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2021-08-15 | 17556 | keep | 0 | Aug | 2021 | 0.011957 | 0.00020978 | Sustained | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2021-08-15 08:38 | 2021-08-15 11:16 | 333 | 002:38 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1105-02 QUE A SU VEZ LLEVA LA CARGA DE LOS ALIMENTADORES 1105-01, 1133-04 SE REALIZARON OPERACIONES DE CAMPO Y SE CERRO AMARRRE CONTRA 1133-04 ENTRA UN 95% | S21081500065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2021-08-15 | 52614 | keep | 0 | Aug | 2021 | 0.035835 | 0.0002268 | Sustained | FALSE | FALSE | Not_TMED_Event | 333
VEGA BAJA | 2021-08-15 08:44 | 2021-08-15 08:45 | 2216 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21081500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 2216 | keep | 0 | Aug | 2021 | 0.0015093 | 0.0015093 | Momentary | FALSE | FALSE | Not_TMED_Event | 2216
PONCE | 2021-08-15 08:56 | 2021-08-15 10:54 | 60 | 001:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA Y 1 X 25 EN TRANSFORMADOR POR CAJA PRIMARIA QUEMADA | P21081500008 | New_Event | Cutout Failure | Include | Include | Equipment | 118 | 2021-08-15 | 7080 | keep | 0 | Aug | 2021 | 0.0048222 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
VEGA BAJA | 2021-08-15 09:01 | 2021-08-15 09:02 | 3000 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 3000 | keep | 0 | Aug | 2021 | 0.0020433 | 0.0020433 | Momentary | FALSE | TRUE | Not_TMED_Event | 3000
VEGA BAJA | 2021-08-15 09:01 | 2021-08-15 09:02 | 908 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 908 | keep | 0 | Aug | 2021 | 0.00061843 | 0.00061843 | Momentary | FALSE | TRUE | Not_TMED_Event | 908
VEGA BAJA | 2021-08-15 09:01 | 2021-08-15 09:02 | 3332 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 3332 | keep | 0 | Aug | 2021 | 0.0022694 | 0.0022694 | Momentary | FALSE | TRUE | Not_TMED_Event | 3332
VEGA BAJA | 2021-08-15 09:01 | 2021-08-15 09:02 | 2610 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 2610 | keep | 0 | Aug | 2021 | 0.0017777 | 0.0017777 | Momentary | FALSE | TRUE | Not_TMED_Event | 2610
VEGA BAJA | 2021-08-15 09:01 | 2021-08-15 09:02 | 3076 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 3076 | keep | 0 | Aug | 2021 | 0.002095 | 0.002095 | Momentary | FALSE | TRUE | Not_TMED_Event | 3076
VEGA BAJA | 2021-08-15 09:02 | 2021-08-15 13:11 | 15 | 004:09 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21081400337 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 249 | 2021-08-15 | 3735 | keep | 0 | Aug | 2021 | 0.0025439 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-08-15 09:05 | 2021-08-15 12:24 | 137 | 003:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21081400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 199 | 2021-08-15 | 27263 | keep | 0 | Aug | 2021 | 0.018569 | 9.331e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 137
SAN JUAN | 2021-08-15 09:05 | 2021-08-15 12:24 | 457 | 003:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21081400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 199 | 2021-08-15 | 90943 | keep | 0 | Aug | 2021 | 0.061941 | 0.00031126 | Sustained | FALSE | TRUE | Not_TMED_Event | 457
SAN JUAN | 2021-08-15 09:05 | 2021-08-15 12:24 | 1225 | 003:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S21081400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 199 | 2021-08-15 | 243775 | keep | 0 | Aug | 2021 | 0.16603 | 0.00083434 | Sustained | FALSE | TRUE | Not_TMED_Event | 1225
HUMACAO | 2021-08-15 09:07 | 2021-08-15 10:14 | 11 | 001:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO BAJANTE SECUNDARIO Y SE BAJO TAP DEL 4 AL 3 124 VOLTIOS POR FASE | C21081400076 | New_Event | Secondary Wire Down | Include | Include | Equipment | 67 | 2021-08-15 | 737 | keep | 0 | Aug | 2021 | 0.00050197 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
PONCE | 2021-08-15 09:07 | 2021-08-16 09:08 | 537 | 024:01 | T | NO SE REPORTO CAUSA | SE CERRO BRAKER | P21081500075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1441 | 2021-08-15 | 773817 | keep | 0 | Aug | 2021 | 0.52704 | 0.00036575 | Sustained | FALSE | FALSE | Not_TMED_Event | 537
VEGA BAJA | 2021-08-15 09:13 | 2021-08-15 09:14 | 1000 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21081500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 1000 | keep | 0 | Aug | 2021 | 0.0006811 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
BAYAMON | 2021-08-15 09:19 | 2021-08-15 15:40 | 20 | 006:21 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S21081500028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 381 | 2021-08-15 | 7620 | keep | 0 | Aug | 2021 | 0.0051899 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-08-15 09:19 | 2021-08-15 12:33 | 75 | 003:14 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO | S21081500019 | New_Event | Switch Failure | Include | Include | Equipment | 194 | 2021-08-15 | 14550 | keep | 0 | Aug | 2021 | 0.0099099 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2021-08-15 09:19 | 2021-08-15 11:05 | 65 | 001:46 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR | B21081500015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2021-08-15 | 6890 | keep | 0 | Aug | 2021 | 0.0046927 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
HUMACAO | 2021-08-15 09:19 | 2021-08-15 16:27 | 10 | 007:08 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR | C21081500008 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 428 | 2021-08-15 | 4280 | keep | 0 | Aug | 2021 | 0.0029151 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-08-15 09:19 | 2021-08-15 14:45 | 60 | 005:26 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21051500016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 326 | 2021-08-15 | 19560 | keep | 0 | Aug | 2021 | 0.013322 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-08-15 09:19 | 2021-08-15 15:13 | 75 | 005:54 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081500003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 354 | 2021-08-15 | 26550 | keep | 0 | Aug | 2021 | 0.018083 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
CANOVANAS | 2021-08-15 09:33 | 2021-08-15 10:33 | 6 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA AJUSTAR BUSHING DEL NEUTRAL Y REPARAR BAJANTE SECUNDARIO | R21081300013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2021-08-15 | 360 | keep | 0 | Aug | 2021 | 0.00024519 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-08-15 09:34 | 2021-08-15 15:08 | 45 | 005:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO CAJA PRIMARIA DEFECTUOSA, NO FUNDIO FUSIBLE | C21081500017 | New_Event | Cutout Failure | Include | Include | Equipment | 334 | 2021-08-15 | 15030 | keep | 0 | Aug | 2021 | 0.010237 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2021-08-15 09:34 | 2021-08-16 11:20 | 70 | 025:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA | M21081500028 | New_Event | Bad Weather | Include | Include | Weather | 1546 | 2021-08-15 | 108220 | keep | 0 | Aug | 2021 | 0.073708 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-08-15 09:34 | 2021-08-15 17:40 | 50 | 008:06 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21081500026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 486 | 2021-08-15 | 24300 | keep | 0 | Aug | 2021 | 0.016551 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-08-15 09:34 | 2021-08-16 19:12 | 25 | 033:38 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE DE METAL 45 PIES Y SE CERRO CORTE DE LINEA | M21081500013 | New_Event | Defective Pole | Include | Include | Equipment | 2018 | 2021-08-15 | 50450 | keep | 0 | Aug | 2021 | 0.034361 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-08-15 09:34 | 2021-08-15 15:10 | 50 | 005:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21081500024 | New_Event | Bad Weather | Include | Include | Weather | 336 | 2021-08-15 | 16800 | keep | 0 | Aug | 2021 | 0.011442 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-15 09:34 | 2021-08-15 20:27 | 40 | 010:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21081500008 | New_Event | Bad Weather | Include | Include | Weather | 653 | 2021-08-15 | 26120 | keep | 0 | Aug | 2021 | 0.01779 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-08-15 09:42 | 2021-08-15 13:55 | 50 | 004:13 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE DESGANCHO | B21081500032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 253 | 2021-08-15 | 12650 | keep | 0 | Aug | 2021 | 0.0086159 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-15 09:48 | 2021-08-15 18:50 | 50 | 009:02 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | A21081500011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 542 | 2021-08-15 | 27100 | keep | 0 | Aug | 2021 | 0.018458 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-15 09:53 | 2021-08-15 11:14 | 1100 | 001:21 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETES | B21081500018 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 81 | 2021-08-15 | 89100 | keep | 0 | Aug | 2021 | 0.060686 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-08-15 10:04 | 2021-08-15 12:58 | 80 | 002:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA LEVANTO NEUTRAL PRIMARIO | R21081500013 | New_Event | Wire Down | Include | Include | Equipment | 174 | 2021-08-15 | 13920 | keep | 0 | Aug | 2021 | 0.0094808 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-08-15 10:11 | 2021-08-15 17:00 | 1011 | 006:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21081500016 | New_Event | Bad Weather | Include | Include | Weather | 409 | 2021-08-15 | 413499 | keep | 0 | Aug | 2021 | 0.28163 | 0.00068859 | Sustained | FALSE | TRUE | Not_TMED_Event | 1011
UTUADO | 2021-08-15 10:17 | 2021-08-16 21:48 | 20 | 035:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21081500018 | New_Event | Bad Weather | Include | Include | Weather | 2131 | 2021-08-15 | 42620 | keep | 0 | Aug | 2021 | 0.029028 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-08-15 10:20 | 2021-08-15 12:33 | 55 | 002:13 | P | ESTRUCTURA AVERIADA | SE SECCIONALIZO POSTE AVERIADO Y SE RESTABLECIO SERVICIO | S21081500073 | New_Event | Defective Pole | Include | Include | Equipment | 133 | 2021-08-15 | 7315 | keep | 0 | Aug | 2021 | 0.0049822 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
SAN JUAN | 2021-08-15 10:26 | 2021-08-16 13:29 | 25 | 027:03 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21081500074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1623 | 2021-08-15 | 40575 | keep | 0 | Aug | 2021 | 0.027635 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
HUMACAO | 2021-08-15 10:41 | 2021-08-15 17:20 | 30 | 006:39 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21081500035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 399 | 2021-08-15 | 11970 | keep | 0 | Aug | 2021 | 0.0081527 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
VEGA BAJA | 2021-08-15 10:43 | 2021-08-15 16:52 | 40 | 006:09 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081500132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 369 | 2021-08-15 | 14760 | keep | 0 | Aug | 2021 | 0.010053 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-08-15 10:45 | 2021-08-15 15:53 | 10 | 005:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A21081500022 | New_Event | Bad Weather | Include | Include | Weather | 308 | 2021-08-15 | 3080 | keep | 0 | Aug | 2021 | 0.0020978 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BARRANQUITAS | 2021-08-15 10:52 | 2021-08-15 14:06 | 100 | 003:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | C21081500036 | New_Event | Bad Weather | Include | Include | Weather | 194 | 2021-08-15 | 19400 | keep | 0 | Aug | 2021 | 0.013213 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
FAJARDO | 2021-08-15 10:58 | 2021-08-15 13:19 | 20 | 002:21 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | R21081500016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2021-08-15 | 2820 | keep | 0 | Aug | 2021 | 0.0019207 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-08-15 11:16 | 2021-08-15 12:01 | 85 | 000:45 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE REEMPLAZARON 60 PIES DE LINEA PRIMARIA | S21081500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 45 | 2021-08-15 | 3825 | keep | 0 | Aug | 2021 | 0.0026052 | 5.7893e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 85
BAYAMON | 2021-08-15 11:20 | 2021-08-15 13:23 | 80 | 002:03 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081500017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2021-08-15 | 9840 | keep | 0 | Aug | 2021 | 0.006702 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-15 11:22 | 2021-08-15 13:23 | 40 | 002:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21081500087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2021-08-15 | 4840 | keep | 0 | Aug | 2021 | 0.0032965 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-08-15 11:24 | 2021-08-15 15:10 | 1 | 003:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE HACIA CAJA PRIMARIA NO FUNDIO FUSIBLE | C21081500045 | New_Event | Wire Down | Include | Include | Equipment | 226 | 2021-08-15 | 226 | keep | 0 | Aug | 2021 | 0.00015393 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-08-15 11:29 | 2021-08-15 11:30 | 3597 | 000:01 | T | DESGANCHE | RECERRO | B21081500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-15 | 3597 | keep | 0 | Aug | 2021 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2021-08-15 11:30 | 2021-08-15 14:38 | 40 | 003:08 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081500052 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 188 | 2021-08-15 | 7520 | keep | 0 | Aug | 2021 | 0.0051218 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-08-15 11:35 | 2021-08-15 14:40 | 6 | 003:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE A TRANSFORMADOR | A21081500030 | New_Event | Wire Down | Include | Include | Equipment | 185 | 2021-08-15 | 1110 | keep | 0 | Aug | 2021 | 0.00075602 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-08-15 11:39 | 2021-08-15 20:01 | 80 | 008:22 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21081500093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 502 | 2021-08-15 | 40160 | keep | 0 | Aug | 2021 | 0.027353 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-15 11:41 | 2021-08-15 11:42 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21081500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 3941 | keep | 0 | Aug | 2021 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
MAYAGÃœEZ | 2021-08-15 11:42 | 2021-08-16 17:18 | 2 | 029:36 | P | DESGANCHE | 1 X 140 EN CORT DE LINEA | M21081500058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1776 | 2021-08-15 | 3552 | keep | 0 | Aug | 2021 | 0.0024193 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
BAYAMON | 2021-08-15 11:46 | 2021-08-15 11:47 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21081500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 3941 | keep | 0 | Aug | 2021 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
SAN JUAN | 2021-08-15 11:48 | 2021-08-15 11:53 | 1825 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-08-15 | 9125 | keep | 0 | Aug | 2021 | 0.006215 | 0.001243 | Momentary | FALSE | TRUE | Not_TMED_Event | 1825
SAN JUAN | 2021-08-15 11:48 | 2021-08-15 11:53 | 47 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-08-15 | 235 | keep | 0 | Aug | 2021 | 0.00016006 | 3.2011e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 47
SAN JUAN | 2021-08-15 11:48 | 2021-08-15 11:53 | 315 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-08-15 | 1575 | keep | 0 | Aug | 2021 | 0.0010727 | 0.00021455 | Momentary | FALSE | TRUE | Not_TMED_Event | 315
SAN JUAN | 2021-08-15 11:48 | 2021-08-15 11:53 | 2 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-08-15 | 10 | keep | 0 | Aug | 2021 | 6.811e-06 | 1.3622e-06 | Momentary | FALSE | TRUE | Not_TMED_Event | 2
SAN JUAN | 2021-08-15 11:48 | 2021-08-15 11:53 | 2391 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-08-15 | 11955 | keep | 0 | Aug | 2021 | 0.0081425 | 0.0016285 | Momentary | FALSE | TRUE | Not_TMED_Event | 2391
SAN JUAN | 2021-08-15 11:48 | 2021-08-15 14:18 | 65 | 002:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21081500019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2021-08-15 | 9750 | keep | 0 | Aug | 2021 | 0.0066407 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
CAGUAS | 2021-08-15 11:48 | 2021-08-15 11:53 | 2276 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAS A MONACILLOS | C21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-08-15 | 11380 | keep | 0 | Aug | 2021 | 0.0077509 | 0.0015502 | Momentary | FALSE | TRUE | Not_TMED_Event | 2276
CAGUAS | 2021-08-15 11:48 | 2021-08-15 11:53 | 777 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAS A MONACILLOS | C21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-08-15 | 3885 | keep | 0 | Aug | 2021 | 0.0026461 | 0.00052921 | Momentary | FALSE | TRUE | Not_TMED_Event | 777
CAGUAS | 2021-08-15 11:48 | 2021-08-15 11:53 | 12 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAS A MONACILLOS | C21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-08-15 | 60 | keep | 0 | Aug | 2021 | 4.0866e-05 | 8.1731e-06 | Momentary | FALSE | TRUE | Not_TMED_Event | 12
CAGUAS | 2021-08-15 11:48 | 2021-08-15 11:53 | 1290 | 000:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAS A MONACILLOS | C21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2021-08-15 | 6450 | keep | 0 | Aug | 2021 | 0.0043931 | 0.00087861 | Momentary | FALSE | TRUE | Not_TMED_Event | 1290
YAUCO | 2021-08-15 11:51 | 2021-08-15 15:13 | 85 | 003:22 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21081500013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2021-08-15 | 17170 | keep | 0 | Aug | 2021 | 0.011694 | 5.7893e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 85
CAGUAS | 2021-08-15 11:56 | 2021-08-15 20:24 | 50 | 008:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE REPARO BAJANTE HACIA CAJA, REEMPLAZO PARARRAYO Y REALIZO DESGANCHE | C21081500056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 508 | 2021-08-15 | 25400 | keep | 0 | Aug | 2021 | 0.0173 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-15 12:01 | 2021-08-15 12:02 | 641 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1105-02 QUE A SU VEZ LLEVA LA CARGA DEL 1133-04 Y 1105-01 | S21081500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-15 | 641 | keep | 0 | Aug | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
BAYAMON | 2021-08-15 12:01 | 2021-08-15 12:02 | 308 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1105-02 QUE A SU VEZ LLEVA LA CARGA DEL 1133-04 Y 1105-01 | S21081500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-15 | 308 | keep | 0 | Aug | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2021-08-15 12:01 | 2021-08-15 12:02 | 333 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1105-02 QUE A SU VEZ LLEVA LA CARGA DEL 1133-04 Y 1105-01 | S21081500000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-15 | 333 | keep | 0 | Aug | 2021 | 0.0002268 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-15 12:02 | 2021-08-15 13:41 | 85 | 001:39 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE REEMPLAZARON 60 PIES DE LINEA PRIMARIA | S21081500000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 99 | 2021-08-15 | 8415 | keep | 0 | Aug | 2021 | 0.0057314 | 5.7893e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 85
PONCE | 2021-08-15 12:03 | 2021-08-15 13:59 | 50 | 001:56 | P | DESGANCHE | 1 POR 65 EN CORTE DE LINEA POR DESGANCHE | P21081500024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2021-08-15 | 5800 | keep | 0 | Aug | 2021 | 0.0039504 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-08-15 12:04 | 2021-08-15 14:52 | 9 | 002:48 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN BANCO DE TRANSFORMADORES DESGANCHO | R21081500021 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 168 | 2021-08-15 | 1512 | keep | 0 | Aug | 2021 | 0.0010298 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-08-15 12:12 | 2021-08-15 14:56 | 40 | 002:44 | P | NO SE REPORTO CAUSA | 1 X 150 EN SU | B21081500102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 164 | 2021-08-15 | 6560 | keep | 0 | Aug | 2021 | 0.004468 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-08-15 12:18 | 2021-08-15 15:23 | 40 | 003:05 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21081500105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 185 | 2021-08-15 | 7400 | keep | 0 | Aug | 2021 | 0.0050401 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-08-15 12:22 | 2021-08-15 15:36 | 95 | 003:14 | P | DESGANCHE | 2 X 40 EN CORTES DE LINEAS | C21081500059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2021-08-15 | 18430 | keep | 0 | Aug | 2021 | 0.012553 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
VEGA BAJA | 2021-08-15 12:26 | 2021-08-15 16:18 | 75 | 003:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE LEVANTO PRIMARIA | B21081500108 | New_Event | Wire Down | Include | Include | Equipment | 232 | 2021-08-15 | 17400 | keep | 0 | Aug | 2021 | 0.011851 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
MAYAGÃœEZ | 2021-08-15 12:36 | 2021-08-16 10:14 | 150 | 021:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081500073 | New_Event | Bad Weather | Include | Include | Weather | 1298 | 2021-08-15 | 194700 | keep | 0 | Aug | 2021 | 0.13261 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
YAUCO | 2021-08-15 12:40 | 2021-08-15 15:13 | 100 | 002:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PRIMARIA BAJITA | P21081500027 | New_Event | Wire Down | Include | Include | Equipment | 153 | 2021-08-15 | 15300 | keep | 0 | Aug | 2021 | 0.010421 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2021-08-15 12:40 | 2021-08-15 12:41 | 485 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21081500028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 485 | keep | 0 | Aug | 2021 | 0.00033033 | 0.00033033 | Momentary | FALSE | FALSE | Not_TMED_Event | 485
MAYAGÃœEZ | 2021-08-15 12:40 | 2021-08-15 12:41 | 4304 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21081500075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 4304 | keep | 0 | Aug | 2021 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
VEGA BAJA | 2021-08-15 12:41 | 2021-08-15 12:42 | 1570 | 000:01 | T | DESGANCHE | RECERRO | B21081500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-15 | 1570 | keep | 0 | Aug | 2021 | 0.0010693 | 0.0010693 | Momentary | FALSE | FALSE | Not_TMED_Event | 1570
VEGA BAJA | 2021-08-15 12:42 | 2021-08-15 18:37 | 60 | 005:55 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081500132 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 355 | 2021-08-15 | 21300 | keep | 0 | Aug | 2021 | 0.014507 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-08-15 12:47 | 2021-08-15 14:57 | 11 | 002:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21081500066 | New_Event | Bad Weather | Include | Include | Weather | 130 | 2021-08-15 | 1430 | keep | 0 | Aug | 2021 | 0.00097397 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2021-08-15 12:48 | 2021-08-15 12:50 | 2124 | 000:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR CARGA POR EL 1657-04 | R21081500025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-08-15 | 4248 | keep | 0 | Aug | 2021 | 0.0028933 | 0.0014466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2124
SAN JUAN | 2021-08-15 12:48 | 2021-08-15 12:50 | 14 | 000:02 | T | DESGANCHE | DISPARO LLEVA LA CARGA DEL 1118-07 | R21081500025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-08-15 | 28 | keep | 0 | Aug | 2021 | 1.9071e-05 | 9.5353e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2021-08-15 12:50 | 2021-08-15 15:44 | 150 | 002:54 | P | DESGANCHE | 1 X 50 Y 1 X 80 EN CORTE DE LINEA | R21081500028 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 174 | 2021-08-15 | 26100 | keep | 0 | Aug | 2021 | 0.017777 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-08-15 12:51 | 2021-08-15 15:06 | 2073 | 002:15 | T | ESTRUCTURA AVERIADA | SE SECCIONALIZO POSTE VIRADO Y LINEAS EN EL PISO Y SE CERRO INTERRUPTOR | M21081500085 | New_Event | Defective Pole | Include | Include | Equipment | 135 | 2021-08-15 | 279855 | keep | 0 | Aug | 2021 | 0.19061 | 0.0014119 | Sustained | FALSE | TRUE | Not_TMED_Event | 2073
VEGA BAJA | 2021-08-15 12:51 | 2021-08-15 12:52 | 3000 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21081500126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 3000 | keep | 0 | Aug | 2021 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
BAYAMON | 2021-08-15 12:56 | 2021-08-15 14:31 | 50 | 001:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO | S21081500121 | New_Event | Wire Down | Include | Include | Equipment | 95 | 2021-08-15 | 4750 | keep | 0 | Aug | 2021 | 0.0032352 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-08-15 13:00 | 2021-08-15 13:01 | 143 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21081500114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 143 | keep | 0 | Aug | 2021 | 9.7397e-05 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
HUMACAO | 2021-08-15 13:01 | 2021-08-15 15:52 | 80 | 002:51 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA BAMBUAS | C21081500070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2021-08-15 | 13680 | keep | 0 | Aug | 2021 | 0.0093174 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-15 13:12 | 2021-08-15 14:36 | 60 | 001:24 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081500130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2021-08-15 | 5040 | keep | 0 | Aug | 2021 | 0.0034327 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
YAUCO | 2021-08-15 13:17 | 2021-08-15 17:40 | 50 | 004:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21081500032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2021-08-15 | 13150 | keep | 0 | Aug | 2021 | 0.0089564 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-15 13:20 | 2021-08-15 20:21 | 100 | 007:01 | P | DESGANCHE | 3 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21081500093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 421 | 2021-08-15 | 42100 | keep | 0 | Aug | 2021 | 0.028674 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-08-15 13:25 | 2021-08-15 13:26 | 1076 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21081500039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 1076 | keep | 0 | Aug | 2021 | 0.00073286 | 0.00073286 | Momentary | FALSE | FALSE | Not_TMED_Event | 1076
YAUCO | 2021-08-15 13:28 | 2021-08-16 13:20 | 100 | 023:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 FUSIBLE DE 100 EN CORETE DE LINEAS MAL TIEMPO | P21081500036 | New_Event | Bad Weather | Include | Include | Weather | 1432 | 2021-08-15 | 143200 | keep | 0 | Aug | 2021 | 0.097533 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-08-15 13:30 | 2021-08-16 09:38 | 30 | 020:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21081500041 | New_Event | Bad Weather | Include | Include | Weather | 1208 | 2021-08-15 | 36240 | keep | 0 | Aug | 2021 | 0.024683 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-08-15 13:32 | 2021-08-16 14:56 | 1 | 025:24 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA 3 X 15 EN TRANSFORMADOR | C21081500078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1524 | 2021-08-15 | 1524 | keep | 0 | Aug | 2021 | 0.001038 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
PONCE | 2021-08-15 13:33 | 2021-08-15 13:34 | 4035 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21081500040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 4035 | keep | 0 | Aug | 2021 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
FAJARDO | 2021-08-15 13:37 | 2021-08-15 18:28 | 20 | 004:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | R21081500034 | New_Event | Bad Weather | Include | Include | Weather | 291 | 2021-08-15 | 5820 | keep | 0 | Aug | 2021 | 0.003964 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
FAJARDO | 2021-08-15 13:45 | 2021-08-15 13:46 | 1234 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | R21081500000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-08-15 | 1234 | keep | 0 | Aug | 2021 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
MAYAGÃœEZ | 2021-08-15 13:48 | 2021-08-15 20:10 | 50 | 006:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21081500103 | New_Event | Bad Weather | Include | Include | Weather | 382 | 2021-08-15 | 19100 | keep | 0 | Aug | 2021 | 0.013009 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-08-15 13:55 | 2021-08-15 17:20 | 80 | 003:25 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN CORTE DE LINEA | C21081500081 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 205 | 2021-08-15 | 16400 | keep | 0 | Aug | 2021 | 0.01117 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
FAJARDO | 2021-08-15 13:56 | 2021-08-15 13:57 | 1234 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | R21081500000 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-08-15 | 1234 | keep | 0 | Aug | 2021 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
FAJARDO | 2021-08-15 13:57 | 2021-08-15 13:58 | 1234 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | R21081500000 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-08-15 | 1234 | keep | 0 | Aug | 2021 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
FAJARDO | 2021-08-15 14:00 | 2021-08-15 15:48 | 1234 | 001:48 | T | PARARRAYOS DEFECTUOSO | SE SECCIONALIZO EL ALIMENTADOR Y SE PASO PARTE DE LA CARGA AL 2305-02 | R21081500038 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 108 | 2021-08-15 | 133272 | keep | 0 | Aug | 2021 | 0.090771 | 0.00084047 | Sustained | FALSE | FALSE | Not_TMED_Event | 1234
HUMACAO | 2021-08-15 14:00 | 2021-08-15 14:01 | 2450 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21081500083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 2450 | keep | 0 | Aug | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
MAYAGÃœEZ | 2021-08-15 14:00 | 2021-08-15 17:20 | 3000 | 003:20 | P | DESCONECTIVO DEFECTUOSO | MACHETE QUEMADO SE ABRIO MACHETES ANTERIORES PARA REMPLAZARLOS | M21081400109 | Additional_clients | Switch Failure | Include | Include | Equipment | 200 | 2021-08-15 | 600000 | keep | 0 | Aug | 2021 | 0.40866 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-15 14:03 | 2021-08-16 09:50 | 1 | 019:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE EN TRANSFORMADOR | M21081500106 | New_Event | Wire Down | Include | Include | Equipment | 1187 | 2021-08-15 | 1187 | keep | 0 | Aug | 2021 | 0.00080846 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-08-15 14:05 | 2021-08-16 13:15 | 382 | 023:10 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE RETIRO ARBOL SOBRE LINEA Y SE CERRO INTERRUPTOR | M21081500110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1390 | 2021-08-15 | 530980 | keep | 0 | Aug | 2021 | 0.36165 | 0.00026018 | Sustained | FALSE | TRUE | Not_TMED_Event | 382
ARECIBO | 2021-08-15 14:07 | 2021-08-15 22:10 | 150 | 008:03 | P | ESTRUCTURA AVERIADA | SE CORRIGIO POSTE PARTIDO EN LA PERILLA Y SE CERRO CORTE DE LINEA | A21081500044 | New_Event | Defective Pole | Include | Include | Equipment | 483 | 2021-08-15 | 72450 | keep | 0 | Aug | 2021 | 0.049345 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
HUMACAO | 2021-08-15 14:14 | 2021-08-15 14:15 | 676 | 000:01 | T | DESGANCHE | RECIERRE | C21081500087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-15 | 676 | keep | 0 | Aug | 2021 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
HUMACAO | 2021-08-15 14:16 | 2021-08-15 15:16 | 676 | 001:00 | T | DESGANCHE | SE RETIRO ARBOL SOBRE LINEA Y CERRO INTERRUPTOR | C21081500087 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 60 | 2021-08-15 | 40560 | keep | 0 | Aug | 2021 | 0.027625 | 0.00046042 | Sustained | FALSE | TRUE | Not_TMED_Event | 676
HUMACAO | 2021-08-15 14:17 | 2021-08-15 16:39 | 95 | 002:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C21081500088 | New_Event | Bad Weather | Include | Include | Weather | 142 | 2021-08-15 | 13490 | keep | 0 | Aug | 2021 | 0.009188 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
CANOVANAS | 2021-08-15 14:18 | 2021-08-15 18:04 | 30 | 003:46 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHO Y LEVANTO CONDUCTOR | R21081500051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2021-08-15 | 6780 | keep | 0 | Aug | 2021 | 0.0046178 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-08-15 14:25 | 2021-08-16 09:48 | 35 | 019:23 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21081500139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1163 | 2021-08-15 | 40705 | keep | 0 | Aug | 2021 | 0.027724 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-08-15 14:27 | 2021-08-16 15:06 | 15 | 024:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21081500047 | New_Event | Bad Weather | Include | Include | Weather | 1479 | 2021-08-15 | 22185 | keep | 0 | Aug | 2021 | 0.01511 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-08-15 14:30 | 2021-08-15 17:45 | 40 | 003:15 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21081500141 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 195 | 2021-08-15 | 7800 | keep | 0 | Aug | 2021 | 0.0053125 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-08-15 14:31 | 2021-08-15 19:09 | 55 | 004:38 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA RETIRO ARBOL SOBRE LINEA | C21081500093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 278 | 2021-08-15 | 15290 | keep | 0 | Aug | 2021 | 0.010414 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
HUMACAO | 2021-08-15 14:34 | 2021-08-15 14:35 | 2450 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21081500095 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 2450 | keep | 0 | Aug | 2021 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
BAYAMON | 2021-08-15 14:37 | 2021-08-15 18:55 | 80 | 004:18 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081500144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 258 | 2021-08-15 | 20640 | keep | 0 | Aug | 2021 | 0.014058 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CANOVANAS | 2021-08-15 14:41 | 2021-08-15 18:39 | 40 | 003:58 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | R21081500061 | New_Event | Bad Weather | Include | Include | Weather | 238 | 2021-08-15 | 9520 | keep | 0 | Aug | 2021 | 0.006484 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-08-15 14:42 | 2021-08-15 15:41 | 1615 | 000:59 | T | DESGANCHE | SE ABRIO LA SALIDA DEL SOTERRADO PARA PROBAR EL INTERRUPTOR QUEDO EN SERVICIO | P21081500047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2021-08-15 | 95285 | keep | 0 | Aug | 2021 | 0.064898 | 0.0011 | Sustained | FALSE | FALSE | Not_TMED_Event | 1615
CAGUAS | 2021-08-15 14:44 | 2021-08-15 14:45 | 2842 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO | C21081500097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 2842 | keep | 0 | Aug | 2021 | 0.0019357 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
HUMACAO | 2021-08-15 14:51 | 2021-08-15 15:57 | 100 | 001:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 Y 1 X 200 EN CORTES DE LINEAS MAL TIEMPO | C21081500099 | New_Event | Bad Weather | Include | Include | Weather | 66 | 2021-08-15 | 6600 | keep | 0 | Aug | 2021 | 0.0044952 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-08-15 14:56 | 2021-08-15 14:57 | 3597 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21081500000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 3597 | keep | 0 | Aug | 2021 | 0.0024499 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-15 15:06 | 2021-08-15 20:19 | 440 | 005:13 | P | ESTRUCTURA AVERIADA | SE ENDEREZO POSTE Y SE REPARO LINEAS PRIMARIAS | M21081500150 | Partial_restoration | Defective Pole | Include | Include | Equipment | 313 | 2021-08-15 | 137720 | keep | 0 | Aug | 2021 | 0.0938 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-08-15 15:12 | 2021-08-15 17:40 | 60 | 002:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21081500101 | New_Event | Bad Weather | Include | Include | Weather | 148 | 2021-08-15 | 8880 | keep | 0 | Aug | 2021 | 0.0060481 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
AGUADILLA | 2021-08-15 15:20 | 2021-08-16 19:00 | 30 | 027:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 75KVA | M21081500154 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1660 | 2021-08-15 | 49800 | keep | 0 | Aug | 2021 | 0.033919 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2021-08-15 15:41 | 2021-08-15 17:25 | 1000 | 001:44 | P | DESGANCHE | SE REALIZO DESGANCHE | P21081500061 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 104 | 2021-08-15 | 104000 | keep | 0 | Aug | 2021 | 0.070834 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-15 15:42 | 2021-08-15 15:43 | 353 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21081500149 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-15 | 353 | keep | 0 | Aug | 2021 | 0.00024043 | 0.00024043 | Momentary | FALSE | FALSE | Not_TMED_Event | 353
BAYAMON | 2021-08-15 15:43 | 2021-08-15 16:53 | 100 | 001:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA TRONCAL TRAS PATIO | S21081500153 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 70 | 2021-08-15 | 7000 | keep | 0 | Aug | 2021 | 0.0047677 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
FAJARDO | 2021-08-15 15:48 | 2021-08-15 17:09 | 200 | 001:21 | P | PARARRAYOS DEFECTUOSO | SE SECCIONALIZO PARARRAYO Y TRANSFORMADOR AVERIADO EN DESUSO | R21081500038 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 81 | 2021-08-15 | 16200 | keep | 0 | Aug | 2021 | 0.011034 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-08-15 16:08 | 2021-08-15 16:10 | 1 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO | R21081500075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-15 | 2 | keep | 0 | Aug | 2021 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-08-15 16:16 | 2021-08-16 11:14 | 50 | 018:58 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REPARO AISLADOR ROTO | A21081500060 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1138 | 2021-08-15 | 56900 | keep | 0 | Aug | 2021 | 0.038754 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-08-15 16:27 | 2021-08-16 10:26 | 60 | 017:59 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21081500163 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1079 | 2021-08-15 | 64740 | keep | 0 | Aug | 2021 | 0.044094 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
PONCE | 2021-08-15 16:35 | 2021-08-15 19:45 | 1 | 003:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN MONTURA TRIFASICA | P21081500073 | New_Event | Bad Weather | Include | Include | Weather | 190 | 2021-08-15 | 190 | keep | 0 | Aug | 2021 | 0.00012941 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-08-15 16:43 | 2021-08-16 10:45 | 155 | 018:02 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | C21081500110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1082 | 2021-08-15 | 167710 | keep | 0 | Aug | 2021 | 0.11423 | 0.00010557 | Sustained | FALSE | TRUE | Not_TMED_Event | 155
BARRANQUITAS | 2021-08-15 16:45 | 2021-08-16 15:02 | 20 | 022:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C21081500111 | New_Event | Bad Weather | Include | Include | Weather | 1337 | 2021-08-15 | 26740 | keep | 0 | Aug | 2021 | 0.018212 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-08-15 16:51 | 2021-08-15 16:52 | 1297 | 000:01 | T | ESTRUCTURA AVERIADA | DISPARO INTERRUPTOR 1904-06 LLEVANDO LAS CARGAS DEL 1901-02 Y 1901-03 | S21081500162 | New_Event | Defective Pole | Include | Include | Equipment | 1 | 2021-08-15 | 1297 | keep | 0 | Aug | 2021 | 0.00088338 | 0.00088338 | Momentary | FALSE | FALSE | Not_TMED_Event | 1297
BAYAMON | 2021-08-15 16:51 | 2021-08-15 16:52 | 451 | 000:01 | T | ESTRUCTURA AVERIADA | DISPARO INTERRUPTOR 1904-06 LLEVANDO LAS CARGAS DEL 1901-02 Y 1901-03 | S21081500162 | New_Event | Defective Pole | Include | Include | Equipment | 1 | 2021-08-15 | 451 | keep | 0 | Aug | 2021 | 0.00030717 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
BAYAMON | 2021-08-15 16:53 | 2021-08-15 17:18 | 353 | 000:25 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE ABIERTO TRASPATIO EN CALLE 4 PUERTO NUEVO | S21081500149 | Additional_clients | Wire Down | Include | Include | Equipment | 25 | 2021-08-15 | 8825 | keep | 0 | Aug | 2021 | 0.0060107 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-15 16:53 | 2021-08-15 16:54 | 1297 | 000:01 | T | ESTRUCTURA AVERIADA | DISPARO INTERRUPTOR 1904-06 LLEVANDO LAS CARGAS DEL 1901-02 Y 1901-03 | S21081500162 | 1st_after_momentary | Defective Pole | Include | Include | Equipment | 1 | 2021-08-15 | 1297 | keep | 0 | Aug | 2021 | 0.00088338 | 0.00088338 | Momentary | FALSE | FALSE | Not_TMED_Event | 1297
BAYAMON | 2021-08-15 16:53 | 2021-08-15 16:54 | 451 | 000:01 | T | ESTRUCTURA AVERIADA | DISPARO INTERRUPTOR 1904-06 LLEVANDO LAS CARGAS DEL 1901-02 Y 1901-03 | S21081500162 | 1st_after_momentary | Defective Pole | Include | Include | Equipment | 1 | 2021-08-15 | 451 | keep | 0 | Aug | 2021 | 0.00030717 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
BAYAMON | 2021-08-15 16:57 | 2021-08-15 17:29 | 1297 | 000:32 | T | ESTRUCTURA AVERIADA | DISPARO INTERRUPTOR 1904-06 LLEVANDO LAS CARGAS DEL 1901-02 Y 1901-03. SE SECCIONALIZO ABRIENDO AMARRE CONTRA EL 1901-03 | S21081500162 | 1st_after_momentary | Defective Pole | Include | Include | Equipment | 32 | 2021-08-15 | 41504 | keep | 0 | Aug | 2021 | 0.028268 | 0.00088338 | Sustained | FALSE | FALSE | Not_TMED_Event | 1297
BAYAMON | 2021-08-15 16:57 | 2021-08-15 20:32 | 451 | 003:35 | T | ESTRUCTURA AVERIADA | DISPARO INTERRUPTOR 1904-06 LLEVANDO LAS CARGAS DEL 1901-02 Y 1901-03. SE SECCIONALIZO ABRIENDO CORTE DE LINEA (NO FUNDIO) SECCIONALIZANDO AISLADOR AVERIADO. 9 CLIENTES SE QUEDARON SIN SERVICIO | S21081500162 | 1st_after_momentary | Defective Pole | Include | Include | Equipment | 215 | 2021-08-15 | 96965 | keep | 0 | Aug | 2021 | 0.066042 | 0.00030717 | Sustained | FALSE | TRUE | Not_TMED_Event | 451
FAJARDO | 2021-08-15 16:58 | 2021-08-15 18:10 | 50 | 001:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R21081500080 | New_Event |  |  | Include | Wildlife | 72 | 2021-08-15 | 3600 | keep | 0 | Aug | 2021 | 0.0024519 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BARRANQUITAS | 2021-08-15 17:07 | 2021-08-15 20:04 | 95 | 002:57 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 30 EN CORTE DE LINEA MAL TIEMPO | C21081500124 | New_Event | Bad Weather | Include | Include | Weather | 177 | 2021-08-15 | 16815 | keep | 0 | Aug | 2021 | 0.011453 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
MAYAGÃœEZ | 2021-08-15 17:12 | 2021-08-15 17:34 | 80 | 000:22 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 100 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M21081500182 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 22 | 2021-08-15 | 1760 | keep | 0 | Aug | 2021 | 0.0011987 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
VEGA BAJA | 2021-08-15 17:13 | 2021-08-16 11:31 | 60 | 018:18 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081500168 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1098 | 2021-08-15 | 65880 | keep | 0 | Aug | 2021 | 0.044871 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-08-15 17:18 | 2021-08-16 10:07 | 100 | 016:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA TRONCAL TRAS PATIO | S21081500153 | Partial_restoration | Wire Down | Include | Include | Equipment | 1009 | 2021-08-15 | 100900 | keep | 0 | Aug | 2021 | 0.068723 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
PONCE | 2021-08-15 17:22 | 2021-08-15 17:23 | 1712 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21081500085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 1712 | keep | 0 | Aug | 2021 | 0.001166 | 0.001166 | Momentary | FALSE | FALSE | Not_TMED_Event | 1712
PONCE | 2021-08-15 17:27 | 2021-08-15 18:35 | 1015 | 001:08 | P | DESGANCHE | SE REALIZO DESGANCHE | P21081500093 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 68 | 2021-08-15 | 69020 | keep | 0 | Aug | 2021 | 0.047009 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-15 17:34 | 2021-08-15 17:35 | 108 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR | M21081500188 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-08-15 | 108 | keep | 0 | Aug | 2021 | 7.3558e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-15 17:35 | 2021-08-15 17:37 | 80 | 000:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 100 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M21081500182 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2021-08-15 | 160 | keep | 0 | Aug | 2021 | 0.00010898 | 5.4488e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-15 17:36 | 2021-08-15 19:05 | 946 | 001:29 | T | DESGANCHE | DISPARO 1525-05 LLEVANDO LA CARGA DEL 1525-02 SE RETIRO RAMA DE LINEA Y SE CERRO AMARRE CON EL 1525-05 | S21081500189 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2021-08-15 | 84194 | keep | 0 | Aug | 2021 | 0.057344 | 0.00064432 | Sustained | FALSE | TRUE | Not_TMED_Event | 946
BAYAMON | 2021-08-15 17:36 | 2021-08-15 18:32 | 937 | 000:56 | T | DESGANCHE | SE ABRIO AMARRE CONTRA EL 1525-02 Y SE CONTINUO PATRULLANDO EL 1525-02 | S21081500189 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2021-08-15 | 52472 | keep | 0 | Aug | 2021 | 0.035738 | 0.00063819 | Sustained | FALSE | FALSE | Not_TMED_Event | 937
MAYAGÃœEZ | 2021-08-15 17:37 | 2021-08-15 17:38 | 108 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR | M21081500189 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-08-15 | 108 | keep | 0 | Aug | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
MAYAGÃœEZ | 2021-08-15 17:38 | 2021-08-15 20:37 | 80 | 002:59 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 100 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M21081500182 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 179 | 2021-08-15 | 14320 | keep | 0 | Aug | 2021 | 0.0097533 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-08-15 17:39 | 2021-08-15 18:48 | 80 | 001:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21081500190 | New_Event | Bad Weather | Include | Include | Weather | 69 | 2021-08-15 | 5520 | keep | 0 | Aug | 2021 | 0.0037596 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
YAUCO | 2021-08-15 17:40 | 2021-08-15 17:41 | 591 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21081500111 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 591 | keep | 0 | Aug | 2021 | 0.00040253 | 0.00040253 | Momentary | FALSE | TRUE | Not_TMED_Event | 591
YAUCO | 2021-08-15 17:40 | 2021-08-15 17:41 | 1924 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21081500111 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 1924 | keep | 0 | Aug | 2021 | 0.0013104 | 0.0013104 | Momentary | FALSE | TRUE | Not_TMED_Event | 1924
YAUCO | 2021-08-15 17:40 | 2021-08-15 17:41 | 968 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21081500111 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 968 | keep | 0 | Aug | 2021 | 0.0006593 | 0.0006593 | Momentary | FALSE | TRUE | Not_TMED_Event | 968
YAUCO | 2021-08-15 17:40 | 2021-08-15 17:41 | 680 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21081500111 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 680 | keep | 0 | Aug | 2021 | 0.00046314 | 0.00046314 | Momentary | FALSE | TRUE | Not_TMED_Event | 680
YAUCO | 2021-08-15 17:40 | 2021-08-15 17:41 | 2246 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21081500111 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 2246 | keep | 0 | Aug | 2021 | 0.0015297 | 0.0015297 | Momentary | FALSE | TRUE | Not_TMED_Event | 2246
YAUCO | 2021-08-15 17:40 | 2021-08-15 17:41 | 2470 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21081500111 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 2470 | keep | 0 | Aug | 2021 | 0.0016823 | 0.0016823 | Momentary | FALSE | TRUE | Not_TMED_Event | 2470
YAUCO | 2021-08-15 17:40 | 2021-08-15 17:41 | 1182 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21081500111 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 1182 | keep | 0 | Aug | 2021 | 0.00080505 | 0.00080505 | Momentary | FALSE | TRUE | Not_TMED_Event | 1182
YAUCO | 2021-08-15 17:40 | 2021-08-15 17:41 | 2340 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21081500111 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 2340 | keep | 0 | Aug | 2021 | 0.0015938 | 0.0015938 | Momentary | FALSE | TRUE | Not_TMED_Event | 2340
YAUCO | 2021-08-15 17:40 | 2021-08-15 17:41 | 1637 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21081500111 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 1637 | keep | 0 | Aug | 2021 | 0.001115 | 0.001115 | Momentary | FALSE | TRUE | Not_TMED_Event | 1637
YAUCO | 2021-08-15 17:40 | 2021-08-15 17:41 | 1475 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21081500111 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 1475 | keep | 0 | Aug | 2021 | 0.0010046 | 0.0010046 | Momentary | FALSE | TRUE | Not_TMED_Event | 1475
YAUCO | 2021-08-15 17:40 | 2021-08-15 17:41 | 661 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21081500111 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 661 | keep | 0 | Aug | 2021 | 0.0004502 | 0.0004502 | Momentary | FALSE | TRUE | Not_TMED_Event | 661
YAUCO | 2021-08-15 17:40 | 2021-08-15 17:41 | 1569 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21081500111 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 1569 | keep | 0 | Aug | 2021 | 0.0010686 | 0.0010686 | Momentary | FALSE | TRUE | Not_TMED_Event | 1569
YAUCO | 2021-08-15 17:40 | 2021-08-15 17:41 | 2309 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21081500111 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 2309 | keep | 0 | Aug | 2021 | 0.0015726 | 0.0015726 | Momentary | FALSE | TRUE | Not_TMED_Event | 2309
YAUCO | 2021-08-15 17:40 | 2021-08-15 17:41 | 2179 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21081500111 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 2179 | keep | 0 | Aug | 2021 | 0.0014841 | 0.0014841 | Momentary | FALSE | TRUE | Not_TMED_Event | 2179
YAUCO | 2021-08-15 17:40 | 2021-08-15 17:41 | 2440 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21081500111 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 2440 | keep | 0 | Aug | 2021 | 0.0016619 | 0.0016619 | Momentary | FALSE | TRUE | Not_TMED_Event | 2440
YAUCO | 2021-08-15 17:40 | 2021-08-15 17:41 | 1352 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21081500111 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 1352 | keep | 0 | Aug | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | TRUE | Not_TMED_Event | 1352
YAUCO | 2021-08-15 17:40 | 2021-08-15 17:41 | 3973 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21081500111 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 3973 | keep | 0 | Aug | 2021 | 0.002706 | 0.002706 | Momentary | FALSE | TRUE | Not_TMED_Event | 3973
YAUCO | 2021-08-15 17:40 | 2021-08-15 17:41 | 2484 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 | P21081500111 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 2484 | keep | 0 | Aug | 2021 | 0.0016918 | 0.0016918 | Momentary | FALSE | TRUE | Not_TMED_Event | 2484
MAYAGÃœEZ | 2021-08-15 17:40 | 2021-08-15 17:48 | 281 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21081500196 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-08-15 | 2248 | keep | 0 | Aug | 2021 | 0.0015311 | 0.00019139 | Sustained | FALSE | TRUE | Not_TMED_Event | 281
MAYAGÃœEZ | 2021-08-15 17:40 | 2021-08-15 17:48 | 1252 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21081500196 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-08-15 | 10016 | keep | 0 | Aug | 2021 | 0.0068219 | 0.00085273 | Sustained | FALSE | TRUE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2021-08-15 17:40 | 2021-08-15 17:48 | 595 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21081500197 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-08-15 | 4760 | keep | 0 | Aug | 2021 | 0.003242 | 0.00040525 | Sustained | FALSE | TRUE | Not_TMED_Event | 595
MAYAGÃœEZ | 2021-08-15 17:40 | 2021-08-15 17:48 | 51 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21081500197 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-08-15 | 408 | keep | 0 | Aug | 2021 | 0.00027789 | 3.4736e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 51
MAYAGÃœEZ | 2021-08-15 17:40 | 2021-08-15 17:48 | 721 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A21081500197 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-08-15 | 5768 | keep | 0 | Aug | 2021 | 0.0039286 | 0.00049107 | Sustained | FALSE | TRUE | Not_TMED_Event | 721
UTUADO | 2021-08-15 17:40 | 2021-08-15 17:48 | 1382 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-08-15 | 11056 | keep | 0 | Aug | 2021 | 0.0075302 | 0.00094127 | Sustained | FALSE | TRUE | Not_TMED_Event | 1382
UTUADO | 2021-08-15 17:40 | 2021-08-15 17:48 | 654 | 000:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2021-08-15 | 5232 | keep | 0 | Aug | 2021 | 0.0035635 | 0.00044544 | Sustained | FALSE | TRUE | Not_TMED_Event | 654
YAUCO | 2021-08-15 17:41 | 2021-08-15 17:51 | 50 | 000:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P21081500032 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 10 | 2021-08-15 | 500 | keep | 0 | Aug | 2021 | 0.00034055 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
GUAYAMA | 2021-08-15 17:45 | 2021-08-15 17:46 | 4132 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21081500103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 4132 | keep | 0 | Aug | 2021 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
PONCE | 2021-08-15 17:46 | 2021-08-15 17:47 | 1979 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR PORTATIL 10 | P21081500108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 1979 | keep | 0 | Aug | 2021 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2021-08-15 17:46 | 2021-08-15 17:47 | 5069 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR PORTATIL 10 | P21081500108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 5069 | keep | 0 | Aug | 2021 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2021-08-15 17:46 | 2021-08-15 17:47 | 5063 | 000:01 | S | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR PORTATIL 10 | P21081500108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 5063 | keep | 0 | Aug | 2021 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
MAYAGÃœEZ | 2021-08-15 17:48 | 2021-08-15 18:25 | 100 | 000:37 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081400011 | Partial_restoration | Bad Weather | Include | Include | Weather | 37 | 2021-08-15 | 3700 | keep | 0 | Aug | 2021 | 0.0025201 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-15 17:48 | 2021-08-15 18:25 | 50 | 000:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21081500026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 37 | 2021-08-15 | 1850 | keep | 0 | Aug | 2021 | 0.00126 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-15 17:48 | 2021-08-16 10:28 | 3 | 016:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA | M21081500201 | New_Event | Bad Weather | Include | Include | Weather | 1000 | 2021-08-15 | 3000 | keep | 0 | Aug | 2021 | 0.0020433 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
ARECIBO | 2021-08-15 17:54 | 2021-08-16 08:51 | 50 | 014:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21081500065 | New_Event | Bad Weather | Include | Include | Weather | 897 | 2021-08-15 | 44850 | keep | 0 | Aug | 2021 | 0.030547 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-08-15 17:58 | 2021-08-16 13:30 | 16 | 019:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | M21081500205 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1172 | 2021-08-15 | 18752 | keep | 0 | Aug | 2021 | 0.012772 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2021-08-15 17:58 | 2021-08-16 15:24 | 30 | 021:26 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21081500130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1286 | 2021-08-15 | 38580 | keep | 0 | Aug | 2021 | 0.026277 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-08-15 18:03 | 2021-08-16 15:07 | 150 | 021:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081500210 | New_Event | Bad Weather | Include | Include | Weather | 1264 | 2021-08-15 | 189600 | keep | 0 | Aug | 2021 | 0.12914 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-08-15 18:04 | 2021-08-16 01:12 | 80 | 007:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081500211 | New_Event | Bad Weather | Include | Include | Weather | 428 | 2021-08-15 | 34240 | keep | 0 | Aug | 2021 | 0.023321 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-15 18:18 | 2021-08-16 10:36 | 12 | 016:18 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21081500172 | New_Event | Secondary Wire Down | Include | Include | Equipment | 978 | 2021-08-15 | 11736 | keep | 0 | Aug | 2021 | 0.0079933 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2021-08-15 18:20 | 2021-08-16 14:20 | 150 | 020:00 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21081500068 | New_Event | Bad Weather | Include | Include | Weather | 1200 | 2021-08-15 | 180000 | keep | 0 | Aug | 2021 | 0.1226 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BARRANQUITAS | 2021-08-15 18:23 | 2021-08-16 12:22 | 80 | 017:59 | P | DESGANCHE | 3 X 40 EN CORTE DE LINEA | C21081500132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1079 | 2021-08-15 | 86320 | keep | 0 | Aug | 2021 | 0.058792 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-15 18:25 | 2021-08-15 21:48 | 60 | 003:23 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081500173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2021-08-15 | 12180 | keep | 0 | Aug | 2021 | 0.0082957 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
YAUCO | 2021-08-15 18:25 | 2021-08-15 21:20 | 591 | 002:55 | S | LINEA DE TRANSMISION 38KV | EN SERVICIO A TRAVES DE LINEA 1400 | P21081500119 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 175 | 2021-08-15 | 103425 | keep | 0 | Aug | 2021 | 0.070442 | 0.00040253 | Sustained | FALSE | TRUE | Not_TMED_Event | 591
MAYAGÃœEZ | 2021-08-15 18:25 | 2021-08-15 22:46 | 281 | 004:21 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M21081500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 261 | 2021-08-15 | 73341 | keep | 0 | Aug | 2021 | 0.049952 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-15 18:25 | 2021-08-15 22:46 | 1252 | 004:21 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M21081500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 261 | 2021-08-15 | 326772 | keep | 0 | Aug | 2021 | 0.22256 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-15 18:25 | 2021-08-15 22:46 | 595 | 004:21 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M21081500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 261 | 2021-08-15 | 155295 | keep | 0 | Aug | 2021 | 0.10577 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-15 18:25 | 2021-08-15 22:46 | 51 | 004:21 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M21081500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 261 | 2021-08-15 | 13311 | keep | 0 | Aug | 2021 | 0.0090661 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-15 18:25 | 2021-08-15 22:46 | 721 | 004:21 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M21081500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 261 | 2021-08-15 | 188181 | keep | 0 | Aug | 2021 | 0.12817 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
UTUADO | 2021-08-15 18:25 | 2021-08-15 21:56 | 3316 | 003:31 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 211 | 2021-08-15 | 699676 | keep | 0 | Aug | 2021 | 0.47655 | 0.0022585 | Sustained | FALSE | TRUE | Not_TMED_Event | 3316
UTUADO | 2021-08-15 18:25 | 2021-08-15 21:56 | 1241 | 003:31 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 211 | 2021-08-15 | 261851 | keep | 0 | Aug | 2021 | 0.17835 | 0.00084524 | Sustained | FALSE | TRUE | Not_TMED_Event | 1241
UTUADO | 2021-08-15 18:25 | 2021-08-15 22:46 | 1382 | 004:21 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | A21081500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 261 | 2021-08-15 | 360702 | keep | 0 | Aug | 2021 | 0.24567 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
UTUADO | 2021-08-15 18:25 | 2021-08-15 22:46 | 654 | 004:21 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | A21081500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 261 | 2021-08-15 | 170694 | keep | 0 | Aug | 2021 | 0.11626 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
UTUADO | 2021-08-15 18:27 | 2021-08-16 10:47 | 650 | 016:20 | T | ESTRUCTURA AVERIADA | SE SECCIONALIZO AVERIA ABRIENDO EN CONVERTIDOR POSTE PARTIDO | A21081500070 | New_Event | Defective Pole | Include | Include | Equipment | 980 | 2021-08-15 | 637000 | keep | 0 | Aug | 2021 | 0.43386 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
ARECIBO | 2021-08-15 18:28 | 2021-08-15 20:26 | 150 | 001:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | A21081500071 | New_Event | Cutout Failure | Include | Include | Equipment | 118 | 2021-08-15 | 17700 | keep | 0 | Aug | 2021 | 0.012055 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-08-15 18:40 | 2021-08-16 16:56 | 80 | 022:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21081500230 | New_Event | Wire Down | Include | Include | Equipment | 1336 | 2021-08-15 | 106880 | keep | 0 | Aug | 2021 | 0.072795 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-15 18:45 | 2021-08-15 18:47 | 823 | 000:02 | P | NO SE REPORTO CAUSA | SE CERRO POR SCADA 95% POR EL 1119-04 | S21081500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-15 | 1646 | keep | 0 | Aug | 2021 | 0.0011211 | 0.00056054 | Momentary | FALSE | FALSE | Not_TMED_Event | 823
BAYAMON | 2021-08-15 18:45 | 2021-08-15 18:47 | 2720 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVANDO 95% DEL 1115-05 | S21081500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-15 | 5440 | keep | 0 | Aug | 2021 | 0.0037052 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
HUMACAO | 2021-08-15 18:51 | 2021-08-15 18:52 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21081500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 2354 | keep | 0 | Aug | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
PONCE | 2021-08-15 18:54 | 2021-08-15 18:55 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21081500125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 1746 | keep | 0 | Aug | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
MAYAGÃœEZ | 2021-08-15 18:57 | 2021-08-16 09:49 | 40 | 014:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081500236 | New_Event | Bad Weather | Include | Include | Weather | 892 | 2021-08-15 | 35680 | keep | 0 | Aug | 2021 | 0.024301 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-08-15 19:02 | 2021-08-17 17:00 | 20 | 045:58 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A21081500079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2758 | 2021-08-15 | 55160 | keep | 0 | Aug | 2021 | 0.037569 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
GUAYAMA | 2021-08-15 19:04 | 2021-08-15 20:19 | 4132 | 001:15 | T | NO SE REPORTO CAUSA | SE SECCIONALIZO AVERIA Y SE CERRO INTERRUPTOR/ SE SIGUE PATRULLANDO | P21081500127 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 75 | 2021-08-15 | 309900 | keep | 0 | Aug | 2021 | 0.21107 | 0.0028143 | Sustained | FALSE | FALSE | Not_TMED_Event | 4132
PONCE | 2021-08-15 19:07 | 2021-08-15 19:08 | 4035 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21081500128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 4035 | keep | 0 | Aug | 2021 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
MAYAGÃœEZ | 2021-08-15 19:11 | 2021-08-16 18:16 | 55 | 023:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA | M21081500241 | New_Event | Wire Down | Include | Include | Equipment | 1385 | 2021-08-15 | 76175 | keep | 0 | Aug | 2021 | 0.051882 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
SAN JUAN | 2021-08-15 19:12 | 2021-08-16 15:36 | 80 | 020:24 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | R21081500085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1224 | 2021-08-15 | 97920 | keep | 0 | Aug | 2021 | 0.066693 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
UTUADO | 2021-08-15 19:16 | 2021-08-16 12:36 | 150 | 017:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA QUEMADA | A21081500084 | New_Event | Cutout Failure | Include | Include | Equipment | 1040 | 2021-08-15 | 156000 | keep | 0 | Aug | 2021 | 0.10625 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
PONCE | 2021-08-15 19:24 | 2021-08-15 19:25 | 4035 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21081500133 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 4035 | keep | 0 | Aug | 2021 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
BAYAMON | 2021-08-15 19:41 | 2021-08-15 20:58 | 50 | 001:17 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081500180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2021-08-15 | 3850 | keep | 0 | Aug | 2021 | 0.0026222 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-08-15 19:41 | 2021-08-15 19:42 | 1843 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21081500143 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 1843 | keep | 0 | Aug | 2021 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
ARECIBO | 2021-08-15 19:54 | 2021-08-16 11:30 | 30 | 015:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21081500092 | New_Event | Bad Weather | Include | Include | Weather | 936 | 2021-08-15 | 28080 | keep | 0 | Aug | 2021 | 0.019125 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-08-15 19:57 | 2021-08-16 10:26 | 100 | 014:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 FUSIBLE DE 100 EN CORETE LINEA MAL TIEMPO | P21081500146 | New_Event | Bad Weather | Include | Include | Weather | 869 | 2021-08-15 | 86900 | keep | 0 | Aug | 2021 | 0.059187 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-08-15 19:58 | 2021-08-15 20:32 | 1297 | 000:34 | T | ESTRUCTURA AVERIADA | DISPARO INTERRUPTOR 1904-06 LLEVANDO LAS CARGAS DEL 1901-02 Y 1901-03. APARTE DE LA AVERIA DE POSTE PARTIDO EN EL 1901-03, TAMBIEN SE SECCIONALIZO ARBOL GRANDE DE MANGO EN EL ALIMENTADOR. 80% DEL 1901-02 SE DEJO FUERA DE SERVICIO | S21081500162 | Partial_restoration | Defective Pole | Include | Include | Equipment | 34 | 2021-08-15 | 44098 | keep | 0 | Aug | 2021 | 0.030035 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-08-15 19:58 | 2021-08-16 08:30 | 50 | 012:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C21081500147 | New_Event | Bad Weather | Include | Include | Weather | 752 | 2021-08-15 | 37600 | keep | 0 | Aug | 2021 | 0.025609 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-08-15 20:01 | 2021-08-15 20:04 | 3957 | 000:03 | T | DESGANCHE | SE DISPARO INTERRUTOR SE CERRO POR SCADA | S21081500000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 3 | 2021-08-15 | 11871 | keep | 0 | Aug | 2021 | 0.0080853 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2021-08-15 20:12 | 2021-08-17 13:27 | 60 | 041:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 30 EN CORTE DE LINEA LINEA CRUZADAS LINEAS | A21081500095 | New_Event | Wire Down | Include | Include | Equipment | 2475 | 2021-08-15 | 148500 | keep | 0 | Aug | 2021 | 0.10114 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-08-15 20:14 | 2021-08-16 10:31 | 40 | 014:17 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21081500097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 857 | 2021-08-15 | 34280 | keep | 0 | Aug | 2021 | 0.023348 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
GUAYAMA | 2021-08-15 20:19 | 2021-08-15 21:27 | 1377 | 001:08 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO AVERIA/ MACHETES AVERIADOS/ QUEDAN 1377 CLIENTES FUERA | P21081500106 | New_Event | Switch Failure | Include | Include | Equipment | 68 | 2021-08-15 | 93636 | keep | 0 | Aug | 2021 | 0.063775 | 0.00093787 | Sustained | FALSE | FALSE | Not_TMED_Event | 1377
MAYAGÃœEZ | 2021-08-15 20:21 | 2021-08-15 20:22 | 411 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR RECIERRE EN OFF NO SE REPORTO CAUSA | M21081500252 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 411 | keep | 0 | Aug | 2021 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2021-08-15 20:21 | 2021-08-15 20:22 | 1339 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 1339 | keep | 0 | Aug | 2021 | 0.00091199 | 0.00091199 | Momentary | FALSE | TRUE | Not_TMED_Event | 1339
MAYAGÃœEZ | 2021-08-15 20:21 | 2021-08-15 20:22 | 470 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 470 | keep | 0 | Aug | 2021 | 0.00032011 | 0.00032011 | Momentary | FALSE | TRUE | Not_TMED_Event | 470
MAYAGÃœEZ | 2021-08-15 20:21 | 2021-08-15 20:22 | 2483 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 2483 | keep | 0 | Aug | 2021 | 0.0016912 | 0.0016912 | Momentary | FALSE | TRUE | Not_TMED_Event | 2483
MAYAGÃœEZ | 2021-08-15 20:21 | 2021-08-15 20:22 | 2190 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 2190 | keep | 0 | Aug | 2021 | 0.0014916 | 0.0014916 | Momentary | FALSE | TRUE | Not_TMED_Event | 2190
MAYAGÃœEZ | 2021-08-15 20:21 | 2021-08-15 20:22 | 3006 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 3006 | keep | 0 | Aug | 2021 | 0.0020474 | 0.0020474 | Momentary | FALSE | TRUE | Not_TMED_Event | 3006
MAYAGÃœEZ | 2021-08-15 20:21 | 2021-08-15 20:22 | 179 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 179 | keep | 0 | Aug | 2021 | 0.00012192 | 0.00012192 | Momentary | FALSE | TRUE | Not_TMED_Event | 179
MAYAGÃœEZ | 2021-08-15 20:21 | 2021-08-15 20:22 | 107 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 107 | keep | 0 | Aug | 2021 | 7.2877e-05 | 7.2877e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 107
MAYAGÃœEZ | 2021-08-15 20:21 | 2021-08-15 20:22 | 1666 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 1666 | keep | 0 | Aug | 2021 | 0.0011347 | 0.0011347 | Momentary | FALSE | TRUE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2021-08-15 20:21 | 2021-08-15 20:22 | 4387 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 4387 | keep | 0 | Aug | 2021 | 0.002988 | 0.002988 | Momentary | FALSE | TRUE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2021-08-15 20:21 | 2021-08-15 20:22 | 1491 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21081500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 1491 | keep | 0 | Aug | 2021 | 0.0010155 | 0.0010155 | Momentary | FALSE | FALSE | Not_TMED_Event | 1491
MAYAGÃœEZ | 2021-08-15 20:21 | 2021-08-15 20:22 | 3147 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 3147 | keep | 0 | Aug | 2021 | 0.0021434 | 0.0021434 | Momentary | FALSE | TRUE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2021-08-15 20:21 | 2021-08-15 20:22 | 4304 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 4304 | keep | 0 | Aug | 2021 | 0.0029314 | 0.0029314 | Momentary | FALSE | TRUE | Not_TMED_Event | 4304
PONCE | 2021-08-15 20:22 | 2021-08-16 10:00 | 50 | 013:38 | P | DESGANCHE | 2 POR 50 EN CORTE DE LINEA POR DESGANCHE | P21081500166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 818 | 2021-08-15 | 40900 | keep | 0 | Aug | 2021 | 0.027857 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-15 20:22 | 2021-08-16 13:27 | 100 | 017:05 | P | DESGANCHE | 3 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21081500093 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1025 | 2021-08-15 | 102500 | keep | 0 | Aug | 2021 | 0.069812 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-15 20:28 | 2021-08-16 11:26 | 80 | 014:58 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21081500186 | New_Event | Vegetation Contact | Include | Include | Vegetation | 898 | 2021-08-15 | 71840 | keep | 0 | Aug | 2021 | 0.04893 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-15 20:32 | 2021-08-16 15:45 | 1000 | 019:13 | P | DESGANCHE | SE SECCIONALIZO ARBOL GRANDE DE MANGO EN EL ALIMENTADOR. SE REALIZO DESGANCHE 1901-02 CARGA POR EL 1901-04 | S21081500183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1153 | 2021-08-15 | 1153000 | keep | 0 | Aug | 2021 | 0.7853 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
BAYAMON | 2021-08-15 20:32 | 2021-08-16 23:00 | 9 | 026:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR AVERIADO | S21081500162 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1588 | 2021-08-15 | 14292 | keep | 0 | Aug | 2021 | 0.0097342 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
YAUCO | 2021-08-15 20:32 | 2021-08-16 09:14 | 50 | 012:42 | P | DESGANCHE | 1 POR 40 EN CORTE DE LINEA POR DESGANCHE | P21081500160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 762 | 2021-08-15 | 38100 | keep | 0 | Aug | 2021 | 0.02595 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-15 20:32 | 2021-08-15 20:33 | 4381 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR POR DESCARGAS ELECTRICAS | M21081500256 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-08-15 | 4381 | keep | 0 | Aug | 2021 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
MAYAGÃœEZ | 2021-08-15 20:33 | 2021-08-15 22:30 | 2713 | 001:57 | T | BREAKER DEFECTUOSO O NO OPERA | INTERRUPTOR CON MOTOR DE RECARGAR PARA CERRAR AVERIADO SE RECARGO MANUAL Y SE CERRO INTERRUPTOR | M21081500276 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 117 | 2021-08-15 | 317421 | keep | 0 | Aug | 2021 | 0.21619 | 0.0018478 | Sustained | FALSE | FALSE | Not_TMED_Event | 2713
MAYAGÃœEZ | 2021-08-15 20:37 | 2021-08-15 20:38 | 1253 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 POR DESCARGAS ELECTRICAS | M21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 1253 | keep | 0 | Aug | 2021 | 0.00085341 | 0.00085341 | Momentary | FALSE | TRUE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2021-08-15 20:37 | 2021-08-15 20:38 | 1266 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 POR DESCARGAS ELECTRICAS | M21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 1266 | keep | 0 | Aug | 2021 | 0.00086227 | 0.00086227 | Momentary | FALSE | TRUE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2021-08-15 20:37 | 2021-08-15 20:38 | 411 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 POR DESCARGAS ELECTRICAS | M21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 411 | keep | 0 | Aug | 2021 | 0.00027993 | 0.00027993 | Momentary | FALSE | TRUE | Not_TMED_Event | 411
MAYAGÃœEZ | 2021-08-15 20:37 | 2021-08-15 20:38 | 108 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 POR DESCARGAS ELECTRICAS | M21081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-15 | 108 | keep | 0 | Aug | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 108
MAYAGÃœEZ | 2021-08-15 20:38 | 2021-08-16 12:11 | 411 | 015:33 | T | DESGANCHE | SE RETIRO BAMBUAS CAIDAS SOBRE EL TRONCAL DEL ALIMENTADOR | M21081500257 | New_Event | Vegetation Contact | Include | Include | Vegetation | 933 | 2021-08-15 | 383463 | keep | 0 | Aug | 2021 | 0.26117 | 0.00027993 | Sustained | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2021-08-15 20:38 | 2021-08-16 12:30 | 80 | 015:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 100 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M21081500182 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 952 | 2021-08-15 | 76160 | keep | 0 | Aug | 2021 | 0.051872 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BARRANQUITAS | 2021-08-15 20:40 | 2021-08-15 20:41 | 2635 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21081500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 2635 | keep | 0 | Aug | 2021 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
SAN JUAN | 2021-08-15 20:42 | 2021-08-16 10:00 | 35 | 013:18 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21081500257 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 798 | 2021-08-15 | 27930 | keep | 0 | Aug | 2021 | 0.019023 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
CANOVANAS | 2021-08-15 20:46 | 2021-08-16 09:22 | 15 | 012:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR CULEBRA | R21081500088 | New_Event |  |  | Include | Wildlife | 756 | 2021-08-15 | 11340 | keep | 0 | Aug | 2021 | 0.0077236 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2021-08-15 20:49 | 2021-08-16 15:23 | 35 | 018:34 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21081500103 | New_Event | Bad Weather | Include | Include | Weather | 1114 | 2021-08-15 | 38990 | keep | 0 | Aug | 2021 | 0.026556 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
SAN JUAN | 2021-08-15 20:51 | 2021-08-16 11:06 | 35 | 014:15 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21081500259 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 855 | 2021-08-15 | 29925 | keep | 0 | Aug | 2021 | 0.020382 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BARRANQUITAS | 2021-08-15 20:51 | 2021-08-16 20:43 | 80 | 023:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO CORTE DE LINEA PARA CERRAR PUENTE | C21081600159 | New_Event | Wire Down | Include | Include | Equipment | 1432 | 2021-08-15 | 114560 | keep | 0 | Aug | 2021 | 0.078026 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-08-15 20:57 | 2021-08-15 20:58 | 2713 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR POR DESCARGAS ELECTRICAS | M21081500262 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-08-15 | 2713 | keep | 0 | Aug | 2021 | 0.0018478 | 0.0018478 | Momentary | FALSE | FALSE | Not_TMED_Event | 2713
BAYAMON | 2021-08-15 21:06 | 2021-08-16 11:28 | 75 | 014:22 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081500193 | New_Event | Vegetation Contact | Include | Include | Vegetation | 862 | 2021-08-15 | 64650 | keep | 0 | Aug | 2021 | 0.044033 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
SAN JUAN | 2021-08-15 21:07 | 2021-08-16 19:21 | 65 | 022:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S21081500260 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1334 | 2021-08-15 | 86710 | keep | 0 | Aug | 2021 | 0.059058 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
CANOVANAS | 2021-08-15 21:12 | 2021-08-16 10:03 | 9 | 012:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | R21081500090 | New_Event | Bad Weather | Include | Include | Weather | 771 | 2021-08-15 | 6939 | keep | 0 | Aug | 2021 | 0.0047261 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2021-08-15 21:16 | 2021-08-15 23:22 | 2906 | 002:06 | T | BREAKER DEFECTUOSO O NO OPERA | INTERRUPTOR SPARE 3603-03 LLEVANDO LA CARGA DEL 3604-06 INTERRUPTOR SPARE 3603-03 DISPARO Y NO CIERRA POR SCADA NI MANUAL SE TRANSFIRIO CARGA AL 3603-01 | C21081500170 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 126 | 2021-08-15 | 366156 | keep | 0 | Aug | 2021 | 0.24939 | 0.0019793 | Sustained | FALSE | FALSE | Not_TMED_Event | 2906
MAYAGÃœEZ | 2021-08-15 21:18 | 2021-08-16 01:05 | 250 | 003:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 Y 2 X 100 EN CORTES DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081500280 | New_Event | Bad Weather | Include | Include | Weather | 227 | 2021-08-15 | 56750 | keep | 0 | Aug | 2021 | 0.038652 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
UTUADO | 2021-08-15 21:18 | 2021-08-16 17:00 | 80 | 019:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEAS PRIMARIAS CRUZADAS Y SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR SE CERRO CORTE DE LINEA | A21081500105 | New_Event | Wire Down | Include | Include | Equipment | 1182 | 2021-08-15 | 94560 | keep | 0 | Aug | 2021 | 0.064404 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-08-15 21:22 | 2021-08-15 21:23 | 863 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR POR DESCARGAS ELECTRICAS | A21081500285 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-08-15 | 863 | keep | 0 | Aug | 2021 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
UTUADO | 2021-08-15 21:27 | 2021-08-16 19:30 | 35 | 022:03 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A21081500107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1323 | 2021-08-15 | 46305 | keep | 0 | Aug | 2021 | 0.031538 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-08-15 21:33 | 2021-08-16 16:19 | 15 | 018:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFROMADOR | M21081500285 | New_Event | Bad Weather | Include | Include | Weather | 1126 | 2021-08-15 | 16890 | keep | 0 | Aug | 2021 | 0.011504 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-08-15 21:36 | 2021-08-16 09:34 | 526 | 011:58 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | R21081500097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 718 | 2021-08-15 | 377668 | keep | 0 | Aug | 2021 | 0.25723 | 0.00035826 | Sustained | FALSE | TRUE | Not_TMED_Event | 526
CAGUAS | 2021-08-15 21:51 | 2021-08-16 16:31 | 50 | 018:40 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21081500183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1120 | 2021-08-15 | 56000 | keep | 0 | Aug | 2021 | 0.038141 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-15 21:56 | 2021-08-16 16:52 | 300 | 018:56 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21081500294 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1136 | 2021-08-15 | 340800 | keep | 0 | Aug | 2021 | 0.23212 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
UTUADO | 2021-08-15 21:56 | 2021-08-16 14:47 | 250 | 016:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21081500091 | New_Event | Bad Weather | Include | Include | Weather | 1011 | 2021-08-15 | 252750 | keep | 0 | Aug | 2021 | 0.17215 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
UTUADO | 2021-08-15 21:56 | 2021-08-16 15:03 | 200 | 017:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 200 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21081500075 | New_Event | Wire Down | Include | Include | Equipment | 1027 | 2021-08-15 | 205400 | keep | 0 | Aug | 2021 | 0.1399 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
FAJARDO | 2021-08-15 22:13 | 2021-08-16 11:13 | 13 | 013:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | R21081500100 | New_Event | Bad Weather | Include | Include | Weather | 780 | 2021-08-15 | 10140 | keep | 0 | Aug | 2021 | 0.0069063 | 8.8542e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 13
MAYAGÃœEZ | 2021-08-15 22:15 | 2021-08-16 16:53 | 70 | 018:38 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21081500296 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1118 | 2021-08-15 | 78260 | keep | 0 | Aug | 2021 | 0.053303 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
UTUADO | 2021-08-15 22:16 | 2021-08-16 16:05 | 25 | 017:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21081500113 | New_Event | Bad Weather | Include | Include | Weather | 1069 | 2021-08-15 | 26725 | keep | 0 | Aug | 2021 | 0.018202 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-08-15 22:24 | 2021-08-16 10:09 | 10 | 011:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A21081500115 | New_Event | Bad Weather | Include | Include | Weather | 705 | 2021-08-15 | 7050 | keep | 0 | Aug | 2021 | 0.0048017 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-08-15 22:28 | 2021-08-17 15:14 | 30 | 040:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO PORTA FUSIBLE QUEMADO 95% POR EL 1120-10 | S21081500283 | New_Event | Cutout Failure | Include | Include | Equipment | 2446 | 2021-08-15 | 73380 | keep | 0 | Aug | 2021 | 0.049979 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2021-08-15 22:32 | 2021-08-17 16:53 | 35 | 042:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 10 EN TRANSFORMADOR Y SE CERRO PUENTE ABIERTO PRIMARIO | C21081500232 | New_Event | Wire Down | Include | Include | Equipment | 2541 | 2021-08-15 | 88935 | keep | 0 | Aug | 2021 | 0.060573 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-08-15 22:46 | 2021-08-16 18:55 | 100 | 020:09 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081400011 | New_Event | Bad Weather | Include | Include | Weather | 1209 | 2021-08-15 | 120900 | keep | 0 | Aug | 2021 | 0.082344 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-08-15 22:46 | 2021-08-16 14:15 | 50 | 015:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21081500026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 929 | 2021-08-15 | 46450 | keep | 0 | Aug | 2021 | 0.031637 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-08-15 22:46 | 2021-08-16 18:38 | 75 | 019:52 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21081500083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1192 | 2021-08-15 | 89400 | keep | 0 | Aug | 2021 | 0.06089 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
PONCE | 2021-08-15 22:53 | 2021-08-15 22:54 | 1905 | 000:01 | T | NO SE REPORTO CAUSA | REIERRE | P21081500188 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 1905 | keep | 0 | Aug | 2021 | 0.0012975 | 0.0012975 | Momentary | FALSE | FALSE | Not_TMED_Event | 1905
CAGUAS | 2021-08-15 22:56 | 2021-08-17 10:49 | 2 | 035:53 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN RISER Y 2 X 30 EN BANCOS DE TRASFORMADORES AVE | C21081500246 | New_Event |  |  | Include | Wildlife | 2153 | 2021-08-15 | 4306 | keep | 0 | Aug | 2021 | 0.0029328 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2021-08-15 23:09 | 2021-08-16 13:34 | 100 | 014:25 | P | DESGANCHE | 2 X 100 Y 2 X 65 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21081500287 | New_Event | Vegetation Contact | Include | Include | Vegetation | 865 | 2021-08-15 | 86500 | keep | 0 | Aug | 2021 | 0.058915 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-08-15 23:16 | 2021-08-15 23:22 | 315 | 000:06 | T | BREAKER DEFECTUOSO O NO OPERA | SE ABRIO INTERRUPTOR PARA QUE PERSONAL CERRARA AMARRE Y TRANSFERIR CARGAS DEL 3604-06 X 3603-03 AL 3603-01 | C21081500249 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 6 | 2021-08-15 | 1890 | keep | 0 | Aug | 2021 | 0.0012873 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
UTUADO | 2021-08-15 23:20 | 2021-08-17 13:11 | 50 | 037:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21081500117 | New_Event | Bad Weather | Include | Include | Weather | 2271 | 2021-08-15 | 113550 | keep | 0 | Aug | 2021 | 0.077338 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-08-15 23:44 | 2021-08-15 23:45 | 2179 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21081500104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-15 | 2179 | keep | 0 | Aug | 2021 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
CAGUAS | 2021-08-15 23:55 | 2021-08-16 17:13 | 80 | 017:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 Y 1 X 50 EN CORTES DE LINEA MAL TIEMPO | C21081500256 | New_Event | Bad Weather | Include | Include | Weather | 1038 | 2021-08-15 | 83040 | keep | 0 | Aug | 2021 | 0.056558 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-08-16 00:06 | 2021-08-16 00:45 | 1000 | 000:39 | P | NO SE REPORTO CAUSA | SE REMPLASO CAJA EN CORTE DE LINEA | P21081600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 39 | 2021-08-16 | 39000 | keep | 0 | Aug | 2021 | 0.026563 | 0.0006811 | Sustained | FALSE | TRUE | TMED_Event | 1000
MAYAGÃœEZ | 2021-08-16 00:15 | 2021-08-16 00:16 | 3147 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21081600001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 3147 | keep | 0 | Aug | 2021 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | TMED_Event | 3147
MAYAGÃœEZ | 2021-08-16 00:17 | 2021-08-16 00:18 | 3147 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21081600001 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 3147 | keep | 0 | Aug | 2021 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | TMED_Event | 3147
MAYAGÃœEZ | 2021-08-16 00:19 | 2021-08-16 00:20 | 3147 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21081600001 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 3147 | keep | 0 | Aug | 2021 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | TMED_Event | 3147
MAYAGÃœEZ | 2021-08-16 00:29 | 2021-08-16 00:30 | 3147 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21081600001 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 3147 | keep | 0 | Aug | 2021 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | TMED_Event | 3147
MAYAGÃœEZ | 2021-08-16 00:34 | 2021-08-16 00:35 | 3147 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21081600004 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 3147 | keep | 0 | Aug | 2021 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | TMED_Event | 3147
MAYAGÃœEZ | 2021-08-16 00:36 | 2021-08-16 00:37 | 3147 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO SE REPORTO CAUSA SE CERRO POR CONTROL SCADA | M21081600005 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 3147 | keep | 0 | Aug | 2021 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | TMED_Event | 3147
PONCE | 2021-08-16 00:38 | 2021-08-16 12:45 | 100 | 012:07 | P | MAL TIEMPO/RAYOS/WET ASH | 1 FUSIBLE DE 80 EN S/W MAL TIEMPO | P21081600004 | New_Event | Bad Weather | Include | Include | Weather | 727 | 2021-08-16 | 72700 | keep | 0 | Aug | 2021 | 0.049516 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
MAYAGÃœEZ | 2021-08-16 00:40 | 2021-08-16 10:45 | 3147 | 010:05 | T | MAL TIEMPO/RAYOS/WET ASH | SE REPORTO EN EL AREA FUERTTE VIENTO SE CERRO EL INTERRUPTOR | M21081600007 | New_Event | Bad Weather | Include | Include | Weather | 605 | 2021-08-16 | 1903935 | keep | 0 | Aug | 2021 | 1.2968 | 0.0021434 | Sustained | FALSE | FALSE | TMED_Event | 3147
YAUCO | 2021-08-16 00:47 | 2021-08-16 00:48 | 3973 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210816000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 3973 | keep | 0 | Aug | 2021 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | TMED_Event | 3973
MAYAGÃœEZ | 2021-08-16 00:58 | 2021-08-16 00:59 | 2064 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21081600007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 2064 | keep | 0 | Aug | 2021 | 0.0014058 | 0.0014058 | Momentary | FALSE | FALSE | TMED_Event | 2064
MAYAGÃœEZ | 2021-08-16 01:00 | 2021-08-16 01:01 | 1671 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21081600009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 1671 | keep | 0 | Aug | 2021 | 0.0011381 | 0.0011381 | Momentary | FALSE | FALSE | TMED_Event | 1671
MAYAGÃœEZ | 2021-08-16 01:00 | 2021-08-16 01:01 | 1097 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21081600008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 1097 | keep | 0 | Aug | 2021 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | TMED_Event | 1097
MAYAGÃœEZ | 2021-08-16 01:05 | 2021-08-16 01:07 | 4381 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR RECIERRE EN OFF NO SE REPORTO CAUSA | M21081600010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-16 | 8762 | keep | 0 | Aug | 2021 | 0.0059678 | 0.0029839 | Momentary | FALSE | FALSE | TMED_Event | 4381
MAYAGÃœEZ | 2021-08-16 01:07 | 2021-08-16 20:57 | 250 | 019:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 Y 2 X 100 EN CORTES DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081500280 | Partial_restoration | Bad Weather | Include | Include | Weather | 1190 | 2021-08-16 | 297500 | keep | 0 | Aug | 2021 | 0.20263 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
MAYAGÃœEZ | 2021-08-16 01:12 | 2021-08-16 01:13 | 2999 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6406-04 | M21081600012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 2999 | keep | 0 | Aug | 2021 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | TMED_Event | 2999
MAYAGÃœEZ | 2021-08-16 01:12 | 2021-08-16 01:13 | 1597 | 000:01 | T | NO SE REPORTO CAUSA | CARGA POR 6406-02 | M21081600012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 1597 | keep | 0 | Aug | 2021 | 0.0010877 | 0.0010877 | Momentary | FALSE | FALSE | TMED_Event | 1597
MAYAGÃœEZ | 2021-08-16 01:13 | 2021-08-16 10:12 | 80 | 008:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081500211 | New_Event | Bad Weather | Include | Include | Weather | 539 | 2021-08-16 | 43120 | keep | 0 | Aug | 2021 | 0.029369 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
MAYAGÃœEZ | 2021-08-16 01:21 | 2021-08-16 08:24 | 2073 | 007:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13500 SE PASO LA SUBESTACION A LA LINEA 13400 | M21081600021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 423 | 2021-08-16 | 876879 | keep | 0 | Aug | 2021 | 0.59724 | 0.0014119 | Sustained | FALSE | TRUE | TMED_Event | 2073
MAYAGÃœEZ | 2021-08-16 01:21 | 2021-08-16 08:24 | 637 | 007:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13500 SE PASO LA SUBESTACION A LA LINEA 13400 | M21081600021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 423 | 2021-08-16 | 269451 | keep | 0 | Aug | 2021 | 0.18352 | 0.00043386 | Sustained | FALSE | TRUE | TMED_Event | 637
MAYAGÃœEZ | 2021-08-16 01:21 | 2021-08-16 08:24 | 1491 | 007:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13500 SE PASO LA SUBESTACION A LA LINEA 13400 | M21081600021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 423 | 2021-08-16 | 630693 | keep | 0 | Aug | 2021 | 0.42956 | 0.0010155 | Sustained | FALSE | TRUE | TMED_Event | 1491
MAYAGÃœEZ | 2021-08-16 01:21 | 2021-08-16 17:27 | 4892 | 016:06 | S | MAL TIEMPO/RAYOS/WET ASH | LA LINEA 13500 DISPARO Y EL INTERRUPTOR 6705-02 TAMBIEN DISPARO. EL MISLO ESTA LLEVANCO LA CARGA DEL 6705-01. SE PATRULLO Y NO SE ENCONTRO CAUSA SOLO MAL TIEMPO EN EL AREA | M21081600022 | New_Event | Bad Weather | Include | Include | Weather | 966 | 2021-08-16 | 4725672 | keep | 0 | Aug | 2021 | 3.2186 | 0.0033319 | Sustained | FALSE | TRUE | TMED_Event | 4892
MAYAGÃœEZ | 2021-08-16 01:21 | 2021-08-16 17:27 | 160 | 016:06 | S | MAL TIEMPO/RAYOS/WET ASH | LA LINEA 13500 DISPARO Y EL INTERRUPTOR 6705-02 TAMBIEN DISPARO. EL MISLO ESTA LLEVANCO LA CARGA DEL 6705-01. SE PATRULLO Y NO SE ENCONTRO CAUSA SOLO MAL TIEMPO EN EL AREA | M21081600022 | New_Event | Bad Weather | Include | Include | Weather | 966 | 2021-08-16 | 154560 | keep | 0 | Aug | 2021 | 0.10527 | 0.00010898 | Sustained | FALSE | TRUE | TMED_Event | 160
MAYAGÃœEZ | 2021-08-16 01:49 | 2021-08-16 11:48 | 528 | 009:59 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO EN EL TRONCAL DEL ALIMENTADOR | M21081600000 | New_Event | Wire Down | Include | Include | Equipment | 599 | 2021-08-16 | 316272 | keep | 0 | Aug | 2021 | 0.21541 | 0.00035962 | Sustained | FALSE | FALSE | TMED_Event | 528
MAYAGÃœEZ | 2021-08-16 01:49 | 2021-08-16 11:48 | 1352 | 009:59 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO EN EL TRONCAL DEL ALIMENTADOR 6012-01 QUE ESTA LLEVANDO LA CARGA DEL ALIMENTADOR 6012-05 | M21081600000 | New_Event | Wire Down | Include | Include | Equipment | 599 | 2021-08-16 | 809848 | keep | 0 | Aug | 2021 | 0.55158 | 0.00092084 | Sustained | FALSE | FALSE | TMED_Event | 1352
MAYAGÃœEZ | 2021-08-16 01:49 | 2021-08-16 11:48 | 871 | 009:59 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO EN EL TRONCAL DEL ALIMENTADOR 6012-01 QUE ESTA LLEVANDO LA CARGA DEL 6014-03 | M21081600000 | New_Event | Wire Down | Include | Include | Equipment | 599 | 2021-08-16 | 521729 | keep | 0 | Aug | 2021 | 0.35535 | 0.00059323 | Sustained | FALSE | FALSE | TMED_Event | 871
MAYAGÃœEZ | 2021-08-16 02:22 | 2021-08-16 16:45 | 100 | 014:23 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081600027 | New_Event | Bad Weather | Include | Include | Weather | 863 | 2021-08-16 | 86300 | keep | 0 | Aug | 2021 | 0.058779 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
PONCE | 2021-08-16 02:40 | 2021-08-16 08:41 | 1076 | 006:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA DE RAMBLA | P21081600050 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 361 | 2021-08-16 | 388436 | keep | 0 | Aug | 2021 | 0.26456 | 0.00073286 | Sustained | FALSE | FALSE | TMED_Event | 1076
PONCE | 2021-08-16 02:40 | 2021-08-16 08:41 | 595 | 006:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA DE RAMBLA | P21081600050 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 361 | 2021-08-16 | 214795 | keep | 0 | Aug | 2021 | 0.1463 | 0.00040525 | Sustained | FALSE | FALSE | TMED_Event | 595
PONCE | 2021-08-16 02:40 | 2021-08-16 08:41 | 1007 | 006:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA DE RAMBLA | P21081600050 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 361 | 2021-08-16 | 363527 | keep | 0 | Aug | 2021 | 0.2476 | 0.00068586 | Sustained | FALSE | FALSE | TMED_Event | 1007
PONCE | 2021-08-16 02:40 | 2021-08-16 08:41 | 9 | 006:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA DE RAMBLA | P21081600050 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 361 | 2021-08-16 | 3249 | keep | 0 | Aug | 2021 | 0.0022129 | 6.1299e-06 | Sustained | FALSE | FALSE | TMED_Event | 9
PONCE | 2021-08-16 02:40 | 2021-08-16 08:46 | 3744 | 006:06 | S | LINEA DE TRANSMISION 38KV | DISPARO BARRA DE RAMBLA | P21081600051 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 366 | 2021-08-16 | 1370304 | keep | 0 | Aug | 2021 | 0.93331 | 0.00255 | Sustained | FALSE | FALSE | TMED_Event | 3744
PONCE | 2021-08-16 02:40 | 2021-08-16 08:46 | 2379 | 006:06 | S | LINEA DE TRANSMISION 38KV | DISPARO BARRA DE RAMBLA | P21081600051 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 366 | 2021-08-16 | 870714 | keep | 0 | Aug | 2021 | 0.59304 | 0.0016203 | Sustained | FALSE | FALSE | TMED_Event | 2379
PONCE | 2021-08-16 02:40 | 2021-08-16 08:46 | 778 | 006:06 | S | LINEA DE TRANSMISION 38KV | DISPARO BARRA DE RAMBLA | P21081600051 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 366 | 2021-08-16 | 284748 | keep | 0 | Aug | 2021 | 0.19394 | 0.00052989 | Sustained | FALSE | FALSE | TMED_Event | 778
PONCE | 2021-08-16 02:40 | 2021-08-16 08:46 | 1746 | 006:06 | S | LINEA DE TRANSMISION 38KV | DISPARO BARRA DE RAMBLA | P21081600051 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 366 | 2021-08-16 | 639036 | keep | 0 | Aug | 2021 | 0.43524 | 0.0011892 | Sustained | FALSE | FALSE | TMED_Event | 1746
PONCE | 2021-08-16 02:40 | 2021-08-16 08:46 | 11 | 006:06 | S | LINEA DE TRANSMISION 38KV | DISPARO BARRA DE RAMBLA | P21081600051 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 366 | 2021-08-16 | 4026 | keep | 0 | Aug | 2021 | 0.0027421 | 7.492e-06 | Sustained | FALSE | FALSE | TMED_Event | 11
PONCE | 2021-08-16 02:40 | 2021-08-16 09:45 | 293 | 007:05 | S | MAL TIEMPO/RAYOS/WET ASH | DSIPARO DE BARRA DE RAMBLA | P2108/16/000 | New_Event | Bad Weather | Include | Include | Weather | 425 | 2021-08-16 | 124525 | keep | 0 | Aug | 2021 | 0.084813 | 0.00019956 | Sustained | FALSE | FALSE | TMED_Event | 293
PONCE | 2021-08-16 02:40 | 2021-08-16 09:45 | 253 | 007:05 | S | MAL TIEMPO/RAYOS/WET ASH | DSIPARO DE BARRA DE RAMBLA | P2108/16/000 | New_Event | Bad Weather | Include | Include | Weather | 425 | 2021-08-16 | 107525 | keep | 0 | Aug | 2021 | 0.073235 | 0.00017232 | Sustained | FALSE | FALSE | TMED_Event | 253
PONCE | 2021-08-16 02:40 | 2021-08-16 09:45 | 900 | 007:05 | S | MAL TIEMPO/RAYOS/WET ASH | DSIPARO DE BARRA DE RAMBLA | P2108/16/000 | New_Event | Bad Weather | Include | Include | Weather | 425 | 2021-08-16 | 382500 | keep | 0 | Aug | 2021 | 0.26052 | 0.00061299 | Sustained | FALSE | FALSE | TMED_Event | 900
PONCE | 2021-08-16 02:40 | 2021-08-16 09:45 | 1615 | 007:05 | S | MAL TIEMPO/RAYOS/WET ASH | DSIPARO DE BARRA DE RAMBLA | P2108/16/000 | New_Event | Bad Weather | Include | Include | Weather | 425 | 2021-08-16 | 686375 | keep | 0 | Aug | 2021 | 0.46749 | 0.0011 | Sustained | FALSE | FALSE | TMED_Event | 1615
PONCE | 2021-08-16 02:40 | 2021-08-16 09:45 | 3 | 007:05 | S | MAL TIEMPO/RAYOS/WET ASH | DSIPARO DE BARRA DE RAMBLA | P2108/16/000 | New_Event | Bad Weather | Include | Include | Weather | 425 | 2021-08-16 | 1275 | keep | 0 | Aug | 2021 | 0.0008684 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
ARECIBO | 2021-08-16 04:09 | 2021-08-16 15:00 | 15 | 010:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21081600009 | New_Event | Bad Weather | Include | Include | Weather | 651 | 2021-08-16 | 9765 | keep | 0 | Aug | 2021 | 0.0066509 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
FAJARDO | 2021-08-16 04:31 | 2021-08-16 04:32 | 76 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | R21081600002 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-08-16 | 76 | keep | 0 | Aug | 2021 | 5.1763e-05 | 5.1763e-05 | Momentary | FALSE | FALSE | TMED_Event | 76
FAJARDO | 2021-08-16 04:32 | 2021-08-16 09:36 | 1 | 005:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN RISER MAL TIEMPO | R21081600010 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 304 | 2021-08-16 | 304 | keep | 0 | Aug | 2021 | 0.00020705 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2021-08-16 05:16 | 2021-08-16 15:24 | 60 | 010:08 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 65 EN SU Y SE REPARO TERMINACION | B21081600002 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 608 | 2021-08-16 | 36480 | keep | 0 | Aug | 2021 | 0.024846 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
AGUADILLA | 2021-08-16 05:25 | 2021-08-16 15:53 | 200 | 010:28 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | M21081600043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 628 | 2021-08-16 | 125600 | keep | 0 | Aug | 2021 | 0.085546 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
MAYAGÃœEZ | 2021-08-16 05:41 | 2021-08-17 14:20 | 10 | 032:39 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA 4160/ 120/240V FID-24406034 | M21081600046 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1959 | 2021-08-16 | 19590 | keep | 0 | Aug | 2021 | 0.013343 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
PONCE | 2021-08-16 05:48 | 2021-08-16 05:49 | 948 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21081600055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 948 | keep | 0 | Aug | 2021 | 0.00064568 | 0.00064568 | Momentary | FALSE | FALSE | TMED_Event | 948
BARRANQUITAS | 2021-08-16 06:08 | 2021-08-17 06:04 | 500 | 023:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 EN CORTE DE LINEA SE LEVANTO CONDUCTOR DEL SUELO | C21081600016 | New_Event | Wire Down | Include | Include | Equipment | 1436 | 2021-08-16 | 718000 | keep | 0 | Aug | 2021 | 0.48903 | 0.00034055 | Sustained | FALSE | TRUE | TMED_Event | 500
CAGUAS | 2021-08-16 06:22 | 2021-08-16 15:40 | 1153 | 009:18 | S | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 125 SLOW SPEED REMPLAZO BUS SUPPORT INSULATOR Y REPARO EL NUMERO 5 | C21081600023 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 558 | 2021-08-16 | 643374 | keep | 0 | Aug | 2021 | 0.4382 | 0.0007853 | Sustained | FALSE | FALSE | TMED_Event | 1153
CAGUAS | 2021-08-16 06:22 | 2021-08-16 15:40 | 1709 | 009:18 | S | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 125 SLOW SPEED REMPLAZO BUS SUPPORT INSULATOR Y REPARO EL NUMERO 5 | C21081600023 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 558 | 2021-08-16 | 953622 | keep | 0 | Aug | 2021 | 0.64951 | 0.001164 | Sustained | FALSE | FALSE | TMED_Event | 1709
CAGUAS | 2021-08-16 06:22 | 2021-08-16 15:40 | 1320 | 009:18 | S | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 125 SLOW SPEED REMPLAZO BUS SUPPORT INSULATOR Y REPARO EL NUMERO 5 | C21081600023 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 558 | 2021-08-16 | 736560 | keep | 0 | Aug | 2021 | 0.50167 | 0.00089905 | Sustained | FALSE | FALSE | TMED_Event | 1320
BAYAMON | 2021-08-16 06:27 | 2021-08-16 11:56 | 60 | 005:29 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA CARGA TRANSFERIDA AL 1709-01 | B21081600004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 329 | 2021-08-16 | 19740 | keep | 0 | Aug | 2021 | 0.013445 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
BAYAMON | 2021-08-16 06:34 | 2021-08-16 13:54 | 10 | 007:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | B21081600005 | New_Event | Wire Down | Include | Include | Equipment | 440 | 2021-08-16 | 4400 | keep | 0 | Aug | 2021 | 0.0029968 | 6.811e-06 | Sustained | FALSE | TRUE | TMED_Event | 10
BAYAMON | 2021-08-16 06:37 | 2021-08-16 14:31 | 75 | 007:54 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B21081600006 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 474 | 2021-08-16 | 35550 | keep | 0 | Aug | 2021 | 0.024213 | 5.1082e-05 | Sustained | FALSE | TRUE | TMED_Event | 75
SAN JUAN | 2021-08-16 06:38 | 2021-08-16 13:02 | 30 | 006:24 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S21081600006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 384 | 2021-08-16 | 11520 | keep | 0 | Aug | 2021 | 0.0078462 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
BAYAMON | 2021-08-16 06:40 | 2021-08-16 20:09 | 50 | 013:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA Y SE DESGANCHO | S21081600008 | New_Event | Cutout Failure | Include | Include | Equipment | 809 | 2021-08-16 | 40450 | keep | 0 | Aug | 2021 | 0.02755 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
AGUADILLA | 2021-08-16 06:56 | 2021-08-16 18:17 | 100 | 011:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE | M21081600064 | New_Event | Wire Down | Include | Include | Equipment | 681 | 2021-08-16 | 68100 | keep | 0 | Aug | 2021 | 0.046383 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
CANOVANAS | 2021-08-16 06:57 | 2021-08-16 10:38 | 2 | 003:41 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | R21081600007 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 221 | 2021-08-16 | 442 | keep | 0 | Aug | 2021 | 0.00030104 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
BAYAMON | 2021-08-16 07:07 | 2021-08-16 13:35 | 12 | 006:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | B21081600010 | New_Event | Secondary Wire Down | Include | Include | Equipment | 388 | 2021-08-16 | 4656 | keep | 0 | Aug | 2021 | 0.0031712 | 8.1731e-06 | Sustained | FALSE | TRUE | TMED_Event | 12
YAUCO | 2021-08-16 07:16 | 2021-08-16 12:25 | 80 | 005:09 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P21081600089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 309 | 2021-08-16 | 24720 | keep | 0 | Aug | 2021 | 0.016837 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
HUMACAO | 2021-08-16 07:19 | 2021-08-16 15:19 | 7 | 008:00 | P | SECUNDARIA/DESGANCHE | ABRIO TRANSFORMADOR PARA DESGANCHAR Y REPARAR SECUNDARIA | C21081600039 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 480 | 2021-08-16 | 3360 | keep | 0 | Aug | 2021 | 0.0022885 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
MAYAGÃœEZ | 2021-08-16 07:21 | 2021-08-16 14:01 | 2530 | 006:40 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA EN EL TRONCAL DEL ALIMENTADOR 6008-05 Y SE CERRO EL INTERRUPTOR ESTE ESTA LLEVANDO LA CARGA DEL 6008-04 | M21081600000 | New_Event | Wire Down | Include | Include | Equipment | 400 | 2021-08-16 | 1012000 | keep | 0 | Aug | 2021 | 0.68927 | 0.0017232 | Sustained | FALSE | TRUE | TMED_Event | 2530
MAYAGÃœEZ | 2021-08-16 07:21 | 2021-08-16 14:01 | 199 | 006:40 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA EN EL TRONCAL DEL ALIMENTADOR Y SE CERRO EL INTERRUPTOR | M21081600000 | New_Event | Wire Down | Include | Include | Equipment | 400 | 2021-08-16 | 79600 | keep | 0 | Aug | 2021 | 0.054215 | 0.00013554 | Sustained | FALSE | TRUE | TMED_Event | 199
MAYAGÃœEZ | 2021-08-16 07:21 | 2021-08-16 21:44 | 100 | 014:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 Y 1 X 40 EN CORTES DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081600076 | New_Event | Bad Weather | Include | Include | Weather | 863 | 2021-08-16 | 86300 | keep | 0 | Aug | 2021 | 0.058779 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
MAYAGÃœEZ | 2021-08-16 07:25 | 2021-08-16 17:09 | 20 | 009:44 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA REQUIERE DESGANCHE | M21081600079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 584 | 2021-08-16 | 11680 | keep | 0 | Aug | 2021 | 0.0079552 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
SAN JUAN | 2021-08-16 07:31 | 2021-08-16 07:32 | 225 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21081600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 225 | keep | 0 | Aug | 2021 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | TMED_Event | 225
SAN JUAN | 2021-08-16 07:31 | 2021-08-16 07:32 | 3957 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21081600000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-08-16 | 3957 | keep | 0 | Aug | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | TMED_Event | 3957
BAYAMON | 2021-08-16 07:32 | 2021-08-16 20:32 | 75 | 013:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE LLEVO LINEA A AISLADOR | S21081600136 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 780 | 2021-08-16 | 58500 | keep | 0 | Aug | 2021 | 0.039844 | 5.1082e-05 | Sustained | FALSE | TRUE | TMED_Event | 75
MAYAGÃœEZ | 2021-08-16 07:33 | 2021-08-16 15:29 | 150 | 007:56 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN CORTES DE LINEA REQUIERE DESGANCHE | M21081600086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 476 | 2021-08-16 | 71400 | keep | 0 | Aug | 2021 | 0.04863 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
BAYAMON | 2021-08-16 07:34 | 2021-08-16 07:35 | 186 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21081600012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 186 | keep | 0 | Aug | 2021 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | TMED_Event | 186
BAYAMON | 2021-08-16 07:35 | 2021-08-16 17:48 | 1 | 010:13 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | B21081600018 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 613 | 2021-08-16 | 613 | keep | 0 | Aug | 2021 | 0.00041751 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2021-08-16 07:36 | 2021-08-16 07:37 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21081600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 2605 | keep | 0 | Aug | 2021 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | TMED_Event | 2605
FAJARDO | 2021-08-16 07:52 | 2021-08-16 10:32 | 32 | 002:40 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 Y 2 X 40 EN CORTES DE LINEA MAL TIEMPO | R21081600013 | New_Event | Bad Weather | Include | Include | Weather | 160 | 2021-08-16 | 5120 | keep | 0 | Aug | 2021 | 0.0034872 | 2.1795e-05 | Sustained | FALSE | TRUE | TMED_Event | 32
ARECIBO | 2021-08-16 07:55 | 2021-08-16 17:40 | 20 | 009:45 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21081600021 | New_Event | Bad Weather | Include | Include | Weather | 585 | 2021-08-16 | 11700 | keep | 0 | Aug | 2021 | 0.0079688 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
PONCE | 2021-08-16 08:08 | 2021-08-16 09:33 | 1979 | 001:25 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO POSTATIL SE FIJO CABLE SFADO EN MACHETES | P21081600119 | New_Event | Wire Down | Include | Include | Equipment | 85 | 2021-08-16 | 168215 | keep | 0 | Aug | 2021 | 0.11457 | 0.0013479 | Sustained | FALSE | FALSE | TMED_Event | 1979
PONCE | 2021-08-16 08:08 | 2021-08-16 09:33 | 3114 | 001:25 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO POSTATIL SE FIJO CABLE SFADO EN MACHETES | P21081600119 | New_Event | Wire Down | Include | Include | Equipment | 85 | 2021-08-16 | 264690 | keep | 0 | Aug | 2021 | 0.18028 | 0.0021209 | Sustained | FALSE | FALSE | TMED_Event | 3114
PONCE | 2021-08-16 08:08 | 2021-08-16 09:33 | 5069 | 001:25 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO POSTATIL SE FIJO CABLE SFADO EN MACHETES | P21081600119 | New_Event | Wire Down | Include | Include | Equipment | 85 | 2021-08-16 | 430865 | keep | 0 | Aug | 2021 | 0.29346 | 0.0034525 | Sustained | FALSE | FALSE | TMED_Event | 5069
PONCE | 2021-08-16 08:08 | 2021-08-16 09:33 | 2696 | 001:25 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PORTATIL SE FIJO CABLE SAFADO EN MACHETES | P21081600119 | New_Event | Wire Down | Include | Include | Equipment | 85 | 2021-08-16 | 229160 | keep | 0 | Aug | 2021 | 0.15608 | 0.0018362 | Sustained | FALSE | FALSE | TMED_Event | 2696
PONCE | 2021-08-16 08:08 | 2021-08-16 09:33 | 5063 | 001:25 | S | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO POSTATIL SE FIJO CABLE SFADO EN MACHETES | P21081600119 | New_Event | Wire Down | Include | Include | Equipment | 85 | 2021-08-16 | 430355 | keep | 0 | Aug | 2021 | 0.29311 | 0.0034484 | Sustained | FALSE | FALSE | TMED_Event | 5063
MAYAGÃœEZ | 2021-08-16 08:09 | 2021-08-16 16:19 | 70 | 008:10 | P | DESGANCHE | 1 X 80 N CORTE DE LINEA | M21081600114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 490 | 2021-08-16 | 34300 | keep | 0 | Aug | 2021 | 0.023362 | 4.7677e-05 | Sustained | FALSE | TRUE | TMED_Event | 70
CAGUAS | 2021-08-16 08:12 | 2021-08-17 15:57 | 9 | 031:45 | P | DESGANCHE | 1 X 10 EN CORTE DE LINEA | C21081600052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1905 | 2021-08-16 | 17145 | keep | 0 | Aug | 2021 | 0.011677 | 6.1299e-06 | Sustained | FALSE | TRUE | TMED_Event | 9
VEGA BAJA | 2021-08-16 08:22 | 2021-08-16 09:50 | 10 | 001:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA | B21081500127 | New_Event | Cutout Failure | Include | Include | Equipment | 88 | 2021-08-16 | 880 | keep | 0 | Aug | 2021 | 0.00059936 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
MAYAGÃœEZ | 2021-08-16 08:25 | 2021-08-16 21:20 | 200 | 012:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081600126 | New_Event | Bad Weather | Include | Include | Weather | 775 | 2021-08-16 | 155000 | keep | 0 | Aug | 2021 | 0.10557 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
CAGUAS | 2021-08-16 08:28 | 2021-08-16 09:07 | 918 | 000:39 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR CONDUCTORES EN EL SUELO | C21081600061 | New_Event | Wire Down | Include | Include | Equipment | 39 | 2021-08-16 | 35802 | keep | 0 | Aug | 2021 | 0.024385 | 0.00062525 | Sustained | FALSE | FALSE | TMED_Event | 918
CAGUAS | 2021-08-16 08:30 | 2021-08-17 09:53 | 1 | 025:23 | P | DESGANCHE | 1 X 15 EN BANCO DE TRANSFORMADORES | C21081600059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1523 | 2021-08-16 | 1523 | keep | 0 | Aug | 2021 | 0.0010373 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
YAUCO | 2021-08-16 08:38 | 2021-08-16 14:06 | 25 | 005:28 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA POR DESGANCHE | P21081600153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 328 | 2021-08-16 | 8200 | keep | 0 | Aug | 2021 | 0.005585 | 1.7027e-05 | Sustained | FALSE | TRUE | TMED_Event | 25
PONCE | 2021-08-16 08:47 | 2021-08-16 09:47 | 2379 | 001:00 | T | MAL TIEMPO/RAYOS/WET ASH | SE CERRO BKR | P21081600153 | New_Event | Bad Weather | Include | Include | Weather | 60 | 2021-08-16 | 142740 | keep | 0 | Aug | 2021 | 0.09722 | 0.0016203 | Sustained | FALSE | FALSE | TMED_Event | 2379
HUMACAO | 2021-08-16 08:53 | 2021-08-16 17:03 | 8 | 008:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | C21081600069 | New_Event | Secondary Wire Down | Include | Include | Equipment | 490 | 2021-08-16 | 3920 | keep | 0 | Aug | 2021 | 0.0026699 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
CAGUAS | 2021-08-16 08:53 | 2021-08-16 13:58 | 1 | 005:05 | P | DESGANCHE | 3 X 50 EN CORTE DE LINEA | C21081600070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 305 | 2021-08-16 | 305 | keep | 0 | Aug | 2021 | 0.00020773 | 6.811e-07 | Sustained | FALSE | TRUE | TMED_Event | 1
HUMACAO | 2021-08-16 08:55 | 2021-08-16 19:35 | 160 | 010:40 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA CONTRATISTA DESGANCHAR | C21081600112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 640 | 2021-08-16 | 102400 | keep | 0 | Aug | 2021 | 0.069744 | 0.00010898 | Sustained | FALSE | TRUE | TMED_Event | 160
ARECIBO | 2021-08-16 08:55 | 2021-08-16 11:22 | 20 | 002:27 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21081500040 | New_Event | Bad Weather | Include | Include | Weather | 147 | 2021-08-16 | 2940 | keep | 0 | Aug | 2021 | 0.0020024 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
PONCE | 2021-08-16 08:57 | 2021-08-16 18:38 | 50 | 009:41 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA POR DESGANCHE | P21081600247 | New_Event | Vegetation Contact | Include | Include | Vegetation | 581 | 2021-08-16 | 29050 | keep | 0 | Aug | 2021 | 0.019786 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
HUMACAO | 2021-08-16 09:01 | 2021-08-16 19:35 | 173 | 010:34 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA CONTRATISTA DESGANCHAR | C21081600075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 634 | 2021-08-16 | 109682 | keep | 0 | Aug | 2021 | 0.074704 | 0.00011783 | Sustained | FALSE | TRUE | TMED_Event | 173
CAGUAS | 2021-08-16 09:07 | 2021-08-16 18:54 | 461 | 009:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTO CONDUCTORES Y CERRO MACHETES | C21081600079 | Partial_restoration | Wire Down | Include | Include | Equipment | 587 | 2021-08-16 | 270607 | keep | 0 | Aug | 2021 | 0.18431 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
BAYAMON | 2021-08-16 09:15 | 2021-08-16 09:16 | 723 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVANDO 1711-05 | B21081600026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 723 | keep | 0 | Aug | 2021 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | TMED_Event | 723
BAYAMON | 2021-08-16 09:15 | 2021-08-16 09:16 | 1976 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL CARGA POR 1711-02 | B21081600026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 1976 | keep | 0 | Aug | 2021 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | TMED_Event | 1976
MAYAGÃœEZ | 2021-08-16 09:19 | 2021-08-16 17:30 | 300 | 008:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21081600171 | New_Event | Wire Down | Include | Include | Equipment | 491 | 2021-08-16 | 147300 | keep | 0 | Aug | 2021 | 0.10033 | 0.00020433 | Sustained | FALSE | TRUE | TMED_Event | 300
MAYAGÃœEZ | 2021-08-16 09:27 | 2021-08-16 12:00 | 100 | 002:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081600177 | New_Event | Bad Weather | Include | Include | Weather | 153 | 2021-08-16 | 15300 | keep | 0 | Aug | 2021 | 0.010421 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
BAYAMON | 2021-08-16 09:28 | 2021-08-17 11:12 | 15 | 025:44 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR TIPO PAD MOUNTED T-7 | B21081600062 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1544 | 2021-08-16 | 23160 | keep | 0 | Aug | 2021 | 0.015774 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
MAYAGÃœEZ | 2021-08-16 09:35 | 2021-08-16 16:16 | 16 | 006:41 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRAMSFORMADOR QUEMADO 37.5 KVA | M21081600186 | New_Event | Service Transformer Failure | Include | Include | Equipment | 401 | 2021-08-16 | 6416 | keep | 0 | Aug | 2021 | 0.0043699 | 1.0898e-05 | Sustained | FALSE | FALSE | TMED_Event | 16
UTUADO | 2021-08-16 09:40 | 2021-08-16 17:30 | 175 | 007:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21081600052 | New_Event | Bad Weather | Include | Include | Weather | 470 | 2021-08-16 | 82250 | keep | 0 | Aug | 2021 | 0.05602 | 0.00011919 | Sustained | FALSE | TRUE | TMED_Event | 175
MAYAGÃœEZ | 2021-08-16 09:44 | 2021-08-16 16:00 | 5 | 006:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | M21081600192 | New_Event | Secondary Wire Down | Include | Include | Equipment | 376 | 2021-08-16 | 1880 | keep | 0 | Aug | 2021 | 0.0012805 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
CANOVANAS | 2021-08-16 09:45 | 2021-08-16 11:42 | 115 | 001:57 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | R21081600021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2021-08-16 | 13455 | keep | 0 | Aug | 2021 | 0.0091641 | 7.8326e-05 | Sustained | FALSE | TRUE | TMED_Event | 115
HUMACAO | 2021-08-16 09:51 | 2021-08-17 11:26 | 7 | 025:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE DE TRANSFORMADOR | C21081600174 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1535 | 2021-08-16 | 10745 | keep | 0 | Aug | 2021 | 0.0073184 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
AGUADILLA | 2021-08-16 09:52 | 2021-08-16 18:39 | 200 | 008:47 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | M21081600197 | New_Event | Vegetation Contact | Include | Include | Vegetation | 527 | 2021-08-16 | 105400 | keep | 0 | Aug | 2021 | 0.071787 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
GUAYAMA | 2021-08-16 09:55 | 2021-08-16 11:20 | 50 | 001:25 | P | MAL TIEMPO/RAYOS/WET ASH | SE REMPASO CAJA PRIMARIA RN CORTE DE LINEA | P21081600206 | New_Event | Bad Weather | Include | Include | Weather | 85 | 2021-08-16 | 4250 | keep | 0 | Aug | 2021 | 0.0028947 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
UTUADO | 2021-08-16 09:58 | 2021-08-17 18:45 | 150 | 032:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A21081600056 | New_Event | Wire Down | Include | Include | Equipment | 1967 | 2021-08-16 | 295050 | keep | 0 | Aug | 2021 | 0.20096 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
CAGUAS | 2021-08-16 10:00 | 2021-08-16 10:01 | 4390 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21081600089 | New_Event |  |  | Include | Wildlife | 1 | 2021-08-16 | 4390 | keep | 0 | Aug | 2021 | 0.00299 | 0.00299 | Momentary | FALSE | FALSE | TMED_Event | 4390
CAGUAS | 2021-08-16 10:01 | 2021-08-16 10:50 | 4000 | 000:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | SECCIONALIZARON POSTE PARTIDO POR CAMION | C21081600123 | 1st_after_momentary |  |  | Include | Wildlife | 49 | 2021-08-16 | 196000 | keep | 0 | Aug | 2021 | 0.13349 | 0.0027244 | Sustained | FALSE | FALSE | TMED_Event | 4000
CAGUAS | 2021-08-16 10:01 | 2021-08-16 10:50 | 39 | 000:49 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DERRIBADO DE 37.5 X 37.5KVA | C21081600123 | New_Event | Service Transformer Failure | Include | Include | Equipment | 49 | 2021-08-16 | 1911 | keep | 0 | Aug | 2021 | 0.0013016 | 2.6563e-05 | Sustained | FALSE | FALSE | TMED_Event | 39
BAYAMON | 2021-08-16 10:07 | 2021-08-16 11:22 | 353 | 001:15 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE DE LINEA TRONCAL | S21081600057 | Additional_clients | Wire Down | Include | Include | Equipment | 75 | 2021-08-16 | 26475 | keep | 0 | Aug | 2021 | 0.018032 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
PONCE | 2021-08-16 10:07 | 2021-08-16 17:19 | 948 | 007:12 | T | DESGANCHE | SE HIZO DESGANCHE MASIVO Y SE RETIRO ARBOL SOBRE LINEA | P21081600211 | New_Event | Vegetation Contact | Include | Include | Vegetation | 432 | 2021-08-16 | 409536 | keep | 0 | Aug | 2021 | 0.27893 | 0.00064568 | Sustained | FALSE | TRUE | TMED_Event | 948
MAYAGÃœEZ | 2021-08-16 10:12 | 2021-08-16 10:13 | 2999 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21081600206 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 2999 | keep | 0 | Aug | 2021 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | TMED_Event | 2999
MAYAGÃœEZ | 2021-08-16 10:13 | 2021-08-16 10:22 | 80 | 000:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081500211 | New_Event | Bad Weather | Include | Include | Weather | 9 | 2021-08-16 | 720 | keep | 0 | Aug | 2021 | 0.00049039 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
CANOVANAS | 2021-08-16 10:17 | 2021-08-16 19:15 | 6 | 008:58 | P | OTRAS CAUSAS | 1 X 15 EN TRANSFORMADOR RETIRO PELIGRO | R21081600024 | New_Event | Other Causes | Include | Include | Other | 538 | 2021-08-16 | 3228 | keep | 0 | Aug | 2021 | 0.0021986 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
AGUADILLA | 2021-08-16 10:28 | 2021-08-16 20:39 | 90 | 010:11 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | M21081600214 | New_Event | Vegetation Contact | Include | Include | Vegetation | 611 | 2021-08-16 | 54990 | keep | 0 | Aug | 2021 | 0.037453 | 6.1299e-05 | Sustained | FALSE | TRUE | TMED_Event | 90
VEGA BAJA | 2021-08-16 10:28 | 2021-08-16 11:09 | 30 | 000:41 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21081600034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 41 | 2021-08-16 | 1230 | keep | 0 | Aug | 2021 | 0.00083775 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
CAGUAS | 2021-08-16 10:32 | 2021-08-16 13:11 | 2906 | 002:39 | T | DESGANCHE | SE ABRIO N/O CONTRA EL 3603-01 PARA RETIRAR ARBOL DE LAS LINEAS | C21081600129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2021-08-16 | 462054 | keep | 0 | Aug | 2021 | 0.3147 | 0.0019793 | Sustained | FALSE | TRUE | TMED_Event | 2906
YAUCO | 2021-08-16 10:35 | 2021-08-16 10:36 | 100 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | P21081600172 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-08-16 | 100 | keep | 0 | Aug | 2021 | 6.811e-05 | 6.811e-05 | Momentary | FALSE | TRUE | TMED_Event | 100
MAYAGÃœEZ | 2021-08-16 10:36 | 2021-08-16 13:42 | 8 | 003:06 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081600218 | New_Event | Bad Weather | Include | Include | Weather | 186 | 2021-08-16 | 1488 | keep | 0 | Aug | 2021 | 0.0010135 | 5.4488e-06 | Sustained | FALSE | TRUE | TMED_Event | 8
YAUCO | 2021-08-16 10:37 | 2021-08-16 10:38 | 50 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X DE 50 EN CORTE DE LINEA MAL TIEMPO | P21081600106 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-08-16 | 50 | keep | 0 | Aug | 2021 | 3.4055e-05 | 3.4055e-05 | Momentary | FALSE | TRUE | TMED_Event | 50
ARECIBO | 2021-08-16 10:45 | 2021-08-16 11:40 | 20 | 000:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21081600070 | New_Event | Bad Weather | Include | Include | Weather | 55 | 2021-08-16 | 1100 | keep | 0 | Aug | 2021 | 0.0007492 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
CAGUAS | 2021-08-16 10:47 | 2021-08-16 11:46 | 30 | 000:59 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA 1 X 10 EN TRANSFORMADOR | C21081600035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2021-08-16 | 1770 | keep | 0 | Aug | 2021 | 0.0012055 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
CANOVANAS | 2021-08-16 10:49 | 2021-08-16 13:45 | 15 | 002:56 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA DESGANCHE | R21081600027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2021-08-16 | 2640 | keep | 0 | Aug | 2021 | 0.0017981 | 1.0216e-05 | Sustained | FALSE | TRUE | TMED_Event | 15
CAGUAS | 2021-08-16 10:50 | 2021-08-16 11:31 | 4390 | 000:41 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO INTERRUPTOR POR POSTE PARTIDO POR CAMION | C21081600107 | Additional_clients |  |  | Include | Wildlife | 41 | 2021-08-16 | 179990 | keep | 0 | Aug | 2021 | 0.12259 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
CAGUAS | 2021-08-16 10:58 | 2021-08-17 18:10 | 100 | 031:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | C21081600109 | New_Event |  |  | Include | Wildlife | 1872 | 2021-08-16 | 187200 | keep | 0 | Aug | 2021 | 0.1275 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
CAGUAS | 2021-08-16 11:04 | 2021-08-17 10:21 | 30 | 023:17 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21081600114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1397 | 2021-08-16 | 41910 | keep | 0 | Aug | 2021 | 0.028545 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
CANOVANAS | 2021-08-16 11:07 | 2021-08-16 11:50 | 11 | 000:43 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | R21081600028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 43 | 2021-08-16 | 473 | keep | 0 | Aug | 2021 | 0.00032216 | 7.492e-06 | Sustained | FALSE | TRUE | TMED_Event | 11
AGUADILLA | 2021-08-16 11:12 | 2021-08-16 13:27 | 5 | 002:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJAS QUEMADAS | M21081200129 | New_Event | Cutout Failure | Include | Include | Equipment | 135 | 2021-08-16 | 675 | keep | 0 | Aug | 2021 | 0.00045974 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
GUAYAMA | 2021-08-16 11:13 | 2021-08-16 12:31 | 50 | 001:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 FUSIBLE DE 40 EN CORTE DE LINEA MAL TIEMPO | P21081600243 | New_Event | Bad Weather | Include | Include | Weather | 78 | 2021-08-16 | 3900 | keep | 0 | Aug | 2021 | 0.0026563 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
UTUADO | 2021-08-16 11:13 | 2021-08-17 17:23 | 30 | 030:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21081600080 | New_Event | Bad Weather | Include | Include | Weather | 1810 | 2021-08-16 | 54300 | keep | 0 | Aug | 2021 | 0.036983 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
BAYAMON | 2021-08-16 11:15 | 2021-08-16 16:54 | 12 | 005:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | B21081600041 | New_Event | Secondary Wire Down | Include | Include | Equipment | 339 | 2021-08-16 | 4068 | keep | 0 | Aug | 2021 | 0.0027707 | 8.1731e-06 | Sustained | FALSE | TRUE | TMED_Event | 12
PONCE | 2021-08-16 11:22 | 2021-08-16 15:33 | 40 | 004:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA POR CAJA PRIMARIA QUEMADA | P21081600248 | New_Event | Cutout Failure | Include | Include | Equipment | 251 | 2021-08-16 | 10040 | keep | 0 | Aug | 2021 | 0.0068382 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
ARECIBO | 2021-08-16 11:25 | 2021-08-16 16:30 | 235 | 005:05 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZO DE POSTE PRIMARIO | A21081600084 | New_Event | Defective Pole | Include | Include | Equipment | 305 | 2021-08-16 | 71675 | keep | 0 | Aug | 2021 | 0.048818 | 0.00016006 | Sustained | FALSE | TRUE | TMED_Event | 235
SAN JUAN | 2021-08-16 11:29 | 2021-08-16 19:30 | 2 | 008:01 | P | DESGANCHE | 2 X 40 EN RISER Y 2 X 20 EN BANCO DE TRANSFORMADORES | R21081600017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 481 | 2021-08-16 | 962 | keep | 0 | Aug | 2021 | 0.00065521 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
CAGUAS | 2021-08-16 11:31 | 2021-08-16 23:31 | 4000 | 012:00 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REEMPLAZO POSTE PARTIDO POR CAMION Y CERRO MACHETES | C21081600123 | Partial_restoration |  |  | Include | Wildlife | 720 | 2021-08-16 | 2880000 | keep | 0 | Aug | 2021 | 1.9616 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
CAGUAS | 2021-08-16 11:31 | 2021-08-16 23:31 | 39 | 012:00 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DERRIBADO DE 37.5 X 37.5KVA | C21081600123 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 720 | 2021-08-16 | 28080 | keep | 0 | Aug | 2021 | 0.019125 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
CAGUAS | 2021-08-16 11:33 | 2021-08-18 11:34 | 2457 | 048:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21081600111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2881 | 2021-08-16 | 7078617 | keep | 0 | Aug | 2021 | 4.8212 | 0.0016735 | Sustained | FALSE | FALSE | TMED_Event | 2457
MAYAGÃœEZ | 2021-08-16 11:34 | 2021-08-16 17:27 | 30 | 005:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M21081600250 | New_Event | Vegetation Contact | Include | Include | Vegetation | 353 | 2021-08-16 | 10590 | keep | 0 | Aug | 2021 | 0.0072128 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
CAGUAS | 2021-08-16 11:37 | 2021-08-16 13:11 | 2343 | 001:34 | T | DESGANCHE | SE RETIRO ARBOL DE LAS LINEAS | C21081600129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2021-08-16 | 220242 | keep | 0 | Aug | 2021 | 0.15001 | 0.0015958 | Sustained | FALSE | TRUE | TMED_Event | 2343
CANOVANAS | 2021-08-16 11:46 | 2021-08-16 13:54 | 12 | 002:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 10 EN TRANSFORMADOR CRUCE POR RATA | R21081600031 | New_Event |  |  | Include | Wildlife | 128 | 2021-08-16 | 1536 | keep | 0 | Aug | 2021 | 0.0010462 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
MAYAGÃœEZ | 2021-08-16 11:52 | 2021-08-16 13:23 | 40 | 001:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA | M21081600258 | New_Event | Bad Weather | Include | Include | Weather | 91 | 2021-08-16 | 3640 | keep | 0 | Aug | 2021 | 0.0024792 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
VEGA BAJA | 2021-08-16 11:53 | 2021-08-16 15:42 | 40 | 003:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081600045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2021-08-16 | 9160 | keep | 0 | Aug | 2021 | 0.0062388 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
PONCE | 2021-08-16 11:56 | 2021-08-16 16:34 | 15 | 004:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR POR PORTAFUSIBLE QUEMADO | P21081600261 | New_Event | Cutout Failure | Include | Include | Equipment | 278 | 2021-08-16 | 4170 | keep | 0 | Aug | 2021 | 0.0028402 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
BAYAMON | 2021-08-16 11:59 | 2021-08-16 12:00 | 1382 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21051600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 1382 | keep | 0 | Aug | 2021 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | TMED_Event | 1382
BAYAMON | 2021-08-16 11:59 | 2021-08-16 12:00 | 663 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21081600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 663 | keep | 0 | Aug | 2021 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | TMED_Event | 663
BAYAMON | 2021-08-16 11:59 | 2021-08-16 12:00 | 74 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21081600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 74 | keep | 0 | Aug | 2021 | 5.0401e-05 | 5.0401e-05 | Momentary | FALSE | FALSE | TMED_Event | 74
MAYAGÃœEZ | 2021-08-16 12:00 | 2021-08-16 17:01 | 20 | 005:01 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CONECTOR | M21081600265 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 301 | 2021-08-16 | 6020 | keep | 0 | Aug | 2021 | 0.0041002 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
SAN JUAN | 2021-08-16 12:05 | 2021-08-16 16:37 | 25 | 004:32 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S21081600083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 272 | 2021-08-16 | 6800 | keep | 0 | Aug | 2021 | 0.0046314 | 1.7027e-05 | Sustained | FALSE | TRUE | TMED_Event | 25
VEGA BAJA | 2021-08-16 12:06 | 2021-08-16 15:43 | 200 | 003:37 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR BAMBUAS | B21081600048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2021-08-16 | 43400 | keep | 0 | Aug | 2021 | 0.02956 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
BAYAMON | 2021-08-16 12:07 | 2021-08-16 20:45 | 30 | 008:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO NEUTRAL PRIMARIO Y SE REPARO LINEA SECUNDARIA | B21081600047 | New_Event | Wire Down | Include | Include | Equipment | 518 | 2021-08-16 | 15540 | keep | 0 | Aug | 2021 | 0.010584 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
CAGUAS | 2021-08-16 12:09 | 2021-08-16 16:13 | 8 | 004:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21081600140 | New_Event | Bad Weather | Include | Include | Weather | 244 | 2021-08-16 | 1952 | keep | 0 | Aug | 2021 | 0.0013295 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
AGUADILLA | 2021-08-16 12:09 | 2021-08-17 16:30 | 10 | 028:21 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO 37.5KVA HOWARD INDUSTRIES 4160V/120/240V FID-1099281018 | M21081600269 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1701 | 2021-08-16 | 17010 | keep | 0 | Aug | 2021 | 0.011585 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
ARECIBO | 2021-08-16 12:23 | 2021-08-16 21:20 | 40 | 008:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21081600096 | New_Event | Wire Down | Include | Include | Equipment | 537 | 2021-08-16 | 21480 | keep | 0 | Aug | 2021 | 0.01463 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
PONCE | 2021-08-16 12:34 | 2021-08-17 12:45 | 100 | 024:11 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | P21081600227 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1451 | 2021-08-16 | 145100 | keep | 0 | Aug | 2021 | 0.098827 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
FAJARDO | 2021-08-16 12:39 | 2021-08-16 14:19 | 50 | 001:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN RISER REEMPLAZO PORTAFUSIBLE QUEMADO | R21081600037 | New_Event | Cutout Failure | Include | Include | Equipment | 100 | 2021-08-16 | 5000 | keep | 0 | Aug | 2021 | 0.0034055 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
BAYAMON | 2021-08-16 12:40 | 2021-08-16 16:47 | 10 | 004:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B21081600054 | New_Event | Secondary Wire Down | Include | Include | Equipment | 247 | 2021-08-16 | 2470 | keep | 0 | Aug | 2021 | 0.0016823 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
SAN JUAN | 2021-08-16 12:50 | 2021-08-16 13:29 | 200 | 000:39 | P | CABLE SOTERRADO AVERIADO | 1 X 140 EN CORTE DE LINEA Y 1 X 100 EN SU - 2A SECCIONALIZO DEL T - 11 HACIA EL T - 40 | R21081600039 | New_Event | UG Cable Fault | Include | Include | Equipment | 39 | 2021-08-16 | 7800 | keep | 0 | Aug | 2021 | 0.0053125 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
ARECIBO | 2021-08-16 12:55 | 2021-08-16 14:30 | 16 | 001:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARAR REPARAR SECUNDARIA AVERIADA | A21081600098 | New_Event | Secondary Wire Down | Include | Include | Equipment | 95 | 2021-08-16 | 1520 | keep | 0 | Aug | 2021 | 0.0010353 | 1.0898e-05 | Sustained | FALSE | FALSE | TMED_Event | 16
MAYAGÃœEZ | 2021-08-16 12:57 | 2021-08-16 13:30 | 50 | 000:33 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21081600289 | New_Event | Vegetation Contact | Include | Include | Vegetation | 33 | 2021-08-16 | 1650 | keep | 0 | Aug | 2021 | 0.0011238 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
SAN JUAN | 2021-08-16 13:00 | 2021-08-16 20:58 | 40 | 007:58 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21081600100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 478 | 2021-08-16 | 19120 | keep | 0 | Aug | 2021 | 0.013023 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
BAYAMON | 2021-08-16 13:10 | 2021-08-16 14:13 | 353 | 001:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR Y SE CERRO PUENTE ABIERTO | S21081600103 | Partial_restoration | Wire Down | Include | Include | Equipment | 63 | 2021-08-16 | 22239 | keep | 0 | Aug | 2021 | 0.015147 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
BAYAMON | 2021-08-16 13:20 | 2021-08-16 15:58 | 3 | 002:38 | P | OTRAS CAUSAS | TOMA VACANTE CAUSO AVERIA EN EL MH-6 | S21081600022 | New_Event | Other Causes | Include | Include | Other | 158 | 2021-08-16 | 474 | keep | 0 | Aug | 2021 | 0.00032284 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
MAYAGÃœEZ | 2021-08-16 13:30 | 2021-08-16 16:09 | 50 | 002:39 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN RISER LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081600305 | New_Event | Bad Weather | Include | Include | Weather | 159 | 2021-08-16 | 7950 | keep | 0 | Aug | 2021 | 0.0054147 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
MAYAGÃœEZ | 2021-08-16 13:30 | 2021-08-16 19:21 | 100 | 005:51 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN RISER Y 1 X 100 Y 1 X 80 EN SU LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081600305 | New_Event | Bad Weather | Include | Include | Weather | 351 | 2021-08-16 | 35100 | keep | 0 | Aug | 2021 | 0.023906 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
PONCE | 2021-08-16 13:32 | 2021-08-16 20:03 | 3 | 006:31 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA POR MAL TIEMPO | P21081600292 | New_Event | Bad Weather | Include | Include | Weather | 391 | 2021-08-16 | 1173 | keep | 0 | Aug | 2021 | 0.00079892 | 2.0433e-06 | Sustained | FALSE | TRUE | TMED_Event | 3
SAN JUAN | 2021-08-16 13:35 | 2021-08-16 20:36 | 25 | 007:01 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21081500074 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 421 | 2021-08-16 | 10525 | keep | 0 | Aug | 2021 | 0.0071685 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
SAN JUAN | 2021-08-16 13:37 | 2021-08-17 21:03 | 300 | 031:26 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO DEL T - 38 Y T - 39 | R21081600048 | New_Event | UG Cable Fault | Include | Include | Equipment | 1886 | 2021-08-16 | 565800 | keep | 0 | Aug | 2021 | 0.38536 | 0.00020433 | Sustained | FALSE | FALSE | TMED_Event | 300
SAN JUAN | 2021-08-16 13:37 | 2021-08-16 17:54 | 40 | 004:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA ELIMINO 2 BAJANTES DE CAJAS | R21081600039 | New_Event | Wire Down | Include | Include | Equipment | 257 | 2021-08-16 | 10280 | keep | 0 | Aug | 2021 | 0.0070017 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
SAN JUAN | 2021-08-16 13:38 | 2021-08-16 14:37 | 1 | 000:59 | P | NO SE REPORTO CAUSA | 2 X 80 EN RISER | R21081600046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 59 | 2021-08-16 | 59 | keep | 0 | Aug | 2021 | 4.0185e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2021-08-16 13:47 | 2021-08-18 13:34 | 50 | 047:47 | P | NO SE REPORTO CAUSA | 2 X 40 EN CORTE DE LINEA | S21081600119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2867 | 2021-08-16 | 143350 | keep | 0 | Aug | 2021 | 0.097635 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
HUMACAO | 2021-08-16 13:47 | 2021-08-16 17:06 | 7 | 003:19 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA X 25 KVA | C21081600184 | New_Event | Service Transformer Failure | Include | Include | Equipment | 199 | 2021-08-16 | 1393 | keep | 0 | Aug | 2021 | 0.00094877 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
PONCE | 2021-08-16 13:57 | 2021-08-16 14:50 | 100 | 000:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 POR 100 EN CORTE DE LINEA POR MAL TIEMPO | P21081600296 | New_Event | Bad Weather | Include | Include | Weather | 53 | 2021-08-16 | 5300 | keep | 0 | Aug | 2021 | 0.0036098 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
BAYAMON | 2021-08-16 13:59 | 2021-08-17 15:50 | 15 | 025:51 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5KVA X 37.5KVA Y SE RETEZO LINEA PRIMARIA | S21081600126 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1551 | 2021-08-16 | 23265 | keep | 0 | Aug | 2021 | 0.015846 | 1.0216e-05 | Sustained | FALSE | TRUE | TMED_Event | 15
UTUADO | 2021-08-16 14:01 | 2021-08-17 14:44 | 6 | 024:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21081600129 | New_Event | Bad Weather | Include | Include | Weather | 1483 | 2021-08-16 | 8898 | keep | 0 | Aug | 2021 | 0.0060604 | 4.0866e-06 | Sustained | FALSE | TRUE | TMED_Event | 6
CANOVANAS | 2021-08-16 14:02 | 2021-08-16 17:34 | 1 | 003:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO CAJA AVERIADA | R21081600066 | New_Event | Cutout Failure | Include | Include | Equipment | 212 | 2021-08-16 | 212 | keep | 0 | Aug | 2021 | 0.00014439 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
ARECIBO | 2021-08-16 14:13 | 2021-08-16 18:15 | 1 | 004:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | A21081600130 | New_Event | Bad Weather | Include | Include | Weather | 242 | 2021-08-16 | 242 | keep | 0 | Aug | 2021 | 0.00016483 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
MAYAGÃœEZ | 2021-08-16 14:17 | 2021-08-16 20:26 | 40 | 006:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081600321 | New_Event | Bad Weather | Include | Include | Weather | 369 | 2021-08-16 | 14760 | keep | 0 | Aug | 2021 | 0.010053 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
BAYAMON | 2021-08-16 14:23 | 2021-08-16 14:24 | 723 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVANDO 1711-05 | B21081600082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 723 | keep | 0 | Aug | 2021 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | TMED_Event | 723
BAYAMON | 2021-08-16 14:23 | 2021-08-16 14:24 | 1976 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR 1711-02 | B21081600082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 1976 | keep | 0 | Aug | 2021 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | TMED_Event | 1976
BAYAMON | 2021-08-16 14:24 | 2021-08-16 15:34 | 30 | 001:10 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA CARGA TRANSFERIDA AL 1711-02 | B21081600032 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 70 | 2021-08-16 | 2100 | keep | 0 | Aug | 2021 | 0.0014303 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
CAGUAS | 2021-08-16 14:28 | 2021-08-16 18:03 | 80 | 003:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA LEVANTO CONDUCTOR | C21081600199 | New_Event | Wire Down | Include | Include | Equipment | 215 | 2021-08-16 | 17200 | keep | 0 | Aug | 2021 | 0.011715 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
SAN JUAN | 2021-08-16 14:41 | 2021-08-16 14:48 | 2891 | 000:07 | T | NO SE REPORTO CAUSA | DISPARO SE VERIFICO PERSONAL FUERA | R21081600073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2021-08-16 | 20237 | keep | 0 | Aug | 2021 | 0.013783 | 0.001969 | Sustained | FALSE | FALSE | TMED_Event | 2891
MAYAGÃœEZ | 2021-08-16 14:44 | 2021-08-17 17:25 | 12 | 026:41 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO 50KVA HOWARD IND. FID-23609800 | M21081600329 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1601 | 2021-08-16 | 19212 | keep | 0 | Aug | 2021 | 0.013085 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
BAYAMON | 2021-08-16 14:50 | 2021-08-16 16:05 | 1 | 001:15 | P | NO SE REPORTO CAUSA | 2 X 80 EN SU-1A | B21081600087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 75 | 2021-08-16 | 75 | keep | 0 | Aug | 2021 | 5.1082e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
GUAYAMA | 2021-08-16 14:55 | 2021-08-16 17:44 | 13 | 002:49 | P | TRANSFORMADOR AVERIADO | SE CAMBIO XMR DE 37.5 A 7620 POR UNO DE 50KVA | P21081600314 | New_Event | Service Transformer Failure | Include | Include | Equipment | 169 | 2021-08-16 | 2197 | keep | 0 | Aug | 2021 | 0.0014964 | 8.8542e-06 | Sustained | FALSE | FALSE | TMED_Event | 13
BAYAMON | 2021-08-16 15:09 | 2021-08-17 09:30 | 20 | 018:21 | P | DESGANCHE | SE ABRIO PUENTE DE LINEA A CAJA PARA REALIZAR DESGANCHE | S21081600143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1101 | 2021-08-16 | 22020 | keep | 0 | Aug | 2021 | 0.014998 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
PONCE | 2021-08-16 15:18 | 2021-08-16 17:49 | 100 | 002:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA POR CAJA PRIMARIA QUEMADA | P21081600319 | New_Event | Cutout Failure | Include | Include | Equipment | 151 | 2021-08-16 | 15100 | keep | 0 | Aug | 2021 | 0.010285 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
PONCE | 2021-08-16 15:21 | 2021-08-16 22:00 | 48 | 006:39 | P | ESTRUCTURA AVERIADA | REMPLAZO DE POSTE PRIMARIO | P21081600039 | New_Event | Defective Pole | Include | Include | Equipment | 399 | 2021-08-16 | 19152 | keep | 0 | Aug | 2021 | 0.013044 | 3.2693e-05 | Sustained | FALSE | FALSE | TMED_Event | 48
YAUCO | 2021-08-16 15:45 | 2021-08-16 20:34 | 15 | 004:49 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR POR DESGANCHE Y SE RETESO LINEAS | P21081600327 | New_Event | Vegetation Contact | Include | Include | Vegetation | 289 | 2021-08-16 | 4335 | keep | 0 | Aug | 2021 | 0.0029525 | 1.0216e-05 | Sustained | FALSE | TRUE | TMED_Event | 15
PONCE | 2021-08-16 15:49 | 2021-08-16 18:05 | 100 | 002:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN SWITCH UNIT 4 Y 2 POR 40 EN SWITCH UNIT 3 POR MAL TIEMPO | P21081600330 | New_Event | Bad Weather | Include | Include | Weather | 136 | 2021-08-16 | 13600 | keep | 0 | Aug | 2021 | 0.0092629 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
BAYAMON | 2021-08-16 16:02 | 2021-08-16 16:05 | 3438 | 000:03 | T | NO SE REPORTO CAUSA | RECERRO | B21081600096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-08-16 | 10314 | keep | 0 | Aug | 2021 | 0.0070248 | 0.0023416 | Momentary | FALSE | FALSE | TMED_Event | 3438
ARECIBO | 2021-08-16 16:15 | 2021-08-16 16:47 | 9 | 000:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARAR REPARAR SECUNDARIA AVERIADA | A21081600149 | New_Event | Secondary Wire Down | Include | Include | Equipment | 32 | 2021-08-16 | 288 | keep | 0 | Aug | 2021 | 0.00019616 | 6.1299e-06 | Sustained | FALSE | FALSE | TMED_Event | 9
ARECIBO | 2021-08-16 16:20 | 2021-08-16 20:40 | 30 | 004:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21081600155 | New_Event | Bad Weather | Include | Include | Weather | 260 | 2021-08-16 | 7800 | keep | 0 | Aug | 2021 | 0.0053125 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
UTUADO | 2021-08-16 16:32 | 2021-08-16 18:42 | 30 | 002:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21081600157 | New_Event | Bad Weather | Include | Include | Weather | 130 | 2021-08-16 | 3900 | keep | 0 | Aug | 2021 | 0.0026563 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
BAYAMON | 2021-08-16 16:43 | 2021-08-16 19:11 | 1 | 002:28 | P | NO SE REPORTO CAUSA | 3 X 100 EN CORTE DE LINEA | S21081600167 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 148 | 2021-08-16 | 148 | keep | 0 | Aug | 2021 | 0.0001008 | 6.811e-07 | Sustained | FALSE | TRUE | TMED_Event | 1
ARECIBO | 2021-08-16 16:43 | 2021-08-17 10:15 | 20 | 017:32 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMA | A21081600162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1052 | 2021-08-16 | 21040 | keep | 0 | Aug | 2021 | 0.01433 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
MAYAGÃœEZ | 2021-08-16 16:46 | 2021-08-16 16:47 | 1266 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21081600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 1266 | keep | 0 | Aug | 2021 | 0.00086227 | 0.00086227 | Momentary | FALSE | FALSE | TMED_Event | 1266
ARECIBO | 2021-08-16 16:47 | 2021-08-16 17:54 | 12 | 001:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A21081600131 | New_Event | Wire Down | Include | Include | Equipment | 67 | 2021-08-16 | 804 | keep | 0 | Aug | 2021 | 0.0005476 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
ARECIBO | 2021-08-16 16:49 | 2021-08-16 19:52 | 1500 | 003:03 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO SE CERRO INTERRUPTOR | A21081600164 | New_Event | Wire Down | Include | Include | Equipment | 183 | 2021-08-16 | 274500 | keep | 0 | Aug | 2021 | 0.18696 | 0.0010216 | Sustained | FALSE | FALSE | TMED_Event | 1500
MAYAGÃœEZ | 2021-08-16 16:52 | 2021-08-17 12:10 | 150 | 019:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | M21081600364 | New_Event | Wire Down | Include | Include | Equipment | 1158 | 2021-08-16 | 173700 | keep | 0 | Aug | 2021 | 0.11831 | 0.00010216 | Sustained | FALSE | FALSE | TMED_Event | 150
VEGA BAJA | 2021-08-16 16:56 | 2021-08-16 17:30 | 6 | 000:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B21081600104 | New_Event | Secondary Wire Down | Include | Include | Equipment | 34 | 2021-08-16 | 204 | keep | 0 | Aug | 2021 | 0.00013894 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
ARECIBO | 2021-08-16 17:10 | 2021-08-16 18:30 | 8 | 001:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA AVERADA | A21081600148 | New_Event | Secondary Wire Down | Include | Include | Equipment | 80 | 2021-08-16 | 640 | keep | 0 | Aug | 2021 | 0.0004359 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
UTUADO | 2021-08-16 17:12 | 2021-08-17 11:19 | 10 | 018:07 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | A21081600167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1087 | 2021-08-16 | 10870 | keep | 0 | Aug | 2021 | 0.0074035 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
AGUADILLA | 2021-08-16 17:20 | 2021-08-16 21:18 | 8 | 003:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE TRANSFORMADOR | M21081600371 | New_Event | Wire Down | Include | Include | Equipment | 238 | 2021-08-16 | 1904 | keep | 0 | Aug | 2021 | 0.0012968 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
BAYAMON | 2021-08-16 17:23 | 2021-08-16 17:55 | 15 | 000:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S21081600000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 32 | 2021-08-16 | 480 | keep | 0 | Aug | 2021 | 0.00032693 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
CAGUAS | 2021-08-16 17:33 | 2021-08-17 11:58 | 1 | 018:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN RISER CRUCE CON AVE | C21081600255 | New_Event |  |  | Include | Wildlife | 1105 | 2021-08-16 | 1105 | keep | 0 | Aug | 2021 | 0.00075261 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2021-08-16 17:46 | 2021-08-16 20:15 | 35 | 002:29 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21081600176 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 149 | 2021-08-16 | 5215 | keep | 0 | Aug | 2021 | 0.0035519 | 2.3838e-05 | Sustained | FALSE | TRUE | TMED_Event | 35
MAYAGÃœEZ | 2021-08-16 18:06 | 2021-08-17 12:15 | 20 | 018:09 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | M21081600383 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1089 | 2021-08-16 | 21780 | keep | 0 | Aug | 2021 | 0.014834 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
MAYAGÃœEZ | 2021-08-16 18:10 | 2021-08-16 18:49 | 500 | 000:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO | M21081600386 | New_Event | Wire Down | Include | Include | Equipment | 39 | 2021-08-16 | 19500 | keep | 0 | Aug | 2021 | 0.013281 | 0.00034055 | Sustained | FALSE | FALSE | TMED_Event | 500
AGUADILLA | 2021-08-16 18:15 | 2021-08-17 10:44 | 10 | 016:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR POR MAL TIEMPO | M21081600384 | New_Event | Bad Weather | Include | Include | Weather | 989 | 2021-08-16 | 9890 | keep | 0 | Aug | 2021 | 0.006736 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
PONCE | 2021-08-16 18:31 | 2021-08-17 14:37 | 100 | 020:06 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE REPORTO LA CAUSA | P21081700351 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1206 | 2021-08-16 | 120600 | keep | 0 | Aug | 2021 | 0.08214 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
AGUADILLA | 2021-08-16 18:32 | 2021-08-17 11:25 | 15 | 016:53 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA POR MAL TIEMPO | M21081600390 | New_Event | Bad Weather | Include | Include | Weather | 1013 | 2021-08-16 | 15195 | keep | 0 | Aug | 2021 | 0.010349 | 1.0216e-05 | Sustained | FALSE | TRUE | TMED_Event | 15
HUMACAO | 2021-08-16 18:40 | 2021-08-16 18:42 | 2450 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO | C21081600269 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-16 | 4900 | keep | 0 | Aug | 2021 | 0.0033374 | 0.0016687 | Momentary | FALSE | FALSE | TMED_Event | 2450
HUMACAO | 2021-08-16 18:42 | 2021-08-17 05:55 | 200 | 011:13 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 Y 1 X 50 EN CORTES DE LINEA SE REEMPLAZO PIN POLE TOP | C21081600268 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 673 | 2021-08-16 | 134600 | keep | 0 | Aug | 2021 | 0.091675 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
MAYAGÃœEZ | 2021-08-16 18:47 | 2021-08-16 22:35 | 15 | 003:48 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR SE RETIRO ENREDADERA | M21081600393 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2021-08-16 | 3420 | keep | 0 | Aug | 2021 | 0.0023293 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
SAN JUAN | 2021-08-16 18:52 | 2021-08-16 20:41 | 50 | 001:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21081600099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2021-08-16 | 5450 | keep | 0 | Aug | 2021 | 0.003712 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
CAGUAS | 2021-08-16 19:14 | 2021-08-17 15:18 | 7 | 020:04 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR | C21081600283 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1204 | 2021-08-16 | 8428 | keep | 0 | Aug | 2021 | 0.0057403 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
SAN JUAN | 2021-08-16 19:21 | 2021-08-16 19:22 | 4291 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21081600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 4291 | keep | 0 | Aug | 2021 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | TMED_Event | 4291
GUAYAMA | 2021-08-16 19:28 | 2021-08-16 19:29 | 215 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21081600355 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 215 | keep | 0 | Aug | 2021 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | TMED_Event | 215
MAYAGÃœEZ | 2021-08-16 19:29 | 2021-08-16 21:31 | 35 | 002:02 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081600400 | New_Event | Bad Weather | Include | Include | Weather | 122 | 2021-08-16 | 4270 | keep | 0 | Aug | 2021 | 0.0029083 | 2.3838e-05 | Sustained | FALSE | TRUE | TMED_Event | 35
MAYAGÃœEZ | 2021-08-16 19:41 | 2021-08-16 20:20 | 200 | 000:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21081600404 | New_Event | Bad Weather | Include | Include | Weather | 39 | 2021-08-16 | 7800 | keep | 0 | Aug | 2021 | 0.0053125 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
PONCE | 2021-08-16 19:48 | 2021-08-17 16:47 | 78 | 020:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN RISER POR MAL TIEMPO | P21081600357 | New_Event | Bad Weather | Include | Include | Weather | 1259 | 2021-08-16 | 98202 | keep | 0 | Aug | 2021 | 0.066885 | 5.3125e-05 | Sustained | FALSE | FALSE | TMED_Event | 78
AGUADILLA | 2021-08-16 20:03 | 2021-08-17 14:58 | 20 | 018:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO SAFADO DEL TRANSFORMADOR | M21081600412 | New_Event | Wire Down | Include | Include | Equipment | 1135 | 2021-08-16 | 22700 | keep | 0 | Aug | 2021 | 0.015461 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
SAN JUAN | 2021-08-16 20:14 | 2021-08-16 21:07 | 2891 | 000:53 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO EL ALIMENTADOR | R21081600104 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 53 | 2021-08-16 | 153223 | keep | 0 | Aug | 2021 | 0.10436 | 0.001969 | Sustained | FALSE | FALSE | TMED_Event | 2891
MAYAGÃœEZ | 2021-08-16 20:14 | 2021-08-17 11:30 | 7 | 015:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR POR MAL TIEMPO | M21081600413 | New_Event | Bad Weather | Include | Include | Weather | 916 | 2021-08-16 | 6412 | keep | 0 | Aug | 2021 | 0.0043672 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
MAYAGÃœEZ | 2021-08-16 20:24 | 2021-08-17 13:10 | 6 | 016:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | M21081600415 | New_Event | Bad Weather | Include | Include | Weather | 1006 | 2021-08-16 | 6036 | keep | 0 | Aug | 2021 | 0.0041111 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
BARRANQUITAS | 2021-08-16 20:53 | 2021-08-17 10:35 | 70 | 013:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA LLUVIAS | C21081600301 | New_Event | Bad Weather | Include | Include | Weather | 822 | 2021-08-16 | 57540 | keep | 0 | Aug | 2021 | 0.03919 | 4.7677e-05 | Sustained | FALSE | TRUE | TMED_Event | 70
SAN JUAN | 2021-08-16 20:58 | 2021-08-16 20:59 | 4133 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | S21081600000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-16 | 4133 | keep | 0 | Aug | 2021 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | TMED_Event | 4133
SAN JUAN | 2021-08-16 20:59 | 2021-08-17 01:23 | 400 | 004:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO DE MACHETE | S21081600189 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 264 | 2021-08-16 | 105600 | keep | 0 | Aug | 2021 | 0.071924 | 0.00027244 | Sustained | FALSE | FALSE | TMED_Event | 400
SAN JUAN | 2021-08-16 20:59 | 2021-08-17 10:49 | 40 | 013:50 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21081600100 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 830 | 2021-08-16 | 33200 | keep | 0 | Aug | 2021 | 0.022612 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
SAN JUAN | 2021-08-16 21:07 | 2021-08-16 23:22 | 1891 | 002:15 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SECCIONALIZARON MACHETES QUEMADOS EN SU-6 Y CONTAMINACION EN SU-7 POR INUNDACION DE AGUA Y FANGO EN AISLADORES. SE TRANSFIRIO PARTE DE LA CARGA DEL 1646-05 A 2404-06, CERRANDO N/O EN VSW-7 A VSW-8 EN CARR 874 HOYO MULA | R21081600104 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 135 | 2021-08-16 | 255285 | keep | 0 | Aug | 2021 | 0.17387 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
PONCE | 2021-08-16 22:29 | 2021-08-16 22:30 | 75 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210816000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-16 | 75 | keep | 0 | Aug | 2021 | 5.1082e-05 | 5.1082e-05 | Momentary | FALSE | FALSE | TMED_Event | 75
SAN JUAN | 2021-08-16 23:22 | 2021-08-17 11:34 | 600 | 012:12 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE DESCONTAMINARON SU - 6 Y SU - 7 | R21081600048 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 732 | 2021-08-16 | 439200 | keep | 0 | Aug | 2021 | 0.29914 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
CAGUAS | 2021-08-16 23:31 | 2021-08-16 23:32 | 4390 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO INTERRUPTOR PARA CERRAR MACHETES ABIERTOS EN AVERIA DE POSTE ROTO POR CAMION | C21081600123 | Additional_clients |  |  | Include | Wildlife | 1 | 2021-08-16 | 4390 | keep | 0 | Aug | 2021 | 0.00299 | 0 | Momentary | FALSE | FALSE | TMED_Event | 0
CAGUAS | 2021-08-16 23:32 | 2021-08-17 14:24 | 39 | 014:52 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DERRIBADO DE 37.5 X 37.5KVA | C21081600123 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 892 | 2021-08-16 | 34788 | keep | 0 | Aug | 2021 | 0.023694 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
CAGUAS | 2021-08-17 01:10 | 2021-08-17 04:52 | 120 | 003:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | C21081700030 | New_Event |  |  | Include | Wildlife | 222 | 2021-08-17 | 26640 | keep | 0 | Aug | 2021 | 0.018144 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
BAYAMON | 2021-08-17 02:34 | 2021-08-17 02:35 | 271 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | S21081700095 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2021-08-17 | 271 | keep | 0 | Aug | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
BAYAMON | 2021-08-17 03:11 | 2021-08-17 03:12 | 271 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | S21081700095 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-08-17 | 271 | keep | 0 | Aug | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
PONCE | 2021-08-17 03:15 | 2021-08-17 03:16 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210817000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-17 | 2113 | keep | 0 | Aug | 2021 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
CANOVANAS | 2021-08-17 04:26 | 2021-08-17 04:27 | 4085 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21081700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-17 | 4085 | keep | 0 | Aug | 2021 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CAGUAS | 2021-08-17 04:52 | 2021-08-17 04:53 | 3005 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO DE INTERRUPTOR NO RECERRO | C21081700000 | Additional_clients |  |  | Include | Wildlife | 1 | 2021-08-17 | 3005 | keep | 0 | Aug | 2021 | 0.0020467 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-08-17 04:53 | 2021-08-17 17:51 | 120 | 012:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | C21081700030 | 1st_after_momentary |  |  | Include | Wildlife | 778 | 2021-08-17 | 93360 | keep | 0 | Aug | 2021 | 0.063587 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
HUMACAO | 2021-08-17 05:55 | 2021-08-17 05:56 | 2450 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO NO RECERRO | C21081700000 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-08-17 | 2450 | keep | 0 | Aug | 2021 | 0.0016687 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-08-17 05:56 | 2021-08-17 16:18 | 200 | 010:22 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 Y 1 X 50 EN CORTES DE LINEA SE REEMPLAZO PIN POLE TOP | C21081600268 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 622 | 2021-08-17 | 124400 | keep | 0 | Aug | 2021 | 0.084728 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BARRANQUITAS | 2021-08-17 06:04 | 2021-08-17 06:05 | 2635 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C21081700000 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2021-08-17 | 2635 | keep | 0 | Aug | 2021 | 0.0017947 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-08-17 06:05 | 2021-08-17 16:36 | 199 | 010:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE LEVANTO CONDUCTOR DEL SUELO | C21081700117 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 631 | 2021-08-17 | 125569 | keep | 0 | Aug | 2021 | 0.085524 | 0.00013554 | Sustained | FALSE | TRUE | Not_TMED_Event | 199
BARRANQUITAS | 2021-08-17 06:05 | 2021-08-17 13:50 | 500 | 007:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 EN CORTE DE LINEA SE LEVANTO CONDUCTOR DEL SUELO | C21081600016 | New_Event | Wire Down | Include | Include | Equipment | 465 | 2021-08-17 | 232500 | keep | 0 | Aug | 2021 | 0.15835 | 0.00034055 | Sustained | FALSE | TRUE | Not_TMED_Event | 500
SAN JUAN | 2021-08-17 08:09 | 2021-08-17 08:10 | 12 | 000:01 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHE | S21081700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-17 | 12 | keep | 0 | Aug | 2021 | 8.1731e-06 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-08-17 08:29 | 2021-08-17 08:30 | 271 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | S21081700095 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2021-08-17 | 271 | keep | 0 | Aug | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
VEGA BAJA | 2021-08-17 08:42 | 2021-08-18 17:10 | 12 | 032:28 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REMPLAZO POSTE SECUNDARIO PARTIDO | B21081700138 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 1948 | 2021-08-17 | 23376 | keep | 0 | Aug | 2021 | 0.015921 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-08-17 08:50 | 2021-08-17 08:51 | 3718 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P210817000XX | New_Event |  |  | Include | Wildlife | 1 | 2021-08-17 | 3718 | keep | 0 | Aug | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
PONCE | 2021-08-17 08:51 | 2021-08-17 13:26 | 65 | 004:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA. AVE CRUZO FASE | P21081700026 | 1st_after_momentary |  |  | Include | Wildlife | 275 | 2021-08-17 | 17875 | keep | 0 | Aug | 2021 | 0.012175 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
ARECIBO | 2021-08-17 09:00 | 2021-08-17 19:50 | 80 | 010:50 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR POSTE | A21081700029 | New_Event | Defective Pole | Include | Include | Equipment | 650 | 2021-08-17 | 52000 | keep | 0 | Aug | 2021 | 0.035417 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-08-17 09:21 | 2021-08-17 09:22 | 4634 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21081600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-17 | 4634 | keep | 0 | Aug | 2021 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
BAYAMON | 2021-08-17 09:28 | 2021-08-17 09:29 | 271 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | S21081700095 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-08-17 | 271 | keep | 0 | Aug | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
HUMACAO | 2021-08-17 09:28 | 2021-08-17 11:26 | 5 | 001:58 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE SECUNDARIO | C21081700000 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 118 | 2021-08-17 | 590 | keep | 0 | Aug | 2021 | 0.00040185 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-08-17 09:30 | 2021-08-17 11:30 | 20 | 002:00 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | A21081700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2021-08-17 | 2400 | keep | 0 | Aug | 2021 | 0.0016346 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-08-17 09:40 | 2021-08-17 09:41 | 271 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | S21081700095 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-08-17 | 271 | keep | 0 | Aug | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
BAYAMON | 2021-08-17 09:53 | 2021-08-17 09:54 | 271 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | S21081700095 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-08-17 | 271 | keep | 0 | Aug | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
BAYAMON | 2021-08-17 09:59 | 2021-08-17 10:00 | 271 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | S21081700095 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-08-17 | 271 | keep | 0 | Aug | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
BAYAMON | 2021-08-17 10:25 | 2021-08-17 10:26 | 271 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | S21081700095 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2021-08-17 | 271 | keep | 0 | Aug | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
BAYAMON | 2021-08-17 10:34 | 2021-08-17 10:35 | 271 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | S21081700095 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-08-17 | 271 | keep | 0 | Aug | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
BAYAMON | 2021-08-17 10:37 | 2021-08-17 10:38 | 271 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | S21081700095 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-08-17 | 271 | keep | 0 | Aug | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
BAYAMON | 2021-08-17 10:39 | 2021-08-17 10:40 | 271 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | S21081700095 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-08-17 | 271 | keep | 0 | Aug | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
MAYAGÃœEZ | 2021-08-17 10:58 | 2021-08-17 17:43 | 35 | 006:45 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | M21081700012 | New_Event | Bad Weather | Include | Include | Weather | 405 | 2021-08-17 | 14175 | keep | 0 | Aug | 2021 | 0.0096545 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
CAGUAS | 2021-08-17 11:07 | 2021-08-17 14:46 | 6 | 003:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO SULFATADO | C21081600103 | New_Event | Secondary Wire Down | Include | Include | Equipment | 219 | 2021-08-17 | 1314 | keep | 0 | Aug | 2021 | 0.00089496 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-08-17 11:10 | 2021-08-17 11:11 | 1417 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR | M21081700111 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-08-17 | 1417 | keep | 0 | Aug | 2021 | 0.00096511 | 0.00096511 | Momentary | FALSE | FALSE | Not_TMED_Event | 1417
MAYAGÃœEZ | 2021-08-17 11:11 | 2021-08-17 16:00 | 35 | 004:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | M21081700117 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 289 | 2021-08-17 | 10115 | keep | 0 | Aug | 2021 | 0.0068893 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-08-17 11:25 | 2021-08-17 11:26 | 271 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | S21081700095 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-08-17 | 271 | keep | 0 | Aug | 2021 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
MAYAGÃœEZ | 2021-08-17 11:28 | 2021-08-17 16:09 | 50 | 004:41 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 65 EN CORTE DE LINEA POR MAL TIEMPO | M21081700014 | New_Event | Bad Weather | Include | Include | Weather | 281 | 2021-08-17 | 14050 | keep | 0 | Aug | 2021 | 0.0095694 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-17 11:29 | 2021-08-17 15:49 | 25 | 004:20 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 40 EN CORTE DE LINEA POR MAL TIEMPO | M21081700039 | New_Event | Bad Weather | Include | Include | Weather | 260 | 2021-08-17 | 6500 | keep | 0 | Aug | 2021 | 0.0044271 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-08-17 11:29 | 2021-08-17 14:39 | 8 | 003:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA POR MAL TIEMPO | M21081700043 | New_Event | Bad Weather | Include | Include | Weather | 190 | 2021-08-17 | 1520 | keep | 0 | Aug | 2021 | 0.0010353 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
BAYAMON | 2021-08-17 11:30 | 2021-08-18 12:01 | 50 | 024:31 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081700037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1471 | 2021-08-17 | 73550 | keep | 0 | Aug | 2021 | 0.050095 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-17 11:30 | 2021-08-17 18:46 | 20 | 007:16 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE E LINEA | B21081700031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 436 | 2021-08-17 | 8720 | keep | 0 | Aug | 2021 | 0.0059392 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
HUMACAO | 2021-08-17 11:30 | 2021-08-17 17:02 | 4 | 005:32 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REEMPLAZO PEDESTAL | C21081700022 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 332 | 2021-08-17 | 1328 | keep | 0 | Aug | 2021 | 0.00090449 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-08-17 11:30 | 2021-08-17 17:18 | 20 | 005:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA POR AVE QUE CRUZO LINEAS | M21081700052 | New_Event |  |  | Include | Wildlife | 348 | 2021-08-17 | 6960 | keep | 0 | Aug | 2021 | 0.0047404 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-08-17 11:30 | 2021-08-17 12:10 | 30 | 000:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21081600108 | New_Event | Bad Weather | Include | Include | Weather | 40 | 2021-08-17 | 1200 | keep | 0 | Aug | 2021 | 0.00081731 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-08-17 11:30 | 2021-08-17 17:35 | 100 | 006:05 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | A21081700022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 365 | 2021-08-17 | 36500 | keep | 0 | Aug | 2021 | 0.02486 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-08-17 11:31 | 2021-08-17 17:29 | 20 | 005:58 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA CARGA POR EL 1903-05 | B21081700055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 358 | 2021-08-17 | 7160 | keep | 0 | Aug | 2021 | 0.0048766 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-08-17 11:31 | 2021-08-17 16:40 | 130 | 005:09 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21081700059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 309 | 2021-08-17 | 40170 | keep | 0 | Aug | 2021 | 0.02736 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
MAYAGÃœEZ | 2021-08-17 11:31 | 2021-08-17 19:25 | 100 | 007:54 | P | PARARRAYOS DEFECTUOSO | 2 X 65 EN CORTE DE LINEA POR PARARRAYO CRUZADO | M21081700090 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 474 | 2021-08-17 | 47400 | keep | 0 | Aug | 2021 | 0.032284 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-08-17 11:31 | 2021-08-17 18:20 | 150 | 006:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE RETEZARON LINEAS PRIMARIAS | M21081700073 | New_Event | Wire Down | Include | Include | Equipment | 409 | 2021-08-17 | 61350 | keep | 0 | Aug | 2021 | 0.041785 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-08-17 11:31 | 2021-08-17 16:13 | 50 | 004:42 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | A21081700025 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 282 | 2021-08-17 | 14100 | keep | 0 | Aug | 2021 | 0.0096034 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-08-17 11:31 | 2021-08-17 19:00 | 8 | 007:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21081700030 | New_Event | Bad Weather | Include | Include | Weather | 449 | 2021-08-17 | 3592 | keep | 0 | Aug | 2021 | 0.0024465 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2021-08-17 11:31 | 2021-08-17 13:50 | 50 | 002:19 | P | DESGANCHE | 1 X 30 EN CCRTE DE LINEA SE RETIRO RAMA | A21081700032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2021-08-17 | 6950 | keep | 0 | Aug | 2021 | 0.0047336 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-17 11:31 | 2021-08-17 15:02 | 7 | 003:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 25 EN RISER SECUNDARIA PARTIDA | A21081700036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 211 | 2021-08-17 | 1477 | keep | 0 | Aug | 2021 | 0.001006 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-08-17 11:31 | 2021-08-17 14:26 | 25 | 002:55 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21081700057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 175 | 2021-08-17 | 4375 | keep | 0 | Aug | 2021 | 0.0029798 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CANOVANAS | 2021-08-17 11:32 | 2021-08-17 16:11 | 55 | 004:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE LEVANTO CONDUCTOR DEL SUELO | R21081700083 | New_Event | Wire Down | Include | Include | Equipment | 279 | 2021-08-17 | 15345 | keep | 0 | Aug | 2021 | 0.010451 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
HUMACAO | 2021-08-17 11:32 | 2021-08-17 18:06 | 100 | 006:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | C21081700099 | New_Event |  |  | Include | Wildlife | 394 | 2021-08-17 | 39400 | keep | 0 | Aug | 2021 | 0.026835 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-08-17 11:32 | 2021-08-18 12:54 | 1 | 025:22 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C21081700087 | New_Event | Bad Weather | Include | Include | Weather | 1522 | 2021-08-17 | 1522 | keep | 0 | Aug | 2021 | 0.0010366 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-08-17 11:32 | 2021-08-18 11:17 | 4 | 023:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES SECUNDARIAS EN TRANSFORMADOR | M21081700118 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1425 | 2021-08-17 | 5700 | keep | 0 | Aug | 2021 | 0.0038822 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-08-17 11:33 | 2021-08-17 11:34 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21081700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-17 | 393 | keep | 0 | Aug | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
BAYAMON | 2021-08-17 11:35 | 2021-08-17 13:41 | 12 | 002:06 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | B21081700078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2021-08-17 | 1512 | keep | 0 | Aug | 2021 | 0.0010298 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
BAYAMON | 2021-08-17 11:52 | 2021-08-17 13:39 | 271 | 001:47 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE ABRIO MACHETES EN MATADERO AVE KENNEDY Y SE CERRO POR SCADA | S21081700095 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 107 | 2021-08-17 | 28997 | keep | 0 | Aug | 2021 | 0.01975 | 0.00018458 | Sustained | FALSE | FALSE | Not_TMED_Event | 271
AGUADILLA | 2021-08-17 11:58 | 2021-08-17 14:00 | 80 | 002:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | M21081700122 | New_Event | Wire Down | Include | Include | Equipment | 122 | 2021-08-17 | 9760 | keep | 0 | Aug | 2021 | 0.0066475 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-17 12:08 | 2021-08-17 15:30 | 12 | 003:22 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21081700087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 202 | 2021-08-17 | 2424 | keep | 0 | Aug | 2021 | 0.001651 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
BAYAMON | 2021-08-17 12:08 | 2021-08-17 15:36 | 10 | 003:28 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21081700083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 208 | 2021-08-17 | 2080 | keep | 0 | Aug | 2021 | 0.0014167 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-08-17 12:09 | 2021-08-17 15:05 | 15 | 002:56 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DEFECTUOSO DE 100KVA MARCA-ERMCO FID-23786345 | M21081700124 | New_Event | Service Transformer Failure | Include | Include | Equipment | 176 | 2021-08-17 | 2640 | keep | 0 | Aug | 2021 | 0.0017981 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-08-17 12:12 | 2021-08-17 17:40 | 400 | 005:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO | S21081700096 | New_Event | Wire Down | Include | Include | Equipment | 328 | 2021-08-17 | 131200 | keep | 0 | Aug | 2021 | 0.08936 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
MAYAGÃœEZ | 2021-08-17 12:14 | 2021-08-17 16:31 | 20 | 004:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA POR MAL TIEMPO | M21081700125 | New_Event | Bad Weather | Include | Include | Weather | 257 | 2021-08-17 | 5140 | keep | 0 | Aug | 2021 | 0.0035008 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
HUMACAO | 2021-08-17 12:16 | 2021-08-17 17:32 | 11 | 005:16 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR POSTE SECUNDARIO Y LINEA SECUNDARIA | C21081700160 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 316 | 2021-08-17 | 3476 | keep | 0 | Aug | 2021 | 0.0023675 | 7.492e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 11
CAGUAS | 2021-08-17 12:16 | 2021-08-17 17:32 | 200 | 005:16 | P | DESGANCHE | 2 X 80 EN CORTES DE LINEA | C21081700126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 316 | 2021-08-17 | 63200 | keep | 0 | Aug | 2021 | 0.043045 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
PONCE | 2021-08-17 12:25 | 2021-08-17 16:43 | 100 | 004:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA EN EL PISO. SE ABRE INTERRUPTOR DE EMERGENCIAS | P21081700042 | New_Event | Wire Down | Include | Include | Equipment | 258 | 2021-08-17 | 25800 | keep | 0 | Aug | 2021 | 0.017572 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-08-17 12:32 | 2021-08-17 18:04 | 150 | 005:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DEL CORTE DE LINEA | M21081700132 | New_Event | Wire Down | Include | Include | Equipment | 332 | 2021-08-17 | 49800 | keep | 0 | Aug | 2021 | 0.033919 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
AGUADILLA | 2021-08-17 12:40 | 2021-08-17 18:12 | 100 | 005:32 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | M21081700133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 332 | 2021-08-17 | 33200 | keep | 0 | Aug | 2021 | 0.022612 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-08-17 12:45 | 2021-08-17 14:37 | 50 | 001:52 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21081700087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2021-08-17 | 5600 | keep | 0 | Aug | 2021 | 0.0038141 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-17 12:51 | 2021-08-18 17:41 | 24 | 028:50 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERRADO AVERIADO DE T 21 A T 22 | B21081700090 | New_Event | UG Cable Fault | Include | Include | Equipment | 1730 | 2021-08-17 | 41520 | keep | 0 | Aug | 2021 | 0.028279 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2021-08-17 12:51 | 2021-08-17 21:07 | 20 | 008:16 | P | NO SE REPORTO CAUSA | 1 X 40 EN AEREO PROVISIONAL | B21081700202 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 496 | 2021-08-17 | 9920 | keep | 0 | Aug | 2021 | 0.0067565 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-08-17 13:00 | 2021-08-17 17:28 | 25 | 004:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | S21081700100 | New_Event | Cutout Failure | Include | Include | Equipment | 268 | 2021-08-17 | 6700 | keep | 0 | Aug | 2021 | 0.0045633 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
PONCE | 2021-08-17 13:01 | 2021-08-17 17:55 | 80 | 004:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA. AVE CRUZO FASE | P21081700051 | New_Event |  |  | Include | Wildlife | 294 | 2021-08-17 | 23520 | keep | 0 | Aug | 2021 | 0.016019 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
VEGA BAJA | 2021-08-17 13:10 | 2021-08-17 14:37 | 7 | 001:27 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CARGA POR EL 9207-08 SE REALIZO DESGANCHE PRIMARIO | B21081700100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2021-08-17 | 609 | keep | 0 | Aug | 2021 | 0.00041479 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-08-17 13:18 | 2021-08-17 13:19 | 528 | 000:01 | T | TRANSFORMADOR AVERIADO | SE ABRIO INTERRUPTOR DE EMERGENCIA POR TRANSFORMADOR QUEMANDOSE | M21081700044 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1 | 2021-08-17 | 528 | keep | 0 | Aug | 2021 | 0.00035962 | 0.00035962 | Momentary | FALSE | FALSE | Not_TMED_Event | 528
ARECIBO | 2021-08-17 13:25 | 2021-08-17 14:36 | 300 | 001:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A21081700061 | New_Event | Bad Weather | Include | Include | Weather | 71 | 2021-08-17 | 21300 | keep | 0 | Aug | 2021 | 0.014507 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-08-17 13:34 | 2021-08-17 19:02 | 40 | 005:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | M21081700221 | New_Event | Bad Weather | Include | Include | Weather | 328 | 2021-08-17 | 13120 | keep | 0 | Aug | 2021 | 0.008936 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-08-17 13:39 | 2021-08-17 15:00 | 217 | 001:21 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO MACHETES EN MATADERO AVE KENNEDY 20% EN SERVICIO | S21081700095 | Partial_restoration | Switch Failure | Include | Include | Equipment | 81 | 2021-08-17 | 17577 | keep | 0 | Aug | 2021 | 0.011972 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-17 13:46 | 2021-08-17 17:46 | 10 | 004:00 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21081700127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 240 | 2021-08-17 | 2400 | keep | 0 | Aug | 2021 | 0.0016346 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-08-17 13:50 | 2021-08-17 13:51 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | S21081700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-17 | 2203 | keep | 0 | Aug | 2021 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
VEGA BAJA | 2021-08-17 13:53 | 2021-08-17 16:05 | 1 | 002:12 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21081700009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 132 | 2021-08-17 | 132 | keep | 0 | Aug | 2021 | 8.9905e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-08-17 14:02 | 2021-08-17 15:57 | 50 | 001:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | M21081700150 | New_Event | Bad Weather | Include | Include | Weather | 115 | 2021-08-17 | 5750 | keep | 0 | Aug | 2021 | 0.0039163 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-08-17 14:03 | 2021-08-17 14:06 | 776 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C21081700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-08-17 | 2328 | keep | 0 | Aug | 2021 | 0.0015856 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
SAN JUAN | 2021-08-17 14:15 | 2021-08-18 11:42 | 200 | 021:27 | P | DESGANCHE | 1 X 80 Y 1 X 40 EN CORTES DE LINEA | R21081700104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1287 | 2021-08-17 | 257400 | keep | 0 | Aug | 2021 | 0.17531 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-08-17 14:21 | 2021-08-17 18:44 | 40 | 004:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | S21081700116 | New_Event | Cutout Failure | Include | Include | Equipment | 263 | 2021-08-17 | 10520 | keep | 0 | Aug | 2021 | 0.0071651 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
GUAYAMA | 2021-08-17 14:30 | 2021-08-17 14:37 | 4132 | 000:07 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | P21081700064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2021-08-17 | 28924 | keep | 0 | Aug | 2021 | 0.0197 | 0.0028143 | Sustained | FALSE | FALSE | Not_TMED_Event | 4132
MAYAGÃœEZ | 2021-08-17 14:35 | 2021-08-17 16:50 | 528 | 002:15 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | M21081700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 135 | 2021-08-17 | 71280 | keep | 0 | Aug | 2021 | 0.048548 | 0.00035962 | Sustained | FALSE | FALSE | Not_TMED_Event | 528
ARECIBO | 2021-08-17 14:37 | 2021-08-17 17:05 | 20 | 002:28 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A21081700069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2021-08-17 | 2960 | keep | 0 | Aug | 2021 | 0.002016 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-08-17 14:39 | 2021-08-18 11:28 | 60 | 020:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA POR AVE EN LAS LINEAS | B21081700157 | New_Event |  |  | Include | Wildlife | 1249 | 2021-08-17 | 74940 | keep | 0 | Aug | 2021 | 0.051041 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
GUAYAMA | 2021-08-17 14:45 | 2021-08-17 14:46 | 4132 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21081700068 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-17 | 4132 | keep | 0 | Aug | 2021 | 0.0028143 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-08-17 15:08 | 2021-08-17 18:45 | 4 | 003:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21081700072 | New_Event | Bad Weather | Include | Include | Weather | 217 | 2021-08-17 | 868 | keep | 0 | Aug | 2021 | 0.00059119 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-08-17 15:18 | 2021-08-17 19:19 | 20 | 004:01 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA DESGANCHE | M21081700183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2021-08-17 | 4820 | keep | 0 | Aug | 2021 | 0.0032829 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-08-17 15:21 | 2021-08-17 20:00 | 50 | 004:39 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PRIMARIO DE 45 PIES DE METAL FID-19690351 | M21081700187 | New_Event | Defective Pole | Include | Include | Equipment | 279 | 2021-08-17 | 13950 | keep | 0 | Aug | 2021 | 0.0095013 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-08-17 15:29 | 2021-08-17 18:59 | 150 | 003:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | M21081700193 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2021-08-17 | 31500 | keep | 0 | Aug | 2021 | 0.021455 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-08-17 15:30 | 2021-08-18 18:19 | 12 | 026:49 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER SE INSPECCIONO | C21081700180 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1609 | 2021-08-17 | 19308 | keep | 0 | Aug | 2021 | 0.013151 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-08-17 15:39 | 2021-08-18 03:59 | 20 | 012:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081700186 | New_Event | Vegetation Contact | Include | Include | Vegetation | 740 | 2021-08-17 | 14800 | keep | 0 | Aug | 2021 | 0.01008 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
YAUCO | 2021-08-17 15:40 | 2021-08-18 10:00 | 53 | 018:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO | P21081700076 | New_Event | Wire Down | Include | Include | Equipment | 1100 | 2021-08-17 | 58300 | keep | 0 | Aug | 2021 | 0.039708 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
MAYAGÃœEZ | 2021-08-17 15:50 | 2021-08-17 18:30 | 80 | 002:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | M21081700207 | New_Event | Bad Weather | Include | Include | Weather | 160 | 2021-08-17 | 12800 | keep | 0 | Aug | 2021 | 0.008718 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CANOVANAS | 2021-08-17 15:53 | 2021-08-17 17:20 | 9 | 001:27 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE CON AVE | R21071700117 | New_Event |  |  | Include | Wildlife | 87 | 2021-08-17 | 783 | keep | 0 | Aug | 2021 | 0.0005333 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-08-17 16:14 | 2021-08-17 16:15 | 271 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA SE VERIFICO CON PERSONAL QUE TENIA SECCIONALIZADO TRAMO POR MACHETE AVERIADO | S21081700095 | Additional_clients | Switch Failure | Include | Include | Equipment | 1 | 2021-08-17 | 271 | keep | 0 | Aug | 2021 | 0.00018458 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-08-17 16:16 | 2021-08-18 16:05 | 8 | 023:49 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHO | C21081700200 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1429 | 2021-08-17 | 11432 | keep | 0 | Aug | 2021 | 0.0077863 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2021-08-17 16:18 | 2021-08-18 13:50 | 30 | 021:32 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21081700233 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1292 | 2021-08-17 | 38760 | keep | 0 | Aug | 2021 | 0.026399 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-08-17 16:27 | 2021-08-17 16:29 | 143 | 000:02 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR A PETICION DE JESUS MARRERO POR MACHETE DEFECTUOSO Y SE CERRO POR ESCADA | S21081700144 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2021-08-17 | 286 | keep | 0 | Aug | 2021 | 0.00019479 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
BAYAMON | 2021-08-17 16:29 | 2021-08-17 16:57 | 30 | 000:28 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21081700007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 28 | 2021-08-17 | 840 | keep | 0 | Aug | 2021 | 0.00057212 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-08-17 16:34 | 2021-08-17 16:57 | 271 | 000:23 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR AL CERRAR MACHETE FRENTE AL NUEVO DIA AMELIA INDUSTRIAL PARK SE ENCONTRO MACHETE QUEMADO EN LA ENTRADA DE INSDUSTRIAL PARK | S21081700095 | Additional_clients | Switch Failure | Include | Include | Equipment | 23 | 2021-08-17 | 6233 | keep | 0 | Aug | 2021 | 0.0042453 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-08-17 16:43 | 2021-08-17 17:52 | 891 | 001:09 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR PARA LEVANTAR LINEA PRIMARIA DEL PISO | P21081700083 | Additional_clients | Wire Down | Include | Include | Equipment | 69 | 2021-08-17 | 61479 | keep | 0 | Aug | 2021 | 0.041873 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BARRANQUITAS | 2021-08-17 16:45 | 2021-08-17 21:59 | 55 | 005:14 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21081700201 | New_Event | Vegetation Contact | Include | Include | Vegetation | 314 | 2021-08-17 | 17270 | keep | 0 | Aug | 2021 | 0.011763 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
SAN JUAN | 2021-08-17 16:49 | 2021-08-17 21:32 | 65 | 004:43 | P | DESGANCHE | 1 X 50 Y 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21081700150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2021-08-17 | 18395 | keep | 0 | Aug | 2021 | 0.012529 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BAYAMON | 2021-08-17 16:53 | 2021-08-17 19:31 | 60 | 002:38 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21081700144 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 158 | 2021-08-17 | 9480 | keep | 0 | Aug | 2021 | 0.0064568 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-08-17 17:01 | 2021-08-17 17:05 | 1417 | 000:04 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO INTERRUPTOR | M21081700000 | New_Event | Bad Weather | Include | Include | Weather | 4 | 2021-08-17 | 5668 | keep | 0 | Aug | 2021 | 0.0038604 | 0.00096511 | Momentary | FALSE | FALSE | Not_TMED_Event | 1417
MAYAGÃœEZ | 2021-08-17 17:05 | 2021-08-17 20:45 | 70 | 003:40 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO | M21081700254 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 220 | 2021-08-17 | 15400 | keep | 0 | Aug | 2021 | 0.010489 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BAYAMON | 2021-08-17 17:07 | 2021-08-17 19:52 | 20 | 002:45 | P | NO SE REPORTO CAUSA | SE REEMPLAZO CAJA EN AEREO PROVISIONAL | B21080700090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 165 | 2021-08-17 | 3300 | keep | 0 | Aug | 2021 | 0.0022476 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-08-17 17:13 | 2021-08-17 17:58 | 271 | 000:45 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE ENCONTRO MACHETE QUEMADO EN LA CARR 165 WATERFRONT AMELIA | S21081700095 | Additional_clients | Switch Failure | Include | Include | Equipment | 45 | 2021-08-17 | 12195 | keep | 0 | Aug | 2021 | 0.008306 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-08-17 17:18 | 2021-08-18 10:44 | 106 | 017:26 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | P21081700088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1046 | 2021-08-17 | 110876 | keep | 0 | Aug | 2021 | 0.075517 | 7.2196e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 106
SAN JUAN | 2021-08-17 17:30 | 2021-08-17 22:27 | 200 | 004:57 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA | S21081700157 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 297 | 2021-08-17 | 59400 | keep | 0 | Aug | 2021 | 0.040457 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-08-17 17:50 | 2021-08-17 18:50 | 10 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONECTORES SECUNDARIOS | A21081700040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2021-08-17 | 600 | keep | 0 | Aug | 2021 | 0.00040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-08-17 17:58 | 2021-08-17 20:12 | 136 | 002:14 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO 100% EN SERVICIO | S21081700095 | Partial_restoration | Switch Failure | Include | Include | Equipment | 134 | 2021-08-17 | 18224 | keep | 0 | Aug | 2021 | 0.012412 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-08-17 17:58 | 2021-08-17 18:00 | 436 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL 80% DE LA CARGA POR EL 3015-07 | C21081700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-17 | 872 | keep | 0 | Aug | 2021 | 0.00059392 | 0.00029696 | Momentary | FALSE | FALSE | Not_TMED_Event | 436
YAUCO | 2021-08-17 18:02 | 2021-08-18 16:50 | 15 | 022:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE EN CAJA DE TRANSFORMADOR | P21081700092 | New_Event | Wire Down | Include | Include | Equipment | 1368 | 2021-08-17 | 20520 | keep | 0 | Aug | 2021 | 0.013976 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-08-17 18:10 | 2021-08-17 20:48 | 80 | 002:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | M21071700237 | New_Event |  |  | Include | Wildlife | 158 | 2021-08-17 | 12640 | keep | 0 | Aug | 2021 | 0.008609 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
GUAYAMA | 2021-08-17 18:13 | 2021-08-18 11:45 | 15 | 017:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA EN TRANSFORMADOR | P21081700093 | New_Event | Cutout Failure | Include | Include | Equipment | 1052 | 2021-08-17 | 15780 | keep | 0 | Aug | 2021 | 0.010748 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-08-17 18:27 | 2021-08-18 18:00 | 150 | 023:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA LEVANTO CONDUCTOR | C21081700220 | New_Event | Wire Down | Include | Include | Equipment | 1413 | 2021-08-17 | 211950 | keep | 0 | Aug | 2021 | 0.14436 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-08-17 18:44 | 2021-08-17 18:48 | 1017 | 000:04 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO INTERRUPTOR | M21081700261 | New_Event | Bad Weather | Include | Include | Weather | 4 | 2021-08-17 | 4068 | keep | 0 | Aug | 2021 | 0.0027707 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-08-17 19:02 | 2021-08-18 15:05 | 40 | 020:03 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | M21081700262 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1203 | 2021-08-17 | 48120 | keep | 0 | Aug | 2021 | 0.032774 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-08-17 19:10 | 2021-08-18 15:57 | 12 | 020:47 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | P21081800026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1247 | 2021-08-17 | 14964 | keep | 0 | Aug | 2021 | 0.010192 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
YAUCO | 2021-08-17 19:15 | 2021-08-18 18:21 | 8 | 023:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN CORTE DE LINEA POR LINEAS ARREADAS | P21081700098 | New_Event | Wire Down | Include | Include | Equipment | 1386 | 2021-08-17 | 11088 | keep | 0 | Aug | 2021 | 0.007552 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
AGUADILLA | 2021-08-17 19:17 | 2021-08-18 12:30 | 200 | 017:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA MARCA SHINT | M21081700269 | New_Event | Cutout Failure | Include | Include | Equipment | 1033 | 2021-08-17 | 206600 | keep | 0 | Aug | 2021 | 0.14071 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2021-08-17 19:19 | 2021-08-18 10:05 | 20 | 014:46 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMA | A21081700099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 886 | 2021-08-17 | 17720 | keep | 0 | Aug | 2021 | 0.012069 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-08-17 19:29 | 2021-08-17 22:10 | 30 | 002:41 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA MAL TIEMPO | M21081700283 | New_Event | Bad Weather | Include | Include | Weather | 161 | 2021-08-17 | 4830 | keep | 0 | Aug | 2021 | 0.0032897 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
HUMACAO | 2021-08-17 19:31 | 2021-08-18 11:37 | 20 | 016:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21081700228 | New_Event | Bad Weather | Include | Include | Weather | 966 | 2021-08-17 | 19320 | keep | 0 | Aug | 2021 | 0.013159 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-08-17 19:40 | 2021-08-18 14:04 | 20 | 018:24 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO CAUSA | C21081700230 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1104 | 2021-08-17 | 22080 | keep | 0 | Aug | 2021 | 0.015039 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-08-17 19:52 | 2021-08-18 18:25 | 211 | 022:33 | P | ESTRUCTURA AVERIADA | 2 X 30 EN TRANSFORMADOR SE ABRE MACHETE Y RISER PARA REEMPLAZAR BANCO DE TRANSFORMADORES DE 100 KVA Y FIJAR CRUCETA | S21081700186 | New_Event | Defective Pole | Include | Include | Equipment | 1353 | 2021-08-17 | 285483 | keep | 0 | Aug | 2021 | 0.19444 | 0.00014371 | Sustained | FALSE | FALSE | Not_TMED_Event | 211
BAYAMON | 2021-08-17 19:58 | 2021-08-18 12:04 | 50 | 016:06 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21081700189 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 966 | 2021-08-17 | 48300 | keep | 0 | Aug | 2021 | 0.032897 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-17 20:09 | 2021-08-18 10:00 | 6 | 013:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CULEBRA CRUZO FASES | A21081700102 | New_Event |  |  | Include | Wildlife | 831 | 2021-08-17 | 4986 | keep | 0 | Aug | 2021 | 0.0033959 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2021-08-17 20:16 | 2021-08-18 11:03 | 17 | 014:47 | P | DESGANCHE | 1 X 10 Y 1 X 20 EN TRANSFORMADORES | R21081700143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 887 | 2021-08-17 | 15079 | keep | 0 | Aug | 2021 | 0.01027 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
AGUADILLA | 2021-08-17 20:21 | 2021-08-18 17:35 | 80 | 021:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M21081700300 | New_Event | Wire Down | Include | Include | Equipment | 1274 | 2021-08-17 | 101920 | keep | 0 | Aug | 2021 | 0.069417 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-08-17 20:52 | 2021-08-18 15:15 | 100 | 018:23 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | M21081700309 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1103 | 2021-08-17 | 110300 | keep | 0 | Aug | 2021 | 0.075125 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-08-17 21:12 | 2021-08-18 12:45 | 50 | 015:33 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21081700201 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 933 | 2021-08-17 | 46650 | keep | 0 | Aug | 2021 | 0.031773 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-08-17 21:15 | 2021-08-18 02:10 | 442 | 004:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABREN MACHETES PARA LEVANTAR LINEA PRIMARIA DEL PISO | P21081700112 | New_Event | Wire Down | Include | Include | Equipment | 295 | 2021-08-17 | 130390 | keep | 0 | Aug | 2021 | 0.088808 | 0.00030104 | Sustained | FALSE | TRUE | Not_TMED_Event | 442
SAN JUAN | 2021-08-17 21:25 | 2021-08-18 11:18 | 25 | 013:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21081700202 | New_Event | Vegetation Contact | Include | Include | Vegetation | 833 | 2021-08-17 | 20825 | keep | 0 | Aug | 2021 | 0.014184 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-08-17 21:40 | 2021-08-17 22:46 | 240 | 001:06 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21081700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2021-08-17 | 15840 | keep | 0 | Aug | 2021 | 0.010789 | 0.00016346 | Sustained | FALSE | TRUE | Not_TMED_Event | 240
SAN JUAN | 2021-08-17 22:20 | 2021-08-18 12:33 | 3 | 014:13 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21081700151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 853 | 2021-08-17 | 2559 | keep | 0 | Aug | 2021 | 0.0017429 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-08-17 22:21 | 2021-08-17 22:25 | 1617 | 000:04 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4 | 2021-08-17 | 6468 | keep | 0 | Aug | 2021 | 0.0044053 | 0.0011013 | Momentary | FALSE | TRUE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-08-17 22:21 | 2021-08-17 22:25 | 1017 | 000:04 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4 | 2021-08-17 | 4068 | keep | 0 | Aug | 2021 | 0.0027707 | 0.00069267 | Momentary | FALSE | TRUE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-08-17 22:21 | 2021-08-17 22:25 | 828 | 000:04 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4 | 2021-08-17 | 3312 | keep | 0 | Aug | 2021 | 0.0022558 | 0.00056395 | Momentary | FALSE | TRUE | Not_TMED_Event | 828
MAYAGÃœEZ | 2021-08-17 22:21 | 2021-08-17 22:31 | 863 | 000:10 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 10 | 2021-08-17 | 8630 | keep | 0 | Aug | 2021 | 0.0058779 | 0.00058779 | Sustained | FALSE | TRUE | Not_TMED_Event | 863
MAYAGÃœEZ | 2021-08-17 22:21 | 2021-08-17 22:31 | 309 | 000:10 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 10 | 2021-08-17 | 3090 | keep | 0 | Aug | 2021 | 0.0021046 | 0.00021046 | Sustained | FALSE | TRUE | Not_TMED_Event | 309
MAYAGÃœEZ | 2021-08-17 22:21 | 2021-08-17 22:31 | 176 | 000:10 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 10 | 2021-08-17 | 1760 | keep | 0 | Aug | 2021 | 0.0011987 | 0.00011987 | Sustained | FALSE | TRUE | Not_TMED_Event | 176
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:25 | 693 | 000:04 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4 | 2021-08-17 | 2772 | keep | 0 | Aug | 2021 | 0.001888 | 0.000472 | Momentary | FALSE | TRUE | Not_TMED_Event | 693
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:25 | 47 | 000:04 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4 | 2021-08-17 | 188 | keep | 0 | Aug | 2021 | 0.00012805 | 3.2011e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 47
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:25 | 1256 | 000:04 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4 | 2021-08-17 | 5024 | keep | 0 | Aug | 2021 | 0.0034218 | 0.00085546 | Momentary | FALSE | TRUE | Not_TMED_Event | 1256
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:25 | 558 | 000:04 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4 | 2021-08-17 | 2232 | keep | 0 | Aug | 2021 | 0.0015202 | 0.00038005 | Momentary | FALSE | TRUE | Not_TMED_Event | 558
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 470 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 2350 | keep | 0 | Aug | 2021 | 0.0016006 | 0.00032011 | Momentary | FALSE | TRUE | Not_TMED_Event | 470
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 1345 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 6725 | keep | 0 | Aug | 2021 | 0.0045804 | 0.00091607 | Momentary | FALSE | TRUE | Not_TMED_Event | 1345
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 2946 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 14730 | keep | 0 | Aug | 2021 | 0.010033 | 0.0020065 | Momentary | FALSE | TRUE | Not_TMED_Event | 2946
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 103 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 515 | keep | 0 | Aug | 2021 | 0.00035076 | 7.0153e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 103
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 1057 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 5285 | keep | 0 | Aug | 2021 | 0.0035996 | 0.00071992 | Momentary | FALSE | TRUE | Not_TMED_Event | 1057
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 99 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 495 | keep | 0 | Aug | 2021 | 0.00033714 | 6.7428e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 99
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 52 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 260 | keep | 0 | Aug | 2021 | 0.00017708 | 3.5417e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 52
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 32 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 160 | keep | 0 | Aug | 2021 | 0.00010898 | 2.1795e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 32
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 129 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 645 | keep | 0 | Aug | 2021 | 0.00043931 | 8.7861e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 129
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 146 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 730 | keep | 0 | Aug | 2021 | 0.0004972 | 9.944e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 146
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 69 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 345 | keep | 0 | Aug | 2021 | 0.00023498 | 4.6996e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 69
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 15 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 75 | keep | 0 | Aug | 2021 | 5.1082e-05 | 1.0216e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 15
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 132 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 660 | keep | 0 | Aug | 2021 | 0.00044952 | 8.9905e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 132
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 1157 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 5785 | keep | 0 | Aug | 2021 | 0.0039401 | 0.00078803 | Momentary | FALSE | TRUE | Not_TMED_Event | 1157
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 376 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 1880 | keep | 0 | Aug | 2021 | 0.0012805 | 0.00025609 | Momentary | FALSE | TRUE | Not_TMED_Event | 376
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 1943 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 9715 | keep | 0 | Aug | 2021 | 0.0066168 | 0.0013234 | Momentary | FALSE | TRUE | Not_TMED_Event | 1943
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 5 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 25 | keep | 0 | Aug | 2021 | 1.7027e-05 | 3.4055e-06 | Momentary | FALSE | TRUE | Not_TMED_Event | 5
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 1024 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 5120 | keep | 0 | Aug | 2021 | 0.0034872 | 0.00069744 | Momentary | FALSE | TRUE | Not_TMED_Event | 1024
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 1192 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 5960 | keep | 0 | Aug | 2021 | 0.0040593 | 0.00081187 | Momentary | FALSE | TRUE | Not_TMED_Event | 1192
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 3041 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 15205 | keep | 0 | Aug | 2021 | 0.010356 | 0.0020712 | Momentary | FALSE | TRUE | Not_TMED_Event | 3041
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 390 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 1950 | keep | 0 | Aug | 2021 | 0.0013281 | 0.00026563 | Momentary | FALSE | TRUE | Not_TMED_Event | 390
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 650 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 3250 | keep | 0 | Aug | 2021 | 0.0022136 | 0.00044271 | Momentary | FALSE | TRUE | Not_TMED_Event | 650
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 1827 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 9135 | keep | 0 | Aug | 2021 | 0.0062218 | 0.0012444 | Momentary | FALSE | TRUE | Not_TMED_Event | 1827
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 1047 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 5235 | keep | 0 | Aug | 2021 | 0.0035655 | 0.00071311 | Momentary | FALSE | TRUE | Not_TMED_Event | 1047
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 4882 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 24410 | keep | 0 | Aug | 2021 | 0.016626 | 0.0033251 | Momentary | FALSE | TRUE | Not_TMED_Event | 4882
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 1485 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 7425 | keep | 0 | Aug | 2021 | 0.0050571 | 0.0010114 | Momentary | FALSE | TRUE | Not_TMED_Event | 1485
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:26 | 543 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 2715 | keep | 0 | Aug | 2021 | 0.0018492 | 0.00036983 | Momentary | FALSE | TRUE | Not_TMED_Event | 543
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:23 | 569 | 000:02 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2 | 2021-08-17 | 1138 | keep | 0 | Aug | 2021 | 0.00077509 | 0.00038754 | Momentary | FALSE | TRUE | Not_TMED_Event | 569
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:23 | 1245 | 000:02 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2 | 2021-08-17 | 2490 | keep | 0 | Aug | 2021 | 0.0016959 | 0.00084796 | Momentary | FALSE | TRUE | Not_TMED_Event | 1245
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:23 | 1155 | 000:02 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2 | 2021-08-17 | 2310 | keep | 0 | Aug | 2021 | 0.0015733 | 0.00078667 | Momentary | FALSE | TRUE | Not_TMED_Event | 1155
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:23 | 867 | 000:02 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2 | 2021-08-17 | 1734 | keep | 0 | Aug | 2021 | 0.001181 | 0.00059051 | Momentary | FALSE | TRUE | Not_TMED_Event | 867
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:23 | 257 | 000:02 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2 | 2021-08-17 | 514 | keep | 0 | Aug | 2021 | 0.00035008 | 0.00017504 | Momentary | FALSE | TRUE | Not_TMED_Event | 257
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:23 | 1336 | 000:02 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2 | 2021-08-17 | 2672 | keep | 0 | Aug | 2021 | 0.0018199 | 0.00090994 | Momentary | FALSE | TRUE | Not_TMED_Event | 1336
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:23 | 3315 | 000:02 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2 | 2021-08-17 | 6630 | keep | 0 | Aug | 2021 | 0.0045157 | 0.0022578 | Momentary | FALSE | TRUE | Not_TMED_Event | 3315
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:23 | 1718 | 000:02 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 2 | 2021-08-17 | 3436 | keep | 0 | Aug | 2021 | 0.0023402 | 0.0011701 | Momentary | FALSE | TRUE | Not_TMED_Event | 1718
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:25 | 154 | 000:04 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4 | 2021-08-17 | 616 | keep | 0 | Aug | 2021 | 0.00041955 | 0.00010489 | Momentary | FALSE | TRUE | Not_TMED_Event | 154
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:25 | 1261 | 000:04 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4 | 2021-08-17 | 5044 | keep | 0 | Aug | 2021 | 0.0034354 | 0.00085886 | Momentary | FALSE | TRUE | Not_TMED_Event | 1261
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:25 | 3894 | 000:04 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4 | 2021-08-17 | 15576 | keep | 0 | Aug | 2021 | 0.010609 | 0.0026522 | Momentary | FALSE | TRUE | Not_TMED_Event | 3894
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:25 | 997 | 000:04 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4 | 2021-08-17 | 3988 | keep | 0 | Aug | 2021 | 0.0027162 | 0.00067905 | Momentary | FALSE | TRUE | Not_TMED_Event | 997
AGUADILLA | 2021-08-17 22:21 | 2021-08-17 22:25 | 1497 | 000:04 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 4 | 2021-08-17 | 5988 | keep | 0 | Aug | 2021 | 0.0040784 | 0.0010196 | Momentary | FALSE | TRUE | Not_TMED_Event | 1497
ARECIBO | 2021-08-17 22:21 | 2021-08-17 22:25 | 1541 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 | A21081700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-08-17 | 6164 | keep | 0 | Aug | 2021 | 0.0041983 | 0.0010496 | Momentary | FALSE | TRUE | Not_TMED_Event | 1541
ARECIBO | 2021-08-17 22:21 | 2021-08-17 22:25 | 307 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 | A21081700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-08-17 | 1228 | keep | 0 | Aug | 2021 | 0.00083639 | 0.0002091 | Momentary | FALSE | TRUE | Not_TMED_Event | 307
ARECIBO | 2021-08-17 22:21 | 2021-08-17 22:25 | 1277 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 | A21081700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-08-17 | 5108 | keep | 0 | Aug | 2021 | 0.003479 | 0.00086976 | Momentary | FALSE | TRUE | Not_TMED_Event | 1277
ARECIBO | 2021-08-17 22:21 | 2021-08-17 22:25 | 1644 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 | A21081700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-08-17 | 6576 | keep | 0 | Aug | 2021 | 0.0044789 | 0.0011197 | Momentary | FALSE | TRUE | Not_TMED_Event | 1644
ARECIBO | 2021-08-17 22:21 | 2021-08-17 22:25 | 1831 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 | A21081700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-08-17 | 7324 | keep | 0 | Aug | 2021 | 0.0049883 | 0.0012471 | Momentary | FALSE | TRUE | Not_TMED_Event | 1831
ARECIBO | 2021-08-17 22:21 | 2021-08-17 22:25 | 1483 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 | A21081700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-08-17 | 5932 | keep | 0 | Aug | 2021 | 0.0040403 | 0.0010101 | Momentary | FALSE | TRUE | Not_TMED_Event | 1483
ARECIBO | 2021-08-17 22:21 | 2021-08-17 22:25 | 89 | 000:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 | A21081700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2021-08-17 | 356 | keep | 0 | Aug | 2021 | 0.00024247 | 6.0617e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 89
MAYAGÃœEZ | 2021-08-17 22:21 | 2021-08-17 22:26 | 3087 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 15435 | keep | 0 | Aug | 2021 | 0.010513 | 0.0021025 | Momentary | FALSE | TRUE | Not_TMED_Event | 3087
MAYAGÃœEZ | 2021-08-17 22:21 | 2021-08-17 22:26 | 770 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 3850 | keep | 0 | Aug | 2021 | 0.0026222 | 0.00052444 | Momentary | FALSE | TRUE | Not_TMED_Event | 770
MAYAGÃœEZ | 2021-08-17 22:21 | 2021-08-17 22:26 | 1192 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 5960 | keep | 0 | Aug | 2021 | 0.0040593 | 0.00081187 | Momentary | FALSE | TRUE | Not_TMED_Event | 1192
MAYAGÃœEZ | 2021-08-17 22:21 | 2021-08-17 22:26 | 1772 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 8860 | keep | 0 | Aug | 2021 | 0.0060345 | 0.0012069 | Momentary | FALSE | TRUE | Not_TMED_Event | 1772
MAYAGÃœEZ | 2021-08-17 22:21 | 2021-08-17 22:26 | 2174 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 10870 | keep | 0 | Aug | 2021 | 0.0074035 | 0.0014807 | Momentary | FALSE | TRUE | Not_TMED_Event | 2174
MAYAGÃœEZ | 2021-08-17 22:21 | 2021-08-17 22:26 | 64 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 320 | keep | 0 | Aug | 2021 | 0.00021795 | 4.359e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 64
MAYAGÃœEZ | 2021-08-17 22:21 | 2021-08-17 22:26 | 2658 | 000:05 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 5 | 2021-08-17 | 13290 | keep | 0 | Aug | 2021 | 0.0090518 | 0.0018104 | Momentary | FALSE | TRUE | Not_TMED_Event | 2658
MAYAGÃœEZ | 2021-08-17 22:21 | 2021-08-17 22:30 | 3522 | 000:09 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 9 | 2021-08-17 | 31698 | keep | 0 | Aug | 2021 | 0.021589 | 0.0023988 | Sustained | FALSE | TRUE | Not_TMED_Event | 3522
MAYAGÃœEZ | 2021-08-17 22:21 | 2021-08-17 22:30 | 1337 | 000:09 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 9 | 2021-08-17 | 12033 | keep | 0 | Aug | 2021 | 0.0081956 | 0.00091062 | Sustained | FALSE | TRUE | Not_TMED_Event | 1337
MAYAGÃœEZ | 2021-08-17 22:21 | 2021-08-17 22:30 | 2825 | 000:09 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 9 | 2021-08-17 | 25425 | keep | 0 | Aug | 2021 | 0.017317 | 0.0019241 | Sustained | FALSE | TRUE | Not_TMED_Event | 2825
MAYAGÃœEZ | 2021-08-17 22:21 | 2021-08-17 22:30 | 1287 | 000:09 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 9 | 2021-08-17 | 11583 | keep | 0 | Aug | 2021 | 0.0078891 | 0.00087657 | Sustained | FALSE | TRUE | Not_TMED_Event | 1287
MAYAGÃœEZ | 2021-08-17 22:21 | 2021-08-17 22:30 | 1417 | 000:09 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 9 | 2021-08-17 | 12753 | keep | 0 | Aug | 2021 | 0.008686 | 0.00096511 | Sustained | FALSE | TRUE | Not_TMED_Event | 1417
MAYAGÃœEZ | 2021-08-17 22:21 | 2021-08-17 22:30 | 80 | 000:09 | S | LINEA DE TRANSMISION | DISPARO LINEA TRANSMISION 50500 | M21081700000 | New_Event | 230 kV Transmission Line Source | Include | Include | Power Supply | 9 | 2021-08-17 | 720 | keep | 0 | Aug | 2021 | 0.00049039 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
AGUADILLA | 2021-08-17 22:25 | 2021-08-18 20:00 | 80 | 021:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | M21081700321 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1295 | 2021-08-17 | 103600 | keep | 0 | Aug | 2021 | 0.070561 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-17 22:42 | 2021-08-19 12:08 | 15 | 037:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN TRANSFORMADOR Y SE REEMPLAZO CAJA AVERIADA | S21081700212 | New_Event | Cutout Failure | Include | Include | Equipment | 2246 | 2021-08-17 | 33690 | keep | 0 | Aug | 2021 | 0.022946 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-08-18 02:23 | 2021-08-18 11:45 | 2 | 009:22 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | A21081800002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 562 | 2021-08-18 | 1124 | keep | 0 | Aug | 2021 | 0.00076555 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2021-08-18 03:01 | 2021-08-18 03:02 | 473 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21081800001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-18 | 473 | keep | 0 | Aug | 2021 | 0.00032216 | 0.00032216 | Momentary | FALSE | FALSE | Not_TMED_Event | 473
CAGUAS | 2021-08-18 03:02 | 2021-08-18 09:39 | 150 | 006:37 | P | NO SE REPORTO CAUSA | 1 X 80 Y 1 X 40 EN CORTES DE LINEA NO CAUSA | C21081800002 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 397 | 2021-08-18 | 59550 | keep | 0 | Aug | 2021 | 0.040559 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-08-18 03:59 | 2021-08-18 04:00 | 4028 | 000:01 | T | DESGANCHE | DISPARO Y SE CERRO POR SCADA | B21081800000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-18 | 4028 | keep | 0 | Aug | 2021 | 0.0027435 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-18 04:00 | 2021-08-18 14:39 | 20 | 010:39 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081700186 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 639 | 2021-08-18 | 12780 | keep | 0 | Aug | 2021 | 0.0087044 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-08-18 04:00 | 2021-08-18 14:29 | 20 | 010:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA PRINCIPAL Y 1 X 40 EN CORTE DE LINEA INTERMEDIO | B21081800015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 629 | 2021-08-18 | 12580 | keep | 0 | Aug | 2021 | 0.0085682 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
YAUCO | 2021-08-18 04:03 | 2021-08-18 10:17 | 40 | 006:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE | P21081800003 | New_Event |  |  | Include | Wildlife | 374 | 2021-08-18 | 14960 | keep | 0 | Aug | 2021 | 0.010189 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
AGUADILLA | 2021-08-18 04:37 | 2021-08-18 04:38 | 3041 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21081800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-18 | 3041 | keep | 0 | Aug | 2021 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2021-08-18 05:40 | 2021-08-18 09:28 | 20 | 003:48 | P | PARARRAYOS DEFECTUOSO | 2 X 65 EN CORTE DE LINEA PARARRAYOS | M21081800006 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 228 | 2021-08-18 | 4560 | keep | 0 | Aug | 2021 | 0.0031058 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-08-18 06:53 | 2021-08-18 14:13 | 1 | 007:20 | P | OTRAS CAUSAS | 1 X 20 EN RISER PROA | C21081800006 | New_Event | Other Causes | Include | Include | Other | 440 | 2021-08-18 | 440 | keep | 0 | Aug | 2021 | 0.00029968 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2021-08-18 07:01 | 2021-08-18 12:40 | 40 | 005:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA, SE ELIMINO BAJANTE PRIMARIO DE TRANSFORMADOR EN DESUSO | P21081800022 | New_Event | Wire Down | Include | Include | Equipment | 339 | 2021-08-18 | 13560 | keep | 0 | Aug | 2021 | 0.0092357 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-08-18 07:01 | 2021-08-18 18:52 | 40 | 011:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA REPARO BAJANTE DE LINEA A CAJA DE TRANSFORMADOR | C21081800008 | New_Event | Wire Down | Include | Include | Equipment | 711 | 2021-08-18 | 28440 | keep | 0 | Aug | 2021 | 0.01937 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-18 07:23 | 2021-08-18 09:50 | 25 | 002:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA DE 100AMP. MARCA SHINT | M21081800013 | New_Event | Cutout Failure | Include | Include | Equipment | 147 | 2021-08-18 | 3675 | keep | 0 | Aug | 2021 | 0.002503 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-08-18 07:35 | 2021-08-18 10:34 | 40 | 002:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA POR PAJARO QUE CRUZO LINEAS | M21081800014 | New_Event |  |  | Include | Wildlife | 179 | 2021-08-18 | 7160 | keep | 0 | Aug | 2021 | 0.0048766 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-08-18 07:44 | 2021-08-18 09:38 | 30 | 001:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA SE RETIRO GLOBO | B21081800034 | New_Event |  |  | Include | Wildlife | 114 | 2021-08-18 | 3420 | keep | 0 | Aug | 2021 | 0.0023293 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-08-18 07:45 | 2021-08-18 15:03 | 20 | 007:18 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA REMPLAZO 6 PARARRAYOS Y RETEZO LINEAS | C21081800011 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 438 | 2021-08-18 | 8760 | keep | 0 | Aug | 2021 | 0.0059664 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-08-18 07:53 | 2021-08-18 12:43 | 50 | 004:50 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA POR AISLADOR PRIMARIO QUEMADO | M21081800017 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 290 | 2021-08-18 | 14500 | keep | 0 | Aug | 2021 | 0.0098759 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-18 07:54 | 2021-08-18 09:34 | 25 | 001:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO CONECTORES SECUNDARIOS | A21081800004 | New_Event | Secondary Wire Down | Include | Include | Equipment | 100 | 2021-08-18 | 2500 | keep | 0 | Aug | 2021 | 0.0017027 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-08-18 07:55 | 2021-08-18 14:52 | 45 | 006:57 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S21081800009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 417 | 2021-08-18 | 18765 | keep | 0 | Aug | 2021 | 0.012781 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
PONCE | 2021-08-18 08:00 | 2021-08-18 12:50 | 2 | 004:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN RISER POR MAL TIEMPO | P210818000XX | New_Event | Bad Weather | Include | Include | Weather | 290 | 2021-08-18 | 580 | keep | 0 | Aug | 2021 | 0.00039504 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2021-08-18 08:05 | 2021-08-18 13:07 | 50 | 005:02 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTES DE LINEA | S21081800014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 302 | 2021-08-18 | 15100 | keep | 0 | Aug | 2021 | 0.010285 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-08-18 08:06 | 2021-08-18 13:34 | 100 | 005:28 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | M21081800019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 328 | 2021-08-18 | 32800 | keep | 0 | Aug | 2021 | 0.02234 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-08-18 08:12 | 2021-08-18 14:19 | 20 | 006:07 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA X 50 KVA | C21081800014 | New_Event | Service Transformer Failure | Include | Include | Equipment | 367 | 2021-08-18 | 7340 | keep | 0 | Aug | 2021 | 0.0049992 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-08-18 08:19 | 2021-08-18 18:37 | 10 | 010:18 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C21081800016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 618 | 2021-08-18 | 6180 | keep | 0 | Aug | 2021 | 0.0042092 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-08-18 08:20 | 2021-08-19 10:54 | 10 | 026:34 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO CAUSA | C21081800065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1594 | 2021-08-18 | 15940 | keep | 0 | Aug | 2021 | 0.010857 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-08-18 08:25 | 2021-08-18 08:26 | 638 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21081800019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-18 | 638 | keep | 0 | Aug | 2021 | 0.00043454 | 0.00043454 | Momentary | FALSE | FALSE | Not_TMED_Event | 638
UTUADO | 2021-08-18 08:31 | 2021-08-18 21:55 | 50 | 013:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A21081800010 | New_Event | Wire Down | Include | Include | Equipment | 804 | 2021-08-18 | 40200 | keep | 0 | Aug | 2021 | 0.02738 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-08-18 08:37 | 2021-08-18 19:00 | 200 | 010:23 | P | ESTRUCTURA AVERIADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO POSTE DE 45' METAL | M21081800023 | New_Event | Defective Pole | Include | Include | Equipment | 623 | 2021-08-18 | 124600 | keep | 0 | Aug | 2021 | 0.084864 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
AGUADILLA | 2021-08-18 08:51 | 2021-08-18 17:15 | 300 | 008:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | M21081800026 | New_Event | Wire Down | Include | Include | Equipment | 504 | 2021-08-18 | 151200 | keep | 0 | Aug | 2021 | 0.10298 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-08-18 08:54 | 2021-08-18 13:34 | 3 | 004:40 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR POR DESGANCHE | M21081800028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2021-08-18 | 840 | keep | 0 | Aug | 2021 | 0.00057212 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2021-08-18 08:59 | 2021-08-18 11:40 | 40 | 002:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | A21081800001 | New_Event | Wire Down | Include | Include | Equipment | 161 | 2021-08-18 | 6440 | keep | 0 | Aug | 2021 | 0.0043863 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-08-18 09:08 | 2021-08-18 16:06 | 40 | 006:58 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO CARGA TRANSFERIDA AL 1709-01 | B21081800045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 418 | 2021-08-18 | 16720 | keep | 0 | Aug | 2021 | 0.011388 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-08-18 09:20 | 2021-08-18 12:57 | 100 | 003:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | C21081800023 | New_Event |  |  | Include | Wildlife | 217 | 2021-08-18 | 21700 | keep | 0 | Aug | 2021 | 0.01478 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-08-18 09:28 | 2021-08-18 09:29 | 3041 | 000:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE DE INTERRUPTOR | M21081800000 | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2021-08-18 | 3041 | keep | 0 | Aug | 2021 | 0.0020712 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-08-18 09:29 | 2021-08-18 14:35 | 20 | 005:06 | P | PARARRAYOS DEFECTUOSO | 2 X 65 EN CORTE DE LINEA PARARRAYOS | M21081800006 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 306 | 2021-08-18 | 6120 | keep | 0 | Aug | 2021 | 0.0041683 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-08-18 09:35 | 2021-08-20 16:35 | 9 | 055:00 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 15 KVA X 37.5 KVA HC @ GIS UPDATES | C21081800025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 3300 | 2021-08-18 | 29700 | keep | 0 | Aug | 2021 | 0.020229 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2021-08-18 09:41 | 2021-08-18 09:42 | 1227 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21081800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-18 | 1227 | keep | 0 | Aug | 2021 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
HUMACAO | 2021-08-18 09:44 | 2021-08-18 11:37 | 7 | 001:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21081800027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 113 | 2021-08-18 | 791 | keep | 0 | Aug | 2021 | 0.00053875 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-08-18 09:50 | 2021-08-18 11:50 | 15 | 002:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONECTORES SECUNDARIOS | A21081800018 | New_Event | Secondary Wire Down | Include | Include | Equipment | 120 | 2021-08-18 | 1800 | keep | 0 | Aug | 2021 | 0.001226 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-08-18 09:55 | 2021-08-18 14:50 | 130 | 004:55 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO DISCO QUEMADO | R21081800011 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 295 | 2021-08-18 | 38350 | keep | 0 | Aug | 2021 | 0.02612 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
PONCE | 2021-08-18 10:00 | 2021-08-18 16:18 | 5 | 006:18 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE CAMBIO POSTE SECUNDARIO PARTIDO | P21081800039 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 378 | 2021-08-18 | 1890 | keep | 0 | Aug | 2021 | 0.0012873 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-08-18 10:01 | 2021-08-18 14:28 | 12 | 004:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | P21081800040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 267 | 2021-08-18 | 3204 | keep | 0 | Aug | 2021 | 0.0021822 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
SAN JUAN | 2021-08-18 10:12 | 2021-08-19 11:15 | 1 | 025:03 | P | NO SE REPORTO CAUSA | 1 X 25 EN SU-3 | R21081800012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1503 | 2021-08-18 | 1503 | keep | 0 | Aug | 2021 | 0.0010237 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-08-18 10:19 | 2021-08-18 17:22 | 100 | 007:03 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE REPORTA CAUSA | P21081800043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 423 | 2021-08-18 | 42300 | keep | 0 | Aug | 2021 | 0.02881 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-08-18 10:28 | 2021-08-18 13:20 | 150 | 002:52 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A21081800025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2021-08-18 | 25800 | keep | 0 | Aug | 2021 | 0.017572 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-08-18 10:29 | 2021-08-18 19:07 | 10 | 008:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO BAJANTE SECUNDARIO | C21081800032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 518 | 2021-08-18 | 5180 | keep | 0 | Aug | 2021 | 0.0035281 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-08-18 10:46 | 2021-08-18 15:44 | 25 | 004:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 65 EN CORTE DE LINEA SE REPARO PEDESTAL EN FUEGO | B21081800065 | New_Event | Secondary Wire Down | Include | Include | Equipment | 298 | 2021-08-18 | 7450 | keep | 0 | Aug | 2021 | 0.0050742 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-08-18 10:48 | 2021-08-18 15:35 | 15 | 004:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARARON BAJANTES EN TRANSFORMADOR | M21081800057 | New_Event | Wire Down | Include | Include | Equipment | 287 | 2021-08-18 | 4305 | keep | 0 | Aug | 2021 | 0.0029321 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-08-18 10:48 | 2021-08-19 18:09 | 8 | 031:21 | P | OTRAS CAUSAS | SE MOVIO TRANSFORMADOR A POSTE NUEVO POSTE EXISTENTE EN MALAS CONDICIONES | A21081900024 | New_Event | Other Causes | Include | Include | Other | 1881 | 2021-08-18 | 15048 | keep | 0 | Aug | 2021 | 0.010249 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-08-18 10:57 | 2021-08-18 10:58 | 1085 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | S21081800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-18 | 1085 | keep | 0 | Aug | 2021 | 0.00073899 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
BAYAMON | 2021-08-18 10:58 | 2021-08-18 16:00 | 87 | 005:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE MACHETE PARA CERRAR PUENTE PRIMARIO TRAS PATIO | S21081800044 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 302 | 2021-08-18 | 26274 | keep | 0 | Aug | 2021 | 0.017895 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
MAYAGÃœEZ | 2021-08-18 11:09 | 2021-08-18 17:25 | 200 | 006:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | M21081800064 | New_Event | Bad Weather | Include | Include | Weather | 376 | 2021-08-18 | 75200 | keep | 0 | Aug | 2021 | 0.051218 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-08-18 11:11 | 2021-08-18 13:56 | 40 | 002:45 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21081800036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2021-08-18 | 6600 | keep | 0 | Aug | 2021 | 0.0044952 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-08-18 11:20 | 2021-08-18 11:21 | 1983 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO 1801-02 LLEVANDO LA CARGA DEL 1711-04 | B21081800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-18 | 1983 | keep | 0 | Aug | 2021 | 0.0013506 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-08-18 11:20 | 2021-08-18 11:21 | 186 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO 1801-02 LLEVANDO LA CARGA DEL 1711-04 | B21081800000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-18 | 186 | keep | 0 | Aug | 2021 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2021-08-18 11:21 | 2021-08-18 19:16 | 100 | 007:55 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARARON PUENTES PRIMARIOS EN MACHETES | B21081800102 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 475 | 2021-08-18 | 47500 | keep | 0 | Aug | 2021 | 0.032352 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2021-08-18 11:34 | 2021-08-19 12:09 | 50 | 024:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR REMPLAZO CAJA QUEMADA Y PARARRAYO | C21081800038 | New_Event | Cutout Failure | Include | Include | Equipment | 1475 | 2021-08-18 | 73750 | keep | 0 | Aug | 2021 | 0.050231 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-18 11:47 | 2021-08-18 15:03 | 30 | 003:16 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | B21081800085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2021-08-18 | 5880 | keep | 0 | Aug | 2021 | 0.0040048 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-08-18 11:58 | 2021-08-18 16:46 | 150 | 004:48 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P21081800062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2021-08-18 | 43200 | keep | 0 | Aug | 2021 | 0.029423 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-08-18 12:01 | 2021-08-18 16:10 | 40 | 004:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21081800038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 249 | 2021-08-18 | 9960 | keep | 0 | Aug | 2021 | 0.0067837 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-08-18 12:04 | 2021-08-18 19:45 | 20 | 007:41 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21081800039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 461 | 2021-08-18 | 9220 | keep | 0 | Aug | 2021 | 0.0062797 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-08-18 12:22 | 2021-08-18 16:48 | 12 | 004:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21081800040 | New_Event | Bad Weather | Include | Include | Weather | 266 | 2021-08-18 | 3192 | keep | 0 | Aug | 2021 | 0.0021741 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2021-08-18 12:23 | 2021-08-18 15:58 | 4 | 003:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR REMPLAZO CAJA QUEMADA | C21081800042 | New_Event | Cutout Failure | Include | Include | Equipment | 215 | 2021-08-18 | 860 | keep | 0 | Aug | 2021 | 0.00058574 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2021-08-18 12:40 | 2021-08-18 18:34 | 100 | 005:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO | R21081800023 | New_Event | Cutout Failure | Include | Include | Equipment | 354 | 2021-08-18 | 35400 | keep | 0 | Aug | 2021 | 0.024111 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-08-18 12:53 | 2021-08-18 19:05 | 50 | 006:12 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A21081800078 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 372 | 2021-08-18 | 18600 | keep | 0 | Aug | 2021 | 0.012668 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-18 12:54 | 2021-08-18 14:30 | 25 | 001:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA IGUANA | M21081800079 | New_Event |  |  | Include | Wildlife | 96 | 2021-08-18 | 2400 | keep | 0 | Aug | 2021 | 0.0016346 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BARRANQUITAS | 2021-08-18 12:54 | 2021-08-18 16:45 | 50 | 003:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21081800050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 231 | 2021-08-18 | 11550 | keep | 0 | Aug | 2021 | 0.0078667 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
FAJARDO | 2021-08-18 13:05 | 2021-08-18 15:33 | 100 | 002:28 | P | ESTRUCTURA AVERIADA | 1 X 50 EN CORTE DE LINEA SE SECCIONALIZO POSTE EN EL SUELO | R21081800026 | New_Event | Defective Pole | Include | Include | Equipment | 148 | 2021-08-18 | 14800 | keep | 0 | Aug | 2021 | 0.01008 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-08-18 13:24 | 2021-08-20 19:10 | 24 | 053:46 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR 37.5KVA | B21081800118 | New_Event | Service Transformer Failure | Include | Include | Equipment | 3226 | 2021-08-18 | 77424 | keep | 0 | Aug | 2021 | 0.052733 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
GUAYAMA | 2021-08-18 13:37 | 2021-08-18 14:55 | 150 | 001:18 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIERON MACHETES PARA REMPLAZAR AISLADOR AVERIADO | P21081800074 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 78 | 2021-08-18 | 11700 | keep | 0 | Aug | 2021 | 0.0079688 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2021-08-18 13:40 | 2021-08-18 19:57 | 12 | 006:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B21081800124 | New_Event | Cutout Failure | Include | Include | Equipment | 377 | 2021-08-18 | 4524 | keep | 0 | Aug | 2021 | 0.0030813 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
AGUADILLA | 2021-08-18 14:08 | 2021-08-18 18:10 | 200 | 004:02 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | M21081800091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2021-08-18 | 48400 | keep | 0 | Aug | 2021 | 0.032965 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-08-18 14:19 | 2021-08-18 20:00 | 25 | 005:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA MAL TIEMPO | M21081800092 | New_Event | Bad Weather | Include | Include | Weather | 341 | 2021-08-18 | 8525 | keep | 0 | Aug | 2021 | 0.0058063 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
VEGA BAJA | 2021-08-18 14:28 | 2021-08-18 19:56 | 20 | 005:28 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO | B21081800141 | New_Event | Defective Pole | Include | Include | Equipment | 328 | 2021-08-18 | 6560 | keep | 0 | Aug | 2021 | 0.004468 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-08-18 14:36 | 2021-08-18 19:27 | 10 | 004:51 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHO | C21081800063 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 291 | 2021-08-18 | 2910 | keep | 0 | Aug | 2021 | 0.001982 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-08-18 14:44 | 2021-08-19 12:45 | 100 | 022:01 | P | DESGANCHE | SE CERRO ALIMENTADOR Y SE RETIRO RAMA | M21081800096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1321 | 2021-08-18 | 132100 | keep | 0 | Aug | 2021 | 0.089973 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-08-18 14:58 | 2021-08-18 18:18 | 50 | 003:20 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21081800059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 200 | 2021-08-18 | 10000 | keep | 0 | Aug | 2021 | 0.006811 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-08-18 15:03 | 2021-08-18 18:57 | 11 | 003:54 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR POSTE SECUNDARIO | C21081700200 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 234 | 2021-08-18 | 2574 | keep | 0 | Aug | 2021 | 0.0017531 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
PONCE | 2021-08-18 15:06 | 2021-08-18 16:40 | 100 | 001:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE EN CORTE DE LINEA | P21081800081 | New_Event | Wire Down | Include | Include | Equipment | 94 | 2021-08-18 | 9400 | keep | 0 | Aug | 2021 | 0.0064023 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
GUAYAMA | 2021-08-18 15:09 | 2021-08-18 15:27 | 215 | 000:18 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO INTERRUPTOR PARA REMPLAZAR AISLADOR AVERIADO EN TRONCAL PRIMARIO AUTORIZADO POR JOSE MORALES | P21081800083 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 18 | 2021-08-18 | 3870 | keep | 0 | Aug | 2021 | 0.0026358 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
ARECIBO | 2021-08-18 15:16 | 2021-08-18 15:45 | 20 | 000:29 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA IGUANA CRUZO LINEAS | A21081800057 | New_Event |  |  | Include | Wildlife | 29 | 2021-08-18 | 580 | keep | 0 | Aug | 2021 | 0.00039504 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-08-18 15:19 | 2021-08-19 11:13 | 50 | 019:54 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21081800085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1194 | 2021-08-18 | 59700 | keep | 0 | Aug | 2021 | 0.040661 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-08-18 15:20 | 2021-08-18 18:11 | 12 | 002:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZARON CONECTORES A LA SALIDA DE TRANSFORMADOR | B21081800153 | New_Event | Secondary Wire Down | Include | Include | Equipment | 171 | 2021-08-18 | 2052 | keep | 0 | Aug | 2021 | 0.0013976 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2021-08-18 15:28 | 2021-08-18 17:38 | 100 | 002:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO PORTA FUSIBLE AVERIADO | A21081800059 | New_Event | Cutout Failure | Include | Include | Equipment | 130 | 2021-08-18 | 13000 | keep | 0 | Aug | 2021 | 0.0088542 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-08-18 15:36 | 2021-08-19 12:20 | 30 | 020:44 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21081800106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1244 | 2021-08-18 | 37320 | keep | 0 | Aug | 2021 | 0.025418 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-08-18 15:42 | 2021-08-18 17:25 | 100 | 001:43 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R21081800035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2021-08-18 | 10300 | keep | 0 | Aug | 2021 | 0.0070153 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-08-18 15:57 | 2021-08-19 11:50 | 20 | 019:53 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA POR DESGANCHE | A21081800066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1193 | 2021-08-18 | 23860 | keep | 0 | Aug | 2021 | 0.016251 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-08-18 16:00 | 2021-08-18 17:44 | 844 | 001:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO TRAS PATIO Y AL CERRAR MACHETE DISPARO INTERRUPTOR | S21081800044 | Additional_clients | Wire Down | Include | Include | Equipment | 104 | 2021-08-18 | 87776 | keep | 0 | Aug | 2021 | 0.059784 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-18 16:00 | 2021-08-18 17:30 | 20 | 001:30 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | M21081800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2021-08-18 | 1800 | keep | 0 | Aug | 2021 | 0.001226 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-08-18 16:03 | 2021-08-18 18:36 | 5 | 002:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21081600279 | New_Event | Secondary Wire Down | Include | Include | Equipment | 153 | 2021-08-18 | 765 | keep | 0 | Aug | 2021 | 0.00052104 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-08-18 16:17 | 2021-08-18 21:18 | 50 | 005:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21081800078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 301 | 2021-08-18 | 15050 | keep | 0 | Aug | 2021 | 0.01025 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-18 16:19 | 2021-08-18 17:30 | 80 | 001:11 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | M21081800119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2021-08-18 | 5680 | keep | 0 | Aug | 2021 | 0.0038686 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-08-18 16:20 | 2021-08-18 18:12 | 20 | 001:52 | P | HERRAJE ROTO O PODRIDO | SE ABRIO CORTE DE LINEA PARA REMPLAZO DE CRUCETA PARTIDA | A21081800068 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 112 | 2021-08-18 | 2240 | keep | 0 | Aug | 2021 | 0.0015257 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BARRANQUITAS | 2021-08-18 16:29 | 2021-08-18 17:13 | 40 | 000:44 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21081800082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 44 | 2021-08-18 | 1760 | keep | 0 | Aug | 2021 | 0.0011987 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-08-18 16:30 | 2021-08-19 14:30 | 8 | 022:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | A21081800070 | New_Event | Cutout Failure | Include | Include | Equipment | 1320 | 2021-08-18 | 10560 | keep | 0 | Aug | 2021 | 0.0071924 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-08-18 16:31 | 2021-08-19 14:14 | 50 | 021:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21081800133 | New_Event | Bad Weather | Include | Include | Weather | 1303 | 2021-08-18 | 65150 | keep | 0 | Aug | 2021 | 0.044373 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-18 16:32 | 2021-08-18 19:00 | 10 | 002:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A21081800071 | New_Event | Wire Down | Include | Include | Equipment | 148 | 2021-08-18 | 1480 | keep | 0 | Aug | 2021 | 0.001008 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-08-18 16:35 | 2021-08-18 17:14 | 12 | 000:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE RETEZO SECUNDARIA | S21081800066 | New_Event | Secondary Wire Down | Include | Include | Equipment | 39 | 2021-08-18 | 468 | keep | 0 | Aug | 2021 | 0.00031875 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2021-08-18 16:45 | 2021-08-18 16:48 | 1352 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON RECIERRE EN OFF | P21081800096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-08-18 | 4056 | keep | 0 | Aug | 2021 | 0.0027625 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
PONCE | 2021-08-18 16:51 | 2021-08-18 16:52 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | P21081800101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-18 | 3114 | keep | 0 | Aug | 2021 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
HUMACAO | 2021-08-18 16:54 | 2021-08-18 18:19 | 65 | 001:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21081800087 | New_Event |  |  | Include | Wildlife | 85 | 2021-08-18 | 5525 | keep | 0 | Aug | 2021 | 0.0037631 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BAYAMON | 2021-08-18 17:10 | 2021-08-18 18:20 | 12 | 001:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO 75 PIES SECUNDARIA | S21081800063 | New_Event | Secondary Wire Down | Include | Include | Equipment | 70 | 2021-08-18 | 840 | keep | 0 | Aug | 2021 | 0.00057212 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-08-18 17:10 | 2021-08-18 17:11 | 3511 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21081800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-18 | 3511 | keep | 0 | Aug | 2021 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
UTUADO | 2021-08-18 17:20 | 2021-08-18 19:30 | 20 | 002:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21081800076 | New_Event | Bad Weather | Include | Include | Weather | 130 | 2021-08-18 | 2600 | keep | 0 | Aug | 2021 | 0.0017708 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
UTUADO | 2021-08-18 17:28 | 2021-08-18 18:20 | 8 | 000:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21081800000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 52 | 2021-08-18 | 416 | keep | 0 | Aug | 2021 | 0.00028334 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-08-18 17:29 | 2021-08-18 22:12 | 50 | 004:43 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21081800172 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2021-08-18 | 14150 | keep | 0 | Aug | 2021 | 0.0096375 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-18 17:44 | 2021-08-18 17:53 | 1085 | 000:09 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | AL CERRAR MACHETE DISPARO INTERRUPTOR SE ABRE MACHETE CONTINUARAN PATRULLANDO | S21081800088 | Additional_clients | Wire Down | Include | Include | Equipment | 9 | 2021-08-18 | 9765 | keep | 0 | Aug | 2021 | 0.0066509 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-18 17:45 | 2021-08-18 17:46 | 1420 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR 1530-06 | S21081800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-18 | 1420 | keep | 0 | Aug | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-08-18 17:45 | 2021-08-18 17:46 | 437 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVANDO 1526-02 | S21081800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-18 | 437 | keep | 0 | Aug | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
VEGA BAJA | 2021-08-18 17:49 | 2021-08-19 19:37 | 12 | 025:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA SE REMPLAZARON BAJANTES PRIMARIOS Y SECUNDARIOS | B21081800180 | New_Event | Cutout Failure | Include | Include | Equipment | 1548 | 2021-08-18 | 18576 | keep | 0 | Aug | 2021 | 0.012652 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-08-18 17:53 | 2021-08-18 18:29 | 844 | 000:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ENCONTRO LINEA CRUZADAS TRASPATIO CALLE ESCORIAL Y SE REPARO CERRO MACHETE 100% EN SERVICIO | S21081800088 | Partial_restoration | Wire Down | Include | Include | Equipment | 36 | 2021-08-18 | 30384 | keep | 0 | Aug | 2021 | 0.020694 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
PONCE | 2021-08-18 18:03 | 2021-08-19 16:49 | 10 | 022:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO XMR PARA REPARAR SECUNDARIA Y SE HIZO DESGANCHE | P21081800107 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1366 | 2021-08-18 | 13660 | keep | 0 | Aug | 2021 | 0.0093038 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-08-18 18:15 | 2021-08-18 18:16 | 3957 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21081800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-18 | 3957 | keep | 0 | Aug | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
MAYAGÃœEZ | 2021-08-18 18:19 | 2021-08-18 20:54 | 10 | 002:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | M21081800163 | New_Event | Bad Weather | Include | Include | Weather | 155 | 2021-08-18 | 1550 | keep | 0 | Aug | 2021 | 0.0010557 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-08-18 18:20 | 2021-08-19 14:09 | 24 | 019:49 | P | DESGANCHE | 2 X 40 EN CORTES DE LINEA | C21081800094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1189 | 2021-08-18 | 28536 | keep | 0 | Aug | 2021 | 0.019436 | 1.6346e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 24
AGUADILLA | 2021-08-18 18:20 | 2021-08-18 22:45 | 70 | 004:25 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21081800164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 265 | 2021-08-18 | 18550 | keep | 0 | Aug | 2021 | 0.012634 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
ARECIBO | 2021-08-18 18:26 | 2021-08-19 11:55 | 10 | 017:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES SECUNDARIAS | A21081800083 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1049 | 2021-08-18 | 10490 | keep | 0 | Aug | 2021 | 0.0071447 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-08-18 18:37 | 2021-08-18 18:38 | 1017 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | M21081800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-18 | 1017 | keep | 0 | Aug | 2021 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
CANOVANAS | 2021-08-18 18:38 | 2021-08-18 18:39 | 1894 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21081800039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-18 | 1894 | keep | 0 | Aug | 2021 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
CANOVANAS | 2021-08-18 18:38 | 2021-08-18 18:40 | 1648 | 000:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | R21081800039 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2021-08-18 | 3296 | keep | 0 | Aug | 2021 | 0.0022449 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2021-08-18 18:40 | 2021-08-18 22:30 | 549 | 003:50 | P | DESCONECTIVO DEFECTUOSO | MACHETE QUEMADO EN LA SALIDA DEL ALIMENTADOR | R21081800081 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 230 | 2021-08-18 | 126270 | keep | 0 | Aug | 2021 | 0.086002 | 0.00037392 | Sustained | FALSE | FALSE | Not_TMED_Event | 549
ARECIBO | 2021-08-18 18:52 | 2021-08-18 19:04 | 6 | 000:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21081800077 | New_Event | Secondary Wire Down | Include | Include | Equipment | 12 | 2021-08-18 | 72 | keep | 0 | Aug | 2021 | 4.9039e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-08-18 19:20 | 2021-08-18 19:40 | 12 | 000:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONECTOR SECUNDARIO SULFATADO | P21081800108 | New_Event | Secondary Wire Down | Include | Include | Equipment | 20 | 2021-08-18 | 240 | keep | 0 | Aug | 2021 | 0.00016346 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-08-18 19:43 | 2021-08-19 11:26 | 20 | 015:43 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR POR DESGANCHE | A21081800090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 943 | 2021-08-18 | 18860 | keep | 0 | Aug | 2021 | 0.012845 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-08-18 19:44 | 2021-08-18 22:30 | 11 | 002:46 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE DIO MANTENIMIENTO AL SU-4A | R21081800057 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 166 | 2021-08-18 | 1826 | keep | 0 | Aug | 2021 | 0.0012437 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
VEGA BAJA | 2021-08-18 19:56 | 2021-08-18 20:41 | 12 | 000:45 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21081800257 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 45 | 2021-08-18 | 540 | keep | 0 | Aug | 2021 | 0.00036779 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2021-08-18 20:17 | 2021-08-19 16:31 | 50 | 020:14 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P21081800115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1214 | 2021-08-18 | 60700 | keep | 0 | Aug | 2021 | 0.041342 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-08-18 20:18 | 2021-08-19 10:29 | 40 | 014:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C21081800117 | New_Event | Bad Weather | Include | Include | Weather | 851 | 2021-08-18 | 34040 | keep | 0 | Aug | 2021 | 0.023184 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-08-18 20:45 | 2021-08-19 12:05 | 65 | 015:20 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21081800069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 920 | 2021-08-18 | 59800 | keep | 0 | Aug | 2021 | 0.04073 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
AGUADILLA | 2021-08-18 20:49 | 2021-08-18 23:36 | 200 | 002:47 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M21081800177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2021-08-18 | 33400 | keep | 0 | Aug | 2021 | 0.022749 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
PONCE | 2021-08-18 20:57 | 2021-08-19 10:10 | 100 | 013:13 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | P21081800123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 793 | 2021-08-18 | 79300 | keep | 0 | Aug | 2021 | 0.054011 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-08-18 21:09 | 2021-08-19 10:01 | 80 | 012:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | R21081800075 | New_Event |  |  | Include | Wildlife | 772 | 2021-08-18 | 61760 | keep | 0 | Aug | 2021 | 0.042064 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-08-18 21:20 | 2021-08-19 09:21 | 80 | 012:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA. | P21081800126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 721 | 2021-08-18 | 57680 | keep | 0 | Aug | 2021 | 0.039286 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-08-18 21:43 | 2021-08-20 19:16 | 24 | 045:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO GROUND PRIMARIO DEL TRANSFORMADOR | C21081800121 | New_Event | Wire Down | Include | Include | Equipment | 2733 | 2021-08-18 | 65592 | keep | 0 | Aug | 2021 | 0.044674 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
SAN JUAN | 2021-08-18 21:51 | 2021-08-19 12:29 | 35 | 014:38 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21081800108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 878 | 2021-08-18 | 30730 | keep | 0 | Aug | 2021 | 0.02093 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-08-18 21:57 | 2021-08-19 11:20 | 75 | 013:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA MARCA:ABB 200AMP. | A21081800094 | New_Event | Cutout Failure | Include | Include | Equipment | 803 | 2021-08-18 | 60225 | keep | 0 | Aug | 2021 | 0.041019 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
CANOVANAS | 2021-08-18 22:30 | 2021-08-18 22:43 | 1648 | 000:13 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA COLOCAR PUENTE SOBRE MACHETE QUEMADO EN LA SALIDA DEL ALIMENTADOR | R21081800081 | Additional_clients | Switch Failure | Include | Include | Equipment | 13 | 2021-08-18 | 21424 | keep | 0 | Aug | 2021 | 0.014592 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-18 22:33 | 2021-08-19 09:15 | 40 | 010:42 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | M21081800193 | New_Event | Vegetation Contact | Include | Include | Vegetation | 642 | 2021-08-18 | 25680 | keep | 0 | Aug | 2021 | 0.017491 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-08-18 22:43 | 2021-08-19 15:36 | 11 | 016:53 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE DIO MANTENIMIENTO AL SU-4A | R21081800057 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 1013 | 2021-08-18 | 11143 | keep | 0 | Aug | 2021 | 0.0075894 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-18 22:56 | 2021-08-19 12:30 | 300 | 013:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA DE EMERGENCIA PARA REPARAR ALAMBRE PARTIDO | M21081800196 | New_Event | Wire Down | Include | Include | Equipment | 814 | 2021-08-18 | 244200 | keep | 0 | Aug | 2021 | 0.16632 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
ARECIBO | 2021-08-18 23:03 | 2021-08-19 09:39 | 30 | 010:36 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | A21081800095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 636 | 2021-08-18 | 19080 | keep | 0 | Aug | 2021 | 0.012995 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-08-18 23:33 | 2021-08-19 16:11 | 300 | 016:38 | P | DESGANCHE | REPUSO 2 X 100 EN CORTE DE LINEA Y SE RETIRO RAMA SOBRE LINEA | C21081800122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 998 | 2021-08-18 | 299400 | keep | 0 | Aug | 2021 | 0.20392 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-08-19 02:55 | 2021-08-19 02:56 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21081900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-19 | 990 | keep | 0 | Aug | 2021 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
BARRANQUITAS | 2021-08-19 04:40 | 2021-08-19 11:32 | 40 | 006:52 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21081900003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 412 | 2021-08-19 | 16480 | keep | 0 | Aug | 2021 | 0.011224 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-19 05:30 | 2021-08-19 11:50 | 60 | 006:20 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M21081900006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 380 | 2021-08-19 | 22800 | keep | 0 | Aug | 2021 | 0.015529 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
FAJARDO | 2021-08-19 05:52 | 2021-08-19 11:10 | 20 | 005:18 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA | R21081900002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 318 | 2021-08-19 | 6360 | keep | 0 | Aug | 2021 | 0.0043318 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-08-19 06:00 | 2021-08-19 17:30 | 1 | 011:30 | P | DESGANCHE | 1 X 5 EN TRANSFORMADOR SE RETIRO ENREDADERAS | M21081800012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 690 | 2021-08-19 | 690 | keep | 0 | Aug | 2021 | 0.00046996 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2021-08-19 06:29 | 2021-08-19 06:30 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210819000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-19 | 3744 | keep | 0 | Aug | 2021 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
GUAYAMA | 2021-08-19 06:43 | 2021-08-19 06:44 | 464 | 000:01 | T | DESGANCHE | RECIERRE | P210819000XX | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-19 | 464 | keep | 0 | Aug | 2021 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2021-08-19 06:44 | 2021-08-19 11:55 | 65 | 005:11 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21081900028 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 311 | 2021-08-19 | 20215 | keep | 0 | Aug | 2021 | 0.013768 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BAYAMON | 2021-08-19 07:07 | 2021-08-19 14:22 | 12 | 007:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO Y NEUTRAL EN LINEA SECUNDARIA | B21081900006 | New_Event | Secondary Wire Down | Include | Include | Equipment | 435 | 2021-08-19 | 5220 | keep | 0 | Aug | 2021 | 0.0035553 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
CAGUAS | 2021-08-19 07:37 | 2021-08-19 09:44 | 300 | 002:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA REMPLAZO CAJA QUEMADA | C21081900008 | New_Event | Cutout Failure | Include | Include | Equipment | 127 | 2021-08-19 | 38100 | keep | 0 | Aug | 2021 | 0.02595 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
BAYAMON | 2021-08-19 07:45 | 2021-08-19 15:38 | 15 | 007:53 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | B21081900007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 473 | 2021-08-19 | 7095 | keep | 0 | Aug | 2021 | 0.0048324 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
GUAYAMA | 2021-08-19 08:01 | 2021-08-19 16:30 | 8 | 008:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR FUERTES VIENTOS | P21081900008 | New_Event | Bad Weather | Include | Include | Weather | 509 | 2021-08-19 | 4072 | keep | 0 | Aug | 2021 | 0.0027734 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-08-19 08:13 | 2021-08-19 17:50 | 100 | 009:37 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21081900004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 577 | 2021-08-19 | 57700 | keep | 0 | Aug | 2021 | 0.039299 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-08-19 08:15 | 2021-08-20 11:00 | 100 | 026:45 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | C21081900015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1605 | 2021-08-19 | 160500 | keep | 0 | Aug | 2021 | 0.10932 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-08-19 08:24 | 2021-08-21 17:13 | 20 | 056:49 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU 4 | B21081900010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3409 | 2021-08-19 | 68180 | keep | 0 | Aug | 2021 | 0.046437 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-08-19 08:26 | 2021-08-19 13:30 | 40 | 005:04 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUAS SOBRE LINEA PRIMARIA | M21081900007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 304 | 2021-08-19 | 12160 | keep | 0 | Aug | 2021 | 0.0082821 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-08-19 08:32 | 2021-08-19 08:33 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21081900013 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-19 | 3744 | keep | 0 | Aug | 2021 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
AGUADILLA | 2021-08-19 08:45 | 2021-08-19 15:50 | 150 | 007:05 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | M21081900024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 425 | 2021-08-19 | 63750 | keep | 0 | Aug | 2021 | 0.04342 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-08-19 09:03 | 2021-08-19 10:09 | 6 | 001:06 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M21081900033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2021-08-19 | 396 | keep | 0 | Aug | 2021 | 0.00026971 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
CANOVANAS | 2021-08-19 09:15 | 2021-08-19 09:16 | 539 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE LLEVA LA CARGA DEL 2305-04 | R21081900000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2021-08-19 | 539 | keep | 0 | Aug | 2021 | 0.00036711 | 0.00036711 | Momentary | FALSE | FALSE | Not_TMED_Event | 539
CANOVANAS | 2021-08-19 09:15 | 2021-08-19 09:16 | 635 | 000:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE LLEVA LA CARGA DEL 2305-04 | R21081900000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2021-08-19 | 635 | keep | 0 | Aug | 2021 | 0.0004325 | 0.0004325 | Momentary | FALSE | FALSE | Not_TMED_Event | 635
CANOVANAS | 2021-08-19 09:16 | 2021-08-19 10:56 | 180 | 001:40 | P | DESCONECTIVO DEFECTUOSO | SE ENCONTRO MACHETE QUEMADO EN RISER DE SALIDA | R21081900000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 100 | 2021-08-19 | 18000 | keep | 0 | Aug | 2021 | 0.01226 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
CANOVANAS | 2021-08-19 09:16 | 2021-08-19 10:56 | 211 | 001:40 | P | DESCONECTIVO DEFECTUOSO | SE ENCONTRO MACHETE QUEMADO EN RISER DE SALIDA CARGA POR 2305-01 | R21081900000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 100 | 2021-08-19 | 21100 | keep | 0 | Aug | 2021 | 0.014371 | 0.00014371 | Sustained | FALSE | FALSE | Not_TMED_Event | 211
ARECIBO | 2021-08-19 09:20 | 2021-08-19 14:16 | 75 | 004:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | A21081900010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 296 | 2021-08-19 | 22200 | keep | 0 | Aug | 2021 | 0.01512 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
PONCE | 2021-08-19 09:26 | 2021-08-19 18:34 | 200 | 009:08 | P | DESGANCHE | 2 X 140 EN CORTE DE LINEA POR DESGANCHE | P21081900021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 548 | 2021-08-19 | 109600 | keep | 0 | Aug | 2021 | 0.074648 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
AGUADILLA | 2021-08-19 09:32 | 2021-08-19 16:00 | 12 | 006:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZARON CONECTORES | M21081900039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 388 | 2021-08-19 | 4656 | keep | 0 | Aug | 2021 | 0.0031712 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-08-19 09:33 | 2021-08-19 18:05 | 30 | 008:32 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 50KVA X 50KVA | C21081900019 | New_Event | Service Transformer Failure | Include | Include | Equipment | 512 | 2021-08-19 | 15360 | keep | 0 | Aug | 2021 | 0.010462 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-08-19 09:39 | 2021-08-19 18:55 | 100 | 009:16 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL SU-15 AL SU-13 | C21081900021 | New_Event | UG Cable Fault | Include | Include | Equipment | 556 | 2021-08-19 | 55600 | keep | 0 | Aug | 2021 | 0.037869 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-08-19 09:42 | 2021-08-19 23:23 | 40 | 013:41 | P | HERRAJE ROTO O PODRIDO | SE REEMPLAZO CRUCETA Y SE CERRO CORTE DE LINEA | S21081900018 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 821 | 2021-08-19 | 32840 | keep | 0 | Aug | 2021 | 0.022367 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-08-19 09:45 | 2021-08-19 09:46 | 1533 | 000:01 | T | DESGANCHE | RECERRO LLEVA EL 1709-05 | S21081900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-19 | 1533 | keep | 0 | Aug | 2021 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
BAYAMON | 2021-08-19 09:45 | 2021-08-19 09:46 | 2364 | 000:01 | T | DESGANCHE | RECERRO CARGA POR EL 1709-03 | S21081900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-19 | 2364 | keep | 0 | Aug | 2021 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
BAYAMON | 2021-08-19 09:46 | 2021-08-19 16:11 | 1 | 006:25 | P | DESGANCHE | SE REALIZO DESGANCHE | S21081900023 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 385 | 2021-08-19 | 385 | keep | 0 | Aug | 2021 | 0.00026222 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2021-08-19 09:46 | 2021-08-19 22:38 | 250 | 012:52 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | M21081900041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 772 | 2021-08-19 | 193000 | keep | 0 | Aug | 2021 | 0.13145 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
BAYAMON | 2021-08-19 09:50 | 2021-08-19 14:10 | 12 | 004:20 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REEMPLAZARON 2 POSTES SECUNDARIOS PARTIDOS | S21081900000 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 260 | 2021-08-19 | 3120 | keep | 0 | Aug | 2021 | 0.002125 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-08-19 09:57 | 2021-08-19 16:31 | 1 | 006:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO CONEXIONES SECUNDARIAS | A21081900014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 394 | 2021-08-19 | 394 | keep | 0 | Aug | 2021 | 0.00026835 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-08-19 10:06 | 2021-08-20 12:12 | 8 | 026:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21081900055 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1566 | 2021-08-19 | 12528 | keep | 0 | Aug | 2021 | 0.0085328 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-08-19 10:11 | 2021-08-19 16:00 | 12 | 005:49 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRE MONTURA PARA REEMPLAZO POSTE SECUNDARIO | S21081900021 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 349 | 2021-08-19 | 4188 | keep | 0 | Aug | 2021 | 0.0028524 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-08-19 10:11 | 2021-08-20 11:47 | 30 | 025:36 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21081900023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1536 | 2021-08-19 | 46080 | keep | 0 | Aug | 2021 | 0.031385 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-08-19 10:11 | 2021-08-19 10:25 | 316 | 000:14 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR RELAY RECLOSER SE ENCONTRABA DESACTIVADO | A21081900017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 14 | 2021-08-19 | 4424 | keep | 0 | Aug | 2021 | 0.0030132 | 0.00021523 | Sustained | FALSE | FALSE | Not_TMED_Event | 316
HUMACAO | 2021-08-19 10:25 | 2021-08-19 11:01 | 8 | 000:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BARRA DE PEDESTAL QUEMADA | C21081800043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 36 | 2021-08-19 | 288 | keep | 0 | Aug | 2021 | 0.00019616 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-08-19 10:29 | 2021-08-19 15:15 | 15 | 004:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80, 1 X 20 EN CORTES DE LINEA Y 1 X 15 EN RISER CONTAMINACION EN CAJA PRIMARIA | R21081900029 | New_Event | Cutout Failure | Include | Include | Equipment | 286 | 2021-08-19 | 4290 | keep | 0 | Aug | 2021 | 0.0029219 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CANOVANAS | 2021-08-19 10:56 | 2021-08-19 11:54 | 539 | 000:58 | T | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO EN EL RISER DE SALIDA LLEVA LA CARGA DEL 2305-04 | R21081900041 | New_Event | Switch Failure | Include | Include | Equipment | 58 | 2021-08-19 | 31262 | keep | 0 | Aug | 2021 | 0.021292 | 0.00036711 | Sustained | FALSE | FALSE | Not_TMED_Event | 539
CANOVANAS | 2021-08-19 10:56 | 2021-08-19 11:54 | 635 | 000:58 | T | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO EN EL RISER DE SALIDA DEL 2305-01 | R21081900041 | New_Event | Switch Failure | Include | Include | Equipment | 58 | 2021-08-19 | 36830 | keep | 0 | Aug | 2021 | 0.025085 | 0.0004325 | Sustained | FALSE | FALSE | Not_TMED_Event | 635
UTUADO | 2021-08-19 10:59 | 2021-08-19 16:55 | 80 | 005:56 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | A21081900023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 356 | 2021-08-19 | 28480 | keep | 0 | Aug | 2021 | 0.019398 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-08-19 11:00 | 2021-08-19 11:45 | 4 | 000:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR NEUTRAL SECUNDARIO PARTIDO | M21081900017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 45 | 2021-08-19 | 180 | keep | 0 | Aug | 2021 | 0.0001226 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2021-08-19 11:00 | 2021-08-19 15:50 | 10 | 004:50 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 100 KVA MARCA EMMCO FID-1001781926 | M21081900053 | New_Event | Service Transformer Failure | Include | Include | Equipment | 290 | 2021-08-19 | 2900 | keep | 0 | Aug | 2021 | 0.0019752 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-08-19 11:07 | 2021-08-19 16:11 | 50 | 005:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA CABLE ZAFADO DE LA AISLACION | C21081900042 | New_Event | Wire Down | Include | Include | Equipment | 304 | 2021-08-19 | 15200 | keep | 0 | Aug | 2021 | 0.010353 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-08-19 11:36 | 2021-08-19 13:32 | 40 | 001:56 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21081900045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2021-08-19 | 4640 | keep | 0 | Aug | 2021 | 0.0031603 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-08-19 11:37 | 2021-08-19 11:56 | 5 | 000:19 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE SECUNDARIO A TRANSFORMADOR WR 5907676 | A21081900000 | New_Event | Wire Down | Include | Include | Equipment | 19 | 2021-08-19 | 95 | keep | 0 | Aug | 2021 | 6.4704e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-08-19 11:45 | 2021-08-19 16:00 | 12 | 004:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO BAJANTE SECUNDARIO SE REPARO LINEA SECUNDARIA Y VARIAS TOMAS | B21081900031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 255 | 2021-08-19 | 3060 | keep | 0 | Aug | 2021 | 0.0020842 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
SAN JUAN | 2021-08-19 11:50 | 2021-08-19 12:55 | 12 | 001:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | S21081800020 | New_Event | Secondary Wire Down | Include | Include | Equipment | 65 | 2021-08-19 | 780 | keep | 0 | Aug | 2021 | 0.00053125 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-08-19 12:05 | 2021-08-19 16:32 | 15 | 004:27 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LA LINEA | A21081890034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 267 | 2021-08-19 | 4005 | keep | 0 | Aug | 2021 | 0.0027278 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-08-19 12:11 | 2021-08-19 19:46 | 60 | 007:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21081900063 | New_Event | Bad Weather | Include | Include | Weather | 455 | 2021-08-19 | 27300 | keep | 0 | Aug | 2021 | 0.018594 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-08-19 12:14 | 2021-08-19 12:15 | 2697 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21081900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-19 | 2697 | keep | 0 | Aug | 2021 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
BARRANQUITAS | 2021-08-19 12:23 | 2021-08-19 16:29 | 39 | 004:06 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | C21081900055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 246 | 2021-08-19 | 9594 | keep | 0 | Aug | 2021 | 0.0065344 | 2.6563e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 39
MAYAGÃœEZ | 2021-08-19 12:30 | 2021-08-19 15:15 | 400 | 002:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR NEUTRAL PRIMARIO | M21081900042 | New_Event | Wire Down | Include | Include | Equipment | 165 | 2021-08-19 | 66000 | keep | 0 | Aug | 2021 | 0.044952 | 0.00027244 | Sustained | FALSE | TRUE | Not_TMED_Event | 400
CAGUAS | 2021-08-19 12:34 | 2021-08-19 21:08 | 26 | 008:34 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25KVA X 25KVA | C21081900057 | New_Event | Service Transformer Failure | Include | Include | Equipment | 514 | 2021-08-19 | 13364 | keep | 0 | Aug | 2021 | 0.0091022 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
SAN JUAN | 2021-08-19 12:42 | 2021-08-19 12:43 | 2391 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRPTOR Y SE CERRO POR SCADA | S21081900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-19 | 2391 | keep | 0 | Aug | 2021 | 0.0016285 | 0.0016285 | Momentary | FALSE | FALSE | Not_TMED_Event | 2391
BAYAMON | 2021-08-19 12:42 | 2021-08-19 13:52 | 12 | 001:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO DE LINEA A CAJA EN TRANSFORMADOR | S21081900016 | New_Event | Wire Down | Include | Include | Equipment | 70 | 2021-08-19 | 840 | keep | 0 | Aug | 2021 | 0.00057212 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
BAYAMON | 2021-08-19 12:46 | 2021-08-20 12:53 | 30 | 024:07 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA CARGA POR EL 1709-01 | B21081900037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1447 | 2021-08-19 | 43410 | keep | 0 | Aug | 2021 | 0.029566 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-08-19 12:52 | 2021-08-19 15:41 | 50 | 002:49 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTA CAUSA | P21081900052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2021-08-19 | 8450 | keep | 0 | Aug | 2021 | 0.0057553 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-08-19 12:57 | 2021-08-19 17:24 | 4 | 004:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 25 EN TRANSFORMADOR SE REPARO CONEXIONES SECUNDARIAS | A21081800045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 267 | 2021-08-19 | 1068 | keep | 0 | Aug | 2021 | 0.00072741 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-08-19 12:57 | 2021-08-19 13:37 | 3 | 000:40 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA PARTIDA | A21081800049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 40 | 2021-08-19 | 120 | keep | 0 | Aug | 2021 | 8.1731e-05 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
MAYAGÃœEZ | 2021-08-19 13:00 | 2021-08-19 17:35 | 60 | 004:35 | P | DESGANCHE | SE REMPLAZO 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE EN LINEA PRIMARIA | M21081900052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2021-08-19 | 16500 | keep | 0 | Aug | 2021 | 0.011238 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
VEGA BAJA | 2021-08-19 13:10 | 2021-08-19 14:37 | 1859 | 001:27 | T | DESGANCHE | DISPARO DE INTERRUPTOR LLEVA LA CARGA DEL 9207-09 SE REALIZO DESGANCHE PRIMARIO | B21081700100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2021-08-19 | 161733 | keep | 0 | Aug | 2021 | 0.11016 | 0.0012662 | Sustained | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2021-08-19 13:10 | 2021-08-19 14:37 | 7 | 001:27 | T | DESGANCHE | DISPARO DE INTERRUPTOR 9207-08 LLEVA LA CARGA DEL 9207-09 SE REALIZO DESGANCHE PRIMARIO | B21081700100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2021-08-19 | 609 | keep | 0 | Aug | 2021 | 0.00041479 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-08-19 13:11 | 2021-08-19 15:41 | 10211 | 002:30 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO AL CERRAR MACHETE CARR 181 Y SE SECCIONALIZO ABRIENDO CARR 846 FRENTE A CIUDAD UNIVERSITARIA CENTRO COMERCIAL Y SE CERRO N/O FRENTE A AUTOZONE 100% EN SERVICIO 1206-3 Y 50% 1204-5 | S21081900010 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 150 | 2021-08-19 | 1531650 | keep | 0 | Aug | 2021 | 1.0432 | 0.0069547 | Sustained | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-08-19 13:11 | 2021-08-19 13:57 | 4133 | 000:46 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO QUEDO ABIERTO SE ABRIO N/O CONTRA 1204-5 CARR 876 INT 181 FRENTE A AUTOZONE SE CERRO INTERRUPTOR 100% 1206-3 | S21081900041 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 46 | 2021-08-19 | 190118 | keep | 0 | Aug | 2021 | 0.12949 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
MAYAGÃœEZ | 2021-08-19 13:14 | 2021-08-19 17:30 | 60 | 004:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21081800078 | New_Event | Bad Weather | Include | Include | Weather | 256 | 2021-08-19 | 15360 | keep | 0 | Aug | 2021 | 0.010462 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-08-19 13:28 | 2021-08-19 16:40 | 50 | 003:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21081900080 | New_Event | Bad Weather | Include | Include | Weather | 192 | 2021-08-19 | 9600 | keep | 0 | Aug | 2021 | 0.0065385 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-08-19 13:33 | 2021-08-19 15:22 | 554 | 001:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA EN EL CONVERTIDOR | R21081900068 | New_Event | Cutout Failure | Include | Include | Equipment | 109 | 2021-08-19 | 60386 | keep | 0 | Aug | 2021 | 0.041129 | 0.00037733 | Sustained | FALSE | FALSE | Not_TMED_Event | 554
BARRANQUITAS | 2021-08-19 13:50 | 2021-08-19 14:30 | 7 | 000:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO | C21081900068 | New_Event | Cutout Failure | Include | Include | Equipment | 40 | 2021-08-19 | 280 | keep | 0 | Aug | 2021 | 0.00019071 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2021-08-19 14:04 | 2021-08-19 17:03 | 25 | 002:59 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO DISCO AVERIADO | R21081900072 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 179 | 2021-08-19 | 4475 | keep | 0 | Aug | 2021 | 0.0030479 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-08-19 14:05 | 2021-08-19 14:07 | 2791 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21081900049 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-08-19 | 5582 | keep | 0 | Aug | 2021 | 0.0038019 | 0.0019009 | Momentary | FALSE | TRUE | Not_TMED_Event | 2791
ARECIBO | 2021-08-19 14:05 | 2021-08-19 14:07 | 1464 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21081900049 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-08-19 | 2928 | keep | 0 | Aug | 2021 | 0.0019942 | 0.00099712 | Momentary | FALSE | TRUE | Not_TMED_Event | 1464
ARECIBO | 2021-08-19 14:05 | 2021-08-19 14:07 | 759 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21081900049 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-08-19 | 1518 | keep | 0 | Aug | 2021 | 0.0010339 | 0.00051695 | Momentary | FALSE | TRUE | Not_TMED_Event | 759
ARECIBO | 2021-08-19 14:05 | 2021-08-19 14:07 | 1500 | 000:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A21081900049 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-08-19 | 3000 | keep | 0 | Aug | 2021 | 0.0020433 | 0.0010216 | Momentary | FALSE | TRUE | Not_TMED_Event | 1500
AGUADILLA | 2021-08-19 14:10 | 2021-08-20 11:25 | 100 | 021:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA DE 100AMP MARCA SHINT | M21081900093 | New_Event | Cutout Failure | Include | Include | Equipment | 1275 | 2021-08-19 | 127500 | keep | 0 | Aug | 2021 | 0.08684 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-08-19 14:16 | 2021-08-19 17:26 | 9 | 003:10 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA CRUCE POR RAMA | R21081900076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2021-08-19 | 1710 | keep | 0 | Aug | 2021 | 0.0011647 | 6.1299e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 9
CAGUAS | 2021-08-19 14:16 | 2021-08-21 10:39 | 8 | 044:23 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C21081900072 | New_Event | Bad Weather | Include | Include | Weather | 2663 | 2021-08-19 | 21304 | keep | 0 | Aug | 2021 | 0.01451 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-08-19 14:23 | 2021-08-19 14:24 | 350 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1100-02 QUE LLEVA 1100-01 | S21081900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-19 | 350 | keep | 0 | Aug | 2021 | 0.00023838 | 0.00023838 | Momentary | FALSE | FALSE | Not_TMED_Event | 350
BAYAMON | 2021-08-19 14:23 | 2021-08-19 14:24 | 215 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1100-01 | S21081900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-19 | 215 | keep | 0 | Aug | 2021 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
AGUADILLA | 2021-08-19 14:28 | 2021-08-19 15:05 | 70 | 000:37 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | M21081900095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 37 | 2021-08-19 | 2590 | keep | 0 | Aug | 2021 | 0.001764 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
SAN JUAN | 2021-08-19 14:30 | 2021-08-19 16:39 | 15 | 002:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | S21081700093 | New_Event | Secondary Wire Down | Include | Include | Equipment | 129 | 2021-08-19 | 1935 | keep | 0 | Aug | 2021 | 0.0013179 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-08-19 14:30 | 2021-08-19 16:15 | 5 | 001:45 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR SECUNDARIA | M21081900035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 105 | 2021-08-19 | 525 | keep | 0 | Aug | 2021 | 0.00035758 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-08-19 15:18 | 2021-08-19 16:22 | 20 | 001:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE RETIRO IGUANA CRUZANDO LINEAS | B21081900045 | New_Event |  |  | Include | Wildlife | 64 | 2021-08-19 | 1280 | keep | 0 | Aug | 2021 | 0.0008718 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-08-19 15:21 | 2021-08-19 15:23 | 353 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO | S21081900101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-19 | 706 | keep | 0 | Aug | 2021 | 0.00048085 | 0.00024043 | Momentary | FALSE | FALSE | Not_TMED_Event | 353
ARECIBO | 2021-08-19 15:24 | 2021-08-19 17:01 | 1879 | 001:37 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A21081900144 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 97 | 2021-08-19 | 182263 | keep | 0 | Aug | 2021 | 0.12414 | 0.0012798 | Sustained | FALSE | TRUE | Not_TMED_Event | 1879
ARECIBO | 2021-08-19 15:24 | 2021-08-19 17:01 | 2777 | 001:37 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A21081900144 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 97 | 2021-08-19 | 269369 | keep | 0 | Aug | 2021 | 0.18347 | 0.0018914 | Sustained | FALSE | TRUE | Not_TMED_Event | 2777
ARECIBO | 2021-08-19 15:24 | 2021-08-19 17:01 | 2 | 001:37 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A21081900144 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 97 | 2021-08-19 | 194 | keep | 0 | Aug | 2021 | 0.00013213 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
ARECIBO | 2021-08-19 15:24 | 2021-08-19 17:01 | 2839 | 001:37 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A21081900146 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 97 | 2021-08-19 | 275383 | keep | 0 | Aug | 2021 | 0.18756 | 0.0019336 | Sustained | FALSE | TRUE | Not_TMED_Event | 2839
ARECIBO | 2021-08-19 15:24 | 2021-08-19 17:01 | 1160 | 001:37 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A21081900146 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 97 | 2021-08-19 | 112520 | keep | 0 | Aug | 2021 | 0.076637 | 0.00079007 | Sustained | FALSE | TRUE | Not_TMED_Event | 1160
ARECIBO | 2021-08-19 15:24 | 2021-08-19 17:01 | 1860 | 001:37 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A21081900146 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 97 | 2021-08-19 | 180420 | keep | 0 | Aug | 2021 | 0.12288 | 0.0012668 | Sustained | FALSE | TRUE | Not_TMED_Event | 1860
SAN JUAN | 2021-08-19 15:28 | 2021-08-19 15:41 | 4133 | 000:13 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO AL CERRAR MACHETE CARR 181 Y SE SECCIONALIZO ABRIENDO CARR 846 FRENTE CUIDAD UNIVERSITARIA CENTRO COMERCIAL Y SE CERRO N/O FRENTE AUTOZONE 100% EN SERVICIO 1206-3 Y 50% 1204-5 | S21081900010 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 13 | 2021-08-19 | 53729 | keep | 0 | Aug | 2021 | 0.036595 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-08-19 15:32 | 2021-08-19 16:45 | 40 | 001:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA | R21081900080 | New_Event | Wire Down | Include | Include | Equipment | 73 | 2021-08-19 | 2920 | keep | 0 | Aug | 2021 | 0.0019888 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-08-19 15:41 | 2021-08-19 16:46 | 5100 | 001:05 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR PLANCHA DE MACHETE Y SE CERRO MACHETE FRENTE CENTRO COMERCIAL CARR 846 100% EN SERVICIO | S21081900106 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 65 | 2021-08-19 | 331500 | keep | 0 | Aug | 2021 | 0.22578 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-08-19 15:41 | 2021-08-20 13:00 | 1 | 021:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN CORTE DE LINEA SE REEMPLAZO PORTA FUSIBLES | S21081900178 | New_Event | Cutout Failure | Include | Include | Equipment | 1279 | 2021-08-19 | 1279 | keep | 0 | Aug | 2021 | 0.00087112 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-08-19 16:09 | 2021-08-19 20:55 | 20 | 004:46 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21081900120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 286 | 2021-08-19 | 5720 | keep | 0 | Aug | 2021 | 0.0038959 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-08-19 16:10 | 2021-08-19 16:44 | 12 | 000:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE MONTURA PARA REPARAR BAJANTE DE LINEA A CAJA TRANSFORMADOR | S21081800032 | New_Event | Wire Down | Include | Include | Equipment | 34 | 2021-08-19 | 408 | keep | 0 | Aug | 2021 | 0.00027789 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
AGUADILLA | 2021-08-19 16:32 | 2021-08-19 18:53 | 10 | 002:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE A TRANSFORMADOR | M21081900124 | New_Event | Wire Down | Include | Include | Equipment | 141 | 2021-08-19 | 1410 | keep | 0 | Aug | 2021 | 0.00096034 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-08-19 16:41 | 2021-08-19 20:00 | 80 | 003:19 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO ENREDADERAS | A21081900150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2021-08-19 | 15920 | keep | 0 | Aug | 2021 | 0.010843 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-08-19 16:43 | 2021-08-19 16:44 | 2203 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21081900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-19 | 2203 | keep | 0 | Aug | 2021 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
CAGUAS | 2021-08-19 16:46 | 2021-08-20 12:17 | 7 | 019:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR RATA | C21081900094 | New_Event |  |  | Include | Wildlife | 1171 | 2021-08-19 | 8197 | keep | 0 | Aug | 2021 | 0.0055829 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2021-08-19 16:47 | 2021-08-19 18:50 | 15 | 002:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 20 EN TRANSFORMADOR SE REMPLAZO CAJA QUEMADA | A21081800074 | New_Event | Cutout Failure | Include | Include | Equipment | 123 | 2021-08-19 | 1845 | keep | 0 | Aug | 2021 | 0.0012566 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-08-19 17:00 | 2021-08-19 18:45 | 1 | 001:45 | P | DESGANCHE | 2 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERAS | M21081900062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2021-08-19 | 105 | keep | 0 | Aug | 2021 | 7.1515e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-08-19 17:00 | 2021-08-19 19:11 | 80 | 002:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21081900128 | New_Event | Bad Weather | Include | Include | Weather | 131 | 2021-08-19 | 10480 | keep | 0 | Aug | 2021 | 0.0071379 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-08-19 17:14 | 2021-08-19 19:24 | 100 | 002:10 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA. NO SE REPORTA CAUSA | P21081900080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2021-08-19 | 13000 | keep | 0 | Aug | 2021 | 0.0088542 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-08-19 17:52 | 2021-08-19 19:37 | 170 | 001:45 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 80 EN CORTE DE LINEA SE PATRULLO | C21081900103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2021-08-19 | 17850 | keep | 0 | Aug | 2021 | 0.012158 | 0.00011579 | Sustained | FALSE | TRUE | Not_TMED_Event | 170
CANOVANAS | 2021-08-19 18:14 | 2021-08-19 19:34 | 285 | 001:20 | P | TRANSFORMADOR AVERIADO | 1 X 80 Y 1 X 50 EN CORTES DE LINEA BANCO DE TRANSFORMADORES VACANTE AVERIADO | R21081900088 | New_Event | Service Transformer Failure | Include | Include | Equipment | 80 | 2021-08-19 | 22800 | keep | 0 | Aug | 2021 | 0.015529 | 0.00019411 | Sustained | FALSE | TRUE | Not_TMED_Event | 285
BARRANQUITAS | 2021-08-19 18:14 | 2021-08-20 12:46 | 70 | 018:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21081900105 | New_Event | Bad Weather | Include | Include | Weather | 1112 | 2021-08-19 | 77840 | keep | 0 | Aug | 2021 | 0.053016 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BAYAMON | 2021-08-19 18:25 | 2021-08-19 20:14 | 5 | 001:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO SECUNDARIA | S21081900149 | New_Event | Secondary Wire Down | Include | Include | Equipment | 109 | 2021-08-19 | 545 | keep | 0 | Aug | 2021 | 0.0003712 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-08-19 18:39 | 2021-08-20 16:35 | 80 | 021:56 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21081900150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1316 | 2021-08-19 | 105280 | keep | 0 | Aug | 2021 | 0.071706 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-08-19 18:43 | 2021-08-19 20:11 | 50 | 001:28 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21081900151 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 88 | 2021-08-19 | 4400 | keep | 0 | Aug | 2021 | 0.0029968 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-08-19 18:43 | 2021-08-20 11:30 | 10 | 016:47 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHO Y REPARO BAJANTE DE LINEA A CAJA | C21081900111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1007 | 2021-08-19 | 10070 | keep | 0 | Aug | 2021 | 0.0068586 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-08-19 18:46 | 2021-08-19 21:27 | 300 | 002:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | M21081900143 | New_Event | Cutout Failure | Include | Include | Equipment | 161 | 2021-08-19 | 48300 | keep | 0 | Aug | 2021 | 0.032897 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
CAGUAS | 2021-08-19 19:01 | 2021-08-20 08:39 | 60 | 013:38 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | C21081900118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 818 | 2021-08-19 | 49080 | keep | 0 | Aug | 2021 | 0.033428 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-08-19 19:10 | 2021-08-19 19:12 | 40 | 000:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LA LINEA | A21081900152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-08-19 | 80 | keep | 0 | Aug | 2021 | 5.4488e-05 | 2.7244e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-08-19 19:15 | 2021-08-19 21:28 | 15 | 002:13 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO | R21081900090 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 133 | 2021-08-19 | 1995 | keep | 0 | Aug | 2021 | 0.0013588 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
GUAYAMA | 2021-08-19 19:18 | 2021-08-19 21:32 | 50 | 002:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR FUERTES VIENTOS | P21081900091 | New_Event | Bad Weather | Include | Include | Weather | 134 | 2021-08-19 | 6700 | keep | 0 | Aug | 2021 | 0.0045633 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-19 19:26 | 2021-08-19 22:23 | 3511 | 002:57 | T | ESTRUCTURA AVERIADA | SE SECCIONALIZO DOS POSTES PARTIDOS | B21081900000 | New_Event | Defective Pole | Include | Include | Equipment | 177 | 2021-08-19 | 621447 | keep | 0 | Aug | 2021 | 0.42326 | 0.0023913 | Sustained | FALSE | FALSE | Not_TMED_Event | 3511
ARECIBO | 2021-08-19 19:28 | 2021-08-19 22:56 | 1986 | 003:28 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REPARO BAJANTES PRIMARIOS Y SE REMPLAZO 3 CAJAS QUEMADAS EN EL FID 31411464 MARCA ABB DE 100AMP Y 3 X 50 EN CORTE DE LINEA ALIMENTADOR 8013-02 QUE SU CARGA ESTA POR EL INTARRUPTOR 8013-04 | A21081900160 | New_Event | Cutout Failure | Include | Include | Equipment | 208 | 2021-08-19 | 413088 | keep | 0 | Aug | 2021 | 0.28135 | 0.0013527 | Sustained | FALSE | TRUE | Not_TMED_Event | 1986
ARECIBO | 2021-08-19 19:28 | 2021-08-19 22:56 | 24 | 003:28 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REPARO BAJANTES PRIMARIOS Y SE REMPLAZO 3 CAJAS QUEMADAS EN EL FID 31411464 MARCA ABB DE 100AMP Y 3 X 50 EN CORTE DE LINEA ALIMENTADOR 8013-02 LLEVA LA CARGA DEL 8013-02 | A21081900160 | New_Event | Cutout Failure | Include | Include | Equipment | 208 | 2021-08-19 | 4992 | keep | 0 | Aug | 2021 | 0.0034 | 1.6346e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 24
BAYAMON | 2021-08-19 19:28 | 2021-08-20 12:05 | 50 | 016:37 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | B21081900064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 997 | 2021-08-19 | 49850 | keep | 0 | Aug | 2021 | 0.033953 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-19 19:34 | 2021-08-21 21:09 | 12 | 049:35 | P | CABLE SOTERRADO AVERIADO | SE CERRO DE T 4 A T 3 SE CORRIO N/O | S21081900156 | New_Event | UG Cable Fault | Include | Include | Equipment | 2975 | 2021-08-19 | 35700 | keep | 0 | Aug | 2021 | 0.024315 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-08-19 20:14 | 2021-08-19 20:18 | 1746 | 000:04 | T | SOBRECARGA | SE ABRE INTERRUPTOR PARA TRANSFERENCIA DE CARGAS POR ALARMA DE MVA Y WINDING TEMP | P21081900096 | New_Event | Trip Due To Overload | Include | Include | Other | 4 | 2021-08-19 | 6984 | keep | 0 | Aug | 2021 | 0.0047568 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
BAYAMON | 2021-08-19 20:19 | 2021-08-19 21:53 | 100 | 001:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA | S21081900160 | New_Event | Cutout Failure | Include | Include | Equipment | 94 | 2021-08-19 | 9400 | keep | 0 | Aug | 2021 | 0.0064023 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-08-19 20:19 | 2021-08-19 20:20 | 1565 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C21081900125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-19 | 1565 | keep | 0 | Aug | 2021 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
HUMACAO | 2021-08-19 20:32 | 2021-08-20 09:30 | 30 | 012:58 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21081900128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 778 | 2021-08-19 | 23340 | keep | 0 | Aug | 2021 | 0.015897 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-08-19 20:36 | 2021-08-19 23:05 | 200 | 002:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA | S21081900161 | New_Event | Cutout Failure | Include | Include | Equipment | 149 | 2021-08-19 | 29800 | keep | 0 | Aug | 2021 | 0.020297 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
UTUADO | 2021-08-19 20:36 | 2021-08-19 22:24 | 300 | 001:48 | P | ESTRUCTURA AVERIADA | SE SECCIONALIZO POSTE PRIMARIO PARTIDO CON TRANSFORMADOR | A21081900193 | New_Event | Defective Pole | Include | Include | Equipment | 108 | 2021-08-19 | 32400 | keep | 0 | Aug | 2021 | 0.022067 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2021-08-19 20:44 | 2021-08-20 17:52 | 108 | 021:08 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C21081900130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1268 | 2021-08-19 | 136944 | keep | 0 | Aug | 2021 | 0.093272 | 7.3558e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 108
CAGUAS | 2021-08-19 21:06 | 2021-08-20 08:57 | 336 | 011:51 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 Y 2 X 140 EN CORTES DE LINEA SE DESGANCHO Y LEVANTARON CONDUCTOR PRIMARIO | C21081900135 | New_Event | Wire Down | Include | Include | Equipment | 711 | 2021-08-19 | 238896 | keep | 0 | Aug | 2021 | 0.16271 | 0.00022885 | Sustained | FALSE | TRUE | Not_TMED_Event | 336
ARECIBO | 2021-08-19 21:10 | 2021-08-19 22:34 | 150 | 001:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21081900207 | New_Event | Bad Weather | Include | Include | Weather | 84 | 2021-08-19 | 12600 | keep | 0 | Aug | 2021 | 0.0085818 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
UTUADO | 2021-08-19 21:10 | 2021-08-20 13:30 | 60 | 016:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA | A21081900208 | New_Event | Cutout Failure | Include | Include | Equipment | 980 | 2021-08-19 | 58800 | keep | 0 | Aug | 2021 | 0.040048 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-08-19 21:20 | 2021-08-20 14:52 | 15 | 017:32 | P | NO SE REPORTO CAUSA | 1 X 50 EN SU 1 | B21081900187 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1052 | 2021-08-19 | 15780 | keep | 0 | Aug | 2021 | 0.010748 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-08-19 21:56 | 2021-08-20 00:08 | 200 | 002:12 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M21081900156 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 132 | 2021-08-19 | 26400 | keep | 0 | Aug | 2021 | 0.017981 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-08-19 22:01 | 2021-08-19 22:02 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21081900158 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-19 | 108 | keep | 0 | Aug | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
BAYAMON | 2021-08-19 22:23 | 2021-08-19 22:36 | 1053 | 000:13 | P | ESTRUCTURA AVERIADA | SE CERRO N/O CONTRA MISMO ALIMENTADOR 70% EN SERVICIO | B21081900000 | Partial_restoration | Defective Pole | Include | Include | Equipment | 13 | 2021-08-19 | 13689 | keep | 0 | Aug | 2021 | 0.0093235 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-19 22:24 | 2021-08-19 22:25 | 108 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21081900162 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-19 | 108 | keep | 0 | Aug | 2021 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
UTUADO | 2021-08-19 22:24 | 2021-08-21 00:30 | 200 | 026:06 | P | ESTRUCTURA AVERIADA | REMPLAZO DE POSTE CON TRANSFORMADOR POR POSTE 45 METAL | A21081900193 | Partial_restoration | Defective Pole | Include | Include | Equipment | 1566 | 2021-08-19 | 313200 | keep | 0 | Aug | 2021 | 0.21332 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-19 22:36 | 2021-08-19 22:51 | 176 | 000:15 | P | ESTRUCTURA AVERIADA | SE CERRO N/O CON 1710-05 95% EN SERVICIO | B21081900000 | Partial_restoration | Defective Pole | Include | Include | Equipment | 15 | 2021-08-19 | 2640 | keep | 0 | Aug | 2021 | 0.0017981 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-08-19 22:40 | 2021-08-20 10:29 | 75 | 011:49 | P | DESGANCHE | 1 X DE 65 EN CORTE DE LINEA SE DESGANCHO | P21081900103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 709 | 2021-08-19 | 53175 | keep | 0 | Aug | 2021 | 0.036217 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
PONCE | 2021-08-19 22:47 | 2021-08-20 07:35 | 15 | 008:48 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANFORMADOR NO SE REPORTO CAUSA | P21081900104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 528 | 2021-08-19 | 7920 | keep | 0 | Aug | 2021 | 0.0053943 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-08-20 00:01 | 2021-08-20 08:39 | 25 | 008:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A21082000001 | New_Event | Wire Down | Include | Include | Equipment | 518 | 2021-08-20 | 12950 | keep | 0 | Aug | 2021 | 0.0088202 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-08-20 00:13 | 2021-08-20 08:35 | 30 | 008:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN AEREO SE LEVANTO PROVISIONAL AEREAO | B21082000002 | New_Event | Wire Down | Include | Include | Equipment | 502 | 2021-08-20 | 15060 | keep | 0 | Aug | 2021 | 0.010257 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-08-20 01:22 | 2021-08-20 01:42 | 1051 | 000:20 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA RETIRAR ARBOL DE LA LINEA Y SECCIONALIZAR CONDUCTOR PRIMARIO EN EL SUELO | R21082000005 | New_Event | Wire Down | Include | Include | Equipment | 20 | 2021-08-20 | 21020 | keep | 0 | Aug | 2021 | 0.014317 | 0.00071583 | Sustained | FALSE | TRUE | Not_TMED_Event | 1051
SAN JUAN | 2021-08-20 01:42 | 2021-08-20 08:39 | 150 | 006:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR DEL SUELO 100% EN SERVICIO | R21082000018 | Partial_restoration | Wire Down | Include | Include | Equipment | 417 | 2021-08-20 | 62550 | keep | 0 | Aug | 2021 | 0.042603 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-20 02:00 | 2021-08-20 16:04 | 5 | 014:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN CORTE DE LINEA | M21082000001 | New_Event | Bad Weather | Include | Include | Weather | 844 | 2021-08-20 | 4220 | keep | 0 | Aug | 2021 | 0.0028742 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
CANOVANAS | 2021-08-20 02:16 | 2021-08-20 11:25 | 80 | 009:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA CERRO PUENTE | R21082000012 | New_Event | Wire Down | Include | Include | Equipment | 549 | 2021-08-20 | 43920 | keep | 0 | Aug | 2021 | 0.029914 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-08-20 02:23 | 2021-08-20 10:25 | 60 | 008:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A21082000002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 482 | 2021-08-20 | 28920 | keep | 0 | Aug | 2021 | 0.019697 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-08-20 02:25 | 2021-08-20 02:26 | 1835 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21082000002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-20 | 1835 | keep | 0 | Aug | 2021 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
AGUADILLA | 2021-08-20 03:08 | 2021-08-20 11:30 | 80 | 008:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | M21082000002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 502 | 2021-08-20 | 40160 | keep | 0 | Aug | 2021 | 0.027353 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-20 03:24 | 2021-08-20 08:35 | 40 | 005:11 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21082000007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 311 | 2021-08-20 | 12440 | keep | 0 | Aug | 2021 | 0.0084728 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-08-20 03:33 | 2021-08-20 09:55 | 2402 | 006:22 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y SE REALIZO DESGANCHE LLEVA LA CARGA 1720-08 | B21082000008 | New_Event | Cutout Failure | Include | Include | Equipment | 382 | 2021-08-20 | 917564 | keep | 0 | Aug | 2021 | 0.62495 | 0.001636 | Sustained | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2021-08-20 03:33 | 2021-08-20 09:55 | 1 | 006:22 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y SE REALIZO DESGANCHE CARGA POR EL 1709-02 | B21082000008 | New_Event | Cutout Failure | Include | Include | Equipment | 382 | 2021-08-20 | 382 | keep | 0 | Aug | 2021 | 0.00026018 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-08-20 03:53 | 2021-08-20 03:54 | 74 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LA CARGA ESTA POR 1529-11 | S21082000005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-20 | 74 | keep | 0 | Aug | 2021 | 5.0401e-05 | 5.0401e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 74
BAYAMON | 2021-08-20 03:53 | 2021-08-20 03:54 | 1370 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA LA CARGA DEL 1521-02 | S21082000005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-20 | 1370 | keep | 0 | Aug | 2021 | 0.0009331 | 0.0009331 | Momentary | FALSE | FALSE | Not_TMED_Event | 1370
BAYAMON | 2021-08-20 04:56 | 2021-08-20 11:45 | 10 | 006:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE LLEVO CONDUCTOR A AISLADOR Y SE REMPLAZO CAJA PRIMARIA CARGA TRANSFERIDA AL 1709-01 | B21082000013 | New_Event | Wire Down | Include | Include | Equipment | 409 | 2021-08-20 | 4090 | keep | 0 | Aug | 2021 | 0.0027857 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CAGUAS | 2021-08-20 05:23 | 2021-08-20 05:24 | 2900 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO RECIERRA CERRADO POR CONTROL | C21082000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-20 | 2900 | keep | 0 | Aug | 2021 | 0.0019752 | 0.0019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 2900
CAGUAS | 2021-08-20 06:30 | 2021-08-20 06:31 | 540 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21082000009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-20 | 540 | keep | 0 | Aug | 2021 | 0.00036779 | 0.00036779 | Momentary | FALSE | FALSE | Not_TMED_Event | 540
BAYAMON | 2021-08-20 06:37 | 2021-08-20 08:35 | 20 | 001:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO PUENTE PRIMARIO DE LINEA A CAJA EN CORTE DE LINEA | B21082000011 | New_Event | Wire Down | Include | Include | Equipment | 118 | 2021-08-20 | 2360 | keep | 0 | Aug | 2021 | 0.0016074 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-08-20 06:44 | 2021-08-20 06:45 | 4607 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21082000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-20 | 4607 | keep | 0 | Aug | 2021 | 0.0031378 | 0.0031378 | Momentary | FALSE | FALSE | Not_TMED_Event | 4607
BAYAMON | 2021-08-20 06:54 | 2021-08-20 08:39 | 30 | 001:45 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y 1 X 25 EN TRANSFORMADOR SE REALIZO DESGANCHE CARGA TRANSFERIDA AL 1704-04 | B21082000028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2021-08-20 | 3150 | keep | 0 | Aug | 2021 | 0.0021455 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-08-20 07:33 | 2021-08-20 08:39 | 65 | 001:06 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21082000020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2021-08-20 | 4290 | keep | 0 | Aug | 2021 | 0.0029219 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
SAN JUAN | 2021-08-20 07:36 | 2021-08-20 12:22 | 100 | 004:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | R21082000022 | New_Event |  |  | Include | Wildlife | 286 | 2021-08-20 | 28600 | keep | 0 | Aug | 2021 | 0.019479 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-08-20 07:36 | 2021-08-20 11:45 | 150 | 004:09 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | A21082000012 | New_Event | Bad Weather | Include | Include | Weather | 249 | 2021-08-20 | 37350 | keep | 0 | Aug | 2021 | 0.025439 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
MAYAGÃœEZ | 2021-08-20 07:40 | 2021-08-20 21:31 | 7 | 013:51 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | M21082000007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 831 | 2021-08-20 | 5817 | keep | 0 | Aug | 2021 | 0.0039619 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-08-20 07:40 | 2021-08-20 17:19 | 375 | 009:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO BAJANTE EN MACHETE | M21082000007 | New_Event | Wire Down | Include | Include | Equipment | 579 | 2021-08-20 | 217125 | keep | 0 | Aug | 2021 | 0.14788 | 0.00025541 | Sustained | FALSE | FALSE | Not_TMED_Event | 375
AGUADILLA | 2021-08-20 07:40 | 2021-08-20 17:54 | 100 | 010:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | M21082000007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 614 | 2021-08-20 | 61400 | keep | 0 | Aug | 2021 | 0.041819 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-08-20 07:57 | 2021-08-20 17:29 | 28 | 009:32 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA DESGANCHE | C21082000016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 572 | 2021-08-20 | 16016 | keep | 0 | Aug | 2021 | 0.010908 | 1.9071e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 28
SAN JUAN | 2021-08-20 08:09 | 2021-08-20 08:10 | 3957 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | S21082000000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-20 | 3957 | keep | 0 | Aug | 2021 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
UTUADO | 2021-08-20 08:11 | 2021-08-20 18:23 | 15 | 010:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE EN TRANSFORMADOR | A21082000013 | New_Event | Wire Down | Include | Include | Equipment | 612 | 2021-08-20 | 9180 | keep | 0 | Aug | 2021 | 0.0062525 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2021-08-20 08:35 | 2021-08-20 10:24 | 30 | 001:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | R21082000026 | New_Event |  |  | Include | Wildlife | 109 | 2021-08-20 | 3270 | keep | 0 | Aug | 2021 | 0.0022272 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-08-20 08:35 | 2021-08-20 09:55 | 1 | 001:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | A21082000014 | New_Event | Cutout Failure | Include | Include | Equipment | 80 | 2021-08-20 | 80 | keep | 0 | Aug | 2021 | 5.4488e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-08-20 08:39 | 2021-08-20 09:22 | 643 | 000:43 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA | S21082000042 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 43 | 2021-08-20 | 27649 | keep | 0 | Aug | 2021 | 0.018832 | 0.00043794 | Sustained | FALSE | FALSE | Not_TMED_Event | 643
BAYAMON | 2021-08-20 08:41 | 2021-08-20 08:43 | 1356 | 000:02 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR Y SE CERRO POR SCADA | S21082000045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-20 | 2712 | keep | 0 | Aug | 2021 | 0.0018471 | 0.00092357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1356
ARECIBO | 2021-08-20 08:49 | 2021-08-20 10:45 | 50 | 001:56 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN RISER DESCARGAS ELECTRICAS | A21082000018 | New_Event | Bad Weather | Include | Include | Weather | 116 | 2021-08-20 | 5800 | keep | 0 | Aug | 2021 | 0.0039504 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-08-20 08:49 | 2021-08-20 11:45 | 25 | 002:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A21082000001 | New_Event | Wire Down | Include | Include | Equipment | 176 | 2021-08-20 | 4400 | keep | 0 | Aug | 2021 | 0.0029968 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-08-20 08:49 | 2021-08-20 15:13 | 20 | 006:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REEMPLAZO PUENTE PRIMARIO DE LINEA A CAJA EN CORTE DE LINEA | B21082000011 | Partial_restoration | Wire Down | Include | Include | Equipment | 384 | 2021-08-20 | 7680 | keep | 0 | Aug | 2021 | 0.0052308 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-08-20 08:54 | 2021-08-20 17:25 | 50 | 008:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | C202100112 PARA REEMPLAZO DE 3 POSTES PRIMARIOS | C21082000089 | New_Event | Wire Down | Include | Include | Equipment | 511 | 2021-08-20 | 25550 | keep | 0 | Aug | 2021 | 0.017402 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2021-08-20 09:00 | 2021-08-20 14:30 | 2 | 005:30 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO MADERA 35' POR 45-H2 MADERA. FID-20651740 | A21082000021 | New_Event | Defective Pole | Include | Include | Equipment | 330 | 2021-08-20 | 660 | keep | 0 | Aug | 2021 | 0.00044952 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2021-08-20 09:14 | 2021-08-20 18:23 | 336 | 009:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 Y 2 X 140 EN CORTES DE LINEA SE DESGANCHO Y LEVANTARON CONDUCTOR PRIMARIO | C21081900135 | Partial_restoration | Wire Down | Include | Include | Equipment | 549 | 2021-08-20 | 184464 | keep | 0 | Aug | 2021 | 0.12564 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-08-20 09:16 | 2021-08-20 11:15 | 1 | 001:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 20 EN TRANSFORMADOR SE REPARO BAJANTE ZAFADO | A21082000022 | New_Event | Wire Down | Include | Include | Equipment | 119 | 2021-08-20 | 119 | keep | 0 | Aug | 2021 | 8.105e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-08-20 09:19 | 2021-08-20 11:40 | 8 | 002:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZARON CONECTORES EN LA SECUNDARIA | A21082000024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 141 | 2021-08-20 | 1128 | keep | 0 | Aug | 2021 | 0.00076828 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-08-20 09:20 | 2021-08-20 17:20 | 25 | 008:00 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE PARTIDO | M21082000045 | New_Event | Defective Pole | Include | Include | Equipment | 480 | 2021-08-20 | 12000 | keep | 0 | Aug | 2021 | 0.0081731 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-08-20 09:21 | 2021-08-20 13:15 | 20 | 003:54 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21082000132 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 234 | 2021-08-20 | 4680 | keep | 0 | Aug | 2021 | 0.0031875 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-08-20 09:21 | 2021-08-20 11:30 | 30 | 002:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN AEREO SE LEVANTO PROVISIONAL AEREO | B21082000002 | Partial_restoration | Wire Down | Include | Include | Equipment | 129 | 2021-08-20 | 3870 | keep | 0 | Aug | 2021 | 0.0026358 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-20 09:21 | 2021-08-20 17:38 | 40 | 008:17 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21082000007 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 497 | 2021-08-20 | 19880 | keep | 0 | Aug | 2021 | 0.01354 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
VEGA BAJA | 2021-08-20 09:21 | 2021-08-20 09:30 | 15 | 000:09 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21082000107 | New_Event | Secondary Wire Down | Include | Include | Equipment | 9 | 2021-08-20 | 135 | keep | 0 | Aug | 2021 | 9.1948e-05 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-08-20 09:22 | 2021-08-20 18:04 | 30 | 008:42 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y 1 X 25 EN TRANSFORMADOR SE REALIZO DESGANCHE CARGA TRANSFERIDA AL 1704-04 | B21082000028 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 522 | 2021-08-20 | 15660 | keep | 0 | Aug | 2021 | 0.010666 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
VEGA BAJA | 2021-08-20 09:30 | 2021-08-20 11:13 | 290 | 001:43 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE CERRO INTERRUPTOR ABRIENDO MACHETES EN CARRETERA 155 EN PUENTE DE EXPRESO POR GLOBO METALICO Y CONDUCTOR FUERA DE AISLADOR | B21082000107 | New_Event |  |  | Include | Wildlife | 103 | 2021-08-20 | 29870 | keep | 0 | Aug | 2021 | 0.020344 | 0.00019752 | Sustained | FALSE | FALSE | Not_TMED_Event | 290
SAN JUAN | 2021-08-20 09:46 | 2021-08-20 10:36 | 65 | 000:50 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21082000020 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 50 | 2021-08-20 | 3250 | keep | 0 | Aug | 2021 | 0.0022136 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-08-20 09:46 | 2021-08-20 13:38 | 150 | 003:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR DEL SUELO 100% EN SERVICIO | R21082000018 | Partial_restoration | Wire Down | Include | Include | Equipment | 232 | 2021-08-20 | 34800 | keep | 0 | Aug | 2021 | 0.023702 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-20 09:50 | 2021-08-20 13:27 | 8 | 003:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21082000000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 217 | 2021-08-20 | 1736 | keep | 0 | Aug | 2021 | 0.0011824 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-08-20 10:11 | 2021-08-20 21:44 | 30 | 011:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEAPOR DESCARGAS ELECTRICAS | M21082000080 | New_Event | Bad Weather | Include | Include | Weather | 693 | 2021-08-20 | 20790 | keep | 0 | Aug | 2021 | 0.01416 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
AGUADILLA | 2021-08-20 10:15 | 2021-08-20 22:53 | 80 | 012:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21082000083 | New_Event | Bad Weather | Include | Include | Weather | 758 | 2021-08-20 | 60640 | keep | 0 | Aug | 2021 | 0.041302 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-08-20 10:17 | 2021-08-20 19:00 | 100 | 008:43 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | M21082000085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 523 | 2021-08-20 | 52300 | keep | 0 | Aug | 2021 | 0.035621 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-08-20 10:26 | 2021-08-20 12:33 | 50 | 002:07 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO CAUSA | C21082000078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 127 | 2021-08-20 | 6350 | keep | 0 | Aug | 2021 | 0.004325 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-08-20 10:37 | 2021-08-20 17:12 | 70 | 006:35 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21082000109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 395 | 2021-08-20 | 27650 | keep | 0 | Aug | 2021 | 0.018832 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
CAGUAS | 2021-08-20 10:41 | 2021-08-20 13:53 | 13 | 003:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN CORTE DE LINEA CRUCE POR AVE | C21082000080 | New_Event |  |  | Include | Wildlife | 192 | 2021-08-20 | 2496 | keep | 0 | Aug | 2021 | 0.0017 | 8.8542e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 13
BARRANQUITAS | 2021-08-20 10:41 | 2021-08-20 15:30 | 58 | 004:49 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | C21082000081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 289 | 2021-08-20 | 16762 | keep | 0 | Aug | 2021 | 0.011417 | 3.9504e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 58
MAYAGÃœEZ | 2021-08-20 10:45 | 2021-08-21 09:06 | 1 | 022:21 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21082000096 | New_Event | Bad Weather | Include | Include | Weather | 1341 | 2021-08-20 | 1341 | keep | 0 | Aug | 2021 | 0.00091335 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CANOVANAS | 2021-08-20 10:54 | 2021-08-20 16:38 | 100 | 005:44 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21082000084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 344 | 2021-08-20 | 34400 | keep | 0 | Aug | 2021 | 0.02343 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-08-20 11:01 | 2021-08-20 13:40 | 50 | 002:39 | P | DESGANCHE | 1 X 100 AMP EN CORTE DE LINEA DESGANCHE | P21082000025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2021-08-20 | 7950 | keep | 0 | Aug | 2021 | 0.0054147 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-08-20 11:01 | 2021-08-20 11:21 | 100 | 000:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 Y 1 X 65 EN DIFERENTES CORTE DE LINEAS AVE CRUZO LINEAS | P21082000024 | New_Event |  |  | Include | Wildlife | 20 | 2021-08-20 | 2000 | keep | 0 | Aug | 2021 | 0.0013622 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-08-20 11:12 | 2021-08-20 15:24 | 2 | 004:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA REEMPLAZAR 3 BARRAS EN PEDESTAL | C21082000087 | New_Event | Secondary Wire Down | Include | Include | Equipment | 252 | 2021-08-20 | 504 | keep | 0 | Aug | 2021 | 0.00034327 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2021-08-20 11:13 | 2021-08-20 13:14 | 87 | 002:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE CERRO MACHETES EN CARRETERA 155 EN PUENTE EXPRESO SE RETIRO GLOBO METALICO Y SE LLEVO CONDUCTOR A AISLADOR | B21082000107 | New_Event |  |  | Include | Wildlife | 121 | 2021-08-20 | 10527 | keep | 0 | Aug | 2021 | 0.0071699 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
VEGA BAJA | 2021-08-20 11:13 | 2021-08-20 14:21 | 15 | 003:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21082000107 | New_Event | Secondary Wire Down | Include | Include | Equipment | 188 | 2021-08-20 | 2820 | keep | 0 | Aug | 2021 | 0.0019207 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-08-20 11:19 | 2021-08-20 12:30 | 20 | 001:11 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA REPARAR SECUNDARIA | C21081900044 | New_Event | Secondary Wire Down | Include | Include | Equipment | 71 | 2021-08-20 | 1420 | keep | 0 | Aug | 2021 | 0.00096716 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-08-20 11:39 | 2021-08-20 17:07 | 241 | 005:28 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | C21082000093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 328 | 2021-08-20 | 79048 | keep | 0 | Aug | 2021 | 0.053839 | 0.00016414 | Sustained | FALSE | TRUE | Not_TMED_Event | 241
CAGUAS | 2021-08-20 11:39 | 2021-08-20 16:02 | 49 | 004:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | C21082000092 | New_Event | Cutout Failure | Include | Include | Equipment | 263 | 2021-08-20 | 12887 | keep | 0 | Aug | 2021 | 0.0087773 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
CANOVANAS | 2021-08-20 11:48 | 2021-08-20 14:18 | 5 | 002:30 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R21082000075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 150 | 2021-08-20 | 750 | keep | 0 | Aug | 2021 | 0.00051082 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-08-20 11:54 | 2021-08-20 11:55 | 1261 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21082000097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-20 | 1261 | keep | 0 | Aug | 2021 | 0.00085886 | 0.00085886 | Momentary | FALSE | FALSE | Not_TMED_Event | 1261
BAYAMON | 2021-08-20 12:01 | 2021-08-20 22:00 | 30 | 009:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA PRIMARIA | B21082000151 | New_Event | Wire Down | Include | Include | Equipment | 599 | 2021-08-20 | 17970 | keep | 0 | Aug | 2021 | 0.012239 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-08-20 12:02 | 2021-08-20 12:30 | 3957 | 000:28 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR Y SE CERRO PUENTE ABIERTO | S21082000130 | New_Event | Wire Down | Include | Include | Equipment | 28 | 2021-08-20 | 110796 | keep | 0 | Aug | 2021 | 0.075463 | 0.0026951 | Sustained | FALSE | FALSE | Not_TMED_Event | 3957
MAYAGÃœEZ | 2021-08-20 12:05 | 2021-08-20 12:06 | 2073 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13500 | M21082000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-20 | 2073 | keep | 0 | Aug | 2021 | 0.0014119 | 0.0014119 | Momentary | FALSE | TRUE | Not_TMED_Event | 2073
MAYAGÃœEZ | 2021-08-20 12:05 | 2021-08-20 12:06 | 637 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13500 | M21082000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-20 | 637 | keep | 0 | Aug | 2021 | 0.00043386 | 0.00043386 | Momentary | FALSE | TRUE | Not_TMED_Event | 637
MAYAGÃœEZ | 2021-08-20 12:05 | 2021-08-20 12:06 | 1491 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13500 | M21082000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-20 | 1491 | keep | 0 | Aug | 2021 | 0.0010155 | 0.0010155 | Momentary | FALSE | TRUE | Not_TMED_Event | 1491
MAYAGÃœEZ | 2021-08-20 12:05 | 2021-08-20 12:06 | 4892 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13500 | M21082000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-20 | 4892 | keep | 0 | Aug | 2021 | 0.0033319 | 0.0033319 | Momentary | FALSE | TRUE | Not_TMED_Event | 4892
MAYAGÃœEZ | 2021-08-20 12:05 | 2021-08-20 12:06 | 160 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13500 | M21082000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-20 | 160 | keep | 0 | Aug | 2021 | 0.00010898 | 0.00010898 | Momentary | FALSE | TRUE | Not_TMED_Event | 160
SAN JUAN | 2021-08-20 12:08 | 2021-08-20 17:52 | 70 | 005:44 | P | OTRAS CAUSAS | 2 X 80 EN CORTES DE LINEA PROBLEMA DEL CLIENTE | R21082000076 | New_Event | Other Causes | Include | Include | Other | 344 | 2021-08-20 | 24080 | keep | 0 | Aug | 2021 | 0.016401 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
UTUADO | 2021-08-20 12:16 | 2021-08-20 17:00 | 20 | 004:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21082000052 | New_Event | Bad Weather | Include | Include | Weather | 284 | 2021-08-20 | 5680 | keep | 0 | Aug | 2021 | 0.0038686 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-08-20 12:16 | 2021-08-20 16:02 | 15 | 003:46 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | S21082000154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2021-08-20 | 3390 | keep | 0 | Aug | 2021 | 0.0023089 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
HUMACAO | 2021-08-20 12:19 | 2021-08-20 15:10 | 4 | 002:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR PARA REEMPLAZO DE 30 PIES DE SECUNDARIA | C21081900097 | New_Event | Secondary Wire Down | Include | Include | Equipment | 171 | 2021-08-20 | 684 | keep | 0 | Aug | 2021 | 0.00046587 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2021-08-20 12:20 | 2021-08-20 16:00 | 1 | 003:40 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | M21082000121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2021-08-20 | 220 | keep | 0 | Aug | 2021 | 0.00014984 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-08-20 12:26 | 2021-08-21 10:19 | 1 | 021:53 | P | NO SE REPORTO CAUSA | 3 X 100 EN CORTE DE LINEA | S21082000145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1313 | 2021-08-20 | 1313 | keep | 0 | Aug | 2021 | 0.00089428 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-08-20 12:31 | 2021-08-20 16:14 | 3147 | 003:43 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR POR LINEA PARTIDA | M21082000127 | New_Event | Wire Down | Include | Include | Equipment | 223 | 2021-08-20 | 701781 | keep | 0 | Aug | 2021 | 0.47798 | 0.0021434 | Sustained | FALSE | TRUE | Not_TMED_Event | 3147
HUMACAO | 2021-08-20 12:35 | 2021-08-20 15:56 | 11 | 003:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | C21082000102 | New_Event |  |  | Include | Wildlife | 201 | 2021-08-20 | 2211 | keep | 0 | Aug | 2021 | 0.0015059 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
FAJARDO | 2021-08-20 12:39 | 2021-08-20 18:52 | 4 | 006:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SULFATADA | R21082000103 | New_Event | Secondary Wire Down | Include | Include | Equipment | 373 | 2021-08-20 | 1492 | keep | 0 | Aug | 2021 | 0.0010162 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
VEGA BAJA | 2021-08-20 12:49 | 2021-08-20 16:36 | 40 | 003:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA SE RETIRO AVE CRUZANDO LINEAS | B21082000168 | New_Event |  |  | Include | Wildlife | 227 | 2021-08-20 | 9080 | keep | 0 | Aug | 2021 | 0.0061843 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-08-20 12:49 | 2021-08-20 18:33 | 70 | 005:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO EN TRONCAL | B21082000231 | New_Event | Wire Down | Include | Include | Equipment | 344 | 2021-08-20 | 24080 | keep | 0 | Aug | 2021 | 0.016401 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2021-08-20 12:53 | 2021-08-21 14:15 | 10 | 025:22 | P | NO SE REPORTO CAUSA | 1 X 3O EN CORTE DE LINEA | B21082000170 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1522 | 2021-08-20 | 15220 | keep | 0 | Aug | 2021 | 0.010366 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
UTUADO | 2021-08-20 13:01 | 2021-08-21 10:55 | 5 | 021:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR MAL TIEMPO | A21082000058 | New_Event | Bad Weather | Include | Include | Weather | 1314 | 2021-08-20 | 6570 | keep | 0 | Aug | 2021 | 0.0044748 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2021-08-20 13:07 | 2021-08-21 11:21 | 5 | 022:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA DESGANCHAR Y REPARAR SECUNDARIA | C21082000113 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1334 | 2021-08-20 | 6670 | keep | 0 | Aug | 2021 | 0.0045429 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-08-20 13:08 | 2021-08-20 15:11 | 3 | 002:03 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR 25KVA POR 50KVA | S21082000151 | New_Event | Service Transformer Failure | Include | Include | Equipment | 123 | 2021-08-20 | 369 | keep | 0 | Aug | 2021 | 0.00025132 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2021-08-20 13:12 | 2021-08-20 16:23 | 50 | 003:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA POR CAJA PRIMARIA QUEMADA | P21082000039 | New_Event | Cutout Failure | Include | Include | Equipment | 191 | 2021-08-20 | 9550 | keep | 0 | Aug | 2021 | 0.0065045 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-08-20 13:14 | 2021-08-20 18:49 | 4 | 005:35 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE REPARO PEDESTAL | R21082000085 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 335 | 2021-08-20 | 1340 | keep | 0 | Aug | 2021 | 0.00091267 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2021-08-20 13:17 | 2021-08-20 18:44 | 60 | 005:27 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | B21082000060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 327 | 2021-08-20 | 19620 | keep | 0 | Aug | 2021 | 0.013363 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-08-20 13:29 | 2021-08-20 15:52 | 60 | 002:23 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA Y 1 X 25 EN TRANSFORMADOR | B21082000179 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 143 | 2021-08-20 | 8580 | keep | 0 | Aug | 2021 | 0.0058438 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
AGUADILLA | 2021-08-20 13:30 | 2021-08-20 16:20 | 50 | 002:50 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | M21082000142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2021-08-20 | 8500 | keep | 0 | Aug | 2021 | 0.0057893 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-08-20 13:38 | 2021-08-20 13:49 | 1051 | 000:11 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA REEMPLAZAR MACHETE QUEMADO | R21082000087 | New_Event | Switch Failure | Include | Include | Equipment | 11 | 2021-08-20 | 11561 | keep | 0 | Aug | 2021 | 0.0078741 | 0.00071583 | Sustained | FALSE | FALSE | Not_TMED_Event | 1051
MAYAGÃœEZ | 2021-08-20 13:41 | 2021-08-20 17:41 | 2 | 004:00 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 15KVA CON DERRAME DE ACEITE | M21082000000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 240 | 2021-08-20 | 480 | keep | 0 | Aug | 2021 | 0.00032693 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2021-08-20 13:49 | 2021-08-20 13:50 | 1420 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE 1530-06 LLEVA 1526-02 | S21082000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-20 | 1420 | keep | 0 | Aug | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-08-20 13:49 | 2021-08-20 13:50 | 437 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 1526-02 | S21082000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-20 | 437 | keep | 0 | Aug | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
MAYAGÃœEZ | 2021-08-20 13:49 | 2021-08-20 17:40 | 35 | 003:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA | M21082000145 | New_Event | Bad Weather | Include | Include | Weather | 231 | 2021-08-20 | 8085 | keep | 0 | Aug | 2021 | 0.0055067 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
CAGUAS | 2021-08-20 13:52 | 2021-08-20 16:35 | 60 | 002:43 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | C21081900118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2021-08-20 | 9780 | keep | 0 | Aug | 2021 | 0.0066611 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
UTUADO | 2021-08-20 14:00 | 2021-08-20 15:30 | 80 | 001:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | A21082000065 | New_Event | Bad Weather | Include | Include | Weather | 90 | 2021-08-20 | 7200 | keep | 0 | Aug | 2021 | 0.0049039 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
GUAYAMA | 2021-08-20 14:03 | 2021-08-21 17:42 | 40 | 027:39 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO METAL 45 PIES Y SE CERRO CORTE DE LINEA | P21082000043 | New_Event | Defective Pole | Include | Include | Equipment | 1659 | 2021-08-20 | 66360 | keep | 0 | Aug | 2021 | 0.045197 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-08-20 14:05 | 2021-08-20 14:07 | 1420 | 000:02 | T | NO SE REPORTO CAUSA | RECERRO 1530-6 LLEVA 1526-2 | S21082000000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-20 | 2840 | keep | 0 | Aug | 2021 | 0.0019343 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-08-20 14:05 | 2021-08-20 14:07 | 437 | 000:02 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1526-2 | S21082000000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-20 | 874 | keep | 0 | Aug | 2021 | 0.00059528 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
PONCE | 2021-08-20 14:07 | 2021-08-20 15:02 | 778 | 000:55 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO INTERRUPTOR 5011-05 POR ACCIDENTE DE CAMION PARTIENDO 3 POSTES. SE SECCIONALIZO AVERIA. LA CARGA ESTA POR EL 5011-05 | P21082000044 | New_Event |  |  | Include | Wildlife | 55 | 2021-08-20 | 42790 | keep | 0 | Aug | 2021 | 0.029144 | 0.00052989 | Sustained | FALSE | FALSE | Not_TMED_Event | 778
PONCE | 2021-08-20 14:07 | 2021-08-20 15:02 | 1746 | 000:55 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO INTERRUPTOR 5011-05 POR ACCIDENTE DE CAMION PARTIENDO 3 POSTES. SE SECCIONALIZO AVERIA. LA CARGA ESTA POR 5011-05 | P21082000044 | New_Event |  |  | Include | Wildlife | 55 | 2021-08-20 | 96030 | keep | 0 | Aug | 2021 | 0.065406 | 0.0011892 | Sustained | FALSE | FALSE | Not_TMED_Event | 1746
PONCE | 2021-08-20 14:07 | 2021-08-20 15:02 | 113 | 000:55 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO INTERRUPTOR POR ACCIDENTE DE CAMION PARTIENDO 3 POSTES. SE SECCIONALIZO AVERIA. LLEVA LA CARGA DEL 5004-08 Y 5004-09 | P21082000044 | New_Event |  |  | Include | Wildlife | 55 | 2021-08-20 | 6215 | keep | 0 | Aug | 2021 | 0.004233 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
ARECIBO | 2021-08-20 14:07 | 2021-08-21 09:14 | 20 | 019:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | A21082000066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1147 | 2021-08-20 | 22940 | keep | 0 | Aug | 2021 | 0.015624 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
VEGA BAJA | 2021-08-20 14:25 | 2021-08-20 15:01 | 20 | 000:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | B21082000185 | New_Event | Secondary Wire Down | Include | Include | Equipment | 36 | 2021-08-20 | 720 | keep | 0 | Aug | 2021 | 0.00049039 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-08-20 14:27 | 2021-08-20 17:48 | 20 | 003:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE CARGA TRANSFERIDA AL 1709-01 | B21082000187 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2021-08-20 | 4020 | keep | 0 | Aug | 2021 | 0.002738 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-08-20 14:41 | 2021-08-20 16:31 | 60 | 001:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA | M21082000149 | New_Event | Bad Weather | Include | Include | Weather | 110 | 2021-08-20 | 6600 | keep | 0 | Aug | 2021 | 0.0044952 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
YAUCO | 2021-08-20 14:54 | 2021-08-20 17:11 | 100 | 002:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR FUERTES VIENTOS | P21082000057 | New_Event | Bad Weather | Include | Include | Weather | 137 | 2021-08-20 | 13700 | keep | 0 | Aug | 2021 | 0.009331 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-08-20 15:06 | 2021-08-21 16:30 | 8 | 025:24 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | M21082000157 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1524 | 2021-08-20 | 12192 | keep | 0 | Aug | 2021 | 0.0083039 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-08-20 15:10 | 2021-08-20 20:08 | 3 | 004:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE | M21082000159 | New_Event | Wire Down | Include | Include | Equipment | 298 | 2021-08-20 | 894 | keep | 0 | Aug | 2021 | 0.0006089 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2021-08-20 15:11 | 2021-08-20 18:45 | 12 | 003:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR Y SE REPARO SECUNDARIA | S21082000173 | New_Event | Secondary Wire Down | Include | Include | Equipment | 214 | 2021-08-20 | 2568 | keep | 0 | Aug | 2021 | 0.0017491 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2021-08-20 15:12 | 2021-08-20 16:20 | 5 | 001:08 | P | SECUNDARIA/ESTRUCTURA AVERIADA | 1 X 10 EN TRANSFORMADOR SE AJUSTO BUSHING SECUNDARIO | C21082000136 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 68 | 2021-08-20 | 340 | keep | 0 | Aug | 2021 | 0.00023157 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-08-20 15:14 | 2021-08-20 18:25 | 50 | 003:11 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21082000174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 191 | 2021-08-20 | 9550 | keep | 0 | Aug | 2021 | 0.0065045 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-08-20 15:20 | 2021-08-20 15:55 | 50 | 000:35 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21082000177 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 35 | 2021-08-20 | 1750 | keep | 0 | Aug | 2021 | 0.0011919 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BARRANQUITAS | 2021-08-20 15:33 | 2021-08-20 18:58 | 70 | 003:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO DISCO PARTIDO | C21082000110 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 205 | 2021-08-20 | 14350 | keep | 0 | Aug | 2021 | 0.0097737 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
GUAYAMA | 2021-08-20 15:42 | 2021-08-20 17:49 | 75 | 002:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE A CAJA DE CORTE DE LINEA | P21082000067 | New_Event | Wire Down | Include | Include | Equipment | 127 | 2021-08-20 | 9525 | keep | 0 | Aug | 2021 | 0.0064874 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
AGUADILLA | 2021-08-20 15:43 | 2021-08-20 21:47 | 200 | 006:04 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21082000166 | New_Event | Bad Weather | Include | Include | Weather | 364 | 2021-08-20 | 72800 | keep | 0 | Aug | 2021 | 0.049584 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
PONCE | 2021-08-20 15:46 | 2021-08-20 15:47 | 595 | 000:01 | T | DESGANCHE | RECIERRE | P21082000068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-20 | 595 | keep | 0 | Aug | 2021 | 0.00040525 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
PONCE | 2021-08-20 15:47 | 2021-08-21 11:45 | 100 | 019:58 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA CRUCE DE FASES POR RAMAS | P21082000079 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1198 | 2021-08-20 | 119800 | keep | 0 | Aug | 2021 | 0.081595 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-08-20 16:00 | 2021-08-21 19:13 | 12 | 027:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE CAMBIO BAJANTE SECUNDARIO Y SE RELOCALIZO SECUNDARIA | B21082000184 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1633 | 2021-08-20 | 19596 | keep | 0 | Aug | 2021 | 0.013347 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-08-20 16:01 | 2021-08-20 16:50 | 778 | 000:49 | T | NO SE REPORTO CAUSA | SE ABRIO AMARRE DEL 5011-05 CON EL 5004-08 EN MH-7A. Y SE PUSO EN SERVICIO 5004-08 Y 5004-09 POR BARRA DE INSPECCION | P21082000070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 49 | 2021-08-20 | 38122 | keep | 0 | Aug | 2021 | 0.025965 | 0.00052989 | Sustained | FALSE | FALSE | Not_TMED_Event | 778
PONCE | 2021-08-20 16:01 | 2021-08-21 00:55 | 25 | 008:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | CAMION PARTE TRES POSTES PRIMARIOS SE TRANSFIERE LINEA SECUNDARIA A TRANSFORMADOR CERCANO | P21082000140 | New_Event |  |  | Include | Wildlife | 534 | 2021-08-20 | 13350 | keep | 0 | Aug | 2021 | 0.0090926 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
PONCE | 2021-08-20 16:01 | 2021-08-20 16:50 | 1746 | 000:49 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO AMARRE DEL 5011-05 CON EL 5004-08 EN MH-7A. Y SE PUSO EN SERVICIO 5004-08 Y 5004-09 POR BARRA DE INSPECCION | P21082000070 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 49 | 2021-08-20 | 85554 | keep | 0 | Aug | 2021 | 0.05827 | 0.0011892 | Sustained | FALSE | FALSE | Not_TMED_Event | 1746
PONCE | 2021-08-20 16:01 | 2021-08-20 18:59 | 113 | 002:58 | T | CABLE SOTERRADO AVERIADO | AVERIA SOTERRADA DEL MH-6A AL MH-7A. SE ABRIO AMBOS EXTREMOS Y SE PUSO EL INTERRUPTOR EN SERVICIO | P21082000070 | New_Event | UG Cable Fault | Include | Include | Equipment | 178 | 2021-08-20 | 20114 | keep | 0 | Aug | 2021 | 0.0137 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
BAYAMON | 2021-08-20 16:23 | 2021-08-20 19:01 | 94 | 002:38 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO INTERRUPTOR ABRIENDO MACHETES EN CALLE SONIA HERMANAS DAVILA 1705 05 POR CONDUCTOR ENCIMA DE CRUCETA EN ALIMENTADOR 1705 05 | B2108200212 | New_Event | Wire Down | Include | Include | Equipment | 158 | 2021-08-20 | 14852 | keep | 0 | Aug | 2021 | 0.010116 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
BAYAMON | 2021-08-20 16:23 | 2021-08-20 19:01 | 67 | 002:38 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO INTERRUPTOR ABRIENDO MACHETES EN CALLE SONIA HERMANAS DAVILA 1705 05 POR CONDUCTOR ENCIMA DE CRUCETA EN ALIMENTADOR 1705 05 | B2108200212 | New_Event | Wire Down | Include | Include | Equipment | 158 | 2021-08-20 | 10586 | keep | 0 | Aug | 2021 | 0.0072101 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2021-08-20 16:23 | 2021-08-20 19:01 | 100 | 002:38 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO MACHETES EN CALLE SONIA HERMANAS DAVILA SE LLEVO CONDUCTOR A AISLADOR | S2108200212 | New_Event | Wire Down | Include | Include | Equipment | 158 | 2021-08-20 | 15800 | keep | 0 | Aug | 2021 | 0.010761 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-08-20 16:24 | 2021-08-20 19:05 | 20 | 002:41 | P | ERROR HUMANO | 2 X 25 EN CORTE DE LINEA MAQUINA IMPACTO POSTE | M21082000175 | New_Event | Human Error | Include | Include | Other | 161 | 2021-08-20 | 3220 | keep | 0 | Aug | 2021 | 0.0021931 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
GUAYAMA | 2021-08-20 16:50 | 2021-08-20 22:05 | 150 | 005:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABREN MACHETES PARA CERRAR PUENTE PRIMARIO | P21082000085 | New_Event | Wire Down | Include | Include | Equipment | 315 | 2021-08-20 | 47250 | keep | 0 | Aug | 2021 | 0.032182 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2021-08-20 17:13 | 2021-08-21 10:56 | 20 | 017:43 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21082000226 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1063 | 2021-08-20 | 21260 | keep | 0 | Aug | 2021 | 0.01448 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-08-20 17:24 | 2021-08-21 11:12 | 50 | 017:48 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21082000146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1068 | 2021-08-20 | 53400 | keep | 0 | Aug | 2021 | 0.03637 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-08-20 17:33 | 2021-08-20 18:50 | 100 | 001:17 | P | DESGANCHE | SE ABRIO TOTAL PARA PODER REALIZAR DESGANCHE | S21082000187 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2021-08-20 | 7700 | keep | 0 | Aug | 2021 | 0.0052444 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-08-20 17:35 | 2021-08-20 21:14 | 7 | 003:39 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21082000189 | New_Event | Bad Weather | Include | Include | Weather | 219 | 2021-08-20 | 1533 | keep | 0 | Aug | 2021 | 0.0010441 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-08-20 17:55 | 2021-08-21 00:08 | 25 | 006:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO CONDUCTOR | B21082000236 | New_Event | Wire Down | Include | Include | Equipment | 373 | 2021-08-20 | 9325 | keep | 0 | Aug | 2021 | 0.0063512 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-08-20 18:00 | 2021-08-20 19:56 | 45 | 001:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | M21082000194 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2021-08-20 | 5220 | keep | 0 | Aug | 2021 | 0.0035553 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
PONCE | 2021-08-20 18:15 | 2021-08-20 19:17 | 1 | 001:02 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | EMPALME SOTERRADO EM MH-7 AVERIADA SE CERRO DE MH-3 AL MH-5 | P21082200022 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 62 | 2021-08-20 | 62 | keep | 0 | Aug | 2021 | 4.2228e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-08-20 18:22 | 2021-08-21 08:31 | 1 | 014:09 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER NO CAUSA | C21082000153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 849 | 2021-08-20 | 849 | keep | 0 | Aug | 2021 | 0.00057825 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-08-20 18:50 | 2021-08-20 19:28 | 250 | 000:38 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE ABRIO TOTAL PARA PODER REALIZAR DESGANCHE | S21082000187 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 38 | 2021-08-20 | 9500 | keep | 0 | Aug | 2021 | 0.0064704 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
VEGA BAJA | 2021-08-20 18:52 | 2021-08-20 20:18 | 12 | 001:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | B21082000190 | New_Event | Secondary Wire Down | Include | Include | Equipment | 86 | 2021-08-20 | 1032 | keep | 0 | Aug | 2021 | 0.00070289 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
CAGUAS | 2021-08-20 18:57 | 2021-08-20 18:58 | 1271 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO INTERRUPTOR | C21082000155 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-20 | 1271 | keep | 0 | Aug | 2021 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
CAGUAS | 2021-08-20 18:58 | 2021-08-20 21:55 | 1271 | 002:57 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO INTERRUPTOR SE DEJO FUERA SE SECCIONALIZO ALAMBRE PRIMARIO EN EL SUELO | C21082000156 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 177 | 2021-08-20 | 224967 | keep | 0 | Aug | 2021 | 0.15322 | 0.00086567 | Sustained | FALSE | FALSE | Not_TMED_Event | 1271
PONCE | 2021-08-20 19:17 | 2021-08-20 19:18 | 778 | 000:01 | T | CABLE SOTERRADO AVERIADO | AVERIA SOTERRADA EN MH 7A. TODO ESTA EN SERVICIO | P21082000134 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2021-08-20 | 778 | keep | 0 | Aug | 2021 | 0.00052989 | 0.00052989 | Momentary | FALSE | FALSE | Not_TMED_Event | 778
PONCE | 2021-08-20 19:18 | 2021-08-20 21:43 | 300 | 002:25 | P | CABLE SOTERRADO AVERIADO | AVERIA SOTERRADA EN MH-7A HACIA MH-6A | P21092000134 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 145 | 2021-08-20 | 43500 | keep | 0 | Aug | 2021 | 0.029628 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
PONCE | 2021-08-20 19:18 | 2021-08-22 17:27 | 1 | 046:09 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | EMPALME SOTERRADO EM MH-7 AVERIADA SE CERRO DE MH-3 AL MH-5 | P21082200022 | Partial_restoration | UG - Broken Splice / Terminal | Include | Include | Equipment | 2769 | 2021-08-20 | 2769 | keep | 0 | Aug | 2021 | 0.001886 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-08-20 19:59 | 2021-08-21 21:54 | 170 | 025:55 | P | AISLADOR ROTO, PARTIDO O SAFADO | 3 X 40 EN CORTES DE LINEA SE REEMPLAZARON DISCOS ROTOS | C21082000162 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1555 | 2021-08-20 | 264350 | keep | 0 | Aug | 2021 | 0.18005 | 0.00011579 | Sustained | FALSE | TRUE | Not_TMED_Event | 170
ARECIBO | 2021-08-20 20:01 | 2021-08-21 09:35 | 1 | 013:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO TREE WIRE A CAJA PRIMARIA DE TRANSFORMADOR | A21082000094 | New_Event | Wire Down | Include | Include | Equipment | 814 | 2021-08-20 | 814 | keep | 0 | Aug | 2021 | 0.00055441 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-08-20 20:05 | 2021-08-21 09:55 | 40 | 013:50 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21082000261 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 830 | 2021-08-20 | 33200 | keep | 0 | Aug | 2021 | 0.022612 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-08-20 20:05 | 2021-08-21 17:28 | 15 | 021:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21082000260 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1283 | 2021-08-20 | 19245 | keep | 0 | Aug | 2021 | 0.013108 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CAGUAS | 2021-08-20 20:08 | 2021-08-20 20:09 | 4634 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECERRO INTERRUPTOR PUENTE ABIERTO EN LA SALIDA DEL ALIMENTADOR | C21082000180 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-20 | 4634 | keep | 0 | Aug | 2021 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
CAGUAS | 2021-08-20 20:09 | 2021-08-20 22:56 | 1544 | 002:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | PUENTE ABIERTO EN SALIDA DE ALIMENTADOR | C21082000180 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 167 | 2021-08-20 | 257848 | keep | 0 | Aug | 2021 | 0.17562 | 0.0010516 | Sustained | FALSE | FALSE | Not_TMED_Event | 1544
CAGUAS | 2021-08-20 20:19 | 2021-08-21 12:27 | 200 | 016:08 | P | DESGANCHE | 1 X 50 Y 1 X 65 EN CORTES DE LINEA | C21082000179 | New_Event | Vegetation Contact | Include | Include | Vegetation | 968 | 2021-08-20 | 193600 | keep | 0 | Aug | 2021 | 0.13186 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-08-20 20:20 | 2021-08-20 20:51 | 12 | 000:31 | P | SECUNDARIA/DESGANCHE | SE ABRIO MONTURA PARA REPARAR CONECTOR Y DESGANCHE SECUNDARIO | S21082000192 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 31 | 2021-08-20 | 372 | keep | 0 | Aug | 2021 | 0.00025337 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-08-20 20:33 | 2021-08-20 20:35 | 1000 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA CARGA 80% 1348-6, 1348-7 Y PARTE DEL 1336-8 SE PROBO QUEDO EN SERVICIO | S21082000196 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-20 | 2000 | keep | 0 | Aug | 2021 | 0.0013622 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2021-08-20 20:33 | 2021-08-20 20:35 | 1000 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA CARGA 80% 1348-6 Y LLEVA 1348-7 Y PARTE DEL 1336-8 SE PROBO QUEDO EN SERVICIO | S21082000196 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-20 | 2000 | keep | 0 | Aug | 2021 | 0.0013622 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2021-08-20 20:33 | 2021-08-20 20:35 | 278 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA CARGA 80% 1348-6 Y LLEVA 1348-7 Y PARTE DEL 1336-8 SE PROBO QUEDO EN SERVICIO | S21082000196 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-20 | 556 | keep | 0 | Aug | 2021 | 0.00037869 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2021-08-20 20:33 | 2021-08-20 20:35 | 9 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA CARGA 80% 1348-6 Y LLEVA 1348-7 Y PARTE DEL 1336-8 SE PROBO QUEDO EN SERVICIO | S21082000196 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-20 | 18 | keep | 0 | Aug | 2021 | 1.226e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2021-08-20 20:47 | 2021-08-20 20:49 | 1000 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA 80% 1348-6, 1348-7 Y PARTE DEL 1336-8 | S21082000197 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-20 | 2000 | keep | 0 | Aug | 2021 | 0.0013622 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2021-08-20 20:47 | 2021-08-20 20:49 | 1000 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA 80% 1348-6 LLEVA 1348-7 Y PARTE DEL 1336-8 | S21082000197 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-20 | 2000 | keep | 0 | Aug | 2021 | 0.0013622 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2021-08-20 20:47 | 2021-08-20 20:49 | 278 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA 80% 1348-6 LLEVA 1348-7 Y PARTE DEL 1336-8 | S21082000197 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-20 | 556 | keep | 0 | Aug | 2021 | 0.00037869 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2021-08-20 20:47 | 2021-08-20 20:49 | 9 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA 80% 1348-6 LLEVA 1348-7 Y PARTE DEL 1336-8 | S21082000197 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-20 | 18 | keep | 0 | Aug | 2021 | 1.226e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2021-08-20 21:55 | 2021-08-20 23:44 | 889 | 001:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO PUENTES PARA SECCIONALIZAR ALAMBRE PRIMARIO EN EL SUELO SE CERRO MACHETES | C21082000156 | Partial_restoration | Wire Down | Include | Include | Equipment | 109 | 2021-08-20 | 96901 | keep | 0 | Aug | 2021 | 0.065999 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-20 21:56 | 2021-08-20 22:59 | 200 | 001:03 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21082000221 | New_Event | Bad Weather | Include | Include | Weather | 63 | 2021-08-20 | 12600 | keep | 0 | Aug | 2021 | 0.0085818 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
HUMACAO | 2021-08-20 22:02 | 2021-08-20 22:14 | 3785 | 000:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE NORMALIZO LA CARGA DEL INTELLIRRUPTER 2603-08D PARA CERRAR PUENTE DEL 3205-07 | C21082000180 | New_Event | Wire Down | Include | Include | Equipment | 12 | 2021-08-20 | 45420 | keep | 0 | Aug | 2021 | 0.030935 | 0.0025779 | Sustained | FALSE | FALSE | Not_TMED_Event | 3785
PONCE | 2021-08-20 22:55 | 2021-08-21 12:12 | 150 | 013:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 80 EN CORTE DE LINEA CRUCE DE FASES POR AVE | P21082000165 | New_Event |  |  | Include | Wildlife | 797 | 2021-08-20 | 119550 | keep | 0 | Aug | 2021 | 0.081425 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-08-20 22:56 | 2021-08-20 23:44 | 4634 | 000:48 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A MACHETE CERRADO POR CONTROL | C21082000180 | Additional_clients | Wire Down | Include | Include | Equipment | 48 | 2021-08-20 | 222432 | keep | 0 | Aug | 2021 | 0.1515 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-20 22:58 | 2021-08-21 11:10 | 60 | 012:12 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M21082100005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 732 | 2021-08-20 | 43920 | keep | 0 | Aug | 2021 | 0.029914 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-08-20 23:02 | 2021-08-21 11:19 | 20 | 012:17 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | S21082000209 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 737 | 2021-08-20 | 14740 | keep | 0 | Aug | 2021 | 0.010039 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-08-20 23:21 | 2021-08-21 11:17 | 50 | 011:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21082000284 | New_Event | Vegetation Contact | Include | Include | Vegetation | 716 | 2021-08-20 | 35800 | keep | 0 | Aug | 2021 | 0.024383 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-08-20 23:32 | 2021-08-21 10:30 | 30 | 010:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | R21082000112 | New_Event |  |  | Include | Wildlife | 658 | 2021-08-20 | 19740 | keep | 0 | Aug | 2021 | 0.013445 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-08-20 23:44 | 2021-08-21 16:46 | 70 | 017:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR DEL SUELO | C21082100001 | Partial_restoration | Wire Down | Include | Include | Equipment | 1022 | 2021-08-20 | 71540 | keep | 0 | Aug | 2021 | 0.048726 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-21 00:38 | 2021-08-21 10:18 | 15 | 009:40 | P | NO SE REPORTO CAUSA | 3 X 100 EN SU-1 | S21082100002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 580 | 2021-08-21 | 8700 | keep | 0 | Aug | 2021 | 0.0059255 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-08-21 02:52 | 2021-08-21 02:53 | 817 | 000:01 | T | OTRAS CAUSAS | RECERRO INTERRUPTOR | C21082100005 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-08-21 | 817 | keep | 0 | Aug | 2021 | 0.00055645 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
CAGUAS | 2021-08-21 02:53 | 2021-08-21 16:26 | 50 | 013:33 | P | OTRAS CAUSAS | 1 X 30 EN RISER PROBLEMA DEL CLIENTE | C21082100043 | 1st_after_momentary | Other Causes | Include | Include | Other | 813 | 2021-08-21 | 40650 | keep | 0 | Aug | 2021 | 0.027687 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2021-08-21 02:58 | 2021-08-21 04:04 | 1785 | 001:06 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRE INTERRUPTOR PARA ABRIR MACHETES Y SECCIONALIZAR AVERIA POSTE PRIMARIO PARTIDO POR IMPACTO DE VEHICULO | P21082100003 | New_Event |  |  | Include | Wildlife | 66 | 2021-08-21 | 117810 | keep | 0 | Aug | 2021 | 0.08024 | 0.0012158 | Sustained | FALSE | FALSE | Not_TMED_Event | 1785
AGUADILLA | 2021-08-21 03:13 | 2021-08-21 03:14 | 4882 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M21082100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-21 | 4882 | keep | 0 | Aug | 2021 | 0.0033251 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
AGUADILLA | 2021-08-21 03:14 | 2021-08-21 17:43 | 80 | 014:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | M21082100036 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 869 | 2021-08-21 | 69520 | keep | 0 | Aug | 2021 | 0.04735 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
AGUADILLA | 2021-08-21 03:48 | 2021-08-21 03:49 | 390 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21082100002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-21 | 390 | keep | 0 | Aug | 2021 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
GUAYAMA | 2021-08-21 04:04 | 2021-08-21 17:38 | 1000 | 013:34 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO 45 PIES METAL Y SE CERRO MACHETES | P21082100011 | New_Event | Defective Pole | Include | Include | Equipment | 814 | 2021-08-21 | 814000 | keep | 0 | Aug | 2021 | 0.55441 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
YAUCO | 2021-08-21 04:23 | 2021-08-21 12:00 | 80 | 007:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE DE FASES POR AVE | P21082100013 | New_Event |  |  | Include | Wildlife | 457 | 2021-08-21 | 36560 | keep | 0 | Aug | 2021 | 0.024901 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CAGUAS | 2021-08-21 05:51 | 2021-08-21 13:27 | 100 | 007:36 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | C21082100007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 456 | 2021-08-21 | 45600 | keep | 0 | Aug | 2021 | 0.031058 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-08-21 07:17 | 2021-08-21 09:58 | 65 | 002:41 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21082100012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2021-08-21 | 10465 | keep | 0 | Aug | 2021 | 0.0071277 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
MAYAGÃœEZ | 2021-08-21 07:17 | 2021-08-21 08:30 | 40 | 001:13 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | M21082100006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2021-08-21 | 2920 | keep | 0 | Aug | 2021 | 0.0019888 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-08-21 07:19 | 2021-08-21 09:58 | 200 | 002:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE QUEMADO | A21082100023 | New_Event | Cutout Failure | Include | Include | Equipment | 159 | 2021-08-21 | 31800 | keep | 0 | Aug | 2021 | 0.021659 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
BAYAMON | 2021-08-21 07:24 | 2021-08-21 14:24 | 15 | 007:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA QUEMADA | S21082100014 | New_Event | Cutout Failure | Include | Include | Equipment | 420 | 2021-08-21 | 6300 | keep | 0 | Aug | 2021 | 0.0042909 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-08-21 07:25 | 2021-08-21 08:35 | 100 | 001:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO PORTA FUSIBLE QUEMADO | A21082100025 | New_Event | Cutout Failure | Include | Include | Equipment | 70 | 2021-08-21 | 7000 | keep | 0 | Aug | 2021 | 0.0047677 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-08-21 07:39 | 2021-08-21 07:40 | 4641 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21082100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-21 | 4641 | keep | 0 | Aug | 2021 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
CAGUAS | 2021-08-21 07:41 | 2021-08-21 12:36 | 4 | 004:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REMPLAZO BAJANTE SECUNDARIO | C21082100009 | New_Event | Secondary Wire Down | Include | Include | Equipment | 295 | 2021-08-21 | 1180 | keep | 0 | Aug | 2021 | 0.00080369 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2021-08-21 07:51 | 2021-08-21 17:25 | 4 | 009:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARA SULFATADA | C21082100011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 574 | 2021-08-21 | 2296 | keep | 0 | Aug | 2021 | 0.0015638 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
ARECIBO | 2021-08-21 08:17 | 2021-08-21 17:27 | 5 | 009:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA SE REEMPLAZAR CONEXIONES SECUNDARIAS | A21082100032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 550 | 2021-08-21 | 2750 | keep | 0 | Aug | 2021 | 0.001873 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-08-21 08:19 | 2021-08-21 17:30 | 40 | 009:11 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | M21082100012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 551 | 2021-08-21 | 22040 | keep | 0 | Aug | 2021 | 0.015011 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-08-21 08:24 | 2021-08-21 14:54 | 50 | 006:30 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN SU AVERIA DEL T33 AL T32 | C21082100013 | New_Event | UG Cable Fault | Include | Include | Equipment | 390 | 2021-08-21 | 19500 | keep | 0 | Aug | 2021 | 0.013281 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-08-21 08:39 | 2021-08-21 12:15 | 45 | 003:36 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU#3 | P21082100132 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 216 | 2021-08-21 | 9720 | keep | 0 | Aug | 2021 | 0.0066202 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2021-08-21 08:54 | 2021-08-21 13:33 | 1 | 004:39 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C21082100015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 279 | 2021-08-21 | 279 | keep | 0 | Aug | 2021 | 0.00019003 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-08-21 09:06 | 2021-08-21 09:07 | 3006 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21082100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-21 | 3006 | keep | 0 | Aug | 2021 | 0.0020474 | 0.0020474 | Momentary | FALSE | FALSE | Not_TMED_Event | 3006
MAYAGÃœEZ | 2021-08-21 09:07 | 2021-08-24 13:10 | 1 | 076:03 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21082000096 | Partial_restoration | Bad Weather | Include | Include | Weather | 4563 | 2021-08-21 | 4563 | keep | 0 | Aug | 2021 | 0.0031078 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
FAJARDO | 2021-08-21 09:17 | 2021-08-21 11:40 | 10 | 002:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR REEMPLAZO CAJA PRIMARIA AVERIADA | R21082100015 | New_Event | Cutout Failure | Include | Include | Equipment | 143 | 2021-08-21 | 1430 | keep | 0 | Aug | 2021 | 0.00097397 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-21 09:37 | 2021-08-21 13:02 | 20 | 003:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO AISLADOR ROTO EN LINEA PRIMARIA | A21082000043 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 205 | 2021-08-21 | 4100 | keep | 0 | Aug | 2021 | 0.0027925 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
FAJARDO | 2021-08-21 09:53 | 2021-08-21 15:21 | 48 | 005:28 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | R21082100019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 328 | 2021-08-21 | 15744 | keep | 0 | Aug | 2021 | 0.010723 | 3.2693e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 48
SAN JUAN | 2021-08-21 09:54 | 2021-08-21 16:00 | 380 | 006:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE MACHETE PARA LEVANTAR PRIMARIA | S21082100023 | New_Event | Wire Down | Include | Include | Equipment | 366 | 2021-08-21 | 139080 | keep | 0 | Aug | 2021 | 0.094727 | 0.00025882 | Sustained | FALSE | FALSE | Not_TMED_Event | 380
UTUADO | 2021-08-21 09:55 | 2021-08-21 13:22 | 5 | 003:27 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50KVA MARCA HOWARD 120/240 4160/7200 S/N 1724981218 FID33721610 AVERIADO | A21082100045 | New_Event | Service Transformer Failure | Include | Include | Equipment | 207 | 2021-08-21 | 1035 | keep | 0 | Aug | 2021 | 0.00070493 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2021-08-21 10:13 | 2021-08-21 19:16 | 5 | 009:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTA FUSIBLE QUEMADO | A21082100047 | New_Event | Cutout Failure | Include | Include | Equipment | 543 | 2021-08-21 | 2715 | keep | 0 | Aug | 2021 | 0.0018492 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-08-21 10:19 | 2021-08-21 21:11 | 1 | 010:52 | P | PARARRAYOS DEFECTUOSO | 3 X 30 EN CAJAS PRIMARIAS SE REEMPLAZARON | C21082100029 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 652 | 2021-08-21 | 652 | keep | 0 | Aug | 2021 | 0.00044407 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2021-08-21 10:29 | 2021-08-21 16:32 | 155 | 006:03 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 40 EN CORTES DE LINEA SE PATRULLO | C21082100031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 363 | 2021-08-21 | 56265 | keep | 0 | Aug | 2021 | 0.038322 | 0.00010557 | Sustained | FALSE | TRUE | Not_TMED_Event | 155
AGUADILLA | 2021-08-21 10:41 | 2021-08-21 20:22 | 15 | 009:41 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE DE METAL PARTIDO | M21082100028 | New_Event | Defective Pole | Include | Include | Equipment | 581 | 2021-08-21 | 8715 | keep | 0 | Aug | 2021 | 0.0059357 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-08-21 10:58 | 2021-08-21 14:57 | 1 | 003:59 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER | B21082100016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 239 | 2021-08-21 | 239 | keep | 0 | Aug | 2021 | 0.00016278 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-08-21 11:03 | 2021-08-21 12:53 | 25 | 001:50 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21082100017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 110 | 2021-08-21 | 2750 | keep | 0 | Aug | 2021 | 0.001873 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CANOVANAS | 2021-08-21 11:06 | 2021-08-21 12:17 | 539 | 001:11 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO TIENE RTU SE CERRO ELECTRICAMENTE | R21082100024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 71 | 2021-08-21 | 38269 | keep | 0 | Aug | 2021 | 0.026065 | 0.00036711 | Sustained | FALSE | FALSE | Not_TMED_Event | 539
CANOVANAS | 2021-08-21 11:06 | 2021-08-21 12:47 | 635 | 001:41 | T | NO SE REPORTO CAUSA | DISPARO DEL 2305-01 NO TIENE RTU SE ABRIO N/O Y SE CERRO EL INTERRUPTOR | R21082100024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 101 | 2021-08-21 | 64135 | keep | 0 | Aug | 2021 | 0.043682 | 0.0004325 | Sustained | FALSE | FALSE | Not_TMED_Event | 635
PONCE | 2021-08-21 11:20 | 2021-08-21 12:05 | 158 | 000:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN RISER SE REMPLAZO CAJA PRIMARIA QUEMADA | P21082100019 | New_Event | Cutout Failure | Include | Include | Equipment | 45 | 2021-08-21 | 7110 | keep | 0 | Aug | 2021 | 0.0048426 | 0.00010761 | Sustained | FALSE | FALSE | Not_TMED_Event | 158
PONCE | 2021-08-21 11:24 | 2021-08-21 14:31 | 15 | 003:07 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | P21082100065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 187 | 2021-08-21 | 2805 | keep | 0 | Aug | 2021 | 0.0019105 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2021-08-21 11:31 | 2021-08-21 14:30 | 1 | 002:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES EN LA TOMA SECUNDARIA | R21082100045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 179 | 2021-08-21 | 179 | keep | 0 | Aug | 2021 | 0.00012192 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-08-21 11:43 | 2021-08-21 14:14 | 20 | 002:31 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE CARGA TRANSFERIDA AL 1709-01 | B21082100020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2021-08-21 | 3020 | keep | 0 | Aug | 2021 | 0.0020569 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-08-21 12:12 | 2021-08-21 12:13 | 1979 | 000:01 | S | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE BREAKER PORTATIL | P21082100073 | New_Event |  |  | Include | Wildlife | 1 | 2021-08-21 | 1979 | keep | 0 | Aug | 2021 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2021-08-21 12:12 | 2021-08-21 12:13 | 5069 | 000:01 | S | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE BREAKER PORTATIL | P21082100073 | Additional_clients |  |  | Include | Wildlife | 1 | 2021-08-21 | 5069 | keep | 0 | Aug | 2021 | 0.0034525 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-08-21 12:12 | 2021-08-21 12:13 | 5063 | 000:01 | S | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE BREAKER PORTATIL | P21082100073 | New_Event |  |  | Include | Wildlife | 1 | 2021-08-21 | 5063 | keep | 0 | Aug | 2021 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
PONCE | 2021-08-21 12:13 | 2021-08-21 13:08 | 150 | 000:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 80 EN CORTE DE LINEA CRUCE DE FASES POR AVE | P21082000165 | 1st_after_momentary |  |  | Include | Wildlife | 55 | 2021-08-21 | 8250 | keep | 0 | Aug | 2021 | 0.005619 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-08-21 12:13 | 2021-08-21 17:12 | 100 | 004:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA ABB | A21082100054 | New_Event | Cutout Failure | Include | Include | Equipment | 299 | 2021-08-21 | 29900 | keep | 0 | Aug | 2021 | 0.020365 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-08-21 12:16 | 2021-08-21 17:05 | 40 | 004:49 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN PROVISIONAL, 1 X 80 EN SU-1 AVERIA NUEVA T-2 A T-3 AVERIA VIEJA T-3 A T-4 Y QUEDO FUERA T-3 | S21082100039 | New_Event | UG Cable Fault | Include | Include | Equipment | 289 | 2021-08-21 | 11560 | keep | 0 | Aug | 2021 | 0.0078735 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2021-08-21 12:22 | 2021-08-21 13:42 | 40 | 001:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | A21082100056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2021-08-21 | 3200 | keep | 0 | Aug | 2021 | 0.0021795 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-08-21 12:28 | 2021-08-21 15:09 | 20 | 002:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE RETIRO AVE CRUZANDO LINEAS | B21082100022 | New_Event |  |  | Include | Wildlife | 161 | 2021-08-21 | 3220 | keep | 0 | Aug | 2021 | 0.0021931 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-08-21 12:34 | 2021-08-21 17:18 | 120 | 004:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE CERRO PUENTE ABIERTO | C21082100037 | New_Event | Wire Down | Include | Include | Equipment | 284 | 2021-08-21 | 34080 | keep | 0 | Aug | 2021 | 0.023212 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
AGUADILLA | 2021-08-21 12:49 | 2021-08-21 17:09 | 200 | 004:20 | P | NO SE REPORTO CAUSA | 1 X 140 Y 1 X 80 EN CORTE DE LINEA | M21082100034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 260 | 2021-08-21 | 52000 | keep | 0 | Aug | 2021 | 0.035417 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CANOVANAS | 2021-08-21 12:55 | 2021-08-21 14:55 | 2106 | 002:00 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SUBESTACION SIN RTU CERRADO EN LA SUBESTACION | R21082100064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2021-08-21 | 252720 | keep | 0 | Aug | 2021 | 0.17213 | 0.0014344 | Sustained | FALSE | FALSE | Not_TMED_Event | 2106
BAYAMON | 2021-08-21 13:01 | 2021-08-22 19:58 | 10 | 030:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA Y SE REPARO SECUNDARIA | B21082100025 | New_Event | Cutout Failure | Include | Include | Equipment | 1857 | 2021-08-21 | 18570 | keep | 0 | Aug | 2021 | 0.012648 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2021-08-21 13:33 | 2021-08-22 16:14 | 12 | 026:41 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR AVERIADO DE 50 KVA A 2.4/4.16 KV X LO MISMO | P21082100085 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1601 | 2021-08-21 | 19212 | keep | 0 | Aug | 2021 | 0.013085 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-08-21 13:36 | 2021-08-21 19:31 | 228 | 005:55 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE CERRO PUENTE PRIMARIO | R21082100076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 355 | 2021-08-21 | 80940 | keep | 0 | Aug | 2021 | 0.055128 | 0.00015529 | Sustained | FALSE | TRUE | Not_TMED_Event | 228
YAUCO | 2021-08-21 13:50 | 2021-08-21 17:05 | 40 | 003:15 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA CRUCE DE FASES POR RAMA | P21082100080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2021-08-21 | 7800 | keep | 0 | Aug | 2021 | 0.0053125 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-21 14:48 | 2021-08-21 17:23 | 528 | 002:35 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | M21082100073 | New_Event | Cutout Failure | Include | Include | Equipment | 155 | 2021-08-21 | 81840 | keep | 0 | Aug | 2021 | 0.055741 | 0.00035962 | Sustained | FALSE | FALSE | Not_TMED_Event | 528
MAYAGÃœEZ | 2021-08-21 14:48 | 2021-08-21 17:23 | 871 | 002:35 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | M21082100073 | New_Event | Cutout Failure | Include | Include | Equipment | 155 | 2021-08-21 | 135005 | keep | 0 | Aug | 2021 | 0.091951 | 0.00059323 | Sustained | FALSE | FALSE | Not_TMED_Event | 871
HUMACAO | 2021-08-21 14:54 | 2021-08-21 14:55 | 2354 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE | C21082100000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2021-08-21 | 2354 | keep | 0 | Aug | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
HUMACAO | 2021-08-21 14:55 | 2021-08-21 16:18 | 50 | 001:23 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN SU AVERIA DEL T33 AL T32 | C21082100013 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 83 | 2021-08-21 | 4150 | keep | 0 | Aug | 2021 | 0.0028265 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-08-21 15:22 | 2021-08-22 09:30 | 40 | 018:08 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21082100066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1088 | 2021-08-21 | 43520 | keep | 0 | Aug | 2021 | 0.029641 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-08-21 15:46 | 2021-08-21 18:37 | 5 | 002:51 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5 KVA EATON 4800-8320 120/240 FID 33599449 AVERIADO WR5918765 | A21082100000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 171 | 2021-08-21 | 855 | keep | 0 | Aug | 2021 | 0.00058234 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-08-21 15:57 | 2021-08-22 09:14 | 20 | 017:17 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | S21082100070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1037 | 2021-08-21 | 20740 | keep | 0 | Aug | 2021 | 0.014126 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-08-21 16:05 | 2021-08-21 21:42 | 4369 | 005:37 | S | BREAKER DEFECTUOSO O NO OPERA | INTERRUPTOR 3010-4 BUSHINGS QUEMADOS. | C21082100053 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 337 | 2021-08-21 | 1472353 | keep | 0 | Aug | 2021 | 1.0028 | 0.0029757 | Sustained | FALSE | FALSE | Not_TMED_Event | 4369
CAGUAS | 2021-08-21 16:05 | 2021-08-21 21:42 | 676 | 005:37 | S | BREAKER DEFECTUOSO O NO OPERA | INTERRUPTOR 3010-4 BUSHINGS QUEMADOS. | C21082100053 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 337 | 2021-08-21 | 227812 | keep | 0 | Aug | 2021 | 0.15516 | 0.00046042 | Sustained | FALSE | FALSE | Not_TMED_Event | 676
CAGUAS | 2021-08-21 16:05 | 2021-08-21 21:42 | 1606 | 005:37 | S | BREAKER DEFECTUOSO O NO OPERA | INTERRUPTOR 3010-4 BUSHINGS QUEMADOS. | C21082100053 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 337 | 2021-08-21 | 541222 | keep | 0 | Aug | 2021 | 0.36862 | 0.0010938 | Sustained | FALSE | FALSE | Not_TMED_Event | 1606
CAGUAS | 2021-08-21 16:05 | 2021-08-21 21:42 | 725 | 005:37 | S | BREAKER DEFECTUOSO O NO OPERA | INTERRUPTOR 3010-4 BUSHINGS QUEMADOS. | C21082100053 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 337 | 2021-08-21 | 244325 | keep | 0 | Aug | 2021 | 0.16641 | 0.00049379 | Sustained | FALSE | FALSE | Not_TMED_Event | 725
BAYAMON | 2021-08-21 16:14 | 2021-08-22 13:21 | 69 | 021:07 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | B21082100033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1267 | 2021-08-21 | 87423 | keep | 0 | Aug | 2021 | 0.059543 | 4.6996e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 69
SAN JUAN | 2021-08-21 16:16 | 2021-08-22 10:54 | 10 | 018:38 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21082100072 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1118 | 2021-08-21 | 11180 | keep | 0 | Aug | 2021 | 0.0076146 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-21 16:54 | 2021-08-22 17:45 | 8 | 024:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE CAMBIO DE FASE DE LA CUAL SE ALIMENTABA EL TRANSFORMADOR | A21082100062 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1491 | 2021-08-21 | 11928 | keep | 0 | Aug | 2021 | 0.0081241 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-08-21 17:00 | 2021-08-21 17:39 | 4 | 000:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO CONEXIONES SECUNDARIAS | A21082100039 | New_Event | Secondary Wire Down | Include | Include | Equipment | 39 | 2021-08-21 | 156 | keep | 0 | Aug | 2021 | 0.00010625 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-08-21 17:05 | 2021-08-22 18:52 | 25 | 025:47 | P | CABLE SOTERRADO AVERIADO | SE CONTRUYO PROVISIONAL AEREO DE SU-1 HACIA T-3 | S21082100039 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1547 | 2021-08-21 | 38675 | keep | 0 | Aug | 2021 | 0.026341 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-21 17:54 | 2021-08-21 22:37 | 60 | 004:43 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21082100077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2021-08-21 | 16980 | keep | 0 | Aug | 2021 | 0.011565 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-08-21 17:54 | 2021-08-21 23:05 | 50 | 005:11 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE RETIRO PARARRAYOS CRUZADO | A21082100067 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 311 | 2021-08-21 | 15550 | keep | 0 | Aug | 2021 | 0.010591 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-21 18:56 | 2021-08-21 18:57 | 492 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21082100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-21 | 492 | keep | 0 | Aug | 2021 | 0.0003351 | 0.0003351 | Momentary | FALSE | FALSE | Not_TMED_Event | 492
BAYAMON | 2021-08-21 18:57 | 2021-08-22 11:25 | 1 | 016:28 | P | NO SE REPORTO CAUSA | 3 SMU-20 X 100 EN SU-212 | B21082100040 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 988 | 2021-08-21 | 988 | keep | 0 | Aug | 2021 | 0.00067292 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-08-21 19:09 | 2021-08-22 09:56 | 50 | 014:47 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21082100037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 887 | 2021-08-21 | 44350 | keep | 0 | Aug | 2021 | 0.030207 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-21 20:30 | 2021-08-22 09:05 | 100 | 012:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21082100141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 755 | 2021-08-21 | 75500 | keep | 0 | Aug | 2021 | 0.051423 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-08-21 20:45 | 2021-08-22 09:35 | 45 | 012:50 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21082100085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 770 | 2021-08-21 | 34650 | keep | 0 | Aug | 2021 | 0.0236 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
GUAYAMA | 2021-08-21 20:49 | 2021-08-21 22:45 | 75 | 001:56 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | P21082100100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2021-08-21 | 8700 | keep | 0 | Aug | 2021 | 0.0059255 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
ARECIBO | 2021-08-21 21:40 | 2021-08-21 22:20 | 225 | 000:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 200 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21082100075 | New_Event | Bad Weather | Include | Include | Weather | 40 | 2021-08-21 | 9000 | keep | 0 | Aug | 2021 | 0.0061299 | 0.00015325 | Sustained | FALSE | TRUE | Not_TMED_Event | 225
CAGUAS | 2021-08-21 22:42 | 2021-08-21 23:20 | 2900 | 000:38 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR CONDUCTOR EN EL SUELO SE SECCIONALIZO CERRADO POR CONTROL | C21082100173 | New_Event | Wire Down | Include | Include | Equipment | 38 | 2021-08-21 | 110200 | keep | 0 | Aug | 2021 | 0.075057 | 0.0019752 | Sustained | FALSE | FALSE | Not_TMED_Event | 2900
MAYAGÃœEZ | 2021-08-21 23:30 | 2021-08-22 10:35 | 75 | 011:05 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21082100151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 665 | 2021-08-21 | 49875 | keep | 0 | Aug | 2021 | 0.03397 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
ARECIBO | 2021-08-21 23:56 | 2021-08-21 23:57 | 2697 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21082100081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-21 | 2697 | keep | 0 | Aug | 2021 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
MAYAGÃœEZ | 2021-08-22 00:11 | 2021-08-22 12:38 | 30 | 012:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21082200001 | New_Event | Bad Weather | Include | Include | Weather | 747 | 2021-08-22 | 22410 | keep | 0 | Aug | 2021 | 0.015263 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-08-22 00:56 | 2021-08-22 11:21 | 85 | 010:25 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21082200003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 625 | 2021-08-22 | 53125 | keep | 0 | Aug | 2021 | 0.036183 | 5.7893e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 85
ARECIBO | 2021-08-22 01:08 | 2021-08-22 09:25 | 100 | 008:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON 2 CAJAS PRIMARIAS AVERIADAS EN CORTE DE LINEA | A21082200003 | New_Event | Cutout Failure | Include | Include | Equipment | 497 | 2021-08-22 | 49700 | keep | 0 | Aug | 2021 | 0.03385 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-08-22 01:35 | 2021-08-22 07:03 | 1516 | 005:28 | T | DESGANCHE | DISPARO CERRADO ELECTRICAMENTE NO RTU SECCIONALIZO ARBOL SOBRE LAS LINEAS | C21082200002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 328 | 2021-08-22 | 497248 | keep | 0 | Aug | 2021 | 0.33867 | 0.0010325 | Sustained | FALSE | TRUE | Not_TMED_Event | 1516
ARECIBO | 2021-08-22 03:28 | 2021-08-22 03:29 | 2201 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR | A21082200004 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-08-22 | 2201 | keep | 0 | Aug | 2021 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2021-08-22 03:29 | 2021-08-22 11:35 | 100 | 008:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | AISLADOR PARTIDO CORTE DE LINEA ABIERTO SE DISPARO INTERRUPTOR | A21082200005 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 486 | 2021-08-22 | 48600 | keep | 0 | Aug | 2021 | 0.033101 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-08-22 03:52 | 2021-08-22 12:07 | 6 | 008:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | C21082200004 | New_Event |  |  | Include | Wildlife | 495 | 2021-08-22 | 2970 | keep | 0 | Aug | 2021 | 0.0020229 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-08-22 04:40 | 2021-08-22 04:41 | 721 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | S21082200008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-22 | 721 | keep | 0 | Aug | 2021 | 0.00049107 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
BAYAMON | 2021-08-22 04:40 | 2021-08-22 11:06 | 35 | 006:26 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S21082200007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 386 | 2021-08-22 | 13510 | keep | 0 | Aug | 2021 | 0.0092016 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
PONCE | 2021-08-22 04:51 | 2021-08-22 07:13 | 1615 | 002:22 | T | ANIMAL U OBJETO EXTRAÃ‘O | AUTO IMPACTO Y PARTIO POSTE | P21082200009 | New_Event |  |  | Include | Wildlife | 142 | 2021-08-22 | 229330 | keep | 0 | Aug | 2021 | 0.1562 | 0.0011 | Sustained | FALSE | FALSE | Not_TMED_Event | 1615
HUMACAO | 2021-08-22 06:17 | 2021-08-22 09:42 | 80 | 003:25 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21082200019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2021-08-22 | 16400 | keep | 0 | Aug | 2021 | 0.01117 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-08-22 06:23 | 2021-08-22 10:13 | 10 | 003:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A21082200011 | New_Event | Wire Down | Include | Include | Equipment | 230 | 2021-08-22 | 2300 | keep | 0 | Aug | 2021 | 0.0015665 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-08-22 06:30 | 2021-08-22 11:54 | 40 | 005:24 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C21082200024 | New_Event |  |  | Include | Wildlife | 324 | 2021-08-22 | 12960 | keep | 0 | Aug | 2021 | 0.008827 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-22 06:32 | 2021-08-22 10:15 | 200 | 003:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | M21082200011 | New_Event | Bad Weather | Include | Include | Weather | 223 | 2021-08-22 | 44600 | keep | 0 | Aug | 2021 | 0.030377 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-08-22 06:47 | 2021-08-22 11:38 | 140 | 004:51 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 140 EN CORTE DE LINEA REMPLAZO AISLADOR, REPARO Y LEVANTO CONDUCTOR | C21082200026 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 291 | 2021-08-22 | 40740 | keep | 0 | Aug | 2021 | 0.027748 | 9.5353e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 140
YAUCO | 2021-08-22 06:53 | 2021-08-22 13:11 | 17 | 006:18 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA | P21082200011 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 378 | 2021-08-22 | 6426 | keep | 0 | Aug | 2021 | 0.0043767 | 1.1579e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 17
UTUADO | 2021-08-22 07:05 | 2021-08-22 09:22 | 75 | 002:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21082200017 | New_Event | Bad Weather | Include | Include | Weather | 137 | 2021-08-22 | 10275 | keep | 0 | Aug | 2021 | 0.0069983 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
PONCE | 2021-08-22 07:13 | 2021-08-22 16:35 | 1000 | 009:22 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REMPLAZO POSTE PRIMARIO PARTIDO POR IMPACTO DE VEHICULO Y SE CERRO MACHETES | P21082200036 | Partial_restoration |  |  | Include | Wildlife | 562 | 2021-08-22 | 562000 | keep | 0 | Aug | 2021 | 0.38278 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-22 07:21 | 2021-08-22 11:58 | 120 | 004:37 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE REALIZO DESGANCHE CARGA TRANSFERIDA AL 1709-01 | B21082200013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 277 | 2021-08-22 | 33240 | keep | 0 | Aug | 2021 | 0.02264 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
AGUADILLA | 2021-08-22 07:22 | 2021-08-22 16:39 | 50 | 009:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO BAJANTE A CAJA PRIMARIA | M21082200007 | New_Event | Wire Down | Include | Include | Equipment | 557 | 2021-08-22 | 27850 | keep | 0 | Aug | 2021 | 0.018969 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BARRANQUITAS | 2021-08-22 07:40 | 2021-08-22 14:40 | 80 | 007:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 40 EN CORTE DE LINEA RETEZO LINEAS | C21082200034 | New_Event | Wire Down | Include | Include | Equipment | 420 | 2021-08-22 | 33600 | keep | 0 | Aug | 2021 | 0.022885 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BARRANQUITAS | 2021-08-22 07:46 | 2021-08-22 16:58 | 50 | 009:12 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA REMPLAZO AISLADORES | C21082200036 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 552 | 2021-08-22 | 27600 | keep | 0 | Aug | 2021 | 0.018798 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-22 07:48 | 2021-08-22 18:20 | 80 | 010:32 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUAS SOBRE LINEA PRIMARIA | M21082200053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 632 | 2021-08-22 | 50560 | keep | 0 | Aug | 2021 | 0.034436 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-08-22 08:03 | 2021-08-22 10:00 | 30 | 001:57 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA REMPLAZO AISLADOR | P21082200014 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 117 | 2021-08-22 | 3510 | keep | 0 | Aug | 2021 | 0.0023906 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-08-22 08:07 | 2021-08-22 11:03 | 100 | 002:56 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | S21082200017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 176 | 2021-08-22 | 17600 | keep | 0 | Aug | 2021 | 0.011987 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-08-22 08:32 | 2021-08-22 12:32 | 250 | 004:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M21082200013 | New_Event | Wire Down | Include | Include | Equipment | 240 | 2021-08-22 | 60000 | keep | 0 | Aug | 2021 | 0.040866 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
BAYAMON | 2021-08-22 08:53 | 2021-08-22 12:30 | 30 | 003:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | ACCIDENTE DE AUTO SE REEMPLAZO DOS POSTES 45', TRANSFORMADOR 50 KVA Y SE LEVANTO CONDUCTOR | B21082200007 | New_Event |  |  | Include | Wildlife | 217 | 2021-08-22 | 6510 | keep | 0 | Aug | 2021 | 0.0044339 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-08-22 08:58 | 2021-08-22 12:28 | 50 | 003:30 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21082200020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 210 | 2021-08-22 | 10500 | keep | 0 | Aug | 2021 | 0.0071515 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-22 09:00 | 2021-08-22 12:28 | 20 | 003:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA PASAR LINEAS SECUNDARIAS A POSTE NUEVO | M21082200026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 208 | 2021-08-22 | 4160 | keep | 0 | Aug | 2021 | 0.0028334 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
FAJARDO | 2021-08-22 09:11 | 2021-08-22 09:12 | 1234 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | R21082200004 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-22 | 1234 | keep | 0 | Aug | 2021 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
FAJARDO | 2021-08-22 09:12 | 2021-08-22 12:13 | 232 | 003:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE | R21082200001 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 181 | 2021-08-22 | 41992 | keep | 0 | Aug | 2021 | 0.028601 | 0.00015801 | Sustained | FALSE | FALSE | Not_TMED_Event | 232
BAYAMON | 2021-08-22 09:14 | 2021-08-22 10:16 | 28 | 001:02 | P | NO SE REPORTO CAUSA | 3 X 125 SMU-20 EN SU-4 | S21082200027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 62 | 2021-08-22 | 1736 | keep | 0 | Aug | 2021 | 0.0011824 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
ARECIBO | 2021-08-22 09:34 | 2021-08-22 11:42 | 1 | 002:08 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA IGLESIA AVE CRUZO LINEAS | A21082200042 | New_Event |  |  | Include | Wildlife | 128 | 2021-08-22 | 128 | keep | 0 | Aug | 2021 | 8.718e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-08-22 10:21 | 2021-08-22 10:27 | 870 | 000:06 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | S21082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2021-08-22 | 5220 | keep | 0 | Aug | 2021 | 0.0035553 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
VEGA BAJA | 2021-08-22 10:34 | 2021-08-22 14:19 | 80 | 003:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE CORTE DE LINEA NO FUNDIO FUSIBLE | B21082200011 | New_Event | Wire Down | Include | Include | Equipment | 225 | 2021-08-22 | 18000 | keep | 0 | Aug | 2021 | 0.01226 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
UTUADO | 2021-08-22 10:35 | 2021-08-22 11:22 | 80 | 000:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21082200050 | New_Event | Bad Weather | Include | Include | Weather | 47 | 2021-08-22 | 3760 | keep | 0 | Aug | 2021 | 0.0025609 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-08-22 10:48 | 2021-08-22 12:56 | 5 | 002:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21082200057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 128 | 2021-08-22 | 640 | keep | 0 | Aug | 2021 | 0.0004359 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-08-22 10:49 | 2021-08-22 12:28 | 50 | 001:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO CORTE DE LINEA PARA REPARAR CONDUCTOR | C21082100116 | New_Event | Wire Down | Include | Include | Equipment | 99 | 2021-08-22 | 4950 | keep | 0 | Aug | 2021 | 0.0033714 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-08-22 10:51 | 2021-08-22 12:28 | 6 | 001:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REGULARLO Y REPARO BAJANTE SECUNDARIO | C21082100077 | New_Event | Secondary Wire Down | Include | Include | Equipment | 97 | 2021-08-22 | 582 | keep | 0 | Aug | 2021 | 0.0003964 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2021-08-22 10:58 | 2021-08-22 12:29 | 140 | 001:31 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | C21082200060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2021-08-22 | 12740 | keep | 0 | Aug | 2021 | 0.0086772 | 9.5353e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 140
AGUADILLA | 2021-08-22 10:59 | 2021-08-22 17:00 | 15 | 006:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA ROTA | M21082200030 | New_Event | Secondary Wire Down | Include | Include | Equipment | 361 | 2021-08-22 | 5415 | keep | 0 | Aug | 2021 | 0.0036881 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-08-22 11:03 | 2021-08-22 13:46 | 80 | 002:43 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21082200013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 163 | 2021-08-22 | 13040 | keep | 0 | Aug | 2021 | 0.0088815 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-08-22 11:08 | 2021-08-22 19:13 | 20 | 008:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES | A21082200051 | New_Event | Secondary Wire Down | Include | Include | Equipment | 485 | 2021-08-22 | 9700 | keep | 0 | Aug | 2021 | 0.0066066 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-08-22 11:20 | 2021-08-22 13:46 | 90 | 002:26 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 40 EN CORTE DE LINEA | B21082200017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2021-08-22 | 13140 | keep | 0 | Aug | 2021 | 0.0089496 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
SAN JUAN | 2021-08-22 11:22 | 2021-08-22 11:23 | 4291 | 000:01 | S | NO SE REPORTO CAUSA | SE ENCONTRO MAIN BREAKER ABIERTO SE VERIFICO Y SE CERRO | S21082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-22 | 4291 | keep | 0 | Aug | 2021 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
SAN JUAN | 2021-08-22 11:22 | 2021-08-22 11:23 | 1381 | 000:01 | S | NO SE REPORTO CAUSA | SE ENCONTRO MAIN BREAKER ABIERTO SE VERIFICO Y SE CERRO | S21082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-22 | 1381 | keep | 0 | Aug | 2021 | 0.00094059 | 0.00094059 | Momentary | FALSE | FALSE | Not_TMED_Event | 1381
SAN JUAN | 2021-08-22 11:24 | 2021-08-22 13:51 | 50 | 002:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO Y SE REEMPLAZO CAJA PRIMARIA CARGA POR 1335-04 | S21082200062 | New_Event | Wire Down | Include | Include | Equipment | 147 | 2021-08-22 | 7350 | keep | 0 | Aug | 2021 | 0.0050061 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2021-08-22 11:32 | 2021-08-22 15:55 | 20 | 004:23 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21082200067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2021-08-22 | 5260 | keep | 0 | Aug | 2021 | 0.0035826 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-08-22 11:34 | 2021-08-22 15:39 | 40 | 004:05 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHO Y LEVANTO CONDUCTOR | C21082200069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2021-08-22 | 9800 | keep | 0 | Aug | 2021 | 0.0066747 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-22 11:34 | 2021-08-22 15:00 | 25 | 003:26 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | M21082200032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2021-08-22 | 5150 | keep | 0 | Aug | 2021 | 0.0035076 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-08-22 11:35 | 2021-08-22 12:20 | 2201 | 000:45 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE ZAFADO DE LINEA PRIMARIA A RISER Y SE CERRO INTERRUPTOR | A21082200055 | New_Event | Wire Down | Include | Include | Equipment | 45 | 2021-08-22 | 99045 | keep | 0 | Aug | 2021 | 0.067459 | 0.0014991 | Sustained | FALSE | TRUE | Not_TMED_Event | 2201
ARECIBO | 2021-08-22 11:42 | 2021-08-22 11:43 | 2231 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR | A21082200057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-22 | 2231 | keep | 0 | Aug | 2021 | 0.0015195 | 0.0015195 | Momentary | FALSE | FALSE | Not_TMED_Event | 2231
BAYAMON | 2021-08-22 11:48 | 2021-08-22 12:30 | 150 | 000:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CONVERTIDOR Y SE REMPLAZO PORTAFUSIBLES CARGA TRANSFERIDA AL 1709-01 | B21082200020 | New_Event | Cutout Failure | Include | Include | Equipment | 42 | 2021-08-22 | 6300 | keep | 0 | Aug | 2021 | 0.0042909 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2021-08-22 11:53 | 2021-08-22 22:30 | 35 | 010:37 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21082200185 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 637 | 2021-08-22 | 22295 | keep | 0 | Aug | 2021 | 0.015185 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
AGUADILLA | 2021-08-22 11:54 | 2021-08-22 16:31 | 2 | 004:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA PARTIDA | M21082200035 | New_Event | Secondary Wire Down | Include | Include | Equipment | 277 | 2021-08-22 | 554 | keep | 0 | Aug | 2021 | 0.00037733 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
SAN JUAN | 2021-08-22 12:07 | 2021-08-25 13:25 | 80 | 073:18 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA REEMPLAZO DE CAJA QUEMADA | S21082500023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4398 | 2021-08-22 | 351840 | keep | 0 | Aug | 2021 | 0.23964 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-08-22 12:07 | 2021-08-22 16:54 | 721 | 004:47 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA PRIMARIA | S21082200081 | New_Event | Wire Down | Include | Include | Equipment | 287 | 2021-08-22 | 206927 | keep | 0 | Aug | 2021 | 0.14094 | 0.00049107 | Sustained | FALSE | TRUE | Not_TMED_Event | 721
ARECIBO | 2021-08-22 12:20 | 2021-08-22 13:58 | 200 | 001:38 | P | PARARRAYOS DEFECTUOSO | 2 X 80 EN CORTE DE LINEA REMPLAZO 2 PARARRAYOS AVERIADOS | A21082200005 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 98 | 2021-08-22 | 19600 | keep | 0 | Aug | 2021 | 0.013349 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-08-22 12:28 | 2021-08-22 13:40 | 6481 | 001:12 | P | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | S21082200091 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 72 | 2021-08-22 | 466632 | keep | 0 | Aug | 2021 | 0.31782 | 0.0044142 | Sustained | TRUE | TRUE | Not_TMED_Event | 6481
SAN JUAN | 2021-08-22 12:28 | 2021-08-22 13:40 | 480 | 001:12 | P | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | S21082200090 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 72 | 2021-08-22 | 34560 | keep | 0 | Aug | 2021 | 0.023539 | 0.00032693 | Sustained | TRUE | TRUE | Not_TMED_Event | 480
SAN JUAN | 2021-08-22 12:28 | 2021-08-22 13:40 | 403 | 001:12 | P | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | S21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 72 | 2021-08-22 | 29016 | keep | 0 | Aug | 2021 | 0.019763 | 0.00027448 | Sustained | TRUE | TRUE | Not_TMED_Event | 403
BAYAMON | 2021-08-22 12:28 | 2021-08-22 13:39 | 727 | 001:11 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 & 4 PALO SECO Y 6 DE SAN JUAN DEBIDO A AVERIA LINEA 38900 | S21082200092 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 71 | 2021-08-22 | 51617 | keep | 0 | Aug | 2021 | 0.035156 | 0.00049516 | Sustained | TRUE | TRUE | Not_TMED_Event | 727
BAYAMON | 2021-08-22 12:28 | 2021-08-22 13:39 | 290 | 001:11 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 & 4 PALO SECO Y 6 DE SAN JUAN DEBIDO A AVERIA LINEA 38900 | S21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 71 | 2021-08-22 | 20590 | keep | 0 | Aug | 2021 | 0.014024 | 0.00019752 | Sustained | TRUE | TRUE | Not_TMED_Event | 290
BAYAMON | 2021-08-22 12:28 | 2021-08-22 13:39 | 610 | 001:11 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 & 4 PALO SECO Y 6 DE SAN JUAN DEBIDO A AVERIA LINEA 38900 | S21082200094 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 71 | 2021-08-22 | 43310 | keep | 0 | Aug | 2021 | 0.029498 | 0.00041547 | Sustained | TRUE | TRUE | Not_TMED_Event | 610
SAN JUAN | 2021-08-22 12:28 | 2021-08-22 13:52 | 5668 | 001:24 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | R21082200040 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 84 | 2021-08-22 | 476112 | keep | 0 | Aug | 2021 | 0.32428 | 0.0038604 | Sustained | TRUE | TRUE | Not_TMED_Event | 5668
SAN JUAN | 2021-08-22 12:28 | 2021-08-22 13:52 | 1026 | 001:24 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | R21082200031 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 84 | 2021-08-22 | 86184 | keep | 0 | Aug | 2021 | 0.0587 | 0.0006988 | Sustained | TRUE | TRUE | Not_TMED_Event | 1026
SAN JUAN | 2021-08-22 12:28 | 2021-08-22 14:45 | 3046 | 002:17 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | R21082200032 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 137 | 2021-08-22 | 417302 | keep | 0 | Aug | 2021 | 0.28422 | 0.0020746 | Sustained | TRUE | TRUE | Not_TMED_Event | 3046
SAN JUAN | 2021-08-22 12:28 | 2021-08-22 14:45 | 2891 | 002:17 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | R21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 137 | 2021-08-22 | 396067 | keep | 0 | Aug | 2021 | 0.26976 | 0.001969 | Sustained | TRUE | TRUE | Not_TMED_Event | 2891
SAN JUAN | 2021-08-22 12:28 | 2021-08-22 13:52 | 2053 | 001:24 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | R21082200030 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 84 | 2021-08-22 | 172452 | keep | 0 | Aug | 2021 | 0.11746 | 0.0013983 | Sustained | TRUE | TRUE | Not_TMED_Event | 2053
SAN JUAN | 2021-08-22 12:28 | 2021-08-22 12:39 | 614 | 000:11 | S | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | R21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 11 | 2021-08-22 | 6754 | keep | 0 | Aug | 2021 | 0.0046001 | 0.00041819 | Sustained | TRUE | TRUE | Not_TMED_Event | 614
SAN JUAN | 2021-08-22 12:28 | 2021-08-22 12:39 | 770 | 000:11 | S | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | S21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 11 | 2021-08-22 | 8470 | keep | 0 | Aug | 2021 | 0.0057689 | 0.00052444 | Sustained | TRUE | TRUE | Not_TMED_Event | 770
SAN JUAN | 2021-08-22 12:28 | 2021-08-22 12:39 | 1271 | 000:11 | S | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | S21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 11 | 2021-08-22 | 13981 | keep | 0 | Aug | 2021 | 0.0095224 | 0.00086567 | Sustained | TRUE | TRUE | Not_TMED_Event | 1271
SAN JUAN | 2021-08-22 12:28 | 2021-08-22 12:39 | 247 | 000:11 | S | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | R21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 11 | 2021-08-22 | 2717 | keep | 0 | Aug | 2021 | 0.0018505 | 0.00016823 | Sustained | TRUE | TRUE | Not_TMED_Event | 247
BAYAMON | 2021-08-22 12:28 | 2021-08-22 13:40 | 2466 | 001:12 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | S21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 72 | 2021-08-22 | 177552 | keep | 0 | Aug | 2021 | 0.12093 | 0.0016796 | Sustained | TRUE | TRUE | Not_TMED_Event | 2466
BAYAMON | 2021-08-22 12:28 | 2021-08-22 13:38 | 3 | 001:10 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | S21082200097 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 70 | 2021-08-22 | 210 | keep | 0 | Aug | 2021 | 0.00014303 | 2.0433e-06 | Sustained | TRUE | TRUE | Not_TMED_Event | 3
FAJARDO | 2021-08-22 12:28 | 2021-08-22 14:43 | 1234 | 002:15 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | R21082200035 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 135 | 2021-08-22 | 166590 | keep | 0 | Aug | 2021 | 0.11346 | 0.00084047 | Sustained | TRUE | TRUE | Not_TMED_Event | 1234
FAJARDO | 2021-08-22 12:28 | 2021-08-22 14:44 | 693 | 002:16 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | R21082200036 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 136 | 2021-08-22 | 94248 | keep | 0 | Aug | 2021 | 0.064192 | 0.000472 | Sustained | TRUE | TRUE | Not_TMED_Event | 693
HUMACAO | 2021-08-22 12:28 | 2021-08-22 13:51 | 2354 | 001:23 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 83 | 2021-08-22 | 195382 | keep | 0 | Aug | 2021 | 0.13307 | 0.0016033 | Sustained | TRUE | TRUE | Not_TMED_Event | 2354
HUMACAO | 2021-08-22 12:28 | 2021-08-22 13:51 | 3025 | 001:23 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 83 | 2021-08-22 | 251075 | keep | 0 | Aug | 2021 | 0.17101 | 0.0020603 | Sustained | TRUE | TRUE | Not_TMED_Event | 3025
CAGUAS | 2021-08-22 12:28 | 2021-08-22 13:50 | 638 | 001:22 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200083 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 82 | 2021-08-22 | 52316 | keep | 0 | Aug | 2021 | 0.035632 | 0.00043454 | Sustained | TRUE | TRUE | Not_TMED_Event | 638
CAGUAS | 2021-08-22 12:28 | 2021-08-22 13:46 | 2448 | 001:18 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200081 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 78 | 2021-08-22 | 190944 | keep | 0 | Aug | 2021 | 0.13005 | 0.0016673 | Sustained | TRUE | TRUE | Not_TMED_Event | 2448
CAGUAS | 2021-08-22 12:28 | 2021-08-22 13:46 | 128 | 001:18 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 LLEVA LA CARGA DEL 3009-03 Y 3009-04 | C21082200082 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 78 | 2021-08-22 | 9984 | keep | 0 | Aug | 2021 | 0.0068001 | 8.718e-05 | Sustained | TRUE | TRUE | Not_TMED_Event | 128
CAGUAS | 2021-08-22 12:28 | 2021-08-22 13:46 | 273 | 001:18 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 CARGA POR EL 3009-02 | C21082200082 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 78 | 2021-08-22 | 21294 | keep | 0 | Aug | 2021 | 0.014503 | 0.00018594 | Sustained | TRUE | TRUE | Not_TMED_Event | 273
CAGUAS | 2021-08-22 12:28 | 2021-08-22 13:46 | 1772 | 001:18 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 CARGA POR EL 3009-02 | C21082200082 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 78 | 2021-08-22 | 138216 | keep | 0 | Aug | 2021 | 0.094138 | 0.0012069 | Sustained | TRUE | TRUE | Not_TMED_Event | 1772
CAGUAS | 2021-08-22 12:28 | 2021-08-22 13:47 | 1228 | 001:19 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200078 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 79 | 2021-08-22 | 97012 | keep | 0 | Aug | 2021 | 0.066074 | 0.00083639 | Sustained | TRUE | TRUE | Not_TMED_Event | 1228
CAGUAS | 2021-08-22 12:28 | 2021-08-22 13:47 | 1271 | 001:19 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200079 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 79 | 2021-08-22 | 100409 | keep | 0 | Aug | 2021 | 0.068388 | 0.00086567 | Sustained | TRUE | TRUE | Not_TMED_Event | 1271
CAGUAS | 2021-08-22 12:28 | 2021-08-22 13:47 | 1893 | 001:19 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200077 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 79 | 2021-08-22 | 149547 | keep | 0 | Aug | 2021 | 0.10186 | 0.0012893 | Sustained | TRUE | TRUE | Not_TMED_Event | 1893
CAGUAS | 2021-08-22 12:28 | 2021-08-22 13:49 | 1 | 001:21 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200104 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 81 | 2021-08-22 | 81 | keep | 0 | Aug | 2021 | 5.5169e-05 | 6.811e-07 | Sustained | TRUE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-08-22 12:28 | 2021-08-22 13:49 | 3108 | 001:21 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200085 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 81 | 2021-08-22 | 251748 | keep | 0 | Aug | 2021 | 0.17146 | 0.0021168 | Sustained | TRUE | TRUE | Not_TMED_Event | 3108
CAGUAS | 2021-08-22 12:28 | 2021-08-22 13:49 | 958 | 001:21 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 LLEVA LA CARGA DEL 3202-01 | C21082200084 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 81 | 2021-08-22 | 77598 | keep | 0 | Aug | 2021 | 0.052852 | 0.00065249 | Sustained | TRUE | TRUE | Not_TMED_Event | 958
CAGUAS | 2021-08-22 12:28 | 2021-08-22 13:49 | 1725 | 001:21 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 CARGA POR EL 3201-03 | C21082200084 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 81 | 2021-08-22 | 139725 | keep | 0 | Aug | 2021 | 0.095166 | 0.0011749 | Sustained | TRUE | TRUE | Not_TMED_Event | 1725
CAGUAS | 2021-08-22 12:28 | 2021-08-22 12:40 | 4390 | 000:12 | S | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200119 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 12 | 2021-08-22 | 52680 | keep | 0 | Aug | 2021 | 0.03588 | 0.00299 | Sustained | TRUE | TRUE | Not_TMED_Event | 4390
CAGUAS | 2021-08-22 12:28 | 2021-08-22 12:40 | 2092 | 000:12 | S | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200119 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 12 | 2021-08-22 | 25104 | keep | 0 | Aug | 2021 | 0.017098 | 0.0014249 | Sustained | TRUE | TRUE | Not_TMED_Event | 2092
CAGUAS | 2021-08-22 12:28 | 2021-08-22 12:40 | 540 | 000:12 | S | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200119 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 12 | 2021-08-22 | 6480 | keep | 0 | Aug | 2021 | 0.0044135 | 0.00036779 | Sustained | TRUE | TRUE | Not_TMED_Event | 540
CAGUAS | 2021-08-22 12:28 | 2021-08-22 12:40 | 131 | 000:12 | S | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200119 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 12 | 2021-08-22 | 1572 | keep | 0 | Aug | 2021 | 0.0010707 | 8.9224e-05 | Sustained | TRUE | TRUE | Not_TMED_Event | 131
CAGUAS | 2021-08-22 12:28 | 2021-08-22 12:40 | 2281 | 000:12 | S | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200119 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 12 | 2021-08-22 | 27372 | keep | 0 | Aug | 2021 | 0.018643 | 0.0015536 | Sustained | TRUE | TRUE | Not_TMED_Event | 2281
CAGUAS | 2021-08-22 12:28 | 2021-08-22 12:40 | 1569 | 000:12 | S | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200119 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 12 | 2021-08-22 | 18828 | keep | 0 | Aug | 2021 | 0.012824 | 0.0010686 | Sustained | TRUE | TRUE | Not_TMED_Event | 1569
CAGUAS | 2021-08-22 12:28 | 2021-08-22 12:40 | 2417 | 000:12 | S | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200119 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 12 | 2021-08-22 | 29004 | keep | 0 | Aug | 2021 | 0.019754 | 0.0016462 | Sustained | TRUE | TRUE | Not_TMED_Event | 2417
PONCE | 2021-08-22 12:28 | 2021-08-22 13:39 | 2379 | 001:11 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | P21082200040 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 71 | 2021-08-22 | 168909 | keep | 0 | Aug | 2021 | 0.11504 | 0.0016203 | Sustained | TRUE | TRUE | Not_TMED_Event | 2379
PONCE | 2021-08-22 12:28 | 2021-08-22 13:39 | 11 | 001:11 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | P21082200040 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 71 | 2021-08-22 | 781 | keep | 0 | Aug | 2021 | 0.00053194 | 7.492e-06 | Sustained | TRUE | TRUE | Not_TMED_Event | 11
YAUCO | 2021-08-22 12:28 | 2021-08-22 13:39 | 1475 | 001:11 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | P21082200042 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 71 | 2021-08-22 | 104725 | keep | 0 | Aug | 2021 | 0.071328 | 0.0010046 | Sustained | TRUE | TRUE | Not_TMED_Event | 1475
YAUCO | 2021-08-22 12:28 | 2021-08-22 13:39 | 661 | 001:11 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | P21082200042 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 71 | 2021-08-22 | 46931 | keep | 0 | Aug | 2021 | 0.031964 | 0.0004502 | Sustained | TRUE | TRUE | Not_TMED_Event | 661
ARECIBO | 2021-08-22 12:28 | 2021-08-22 12:39 | 2694 | 000:11 | S | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | A21082200063 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 11 | 2021-08-22 | 29634 | keep | 0 | Aug | 2021 | 0.020184 | 0.0018349 | Sustained | TRUE | TRUE | Not_TMED_Event | 2694
ARECIBO | 2021-08-22 12:28 | 2021-08-22 12:39 | 2228 | 000:11 | S | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | A21082200063 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 11 | 2021-08-22 | 24508 | keep | 0 | Aug | 2021 | 0.016692 | 0.0015175 | Sustained | TRUE | TRUE | Not_TMED_Event | 2228
ARECIBO | 2021-08-22 12:28 | 2021-08-22 12:39 | 438 | 000:11 | S | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | A21082200063 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 11 | 2021-08-22 | 4818 | keep | 0 | Aug | 2021 | 0.0032815 | 0.00029832 | Sustained | TRUE | TRUE | Not_TMED_Event | 438
BAYAMON | 2021-08-22 12:30 | 2021-08-22 13:42 | 679 | 001:12 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200029 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 72 | 2021-08-22 | 48888 | keep | 0 | Aug | 2021 | 0.033297 | 0.00046246 | Sustained | TRUE | TRUE | Not_TMED_Event | 679
BAYAMON | 2021-08-22 12:30 | 2021-08-22 13:42 | 67 | 001:12 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 CARGA POR EL 1705-05 | B21082200029 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 72 | 2021-08-22 | 4824 | keep | 0 | Aug | 2021 | 0.0032856 | 4.5633e-05 | Sustained | TRUE | TRUE | Not_TMED_Event | 67
BAYAMON | 2021-08-22 12:30 | 2021-08-22 13:42 | 637 | 001:12 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200029 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 72 | 2021-08-22 | 45864 | keep | 0 | Aug | 2021 | 0.031238 | 0.00043386 | Sustained | TRUE | TRUE | Not_TMED_Event | 637
BAYAMON | 2021-08-22 12:30 | 2021-08-22 13:42 | 2402 | 001:12 | S | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | S21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 72 | 2021-08-22 | 172944 | keep | 0 | Aug | 2021 | 0.11779 | 0.001636 | Sustained | TRUE | TRUE | Not_TMED_Event | 2402
BAYAMON | 2021-08-22 12:30 | 2021-08-22 13:42 | 1533 | 001:12 | S | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | S21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 72 | 2021-08-22 | 110376 | keep | 0 | Aug | 2021 | 0.075177 | 0.0010441 | Sustained | TRUE | TRUE | Not_TMED_Event | 1533
BAYAMON | 2021-08-22 12:30 | 2021-08-22 13:42 | 2364 | 001:12 | S | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | S21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 72 | 2021-08-22 | 170208 | keep | 0 | Aug | 2021 | 0.11593 | 0.0016101 | Sustained | TRUE | TRUE | Not_TMED_Event | 2364
BAYAMON | 2021-08-22 12:30 | 2021-08-22 13:34 | 5809 | 001:04 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 64 | 2021-08-22 | 371776 | keep | 0 | Aug | 2021 | 0.25321 | 0.0039565 | Sustained | TRUE | TRUE | Not_TMED_Event | 5809
BAYAMON | 2021-08-22 12:30 | 2021-08-22 13:34 | 3941 | 001:04 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 64 | 2021-08-22 | 252224 | keep | 0 | Aug | 2021 | 0.17179 | 0.0026842 | Sustained | TRUE | TRUE | Not_TMED_Event | 3941
BAYAMON | 2021-08-22 12:30 | 2021-08-22 13:34 | 3871 | 001:04 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 64 | 2021-08-22 | 247744 | keep | 0 | Aug | 2021 | 0.16874 | 0.0026365 | Sustained | TRUE | TRUE | Not_TMED_Event | 3871
BAYAMON | 2021-08-22 12:30 | 2021-08-22 13:34 | 5191 | 001:04 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 64 | 2021-08-22 | 332224 | keep | 0 | Aug | 2021 | 0.22628 | 0.0035356 | Sustained | TRUE | TRUE | Not_TMED_Event | 5191
BAYAMON | 2021-08-22 12:30 | 2021-08-22 13:34 | 4533 | 001:04 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 64 | 2021-08-22 | 290112 | keep | 0 | Aug | 2021 | 0.19759 | 0.0030874 | Sustained | TRUE | TRUE | Not_TMED_Event | 4533
BAYAMON | 2021-08-22 12:30 | 2021-08-22 13:34 | 911 | 001:04 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 64 | 2021-08-22 | 58304 | keep | 0 | Aug | 2021 | 0.039711 | 0.00062048 | Sustained | TRUE | TRUE | Not_TMED_Event | 911
BAYAMON | 2021-08-22 12:30 | 2021-08-22 13:34 | 4431 | 001:04 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 64 | 2021-08-22 | 283584 | keep | 0 | Aug | 2021 | 0.19315 | 0.0030179 | Sustained | TRUE | TRUE | Not_TMED_Event | 4431
BAYAMON | 2021-08-22 12:30 | 2021-08-22 13:34 | 1362 | 001:04 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 64 | 2021-08-22 | 87168 | keep | 0 | Aug | 2021 | 0.05937 | 0.00092765 | Sustained | TRUE | TRUE | Not_TMED_Event | 1362
BAYAMON | 2021-08-22 12:30 | 2021-08-22 13:34 | 341 | 001:04 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 64 | 2021-08-22 | 21824 | keep | 0 | Aug | 2021 | 0.014864 | 0.00023225 | Sustained | TRUE | TRUE | Not_TMED_Event | 341
BAYAMON | 2021-08-22 12:30 | 2021-08-22 12:38 | 3597 | 000:08 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 8 | 2021-08-22 | 28776 | keep | 0 | Aug | 2021 | 0.019599 | 0.0024499 | Sustained | TRUE | TRUE | Not_TMED_Event | 3597
BAYAMON | 2021-08-22 12:30 | 2021-08-22 12:38 | 492 | 000:08 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 8 | 2021-08-22 | 3936 | keep | 0 | Aug | 2021 | 0.0026808 | 0.0003351 | Sustained | TRUE | TRUE | Not_TMED_Event | 492
BAYAMON | 2021-08-22 12:30 | 2021-08-22 12:38 | 4028 | 000:08 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 8 | 2021-08-22 | 32224 | keep | 0 | Aug | 2021 | 0.021948 | 0.0027435 | Sustained | TRUE | TRUE | Not_TMED_Event | 4028
BAYAMON | 2021-08-22 12:30 | 2021-08-22 12:38 | 2617 | 000:08 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 8 | 2021-08-22 | 20936 | keep | 0 | Aug | 2021 | 0.014259 | 0.0017824 | Sustained | TRUE | TRUE | Not_TMED_Event | 2617
BAYAMON | 2021-08-22 12:30 | 2021-08-22 13:42 | 6136 | 001:12 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 CARGA TRANSFERIDA AL 1709-01 | B21082200000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 72 | 2021-08-22 | 441792 | keep | 0 | Aug | 2021 | 0.3009 | 0.0041792 | Sustained | TRUE | TRUE | Not_TMED_Event | 6136
BAYAMON | 2021-08-22 12:30 | 2021-08-22 13:42 | 1 | 001:12 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 CARGA TRANSFERIDA AL 1709-02 | B21082200000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 72 | 2021-08-22 | 72 | keep | 0 | Aug | 2021 | 4.9039e-05 | 6.811e-07 | Sustained | TRUE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-08-22 12:30 | 2021-08-22 13:42 | 3798 | 001:12 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200026 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 72 | 2021-08-22 | 273456 | keep | 0 | Aug | 2021 | 0.18625 | 0.0025868 | Sustained | TRUE | TRUE | Not_TMED_Event | 3798
BAYAMON | 2021-08-22 12:30 | 2021-08-22 13:42 | 4622 | 001:12 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200026 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 72 | 2021-08-22 | 332784 | keep | 0 | Aug | 2021 | 0.22666 | 0.003148 | Sustained | TRUE | TRUE | Not_TMED_Event | 4622
BAYAMON | 2021-08-22 12:30 | 2021-08-22 13:42 | 4089 | 001:12 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 & 4 PALO SECO Y 6 DE SAN JUAN DEBIDO A AVERIA LINEA 38900 | B21082200026 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 72 | 2021-08-22 | 294408 | keep | 0 | Aug | 2021 | 0.20052 | 0.002785 | Sustained | TRUE | TRUE | Not_TMED_Event | 4089
VEGA BAJA | 2021-08-22 12:30 | 2021-08-22 13:42 | 603 | 001:12 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200024 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 72 | 2021-08-22 | 43416 | keep | 0 | Aug | 2021 | 0.02957 | 0.0004107 | Sustained | TRUE | TRUE | Not_TMED_Event | 603
VEGA BAJA | 2021-08-22 12:30 | 2021-08-22 13:42 | 6 | 001:12 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200024 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 72 | 2021-08-22 | 432 | keep | 0 | Aug | 2021 | 0.00029423 | 4.0866e-06 | Sustained | TRUE | TRUE | Not_TMED_Event | 6
BAYAMON | 2021-08-22 12:30 | 2021-08-22 14:28 | 3070 | 001:58 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 118 | 2021-08-22 | 362260 | keep | 0 | Aug | 2021 | 0.24673 | 0.002091 | Sustained | TRUE | TRUE | Not_TMED_Event | 3070
BAYAMON | 2021-08-22 12:30 | 2021-08-22 14:28 | 2735 | 001:58 | S | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 118 | 2021-08-22 | 322730 | keep | 0 | Aug | 2021 | 0.21981 | 0.0018628 | Sustained | TRUE | TRUE | Not_TMED_Event | 2735
BAYAMON | 2021-08-22 12:30 | 2021-08-22 14:28 | 1070 | 001:58 | S | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 118 | 2021-08-22 | 126260 | keep | 0 | Aug | 2021 | 0.085995 | 0.00072877 | Sustained | TRUE | TRUE | Not_TMED_Event | 1070
BAYAMON | 2021-08-22 12:30 | 2021-08-22 14:37 | 1647 | 002:07 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 127 | 2021-08-22 | 209169 | keep | 0 | Aug | 2021 | 0.14246 | 0.0011218 | Sustained | TRUE | TRUE | Not_TMED_Event | 1647
BAYAMON | 2021-08-22 12:30 | 2021-08-22 14:37 | 3295 | 002:07 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 127 | 2021-08-22 | 418465 | keep | 0 | Aug | 2021 | 0.28501 | 0.0022442 | Sustained | TRUE | TRUE | Not_TMED_Event | 3295
BAYAMON | 2021-08-22 12:30 | 2021-08-22 14:37 | 1180 | 002:07 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 127 | 2021-08-22 | 149860 | keep | 0 | Aug | 2021 | 0.10207 | 0.00080369 | Sustained | TRUE | TRUE | Not_TMED_Event | 1180
BAYAMON | 2021-08-22 12:30 | 2021-08-22 14:37 | 320 | 002:07 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | B21082200000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 127 | 2021-08-22 | 40640 | keep | 0 | Aug | 2021 | 0.02768 | 0.00021795 | Sustained | TRUE | TRUE | Not_TMED_Event | 320
BAYAMON | 2021-08-22 12:30 | 2021-08-22 14:37 | 2234 | 002:07 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 DE PALO SECO LA UNIDAD 6 DE SAN JUAN Y UNIDAD 5 DE VAPOR EN SAN JUAN DEBIDO A AVERIA LINEA 38900 | B21082200000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 127 | 2021-08-22 | 283718 | keep | 0 | Aug | 2021 | 0.19324 | 0.0015216 | Sustained | TRUE | TRUE | Not_TMED_Event | 2234
BAYAMON | 2021-08-22 12:32 | 2021-08-22 13:49 | 790 | 001:17 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | S21082200098 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 77 | 2021-08-22 | 60830 | keep | 0 | Aug | 2021 | 0.041431 | 0.00053807 | Sustained | TRUE | TRUE | Not_TMED_Event | 790
BAYAMON | 2021-08-22 12:32 | 2021-08-22 13:49 | 193 | 001:17 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | S21082200100 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 77 | 2021-08-22 | 14861 | keep | 0 | Aug | 2021 | 0.010122 | 0.00013145 | Sustained | TRUE | TRUE | Not_TMED_Event | 193
BAYAMON | 2021-08-22 12:32 | 2021-08-22 13:49 | 433 | 001:17 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | S21082200094 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 77 | 2021-08-22 | 33341 | keep | 0 | Aug | 2021 | 0.022708 | 0.00029491 | Sustained | TRUE | TRUE | Not_TMED_Event | 433
BAYAMON | 2021-08-22 12:32 | 2021-08-22 13:50 | 271 | 001:18 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | S21082200099 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 78 | 2021-08-22 | 21138 | keep | 0 | Aug | 2021 | 0.014397 | 0.00018458 | Sustained | TRUE | TRUE | Not_TMED_Event | 271
BAYAMON | 2021-08-22 12:32 | 2021-08-22 13:42 | 222 | 001:10 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | S21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 70 | 2021-08-22 | 15540 | keep | 0 | Aug | 2021 | 0.010584 | 0.0001512 | Sustained | TRUE | TRUE | Not_TMED_Event | 222
BAYAMON | 2021-08-22 12:32 | 2021-08-22 13:42 | 4456 | 001:10 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | S21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 70 | 2021-08-22 | 311920 | keep | 0 | Aug | 2021 | 0.21245 | 0.003035 | Sustained | TRUE | TRUE | Not_TMED_Event | 4456
FAJARDO | 2021-08-22 12:32 | 2021-08-22 14:44 | 2041 | 002:12 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | R21082200033 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 132 | 2021-08-22 | 269412 | keep | 0 | Aug | 2021 | 0.1835 | 0.0013901 | Sustained | TRUE | TRUE | Not_TMED_Event | 2041
FAJARDO | 2021-08-22 12:32 | 2021-08-22 14:44 | 625 | 002:12 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | R21082200037 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 132 | 2021-08-22 | 82500 | keep | 0 | Aug | 2021 | 0.05619 | 0.00042568 | Sustained | TRUE | TRUE | Not_TMED_Event | 625
FAJARDO | 2021-08-22 12:32 | 2021-08-22 14:44 | 1463 | 002:12 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | R21082200034 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 132 | 2021-08-22 | 193116 | keep | 0 | Aug | 2021 | 0.13153 | 0.00099644 | Sustained | TRUE | TRUE | Not_TMED_Event | 1463
FAJARDO | 2021-08-22 12:32 | 2021-08-22 14:43 | 76 | 002:11 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | R21082200035 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 131 | 2021-08-22 | 9956 | keep | 0 | Aug | 2021 | 0.006781 | 5.1763e-05 | Sustained | TRUE | TRUE | Not_TMED_Event | 76
FAJARDO | 2021-08-22 12:32 | 2021-08-22 14:44 | 2286 | 002:12 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | R21082200036 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 132 | 2021-08-22 | 301752 | keep | 0 | Aug | 2021 | 0.20552 | 0.001557 | Sustained | TRUE | TRUE | Not_TMED_Event | 2286
CANOVANAS | 2021-08-22 12:32 | 2021-08-22 13:38 | 2039 | 001:06 | S | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | R21082200044 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 66 | 2021-08-22 | 134574 | keep | 0 | Aug | 2021 | 0.091658 | 0.0013888 | Sustained | TRUE | TRUE | Not_TMED_Event | 2039
CANOVANAS | 2021-08-22 12:32 | 2021-08-22 13:38 | 4188 | 001:06 | S | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | R21082200044 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 66 | 2021-08-22 | 276408 | keep | 0 | Aug | 2021 | 0.18826 | 0.0028524 | Sustained | TRUE | TRUE | Not_TMED_Event | 4188
CANOVANAS | 2021-08-22 12:32 | 2021-08-22 13:38 | 4085 | 001:06 | S | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | R21082200044 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 66 | 2021-08-22 | 269610 | keep | 0 | Aug | 2021 | 0.18363 | 0.0027823 | Sustained | TRUE | TRUE | Not_TMED_Event | 4085
HUMACAO | 2021-08-22 12:32 | 2021-08-22 14:44 | 1593 | 002:12 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 132 | 2021-08-22 | 210276 | keep | 0 | Aug | 2021 | 0.14322 | 0.001085 | Sustained | TRUE | TRUE | Not_TMED_Event | 1593
HUMACAO | 2021-08-22 12:32 | 2021-08-22 14:44 | 3420 | 002:12 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 132 | 2021-08-22 | 451440 | keep | 0 | Aug | 2021 | 0.30747 | 0.0023293 | Sustained | TRUE | TRUE | Not_TMED_Event | 3420
HUMACAO | 2021-08-22 12:32 | 2021-08-22 14:44 | 4 | 002:12 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 132 | 2021-08-22 | 528 | keep | 0 | Aug | 2021 | 0.00035962 | 2.7244e-06 | Sustained | TRUE | TRUE | Not_TMED_Event | 4
HUMACAO | 2021-08-22 12:32 | 2021-08-22 14:44 | 3 | 002:12 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 132 | 2021-08-22 | 396 | keep | 0 | Aug | 2021 | 0.00026971 | 2.0433e-06 | Sustained | TRUE | TRUE | Not_TMED_Event | 3
CAGUAS | 2021-08-22 12:32 | 2021-08-22 14:48 | 1261 | 002:16 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200091 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 136 | 2021-08-22 | 171496 | keep | 0 | Aug | 2021 | 0.11681 | 0.00085886 | Sustained | TRUE | TRUE | Not_TMED_Event | 1261
CAGUAS | 2021-08-22 12:32 | 2021-08-22 13:46 | 1922 | 001:14 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200090 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 74 | 2021-08-22 | 142228 | keep | 0 | Aug | 2021 | 0.096871 | 0.0013091 | Sustained | TRUE | TRUE | Not_TMED_Event | 1922
CAGUAS | 2021-08-22 12:32 | 2021-08-22 14:48 | 853 | 002:16 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200092 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 136 | 2021-08-22 | 116008 | keep | 0 | Aug | 2021 | 0.079013 | 0.00058097 | Sustained | TRUE | TRUE | Not_TMED_Event | 853
CAGUAS | 2021-08-22 12:32 | 2021-08-22 14:48 | 2900 | 002:16 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 136 | 2021-08-22 | 394400 | keep | 0 | Aug | 2021 | 0.26862 | 0.0019752 | Sustained | TRUE | TRUE | Not_TMED_Event | 2900
CAGUAS | 2021-08-22 12:32 | 2021-08-22 14:48 | 2178 | 002:16 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | C21082200098 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 136 | 2021-08-22 | 296208 | keep | 0 | Aug | 2021 | 0.20175 | 0.0014834 | Sustained | TRUE | TRUE | Not_TMED_Event | 2178
GUAYAMA | 2021-08-22 12:32 | 2021-08-22 13:39 | 1173 | 001:07 | S | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | P210822000XX | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 67 | 2021-08-22 | 78591 | keep | 0 | Aug | 2021 | 0.053528 | 0.00079892 | Sustained | TRUE | TRUE | Not_TMED_Event | 1173
GUAYAMA | 2021-08-22 12:32 | 2021-08-22 13:39 | 215 | 001:07 | S | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | P210822000XX | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 67 | 2021-08-22 | 14405 | keep | 0 | Aug | 2021 | 0.0098112 | 0.00014644 | Sustained | TRUE | TRUE | Not_TMED_Event | 215
MAYAGÃœEZ | 2021-08-22 12:32 | 2021-08-22 13:39 | 6285 | 001:07 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | M21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 67 | 2021-08-22 | 421095 | keep | 0 | Aug | 2021 | 0.28681 | 0.0042807 | Sustained | TRUE | TRUE | Not_TMED_Event | 6285
MAYAGÃœEZ | 2021-08-22 12:32 | 2021-08-22 13:39 | 2225 | 001:07 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | M21082200036 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 67 | 2021-08-22 | 149075 | keep | 0 | Aug | 2021 | 0.10153 | 0.0015154 | Sustained | TRUE | TRUE | Not_TMED_Event | 2225
ARECIBO | 2021-08-22 12:32 | 2021-08-22 13:41 | 316 | 001:09 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | A21082200067 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 69 | 2021-08-22 | 21804 | keep | 0 | Aug | 2021 | 0.014851 | 0.00021523 | Sustained | TRUE | TRUE | Not_TMED_Event | 316
ARECIBO | 2021-08-22 12:32 | 2021-08-22 13:41 | 1227 | 001:09 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | A21082200065 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 69 | 2021-08-22 | 84663 | keep | 0 | Aug | 2021 | 0.057664 | 0.0008357 | Sustained | TRUE | TRUE | Not_TMED_Event | 1227
ARECIBO | 2021-08-22 12:32 | 2021-08-22 13:41 | 3431 | 001:09 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | A21082200066 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 69 | 2021-08-22 | 236739 | keep | 0 | Aug | 2021 | 0.16124 | 0.0023368 | Sustained | TRUE | TRUE | Not_TMED_Event | 3431
BAYAMON | 2021-08-22 12:33 | 2021-08-22 13:42 | 2435 | 001:09 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | S21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 69 | 2021-08-22 | 168015 | keep | 0 | Aug | 2021 | 0.11443 | 0.0016585 | Sustained | TRUE | TRUE | Not_TMED_Event | 2435
BAYAMON | 2021-08-22 12:33 | 2021-08-22 13:42 | 1139 | 001:09 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | S21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 69 | 2021-08-22 | 78591 | keep | 0 | Aug | 2021 | 0.053528 | 0.00077577 | Sustained | TRUE | TRUE | Not_TMED_Event | 1139
BAYAMON | 2021-08-22 12:33 | 2021-08-22 13:42 | 2956 | 001:09 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR DISPARO UNIDADES 3 Y 4 PALO SECO, 5 Y 6 DE SAN JUAN JUNTO A DISPARO DE LINEA 38900 | S21082200000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 69 | 2021-08-22 | 203964 | keep | 0 | Aug | 2021 | 0.13892 | 0.0020133 | Sustained | TRUE | TRUE | Not_TMED_Event | 2956
MAYAGÃœEZ | 2021-08-22 12:33 | 2021-08-22 14:23 | 5 | 001:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR FUERTES VIENTOS | M21082200037 | New_Event | Bad Weather | Include | Include | Weather | 110 | 2021-08-22 | 550 | keep | 0 | Aug | 2021 | 0.0003746 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
SAN JUAN | 2021-08-22 12:39 | 2021-08-22 15:30 | 50 | 002:51 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21082200020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 171 | 2021-08-22 | 8550 | keep | 0 | Aug | 2021 | 0.0058234 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-08-22 12:40 | 2021-08-22 13:19 | 50 | 000:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO CORTE DE LINEA PARA REPARAR CONDUCTOR | C21082100116 | Partial_restoration | Wire Down | Include | Include | Equipment | 39 | 2021-08-22 | 1950 | keep | 0 | Aug | 2021 | 0.0013281 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-08-22 12:40 | 2021-08-22 13:10 | 6 | 000:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REGULARLO Y REPARO BAJANTE SECUNDARIO | C21082100077 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 30 | 2021-08-22 | 180 | keep | 0 | Aug | 2021 | 0.0001226 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-22 13:00 | 2021-08-22 17:06 | 60 | 004:06 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 246 | 2021-08-22 | 14760 | keep | 0 | Aug | 2021 | 0.010053 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-08-22 13:03 | 2021-08-22 13:04 | 959 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-22 | 959 | keep | 0 | Aug | 2021 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
ARECIBO | 2021-08-22 13:07 | 2021-08-22 15:09 | 1628 | 002:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO AVERIA Y SE CERRO INTERRUPTOR | A21082200078 | New_Event | Wire Down | Include | Include | Equipment | 122 | 2021-08-22 | 198616 | keep | 0 | Aug | 2021 | 0.13528 | 0.0011088 | Sustained | FALSE | FALSE | Not_TMED_Event | 1628
HUMACAO | 2021-08-22 13:09 | 2021-08-22 13:10 | 1835 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21082200113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-22 | 1835 | keep | 0 | Aug | 2021 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
SAN JUAN | 2021-08-22 13:16 | 2021-08-22 13:50 | 68 | 000:34 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S21082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 34 | 2021-08-22 | 2312 | keep | 0 | Aug | 2021 | 0.0015747 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
BAYAMON | 2021-08-22 13:16 | 2021-08-22 13:50 | 68 | 000:34 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1520-05 | S21082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 34 | 2021-08-22 | 2312 | keep | 0 | Aug | 2021 | 0.0015747 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
BAYAMON | 2021-08-22 13:16 | 2021-08-22 13:50 | 68 | 000:34 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1520-05 | S21082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 34 | 2021-08-22 | 2312 | keep | 0 | Aug | 2021 | 0.0015747 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
BAYAMON | 2021-08-22 13:16 | 2021-08-22 13:50 | 68 | 000:34 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA CARGA DEL 1520-01 Y 1520-04 | S21082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 34 | 2021-08-22 | 2312 | keep | 0 | Aug | 2021 | 0.0015747 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
BAYAMON | 2021-08-22 13:18 | 2021-08-22 13:19 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1105-02 | S21082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-22 | 308 | keep | 0 | Aug | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2021-08-22 13:18 | 2021-08-22 13:19 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVANDO 1105-01 Y 1133-04 | S21082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-22 | 308 | keep | 0 | Aug | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2021-08-22 13:18 | 2021-08-22 13:19 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1105-02 | S21082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-22 | 308 | keep | 0 | Aug | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2021-08-22 13:34 | 2021-08-22 19:22 | 30 | 005:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | ACCIDENTE DE AUTO SE REEMPLAZO DOS POSTES 45', TRANSFORMADOR 50 KVA Y SE LEVANTO CONDUCTOR | B21082200007 | New_Event |  |  | Include | Wildlife | 348 | 2021-08-22 | 10440 | keep | 0 | Aug | 2021 | 0.0071106 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-08-22 13:42 | 2021-08-22 22:30 | 150 | 008:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CONVERTIDOR Y SE REMPLAZO PORTAFUSIBLES CARGA TRANSFERIDA AL 1709-01 | B21082200020 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 528 | 2021-08-22 | 79200 | keep | 0 | Aug | 2021 | 0.053943 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-22 13:47 | 2021-08-23 13:48 | 30 | 024:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR Y SE REEMPLAZO AISLADOR | S21082200253 | New_Event | Wire Down | Include | Include | Equipment | 1441 | 2021-08-22 | 43230 | keep | 0 | Aug | 2021 | 0.029444 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2021-08-22 13:53 | 2021-08-22 13:54 | 257 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR RECIERRE EN OFF NO SE REPORTO CAUSA | M21082200046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-22 | 257 | keep | 0 | Aug | 2021 | 0.00017504 | 0.00017504 | Momentary | FALSE | FALSE | Not_TMED_Event | 257
BAYAMON | 2021-08-22 13:54 | 2021-08-22 14:27 | 308 | 000:33 | T | NO SE REPORTO CAUSA | RECERRO Y SE QUEDO FUERA CARGA POR EL 1105-02 | S21082200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 33 | 2021-08-22 | 10164 | keep | 0 | Aug | 2021 | 0.0069227 | 0.00020978 | Sustained | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2021-08-22 13:54 | 2021-08-22 14:27 | 308 | 000:33 | T | NO SE REPORTO CAUSA | RECERRO Y SE QUEDO FUERA LLEVA LA CARGA DEL 1105-01 Y 1133-04 | S21082200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 33 | 2021-08-22 | 10164 | keep | 0 | Aug | 2021 | 0.0069227 | 0.00020978 | Sustained | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2021-08-22 13:54 | 2021-08-22 14:27 | 308 | 000:33 | T | NO SE REPORTO CAUSA | RECERRO Y SE QUEDO FUERA CARGA POR EL 1105-02 | S21082200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 33 | 2021-08-22 | 10164 | keep | 0 | Aug | 2021 | 0.0069227 | 0.00020978 | Sustained | FALSE | FALSE | Not_TMED_Event | 308
PONCE | 2021-08-22 13:59 | 2021-08-22 15:19 | 10 | 001:20 | P | PARARRAYOS DEFECTUOSO | 1 X 15 EN TRANSFORMADOR PARARRAYO CRUZADO | P21082200045 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 80 | 2021-08-22 | 800 | keep | 0 | Aug | 2021 | 0.00054488 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-22 14:17 | 2021-08-22 17:06 | 80 | 002:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA | A21082200103 | New_Event | Bad Weather | Include | Include | Weather | 169 | 2021-08-22 | 13520 | keep | 0 | Aug | 2021 | 0.0092084 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-08-22 14:17 | 2021-08-23 12:15 | 100 | 021:58 | P | TRANSFORMADOR AVERIADO | 2 X 80 EN RISER TRANSFORMADOR PM DE 75 KVA AVERIADO SE SECCIONALIZO | A21082300005 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1318 | 2021-08-22 | 131800 | keep | 0 | Aug | 2021 | 0.089768 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2021-08-22 14:20 | 2021-08-22 17:45 | 85 | 003:25 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C21082200139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2021-08-22 | 17425 | keep | 0 | Aug | 2021 | 0.011868 | 5.7893e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 85
FAJARDO | 2021-08-22 14:44 | 2021-08-22 17:21 | 5 | 002:37 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21082200082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2021-08-22 | 785 | keep | 0 | Aug | 2021 | 0.00053466 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
AGUADILLA | 2021-08-22 14:51 | 2021-08-22 20:12 | 50 | 005:21 | P | ESTRUCTURA AVERIADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CRUCETA PARTIDA | M21082200053 | New_Event | Defective Pole | Include | Include | Equipment | 321 | 2021-08-22 | 16050 | keep | 0 | Aug | 2021 | 0.010932 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-22 14:54 | 2021-08-22 18:06 | 60 | 003:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | A21082200116 | New_Event | Bad Weather | Include | Include | Weather | 192 | 2021-08-22 | 11520 | keep | 0 | Aug | 2021 | 0.0078462 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-08-22 15:00 | 2021-08-22 17:32 | 60 | 002:32 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21082200182 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2021-08-22 | 9120 | keep | 0 | Aug | 2021 | 0.0062116 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
AGUADILLA | 2021-08-22 15:04 | 2021-08-22 15:05 | 569 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21082200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-22 | 569 | keep | 0 | Aug | 2021 | 0.00038754 | 0.00038754 | Momentary | FALSE | TRUE | Not_TMED_Event | 569
AGUADILLA | 2021-08-22 15:04 | 2021-08-22 15:05 | 1245 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21082200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-22 | 1245 | keep | 0 | Aug | 2021 | 0.00084796 | 0.00084796 | Momentary | FALSE | TRUE | Not_TMED_Event | 1245
AGUADILLA | 2021-08-22 15:04 | 2021-08-22 15:05 | 1155 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21082200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-22 | 1155 | keep | 0 | Aug | 2021 | 0.00078667 | 0.00078667 | Momentary | FALSE | TRUE | Not_TMED_Event | 1155
AGUADILLA | 2021-08-22 15:04 | 2021-08-22 15:05 | 3315 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21082200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-22 | 3315 | keep | 0 | Aug | 2021 | 0.0022578 | 0.0022578 | Momentary | FALSE | TRUE | Not_TMED_Event | 3315
AGUADILLA | 2021-08-22 15:04 | 2021-08-22 15:05 | 1718 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2500 | M21082200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-22 | 1718 | keep | 0 | Aug | 2021 | 0.0011701 | 0.0011701 | Momentary | FALSE | TRUE | Not_TMED_Event | 1718
ARECIBO | 2021-08-22 15:09 | 2021-08-22 18:03 | 125 | 002:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEAS CRUZADAS Y SE CERRO MACHETES | A21082200099 | Partial_restoration | Wire Down | Include | Include | Equipment | 174 | 2021-08-22 | 21750 | keep | 0 | Aug | 2021 | 0.014814 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-08-22 15:10 | 2021-08-22 20:11 | 200 | 005:01 | P | DESGANCHE | 3 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21082200054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 301 | 2021-08-22 | 60200 | keep | 0 | Aug | 2021 | 0.041002 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-08-22 15:14 | 2021-08-22 15:15 | 892 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-22 | 892 | keep | 0 | Aug | 2021 | 0.00060754 | 0.00060754 | Momentary | FALSE | FALSE | Not_TMED_Event | 892
VEGA BAJA | 2021-08-22 15:15 | 2021-08-22 18:06 | 100 | 002:51 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21082200115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2021-08-22 | 17100 | keep | 0 | Aug | 2021 | 0.011647 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-08-22 15:18 | 2021-08-22 17:57 | 12 | 002:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | R21082200067 | New_Event |  |  | Include | Wildlife | 159 | 2021-08-22 | 1908 | keep | 0 | Aug | 2021 | 0.0012995 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-08-22 15:30 | 2021-08-22 15:35 | 1000 | 000:05 | P | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR PERDIDA SISTEMAS RENOVABLES | S21082200189 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 5 | 2021-08-22 | 5000 | keep | 0 | Aug | 2021 | 0.0034055 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2021-08-22 15:30 | 2021-08-22 15:35 | 403 | 000:05 | P | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR PERDIDA SISTEMAS RENOVABLES | S21082200189 | Partial_restoration | Automatic Load Shed | Exclude | Exclude | Power supply | 5 | 2021-08-22 | 2015 | keep | 0 | Aug | 2021 | 0.0013724 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-22 15:30 | 2021-08-22 15:35 | 727 | 000:05 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR PERDIDA SISTEMAS RENOVABLES | S21082200189 | Partial_restoration | Automatic Load Shed | Exclude | Exclude | Power supply | 5 | 2021-08-22 | 3635 | keep | 0 | Aug | 2021 | 0.0024758 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-22 15:30 | 2021-08-22 15:35 | 290 | 000:05 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR PERDIDA SISTEMAS RENOVABLES | S21082200189 | Partial_restoration | Automatic Load Shed | Exclude | Exclude | Power supply | 5 | 2021-08-22 | 1450 | keep | 0 | Aug | 2021 | 0.00098759 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-22 15:30 | 2021-08-22 15:35 | 610 | 000:05 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR PERDIDA SISTEMAS RENOVABLES | S21082200189 | Partial_restoration | Automatic Load Shed | Exclude | Exclude | Power supply | 5 | 2021-08-22 | 3050 | keep | 0 | Aug | 2021 | 0.0020773 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-22 15:30 | 2021-08-22 15:36 | 679 | 000:06 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR PERDIDA DE RENOVABLES | B21082200000 | Partial_restoration | Automatic Load Shed | Exclude | Exclude | Power supply | 6 | 2021-08-22 | 4074 | keep | 0 | Aug | 2021 | 0.0027748 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-22 15:30 | 2021-08-22 15:36 | 67 | 000:06 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR PERDIDA DE RENOVABLES | B21082200000 | Partial_restoration | Automatic Load Shed | Exclude | Exclude | Power supply | 6 | 2021-08-22 | 402 | keep | 0 | Aug | 2021 | 0.0002738 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-22 15:30 | 2021-08-22 15:36 | 637 | 000:06 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR PERDIDA DE RENOVABLES | B21082200000 | Partial_restoration | Automatic Load Shed | Exclude | Exclude | Power supply | 6 | 2021-08-22 | 3822 | keep | 0 | Aug | 2021 | 0.0026031 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-22 15:30 | 2021-08-22 15:35 | 3798 | 000:05 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR PERDIDA DE RENOVABLES | B21082200000 | Partial_restoration | Automatic Load Shed | Exclude | Exclude | Power supply | 5 | 2021-08-22 | 18990 | keep | 0 | Aug | 2021 | 0.012934 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-22 15:30 | 2021-08-22 15:35 | 4622 | 000:05 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR PERDIDA DE RENOVABLES | B21082200000 | Partial_restoration | Automatic Load Shed | Exclude | Exclude | Power supply | 5 | 2021-08-22 | 23110 | keep | 0 | Aug | 2021 | 0.01574 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-22 15:30 | 2021-08-22 15:35 | 4089 | 000:05 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR PERDIDA DE RENOVABLES | B21082200000 | Partial_restoration | Automatic Load Shed | Exclude | Exclude | Power supply | 5 | 2021-08-22 | 20445 | keep | 0 | Aug | 2021 | 0.013925 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-22 15:30 | 2021-08-22 15:35 | 222 | 000:05 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR PERDIDA DE RENOVABLES. LLEVA LA CARGA DEL 1909-09 | S21082200000 | Partial_restoration | Automatic Load Shed | Exclude | Exclude | Power supply | 5 | 2021-08-22 | 1110 | keep | 0 | Aug | 2021 | 0.00075602 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-22 15:30 | 2021-08-22 15:35 | 2466 | 000:05 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR PERDIDA DE RENOVABLES | S21082200000 | Partial_restoration | Automatic Load Shed | Exclude | Exclude | Power supply | 5 | 2021-08-22 | 12330 | keep | 0 | Aug | 2021 | 0.0083979 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-22 15:30 | 2021-08-22 15:35 | 4456 | 000:05 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR PERDIDA DE RENOVABLES. CARGA POR EL 1907-03 | S21082200000 | Partial_restoration | Automatic Load Shed | Exclude | Exclude | Power supply | 5 | 2021-08-22 | 22280 | keep | 0 | Aug | 2021 | 0.015175 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-08-22 15:30 | 2021-08-22 15:39 | 2379 | 000:09 | T | RELEVO DE CARGA AUTOMATICO | RELEVO CARGA AUTOMATICO PERDIDA DE RENOVABLES | P21082200058 | Partial_restoration | Automatic Load Shed | Exclude | Exclude | Power supply | 9 | 2021-08-22 | 21411 | keep | 0 | Aug | 2021 | 0.014583 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-08-22 15:30 | 2021-08-22 15:39 | 11 | 000:09 | T | RELEVO DE CARGA AUTOMATICO | RELEVO CARGA AUTOMATICO | P21082200058 | Partial_restoration | Automatic Load Shed | Exclude | Exclude | Power supply | 9 | 2021-08-22 | 99 | keep | 0 | Aug | 2021 | 6.7428e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2021-08-22 15:30 | 2021-08-22 15:39 | 1475 | 000:09 | T | RELEVO DE CARGA AUTOMATICO | RELEVO CARGA AUTOMATICO PERDIDA DE RENOVABLES | P21082200059 | Partial_restoration | Automatic Load Shed | Exclude | Exclude | Power supply | 9 | 2021-08-22 | 13275 | keep | 0 | Aug | 2021 | 0.0090415 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2021-08-22 15:30 | 2021-08-22 15:39 | 661 | 000:09 | T | RELEVO DE CARGA AUTOMATICO | RELEVO CARGA AUTOMATICO PERDIDA DE RENOVABLES | P21082200059 | Partial_restoration | Automatic Load Shed | Exclude | Exclude | Power supply | 9 | 2021-08-22 | 5949 | keep | 0 | Aug | 2021 | 0.0040518 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-08-22 15:30 | 2021-08-22 15:35 | 603 | 000:05 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA POR PERDIDA DE RENOVABLES | B21082200000 | Partial_restoration | Automatic Load Shed | Exclude | Exclude | Power supply | 5 | 2021-08-22 | 3015 | keep | 0 | Aug | 2021 | 0.0020535 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-08-22 15:33 | 2021-08-22 15:34 | 676 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5300 | C21082200166 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-22 | 676 | keep | 0 | Aug | 2021 | 0.00046042 | 0.00046042 | Momentary | FALSE | TRUE | Not_TMED_Event | 676
HUMACAO | 2021-08-22 15:33 | 2021-08-22 15:34 | 2873 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5300 | C21082200166 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-22 | 2873 | keep | 0 | Aug | 2021 | 0.0019568 | 0.0019568 | Momentary | FALSE | TRUE | Not_TMED_Event | 2873
HUMACAO | 2021-08-22 15:33 | 2021-08-22 15:34 | 3902 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5300 | C21082200166 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-22 | 3902 | keep | 0 | Aug | 2021 | 0.0026576 | 0.0026576 | Momentary | FALSE | TRUE | Not_TMED_Event | 3902
SAN JUAN | 2021-08-22 15:36 | 2021-08-23 15:25 | 50 | 023:49 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21082200020 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 1429 | 2021-08-22 | 71450 | keep | 0 | Aug | 2021 | 0.048664 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
UTUADO | 2021-08-22 15:53 | 2021-08-22 18:29 | 75 | 002:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA | A21082200127 | New_Event | Bad Weather | Include | Include | Weather | 156 | 2021-08-22 | 11700 | keep | 0 | Aug | 2021 | 0.0079688 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
CAGUAS | 2021-08-22 15:54 | 2021-08-22 22:29 | 15 | 006:35 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21082200174 | New_Event | Vegetation Contact | Include | Include | Vegetation | 395 | 2021-08-22 | 5925 | keep | 0 | Aug | 2021 | 0.0040355 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
AGUADILLA | 2021-08-22 15:55 | 2021-08-22 23:47 | 25 | 007:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA FUERTE VIENTO | M21082200098 | New_Event | Bad Weather | Include | Include | Weather | 472 | 2021-08-22 | 11800 | keep | 0 | Aug | 2021 | 0.0080369 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CANOVANAS | 2021-08-22 16:03 | 2021-08-22 17:40 | 30 | 001:37 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL SOBRE LINEA | R21082200065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2021-08-22 | 2910 | keep | 0 | Aug | 2021 | 0.001982 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
HUMACAO | 2021-08-22 16:05 | 2021-08-22 16:45 | 1117 | 000:40 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTRERRUPTOR PARA SECCIONALIZAR FASE DE LA LINEA 5300 SOBRE LA DISTRIBUCUIN | C21082200177 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 40 | 2021-08-22 | 44680 | keep | 0 | Aug | 2021 | 0.030431 | 0.00076078 | Sustained | FALSE | TRUE | Not_TMED_Event | 1117
BAYAMON | 2021-08-22 16:06 | 2021-08-22 19:51 | 80 | 003:45 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | S21082200204 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2021-08-22 | 18000 | keep | 0 | Aug | 2021 | 0.01226 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BARRANQUITAS | 2021-08-22 16:14 | 2021-08-23 10:48 | 50 | 018:34 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21082200178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1114 | 2021-08-22 | 55700 | keep | 0 | Aug | 2021 | 0.037937 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-22 16:25 | 2021-08-23 10:00 | 40 | 017:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21082200132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1055 | 2021-08-22 | 42200 | keep | 0 | Aug | 2021 | 0.028742 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
YAUCO | 2021-08-22 16:39 | 2021-08-22 16:40 | 661 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21082200060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-22 | 661 | keep | 0 | Aug | 2021 | 0.0004502 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
HUMACAO | 2021-08-22 16:45 | 2021-08-22 18:54 | 500 | 002:09 | P | LINEA DE TRANSMISION 38KV | SE LEVANTO FASE DE LINEA 5300 SOBRE LA DISTRIBUCION | C21082200177 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 129 | 2021-08-22 | 64500 | keep | 0 | Aug | 2021 | 0.043931 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-08-22 16:46 | 2021-08-22 20:54 | 30 | 004:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | A21082200134 | New_Event | Bad Weather | Include | Include | Weather | 248 | 2021-08-22 | 7440 | keep | 0 | Aug | 2021 | 0.0050674 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
FAJARDO | 2021-08-22 16:53 | 2021-08-22 17:48 | 55 | 000:55 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | R21082200083 | New_Event |  |  | Include | Wildlife | 55 | 2021-08-22 | 3025 | keep | 0 | Aug | 2021 | 0.0020603 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
PONCE | 2021-08-22 16:57 | 2021-08-22 16:58 | 778 | 000:01 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR DURANTE MANIOBRAS EN SOTERRADO | P21082200061 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1 | 2021-08-22 | 778 | keep | 0 | Aug | 2021 | 0.00052989 | 0.00052989 | Momentary | FALSE | FALSE | Not_TMED_Event | 778
BAYAMON | 2021-08-22 16:58 | 2021-08-22 18:16 | 50 | 001:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE | B21082200136 | New_Event |  |  | Include | Wildlife | 78 | 2021-08-22 | 3900 | keep | 0 | Aug | 2021 | 0.0026563 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-08-22 17:01 | 2021-08-25 13:36 | 60 | 068:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRAR PUENTE DE LINEA A CAJA | S21082200204 | New_Event | Wire Down | Include | Include | Equipment | 4115 | 2021-08-22 | 246900 | keep | 0 | Aug | 2021 | 0.16816 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-08-22 17:10 | 2021-08-22 19:18 | 9 | 002:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO NEUTRAL SECUNDARIO EN TRANSFORMADOR | R21082200085 | New_Event | Secondary Wire Down | Include | Include | Equipment | 128 | 2021-08-22 | 1152 | keep | 0 | Aug | 2021 | 0.00078462 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2021-08-22 17:14 | 2021-08-23 10:55 | 8 | 017:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ALAMBRE PRIMARIO PARTIDO | P21082200056 | New_Event | Wire Down | Include | Include | Equipment | 1061 | 2021-08-22 | 8488 | keep | 0 | Aug | 2021 | 0.0057811 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-08-22 17:32 | 2021-08-22 17:33 | 726 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21082200000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-22 | 726 | keep | 0 | Aug | 2021 | 0.00049448 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-08-22 17:32 | 2021-08-23 10:30 | 30 | 016:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LLEVO CONDUCTOR A CAJA | S21082200216 | New_Event | Wire Down | Include | Include | Equipment | 1018 | 2021-08-22 | 30540 | keep | 0 | Aug | 2021 | 0.020801 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-08-22 17:33 | 2021-08-22 20:45 | 60 | 003:12 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21082200182 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 192 | 2021-08-22 | 11520 | keep | 0 | Aug | 2021 | 0.0078462 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-08-22 17:34 | 2021-08-22 19:59 | 30 | 002:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21082200138 | New_Event | Bad Weather | Include | Include | Weather | 145 | 2021-08-22 | 4350 | keep | 0 | Aug | 2021 | 0.0029628 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-08-22 17:40 | 2021-08-22 20:47 | 30 | 003:07 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA REQUIERE DESGANCHE | A21082200140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2021-08-22 | 5610 | keep | 0 | Aug | 2021 | 0.0038209 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-08-22 17:43 | 2021-08-22 20:45 | 100 | 003:02 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO MACHETES N/O EN LA CARR 199 ESQUINA ROMANI PARA REEMPLAZAR MACHETE QUEMADO | S21082200222 | New_Event | Switch Failure | Include | Include | Equipment | 182 | 2021-08-22 | 18200 | keep | 0 | Aug | 2021 | 0.012396 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2021-08-22 17:44 | 2021-08-22 18:38 | 20 | 000:54 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | R21082200088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 54 | 2021-08-22 | 1080 | keep | 0 | Aug | 2021 | 0.00073558 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-08-22 17:56 | 2021-08-23 10:26 | 8 | 016:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RECONECTO BAJANTE PRIMARIO EN TRANSFORMADOR | P21082200064 | New_Event | Wire Down | Include | Include | Equipment | 990 | 2021-08-22 | 7920 | keep | 0 | Aug | 2021 | 0.0053943 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-08-22 18:26 | 2021-08-22 20:54 | 10 | 002:28 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR, SE REALIZO DESGANCHE Y SE REPARO SECUNDARIA | B21082200050 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 148 | 2021-08-22 | 1480 | keep | 0 | Aug | 2021 | 0.001008 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-22 18:49 | 2021-08-23 10:30 | 10 | 015:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A21082200148 | New_Event | Wire Down | Include | Include | Equipment | 941 | 2021-08-22 | 9410 | keep | 0 | Aug | 2021 | 0.0064091 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2021-08-22 18:50 | 2021-08-23 18:40 | 6 | 023:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BAJANTE SECUNDARIO | C21082200197 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1430 | 2021-08-22 | 8580 | keep | 0 | Aug | 2021 | 0.0058438 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-08-22 19:02 | 2021-08-23 16:20 | 1 | 021:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE A CAJA EN CORTE DE LINEA | A21082300151 | New_Event | Wire Down | Include | Include | Equipment | 1278 | 2021-08-22 | 1278 | keep | 0 | Aug | 2021 | 0.00087044 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
AGUADILLA | 2021-08-22 19:31 | 2021-08-23 10:08 | 60 | 014:37 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21082200093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 877 | 2021-08-22 | 52620 | keep | 0 | Aug | 2021 | 0.035839 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-08-22 19:50 | 2021-08-22 19:51 | 427 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-22 | 427 | keep | 0 | Aug | 2021 | 0.00029083 | 0.00029083 | Momentary | FALSE | FALSE | Not_TMED_Event | 427
PONCE | 2021-08-22 20:21 | 2021-08-22 21:20 | 150 | 000:59 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA CRUCE DE LINEA POR RAMA | P21082200074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2021-08-22 | 8850 | keep | 0 | Aug | 2021 | 0.0060277 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CANOVANAS | 2021-08-22 20:34 | 2021-08-22 20:35 | 2039 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21082200092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-22 | 2039 | keep | 0 | Aug | 2021 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
MAYAGÃœEZ | 2021-08-22 20:49 | 2021-08-23 00:09 | 800 | 003:20 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA NO ENCONTRARON CAUSA | M21082200100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 200 | 2021-08-22 | 160000 | keep | 0 | Aug | 2021 | 0.10898 | 0.00054488 | Sustained | FALSE | TRUE | Not_TMED_Event | 800
BAYAMON | 2021-08-22 20:56 | 2021-08-22 21:50 | 60 | 000:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA SE RETIRO RATA | B21082200188 | New_Event |  |  | Include | Wildlife | 54 | 2021-08-22 | 3240 | keep | 0 | Aug | 2021 | 0.0022067 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-08-22 21:05 | 2021-08-22 22:29 | 25 | 001:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A21082200237 | New_Event | Cutout Failure | Include | Include | Equipment | 84 | 2021-08-22 | 2100 | keep | 0 | Aug | 2021 | 0.0014303 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-08-22 21:57 | 2021-08-25 13:26 | 60 | 063:29 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21082200182 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 3809 | 2021-08-22 | 228540 | keep | 0 | Aug | 2021 | 0.15566 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-08-22 21:57 | 2021-08-22 22:20 | 100 | 000:23 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO MACHETES N/O EN LA CARR 199 ESQUINA ROMANI PARA REEMPLAZAR MACHETE QUEMADO | S21082200222 | Partial_restoration | Switch Failure | Include | Include | Equipment | 23 | 2021-08-22 | 2300 | keep | 0 | Aug | 2021 | 0.0015665 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-08-22 22:32 | 2021-08-23 10:33 | 15 | 012:01 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21082200174 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 721 | 2021-08-22 | 10815 | keep | 0 | Aug | 2021 | 0.007366 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
VEGA BAJA | 2021-08-22 22:40 | 2021-08-23 11:23 | 60 | 012:43 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21082200030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 763 | 2021-08-22 | 45780 | keep | 0 | Aug | 2021 | 0.031181 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-08-22 22:44 | 2021-08-22 22:45 | 3701 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21082200278 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-22 | 3701 | keep | 0 | Aug | 2021 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
BAYAMON | 2021-08-22 22:53 | 2021-08-23 10:33 | 150 | 011:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CONVERTIDOR Y SE REMPLAZO PORTAFUSIBLES CARGA TRANSFERIDA AL 1709-01 | B21082200020 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 700 | 2021-08-22 | 105000 | keep | 0 | Aug | 2021 | 0.071515 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-08-22 23:07 | 2021-08-22 23:12 | 35 | 000:05 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21082200185 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-08-22 | 175 | keep | 0 | Aug | 2021 | 0.00011919 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-08-22 23:21 | 2021-08-23 14:58 | 35 | 015:37 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21082200185 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 937 | 2021-08-22 | 32795 | keep | 0 | Aug | 2021 | 0.022337 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
AGUADILLA | 2021-08-22 23:34 | 2021-08-23 00:26 | 1256 | 000:52 | T | RELEVO DE CARGA POR CONTINGENCIA | SE ABRIO EL 7002-04 POR RELEVO DE CARGA POR CONTINGENCIA ESTE ESTA LLEVANDO LA CARGA DEL 7002-03 | M21082200128 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 52 | 2021-08-22 | 65312 | keep | 0 | Aug | 2021 | 0.044484 | 0.00085546 | Sustained | FALSE | FALSE | Not_TMED_Event | 1256
ARECIBO | 2021-08-22 23:41 | 2021-08-23 12:55 | 25 | 013:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A21082200237 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 794 | 2021-08-22 | 19850 | keep | 0 | Aug | 2021 | 0.01352 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2021-08-23 00:05 | 2021-08-23 10:36 | 100 | 010:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21082300012 | New_Event | Bad Weather | Include | Include | Weather | 631 | 2021-08-23 | 63100 | keep | 0 | Aug | 2021 | 0.042977 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-08-23 00:33 | 2021-08-23 12:48 | 200 | 012:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 Y 3 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE DE BAMBUAS Y SE SUBIO PRIMARIA | B21082300012 | New_Event | Wire Down | Include | Include | Equipment | 735 | 2021-08-23 | 147000 | keep | 0 | Aug | 2021 | 0.10012 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
YAUCO | 2021-08-23 01:39 | 2021-08-23 11:30 | 42 | 009:51 | P | DESGANCHE | 1 X 100 Y 1 X 65 EN CORTE DE LINEA DESGANCHE | P21082300012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 591 | 2021-08-23 | 24822 | keep | 0 | Aug | 2021 | 0.016906 | 2.8606e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 42
CANOVANAS | 2021-08-23 02:46 | 2021-08-23 05:17 | 4188 | 002:31 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO INTERRUPTOR SE SECCIONALIZO Y SE CERRO N/O CON EL 2302-03 CARR. 187 PUENTE HERRERA | R21082400003 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 151 | 2021-08-23 | 632388 | keep | 0 | Aug | 2021 | 0.43072 | 0.0028524 | Sustained | FALSE | FALSE | Not_TMED_Event | 4188
GUAYAMA | 2021-08-23 03:24 | 2021-08-23 11:45 | 76 | 008:21 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | P21082300013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 501 | 2021-08-23 | 38076 | keep | 0 | Aug | 2021 | 0.025933 | 5.1763e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 76
BAYAMON | 2021-08-23 04:08 | 2021-08-23 17:34 | 50 | 013:26 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21082300009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 806 | 2021-08-23 | 40300 | keep | 0 | Aug | 2021 | 0.027448 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-23 04:20 | 2021-08-23 11:33 | 150 | 007:13 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21082300011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 433 | 2021-08-23 | 64950 | keep | 0 | Aug | 2021 | 0.044237 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-08-23 05:04 | 2021-08-23 21:17 | 15 | 016:13 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 75KVA POR 100KVA SEGUN SE DISPONIA | S21082300012 | New_Event | Service Transformer Failure | Include | Include | Equipment | 973 | 2021-08-23 | 14595 | keep | 0 | Aug | 2021 | 0.0099406 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2021-08-23 05:09 | 2021-08-23 05:10 | 2410 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21082300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-23 | 2410 | keep | 0 | Aug | 2021 | 0.0016414 | 0.0016414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2410
BAYAMON | 2021-08-23 05:18 | 2021-08-23 18:36 | 30 | 013:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLES | B21082300024 | New_Event | Cutout Failure | Include | Include | Equipment | 798 | 2021-08-23 | 23940 | keep | 0 | Aug | 2021 | 0.016305 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-08-23 05:41 | 2021-08-23 10:45 | 149 | 005:04 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | P21082300015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 304 | 2021-08-23 | 45296 | keep | 0 | Aug | 2021 | 0.030851 | 0.00010148 | Sustained | FALSE | TRUE | Not_TMED_Event | 149
CANOVANAS | 2021-08-23 06:20 | 2021-08-23 10:49 | 15 | 004:29 | P | TRANSFORMADOR AVERIADO | REEMPLAZO T-31 AVERIADO DE 75KVA X 75KVA | R21082300002 | New_Event | Service Transformer Failure | Include | Include | Equipment | 269 | 2021-08-23 | 4035 | keep | 0 | Aug | 2021 | 0.0027482 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2021-08-23 06:20 | 2021-08-23 10:48 | 30 | 004:28 | P | TRANSFORMADOR AVERIADO | 1 X 40 EN RISER SECCIONALIZO T- 31 AVERIADO | R21082300002 | New_Event | Service Transformer Failure | Include | Include | Equipment | 268 | 2021-08-23 | 8040 | keep | 0 | Aug | 2021 | 0.005476 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-08-23 06:22 | 2021-08-23 11:41 | 80 | 005:19 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | C21082300014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 319 | 2021-08-23 | 25520 | keep | 0 | Aug | 2021 | 0.017382 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
PONCE | 2021-08-23 06:22 | 2021-08-23 12:41 | 35 | 006:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | P21082300016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 379 | 2021-08-23 | 13265 | keep | 0 | Aug | 2021 | 0.0090347 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
UTUADO | 2021-08-23 06:44 | 2021-08-23 11:30 | 60 | 004:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21082300010 | New_Event | Bad Weather | Include | Include | Weather | 286 | 2021-08-23 | 17160 | keep | 0 | Aug | 2021 | 0.011688 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
PONCE | 2021-08-23 06:56 | 2021-08-23 06:57 | 2446 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21082300017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-23 | 2446 | keep | 0 | Aug | 2021 | 0.001666 | 0.001666 | Momentary | FALSE | FALSE | Not_TMED_Event | 2446
BAYAMON | 2021-08-23 07:10 | 2021-08-23 16:21 | 35 | 009:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN BANCO DE TRANSFORMADOR Y 1 X 30 EN RISER. SE RETIRO IGUANA | B21082300031 | New_Event |  |  | Include | Wildlife | 551 | 2021-08-23 | 19285 | keep | 0 | Aug | 2021 | 0.013135 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2021-08-23 07:19 | 2021-08-23 15:33 | 5 | 008:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTES SECUNDARIO A TRANSFORMADOR | A21082300012 | New_Event | Secondary Wire Down | Include | Include | Equipment | 494 | 2021-08-23 | 2470 | keep | 0 | Aug | 2021 | 0.0016823 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2021-08-23 07:25 | 2021-08-23 11:33 | 1271 | 004:08 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SECCIONALIZO CONDUCTOR EN EL SUELO Y TRANSFIRIO PARTE DE LA CARGA AL 3301-02 | C21082300026 | New_Event | Wire Down | Include | Include | Equipment | 248 | 2021-08-23 | 315208 | keep | 0 | Aug | 2021 | 0.21469 | 0.00086567 | Sustained | FALSE | FALSE | Not_TMED_Event | 1271
HUMACAO | 2021-08-23 07:32 | 2021-08-23 20:09 | 4 | 012:37 | P | CABLE SOTERRADO AVERIADO | NO SE PUDO REMPLAZAR EL CABLE Y SE CONECTO LAS CASAS A OTRO PEDESTAL HC-CAG73029-1 | C21082300023 | New_Event | UG Cable Fault | Include | Include | Equipment | 757 | 2021-08-23 | 3028 | keep | 0 | Aug | 2021 | 0.0020624 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2021-08-23 07:36 | 2021-08-23 09:41 | 1 | 002:05 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER NO CAUSA | C21082300029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 125 | 2021-08-23 | 125 | keep | 0 | Aug | 2021 | 8.5137e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-08-23 07:53 | 2021-08-23 13:50 | 65 | 005:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21082300017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 357 | 2021-08-23 | 23205 | keep | 0 | Aug | 2021 | 0.015805 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
MAYAGÃœEZ | 2021-08-23 07:56 | 2021-08-23 13:28 | 50 | 005:32 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | M21082300024 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 332 | 2021-08-23 | 16600 | keep | 0 | Aug | 2021 | 0.011306 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
UTUADO | 2021-08-23 08:06 | 2021-08-23 16:00 | 50 | 007:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21082300017 | New_Event | Wire Down | Include | Include | Equipment | 474 | 2021-08-23 | 23700 | keep | 0 | Aug | 2021 | 0.016142 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-08-23 08:09 | 2021-08-23 18:00 | 12 | 009:51 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR Y SE REALIZO DESGANCHE SECUNDARIO | S21082300029 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 591 | 2021-08-23 | 7092 | keep | 0 | Aug | 2021 | 0.0048303 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2021-08-23 08:09 | 2021-08-23 16:19 | 40 | 008:10 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21082300018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 490 | 2021-08-23 | 19600 | keep | 0 | Aug | 2021 | 0.013349 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-08-23 08:14 | 2021-08-23 12:51 | 40 | 004:37 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA Y 1 X 20 EN TRANSFORMADOR CRUCE POR AVE | C21082300035 | New_Event |  |  | Include | Wildlife | 277 | 2021-08-23 | 11080 | keep | 0 | Aug | 2021 | 0.0075465 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-08-23 08:24 | 2021-08-23 12:30 | 150 | 004:06 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21082300023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2021-08-23 | 36900 | keep | 0 | Aug | 2021 | 0.025132 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-08-23 08:28 | 2021-08-23 10:11 | 45 | 001:43 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21082300039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2021-08-23 | 4635 | keep | 0 | Aug | 2021 | 0.0031569 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
UTUADO | 2021-08-23 08:30 | 2021-08-23 12:40 | 35 | 004:10 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21082300025 | New_Event | Bad Weather | Include | Include | Weather | 250 | 2021-08-23 | 8750 | keep | 0 | Aug | 2021 | 0.0059596 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
HUMACAO | 2021-08-23 08:31 | 2021-08-23 20:48 | 10 | 012:17 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA X 25 KVA | C21082300040 | New_Event | Service Transformer Failure | Include | Include | Equipment | 737 | 2021-08-23 | 7370 | keep | 0 | Aug | 2021 | 0.0050197 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-08-23 08:38 | 2021-08-23 19:32 | 75 | 010:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA | S21082300035 | New_Event | Wire Down | Include | Include | Equipment | 654 | 2021-08-23 | 49050 | keep | 0 | Aug | 2021 | 0.033408 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
PONCE | 2021-08-23 08:57 | 2021-08-23 16:11 | 65 | 007:14 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21082300027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 434 | 2021-08-23 | 28210 | keep | 0 | Aug | 2021 | 0.019214 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BARRANQUITAS | 2021-08-23 09:08 | 2021-08-23 12:33 | 40 | 003:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA RETESO LINEAS | C21082300046 | New_Event | Wire Down | Include | Include | Equipment | 205 | 2021-08-23 | 8200 | keep | 0 | Aug | 2021 | 0.005585 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-23 09:29 | 2021-08-23 11:20 | 6 | 001:51 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M21082300030 | New_Event | Bad Weather | Include | Include | Weather | 111 | 2021-08-23 | 666 | keep | 0 | Aug | 2021 | 0.00045361 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-08-23 09:35 | 2021-08-23 11:50 | 60 | 002:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A21082300050 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 135 | 2021-08-23 | 8100 | keep | 0 | Aug | 2021 | 0.0055169 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-08-23 09:36 | 2021-08-23 16:49 | 50 | 007:13 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA Y SE REEMPLAZO AISLADOR | S21082300114 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 433 | 2021-08-23 | 21650 | keep | 0 | Aug | 2021 | 0.014746 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-08-23 09:36 | 2021-08-23 20:48 | 1 | 011:12 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21082300055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 672 | 2021-08-23 | 672 | keep | 0 | Aug | 2021 | 0.0004577 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
HUMACAO | 2021-08-23 09:48 | 2021-08-23 16:27 | 40 | 006:39 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21082300059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 399 | 2021-08-23 | 15960 | keep | 0 | Aug | 2021 | 0.01087 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-08-23 10:02 | 2021-08-23 10:03 | 1715 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA TRANSFERIDA AL 1708-03 | B21080900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-23 | 1715 | keep | 0 | Aug | 2021 | 0.0011681 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2021-08-23 10:02 | 2021-08-23 10:03 | 1498 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA CARGA DEL 1708-02 | B21080900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-23 | 1498 | keep | 0 | Aug | 2021 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
VEGA BAJA | 2021-08-23 10:07 | 2021-08-23 13:47 | 50 | 003:40 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21002300050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 220 | 2021-08-23 | 11000 | keep | 0 | Aug | 2021 | 0.007492 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-23 10:11 | 2021-08-23 14:37 | 4 | 004:26 | P | NO SE REPORTO CAUSA | 1 X 5 EN TRANSFORMADOR | M21082300039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 266 | 2021-08-23 | 1064 | keep | 0 | Aug | 2021 | 0.00072469 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-08-23 10:13 | 2021-08-23 12:58 | 60 | 002:45 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21082300045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2021-08-23 | 9900 | keep | 0 | Aug | 2021 | 0.0067428 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
VEGA BAJA | 2021-08-23 10:20 | 2021-08-23 11:23 | 100 | 001:03 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 40 EN CORTE DE LINEA | B21082300052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2021-08-23 | 6300 | keep | 0 | Aug | 2021 | 0.0042909 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-08-23 10:27 | 2021-08-23 15:30 | 100 | 005:03 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | M21082300044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 303 | 2021-08-23 | 30300 | keep | 0 | Aug | 2021 | 0.020637 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-08-23 10:32 | 2021-08-23 17:49 | 65 | 007:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA EN CORTE DE LINEA | S21082300070 | New_Event | Wire Down | Include | Include | Equipment | 437 | 2021-08-23 | 28405 | keep | 0 | Aug | 2021 | 0.019347 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
GUAYAMA | 2021-08-23 10:40 | 2021-08-23 11:50 | 100 | 001:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE CRUZO LINEAS | P21082300035 | New_Event |  |  | Include | Wildlife | 70 | 2021-08-23 | 7000 | keep | 0 | Aug | 2021 | 0.0047677 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-08-23 10:43 | 2021-08-23 10:44 | 1408 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1714-03 Y SE CERRO POR SCADA CARGA TRANSFERIDA AL 1714-03 | B21082300059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-23 | 1408 | keep | 0 | Aug | 2021 | 0.00095898 | 0.00095898 | Momentary | FALSE | FALSE | Not_TMED_Event | 1408
BAYAMON | 2021-08-23 10:43 | 2021-08-23 10:44 | 455 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1714-03 Y SE CERRO POR SCADA LLEVA CARGA DEL 1714-02 | B21082300059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-23 | 455 | keep | 0 | Aug | 2021 | 0.0003099 | 0.0003099 | Momentary | FALSE | FALSE | Not_TMED_Event | 455
HUMACAO | 2021-08-23 10:45 | 2021-08-23 10:46 | 3420 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C21082300000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-23 | 3420 | keep | 0 | Aug | 2021 | 0.0023293 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
HUMACAO | 2021-08-23 10:46 | 2021-08-23 12:43 | 200 | 001:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 140 EN LA SALIDA DEL CONVERTIDOR | C21082300011 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 117 | 2021-08-23 | 23400 | keep | 0 | Aug | 2021 | 0.015938 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2021-08-23 10:49 | 2021-08-23 10:50 | 2039 | 000:01 | T | TRANSFORMADOR AVERIADO | RECIERRE PERSONAL REALIZANDO OPERACIONES PARA LOCALIZAR AVERIA | R21082300016 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1 | 2021-08-23 | 2039 | keep | 0 | Aug | 2021 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
CANOVANAS | 2021-08-23 10:50 | 2021-08-23 12:28 | 30 | 001:38 | P | TRANSFORMADOR AVERIADO | 1 X 40 EN RISER SECCIONALIZO T- 31 AVERIADO | R21082300002 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 98 | 2021-08-23 | 2940 | keep | 0 | Aug | 2021 | 0.0020024 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-08-23 10:55 | 2021-08-23 15:56 | 4 | 005:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO TRANSFORMADOR PARA REGAR CONDUCTOR PRIMARIO | C21082300071 | New_Event | Wire Down | Include | Include | Equipment | 301 | 2021-08-23 | 1204 | keep | 0 | Aug | 2021 | 0.00082004 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-08-23 11:04 | 2021-08-23 11:28 | 30 | 000:24 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21082300072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 24 | 2021-08-23 | 720 | keep | 0 | Aug | 2021 | 0.00049039 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-08-23 11:04 | 2021-08-23 12:25 | 60 | 001:21 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21082300058 | New_Event | Bad Weather | Include | Include | Weather | 81 | 2021-08-23 | 4860 | keep | 0 | Aug | 2021 | 0.0033101 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BARRANQUITAS | 2021-08-23 11:14 | 2021-08-23 13:47 | 1 | 002:33 | P | NO SE REPORTO CAUSA | 1 SMU 20 DE 20AMP EN EL SU - 1 NO CAUSA | C21082300078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 153 | 2021-08-23 | 153 | keep | 0 | Aug | 2021 | 0.00010421 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-08-23 11:16 | 2021-08-23 16:52 | 55 | 005:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO BAJANTE SAFADO HACIA CAJA PRIMARIA | R21082300018 | New_Event | Wire Down | Include | Include | Equipment | 336 | 2021-08-23 | 18480 | keep | 0 | Aug | 2021 | 0.012587 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CAGUAS | 2021-08-23 11:33 | 2021-08-23 17:17 | 40 | 005:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTO CONDUCTOR | C21082300089 | New_Event | Wire Down | Include | Include | Equipment | 344 | 2021-08-23 | 13760 | keep | 0 | Aug | 2021 | 0.0093719 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2021-08-23 11:47 | 2021-08-24 13:22 | 35 | 025:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA Y SE REEMPLAZO CAJA PRIMARIA | S21082300095 | New_Event | Cutout Failure | Include | Include | Equipment | 1535 | 2021-08-23 | 53725 | keep | 0 | Aug | 2021 | 0.036592 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
ARECIBO | 2021-08-23 11:47 | 2021-08-23 13:30 | 8 | 001:43 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 37.5 KVA POR LO MISMO | A21082300061 | New_Event | Service Transformer Failure | Include | Include | Equipment | 103 | 2021-08-23 | 824 | keep | 0 | Aug | 2021 | 0.00056122 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-08-23 12:00 | 2021-08-23 18:56 | 10 | 006:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR SE RETIRO AVE | B21082300083 | New_Event |  |  | Include | Wildlife | 416 | 2021-08-23 | 4160 | keep | 0 | Aug | 2021 | 0.0028334 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-23 12:06 | 2021-08-23 17:34 | 30 | 005:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO DISCOS ROTOS EN LINEA PRIMARIA | A21082300069 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 328 | 2021-08-23 | 9840 | keep | 0 | Aug | 2021 | 0.006702 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-08-23 12:13 | 2021-08-23 13:57 | 2486 | 001:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEAS 3800 Y 800 | C21082300091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2021-08-23 | 258544 | keep | 0 | Aug | 2021 | 0.17609 | 0.0016932 | Sustained | FALSE | TRUE | Not_TMED_Event | 2486
CAGUAS | 2021-08-23 12:13 | 2021-08-23 13:57 | 1403 | 001:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEAS 3800 Y 800 | C21082300091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2021-08-23 | 145912 | keep | 0 | Aug | 2021 | 0.09938 | 0.00095558 | Sustained | FALSE | TRUE | Not_TMED_Event | 1403
CAGUAS | 2021-08-23 12:13 | 2021-08-23 13:57 | 1001 | 001:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEAS 3800 Y 800 | C21082300091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2021-08-23 | 104104 | keep | 0 | Aug | 2021 | 0.070905 | 0.00068178 | Sustained | FALSE | TRUE | Not_TMED_Event | 1001
ARECIBO | 2021-08-23 12:15 | 2021-08-23 16:44 | 20 | 004:29 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO PM DE 100KVA MEGATRAN S/N 17100413P-180-16-1 4160 7200 FID 1000754165 | A21082300075 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 269 | 2021-08-23 | 5380 | keep | 0 | Aug | 2021 | 0.0036643 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-08-23 12:28 | 2021-08-23 17:00 | 15 | 004:32 | P | TRANSFORMADOR AVERIADO | REEMPLAZO T-31 AVERIADO DE 75KVA X 75KVA | R21082300002 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 272 | 2021-08-23 | 4080 | keep | 0 | Aug | 2021 | 0.0027789 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-08-23 12:34 | 2021-08-23 14:51 | 6 | 002:17 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO CAUSA | C21082300097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 137 | 2021-08-23 | 822 | keep | 0 | Aug | 2021 | 0.00055986 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2021-08-23 12:53 | 2021-08-23 14:47 | 574 | 001:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21082300072 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2021-08-23 | 65436 | keep | 0 | Aug | 2021 | 0.044568 | 0.00039095 | Sustained | FALSE | TRUE | Not_TMED_Event | 574
AGUADILLA | 2021-08-23 12:53 | 2021-08-23 14:47 | 2493 | 001:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21082300072 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2021-08-23 | 284202 | keep | 0 | Aug | 2021 | 0.19357 | 0.001698 | Sustained | FALSE | TRUE | Not_TMED_Event | 2493
AGUADILLA | 2021-08-23 12:53 | 2021-08-23 14:47 | 1415 | 001:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21082300072 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2021-08-23 | 161310 | keep | 0 | Aug | 2021 | 0.10987 | 0.00096375 | Sustained | FALSE | TRUE | Not_TMED_Event | 1415
AGUADILLA | 2021-08-23 12:53 | 2021-08-23 14:47 | 1428 | 001:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21082300072 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2021-08-23 | 162792 | keep | 0 | Aug | 2021 | 0.11088 | 0.0009726 | Sustained | FALSE | TRUE | Not_TMED_Event | 1428
AGUADILLA | 2021-08-23 12:53 | 2021-08-23 14:47 | 1036 | 001:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21082300072 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2021-08-23 | 118104 | keep | 0 | Aug | 2021 | 0.08044 | 0.00070561 | Sustained | FALSE | TRUE | Not_TMED_Event | 1036
AGUADILLA | 2021-08-23 12:53 | 2021-08-23 14:47 | 382 | 001:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21082300073 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2021-08-23 | 43548 | keep | 0 | Aug | 2021 | 0.02966 | 0.00026018 | Sustained | FALSE | TRUE | Not_TMED_Event | 382
AGUADILLA | 2021-08-23 12:53 | 2021-08-23 14:47 | 39 | 001:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21082300073 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2021-08-23 | 4446 | keep | 0 | Aug | 2021 | 0.0030282 | 2.6563e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 39
AGUADILLA | 2021-08-23 12:53 | 2021-08-23 14:47 | 2366 | 001:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21082300074 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2021-08-23 | 269724 | keep | 0 | Aug | 2021 | 0.18371 | 0.0016115 | Sustained | FALSE | TRUE | Not_TMED_Event | 2366
MAYAGÃœEZ | 2021-08-23 12:53 | 2021-08-23 14:47 | 1337 | 001:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21082300074 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2021-08-23 | 152418 | keep | 0 | Aug | 2021 | 0.10381 | 0.00091062 | Sustained | FALSE | TRUE | Not_TMED_Event | 1337
AGUADILLA | 2021-08-23 12:53 | 2021-08-23 14:47 | 709 | 001:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21082300074 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2021-08-23 | 80826 | keep | 0 | Aug | 2021 | 0.05505 | 0.0004829 | Sustained | FALSE | TRUE | Not_TMED_Event | 709
CAGUAS | 2021-08-23 12:54 | 2021-08-24 13:00 | 10 | 024:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | REMPLAZO TOMA PARARRAYO Y CAJA DE TRANSFORMADOR AFECTADOS POR IMPACTO DE DIGGER | C21082300106 | New_Event |  |  | Include | Wildlife | 1446 | 2021-08-23 | 14460 | keep | 0 | Aug | 2021 | 0.0098486 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-23 13:10 | 2021-08-23 16:20 | 40 | 003:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA SE RETIRO AVE CRUZANDO LAS FASES | A21082300083 | New_Event |  |  | Include | Wildlife | 190 | 2021-08-23 | 7600 | keep | 0 | Aug | 2021 | 0.0051763 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-08-23 13:29 | 2021-08-23 15:12 | 30 | 001:43 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA | B21082300086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 103 | 2021-08-23 | 3090 | keep | 0 | Aug | 2021 | 0.0021046 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
GUAYAMA | 2021-08-23 13:30 | 2021-08-23 15:00 | 11 | 001:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P21082300043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 90 | 2021-08-23 | 990 | keep | 0 | Aug | 2021 | 0.00067428 | 7.492e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 11
BAYAMON | 2021-08-23 13:34 | 2021-08-23 13:35 | 1983 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA TRANSFERIDA AL 1801-02 | B21082300090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-23 | 1983 | keep | 0 | Aug | 2021 | 0.0013506 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-08-23 13:34 | 2021-08-23 13:35 | 1983 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1801-02 LLEVA UN 10% DE LA CARGA DEL 1717-01 SE CERRO POR SCADA | B21082300090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-23 | 1983 | keep | 0 | Aug | 2021 | 0.0013506 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-08-23 13:34 | 2021-08-23 13:35 | 186 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA CARGA DEL 1711-04 Y UN 10% DEL 1717-01 | B21082300090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-23 | 186 | keep | 0 | Aug | 2021 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2021-08-23 13:37 | 2021-08-23 16:42 | 10 | 003:05 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21082300091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 185 | 2021-08-23 | 1850 | keep | 0 | Aug | 2021 | 0.00126 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-08-23 13:45 | 2021-08-23 14:23 | 50 | 000:38 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA CARGA TRANSFERIDA AL INTERRUPTOR SPARE 1709-01 | B21082300084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 38 | 2021-08-23 | 1900 | keep | 0 | Aug | 2021 | 0.0012941 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-08-23 13:47 | 2021-08-23 17:50 | 250 | 004:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA REPARO LINEAS PARTIDAS | M21082300107 | New_Event | Wire Down | Include | Include | Equipment | 243 | 2021-08-23 | 60750 | keep | 0 | Aug | 2021 | 0.041377 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
CAGUAS | 2021-08-23 13:55 | 2021-08-23 17:10 | 1 | 003:15 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO CAUSA | C21082300126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 195 | 2021-08-23 | 195 | keep | 0 | Aug | 2021 | 0.00013281 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-08-23 14:00 | 2021-08-23 14:38 | 50 | 000:38 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21082300069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 38 | 2021-08-23 | 1900 | keep | 0 | Aug | 2021 | 0.0012941 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-08-23 14:24 | 2021-08-23 14:26 | 1008 | 000:02 | P | NO SE REPORTO CAUSA | SE CERRO POR SCADA. CARGA POR EL 1303-04 | S21082300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-23 | 2016 | keep | 0 | Aug | 2021 | 0.0013731 | 0.00068654 | Momentary | FALSE | FALSE | Not_TMED_Event | 1008
SAN JUAN | 2021-08-23 14:24 | 2021-08-23 14:26 | 1598 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA. CARGA POR EL 1303-04 QUE LLEVA TAMBIEN 1303-01 | S21082300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-23 | 3196 | keep | 0 | Aug | 2021 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
BAYAMON | 2021-08-23 14:35 | 2021-08-23 17:07 | 1 | 002:32 | P | HERRAJE ROTO O PODRIDO | 3 X 65 EN CORTE DE LINEA SE RETEZO LINEA Y SE REEMPLAZO CRUCETA | B21082000131 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 152 | 2021-08-23 | 152 | keep | 0 | Aug | 2021 | 0.00010353 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-08-23 14:43 | 2021-08-23 17:46 | 10 | 003:03 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C21082300134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 183 | 2021-08-23 | 1830 | keep | 0 | Aug | 2021 | 0.0012464 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-08-23 14:57 | 2021-08-23 19:14 | 50 | 004:17 | P | ESTRUCTURA AVERIADA | 1 X 50 EN CORTE DE LINEA SE SECCIONALIZO POSTE PARTIDO | B21082300100 | New_Event | Defective Pole | Include | Include | Equipment | 257 | 2021-08-23 | 12850 | keep | 0 | Aug | 2021 | 0.0087521 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-23 14:58 | 2021-08-23 19:31 | 80 | 004:33 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21082300135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 273 | 2021-08-23 | 21840 | keep | 0 | Aug | 2021 | 0.014875 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-08-23 15:05 | 2021-08-24 10:10 | 50 | 019:05 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21082300138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1145 | 2021-08-23 | 57250 | keep | 0 | Aug | 2021 | 0.038993 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-08-23 15:07 | 2021-08-23 21:19 | 200 | 006:12 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 140 EN CORTES DE LINEA NO REPORTO CAUSA | C21082300136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 372 | 2021-08-23 | 74400 | keep | 0 | Aug | 2021 | 0.050674 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
AGUADILLA | 2021-08-23 15:29 | 2021-08-23 17:03 | 46 | 001:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE Y SE CERRO CORTE DE LINEA | M21082200048 | New_Event | Wire Down | Include | Include | Equipment | 94 | 2021-08-23 | 4324 | keep | 0 | Aug | 2021 | 0.0029451 | 3.133e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 46
CAGUAS | 2021-08-23 15:30 | 2021-08-23 18:54 | 434 | 003:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO CORTE DE LINEA PARA LEVANTAR NEUTRAL PRIMARIO | C21082300138 | New_Event | Wire Down | Include | Include | Equipment | 204 | 2021-08-23 | 88536 | keep | 0 | Aug | 2021 | 0.060301 | 0.0002956 | Sustained | FALSE | TRUE | Not_TMED_Event | 434
ARECIBO | 2021-08-23 15:31 | 2021-08-23 18:55 | 80 | 003:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO A CAJA PORTAFUSIBLE | A21082300116 | New_Event | Wire Down | Include | Include | Equipment | 204 | 2021-08-23 | 16320 | keep | 0 | Aug | 2021 | 0.011115 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-08-23 15:37 | 2021-08-23 17:00 | 8 | 001:23 | P | OTRAS CAUSAS | SE PASO TRANSFORMADOR A POSTE EXISTENTE | M21082300124 | New_Event | Other Causes | Include | Include | Other | 83 | 2021-08-23 | 664 | keep | 0 | Aug | 2021 | 0.00045225 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2021-08-23 15:37 | 2021-08-23 18:00 | 100 | 002:23 | P | DESGANCHE | 1 X 100 SE REALIZO DESGANCHE DE BAMBÃšES | A21082300098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2021-08-23 | 14300 | keep | 0 | Aug | 2021 | 0.0097397 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2021-08-23 15:44 | 2021-08-23 18:21 | 70 | 002:37 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21082300071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2021-08-23 | 10990 | keep | 0 | Aug | 2021 | 0.0074852 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BAYAMON | 2021-08-23 15:58 | 2021-08-23 18:31 | 100 | 002:33 | P | NO SE REPORTO CAUSA | 3 X 100 EN CORTE DE LINEA | S21082300150 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 153 | 2021-08-23 | 15300 | keep | 0 | Aug | 2021 | 0.010421 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-08-23 15:58 | 2021-08-24 12:01 | 200 | 020:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 200 EN CORTE DE LINEA ELIMINO BAJANTE VACANTE Y CERRO PUENTE | C21082300143 | Partial_restoration | Wire Down | Include | Include | Equipment | 1203 | 2021-08-23 | 240600 | keep | 0 | Aug | 2021 | 0.16387 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-23 16:04 | 2021-08-23 19:30 | 100 | 003:26 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21082300136 | New_Event | Bad Weather | Include | Include | Weather | 206 | 2021-08-23 | 20600 | keep | 0 | Aug | 2021 | 0.014031 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-08-23 16:04 | 2021-08-23 17:50 | 20 | 001:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA ROTA | A21082300117 | New_Event | Secondary Wire Down | Include | Include | Equipment | 106 | 2021-08-23 | 2120 | keep | 0 | Aug | 2021 | 0.0014439 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-08-23 16:08 | 2021-08-23 19:40 | 60 | 003:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE RETEZO LINEA Y ENDEREZO POSTE | R21082300028 | New_Event | Wire Down | Include | Include | Equipment | 212 | 2021-08-23 | 12720 | keep | 0 | Aug | 2021 | 0.0086635 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-08-23 16:10 | 2021-08-24 11:20 | 7 | 019:10 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR REPARO SECUNDARIA | C21082300144 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1150 | 2021-08-23 | 8050 | keep | 0 | Aug | 2021 | 0.0054828 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2021-08-23 16:21 | 2021-08-23 21:18 | 100 | 004:57 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | P21082300075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 297 | 2021-08-23 | 29700 | keep | 0 | Aug | 2021 | 0.020229 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-08-23 16:21 | 2021-08-23 19:40 | 50 | 003:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA | A21082300120 | New_Event | Cutout Failure | Include | Include | Equipment | 199 | 2021-08-23 | 9950 | keep | 0 | Aug | 2021 | 0.0067769 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-08-23 16:22 | 2021-08-23 17:42 | 55 | 001:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO | S21082300156 | New_Event | Wire Down | Include | Include | Equipment | 80 | 2021-08-23 | 4400 | keep | 0 | Aug | 2021 | 0.0029968 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
BARRANQUITAS | 2021-08-23 16:24 | 2021-08-23 18:52 | 40 | 002:28 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO CAUSA | C21082300146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 148 | 2021-08-23 | 5920 | keep | 0 | Aug | 2021 | 0.0040321 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-08-23 16:28 | 2021-08-24 12:40 | 40 | 020:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA ZAFADA DE AISLADOR | A21082300123 | New_Event | Wire Down | Include | Include | Equipment | 1212 | 2021-08-23 | 48480 | keep | 0 | Aug | 2021 | 0.03302 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-23 16:31 | 2021-08-23 16:59 | 9 | 000:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO | M21082300050 | New_Event | Wire Down | Include | Include | Equipment | 28 | 2021-08-23 | 252 | keep | 0 | Aug | 2021 | 0.00017164 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2021-08-23 16:53 | 2021-08-23 21:15 | 20 | 004:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA QUEMADA | A21082300127 | New_Event | Cutout Failure | Include | Include | Equipment | 262 | 2021-08-23 | 5240 | keep | 0 | Aug | 2021 | 0.0035689 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2021-08-23 16:55 | 2021-08-24 12:00 | 50 | 019:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21082300154 | New_Event | Bad Weather | Include | Include | Weather | 1145 | 2021-08-23 | 57250 | keep | 0 | Aug | 2021 | 0.038993 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-23 16:57 | 2021-08-23 18:30 | 10 | 001:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REEMPLAZO LINEA SECUNDARIA | M21082300153 | New_Event | Secondary Wire Down | Include | Include | Equipment | 93 | 2021-08-23 | 930 | keep | 0 | Aug | 2021 | 0.00063342 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
YAUCO | 2021-08-23 17:00 | 2021-08-23 18:12 | 50 | 001:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA, AVE CRUZO FASE | P21082300081 | New_Event |  |  | Include | Wildlife | 72 | 2021-08-23 | 3600 | keep | 0 | Aug | 2021 | 0.0024519 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-23 17:11 | 2021-08-24 17:20 | 100 | 024:09 | P | HERRAJE ROTO O PODRIDO | SE REMPLAZO CRUCETAS PARTIDAS SE CERRO CORTE DE LINEA | M21082300156 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 1449 | 2021-08-23 | 144900 | keep | 0 | Aug | 2021 | 0.098691 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-08-23 17:17 | 2021-08-24 10:27 | 1 | 017:10 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 80 EN CORTE DE LINEA CRUCE POR AVE | C21082300164 | New_Event |  |  | Include | Wildlife | 1030 | 2021-08-23 | 1030 | keep | 0 | Aug | 2021 | 0.00070153 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-08-23 17:20 | 2021-08-23 17:21 | 478 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1705-01 LLEVANDO 90% DEL 1705-03 | B21082300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-23 | 478 | keep | 0 | Aug | 2021 | 0.00032556 | 0.00032556 | Momentary | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2021-08-23 17:20 | 2021-08-23 17:21 | 850 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO 1705-01 LLEVANDO 90% DEL 1705-03 | B21082300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-23 | 850 | keep | 0 | Aug | 2021 | 0.00057893 | 0.00057893 | Momentary | FALSE | FALSE | Not_TMED_Event | 850
GUAYAMA | 2021-08-23 17:38 | 2021-08-23 18:09 | 52 | 000:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA, AVE CRUZO FASE | P21082300079 | New_Event |  |  | Include | Wildlife | 31 | 2021-08-23 | 1612 | keep | 0 | Aug | 2021 | 0.0010979 | 3.5417e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 52
UTUADO | 2021-08-23 17:53 | 2021-08-23 20:22 | 15 | 002:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21082300141 | New_Event | Bad Weather | Include | Include | Weather | 149 | 2021-08-23 | 2235 | keep | 0 | Aug | 2021 | 0.0015222 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CANOVANAS | 2021-08-23 17:59 | 2021-08-23 23:24 | 1 | 005:25 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR ENREDADERA | R21082300035 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 325 | 2021-08-23 | 325 | keep | 0 | Aug | 2021 | 0.00022136 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-08-23 18:12 | 2021-08-24 12:30 | 45 | 018:18 | P | DESGANCHE | SE REALIZO DESGANCHE MASIVO | M21082300163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1098 | 2021-08-23 | 49410 | keep | 0 | Aug | 2021 | 0.033653 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2021-08-23 18:35 | 2021-08-24 12:12 | 40 | 017:37 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO CAUSA | C21082300178 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1057 | 2021-08-23 | 42280 | keep | 0 | Aug | 2021 | 0.028797 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-23 18:35 | 2021-08-23 19:55 | 7 | 001:20 | P | NO SE REPORTO CAUSA | 1 X 80 EN TRANSFORMADOR | M21082300168 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 80 | 2021-08-23 | 560 | keep | 0 | Aug | 2021 | 0.00038141 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-08-23 18:36 | 2021-08-24 10:04 | 25 | 015:28 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21082300184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 928 | 2021-08-23 | 23200 | keep | 0 | Aug | 2021 | 0.015801 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-08-23 18:59 | 2021-08-24 09:15 | 130 | 014:16 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A21082300145 | New_Event | Bad Weather | Include | Include | Weather | 856 | 2021-08-23 | 111280 | keep | 0 | Aug | 2021 | 0.075792 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
SAN JUAN | 2021-08-23 19:06 | 2021-08-24 14:19 | 90 | 019:13 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21082300042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1153 | 2021-08-23 | 103770 | keep | 0 | Aug | 2021 | 0.070677 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
ARECIBO | 2021-08-23 19:12 | 2021-08-24 10:39 | 60 | 015:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A21082300146 | New_Event | Cutout Failure | Include | Include | Equipment | 927 | 2021-08-23 | 55620 | keep | 0 | Aug | 2021 | 0.037883 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-08-23 19:13 | 2021-08-24 13:22 | 15 | 018:09 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21082300180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1089 | 2021-08-23 | 16335 | keep | 0 | Aug | 2021 | 0.011126 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
PONCE | 2021-08-23 19:19 | 2021-08-23 20:20 | 200 | 001:01 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | P21082300087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2021-08-23 | 12200 | keep | 0 | Aug | 2021 | 0.0083094 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-08-23 19:27 | 2021-08-24 10:11 | 10 | 014:44 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C21082300183 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 884 | 2021-08-23 | 8840 | keep | 0 | Aug | 2021 | 0.0060209 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-08-23 19:32 | 2021-08-23 19:51 | 514 | 000:19 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1520-05 QUE LLEVA LA CARGA DE LOS ALIMENTADORES 1520-01 Y 1520-04 PARA LEVANTAR LINEA PRIMARIA DE SUELO | S21082300197 | New_Event | Wire Down | Include | Include | Equipment | 19 | 2021-08-23 | 9766 | keep | 0 | Aug | 2021 | 0.0066516 | 0.00035008 | Sustained | FALSE | TRUE | Not_TMED_Event | 514
BAYAMON | 2021-08-23 19:32 | 2021-08-23 19:51 | 752 | 000:19 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1520-05 QUE LLEVA LA CARGA DE LOS ALIMENTADORES 1520-01 Y 1520-04 PARA LEVANTAR LINEA PRIMARIA DE SUELO | S21082300197 | New_Event | Wire Down | Include | Include | Equipment | 19 | 2021-08-23 | 14288 | keep | 0 | Aug | 2021 | 0.0097315 | 0.00051218 | Sustained | FALSE | TRUE | Not_TMED_Event | 752
BAYAMON | 2021-08-23 19:32 | 2021-08-23 19:51 | 68 | 000:19 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR 1520-05 QUE LLEVA LA CARGA DE LOS ALIMENTADORES 1520-01 Y 1520-04 PARA LEVANTAR LINEA PRIMARIA DE SUELO | S21082300197 | New_Event | Wire Down | Include | Include | Equipment | 19 | 2021-08-23 | 1292 | keep | 0 | Aug | 2021 | 0.00087998 | 4.6314e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 68
MAYAGÃœEZ | 2021-08-23 19:36 | 2021-08-23 20:29 | 3630 | 000:53 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECIONALIZO AVERIA Y SE CERRO INTERRUPTOR | M21082300168 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 53 | 2021-08-23 | 192390 | keep | 0 | Aug | 2021 | 0.13104 | 0.0024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 3630
HUMACAO | 2021-08-23 20:22 | 2021-08-23 20:23 | 3701 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21082300185 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-23 | 3701 | keep | 0 | Aug | 2021 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
MAYAGÃœEZ | 2021-08-23 20:29 | 2021-08-23 21:45 | 600 | 001:16 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR PARTIDO Y SE CERRO MACHETES | M21082300195 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 76 | 2021-08-23 | 45600 | keep | 0 | Aug | 2021 | 0.031058 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-23 20:35 | 2021-08-24 12:30 | 7 | 015:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21082300198 | New_Event | Bad Weather | Include | Include | Weather | 955 | 2021-08-23 | 6685 | keep | 0 | Aug | 2021 | 0.0045531 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2021-08-23 20:43 | 2021-08-23 22:05 | 80 | 001:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | P21082300104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 82 | 2021-08-23 | 6560 | keep | 0 | Aug | 2021 | 0.004468 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-08-23 20:49 | 2021-08-24 10:25 | 150 | 013:36 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21082300200 | New_Event | Vegetation Contact | Include | Include | Vegetation | 816 | 2021-08-23 | 122400 | keep | 0 | Aug | 2021 | 0.083366 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-08-23 20:54 | 2021-08-24 14:14 | 120 | 017:20 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | S21082300210 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1040 | 2021-08-23 | 124800 | keep | 0 | Aug | 2021 | 0.085001 | 8.1731e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 120
MAYAGÃœEZ | 2021-08-23 21:07 | 2021-08-24 14:43 | 100 | 017:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21082300136 | Partial_restoration | Bad Weather | Include | Include | Weather | 1056 | 2021-08-23 | 105600 | keep | 0 | Aug | 2021 | 0.071924 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-08-23 21:17 | 2021-08-23 21:18 | 641 | 000:01 | T | TRANSFORMADOR AVERIADO | RECIERRE DE INTERRUPTOR PERSONAL TRABAJANDO CON EVENTO TRANSFORMADOR EXPLOTO LLEVANDO 1206-02 | S21082300000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1 | 2021-08-23 | 641 | keep | 0 | Aug | 2021 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-08-23 21:17 | 2021-08-23 21:18 | 733 | 000:01 | T | TRANSFORMADOR AVERIADO | RECIERRE DE INTERRUPTOR PERSONAL TRABAJANDO CON EVENTO TRANSFORMADOR EXPLOTO CARGA POR EL 1206-01 | S21082300000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1 | 2021-08-23 | 733 | keep | 0 | Aug | 2021 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2021-08-23 21:18 | 2021-08-24 13:24 | 15 | 016:06 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 75KVA POR 100KVA SEGUN SE DISPONIA | S21082300012 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 966 | 2021-08-23 | 14490 | keep | 0 | Aug | 2021 | 0.0098691 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-08-23 21:38 | 2021-08-23 21:39 | 1001 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO | C21082300190 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-23 | 1001 | keep | 0 | Aug | 2021 | 0.00068178 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
PONCE | 2021-08-23 21:39 | 2021-08-24 12:45 | 150 | 015:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA REMPLAZO DE CAJA PRIMARIA | P21082300110 | New_Event | Cutout Failure | Include | Include | Equipment | 906 | 2021-08-23 | 135900 | keep | 0 | Aug | 2021 | 0.092561 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-08-23 21:51 | 2021-08-24 14:20 | 200 | 016:29 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A21082300153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 989 | 2021-08-23 | 197800 | keep | 0 | Aug | 2021 | 0.13472 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
PONCE | 2021-08-23 21:52 | 2021-08-23 22:40 | 75 | 000:48 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | P21082300112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 48 | 2021-08-23 | 3600 | keep | 0 | Aug | 2021 | 0.0024519 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
PONCE | 2021-08-23 21:55 | 2021-08-24 11:00 | 75 | 013:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE CORTE DE LINEA PARA CERRAR PUENTE ABIERTO | P21082300013 | New_Event | Wire Down | Include | Include | Equipment | 785 | 2021-08-23 | 58875 | keep | 0 | Aug | 2021 | 0.040099 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
SAN JUAN | 2021-08-23 22:04 | 2021-08-24 09:48 | 40 | 011:44 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | S21082300215 | New_Event | Vegetation Contact | Include | Include | Vegetation | 704 | 2021-08-23 | 28160 | keep | 0 | Aug | 2021 | 0.01918 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-08-23 22:04 | 2021-08-24 09:52 | 80 | 011:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21082300221 | New_Event | Bad Weather | Include | Include | Weather | 708 | 2021-08-23 | 56640 | keep | 0 | Aug | 2021 | 0.038577 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-23 22:26 | 2021-08-23 22:29 | 1221 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21082300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-08-23 | 3663 | keep | 0 | Aug | 2021 | 0.0024949 | 0.00083162 | Momentary | FALSE | FALSE | Not_TMED_Event | 1221
ARECIBO | 2021-08-23 22:56 | 2021-08-24 09:25 | 6 | 010:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A21082300157 | New_Event | Bad Weather | Include | Include | Weather | 629 | 2021-08-23 | 3774 | keep | 0 | Aug | 2021 | 0.0025705 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2021-08-23 23:11 | 2021-08-25 14:21 | 11 | 039:10 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR DE 25KVA X 25 KVA | C21082300195 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2350 | 2021-08-23 | 25850 | keep | 0 | Aug | 2021 | 0.017606 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
HUMACAO | 2021-08-23 23:26 | 2021-08-24 14:59 | 1 | 015:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | C21082300196 | New_Event |  |  | Include | Wildlife | 933 | 2021-08-23 | 933 | keep | 0 | Aug | 2021 | 0.00063546 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-08-23 23:27 | 2021-08-23 23:28 | 1464 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 8701-03 QUE LLEVA LA CARGA DEL 8701-02 | A21082300158 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-23 | 1464 | keep | 0 | Aug | 2021 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
ARECIBO | 2021-08-23 23:27 | 2021-08-23 23:28 | 759 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21082300158 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-23 | 759 | keep | 0 | Aug | 2021 | 0.00051695 | 0.00051695 | Momentary | FALSE | FALSE | Not_TMED_Event | 759
GUAYAMA | 2021-08-24 00:08 | 2021-08-24 11:35 | 47 | 011:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA | P21082400001 | New_Event | Cutout Failure | Include | Include | Equipment | 687 | 2021-08-24 | 32289 | keep | 0 | Aug | 2021 | 0.021992 | 3.2011e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 47
PONCE | 2021-08-24 00:11 | 2021-08-24 11:04 | 35 | 010:53 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | P21042400003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 653 | 2021-08-24 | 22855 | keep | 0 | Aug | 2021 | 0.015566 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-08-24 01:06 | 2021-08-24 10:50 | 80 | 009:44 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21082400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 584 | 2021-08-24 | 46720 | keep | 0 | Aug | 2021 | 0.031821 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-08-24 01:19 | 2021-08-24 12:24 | 30 | 011:05 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21082400001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 665 | 2021-08-24 | 19950 | keep | 0 | Aug | 2021 | 0.013588 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-08-24 01:26 | 2021-08-25 10:45 | 30 | 033:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21082500002 | New_Event | Bad Weather | Include | Include | Weather | 1999 | 2021-08-24 | 59970 | keep | 0 | Aug | 2021 | 0.040845 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-08-24 01:58 | 2021-08-30 11:07 | 1 | 153:09 | P | OTRAS CAUSAS | 1 X 20 EN RISER PROBLEMA DE CLIENTE | M21083000073 | New_Event | Other Causes | Include | Include | Other | 9189 | 2021-08-24 | 9189 | keep | 0 | Aug | 2021 | 0.0062586 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2021-08-24 02:56 | 2021-08-24 11:23 | 30 | 008:27 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21082400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 507 | 2021-08-24 | 15210 | keep | 0 | Aug | 2021 | 0.010359 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-08-24 05:06 | 2021-08-24 12:29 | 100 | 007:23 | P | PARARRAYOS DEFECTUOSO | 1 X 40 Y 1 X 65 EN CORTES DE LINEA REMPLAZO PARARRAYO | C21082400004 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 443 | 2021-08-24 | 44300 | keep | 0 | Aug | 2021 | 0.030173 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-08-24 05:17 | 2021-08-24 07:24 | 1000 | 002:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZARON DISCOS ROTOS | R21082400003 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 127 | 2021-08-24 | 127000 | keep | 0 | Aug | 2021 | 0.086499 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
CANOVANAS | 2021-08-24 05:28 | 2021-08-24 07:24 | 10 | 001:56 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 8 EN TRANSFORMADOR SE REEMPLAZO POSTE SECUNDARIO ROTO POR AUTO | R21082400006 | New_Event |  |  | Include | Wildlife | 116 | 2021-08-24 | 1160 | keep | 0 | Aug | 2021 | 0.00079007 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-08-24 05:28 | 2021-08-24 10:05 | 50 | 004:37 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21082400006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 277 | 2021-08-24 | 13850 | keep | 0 | Aug | 2021 | 0.0094332 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-24 05:40 | 2021-08-24 12:30 | 80 | 006:50 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | M21082400003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 410 | 2021-08-24 | 32800 | keep | 0 | Aug | 2021 | 0.02234 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
ARECIBO | 2021-08-24 06:02 | 2021-08-24 06:03 | 3431 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21082400003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-24 | 3431 | keep | 0 | Aug | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2021-08-24 06:03 | 2021-08-24 17:35 | 30 | 011:32 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMA | A21082400060 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 692 | 2021-08-24 | 20760 | keep | 0 | Aug | 2021 | 0.01414 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BARRANQUITAS | 2021-08-24 06:03 | 2021-08-24 06:04 | 1604 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C21082400000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-24 | 1604 | keep | 0 | Aug | 2021 | 0.0010925 | 0.0010925 | Momentary | FALSE | FALSE | Not_TMED_Event | 1604
BARRANQUITAS | 2021-08-24 06:04 | 2021-08-24 16:24 | 80 | 010:20 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE | C21082400016 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 620 | 2021-08-24 | 49600 | keep | 0 | Aug | 2021 | 0.033782 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2021-08-24 06:05 | 2021-08-24 06:06 | 1227 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21082400004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-24 | 1227 | keep | 0 | Aug | 2021 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2021-08-24 06:06 | 2021-08-24 13:20 | 40 | 007:14 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21082400030 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 434 | 2021-08-24 | 17360 | keep | 0 | Aug | 2021 | 0.011824 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-08-24 06:09 | 2021-08-24 06:10 | 308 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A21082400000 | New_Event |  |  | Include | Wildlife | 1 | 2021-08-24 | 308 | keep | 0 | Aug | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
ARECIBO | 2021-08-24 06:10 | 2021-08-24 12:30 | 25 | 006:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | A21082400006 | 1st_after_momentary |  |  | Include | Wildlife | 380 | 2021-08-24 | 9500 | keep | 0 | Aug | 2021 | 0.0064704 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
SAN JUAN | 2021-08-24 06:14 | 2021-08-24 06:15 | 36 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-24 | 36 | keep | 0 | Aug | 2021 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-08-24 06:14 | 2021-08-24 06:15 | 172 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA. LLEVA 1620-01, 85% DEL 1336-10, 90% DEL 1336-07. | S21082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-24 | 172 | keep | 0 | Aug | 2021 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2021-08-24 06:20 | 2021-08-24 11:18 | 5 | 004:58 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | S21082400007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 298 | 2021-08-24 | 1490 | keep | 0 | Aug | 2021 | 0.0010148 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2021-08-24 06:23 | 2021-08-24 15:26 | 20 | 009:03 | P | NO SE REPORTO CAUSA | 1 SMU 20 DE 40 AMP NO CAUSA | C21082400008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 543 | 2021-08-24 | 10860 | keep | 0 | Aug | 2021 | 0.0073967 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2021-08-24 06:58 | 2021-08-24 09:01 | 7 | 002:03 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | R21082400010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 123 | 2021-08-24 | 861 | keep | 0 | Aug | 2021 | 0.00058642 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-08-24 07:04 | 2021-08-24 18:05 | 30 | 011:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21082400010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 661 | 2021-08-24 | 19830 | keep | 0 | Aug | 2021 | 0.013506 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-08-24 07:16 | 2021-08-24 18:46 | 5 | 011:30 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR DE 15KVA X 15KVA | R21082400011 | New_Event | Service Transformer Failure | Include | Include | Equipment | 690 | 2021-08-24 | 3450 | keep | 0 | Aug | 2021 | 0.0023498 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2021-08-24 07:24 | 2021-08-24 07:26 | 4188 | 000:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO SE VERIFICO PERSONAL FUERA | R21082400003 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2021-08-24 | 8376 | keep | 0 | Aug | 2021 | 0.0057049 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-08-24 07:26 | 2021-08-24 07:54 | 1000 | 000:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZARON DISCOS ROTOS | R21082400003 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 28 | 2021-08-24 | 28000 | keep | 0 | Aug | 2021 | 0.019071 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
CANOVANAS | 2021-08-24 07:26 | 2021-08-24 07:54 | 10 | 000:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 8 EN TRANSFORMADOR SE REEMPLAZO POSTE SECUNDARIO ROTO POR AUTO | R21082400006 | Partial_restoration |  |  | Include | Wildlife | 28 | 2021-08-24 | 280 | keep | 0 | Aug | 2021 | 0.00019071 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-08-24 07:27 | 2021-08-24 07:28 | 1648 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | R21082400015 | New_Event |  |  | Include | Wildlife | 1 | 2021-08-24 | 1648 | keep | 0 | Aug | 2021 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2021-08-24 07:28 | 2021-08-24 10:33 | 40 | 003:05 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | R21042400022 | 1st_after_momentary |  |  | Include | Wildlife | 185 | 2021-08-24 | 7400 | keep | 0 | Aug | 2021 | 0.0050401 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-08-24 07:45 | 2021-08-24 21:39 | 6 | 013:54 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA X 50 KVA | C21082400015 | New_Event | Service Transformer Failure | Include | Include | Equipment | 834 | 2021-08-24 | 5004 | keep | 0 | Aug | 2021 | 0.0034082 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2021-08-24 07:54 | 2021-08-24 07:57 | 4188 | 000:03 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO SE VERIFICO PERSONAL FUERA SE CERRO POR CONTROL | R21082400003 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 3 | 2021-08-24 | 12564 | keep | 0 | Aug | 2021 | 0.0085573 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-08-24 07:57 | 2021-08-24 10:46 | 1000 | 002:49 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZARON DISCOS ROTOS | R21082400003 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 169 | 2021-08-24 | 169000 | keep | 0 | Aug | 2021 | 0.11511 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
CANOVANAS | 2021-08-24 07:57 | 2021-08-24 15:43 | 10 | 007:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 8 EN TRANSFORMADOR SE REEMPLAZO POSTE SECUNDARIO ROTO POR AUTO | R21082400006 | Partial_restoration |  |  | Include | Wildlife | 466 | 2021-08-24 | 4660 | keep | 0 | Aug | 2021 | 0.0031739 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-24 08:06 | 2021-08-24 14:03 | 7 | 005:57 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21082400003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 357 | 2021-08-24 | 2499 | keep | 0 | Aug | 2021 | 0.0017021 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-08-24 08:14 | 2021-08-24 10:49 | 100 | 002:35 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA POR PAJARO QUE CRUZO LINEAS | M21082400020 | New_Event |  |  | Include | Wildlife | 155 | 2021-08-24 | 15500 | keep | 0 | Aug | 2021 | 0.010557 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-08-24 08:24 | 2021-08-24 20:10 | 250 | 011:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETES Y SE LEVANTO CONDUCTOR EN EL SUELO | B21082400045 | New_Event | Wire Down | Include | Include | Equipment | 706 | 2021-08-24 | 176500 | keep | 0 | Aug | 2021 | 0.12021 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
FAJARDO | 2021-08-24 08:31 | 2021-08-24 09:54 | 4 | 001:23 | P | DESGANCHE | 1 X 65 EN CORTES DE LINEA | R21082400018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2021-08-24 | 332 | keep | 0 | Aug | 2021 | 0.00022612 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
VEGA BAJA | 2021-08-24 08:31 | 2021-08-24 13:05 | 35 | 004:34 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B21082400009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 274 | 2021-08-24 | 9590 | keep | 0 | Aug | 2021 | 0.0065317 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
PONCE | 2021-08-24 08:46 | 2021-08-24 12:10 | 85 | 003:24 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | P21082400012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 204 | 2021-08-24 | 17340 | keep | 0 | Aug | 2021 | 0.01181 | 5.7893e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 85
BAYAMON | 2021-08-24 09:09 | 2021-08-25 16:11 | 30 | 031:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA CARGA POR EL 1133-02 | S21082400027 | New_Event | Wire Down | Include | Include | Equipment | 1862 | 2021-08-24 | 55860 | keep | 0 | Aug | 2021 | 0.038046 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-08-24 09:17 | 2021-08-24 18:13 | 25 | 008:56 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE LLEVO CONDUCTOR A CAJA PRIMARIA | S21082400046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 536 | 2021-08-24 | 13400 | keep | 0 | Aug | 2021 | 0.0091267 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-08-24 09:17 | 2021-08-24 11:44 | 75 | 002:27 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y 1 X 20 EN CORTE DE LINEA POR DESGANCHE | M21082400036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2021-08-24 | 11025 | keep | 0 | Aug | 2021 | 0.0075091 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
ARECIBO | 2021-08-24 09:20 | 2021-08-24 12:29 | 8 | 003:09 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE 25 KVA X 25 KVA | A21082400014 | New_Event | Service Transformer Failure | Include | Include | Equipment | 189 | 2021-08-24 | 1512 | keep | 0 | Aug | 2021 | 0.0010298 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2021-08-24 09:20 | 2021-08-24 15:15 | 50 | 005:55 | P | RELEVO DE CARGA AUTOMATICO | VIA LIBRE D2021-00090 RELOCALIZAR LINEA PRIMARIA | A21082400016 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 355 | 2021-08-24 | 17750 | keep | 0 | Aug | 2021 | 0.012089 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-08-24 09:40 | 2021-08-24 13:12 | 1 | 003:32 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | P21082400017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 212 | 2021-08-24 | 212 | keep | 0 | Aug | 2021 | 0.00014439 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-08-24 09:45 | 2021-08-24 09:46 | 908 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE | B21082400000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2021-08-24 | 908 | keep | 0 | Aug | 2021 | 0.00061843 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
VEGA BAJA | 2021-08-24 09:46 | 2021-08-24 13:22 | 50 | 003:36 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN RISER SE SECCIONALIZO TRAMO SOTERRADO AVERIADO DE T-11 @ T-12. EL T-12 ESTA FUERA DE SERVICIO | B21082400019 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 216 | 2021-08-24 | 10800 | keep | 0 | Aug | 2021 | 0.0073558 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-24 09:47 | 2021-08-24 11:38 | 70 | 001:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | M21082400040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2021-08-24 | 7770 | keep | 0 | Aug | 2021 | 0.0052921 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
PONCE | 2021-08-24 09:50 | 2021-08-24 15:31 | 50 | 005:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | P21082400019 | New_Event |  |  | Include | Wildlife | 341 | 2021-08-24 | 17050 | keep | 0 | Aug | 2021 | 0.011613 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-24 09:59 | 2021-08-24 15:00 | 20 | 005:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO SE CERRO CORTE DE LINEA | M21082400043 | New_Event | Wire Down | Include | Include | Equipment | 301 | 2021-08-24 | 6020 | keep | 0 | Aug | 2021 | 0.0041002 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-08-24 09:59 | 2021-08-24 10:26 | 1399 | 000:27 | T | ERROR HUMANO | PERSONAL DESGANCHANDO DISPARO INTERRUPTOR SE VERIFICO PERSONAL FUERA DE LAS LINEAS Y SE CERRO INTERRUPTOR | A21082400020 | New_Event | Human Error | Include | Include | Other | 27 | 2021-08-24 | 37773 | keep | 0 | Aug | 2021 | 0.025727 | 0.00095285 | Sustained | FALSE | TRUE | Not_TMED_Event | 1399
HUMACAO | 2021-08-24 10:04 | 2021-08-24 16:46 | 7 | 006:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21082400034 | New_Event | Secondary Wire Down | Include | Include | Equipment | 402 | 2021-08-24 | 2814 | keep | 0 | Aug | 2021 | 0.0019166 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2021-08-24 10:04 | 2021-08-24 14:51 | 40 | 004:47 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA SE RETIRO AVE | B21082400018 | New_Event |  |  | Include | Wildlife | 287 | 2021-08-24 | 11480 | keep | 0 | Aug | 2021 | 0.007819 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-08-24 10:16 | 2021-08-25 17:19 | 50 | 031:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | S21082400053 | New_Event | Wire Down | Include | Include | Equipment | 1863 | 2021-08-24 | 93150 | keep | 0 | Aug | 2021 | 0.063444 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-08-24 10:17 | 2021-08-24 11:40 | 40 | 001:23 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21082400034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 83 | 2021-08-24 | 3320 | keep | 0 | Aug | 2021 | 0.0022612 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-08-24 10:23 | 2021-08-24 15:16 | 10 | 004:53 | P | NO SE REPORTO CAUSA | 2 X 15 EN TRANSFORMADOR | B21082400020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 293 | 2021-08-24 | 2930 | keep | 0 | Aug | 2021 | 0.0019956 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-24 10:37 | 2021-08-24 10:45 | 2 | 000:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A21082400007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 8 | 2021-08-24 | 16 | keep | 0 | Aug | 2021 | 1.0898e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2021-08-24 10:40 | 2021-08-24 13:45 | 33 | 003:05 | P | DESGANCHE | SE ABRE CORTE DE LINEA PARA HACER DESGANCHE | P21085240004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2021-08-24 | 6105 | keep | 0 | Aug | 2021 | 0.0041581 | 2.2476e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 33
SAN JUAN | 2021-08-24 10:48 | 2021-08-25 13:15 | 12 | 026:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO SECUNDARIA Y SE REPARO TOMA CARGA POR EL 1113-04 | S21082400092 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1587 | 2021-08-24 | 19044 | keep | 0 | Aug | 2021 | 0.012971 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2021-08-24 11:09 | 2021-08-24 17:40 | 50 | 006:31 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | P21082400032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 391 | 2021-08-24 | 19550 | keep | 0 | Aug | 2021 | 0.013315 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-24 11:15 | 2021-08-24 15:24 | 25 | 004:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | S21082400038 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 249 | 2021-08-24 | 6225 | keep | 0 | Aug | 2021 | 0.0042398 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BARRANQUITAS | 2021-08-24 11:17 | 2021-08-24 13:27 | 40 | 002:10 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C21082400047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2021-08-24 | 5200 | keep | 0 | Aug | 2021 | 0.0035417 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-08-24 11:22 | 2021-08-25 09:49 | 9 | 022:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO CONECTORES EN SECUNDARIA | C21082400049 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1347 | 2021-08-24 | 12123 | keep | 0 | Aug | 2021 | 0.0082569 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2021-08-24 11:23 | 2021-08-24 18:23 | 30 | 007:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M21082400067 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 420 | 2021-08-24 | 12600 | keep | 0 | Aug | 2021 | 0.0085818 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-08-24 11:23 | 2021-08-24 17:45 | 40 | 006:22 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A21082400029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 382 | 2021-08-24 | 15280 | keep | 0 | Aug | 2021 | 0.010407 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-08-24 11:32 | 2021-08-24 14:50 | 150 | 003:18 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | A21082400031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2021-08-24 | 29700 | keep | 0 | Aug | 2021 | 0.020229 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-08-24 12:03 | 2021-08-24 16:49 | 40 | 004:46 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA Y 1 X 25 EN BOMBAS A.A.A | B21082400035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 286 | 2021-08-24 | 11440 | keep | 0 | Aug | 2021 | 0.0077917 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-08-24 12:04 | 2021-08-25 15:40 | 55 | 027:36 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR | C21082400092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1656 | 2021-08-24 | 91080 | keep | 0 | Aug | 2021 | 0.062034 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
BAYAMON | 2021-08-24 12:16 | 2021-08-24 15:48 | 1 | 003:32 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR Y SE CERRO BAJANTE SECUNDARIO Y SE REALIZO DESGANCHE | B21082400039 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 212 | 2021-08-24 | 212 | keep | 0 | Aug | 2021 | 0.00014439 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-08-24 12:21 | 2021-08-24 12:50 | 6 | 000:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO TRANSFORMADOR PARA CONECTAR NEUTRAL PRIMARIO | C21082300184 | New_Event | Wire Down | Include | Include | Equipment | 29 | 2021-08-24 | 174 | keep | 0 | Aug | 2021 | 0.00011851 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-08-24 12:23 | 2021-08-24 15:58 | 1 | 003:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | M21082400078 | New_Event | Bad Weather | Include | Include | Weather | 215 | 2021-08-24 | 215 | keep | 0 | Aug | 2021 | 0.00014644 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2021-08-24 12:30 | 2021-08-24 14:35 | 13 | 002:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA NO SE REMPLAZO FUSIBLE | P21082400015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 125 | 2021-08-24 | 1625 | keep | 0 | Aug | 2021 | 0.0011068 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CANOVANAS | 2021-08-24 12:40 | 2021-08-24 13:20 | 50 | 000:40 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA LLUVIAS | R21042400040 | New_Event | Bad Weather | Include | Include | Weather | 40 | 2021-08-24 | 2000 | keep | 0 | Aug | 2021 | 0.0013622 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-08-24 12:54 | 2021-08-24 12:55 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21082400058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-24 | 1827 | keep | 0 | Aug | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
SAN JUAN | 2021-08-24 13:10 | 2021-08-24 13:11 | 1615 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-24 | 1615 | keep | 0 | Aug | 2021 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
SAN JUAN | 2021-08-24 13:22 | 2021-08-24 17:08 | 150 | 003:46 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | R21082400046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2021-08-24 | 33900 | keep | 0 | Aug | 2021 | 0.023089 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
VEGA BAJA | 2021-08-24 13:22 | 2021-08-24 13:23 | 908 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE | B21082400000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2021-08-24 | 908 | keep | 0 | Aug | 2021 | 0.00061843 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
VEGA BAJA | 2021-08-24 13:23 | 2021-08-24 16:57 | 50 | 003:34 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN RISER SE SECCIONALIZO TRAMO SOTERRADO AVERIADO DE T-11 @ T-12. EL T-12 ESTA FUERA DE SERVICIO | B21082400019 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 214 | 2021-08-24 | 10700 | keep | 0 | Aug | 2021 | 0.0072877 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2021-08-24 13:30 | 2021-08-24 16:35 | 1 | 003:05 | P | OTRAS CAUSAS | SE ABRIO RISER PARA INSTALAR CORTE DE LINEA | M21082400087 | New_Event | Other Causes | Include | Include | Other | 185 | 2021-08-24 | 185 | keep | 0 | Aug | 2021 | 0.000126 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
UTUADO | 2021-08-24 13:43 | 2021-08-24 16:55 | 15 | 003:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE RETEZO LINEAS | A21082400048 | New_Event | Wire Down | Include | Include | Equipment | 192 | 2021-08-24 | 2880 | keep | 0 | Aug | 2021 | 0.0019616 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
SAN JUAN | 2021-08-24 14:11 | 2021-08-25 10:24 | 45 | 020:13 | P | DESGANCHE | SE CERRO PUENTE DE CAJA A LINEA Y DESGANCHE | S21082400067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1213 | 2021-08-24 | 54585 | keep | 0 | Aug | 2021 | 0.037178 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
MAYAGÃœEZ | 2021-08-24 14:19 | 2021-08-24 16:53 | 3458 | 002:34 | T | DESGANCHE | DISPARO DEL INTERRUPTOR SE RETIRO RAMAS SOBRE LAS LINEAS | M21082400094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2021-08-24 | 532532 | keep | 0 | Aug | 2021 | 0.36271 | 0.0023552 | Sustained | FALSE | TRUE | Not_TMED_Event | 3458
AGUADILLA | 2021-08-24 14:36 | 2021-08-24 15:32 | 390 | 000:56 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DEL INTERRUPTOR LINEA ZAFADA DE AISLADOR | M21082400097 | New_Event | Wire Down | Include | Include | Equipment | 56 | 2021-08-24 | 21840 | keep | 0 | Aug | 2021 | 0.014875 | 0.00026563 | Sustained | FALSE | TRUE | Not_TMED_Event | 390
BAYAMON | 2021-08-24 14:39 | 2021-08-24 17:33 | 53 | 002:54 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | S21082400066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2021-08-24 | 9222 | keep | 0 | Aug | 2021 | 0.0062811 | 3.6098e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 53
PONCE | 2021-08-24 14:55 | 2021-08-24 18:50 | 12 | 003:55 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRE TRANSFORMADOR PARA REEMPLAZAR POSTE SECUNDARIO | P210824000XX | New_Event | Secondary Defective Pole | Include | Include | Equipment | 235 | 2021-08-24 | 2820 | keep | 0 | Aug | 2021 | 0.0019207 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-08-24 15:00 | 2021-08-24 17:30 | 8 | 002:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M21082400110 | New_Event | Secondary Wire Down | Include | Include | Equipment | 150 | 2021-08-24 | 1200 | keep | 0 | Aug | 2021 | 0.00081731 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-08-24 15:06 | 2021-08-24 15:07 | 1617 | 000:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21082400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-24 | 1617 | keep | 0 | Aug | 2021 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
SAN JUAN | 2021-08-24 15:07 | 2021-08-27 17:27 | 8 | 074:20 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25 KVA X 37.5 KVA | R21082400026 | New_Event | Service Transformer Failure | Include | Include | Equipment | 4460 | 2021-08-24 | 35680 | keep | 0 | Aug | 2021 | 0.024301 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-08-24 15:09 | 2021-08-24 16:57 | 1617 | 001:48 | T | DESGANCHE | DISPARO DEL INTERRUPTOR RAMAS SOBRE LAS LINEAS | M21082400113 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 108 | 2021-08-24 | 174636 | keep | 0 | Aug | 2021 | 0.11894 | 0.0011013 | Sustained | FALSE | TRUE | Not_TMED_Event | 1617
ARECIBO | 2021-08-24 15:17 | 2021-08-24 18:00 | 40 | 002:43 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CONVERTIDOR DESCARGAS ELECTRICAS | A21082400059 | New_Event | Bad Weather | Include | Include | Weather | 163 | 2021-08-24 | 6520 | keep | 0 | Aug | 2021 | 0.0044407 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-08-24 15:22 | 2021-08-24 17:08 | 8 | 001:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21082400074 | New_Event | Secondary Wire Down | Include | Include | Equipment | 106 | 2021-08-24 | 848 | keep | 0 | Aug | 2021 | 0.00057757 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-08-24 15:25 | 2021-08-24 17:28 | 7 | 002:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO Y SE REPARO SECUNDARIA | S21082400060 | New_Event | Secondary Wire Down | Include | Include | Equipment | 123 | 2021-08-24 | 861 | keep | 0 | Aug | 2021 | 0.00058642 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-08-24 15:27 | 2021-08-24 16:50 | 40 | 001:23 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21082400067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2021-08-24 | 3320 | keep | 0 | Aug | 2021 | 0.0022612 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BARRANQUITAS | 2021-08-24 15:37 | 2021-08-24 15:38 | 2565 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C21082400075 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-24 | 2565 | keep | 0 | Aug | 2021 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2021-08-24 15:38 | 2021-08-24 16:55 | 855 | 001:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE EN LA SALIDA DEL ALIMENTADOR | C21082400088 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 77 | 2021-08-24 | 65835 | keep | 0 | Aug | 2021 | 0.04484 | 0.00058234 | Sustained | FALSE | FALSE | Not_TMED_Event | 855
UTUADO | 2021-08-24 15:45 | 2021-08-24 16:10 | 6 | 000:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE ZAFADO | A21082400052 | New_Event | Wire Down | Include | Include | Equipment | 25 | 2021-08-24 | 150 | keep | 0 | Aug | 2021 | 0.00010216 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2021-08-24 15:53 | 2021-08-24 19:50 | 40 | 003:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A21082400063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 237 | 2021-08-24 | 9480 | keep | 0 | Aug | 2021 | 0.0064568 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-08-24 16:07 | 2021-08-25 17:48 | 20 | 025:41 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR 75KVA X 75KVA T-7 | B21082400026 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1541 | 2021-08-24 | 30820 | keep | 0 | Aug | 2021 | 0.020991 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2021-08-24 16:24 | 2021-08-24 18:05 | 10 | 001:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | R21082400056 | New_Event | Secondary Wire Down | Include | Include | Equipment | 101 | 2021-08-24 | 1010 | keep | 0 | Aug | 2021 | 0.00068791 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-08-24 16:29 | 2021-08-24 17:27 | 10 | 000:58 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21082400059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 58 | 2021-08-24 | 580 | keep | 0 | Aug | 2021 | 0.00039504 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-08-24 16:51 | 2021-08-24 21:34 | 40 | 004:43 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21082400094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2021-08-24 | 11320 | keep | 0 | Aug | 2021 | 0.00771 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
UTUADO | 2021-08-24 16:52 | 2021-08-25 13:50 | 60 | 020:58 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21082400071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1258 | 2021-08-24 | 75480 | keep | 0 | Aug | 2021 | 0.051409 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BARRANQUITAS | 2021-08-24 16:55 | 2021-08-24 18:47 | 2565 | 001:52 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE EN LA SALIDA DEL ALIMENTADOR | C21082400088 | Additional_clients | Wire Down | Include | Include | Equipment | 112 | 2021-08-24 | 287280 | keep | 0 | Aug | 2021 | 0.19567 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-24 16:57 | 2021-08-24 18:30 | 100 | 001:33 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21082400142 | New_Event | Bad Weather | Include | Include | Weather | 93 | 2021-08-24 | 9300 | keep | 0 | Aug | 2021 | 0.0063342 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-08-24 16:57 | 2021-08-24 16:58 | 908 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE | B21082400000 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1 | 2021-08-24 | 908 | keep | 0 | Aug | 2021 | 0.00061843 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-08-24 16:58 | 2021-08-24 17:17 | 50 | 000:19 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN RISER SE SECCIONALIZO TRAMO SOTERRADO AVERIADO DE T-11 @ T-12. EL T-12 ESTA FUERA DE SERVICIO | B21082400019 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 19 | 2021-08-24 | 950 | keep | 0 | Aug | 2021 | 0.00064704 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-24 17:11 | 2021-08-24 17:12 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6007-05 | M21082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-24 | 393 | keep | 0 | Aug | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2021-08-24 17:11 | 2021-08-24 17:12 | 4 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR 6007-04 EL CUAL LLEVA LA CARGA DEL 6007-05 NO SE REPORTO CAUSA | M21082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-24 | 4 | keep | 0 | Aug | 2021 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-08-24 17:16 | 2021-08-24 19:00 | 200 | 001:44 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A21082400077 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 104 | 2021-08-24 | 20800 | keep | 0 | Aug | 2021 | 0.014167 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
VEGA BAJA | 2021-08-24 17:17 | 2021-08-24 17:18 | 908 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE | B21082400000 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1 | 2021-08-24 | 908 | keep | 0 | Aug | 2021 | 0.00061843 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-08-24 17:18 | 2021-08-24 19:30 | 50 | 002:12 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN RISER SE SECCIONALIZO TRAMO SOTERRADO AVERIADO DE T-11 @ T-12. EL T-12 ESTA FUERA DE SERVICIO | B21082400019 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 132 | 2021-08-24 | 6600 | keep | 0 | Aug | 2021 | 0.0044952 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-24 17:27 | 2021-08-24 17:28 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6007-05 | M21082400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-24 | 393 | keep | 0 | Aug | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2021-08-24 17:27 | 2021-08-24 17:28 | 4 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR 6007-04 EL CUAL LLEVA LA CARGA DEL 6007-05 NO SE REPORTO CAUSA | M21082400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-24 | 4 | keep | 0 | Aug | 2021 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-08-24 17:43 | 2021-08-24 17:44 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6007-05 | M21082400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-24 | 393 | keep | 0 | Aug | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2021-08-24 17:43 | 2021-08-24 17:44 | 4 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR 6007-04 EL CUAL LLEVA LA CARGA DEL 6007-05 NO SE REPORTO CAUSA | M21082400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-24 | 4 | keep | 0 | Aug | 2021 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2021-08-24 17:47 | 2021-08-24 17:48 | 1 | 000:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | P21082400021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-24 | 1 | keep | 0 | Aug | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | TRUE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-08-24 17:48 | 2021-08-24 18:30 | 60 | 000:42 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21082400167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 42 | 2021-08-24 | 2520 | keep | 0 | Aug | 2021 | 0.0017164 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-08-24 17:54 | 2021-08-25 15:36 | 1 | 021:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21082400169 | New_Event | Bad Weather | Include | Include | Weather | 1302 | 2021-08-24 | 1302 | keep | 0 | Aug | 2021 | 0.00088679 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-08-24 18:00 | 2021-08-24 20:00 | 50 | 002:00 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21082400171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2021-08-24 | 6000 | keep | 0 | Aug | 2021 | 0.0040866 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-24 18:06 | 2021-08-24 20:42 | 100 | 002:36 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21082400173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2021-08-24 | 15600 | keep | 0 | Aug | 2021 | 0.010625 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-08-24 18:26 | 2021-08-25 15:00 | 8 | 020:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON LINEAS SECUNDARIAS PARTIDAS | A21082400086 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1234 | 2021-08-24 | 9872 | keep | 0 | Aug | 2021 | 0.0067238 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
HUMACAO | 2021-08-24 18:27 | 2021-08-25 10:04 | 11 | 015:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | C21082400109 | New_Event | Secondary Wire Down | Include | Include | Equipment | 937 | 2021-08-24 | 10307 | keep | 0 | Aug | 2021 | 0.0070201 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2021-08-24 18:56 | 2021-08-24 20:10 | 10 | 001:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21082400014 | New_Event | Secondary Wire Down | Include | Include | Equipment | 74 | 2021-08-24 | 740 | keep | 0 | Aug | 2021 | 0.00050401 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-08-24 18:59 | 2021-08-24 21:50 | 80 | 002:51 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA ARBOL SOBRE LINEAS | M21082400180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2021-08-24 | 13680 | keep | 0 | Aug | 2021 | 0.0093174 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
VEGA BAJA | 2021-08-24 19:14 | 2021-08-25 20:08 | 35 | 024:54 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE | B21082400102 | New_Event | Defective Pole | Include | Include | Equipment | 1494 | 2021-08-24 | 52290 | keep | 0 | Aug | 2021 | 0.035614 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-08-24 19:25 | 2021-08-24 20:55 | 35 | 001:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21082400190 | New_Event | Bad Weather | Include | Include | Weather | 90 | 2021-08-24 | 3150 | keep | 0 | Aug | 2021 | 0.0021455 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
VEGA BAJA | 2021-08-24 19:30 | 2021-08-25 20:33 | 15 | 025:03 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVISIONAL DEL T-12 AL T-11 | B21082400019 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1503 | 2021-08-24 | 22545 | keep | 0 | Aug | 2021 | 0.015355 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-24 19:44 | 2021-08-24 19:45 | 1935 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 Y APARENTEMENTE TIENE PUENTE ABIERTO | B21082400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-24 | 1935 | keep | 0 | Aug | 2021 | 0.0013179 | 0.0013179 | Momentary | FALSE | TRUE | Not_TMED_Event | 1935
BAYAMON | 2021-08-24 19:44 | 2021-08-24 19:45 | 3 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 Y APARENEMENTE TIENE PUENTE ABIERTO | B21082400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-24 | 3 | keep | 0 | Aug | 2021 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | TRUE | Not_TMED_Event | 3
BAYAMON | 2021-08-24 19:44 | 2021-08-24 19:45 | 61 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 Y APARENEMENTE TIENE PUENTE ABIERTO | B21082400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-24 | 61 | keep | 0 | Aug | 2021 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 61
BAYAMON | 2021-08-24 19:44 | 2021-08-24 19:45 | 1501 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 Y APARENEMENTE TIENE PUENTE ABIERTO | B21082400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-24 | 1501 | keep | 0 | Aug | 2021 | 0.0010223 | 0.0010223 | Momentary | FALSE | TRUE | Not_TMED_Event | 1501
BAYAMON | 2021-08-24 19:44 | 2021-08-24 19:45 | 546 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 Y APARENEMENTE TIENE PUENTE ABIERTO | B21082400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-24 | 546 | keep | 0 | Aug | 2021 | 0.00037188 | 0.00037188 | Momentary | FALSE | TRUE | Not_TMED_Event | 546
BAYAMON | 2021-08-24 19:44 | 2021-08-24 19:45 | 959 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 Y APARENEMENTE TIENE PUENTE ABIERTO | S21082400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-24 | 959 | keep | 0 | Aug | 2021 | 0.00065317 | 0.00065317 | Momentary | FALSE | TRUE | Not_TMED_Event | 959
BAYAMON | 2021-08-24 19:44 | 2021-08-24 19:45 | 1297 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 Y APARENEMENTE TIENE PUENTE ABIERTO | S21082400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-24 | 1297 | keep | 0 | Aug | 2021 | 0.00088338 | 0.00088338 | Momentary | FALSE | TRUE | Not_TMED_Event | 1297
BAYAMON | 2021-08-24 19:44 | 2021-08-24 19:45 | 451 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 Y APARENEMENTE TIENE PUENTE ABIERTO | S21082400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-24 | 451 | keep | 0 | Aug | 2021 | 0.00030717 | 0.00030717 | Momentary | FALSE | TRUE | Not_TMED_Event | 451
BAYAMON | 2021-08-24 19:44 | 2021-08-24 19:45 | 1264 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 Y APARENEMENTE TIENE PUENTE ABIERTO | S21082400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-24 | 1264 | keep | 0 | Aug | 2021 | 0.0008609 | 0.0008609 | Momentary | FALSE | TRUE | Not_TMED_Event | 1264
BAYAMON | 2021-08-24 19:44 | 2021-08-24 19:45 | 620 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 Y APARENEMENTE TIENE PUENTE ABIERTO | S21082400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-24 | 620 | keep | 0 | Aug | 2021 | 0.00042228 | 0.00042228 | Momentary | FALSE | TRUE | Not_TMED_Event | 620
BAYAMON | 2021-08-24 19:45 | 2021-08-24 21:44 | 690 | 001:59 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 PUENTE ABIERTO | B21082400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 119 | 2021-08-24 | 82110 | keep | 0 | Aug | 2021 | 0.055925 | 0.00046996 | Sustained | FALSE | TRUE | Not_TMED_Event | 690
BAYAMON | 2021-08-24 19:45 | 2021-08-24 21:44 | 1 | 001:59 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 PUENTE ABIERTO | B21082400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 119 | 2021-08-24 | 119 | keep | 0 | Aug | 2021 | 8.105e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-08-24 19:45 | 2021-08-24 21:44 | 20 | 001:59 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 PUENTE ABIERTO | B21082400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 119 | 2021-08-24 | 2380 | keep | 0 | Aug | 2021 | 0.001621 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-08-24 19:45 | 2021-08-24 21:44 | 500 | 001:59 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 PUENTE ABIERTO | B21082400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 119 | 2021-08-24 | 59500 | keep | 0 | Aug | 2021 | 0.040525 | 0.00034055 | Sustained | FALSE | TRUE | Not_TMED_Event | 500
BAYAMON | 2021-08-24 19:45 | 2021-08-24 21:44 | 175 | 001:59 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 PUENTE ABIERTO | B21082400000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 119 | 2021-08-24 | 20825 | keep | 0 | Aug | 2021 | 0.014184 | 0.00011919 | Sustained | FALSE | TRUE | Not_TMED_Event | 175
AGUADILLA | 2021-08-24 19:51 | 2021-08-25 15:30 | 5 | 019:39 | P | DESGANCHE | 1 X 8 EN TRANSFORMADOR SE RETIRO ENREDADERA | M21082400197 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1179 | 2021-08-24 | 5895 | keep | 0 | Aug | 2021 | 0.0040151 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2021-08-24 20:36 | 2021-08-25 11:00 | 95 | 014:24 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 Y 2 X 40 EN CORTES DE LINEAS REPARO AISLADOR ROTO | R21082400064 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 864 | 2021-08-24 | 82080 | keep | 0 | Aug | 2021 | 0.055904 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
PONCE | 2021-08-24 20:45 | 2021-08-25 16:27 | 90 | 019:42 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P21082400061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1182 | 2021-08-24 | 106380 | keep | 0 | Aug | 2021 | 0.072455 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
CANOVANAS | 2021-08-24 20:57 | 2021-08-24 22:11 | 80 | 001:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | R21082400066 | New_Event | Bad Weather | Include | Include | Weather | 74 | 2021-08-24 | 5920 | keep | 0 | Aug | 2021 | 0.0040321 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-24 21:11 | 2021-08-25 00:08 | 68 | 002:57 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA CARGA 1102 04 Y 1102 05 | S21082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 177 | 2021-08-24 | 12036 | keep | 0 | Aug | 2021 | 0.0081977 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
BAYAMON | 2021-08-24 21:11 | 2021-08-25 00:08 | 536 | 002:57 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR 1102 01 | S21082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 177 | 2021-08-24 | 94872 | keep | 0 | Aug | 2021 | 0.064617 | 0.00036507 | Sustained | FALSE | FALSE | Not_TMED_Event | 536
BAYAMON | 2021-08-24 21:11 | 2021-08-25 00:08 | 348 | 002:57 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA CARGA POR 1102 01 | S21082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 177 | 2021-08-24 | 61596 | keep | 0 | Aug | 2021 | 0.041953 | 0.00023702 | Sustained | FALSE | FALSE | Not_TMED_Event | 348
BAYAMON | 2021-08-24 21:32 | 2021-08-24 21:33 | 1420 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1530-06 LLEVANDO LA CARGA DEL 1526-02 | S21082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-24 | 1420 | keep | 0 | Aug | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-08-24 21:32 | 2021-08-24 21:33 | 437 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1530-06 LLEVANDO LA CARGA DEL 1526-02 | S21082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-24 | 437 | keep | 0 | Aug | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
PONCE | 2021-08-24 21:32 | 2021-08-24 22:35 | 100 | 001:03 | P | DESGANCHE | 1 X 100 EN RISER POR DESGANCHE | P21082400069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2021-08-24 | 6300 | keep | 0 | Aug | 2021 | 0.0042909 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2021-08-24 21:35 | 2021-08-24 22:34 | 800 | 000:59 | P | NO SE REPORTO CAUSA | SE CERRO POR CONTROL AL RESTABLECERSE RTU PARTE DE SU CARGA POR 1119 04 | S21082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 59 | 2021-08-24 | 47200 | keep | 0 | Aug | 2021 | 0.032148 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
BAYAMON | 2021-08-24 21:35 | 2021-08-24 22:34 | 2720 | 000:59 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL AL RESTABLECERSE RTU LLEVA PARTE DE LA CARGA DE 1115 05 | S21082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 59 | 2021-08-24 | 160480 | keep | 0 | Aug | 2021 | 0.1093 | 0.0018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 2720
CANOVANAS | 2021-08-24 21:40 | 2021-08-24 21:41 | 2708 | 000:01 | T | DESGANCHE | RECIERRE | R21082400068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-24 | 2708 | keep | 0 | Aug | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CAGUAS | 2021-08-24 21:40 | 2021-08-25 18:46 | 200 | 021:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON LAS TRES CAJAS DEL CORTE DE LINEA AVERIADAS | C21082400124 | New_Event | Cutout Failure | Include | Include | Equipment | 1266 | 2021-08-24 | 253200 | keep | 0 | Aug | 2021 | 0.17245 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-08-24 21:40 | 2021-08-25 13:50 | 200 | 016:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN CORTE DE LINEA | M21082400203 | New_Event | Cutout Failure | Include | Include | Equipment | 970 | 2021-08-24 | 194000 | keep | 0 | Aug | 2021 | 0.13213 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CANOVANAS | 2021-08-24 21:41 | 2021-08-24 23:03 | 185 | 001:22 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | R21082400070 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 82 | 2021-08-24 | 15170 | keep | 0 | Aug | 2021 | 0.010332 | 0.000126 | Sustained | FALSE | TRUE | Not_TMED_Event | 185
BAYAMON | 2021-08-24 21:43 | 2021-08-24 21:44 | 1420 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1530-06 LLEVANDO LA CARGA DEL 1526-02 | S21082400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-24 | 1420 | keep | 0 | Aug | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-08-24 21:43 | 2021-08-24 21:44 | 437 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1530-06 LLEVANDO LA CARGA DEL 1526-02 | S21082400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-24 | 437 | keep | 0 | Aug | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2021-08-24 21:44 | 2021-08-24 23:32 | 1935 | 001:48 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 9800 | B21082400148 | Additional_clients | 38 kV Transmission Line Source | Include | Include | Power supply | 108 | 2021-08-24 | 208980 | keep | 0 | Aug | 2021 | 0.14234 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-24 21:44 | 2021-08-24 23:32 | 3 | 001:48 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 9800 | B21082400148 | Additional_clients | 38 kV Transmission Line Source | Include | Include | Power supply | 108 | 2021-08-24 | 324 | keep | 0 | Aug | 2021 | 0.00022067 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-24 21:44 | 2021-08-24 23:32 | 61 | 001:48 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 9800 | B21082400148 | Additional_clients | 38 kV Transmission Line Source | Include | Include | Power supply | 108 | 2021-08-24 | 6588 | keep | 0 | Aug | 2021 | 0.0044871 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-24 21:44 | 2021-08-24 23:32 | 1501 | 001:48 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 9800 | B21082400148 | Additional_clients | 38 kV Transmission Line Source | Include | Include | Power supply | 108 | 2021-08-24 | 162108 | keep | 0 | Aug | 2021 | 0.11041 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-24 21:44 | 2021-08-24 23:32 | 546 | 001:48 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 9800 | B21082400148 | Additional_clients | 38 kV Transmission Line Source | Include | Include | Power supply | 108 | 2021-08-24 | 58968 | keep | 0 | Aug | 2021 | 0.040163 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-24 21:44 | 2021-08-24 23:32 | 1715 | 001:48 | P | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO LINEA 9800 CARGA POR 1707 01 | B21082400148 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 108 | 2021-08-24 | 185220 | keep | 0 | Aug | 2021 | 0.12615 | 0.0011681 | Sustained | FALSE | TRUE | Not_TMED_Event | 1715
BAYAMON | 2021-08-24 21:44 | 2021-08-24 23:32 | 959 | 001:48 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 9800 CARGA POR SUBESTACIN 1904 00 | S21082400146 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 108 | 2021-08-24 | 103572 | keep | 0 | Aug | 2021 | 0.070542 | 0.00065317 | Sustained | FALSE | TRUE | Not_TMED_Event | 959
BAYAMON | 2021-08-24 21:44 | 2021-08-24 23:32 | 1297 | 001:48 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 9800 CARGA POR SUBESTACIN 1904 00 | S21082400146 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 108 | 2021-08-24 | 140076 | keep | 0 | Aug | 2021 | 0.095405 | 0.00088338 | Sustained | FALSE | TRUE | Not_TMED_Event | 1297
BAYAMON | 2021-08-24 21:44 | 2021-08-24 23:32 | 451 | 001:48 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 9800 CARGA POR SUBESTACIN 1904 00 | S21082400146 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 108 | 2021-08-24 | 48708 | keep | 0 | Aug | 2021 | 0.033175 | 0.00030717 | Sustained | FALSE | TRUE | Not_TMED_Event | 451
BAYAMON | 2021-08-24 21:44 | 2021-08-24 23:32 | 1264 | 001:48 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 9800 CARGA POR SUBESTACIN 1904 00 | S21082400146 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 108 | 2021-08-24 | 136512 | keep | 0 | Aug | 2021 | 0.092978 | 0.0008609 | Sustained | FALSE | TRUE | Not_TMED_Event | 1264
BAYAMON | 2021-08-24 21:44 | 2021-08-24 23:32 | 620 | 001:48 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA 9800 CARGA POR SUBESTACIN 1904 00 | S21082400146 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 108 | 2021-08-24 | 66960 | keep | 0 | Aug | 2021 | 0.045606 | 0.00042228 | Sustained | FALSE | TRUE | Not_TMED_Event | 620
CANOVANAS | 2021-08-24 21:47 | 2021-08-25 10:12 | 11 | 012:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA ROTA | R21082400069 | New_Event | Secondary Wire Down | Include | Include | Equipment | 745 | 2021-08-24 | 8195 | keep | 0 | Aug | 2021 | 0.0055816 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2021-08-24 21:50 | 2021-08-24 21:51 | 1420 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1530-06 LLEVANDO LA CARGA DEL 1526-02 | S21082400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-24 | 1420 | keep | 0 | Aug | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-08-24 21:50 | 2021-08-24 21:51 | 437 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1530-06 LLEVANDO LA CARGA DEL 1526-02 | S21082400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-24 | 437 | keep | 0 | Aug | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
MAYAGÃœEZ | 2021-08-24 22:15 | 2021-08-25 10:45 | 10 | 012:30 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA SE RETIRO RAMA | M21082400206 | New_Event | Vegetation Contact | Include | Include | Vegetation | 750 | 2021-08-24 | 7500 | keep | 0 | Aug | 2021 | 0.0051082 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BAYAMON | 2021-08-24 22:24 | 2021-08-24 22:25 | 1420 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR CARGA POR 1530 06 | S21082400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-24 | 1420 | keep | 0 | Aug | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-08-24 22:24 | 2021-08-24 22:25 | 437 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 1526 02 | S21082400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-24 | 437 | keep | 0 | Aug | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
ARECIBO | 2021-08-24 22:27 | 2021-08-25 09:50 | 30 | 011:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA POR AVE QUE CRUZO LINEAS | A21082400102 | New_Event |  |  | Include | Wildlife | 683 | 2021-08-24 | 20490 | keep | 0 | Aug | 2021 | 0.013956 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-08-24 22:28 | 2021-08-25 10:20 | 100 | 011:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE AVERIADO | A21082400101 | New_Event | Cutout Failure | Include | Include | Equipment | 712 | 2021-08-24 | 71200 | keep | 0 | Aug | 2021 | 0.048494 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-08-24 22:33 | 2021-08-25 16:55 | 15 | 018:22 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21082400103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1102 | 2021-08-24 | 16530 | keep | 0 | Aug | 2021 | 0.011259 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-08-24 22:40 | 2021-08-25 09:40 | 80 | 011:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21082400210 | New_Event | Bad Weather | Include | Include | Weather | 660 | 2021-08-24 | 52800 | keep | 0 | Aug | 2021 | 0.035962 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-24 23:32 | 2021-08-25 01:46 | 690 | 002:14 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 PUENTE ABIERTO | B21082400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 134 | 2021-08-24 | 92460 | keep | 0 | Aug | 2021 | 0.062974 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-24 23:32 | 2021-08-25 01:46 | 1 | 002:14 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 PUENTE ABIERTO | B21082400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 134 | 2021-08-24 | 134 | keep | 0 | Aug | 2021 | 9.1267e-05 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-24 23:32 | 2021-08-25 01:46 | 20 | 002:14 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 PUENTE ABIERTO | B21082400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 134 | 2021-08-24 | 2680 | keep | 0 | Aug | 2021 | 0.0018253 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-24 23:32 | 2021-08-25 01:46 | 500 | 002:14 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 PUENTE ABIERTO | B21082400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 134 | 2021-08-24 | 67000 | keep | 0 | Aug | 2021 | 0.045633 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-24 23:32 | 2021-08-25 01:46 | 175 | 002:14 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 9800 PUENTE ABIERTO | B21082400000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 134 | 2021-08-24 | 23450 | keep | 0 | Aug | 2021 | 0.015972 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
FAJARDO | 2021-08-24 23:38 | 2021-08-24 23:39 | 424 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-24 | 424 | keep | 0 | Aug | 2021 | 0.00028878 | 0.00028878 | Momentary | FALSE | FALSE | Not_TMED_Event | 424
HUMACAO | 2021-08-25 00:08 | 2021-08-25 00:09 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21082500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-25 | 1827 | keep | 0 | Aug | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
BAYAMON | 2021-08-25 00:55 | 2021-08-25 02:34 | 68 | 001:39 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA LA CARGA DEL 1102-04 Y 1102-05 | S21082500002 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 99 | 2021-08-25 | 6732 | keep | 0 | Aug | 2021 | 0.0045851 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-25 00:55 | 2021-08-25 02:34 | 68 | 001:39 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CARGA POR EL 1102-01 | S21082500002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2021-08-25 | 6732 | keep | 0 | Aug | 2021 | 0.0045851 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
BAYAMON | 2021-08-25 00:55 | 2021-08-25 02:34 | 348 | 001:39 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CARGA POR EL 1102-01 | S21082500002 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 99 | 2021-08-25 | 34452 | keep | 0 | Aug | 2021 | 0.023465 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-25 01:46 | 2021-08-25 10:29 | 1935 | 008:43 | S | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA DE SUBESTACION PARA CERRAR PUENTE EN LINEA 38KV | B21082400148 | Additional_clients | 38 kV Transmission Line Source | Include | Include | Power supply | 523 | 2021-08-25 | 1012005 | keep | 0 | Aug | 2021 | 0.68927 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-25 01:46 | 2021-08-25 10:29 | 3 | 008:43 | S | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA DE SUBESTACION PARA CERRAR PUENTE EN LINEA 38KV | B21082400148 | Additional_clients | 38 kV Transmission Line Source | Include | Include | Power supply | 523 | 2021-08-25 | 1569 | keep | 0 | Aug | 2021 | 0.0010686 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-25 01:46 | 2021-08-25 10:29 | 61 | 008:43 | S | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA DE SUBESTACION PARA CERRAR PUENTE EN LINEA 38KV | B21082400148 | Additional_clients | 38 kV Transmission Line Source | Include | Include | Power supply | 523 | 2021-08-25 | 31903 | keep | 0 | Aug | 2021 | 0.021729 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-25 01:46 | 2021-08-25 10:29 | 1501 | 008:43 | S | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA DE SUBESTACION PARA CERRAR PUENTE EN LINEA 38KV | B21082400148 | Additional_clients | 38 kV Transmission Line Source | Include | Include | Power supply | 523 | 2021-08-25 | 785023 | keep | 0 | Aug | 2021 | 0.53468 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-25 01:46 | 2021-08-25 10:29 | 546 | 008:43 | S | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA DE SUBESTACION PARA CERRAR PUENTE EN LINEA 38KV | B21082400148 | Additional_clients | 38 kV Transmission Line Source | Include | Include | Power supply | 523 | 2021-08-25 | 285558 | keep | 0 | Aug | 2021 | 0.19449 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-25 01:51 | 2021-08-25 13:00 | 40 | 011:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M21082500003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 669 | 2021-08-25 | 26760 | keep | 0 | Aug | 2021 | 0.018226 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-08-25 03:28 | 2021-08-25 14:40 | 959 | 011:12 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA SUBESTACION 1901-00 | S21082500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 672 | 2021-08-25 | 644448 | keep | 0 | Aug | 2021 | 0.43893 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-25 03:28 | 2021-08-25 14:40 | 1297 | 011:12 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA SUBESTACION 1901-00 | S21082500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 672 | 2021-08-25 | 871584 | keep | 0 | Aug | 2021 | 0.59363 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-25 03:28 | 2021-08-25 14:40 | 451 | 011:12 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA SUBESTACION 1901-00 | S21082500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 672 | 2021-08-25 | 303072 | keep | 0 | Aug | 2021 | 0.20642 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-25 03:28 | 2021-08-25 14:40 | 1264 | 011:12 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA SUBESTACION 1901-00 | S21082500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 672 | 2021-08-25 | 849408 | keep | 0 | Aug | 2021 | 0.57853 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-25 03:28 | 2021-08-25 14:40 | 620 | 011:12 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN LINEA SUBESTACION 1901-00 | S21082500000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 672 | 2021-08-25 | 416640 | keep | 0 | Aug | 2021 | 0.28377 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-25 05:27 | 2021-08-25 05:28 | 1533 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA CARGA DEL 1709-5 | S21082500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-25 | 1533 | keep | 0 | Aug | 2021 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
BAYAMON | 2021-08-25 05:27 | 2021-08-25 05:28 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1709-3 | S21082500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-25 | 2364 | keep | 0 | Aug | 2021 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
HUMACAO | 2021-08-25 07:10 | 2021-08-25 20:47 | 4 | 013:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR REPARO SECUNDARIA | C21082500003 | New_Event | Secondary Wire Down | Include | Include | Equipment | 817 | 2021-08-25 | 3268 | keep | 0 | Aug | 2021 | 0.0022258 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-08-25 07:32 | 2021-08-25 13:30 | 50 | 005:58 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | M21082500009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 358 | 2021-08-25 | 17900 | keep | 0 | Aug | 2021 | 0.012192 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-25 07:52 | 2021-08-25 07:53 | 679 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA UN 85% DE LA CARGA DEL 1705-05 | B21082500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-25 | 679 | keep | 0 | Aug | 2021 | 0.00046246 | 0.00046246 | Momentary | FALSE | FALSE | Not_TMED_Event | 679
BAYAMON | 2021-08-25 07:52 | 2021-08-25 07:53 | 541 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA UN 85% DE LA CARGA DEL 1705-05 | B21082500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-25 | 541 | keep | 0 | Aug | 2021 | 0.00036847 | 0.00036847 | Momentary | FALSE | FALSE | Not_TMED_Event | 541
BAYAMON | 2021-08-25 07:53 | 2021-08-26 09:47 | 8 | 025:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21082500089 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1554 | 2021-08-25 | 12432 | keep | 0 | Aug | 2021 | 0.0084674 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2021-08-25 07:54 | 2021-08-25 15:20 | 60 | 007:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN CORTE DE LINEA | M21082500013 | New_Event | Cutout Failure | Include | Include | Equipment | 446 | 2021-08-25 | 26760 | keep | 0 | Aug | 2021 | 0.018226 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
PONCE | 2021-08-25 08:44 | 2021-08-25 08:45 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P210825000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-25 | 3718 | keep | 0 | Aug | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
PONCE | 2021-08-25 08:45 | 2021-08-25 11:14 | 49 | 002:29 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE REPORTO CAUSA | P21082500005 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 149 | 2021-08-25 | 7301 | keep | 0 | Aug | 2021 | 0.0049727 | 3.3374e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 49
VEGA BAJA | 2021-08-25 09:31 | 2021-08-26 09:47 | 8 | 024:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21082500089 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1456 | 2021-08-25 | 11648 | keep | 0 | Aug | 2021 | 0.0079334 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2021-08-25 09:35 | 2021-08-25 17:55 | 7 | 008:20 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 37.5KVA X 37.5KVA | M21082500000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 500 | 2021-08-25 | 3500 | keep | 0 | Aug | 2021 | 0.0023838 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-08-25 10:02 | 2021-08-26 11:28 | 25 | 025:26 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S21082500014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1526 | 2021-08-25 | 38150 | keep | 0 | Aug | 2021 | 0.025984 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BARRANQUITAS | 2021-08-25 10:46 | 2021-08-25 12:02 | 100 | 001:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21082500008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2021-08-25 | 7600 | keep | 0 | Aug | 2021 | 0.0051763 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-08-25 10:53 | 2021-08-25 14:55 | 10 | 004:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES SECUNDARIAS EN TRANSFORMADOR | A21082500007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 242 | 2021-08-25 | 2420 | keep | 0 | Aug | 2021 | 0.0016483 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-08-25 11:07 | 2021-08-25 13:55 | 390 | 002:48 | T | DESGANCHE | SE RETIRO ARBOL SOBRE LINEA | M21082500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2021-08-25 | 65520 | keep | 0 | Aug | 2021 | 0.044625 | 0.00026563 | Sustained | FALSE | TRUE | Not_TMED_Event | 390
AGUADILLA | 2021-08-25 11:20 | 2021-08-25 14:05 | 8 | 002:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 37.5 X 50 KVA | M21082500000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 165 | 2021-08-25 | 1320 | keep | 0 | Aug | 2021 | 0.00089905 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-08-25 11:42 | 2021-08-25 18:31 | 15 | 006:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR TRANFORMADOR PARA REPARAR SECUNDARIA | S21082500020 | New_Event | Secondary Wire Down | Include | Include | Equipment | 409 | 2021-08-25 | 6135 | keep | 0 | Aug | 2021 | 0.0041785 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-08-25 11:42 | 2021-08-25 18:31 | 15 | 006:49 | P | NO SE REPORTO CAUSA | 1 X 80 Y 1 X 65 EN CORTE DE LINEA | S21082500020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 409 | 2021-08-25 | 6135 | keep | 0 | Aug | 2021 | 0.0041785 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
FAJARDO | 2021-08-25 12:05 | 2021-08-25 13:45 | 129 | 001:40 | P | DESGANCHE | 1 X 65 Y 1 X 50 EN CORTES DE LINEAS | R21082500002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2021-08-25 | 12900 | keep | 0 | Aug | 2021 | 0.0087861 | 8.7861e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 129
VEGA BAJA | 2021-08-25 12:18 | 2021-08-25 12:19 | 1570 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B08025000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-25 | 1570 | keep | 0 | Aug | 2021 | 0.0010693 | 0.0010693 | Momentary | FALSE | FALSE | Not_TMED_Event | 1570
VEGA BAJA | 2021-08-25 12:19 | 2021-08-25 19:26 | 900 | 007:07 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA Y SE REPARO PUENTE DE LINEA A CAJA | B21082500038 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 427 | 2021-08-25 | 384300 | keep | 0 | Aug | 2021 | 0.26174 | 0.00061299 | Sustained | FALSE | TRUE | Not_TMED_Event | 900
CANOVANAS | 2021-08-25 12:40 | 2021-08-25 14:04 | 635 | 001:24 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO MACHETES EN CARR 3 FRENTE RIO GRANDE ESTATES PARA SECCIONALIZAR AISLADOR ROTO | R21082500000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 84 | 2021-08-25 | 53340 | keep | 0 | Aug | 2021 | 0.03633 | 0.0004325 | Sustained | FALSE | FALSE | Not_TMED_Event | 635
CANOVANAS | 2021-08-25 12:42 | 2021-08-25 18:37 | 539 | 005:55 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR ROTO Y CERRO INTERRUPTOR | R21082500000 | New_Event | Wire Down | Include | Include | Equipment | 355 | 2021-08-25 | 191345 | keep | 0 | Aug | 2021 | 0.13032 | 0.00036711 | Sustained | FALSE | FALSE | Not_TMED_Event | 539
PONCE | 2021-08-25 12:56 | 2021-08-25 14:27 | 109 | 001:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | P21082500021 | New_Event | Wire Down | Include | Include | Equipment | 91 | 2021-08-25 | 9919 | keep | 0 | Aug | 2021 | 0.0067558 | 7.4239e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 109
MAYAGÃœEZ | 2021-08-25 13:00 | 2021-08-25 16:30 | 50 | 003:30 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | M21082500043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2021-08-25 | 10500 | keep | 0 | Aug | 2021 | 0.0071515 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-25 13:33 | 2021-08-25 17:38 | 25 | 004:05 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA Y DESGANCHE SE RETIRARON BAMBUAS DEL TENDIDO ELECTRICO PRIMARIO | B21082500027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 245 | 2021-08-25 | 6125 | keep | 0 | Aug | 2021 | 0.0041717 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-08-25 13:37 | 2021-08-25 22:33 | 20 | 008:56 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | S21082500036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 536 | 2021-08-25 | 10720 | keep | 0 | Aug | 2021 | 0.0073013 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-08-25 13:53 | 2021-08-25 13:54 | 2178 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO | C21082500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-25 | 2178 | keep | 0 | Aug | 2021 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
ARECIBO | 2021-08-25 13:58 | 2021-08-25 17:20 | 100 | 003:22 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | A21082500027 | New_Event | Wire Down | Include | Include | Equipment | 202 | 2021-08-25 | 20200 | keep | 0 | Aug | 2021 | 0.013758 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-08-25 13:59 | 2021-08-25 14:00 | 2178 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO | C21082500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-25 | 2178 | keep | 0 | Aug | 2021 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
GUAYAMA | 2021-08-25 13:59 | 2021-08-25 18:04 | 65 | 004:05 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21082500022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2021-08-25 | 15925 | keep | 0 | Aug | 2021 | 0.010846 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
FAJARDO | 2021-08-25 14:00 | 2021-08-25 16:16 | 12 | 002:16 | P | TRANSFORMADOR AVERIADO | REEMPLAZARON T-6 AVERIADO DE 100KVA X 100KVA | R21082500030 | New_Event | Service Transformer Failure | Include | Include | Equipment | 136 | 2021-08-25 | 1632 | keep | 0 | Aug | 2021 | 0.0011115 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2021-08-25 14:04 | 2021-08-25 16:12 | 508 | 002:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | REEMPLAZARON AISLADORES ROTOS Y SE CERRARON LOS MACHETES EN CARR 3 FRENTE RIO GRANDE ESTATES | R21082500000 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 128 | 2021-08-25 | 65024 | keep | 0 | Aug | 2021 | 0.044288 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-08-25 14:11 | 2021-08-25 19:08 | 100 | 004:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA AVERIADA MARCA-SHINT CAPACIDAD-100AMP. | A21082500029 | New_Event | Cutout Failure | Include | Include | Equipment | 297 | 2021-08-25 | 29700 | keep | 0 | Aug | 2021 | 0.020229 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-08-25 14:13 | 2021-08-25 17:26 | 25 | 003:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARAR PUENTE DE LINEA A CAJA | S21082500041 | New_Event | Wire Down | Include | Include | Equipment | 193 | 2021-08-25 | 4825 | keep | 0 | Aug | 2021 | 0.0032863 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BARRANQUITAS | 2021-08-25 14:13 | 2021-08-25 15:01 | 45 | 000:48 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | C21082500024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 48 | 2021-08-25 | 2160 | keep | 0 | Aug | 2021 | 0.0014712 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
MAYAGÃœEZ | 2021-08-25 14:13 | 2021-08-25 14:14 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21082500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-25 | 393 | keep | 0 | Aug | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
PONCE | 2021-08-25 14:20 | 2021-08-25 15:09 | 65 | 000:49 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA. LINEA ZAFADA DE PIN | P210825000XX | New_Event | Wire Down | Include | Include | Equipment | 49 | 2021-08-25 | 3185 | keep | 0 | Aug | 2021 | 0.0021693 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
SAN JUAN | 2021-08-25 14:42 | 2021-08-25 15:46 | 5 | 001:04 | P | OTRAS CAUSAS | INSTALACION DE POSTE PRIMARIO PARA FUTURA VIA LIBRE | S21082500040 | New_Event | Other Causes | Include | Include | Other | 64 | 2021-08-25 | 320 | keep | 0 | Aug | 2021 | 0.00021795 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-08-25 14:50 | 2021-08-25 19:05 | 10 | 004:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIR TRANSFORMADOR PARA REPARAR SECUNDARIA | S21082500043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 255 | 2021-08-25 | 2550 | keep | 0 | Aug | 2021 | 0.0017368 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-25 14:57 | 2021-08-25 16:43 | 80 | 001:46 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | A21082500041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2021-08-25 | 8480 | keep | 0 | Aug | 2021 | 0.0057757 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-08-25 15:00 | 2021-08-25 20:40 | 25 | 005:40 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | M21082500070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 340 | 2021-08-25 | 8500 | keep | 0 | Aug | 2021 | 0.0057893 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
UTUADO | 2021-08-25 15:00 | 2021-08-25 18:49 | 20 | 003:49 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA POR DESGANCHE | A21082500042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2021-08-25 | 4580 | keep | 0 | Aug | 2021 | 0.0031194 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-08-25 15:09 | 2021-08-25 15:10 | 5619 | 000:01 | P | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA. 90% DE LA CARGA ESTA POR EL 1620-04 | S21082500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-25 | 5619 | keep | 0 | Aug | 2021 | 0.0038271 | 0.0038271 | Momentary | FALSE | FALSE | Not_TMED_Event | 5619
SAN JUAN | 2021-08-25 15:09 | 2021-08-25 15:10 | 36 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 90% DE LA CARGA POR EL 1620-04 | S21082500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-25 | 36 | keep | 0 | Aug | 2021 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-08-25 15:09 | 2021-08-25 15:10 | 172 | 000:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA. LLEVA 1620-01, 85% DEL 1336-10, 90% DEL 1336-07 | S21082500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-25 | 172 | keep | 0 | Aug | 2021 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
PONCE | 2021-08-25 15:09 | 2021-08-26 01:57 | 100 | 010:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA Y SE CERRO CORTE DE LINEA | P21082500016 | Additional_clients | Wire Down | Include | Include | Equipment | 648 | 2021-08-25 | 64800 | keep | 0 | Aug | 2021 | 0.044135 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
UTUADO | 2021-08-25 15:22 | 2021-08-25 18:10 | 100 | 002:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA AVERIADA CAPACIDAD-100AMP. MARCA-S&C | A21082500051 | New_Event | Cutout Failure | Include | Include | Equipment | 168 | 2021-08-25 | 16800 | keep | 0 | Aug | 2021 | 0.011442 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-08-25 15:23 | 2021-08-25 22:18 | 45 | 006:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR FUERTES VIENTOS | M21082500075 | New_Event | Bad Weather | Include | Include | Weather | 415 | 2021-08-25 | 18675 | keep | 0 | Aug | 2021 | 0.012719 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
MAYAGÃœEZ | 2021-08-25 15:36 | 2021-08-25 15:45 | 1617 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21082500084 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2021-08-25 | 14553 | keep | 0 | Aug | 2021 | 0.009912 | 0.0011013 | Sustained | FALSE | TRUE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-08-25 15:36 | 2021-08-25 15:45 | 1017 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21082500084 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2021-08-25 | 9153 | keep | 0 | Aug | 2021 | 0.0062341 | 0.00069267 | Sustained | FALSE | TRUE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-08-25 15:36 | 2021-08-25 15:45 | 828 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21082500084 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2021-08-25 | 7452 | keep | 0 | Aug | 2021 | 0.0050755 | 0.00056395 | Sustained | FALSE | TRUE | Not_TMED_Event | 828
MAYAGÃœEZ | 2021-08-25 15:36 | 2021-08-25 15:45 | 863 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21082500085 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2021-08-25 | 7767 | keep | 0 | Aug | 2021 | 0.0052901 | 0.00058779 | Sustained | FALSE | TRUE | Not_TMED_Event | 863
MAYAGÃœEZ | 2021-08-25 15:36 | 2021-08-25 15:45 | 309 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21082500085 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2021-08-25 | 2781 | keep | 0 | Aug | 2021 | 0.0018941 | 0.00021046 | Sustained | FALSE | TRUE | Not_TMED_Event | 309
MAYAGÃœEZ | 2021-08-25 15:36 | 2021-08-25 15:45 | 176 | 000:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21082500085 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2021-08-25 | 1584 | keep | 0 | Aug | 2021 | 0.0010789 | 0.00011987 | Sustained | FALSE | TRUE | Not_TMED_Event | 176
MAYAGÃœEZ | 2021-08-25 15:36 | 2021-08-25 15:38 | 1417 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON RECIERRE EN OFF CERRADO POR SCADA | M21082500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-25 | 2834 | keep | 0 | Aug | 2021 | 0.0019302 | 0.00096511 | Momentary | FALSE | FALSE | Not_TMED_Event | 1417
MAYAGÃœEZ | 2021-08-25 15:45 | 2021-08-26 11:20 | 1 | 019:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M21082400169 | Partial_restoration | Bad Weather | Include | Include | Weather | 1175 | 2021-08-25 | 1175 | keep | 0 | Aug | 2021 | 0.00080029 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-25 16:04 | 2021-08-25 22:18 | 85 | 006:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 50 Y 1 X 40 EN CORTES DE LINEA SE REPARARON LINEAS PRIMARIAS PARTIDAS | M21082500092 | New_Event | Wire Down | Include | Include | Equipment | 374 | 2021-08-25 | 31790 | keep | 0 | Aug | 2021 | 0.021652 | 5.7893e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 85
FAJARDO | 2021-08-25 16:22 | 2021-08-25 17:02 | 21 | 000:40 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | R21082500053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 40 | 2021-08-25 | 840 | keep | 0 | Aug | 2021 | 0.00057212 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
CAGUAS | 2021-08-25 16:26 | 2021-08-26 17:40 | 30 | 025:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE ABRIO PUENTE HACIA AVERIA CONDUCTOR ROTO | C21082500042 | New_Event | Wire Down | Include | Include | Equipment | 1514 | 2021-08-25 | 45420 | keep | 0 | Aug | 2021 | 0.030935 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-08-25 16:42 | 2021-08-25 18:58 | 30 | 002:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21082500000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 136 | 2021-08-25 | 4080 | keep | 0 | Aug | 2021 | 0.0027789 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2021-08-25 16:49 | 2021-08-25 17:46 | 8 | 000:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN TRANSFORMADOR POR MAL TIEMPO | A21082500066 | New_Event | Bad Weather | Include | Include | Weather | 57 | 2021-08-25 | 456 | keep | 0 | Aug | 2021 | 0.00031058 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-08-25 16:54 | 2021-08-26 11:55 | 6 | 019:01 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR PM QUEMADO DE 50 KVA X 50 KVA | A21082500068 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1141 | 2021-08-25 | 6846 | keep | 0 | Aug | 2021 | 0.0046628 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-08-25 16:57 | 2021-08-25 21:57 | 80 | 005:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR FUERTES VIENTOS | M21082500108 | New_Event | Bad Weather | Include | Include | Weather | 300 | 2021-08-25 | 24000 | keep | 0 | Aug | 2021 | 0.016346 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-08-25 17:08 | 2021-08-25 20:29 | 50 | 003:21 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21082500024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 201 | 2021-08-25 | 10050 | keep | 0 | Aug | 2021 | 0.006845 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-08-25 17:16 | 2021-08-25 19:20 | 60 | 002:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA REPARO LINEAS CRUZADAS | C21082500047 | New_Event | Wire Down | Include | Include | Equipment | 124 | 2021-08-25 | 7440 | keep | 0 | Aug | 2021 | 0.0050674 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-08-25 17:31 | 2021-08-25 17:35 | 828 | 000:04 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR DE TRANSFORMDAOR 0060. EL 60% DE LA CARGA ESTA POR EL 1206-04 | S21082500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-08-25 | 3312 | keep | 0 | Aug | 2021 | 0.0022558 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
SAN JUAN | 2021-08-25 17:31 | 2021-08-25 17:35 | 1977 | 000:04 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR DE TRANSFORMDAOR 0060. EL 40% DE LA CARGA ESTA POR EL 1206-04 | S21082500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-08-25 | 7908 | keep | 0 | Aug | 2021 | 0.0053861 | 0.0013465 | Momentary | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2021-08-25 17:31 | 2021-08-25 17:35 | 10211 | 000:04 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR DE TRANSFORMADOR 0060. CARGA POR EL 1206-03 | S21082500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-08-25 | 40844 | keep | 0 | Aug | 2021 | 0.027819 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-08-25 17:31 | 2021-08-25 17:35 | 641 | 000:04 | S | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR DE TRANSFORMADOR, 0060 | S21082500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-08-25 | 2564 | keep | 0 | Aug | 2021 | 0.0017463 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2021-08-25 17:31 | 2021-08-25 17:35 | 733 | 000:04 | S | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR DE TRANSFORMADOR 0060 | S21082500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-08-25 | 2932 | keep | 0 | Aug | 2021 | 0.001997 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2021-08-25 17:31 | 2021-08-25 17:35 | 4133 | 000:04 | S | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR DE TRANSFORMADOR 0060. LLEVA 1204-05 | S21082500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-08-25 | 16532 | keep | 0 | Aug | 2021 | 0.01126 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2021-08-25 17:31 | 2021-08-25 17:35 | 1799 | 000:04 | S | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR DE TRANSFORMDAOR 0060. LLEVA 40% DEL 1204-04 Y 60% DEL 1204-03 | S21082500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-08-25 | 7196 | keep | 0 | Aug | 2021 | 0.0049012 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
HUMACAO | 2021-08-25 17:34 | 2021-08-26 16:07 | 10 | 022:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNADARIO EN TRANSFORMADOR | C21082500048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1353 | 2021-08-25 | 13530 | keep | 0 | Aug | 2021 | 0.0092152 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-08-25 17:36 | 2021-08-25 19:08 | 36 | 001:32 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | S21082500046 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 92 | 2021-08-25 | 3312 | keep | 0 | Aug | 2021 | 0.0022558 | 2.4519e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 36
BAYAMON | 2021-08-25 17:43 | 2021-08-26 18:12 | 10 | 024:29 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21082500058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1469 | 2021-08-25 | 14690 | keep | 0 | Aug | 2021 | 0.010005 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-08-25 18:18 | 2021-08-26 11:20 | 390 | 017:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | C21082500052 | New_Event | Cutout Failure | Include | Include | Equipment | 1022 | 2021-08-25 | 398580 | keep | 0 | Aug | 2021 | 0.27147 | 0.00026563 | Sustained | FALSE | TRUE | Not_TMED_Event | 390
ARECIBO | 2021-08-25 18:33 | 2021-08-26 20:40 | 300 | 026:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | A21082500083 | New_Event | Wire Down | Include | Include | Equipment | 1567 | 2021-08-25 | 470100 | keep | 0 | Aug | 2021 | 0.32018 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
PONCE | 2021-08-25 18:42 | 2021-08-25 19:30 | 60 | 000:48 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21082500044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 48 | 2021-08-25 | 2880 | keep | 0 | Aug | 2021 | 0.0019616 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-08-25 18:46 | 2021-08-25 23:42 | 15 | 004:56 | P | NO SE REPORTO CAUSA | 1 X 140 EN PARALELAS | S21082500140 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 296 | 2021-08-25 | 4440 | keep | 0 | Aug | 2021 | 0.0030241 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-08-25 18:47 | 2021-08-26 10:20 | 80 | 015:33 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21082500118 | New_Event | Bad Weather | Include | Include | Weather | 933 | 2021-08-25 | 74640 | keep | 0 | Aug | 2021 | 0.050837 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-25 18:54 | 2021-08-25 21:20 | 50 | 002:26 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21082500061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2021-08-25 | 7300 | keep | 0 | Aug | 2021 | 0.004972 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-08-25 19:00 | 2021-08-26 01:57 | 8 | 006:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA | C21082500057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 417 | 2021-08-25 | 3336 | keep | 0 | Aug | 2021 | 0.0022721 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-08-25 19:02 | 2021-08-25 19:58 | 15 | 000:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21082500038 | New_Event | Secondary Wire Down | Include | Include | Equipment | 56 | 2021-08-25 | 840 | keep | 0 | Aug | 2021 | 0.00057212 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-08-25 19:23 | 2021-08-25 20:48 | 80 | 001:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA POR CAJA PRIMARIA QUEMADA | P21082500057 | New_Event | Cutout Failure | Include | Include | Equipment | 85 | 2021-08-25 | 6800 | keep | 0 | Aug | 2021 | 0.0046314 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-08-25 19:27 | 2021-08-26 14:43 | 60 | 019:16 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | M21082500125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1156 | 2021-08-25 | 69360 | keep | 0 | Aug | 2021 | 0.047241 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-08-25 19:30 | 2021-08-25 21:40 | 80 | 002:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21082500127 | New_Event | Bad Weather | Include | Include | Weather | 130 | 2021-08-25 | 10400 | keep | 0 | Aug | 2021 | 0.0070834 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-08-25 19:32 | 2021-08-26 09:22 | 2864 | 013:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 80 EN RISER CRUCE POR AVE | C21082500062 | New_Event |  |  | Include | Wildlife | 830 | 2021-08-25 | 2377120 | keep | 0 | Aug | 2021 | 1.619 | 0.0019507 | Sustained | FALSE | FALSE | Not_TMED_Event | 2864
CAGUAS | 2021-08-25 20:13 | 2021-08-26 14:27 | 77 | 018:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | C21082500067 | New_Event | Wire Down | Include | Include | Equipment | 1094 | 2021-08-25 | 84238 | keep | 0 | Aug | 2021 | 0.057374 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
MAYAGÃœEZ | 2021-08-25 20:14 | 2021-08-26 21:01 | 60 | 024:47 | P | CABLE SOTERRADO AVERIADO | USO FUSIBLE BAJA CAPACIDAD PARA HACER PRUEBA POR AVERIA DEL SW-2 AL T-2 T-3 Y T-4 SE ENERGIZO T-3 Y T-4 POR PROVISIONAL AEREO | M21082500131 | New_Event | UG Cable Fault | Include | Include | Equipment | 1487 | 2021-08-25 | 89220 | keep | 0 | Aug | 2021 | 0.060767 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-08-25 20:34 | 2021-08-26 17:56 | 10 | 021:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTE SECUNDARIO | S21082500070 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1282 | 2021-08-25 | 12820 | keep | 0 | Aug | 2021 | 0.0087316 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-25 20:50 | 2021-08-26 10:00 | 150 | 013:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21082500084 | New_Event | Bad Weather | Include | Include | Weather | 790 | 2021-08-25 | 118500 | keep | 0 | Aug | 2021 | 0.08071 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
PONCE | 2021-08-25 20:55 | 2021-08-25 23:09 | 825 | 002:14 | P | DESCONECTIVO DEFECTUOSO | CONECTOR EN MACHETE DE AMARRE 5817-01 Y 5817-02 AVERIADO SE ABRE INTERRUPTOR 5817-01 PARA CORREGIR CONDICION | P21082500072 | New_Event | Switch Failure | Include | Include | Equipment | 134 | 2021-08-25 | 110550 | keep | 0 | Aug | 2021 | 0.075295 | 0.0005619 | Sustained | FALSE | FALSE | Not_TMED_Event | 825
SAN JUAN | 2021-08-25 21:14 | 2021-08-26 13:06 | 6 | 015:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRANDO PUENTE DE LINEA A CAJA | S21082500183 | New_Event | Wire Down | Include | Include | Equipment | 952 | 2021-08-25 | 5712 | keep | 0 | Aug | 2021 | 0.0038904 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
CAGUAS | 2021-08-25 21:34 | 2021-08-26 12:15 | 90 | 014:41 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C21082500079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 881 | 2021-08-25 | 79290 | keep | 0 | Aug | 2021 | 0.054004 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
CAGUAS | 2021-08-25 21:44 | 2021-08-26 19:39 | 5 | 021:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA ABIERTA | C21082400080 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1315 | 2021-08-25 | 6575 | keep | 0 | Aug | 2021 | 0.0044782 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-08-25 21:58 | 2021-08-26 09:46 | 100 | 011:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21082500138 | New_Event | Bad Weather | Include | Include | Weather | 708 | 2021-08-25 | 70800 | keep | 0 | Aug | 2021 | 0.048222 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
YAUCO | 2021-08-25 22:28 | 2021-08-26 10:28 | 900 | 012:00 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ENCONTRO ALAMBRE EN EL PISO PRIMARIO EN TRONCAL | P21082500087 | New_Event | Wire Down | Include | Include | Equipment | 720 | 2021-08-25 | 648000 | keep | 0 | Aug | 2021 | 0.44135 | 0.00061299 | Sustained | FALSE | FALSE | Not_TMED_Event | 900
PONCE | 2021-08-25 23:09 | 2021-08-25 23:35 | 234 | 000:26 | T | DESCONECTIVO DEFECTUOSO | SE REPARA CONECTOR EN MACHETE DE AMARRE 5817-01 Y 5817-02 Y SE COLOCA INTERRPTOR EN SERVICIO | P21082500103 | New_Event | Switch Failure | Include | Include | Equipment | 26 | 2021-08-25 | 6084 | keep | 0 | Aug | 2021 | 0.0041438 | 0.00015938 | Sustained | FALSE | FALSE | Not_TMED_Event | 234
PONCE | 2021-08-25 23:09 | 2021-08-25 23:35 | 2468 | 000:26 | T | DESCONECTIVO DEFECTUOSO | SE REPARA CONECTOR EN MACHETE DE AMARRE 5817-01 Y 5817-02 Y SE COLOCA INTERRPTOR EN SERVICIO CARGA POR 5817-01 | P21082500103 | Additional_clients | Switch Failure | Include | Include | Equipment | 26 | 2021-08-25 | 64168 | keep | 0 | Aug | 2021 | 0.043705 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-08-26 00:23 | 2021-08-26 00:24 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21082600001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-26 | 1827 | keep | 0 | Aug | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
BAYAMON | 2021-08-26 01:20 | 2021-08-26 10:52 | 80 | 009:32 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21082600001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 572 | 2021-08-26 | 45760 | keep | 0 | Aug | 2021 | 0.031167 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-08-26 01:57 | 2021-08-26 01:58 | 3701 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | C21082600002 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-26 | 3701 | keep | 0 | Aug | 2021 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
HUMACAO | 2021-08-26 01:58 | 2021-08-26 10:58 | 8 | 009:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE DESPEJO SECUNDARIA | C21082500057 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 540 | 2021-08-26 | 4320 | keep | 0 | Aug | 2021 | 0.0029423 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2021-08-26 03:32 | 2021-08-26 16:29 | 50 | 012:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 40 EN CORTE DE LINEA SE REPARO ALAMBRE PRIMARIO | P21082600003 | New_Event | Wire Down | Include | Include | Equipment | 777 | 2021-08-26 | 38850 | keep | 0 | Aug | 2021 | 0.026461 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-08-26 05:23 | 2021-08-26 08:22 | 1 | 002:59 | P | OTRAS CAUSAS | DEFECTO INTERIOR | P21082600004 | New_Event | Other Causes | Include | Include | Other | 179 | 2021-08-26 | 179 | keep | 0 | Aug | 2021 | 0.00012192 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-08-26 05:56 | 2021-08-26 05:57 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21082600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-26 | 1827 | keep | 0 | Aug | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
CANOVANAS | 2021-08-26 05:57 | 2021-08-26 10:28 | 40 | 004:31 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21082600002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 271 | 2021-08-26 | 10840 | keep | 0 | Aug | 2021 | 0.0073831 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
HUMACAO | 2021-08-26 06:13 | 2021-08-26 06:14 | 1467 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR | C21082600005 | New_Event |  |  | Include | Wildlife | 1 | 2021-08-26 | 1467 | keep | 0 | Aug | 2021 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
HUMACAO | 2021-08-26 06:14 | 2021-08-26 10:54 | 82 | 004:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN CORTE DE LINEA CRUCE POR AVE | C21082600006 | 1st_after_momentary |  |  | Include | Wildlife | 280 | 2021-08-26 | 22960 | keep | 0 | Aug | 2021 | 0.015638 | 5.585e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 82
AGUADILLA | 2021-08-26 06:41 | 2021-08-26 13:18 | 100 | 006:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | M21082600001 | New_Event | Wire Down | Include | Include | Equipment | 397 | 2021-08-26 | 39700 | keep | 0 | Aug | 2021 | 0.027039 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-08-26 07:05 | 2021-08-27 16:25 | 8 | 033:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BARRAS DE PEDESTAL | C21082600007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2000 | 2021-08-26 | 16000 | keep | 0 | Aug | 2021 | 0.010898 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-08-26 07:11 | 2021-08-26 07:12 | 540 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21082600009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-26 | 540 | keep | 0 | Aug | 2021 | 0.00036779 | 0.00036779 | Momentary | FALSE | FALSE | Not_TMED_Event | 540
CAGUAS | 2021-08-26 07:14 | 2021-08-26 07:15 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21082600010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-26 | 1702 | keep | 0 | Aug | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
ARECIBO | 2021-08-26 07:30 | 2021-08-26 11:30 | 200 | 004:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A21082600006 | New_Event | Cutout Failure | Include | Include | Equipment | 240 | 2021-08-26 | 48000 | keep | 0 | Aug | 2021 | 0.032693 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CANOVANAS | 2021-08-26 07:31 | 2021-08-26 07:32 | 7621 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21082600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-26 | 7621 | keep | 0 | Aug | 2021 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
UTUADO | 2021-08-26 07:51 | 2021-08-26 13:00 | 70 | 005:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21082600008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 309 | 2021-08-26 | 21630 | keep | 0 | Aug | 2021 | 0.014732 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
CANOVANAS | 2021-08-26 08:05 | 2021-08-26 09:25 | 7 | 001:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 Y 1 X 15 EN CORTE DE LINEA Y TRANSFORMADOR SE RETIRO AVE MUERTA | R21082600007 | New_Event |  |  | Include | Wildlife | 80 | 2021-08-26 | 560 | keep | 0 | Aug | 2021 | 0.00038141 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
ARECIBO | 2021-08-26 08:06 | 2021-08-26 11:10 | 100 | 003:04 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO ENREDADERA SOBRE LAS LINEAS | A21082600013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2021-08-26 | 18400 | keep | 0 | Aug | 2021 | 0.012532 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-08-26 08:07 | 2021-08-26 11:32 | 1 | 003:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTES DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | S21082600007 | New_Event | Cutout Failure | Include | Include | Equipment | 205 | 2021-08-26 | 205 | keep | 0 | Aug | 2021 | 0.00013962 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-08-26 08:14 | 2021-08-26 08:15 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE 1909-08 LLEVA 1907-05 | S21082600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-26 | 2435 | keep | 0 | Aug | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-08-26 08:14 | 2021-08-26 08:15 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE 1909-08 LLEVA 1907-05 | S21082600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-26 | 2956 | keep | 0 | Aug | 2021 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2021-08-26 08:32 | 2021-08-26 20:28 | 70 | 011:56 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21082600008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 716 | 2021-08-26 | 50120 | keep | 0 | Aug | 2021 | 0.034137 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-08-26 08:40 | 2021-08-27 14:35 | 5 | 029:55 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA | M21082600011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1795 | 2021-08-26 | 8975 | keep | 0 | Aug | 2021 | 0.0061128 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2021-08-26 08:51 | 2021-08-26 17:10 | 35 | 008:19 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | M21082600014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 499 | 2021-08-26 | 17465 | keep | 0 | Aug | 2021 | 0.011895 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-08-26 09:05 | 2021-08-26 09:54 | 40 | 000:49 | P | HERRAJE ROTO O PODRIDO | SE ABRIO CORTE DE LINEA CON LOAD BOOSTER PARA ABRIR PUENTE PRIMARIO CRUCETA PARTIDA PERSONAL DE LUMA TRATANDO DE HACER UN DESCONECTE | S21082600000 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 49 | 2021-08-26 | 1960 | keep | 0 | Aug | 2021 | 0.0013349 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-08-26 09:16 | 2021-08-26 13:55 | 30 | 004:39 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR LIQUEANDO DE 50 X 50 KVA | R21082600012 | New_Event | Service Transformer Failure | Include | Include | Equipment | 279 | 2021-08-26 | 8370 | keep | 0 | Aug | 2021 | 0.0057008 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-08-26 09:18 | 2021-08-26 12:40 | 15 | 003:22 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21082600011 | New_Event | Secondary Wire Down | Include | Include | Equipment | 202 | 2021-08-26 | 3030 | keep | 0 | Aug | 2021 | 0.0020637 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-08-26 09:26 | 2021-08-28 14:28 | 10 | 053:02 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER HACIA T 30 | B21082600012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3182 | 2021-08-26 | 31820 | keep | 0 | Aug | 2021 | 0.021672 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-08-26 09:26 | 2021-08-26 13:12 | 25 | 003:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA Y 1 X 20 EN TRANSFORMADOR CRUCE POR PALOMA | C21082600021 | New_Event |  |  | Include | Wildlife | 226 | 2021-08-26 | 5650 | keep | 0 | Aug | 2021 | 0.0038482 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-08-26 09:30 | 2021-08-26 12:45 | 1 | 003:15 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 37.5 KVA POR LO MISMO | A21082600043 | New_Event | Service Transformer Failure | Include | Include | Equipment | 195 | 2021-08-26 | 195 | keep | 0 | Aug | 2021 | 0.00013281 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-08-26 09:57 | 2021-08-26 12:10 | 200 | 002:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21082600029 | New_Event | Bad Weather | Include | Include | Weather | 133 | 2021-08-26 | 26600 | keep | 0 | Aug | 2021 | 0.018117 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
SAN JUAN | 2021-08-26 10:00 | 2021-08-26 12:00 | 100 | 002:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA , SE ABRE CORTE DE LINEA PARA INSTALAR AISLADOR Y PICAR PEDAZO POSTE DE MADERA QUEMADO POR LINEA | S21082600045 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 120 | 2021-08-26 | 12000 | keep | 0 | Aug | 2021 | 0.0081731 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-08-26 10:04 | 2021-08-26 14:16 | 50 | 004:12 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE INSTALO TENSOR EN POSTE Y REPARO LINEAS CRUZADAS | C21082600029 | New_Event | Wire Down | Include | Include | Equipment | 252 | 2021-08-26 | 12600 | keep | 0 | Aug | 2021 | 0.0085818 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-26 10:05 | 2021-08-26 14:10 | 30 | 004:05 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 37.5KVA POR LO MISMO | A21082600045 | New_Event | Service Transformer Failure | Include | Include | Equipment | 245 | 2021-08-26 | 7350 | keep | 0 | Aug | 2021 | 0.0050061 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2021-08-26 10:06 | 2021-08-27 15:12 | 20 | 029:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LEVANTO CONDUCTOR Y CERRO PUENTE | C21082600030 | New_Event | Wire Down | Include | Include | Equipment | 1746 | 2021-08-26 | 34920 | keep | 0 | Aug | 2021 | 0.023784 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-08-26 10:10 | 2021-08-26 18:20 | 10 | 008:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | LINEA PRIMARIA PARTIDA SE SECCIONALIZO LA AVERIA | M21082600019 | New_Event | Wire Down | Include | Include | Equipment | 490 | 2021-08-26 | 4900 | keep | 0 | Aug | 2021 | 0.0033374 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
YAUCO | 2021-08-26 10:28 | 2021-08-26 14:41 | 2747 | 004:13 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PRIMARIO | P21082600050 | Additional_clients | Wire Down | Include | Include | Equipment | 253 | 2021-08-26 | 694991 | keep | 0 | Aug | 2021 | 0.47336 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-08-26 11:06 | 2021-08-26 17:13 | 55 | 006:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO CAJA PRIMARA AVERIADA Y 1 X 65 EN CORTE DE LINEA | C21082600038 | New_Event | Cutout Failure | Include | Include | Equipment | 367 | 2021-08-26 | 20185 | keep | 0 | Aug | 2021 | 0.013748 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
BAYAMON | 2021-08-26 11:20 | 2021-08-26 11:21 | 1533 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA EL 1709-05 | S21082600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-26 | 1533 | keep | 0 | Aug | 2021 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
BAYAMON | 2021-08-26 11:20 | 2021-08-26 11:21 | 2364 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1709-3 | S21082600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-26 | 2364 | keep | 0 | Aug | 2021 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
HUMACAO | 2021-08-26 11:26 | 2021-08-26 11:27 | 2354 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR | C21082600000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-08-26 | 2354 | keep | 0 | Aug | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
ARECIBO | 2021-08-26 11:26 | 2021-08-26 18:40 | 50 | 007:14 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A21082600040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 434 | 2021-08-26 | 21700 | keep | 0 | Aug | 2021 | 0.01478 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-08-26 11:27 | 2021-08-26 17:45 | 80 | 006:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SECCIONALIZO CAJA DE RISER AVERIADA ABRIENDO RISER @ SU-2B8D Y CERRO N/O EN SU-2B4 | C21082600041 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 378 | 2021-08-26 | 30240 | keep | 0 | Aug | 2021 | 0.020596 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-08-26 11:34 | 2021-08-26 20:15 | 40 | 008:41 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21082600035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 521 | 2021-08-26 | 20840 | keep | 0 | Aug | 2021 | 0.014194 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
AGUADILLA | 2021-08-26 11:46 | 2021-08-26 11:49 | 154 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21082600037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-08-26 | 462 | keep | 0 | Aug | 2021 | 0.00031467 | 0.00010489 | Momentary | FALSE | TRUE | Not_TMED_Event | 154
AGUADILLA | 2021-08-26 11:46 | 2021-08-26 11:49 | 1261 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21082600037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-08-26 | 3783 | keep | 0 | Aug | 2021 | 0.0025766 | 0.00085886 | Momentary | FALSE | TRUE | Not_TMED_Event | 1261
AGUADILLA | 2021-08-26 11:46 | 2021-08-26 11:49 | 3894 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21082600037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-08-26 | 11682 | keep | 0 | Aug | 2021 | 0.0079566 | 0.0026522 | Momentary | FALSE | TRUE | Not_TMED_Event | 3894
AGUADILLA | 2021-08-26 11:46 | 2021-08-26 11:49 | 997 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21082600037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-08-26 | 2991 | keep | 0 | Aug | 2021 | 0.0020372 | 0.00067905 | Momentary | FALSE | TRUE | Not_TMED_Event | 997
AGUADILLA | 2021-08-26 11:46 | 2021-08-26 11:49 | 1497 | 000:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M21082600037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2021-08-26 | 4491 | keep | 0 | Aug | 2021 | 0.0030588 | 0.0010196 | Momentary | FALSE | TRUE | Not_TMED_Event | 1497
YAUCO | 2021-08-26 11:48 | 2021-08-26 17:11 | 25 | 005:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEAS AVE CRUZO LINEAS | P21082600057 | New_Event |  |  | Include | Wildlife | 323 | 2021-08-26 | 8075 | keep | 0 | Aug | 2021 | 0.0054998 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
AGUADILLA | 2021-08-26 11:57 | 2021-08-26 21:25 | 5 | 009:28 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO TREE WIRE SAFADO | M21082600039 | New_Event | Wire Down | Include | Include | Equipment | 568 | 2021-08-26 | 2840 | keep | 0 | Aug | 2021 | 0.0019343 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2021-08-26 12:01 | 2021-08-27 14:09 | 1 | 026:08 | P | HERRAJE ROTO O PODRIDO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO CRUCETA PARTIDA | B21082600027 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 1568 | 2021-08-26 | 1568 | keep | 0 | Aug | 2021 | 0.001068 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-08-26 12:21 | 2021-08-26 16:47 | 90 | 004:26 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21082600056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2021-08-26 | 23940 | keep | 0 | Aug | 2021 | 0.016305 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
MAYAGÃœEZ | 2021-08-26 12:28 | 2021-08-26 17:00 | 5 | 004:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO TREE WIRE PARTIDO | A21082600043 | New_Event | Wire Down | Include | Include | Equipment | 272 | 2021-08-26 | 1360 | keep | 0 | Aug | 2021 | 0.00092629 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-08-26 13:04 | 2021-08-26 19:35 | 80 | 006:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ARIO PUENTES PARA REPARAR ALAMBRE PARTIDO | A21082600059 | New_Event | Wire Down | Include | Include | Equipment | 391 | 2021-08-26 | 31280 | keep | 0 | Aug | 2021 | 0.021305 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-08-26 13:10 | 2021-08-26 13:15 | 393 | 000:05 | T | DESGANCHE | DISPARO INTERRUPTOR | M21082600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 5 | 2021-08-26 | 1965 | keep | 0 | Aug | 2021 | 0.0013384 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2021-08-26 13:10 | 2021-08-26 13:15 | 4 | 000:05 | T | DESGANCHE | DISPARO 6007-4 LLEVANDO CARGA DEL 6007-05 | M21082600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 5 | 2021-08-26 | 20 | keep | 0 | Aug | 2021 | 1.3622e-05 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2021-08-26 13:11 | 2021-08-26 13:12 | 1494 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21082600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-26 | 1494 | keep | 0 | Aug | 2021 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
MAYAGÃœEZ | 2021-08-26 13:21 | 2021-08-26 13:25 | 393 | 000:04 | T | DESGANCHE | DISPARO INTERRUPTOR | M21082600000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 4 | 2021-08-26 | 1572 | keep | 0 | Aug | 2021 | 0.0010707 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-26 13:21 | 2021-08-26 13:25 | 4 | 000:04 | T | DESGANCHE | DISPARO INTERRUPTOR 6007-04 LLEVANDO LA CARGA DEL 6007-05 | M21082600000 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 4 | 2021-08-26 | 16 | keep | 0 | Aug | 2021 | 1.0898e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2021-08-26 13:24 | 2021-08-26 13:51 | 35 | 000:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO LINEA A PIN | P21082600071 | New_Event | Wire Down | Include | Include | Equipment | 27 | 2021-08-26 | 945 | keep | 0 | Aug | 2021 | 0.00064364 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-08-26 13:24 | 2021-08-26 14:47 | 30 | 001:23 | P | SOBRECARGA | SE CAMBIARON DE FASE C A FASE A TRES TRANSFORMADORES PARA BALANCEAR LAS LINEAS FUSIBLE CORTE DE LINEA FUNDIENDO CONSTANTEMENTE | M21082600049 | New_Event | Trip Due To Overload | Include | Include | Other | 83 | 2021-08-26 | 2490 | keep | 0 | Aug | 2021 | 0.0016959 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-08-26 13:28 | 2021-08-26 18:50 | 50 | 005:22 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21082600033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 322 | 2021-08-26 | 16100 | keep | 0 | Aug | 2021 | 0.010966 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-26 13:32 | 2021-08-27 16:00 | 10 | 026:28 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | S21082600043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1588 | 2021-08-26 | 15880 | keep | 0 | Aug | 2021 | 0.010816 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-08-26 13:32 | 2021-08-26 16:42 | 393 | 003:10 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZO DESGANCHE | M21082600000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 190 | 2021-08-26 | 74670 | keep | 0 | Aug | 2021 | 0.050857 | 0.00026767 | Sustained | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2021-08-26 13:32 | 2021-08-26 16:42 | 4 | 003:10 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZO DESGANCHE | M21082600000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 190 | 2021-08-26 | 760 | keep | 0 | Aug | 2021 | 0.00051763 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-08-26 13:43 | 2021-08-27 10:00 | 35 | 020:17 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRE CORTE DE LINEA PARA INSTALAR AISLADOR Y PICAR PEDAZO POSTE DE MADERA QUEMADO POR LINEA | S21082600045 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1217 | 2021-08-26 | 42595 | keep | 0 | Aug | 2021 | 0.029011 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-08-26 13:50 | 2021-08-26 16:46 | 50 | 002:56 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21082600046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 176 | 2021-08-26 | 8800 | keep | 0 | Aug | 2021 | 0.0059936 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-08-26 13:59 | 2021-08-26 14:00 | 3387 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO Y SE CERRO POR SCADA | B21082600064 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2021-08-26 | 3387 | keep | 0 | Aug | 2021 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
UTUADO | 2021-08-26 14:00 | 2021-08-26 15:40 | 30 | 001:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO ALAMBRE PARTIDO | A21082600000 | New_Event | Wire Down | Include | Include | Equipment | 100 | 2021-08-26 | 3000 | keep | 0 | Aug | 2021 | 0.0020433 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-08-26 14:09 | 2021-08-26 16:29 | 10 | 002:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21082600040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 140 | 2021-08-26 | 1400 | keep | 0 | Aug | 2021 | 0.00095353 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-08-26 14:09 | 2021-08-26 17:06 | 60 | 002:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21082600068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2021-08-26 | 10620 | keep | 0 | Aug | 2021 | 0.0072332 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
VEGA BAJA | 2021-08-26 14:55 | 2021-08-26 14:56 | 3387 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | B21082600064 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-08-26 | 3387 | keep | 0 | Aug | 2021 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
MAYAGÃœEZ | 2021-08-26 15:30 | 2021-08-26 23:45 | 100 | 008:15 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LA LINEA | M21082600062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 495 | 2021-08-26 | 49500 | keep | 0 | Aug | 2021 | 0.033714 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-08-26 15:31 | 2021-08-27 12:14 | 10 | 020:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR REMPLAZO CAJA QUEMADA | C21082600077 | New_Event | Cutout Failure | Include | Include | Equipment | 1243 | 2021-08-26 | 12430 | keep | 0 | Aug | 2021 | 0.008466 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-08-26 15:34 | 2021-08-26 15:35 | 3387 | 000:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | B21082600064 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2021-08-26 | 3387 | keep | 0 | Aug | 2021 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
SAN JUAN | 2021-08-26 15:36 | 2021-08-28 17:52 | 50 | 050:16 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | REEMPLAZO EMPALME | R21082600026 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 3016 | 2021-08-26 | 150800 | keep | 0 | Aug | 2021 | 0.10271 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2021-08-26 15:37 | 2021-08-26 16:19 | 10 | 000:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21082500065 | New_Event | Secondary Wire Down | Include | Include | Equipment | 42 | 2021-08-26 | 420 | keep | 0 | Aug | 2021 | 0.00028606 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-08-26 15:47 | 2021-08-26 17:47 | 3387 | 002:00 | T | DESCONECTIVO DEFECTUOSO | DISPARO ALIMENTADOR 9004-08 Y SE REEMPLAZO MACHETE AVERIADO | B21082600064 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 120 | 2021-08-26 | 406440 | keep | 0 | Aug | 2021 | 0.27682 | 0.0023069 | Sustained | FALSE | FALSE | Not_TMED_Event | 3387
BAYAMON | 2021-08-26 15:49 | 2021-08-26 17:28 | 271 | 001:39 | T | HERRAJE ROTO O PODRIDO | DISPARO DE INTERRUPTOR SE LEVANTO LINEA SAFADA DE AISLADOR Y SE LLEVO PROVISIONALMENTE A SU SITIO SE REFIERE PARA REEMPLAZO DE HERRAJE | S21082600065 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 99 | 2021-08-26 | 26829 | keep | 0 | Aug | 2021 | 0.018273 | 0.00018458 | Sustained | FALSE | TRUE | Not_TMED_Event | 271
ARECIBO | 2021-08-26 15:49 | 2021-08-27 17:32 | 30 | 025:43 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21082600077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1543 | 2021-08-26 | 46290 | keep | 0 | Aug | 2021 | 0.031528 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-08-26 15:49 | 2021-08-26 18:06 | 3688 | 002:17 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR PARTIDO Y SE RETIRO RAMA SOBRE LINEA | A21082600078 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 137 | 2021-08-26 | 505256 | keep | 0 | Aug | 2021 | 0.34413 | 0.0025119 | Sustained | FALSE | TRUE | Not_TMED_Event | 3688
BAYAMON | 2021-08-26 15:53 | 2021-08-26 15:54 | 1356 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21082600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-26 | 1356 | keep | 0 | Aug | 2021 | 0.00092357 | 0.00092357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1356
PONCE | 2021-08-26 16:25 | 2021-08-27 00:04 | 150 | 007:39 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO PARARRAYO AVERIADO | P21082600108 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 459 | 2021-08-26 | 68850 | keep | 0 | Aug | 2021 | 0.046893 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
FAJARDO | 2021-08-26 16:29 | 2021-08-26 19:18 | 6 | 002:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REEMPLAZAR BAJANTE SECUNDARIO Y SE REPARO VARIAS TOMAS | R21082600027 | New_Event | Secondary Wire Down | Include | Include | Equipment | 169 | 2021-08-26 | 1014 | keep | 0 | Aug | 2021 | 0.00069063 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-08-26 16:36 | 2021-08-26 17:41 | 110 | 001:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE ABIERTO DE LINEA TRONCAL | S21082600079 | New_Event | Wire Down | Include | Include | Equipment | 65 | 2021-08-26 | 7150 | keep | 0 | Aug | 2021 | 0.0048698 | 7.492e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 110
ARECIBO | 2021-08-26 16:37 | 2021-08-26 22:31 | 30 | 005:54 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21082600090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 354 | 2021-08-26 | 10620 | keep | 0 | Aug | 2021 | 0.0072332 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-08-26 17:10 | 2021-08-26 18:45 | 7 | 001:35 | P | DESGANCHE | SE ABRIO PUENTES PARA RETIRAR ARBOL SOBRE LINEAS | A21082600095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2021-08-26 | 665 | keep | 0 | Aug | 2021 | 0.00045293 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
CAGUAS | 2021-08-26 17:33 | 2021-08-26 20:52 | 11 | 003:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR IGUANA | C21082600083 | New_Event |  |  | Include | Wildlife | 199 | 2021-08-26 | 2189 | keep | 0 | Aug | 2021 | 0.0014909 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2021-08-26 17:41 | 2021-08-26 17:54 | 601 | 000:13 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE DE LINEA TRONCAL ADEMAS LLEVA LA CARGA DEL ALIMENTADOR 1437-02 | S21082600085 | Additional_clients | Wire Down | Include | Include | Equipment | 13 | 2021-08-26 | 7813 | keep | 0 | Aug | 2021 | 0.0053214 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-26 17:47 | 2021-08-27 13:18 | 50 | 019:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA LINEA ARRIADA | M21082600077 | New_Event | Wire Down | Include | Include | Equipment | 1171 | 2021-08-26 | 58550 | keep | 0 | Aug | 2021 | 0.039878 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-08-26 18:47 | 2021-08-27 19:44 | 10 | 024:57 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21082600071 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1497 | 2021-08-26 | 14970 | keep | 0 | Aug | 2021 | 0.010196 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-08-26 19:06 | 2021-08-26 19:07 | 640 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE DE LINEA TRONCAL ADEMAS LLEVA LA CARGA DEL ALIMENTADOR 1437-02 | S21082600085 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-26 | 640 | keep | 0 | Aug | 2021 | 0.0004359 | 0.0004359 | Momentary | FALSE | TRUE | Not_TMED_Event | 640
UTUADO | 2021-08-26 19:27 | 2021-08-27 10:35 | 30 | 015:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | A21082600113 | New_Event | Bad Weather | Include | Include | Weather | 908 | 2021-08-26 | 27240 | keep | 0 | Aug | 2021 | 0.018553 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
VEGA BAJA | 2021-08-26 19:59 | 2021-08-27 17:39 | 30 | 021:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO CONDUCTOR | B21082600078 | New_Event | Wire Down | Include | Include | Equipment | 1300 | 2021-08-26 | 39000 | keep | 0 | Aug | 2021 | 0.026563 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-08-26 20:21 | 2021-08-27 12:01 | 60 | 015:40 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21082600080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 940 | 2021-08-26 | 56400 | keep | 0 | Aug | 2021 | 0.038414 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-08-26 20:23 | 2021-08-27 11:46 | 65 | 015:23 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | M21082600089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 923 | 2021-08-26 | 59995 | keep | 0 | Aug | 2021 | 0.040862 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
ARECIBO | 2021-08-26 20:27 | 2021-08-27 11:30 | 60 | 015:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADORES | A21082600120 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 903 | 2021-08-26 | 54180 | keep | 0 | Aug | 2021 | 0.036902 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
FAJARDO | 2021-08-26 20:35 | 2021-08-27 15:12 | 15 | 018:37 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50 KVA X 50 KVA | R21082600040 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1117 | 2021-08-26 | 16755 | keep | 0 | Aug | 2021 | 0.011412 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-08-26 20:50 | 2021-08-26 22:31 | 50 | 001:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA EN CORTE DE LINEA | A21082600125 | New_Event | Cutout Failure | Include | Include | Equipment | 101 | 2021-08-26 | 5050 | keep | 0 | Aug | 2021 | 0.0034395 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-08-26 20:52 | 2021-08-26 21:13 | 50 | 000:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA DEFECTUOSA ARQUEANDO | C21082600083 | New_Event | Cutout Failure | Include | Include | Equipment | 21 | 2021-08-26 | 1050 | keep | 0 | Aug | 2021 | 0.00071515 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2021-08-26 21:00 | 2021-08-28 14:06 | 7 | 041:06 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR REPTIL | R21082600041 | New_Event |  |  | Include | Wildlife | 2466 | 2021-08-26 | 17262 | keep | 0 | Aug | 2021 | 0.011757 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-08-26 21:26 | 2021-08-26 21:27 | 1 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21082600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-26 | 1 | keep | 0 | Aug | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-08-26 21:26 | 2021-08-26 21:27 | 2891 | 000:01 | T | DESGANCHE | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTORES VIVOS EN EL SUELO | R21082600029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-26 | 2891 | keep | 0 | Aug | 2021 | 0.001969 | 0.001969 | Momentary | FALSE | FALSE | Not_TMED_Event | 2891
SAN JUAN | 2021-08-26 21:27 | 2021-08-26 22:04 | 100 | 000:37 | P | DESGANCHE | RETIRO RAMA DE LAS LINEAS Y LEVANTO CONDUCTOR | R21082600029 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 37 | 2021-08-26 | 3700 | keep | 0 | Aug | 2021 | 0.0025201 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-08-26 21:28 | 2021-08-26 21:29 | 25 | 000:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA EN TRANSFORMADOR | S21082600087 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-26 | 25 | keep | 0 | Aug | 2021 | 1.7027e-05 | 1.7027e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 25
CAGUAS | 2021-08-26 21:32 | 2021-08-27 08:47 | 300 | 011:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 Y 1 X 80 EN CORTES DE LINEA CERRO PUENTE | C21082600088 | New_Event | Wire Down | Include | Include | Equipment | 675 | 2021-08-26 | 202500 | keep | 0 | Aug | 2021 | 0.13792 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
ARECIBO | 2021-08-26 21:40 | 2021-08-27 11:50 | 90 | 014:10 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA DESGANCHE | A21082600129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 850 | 2021-08-26 | 76500 | keep | 0 | Aug | 2021 | 0.052104 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
ARECIBO | 2021-08-26 21:51 | 2021-08-27 09:00 | 40 | 011:09 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | A21082600130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 669 | 2021-08-26 | 26760 | keep | 0 | Aug | 2021 | 0.018226 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-08-26 21:56 | 2021-08-27 00:11 | 300 | 002:15 | P | DESGANCHE | 1 X 200 EN SALIDA DE CONVERTIDOR CRUCE DE FASES POR RAMAS | P21082600166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2021-08-26 | 40500 | keep | 0 | Aug | 2021 | 0.027584 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
FAJARDO | 2021-08-26 22:06 | 2021-08-26 22:07 | 2286 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21082600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-26 | 2286 | keep | 0 | Aug | 2021 | 0.001557 | 0.001557 | Momentary | FALSE | FALSE | Not_TMED_Event | 2286
MAYAGÃœEZ | 2021-08-26 22:27 | 2021-08-27 11:15 | 50 | 012:48 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | M21082600095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 768 | 2021-08-26 | 38400 | keep | 0 | Aug | 2021 | 0.026154 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-08-26 22:28 | 2021-08-26 22:29 | 4 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21082600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-26 | 4 | keep | 0 | Aug | 2021 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2021-08-26 23:02 | 2021-08-27 11:39 | 1320 | 012:37 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE PUSO INTERRUPTOR EN SERVICIO. EXCAVADORA PARTIO TENSORES DE POSTE Y SE PEGARON A LA LINEA. LLEVA LA CARGA DEL INTERRUPTOR 2. | P21082700030 | New_Event |  |  | Include | Wildlife | 757 | 2021-08-26 | 999240 | keep | 0 | Aug | 2021 | 0.68058 | 0.00089905 | Sustained | FALSE | TRUE | Not_TMED_Event | 1320
PONCE | 2021-08-26 23:02 | 2021-08-27 13:18 | 50 | 014:16 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21082600170 | New_Event | Vegetation Contact | Include | Include | Vegetation | 856 | 2021-08-26 | 42800 | keep | 0 | Aug | 2021 | 0.029151 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-08-26 23:02 | 2021-08-27 11:39 | 274 | 012:37 | T | ANIMAL U OBJETO EXTRAÃ‘O | SE PUSO INTERRUPTOR EN SERVICIO. EXCAVADORA PARTIO TENSORES DE POSTE Y SE PEGARON A LA LINEA. SU CARGA ESTA POR EL INTERRUPTOR 1 | P21082700030 | New_Event |  |  | Include | Wildlife | 757 | 2021-08-26 | 207418 | keep | 0 | Aug | 2021 | 0.14127 | 0.00018662 | Sustained | FALSE | TRUE | Not_TMED_Event | 274
ARECIBO | 2021-08-26 23:42 | 2021-08-27 01:12 | 1105 | 001:30 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DOS BOCAS | A21082700008 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 90 | 2021-08-26 | 99450 | keep | 0 | Aug | 2021 | 0.067735 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
UTUADO | 2021-08-26 23:42 | 2021-08-27 01:12 | 1633 | 001:30 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DOS BOCAS | A21082700005 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 90 | 2021-08-26 | 146970 | keep | 0 | Aug | 2021 | 0.1001 | 0.0011122 | Sustained | FALSE | FALSE | Not_TMED_Event | 1633
UTUADO | 2021-08-26 23:42 | 2021-08-27 01:12 | 1624 | 001:30 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DOS BOCAS | A21082700005 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 90 | 2021-08-26 | 146160 | keep | 0 | Aug | 2021 | 0.099549 | 0.0011061 | Sustained | FALSE | FALSE | Not_TMED_Event | 1624
SAN JUAN | 2021-08-27 00:26 | 2021-08-27 00:27 | 4291 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21082700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-27 | 4291 | keep | 0 | Aug | 2021 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
SAN JUAN | 2021-08-27 00:47 | 2021-08-27 02:14 | 1290 | 001:27 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO DE MH-2 A CAJAS SECAS PARA SECCIONALIZAR Y SE CERRO RISER A MH-2 QUEDO EN SERVICIO Y 100% 1346-5 | S21082700028 | New_Event | Switch Failure | Include | Include | Equipment | 87 | 2021-08-27 | 112230 | keep | 0 | Aug | 2021 | 0.076439 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
SAN JUAN | 2021-08-27 00:47 | 2021-08-27 01:58 | 135 | 001:11 | T | DESCONECTIVO DEFECTUOSO | DISPARO CON R/R OFF SE SECCIONALIZO ABRIENDO MH-10 VILLA NEVARES SE DEJO ABIERTO 1346-5 Y PARTE DEL 1348-8 | S21082700006 | New_Event | Switch Failure | Include | Include | Equipment | 71 | 2021-08-27 | 9585 | keep | 0 | Aug | 2021 | 0.0065283 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2021-08-27 01:58 | 2021-08-27 02:14 | 500 | 000:16 | P | DESCONECTIVO DEFECTUOSO | SE CERRO MH-10 HACIA VILLA NEVARES Y PARTE DEL 1348-8 | S21082700006 | New_Event | Switch Failure | Include | Include | Equipment | 16 | 2021-08-27 | 8000 | keep | 0 | Aug | 2021 | 0.0054488 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2021-08-27 02:14 | 2021-08-27 06:46 | 922 | 004:32 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO MH-2 A CAJAS SECAS Y SE CERRO RISER A MH-2 100% EN SERVICIO 1346-5 Y PARTE DEL 1348-8 AVERIA NUEVA CAJAS SECAS MH-2 | S21082700028 | New_Event | Switch Failure | Include | Include | Equipment | 272 | 2021-08-27 | 250784 | keep | 0 | Aug | 2021 | 0.17081 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-08-27 02:14 | 2021-08-27 06:46 | 600 | 004:32 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO DE MH-2 A CAJAS SECAS PARA SECCIONALIZAR Y SE CERRO RISER A MH-2 QUEDO EN SERVICIO Y 100% 1346-5 | S21082700028 | Additional_clients | Switch Failure | Include | Include | Equipment | 272 | 2021-08-27 | 163200 | keep | 0 | Aug | 2021 | 0.11115 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-08-27 02:19 | 2021-08-27 02:21 | 135 | 000:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO NO RECERRO LLEVA CARGA 1346-5 Y PARTE DEL 1348-8 | S21082700018 | Partial_restoration | Switch Failure | Include | Include | Equipment | 2 | 2021-08-27 | 270 | keep | 0 | Aug | 2021 | 0.0001839 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-08-27 03:03 | 2021-08-27 15:11 | 12 | 012:08 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR | S21082700019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 728 | 2021-08-27 | 8736 | keep | 0 | Aug | 2021 | 0.00595 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-08-27 03:23 | 2021-08-27 04:58 | 135 | 001:35 | T | DESCONECTIVO DEFECTUOSO | DISPARO CON R/R OFF SE ABRIO MH-1 FRENTE AL 5 DEALER HYUNDAI 100% 1401-8, QUE FUERA 1346-5 Y 1348-8 | S21082700020 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 95 | 2021-08-27 | 12825 | keep | 0 | Aug | 2021 | 0.008735 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2021-08-27 05:22 | 2021-08-27 06:18 | 135 | 000:56 | T | DESCONECTIVO DEFECTUOSO | DISPARO AL CERRAR RISER FTE. BURGER KING 100% EN SERVICIO QUEDO FUERA 1346-5 Y PARTE DEL 1348-8 | S21082700028 | Partial_restoration | Switch Failure | Include | Include | Equipment | 56 | 2021-08-27 | 7560 | keep | 0 | Aug | 2021 | 0.0051491 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-27 05:59 | 2021-08-27 16:00 | 25 | 010:01 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA SOBRE LINEA | M21082700005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 601 | 2021-08-27 | 15025 | keep | 0 | Aug | 2021 | 0.010233 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-08-27 06:00 | 2021-08-28 12:13 | 12 | 030:13 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5 KVA AVERIADO POR LO MISMO | A21082700000 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1813 | 2021-08-27 | 21756 | keep | 0 | Aug | 2021 | 0.014818 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2021-08-27 06:04 | 2021-08-27 06:05 | 574 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M21082700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-27 | 574 | keep | 0 | Aug | 2021 | 0.00039095 | 0.00039095 | Momentary | FALSE | TRUE | Not_TMED_Event | 574
AGUADILLA | 2021-08-27 06:04 | 2021-08-27 06:05 | 2493 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M21082700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-27 | 2493 | keep | 0 | Aug | 2021 | 0.001698 | 0.001698 | Momentary | FALSE | TRUE | Not_TMED_Event | 2493
AGUADILLA | 2021-08-27 06:04 | 2021-08-27 06:05 | 1415 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M21082700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-27 | 1415 | keep | 0 | Aug | 2021 | 0.00096375 | 0.00096375 | Momentary | FALSE | TRUE | Not_TMED_Event | 1415
AGUADILLA | 2021-08-27 06:04 | 2021-08-27 06:05 | 1428 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M21082700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-27 | 1428 | keep | 0 | Aug | 2021 | 0.0009726 | 0.0009726 | Momentary | FALSE | TRUE | Not_TMED_Event | 1428
AGUADILLA | 2021-08-27 06:04 | 2021-08-27 06:05 | 1036 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M21082700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-27 | 1036 | keep | 0 | Aug | 2021 | 0.00070561 | 0.00070561 | Momentary | FALSE | TRUE | Not_TMED_Event | 1036
AGUADILLA | 2021-08-27 06:04 | 2021-08-27 06:05 | 382 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M21082700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-27 | 382 | keep | 0 | Aug | 2021 | 0.00026018 | 0.00026018 | Momentary | FALSE | TRUE | Not_TMED_Event | 382
AGUADILLA | 2021-08-27 06:04 | 2021-08-27 06:05 | 39 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M21082700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-27 | 39 | keep | 0 | Aug | 2021 | 2.6563e-05 | 2.6563e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 39
AGUADILLA | 2021-08-27 06:04 | 2021-08-27 06:05 | 2366 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M21082700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-27 | 2366 | keep | 0 | Aug | 2021 | 0.0016115 | 0.0016115 | Momentary | FALSE | TRUE | Not_TMED_Event | 2366
MAYAGÃœEZ | 2021-08-27 06:04 | 2021-08-27 06:05 | 1337 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M21082700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-27 | 1337 | keep | 0 | Aug | 2021 | 0.00091062 | 0.00091062 | Momentary | FALSE | TRUE | Not_TMED_Event | 1337
AGUADILLA | 2021-08-27 06:04 | 2021-08-27 06:05 | 709 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5600 | M21082700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-27 | 709 | keep | 0 | Aug | 2021 | 0.0004829 | 0.0004829 | Momentary | FALSE | TRUE | Not_TMED_Event | 709
MAYAGÃœEZ | 2021-08-27 06:05 | 2021-08-27 10:59 | 810 | 004:54 | T | LINEA DE TRANSMISION 38KV | LINEA DE TRANSMISION 5600 SOBRE ALIMENTADOR SE RETIRO Y SE CERRO INTERRUPTOR | M21082700007 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 294 | 2021-08-27 | 238140 | keep | 0 | Aug | 2021 | 0.1622 | 0.00055169 | Sustained | FALSE | TRUE | Not_TMED_Event | 810
BAYAMON | 2021-08-27 06:12 | 2021-08-27 06:13 | 222 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO. LLEVA 99% DEL 1909-09 | S21082700032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-27 | 222 | keep | 0 | Aug | 2021 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2021-08-27 06:12 | 2021-08-27 06:13 | 4411 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO. 99% DE LA CARGA ESTA POR EL 1907-03 | S21082700032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-27 | 4411 | keep | 0 | Aug | 2021 | 0.0030043 | 0.0030043 | Momentary | FALSE | FALSE | Not_TMED_Event | 4411
BAYAMON | 2021-08-27 06:13 | 2021-08-27 14:07 | 1 | 007:54 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21082700051 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 474 | 2021-08-27 | 474 | keep | 0 | Aug | 2021 | 0.00032284 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CANOVANAS | 2021-08-27 06:30 | 2021-08-27 06:31 | 2106 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR RECIERRE NORMALMENTE EN OFF | R21082700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-27 | 2106 | keep | 0 | Aug | 2021 | 0.0014344 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
ARECIBO | 2021-08-27 06:47 | 2021-08-27 11:10 | 80 | 004:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA MARCA CHINT DE 100 AMP. | A21082700038 | New_Event | Cutout Failure | Include | Include | Equipment | 263 | 2021-08-27 | 21040 | keep | 0 | Aug | 2021 | 0.01433 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-08-27 07:09 | 2021-08-27 15:00 | 2 | 007:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA NO FUNDIO FUSIBLE ALGUNO | S21082700041 | New_Event | Cutout Failure | Include | Include | Equipment | 471 | 2021-08-27 | 942 | keep | 0 | Aug | 2021 | 0.00064159 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2021-08-27 07:34 | 2021-08-27 09:22 | 1228 | 001:48 | T | LINEA DE TRANSMISION 38KV | DISPARO DEBIDO A OPERACION DE LA LINEA 14400 SE ACTIVO RELE DE FRECUENCIA | C21082700006 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 108 | 2021-08-27 | 132624 | keep | 0 | Aug | 2021 | 0.09033 | 0.00083639 | Sustained | TRUE | TRUE | Not_TMED_Event | 1228
CAGUAS | 2021-08-27 07:34 | 2021-08-27 09:22 | 1271 | 001:48 | T | LINEA DE TRANSMISION 38KV | DISPARO DEBIDO A OPERACION DE LA LINEA 14400 SE ACTIVO RELE DE FRECUENCIA | C21082700007 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 108 | 2021-08-27 | 137268 | keep | 0 | Aug | 2021 | 0.093493 | 0.00086567 | Sustained | TRUE | TRUE | Not_TMED_Event | 1271
CAGUAS | 2021-08-27 07:34 | 2021-08-27 09:22 | 1893 | 001:48 | T | LINEA DE TRANSMISION 38KV | DISPARO DEBIDO A OPERACION DE LA LINEA 14400 SE ACTIVO RELE DE FRECUENCIA | C21082700008 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 108 | 2021-08-27 | 204444 | keep | 0 | Aug | 2021 | 0.13925 | 0.0012893 | Sustained | TRUE | TRUE | Not_TMED_Event | 1893
CAGUAS | 2021-08-27 07:34 | 2021-08-27 09:22 | 473 | 001:48 | T | LINEA DE TRANSMISION 38KV | DISPARO DEBIDO A OPERACION DE LA LINEA 14400 SE ACTIVO RELE DE FRECUENCIA | C21082700007 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 108 | 2021-08-27 | 51084 | keep | 0 | Aug | 2021 | 0.034793 | 0.00032216 | Sustained | TRUE | TRUE | Not_TMED_Event | 473
PONCE | 2021-08-27 07:47 | 2021-08-27 11:02 | 15 | 003:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN TRANSFORMADOR POR CONTACTO DE AVE | P21082700006 | New_Event |  |  | Include | Wildlife | 195 | 2021-08-27 | 2925 | keep | 0 | Aug | 2021 | 0.0019922 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-08-27 07:51 | 2021-08-27 17:29 | 40 | 009:38 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21082700004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 578 | 2021-08-27 | 23120 | keep | 0 | Aug | 2021 | 0.015747 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-08-27 07:55 | 2021-08-27 07:56 | 1702 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21082700011 | New_Event |  |  | Include | Wildlife | 1 | 2021-08-27 | 1702 | keep | 0 | Aug | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
SAN JUAN | 2021-08-27 08:16 | 2021-08-27 08:17 | 1 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | R21082700005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-27 | 1 | keep | 0 | Aug | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-08-27 08:19 | 2021-08-27 14:11 | 40 | 005:52 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21082700014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 352 | 2021-08-27 | 14080 | keep | 0 | Aug | 2021 | 0.0095898 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-08-27 08:47 | 2021-08-27 08:48 | 906 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO SE CERRO POR CONTROL | C21082700021 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2021-08-27 | 906 | keep | 0 | Aug | 2021 | 0.00061707 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2021-08-27 08:48 | 2021-08-27 16:01 | 300 | 007:13 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 Y 1 X 80 EN CORTES DE LINEA CERRO PUENTE | C21082600088 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 433 | 2021-08-27 | 129900 | keep | 0 | Aug | 2021 | 0.088474 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
HUMACAO | 2021-08-27 08:52 | 2021-08-27 16:31 | 1 | 007:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 65 EN CORTE DE LINEA REPARO NEUTRAL SECUNDARIO | C21082700022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 459 | 2021-08-27 | 459 | keep | 0 | Aug | 2021 | 0.00031262 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
YAUCO | 2021-08-27 09:06 | 2021-08-27 10:46 | 15 | 001:40 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR. NO REPORTAN CAUSA | P21082700019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 100 | 2021-08-27 | 1500 | keep | 0 | Aug | 2021 | 0.0010216 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-08-27 09:14 | 2021-08-27 17:28 | 275 | 008:14 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 RVA DE 100 EN SU-15 POR CONTAMINACION | R21082700013 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 494 | 2021-08-27 | 135850 | keep | 0 | Aug | 2021 | 0.092527 | 0.0001873 | Sustained | FALSE | FALSE | Not_TMED_Event | 275
UTUADO | 2021-08-27 09:15 | 2021-08-27 11:30 | 30 | 002:15 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | A21082700051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2021-08-27 | 4050 | keep | 0 | Aug | 2021 | 0.0027584 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-08-27 09:25 | 2021-08-27 10:15 | 20 | 000:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR BAJANTE Y LINEA SECUNDARIA | S21082700052 | New_Event | Secondary Wire Down | Include | Include | Equipment | 50 | 2021-08-27 | 1000 | keep | 0 | Aug | 2021 | 0.0006811 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-08-27 09:25 | 2021-08-27 11:12 | 20 | 001:47 | P | SECUNDARIA/DESGANCHE | SE ABRE MONTURA PARA DESGANCHE Y REPARAR TOMA SECUNDARIA | S21082500064 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 107 | 2021-08-27 | 2140 | keep | 0 | Aug | 2021 | 0.0014575 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-08-27 09:29 | 2021-08-27 10:30 | 8 | 001:01 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21082700017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 61 | 2021-08-27 | 488 | keep | 0 | Aug | 2021 | 0.00033237 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-08-27 10:02 | 2021-08-27 16:43 | 10 | 006:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21082700029 | New_Event | Secondary Wire Down | Include | Include | Equipment | 401 | 2021-08-27 | 4010 | keep | 0 | Aug | 2021 | 0.0027312 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-08-27 10:05 | 2021-08-27 16:33 | 7 | 006:28 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA PARTIDA | A21082700056 | New_Event | Secondary Wire Down | Include | Include | Equipment | 388 | 2021-08-27 | 2716 | keep | 0 | Aug | 2021 | 0.0018499 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
HUMACAO | 2021-08-27 10:10 | 2021-08-27 16:28 | 50 | 006:18 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C21082700031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 378 | 2021-08-27 | 18900 | keep | 0 | Aug | 2021 | 0.012873 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-08-27 10:11 | 2021-08-27 12:34 | 100 | 002:23 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P21082700033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2021-08-27 | 14300 | keep | 0 | Aug | 2021 | 0.0097397 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
UTUADO | 2021-08-27 10:16 | 2021-08-27 11:35 | 7 | 001:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21082700059 | New_Event | Secondary Wire Down | Include | Include | Equipment | 79 | 2021-08-27 | 553 | keep | 0 | Aug | 2021 | 0.00037665 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2021-08-27 10:38 | 2021-08-27 15:08 | 1 | 004:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO 3 CAJAS QUEMADAS | C21082700036 | New_Event | Cutout Failure | Include | Include | Equipment | 270 | 2021-08-27 | 270 | keep | 0 | Aug | 2021 | 0.0001839 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-08-27 10:42 | 2021-08-27 13:34 | 1 | 002:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA | R21082700021 | New_Event | Secondary Wire Down | Include | Include | Equipment | 172 | 2021-08-27 | 172 | keep | 0 | Aug | 2021 | 0.00011715 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-08-27 11:11 | 2021-08-27 16:56 | 139 | 005:45 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN SU-2 AVERIA DEL T-49 AL T-50 | R21082700029 | New_Event | UG Cable Fault | Include | Include | Equipment | 345 | 2021-08-27 | 47955 | keep | 0 | Aug | 2021 | 0.032662 | 9.4672e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 139
ARECIBO | 2021-08-27 11:24 | 2021-08-27 19:09 | 20 | 007:45 | P | ESTRUCTURA AVERIADA | SE REEMPLAZO POSTE 45' METAL Y TRANSFORMADOR 25KVA HOWARD INDUSTRY 4160V/120/240V SER.#1638951018 | A21082700069 | New_Event | Defective Pole | Include | Include | Equipment | 465 | 2021-08-27 | 9300 | keep | 0 | Aug | 2021 | 0.0063342 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2021-08-27 11:26 | 2021-08-27 11:27 | 1234 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR | R21082700032 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-08-27 | 1234 | keep | 0 | Aug | 2021 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
FAJARDO | 2021-08-27 11:27 | 2021-08-27 15:13 | 8 | 003:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA DE TRANSFORMADOR | R21082700034 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 226 | 2021-08-27 | 1808 | keep | 0 | Aug | 2021 | 0.0012314 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2021-08-27 11:29 | 2021-08-27 16:00 | 60 | 004:31 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21082700035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 271 | 2021-08-27 | 16260 | keep | 0 | Aug | 2021 | 0.011075 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-08-27 11:43 | 2021-08-27 15:11 | 65 | 003:28 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO ENCONTRO CAUSA | C21082700042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 208 | 2021-08-27 | 13520 | keep | 0 | Aug | 2021 | 0.0092084 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
YAUCO | 2021-08-27 12:19 | 2021-08-27 16:22 | 100 | 004:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 Y 1 X 65 EN DISTINTOS CORTES DE LINEA, GLOBO CRUZO FASE | P21082700050 | New_Event |  |  | Include | Wildlife | 243 | 2021-08-27 | 24300 | keep | 0 | Aug | 2021 | 0.016551 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-08-27 12:23 | 2021-08-27 12:24 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21082700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-27 | 1310 | keep | 0 | Aug | 2021 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
ARECIBO | 2021-08-27 12:40 | 2021-08-27 13:40 | 6 | 001:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21082700043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 60 | 2021-08-27 | 360 | keep | 0 | Aug | 2021 | 0.00024519 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2021-08-27 12:56 | 2021-08-27 16:00 | 30 | 003:04 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | A21082700076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2021-08-27 | 5520 | keep | 0 | Aug | 2021 | 0.0037596 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-08-27 12:58 | 2021-08-27 20:20 | 30 | 007:22 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA POR DESGANCHE | A21082700077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 442 | 2021-08-27 | 13260 | keep | 0 | Aug | 2021 | 0.0090313 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-08-27 13:09 | 2021-08-27 13:11 | 2466 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S21082700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-27 | 4932 | keep | 0 | Aug | 2021 | 0.0033592 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
MAYAGÃœEZ | 2021-08-27 13:11 | 2021-08-27 17:00 | 50 | 003:49 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M21082700065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2021-08-27 | 11450 | keep | 0 | Aug | 2021 | 0.0077985 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-27 13:22 | 2021-08-27 21:24 | 1 | 008:02 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA POR DESGANCHE | A21082700082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 482 | 2021-08-27 | 482 | keep | 0 | Aug | 2021 | 0.00032829 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-08-27 13:30 | 2021-08-27 16:55 | 100 | 003:25 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZO DE POSTE Y REALIZAR DESGANCHE | B21082700052 | New_Event | Defective Pole | Include | Include | Equipment | 205 | 2021-08-27 | 20500 | keep | 0 | Aug | 2021 | 0.013962 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-08-27 13:40 | 2021-08-27 17:00 | 50 | 003:20 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | M21082700065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2021-08-27 | 10000 | keep | 0 | Aug | 2021 | 0.006811 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-08-27 13:45 | 2021-08-27 13:48 | 3387 | 000:03 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO Y SE CERRO POR CONTROL | B21082700055 | New_Event | Cutout Failure | Include | Include | Equipment | 3 | 2021-08-27 | 10161 | keep | 0 | Aug | 2021 | 0.0069206 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
VEGA BAJA | 2021-08-27 13:51 | 2021-08-27 15:42 | 10 | 001:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21082500042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 111 | 2021-08-27 | 1110 | keep | 0 | Aug | 2021 | 0.00075602 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-08-27 13:54 | 2021-08-27 13:55 | 1702 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | C21082700000 | New_Event |  |  | Include | Wildlife | 1 | 2021-08-27 | 1702 | keep | 0 | Aug | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2021-08-27 13:55 | 2021-08-27 17:44 | 1 | 003:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA Y 2 X 20 EN BANCO DE TRANSFORMADORES | C21082700066 | 1st_after_momentary |  |  | Include | Wildlife | 229 | 2021-08-27 | 229 | keep | 0 | Aug | 2021 | 0.00015597 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
VEGA BAJA | 2021-08-27 14:02 | 2021-08-27 16:04 | 3387 | 002:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B21082700059 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 122 | 2021-08-27 | 413214 | keep | 0 | Aug | 2021 | 0.28144 | 0.0023069 | Sustained | FALSE | FALSE | Not_TMED_Event | 3387
FAJARDO | 2021-08-27 14:21 | 2021-08-27 16:30 | 30 | 002:09 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO AVERIADO | R21082700050 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 129 | 2021-08-27 | 3870 | keep | 0 | Aug | 2021 | 0.0026358 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
FAJARDO | 2021-08-27 14:37 | 2021-08-27 16:25 | 40 | 001:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE CORTE DE LINEA | R21082700063 | New_Event | Wire Down | Include | Include | Equipment | 108 | 2021-08-27 | 4320 | keep | 0 | Aug | 2021 | 0.0029423 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-08-27 14:40 | 2021-08-27 16:51 | 100 | 002:11 | P | SOBRECARGA | SE ABRE CORTE DE LINEA PARA BALANCEAR CARGAS | P21082700082 | New_Event | Trip Due To Overload | Include | Include | Other | 131 | 2021-08-27 | 13100 | keep | 0 | Aug | 2021 | 0.0089224 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-08-27 14:42 | 2021-08-27 16:53 | 300 | 002:11 | P | DESGANCHE | 2 X 100 Y 2 X 80 EN CORTES DE LINEA | C21082700064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2021-08-27 | 39300 | keep | 0 | Aug | 2021 | 0.026767 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
CAGUAS | 2021-08-27 15:08 | 2021-08-27 20:29 | 1 | 005:21 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | C21082700067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 321 | 2021-08-27 | 321 | keep | 0 | Aug | 2021 | 0.00021863 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-08-27 15:35 | 2021-08-27 17:04 | 40 | 001:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C21082700068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2021-08-27 | 3560 | keep | 0 | Aug | 2021 | 0.0024247 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-08-27 15:35 | 2021-08-27 17:12 | 1400 | 001:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE RISER PARA CERRAR PUENTE PRIMARIO. | P21082700063 | New_Event | Wire Down | Include | Include | Equipment | 97 | 2021-08-27 | 135800 | keep | 0 | Aug | 2021 | 0.092493 | 0.00095353 | Sustained | FALSE | FALSE | Not_TMED_Event | 1400
HUMACAO | 2021-08-27 15:42 | 2021-08-27 17:16 | 40 | 001:34 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C21082700070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 94 | 2021-08-27 | 3760 | keep | 0 | Aug | 2021 | 0.0025609 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-08-27 16:08 | 2021-08-27 18:10 | 7 | 002:02 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA X 37.5 KVA | C21082700072 | New_Event | Service Transformer Failure | Include | Include | Equipment | 122 | 2021-08-27 | 854 | keep | 0 | Aug | 2021 | 0.00058166 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2021-08-27 16:22 | 2021-08-27 16:23 | 2354 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21082700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-27 | 2354 | keep | 0 | Aug | 2021 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
MAYAGÃœEZ | 2021-08-27 16:27 | 2021-08-27 19:30 | 100 | 003:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA | M21082700092 | New_Event | Cutout Failure | Include | Include | Equipment | 183 | 2021-08-27 | 18300 | keep | 0 | Aug | 2021 | 0.012464 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2021-08-27 16:43 | 2021-08-27 19:59 | 4 | 003:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO BANCO DE TRANSFORMADOR PARA QUE PERITO REPARARA NEUTRAL PARTIDO | S21082700057 | New_Event | Secondary Wire Down | Include | Include | Equipment | 196 | 2021-08-27 | 784 | keep | 0 | Aug | 2021 | 0.00053398 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-08-27 16:58 | 2021-08-27 21:17 | 60 | 004:19 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21082700077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2021-08-27 | 15540 | keep | 0 | Aug | 2021 | 0.010584 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BARRANQUITAS | 2021-08-27 18:07 | 2021-08-27 18:08 | 1364 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21082700081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-27 | 1364 | keep | 0 | Aug | 2021 | 0.00092901 | 0.00092901 | Momentary | FALSE | FALSE | Not_TMED_Event | 1364
ARECIBO | 2021-08-27 18:22 | 2021-08-27 20:04 | 8 | 001:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES SECUNDARIAS | A21082700099 | New_Event | Secondary Wire Down | Include | Include | Equipment | 102 | 2021-08-27 | 816 | keep | 0 | Aug | 2021 | 0.00055577 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-08-27 19:10 | 2021-08-27 19:11 | 3701 | 000:01 | T | DESGANCHE | RECIERRE | C21082700087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-27 | 3701 | keep | 0 | Aug | 2021 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
HUMACAO | 2021-08-27 19:21 | 2021-08-27 19:22 | 3701 | 000:01 | T | DESGANCHE | RECIERRE | C21082700089 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-27 | 3701 | keep | 0 | Aug | 2021 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
PONCE | 2021-08-27 19:26 | 2021-08-28 12:50 | 35 | 017:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RETEZO LINEA PRIMARIA 1 X 40 EN CORTE DE LINEA | P21082700095 | New_Event | Wire Down | Include | Include | Equipment | 1044 | 2021-08-27 | 36540 | keep | 0 | Aug | 2021 | 0.024887 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
HUMACAO | 2021-08-27 19:32 | 2021-08-27 19:33 | 3701 | 000:01 | T | DESGANCHE | RECIERRE | C21082700091 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-27 | 3701 | keep | 0 | Aug | 2021 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
MAYAGÃœEZ | 2021-08-27 19:35 | 2021-08-28 08:45 | 100 | 013:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | M21082700112 | New_Event | Bad Weather | Include | Include | Weather | 790 | 2021-08-27 | 79000 | keep | 0 | Aug | 2021 | 0.053807 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
HUMACAO | 2021-08-27 19:50 | 2021-08-27 19:51 | 3701 | 000:01 | T | DESGANCHE | RECIERRE | C21082700094 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-27 | 3701 | keep | 0 | Aug | 2021 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
PONCE | 2021-08-27 20:06 | 2021-08-28 10:40 | 241 | 014:34 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA AUTO IMPACTO POSTE | P21082700097 | New_Event |  |  | Include | Wildlife | 874 | 2021-08-27 | 210634 | keep | 0 | Aug | 2021 | 0.14346 | 0.00016414 | Sustained | FALSE | TRUE | Not_TMED_Event | 241
BAYAMON | 2021-08-27 20:16 | 2021-08-28 13:10 | 40 | 016:54 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | B21082700100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1014 | 2021-08-27 | 40560 | keep | 0 | Aug | 2021 | 0.027625 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
YAUCO | 2021-08-27 20:30 | 2021-08-28 09:15 | 55 | 012:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA REMPLAZO CAJA | P21082700110 | New_Event | Cutout Failure | Include | Include | Equipment | 765 | 2021-08-27 | 42075 | keep | 0 | Aug | 2021 | 0.028657 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
HUMACAO | 2021-08-27 20:35 | 2021-08-27 22:58 | 3701 | 002:23 | T | DESGANCHE | DESGANCHO EN CONVERTIDOR | C21082700101 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 143 | 2021-08-27 | 529243 | keep | 0 | Aug | 2021 | 0.36046 | 0.0025207 | Sustained | FALSE | FALSE | Not_TMED_Event | 3701
SAN JUAN | 2021-08-27 21:12 | 2021-08-27 21:27 | 10211 | 000:15 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE CARGA POR EL 1206-03 | S21082700108 | New_Event | Switch Failure | Include | Include | Equipment | 15 | 2021-08-27 | 153165 | keep | 0 | Aug | 2021 | 0.10432 | 0.0069547 | Sustained | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2021-08-27 21:12 | 2021-08-27 21:27 | 4133 | 000:15 | T | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE LLEVA 1204-05 | S21082700108 | New_Event | Switch Failure | Include | Include | Equipment | 15 | 2021-08-27 | 61995 | keep | 0 | Aug | 2021 | 0.042225 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
PONCE | 2021-08-27 21:46 | 2021-08-28 11:19 | 10 | 013:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE RECONECTO BAJANTE EN TRANSFORMADOR | P21082600164 | New_Event | Wire Down | Include | Include | Equipment | 813 | 2021-08-27 | 8130 | keep | 0 | Aug | 2021 | 0.0055373 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2021-08-27 22:30 | 2021-08-28 13:00 | 820 | 014:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CONEXIONES QUEMADAS EN MACHETE | P21082800038 | New_Event | Wire Down | Include | Include | Equipment | 870 | 2021-08-27 | 713400 | keep | 0 | Aug | 2021 | 0.48589 | 0.0005585 | Sustained | FALSE | FALSE | Not_TMED_Event | 820
HUMACAO | 2021-08-27 23:10 | 2021-08-27 23:11 | 3701 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21082700113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-27 | 3701 | keep | 0 | Aug | 2021 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
UTUADO | 2021-08-28 00:14 | 2021-08-28 17:40 | 80 | 017:26 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A21082800001 | New_Event | Wire Down | Include | Include | Equipment | 1046 | 2021-08-28 | 83680 | keep | 0 | Aug | 2021 | 0.056994 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-08-28 00:47 | 2021-08-28 10:49 | 65 | 010:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO ARBOL DE LA LINEA Y SE REEMPLAZO CAJA PRIMARIA | C21082800002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 602 | 2021-08-28 | 39130 | keep | 0 | Aug | 2021 | 0.026651 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BAYAMON | 2021-08-28 01:01 | 2021-08-28 01:02 | 5252 | 000:01 | T | ESTRUCTURA AVERIADA | RECIERRE DE INTERRUPTOR | B21082800000 | New_Event | Defective Pole | Include | Include | Equipment | 1 | 2021-08-28 | 5252 | keep | 0 | Aug | 2021 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
BAYAMON | 2021-08-28 01:26 | 2021-08-28 09:20 | 60 | 007:54 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21082800001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 474 | 2021-08-28 | 28440 | keep | 0 | Aug | 2021 | 0.01937 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CANOVANAS | 2021-08-28 03:00 | 2021-08-28 08:44 | 50 | 005:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA SE RETIRO AVE MUERTA | R21082800002 | New_Event |  |  | Include | Wildlife | 344 | 2021-08-28 | 17200 | keep | 0 | Aug | 2021 | 0.011715 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-08-28 03:08 | 2021-08-28 08:53 | 1 | 005:45 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN BANCO DE TRANSFORMADORES CRUCE CON AVE | R21082800003 | New_Event |  |  | Include | Wildlife | 345 | 2021-08-28 | 345 | keep | 0 | Aug | 2021 | 0.00023498 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-08-28 03:33 | 2021-08-28 11:00 | 50 | 007:27 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMA | A21082800002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 447 | 2021-08-28 | 22350 | keep | 0 | Aug | 2021 | 0.015222 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-28 05:12 | 2021-08-28 05:13 | 1834 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21082800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-28 | 1834 | keep | 0 | Aug | 2021 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
ARECIBO | 2021-08-28 05:30 | 2021-08-28 11:29 | 5 | 005:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARARON CONEXIONES | A21082800002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 359 | 2021-08-28 | 1795 | keep | 0 | Aug | 2021 | 0.0012226 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-08-28 06:36 | 2021-08-28 06:37 | 5809 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO | B21082800000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-08-28 | 5809 | keep | 0 | Aug | 2021 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
BAYAMON | 2021-08-28 06:37 | 2021-08-28 12:36 | 75 | 005:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN CORTE DE LINEA SE REPARO CAJA | B21082700097 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 359 | 2021-08-28 | 26925 | keep | 0 | Aug | 2021 | 0.018338 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
SAN JUAN | 2021-08-28 06:40 | 2021-08-28 06:41 | 2782 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO CON R/R ON SE PROBO CON R/R OFF QUEDO EN SERVICIO | S21082800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-28 | 2782 | keep | 0 | Aug | 2021 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
ARECIBO | 2021-08-28 06:43 | 2021-08-28 08:32 | 1 | 001:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA POR PALOMA | A21082800004 | New_Event |  |  | Include | Wildlife | 109 | 2021-08-28 | 109 | keep | 0 | Aug | 2021 | 7.4239e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-08-28 07:05 | 2021-08-28 07:06 | 5252 | 000:01 | T | ESTRUCTURA AVERIADA | RECERRO | B21082800000 | New_Event | Defective Pole | Include | Include | Equipment | 1 | 2021-08-28 | 5252 | keep | 0 | Aug | 2021 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
BAYAMON | 2021-08-28 07:06 | 2021-08-28 21:08 | 60 | 014:02 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO | B21082800003 | 1st_after_momentary | Defective Pole | Include | Include | Equipment | 842 | 2021-08-28 | 50520 | keep | 0 | Aug | 2021 | 0.034409 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2021-08-28 07:32 | 2021-08-28 17:47 | 23 | 010:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE REEMPLAZO AISLADOR PARTIDO Y CAJA PRIMARIA | C21082800006 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 615 | 2021-08-28 | 14145 | keep | 0 | Aug | 2021 | 0.0096341 | 1.5665e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 23
FAJARDO | 2021-08-28 07:43 | 2021-08-28 10:17 | 10 | 002:34 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE DESGANCHO | R21082800005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2021-08-28 | 1540 | keep | 0 | Aug | 2021 | 0.0010489 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BAYAMON | 2021-08-28 07:44 | 2021-08-28 16:17 | 20 | 008:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO EN LINEA PRIMARIA | B21082800017 | New_Event | Wire Down | Include | Include | Equipment | 513 | 2021-08-28 | 10260 | keep | 0 | Aug | 2021 | 0.006988 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-08-28 07:54 | 2021-08-28 07:56 | 6200 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL VERIFICADO CON COD CAROLINA LLEVA CARGA 1620-1 QUEDO EN SERVICIO LLEVA CARGA 85% 1336-10 Y 90% 1336-7 | S21082800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-28 | 12400 | keep | 0 | Aug | 2021 | 0.0084456 | 0.0042228 | Momentary | FALSE | FALSE | Not_TMED_Event | 6200
SAN JUAN | 2021-08-28 07:54 | 2021-08-28 07:56 | 350 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL VERIFICADO CON COD CAROLINA LLEVA CARGA 1620-1 QUEDO EN SERVICIO LLEVA CARGA 85% 1336-10 Y 90% 1336-7 | S21082800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-28 | 700 | keep | 0 | Aug | 2021 | 0.00047677 | 0.00023838 | Momentary | FALSE | FALSE | Not_TMED_Event | 350
SAN JUAN | 2021-08-28 07:54 | 2021-08-28 07:56 | 36 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL VERIFICADO CON COD CAROLINA LLEVA CARGA 1620-1 QUEDO EN SERVICIO LLEVA 85% 1336-10 Y 90% 1336-7 | S21082800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-28 | 72 | keep | 0 | Aug | 2021 | 4.9039e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-08-28 07:54 | 2021-08-28 07:56 | 172 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL VERIFICADO CON COD CAROLINA LLEVA CARGA 1620-1 QUEDO EN SERVICIO LLEVA 85% DEL 1336-10 Y 90% 1336-7 | S21082800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-28 | 344 | keep | 0 | Aug | 2021 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2021-08-28 08:04 | 2021-08-28 09:53 | 100 | 001:49 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE DESGANCHO | R21082800009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2021-08-28 | 10900 | keep | 0 | Aug | 2021 | 0.0074239 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-08-28 08:09 | 2021-08-28 10:40 | 70 | 002:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA AVE | M21082800006 | New_Event |  |  | Include | Wildlife | 151 | 2021-08-28 | 10570 | keep | 0 | Aug | 2021 | 0.0071992 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
SAN JUAN | 2021-08-28 09:15 | 2021-08-28 10:16 | 8 | 001:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR CONECTOR SECUNDARIO | S21082700071 | New_Event | Secondary Wire Down | Include | Include | Equipment | 61 | 2021-08-28 | 488 | keep | 0 | Aug | 2021 | 0.00033237 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-08-28 09:17 | 2021-08-28 10:22 | 7 | 001:05 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C21082800010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 65 | 2021-08-28 | 455 | keep | 0 | Aug | 2021 | 0.0003099 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-08-28 09:29 | 2021-08-28 09:31 | 393 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON EL RECIERRE EN OFF SE VERIFICO PERSONAL FUERA DE LAS LINEAS Y SE CERRO EL INTERRUPTOR | M21082800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-28 | 786 | keep | 0 | Aug | 2021 | 0.00053534 | 0.00026767 | Momentary | FALSE | TRUE | Not_TMED_Event | 393
MAYAGÃœEZ | 2021-08-28 09:29 | 2021-08-28 09:31 | 4 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 6007-04 CON EL RECIERRE EN OFF SE VERIFICO PERSONAL FUERA DE LAS LINEAS Y SE CERRO EL INTERRUPTOR ESTA LLEVANDO LA CARGA DEL 6007-05 | M21082800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-28 | 8 | keep | 0 | Aug | 2021 | 5.4488e-06 | 2.7244e-06 | Momentary | FALSE | TRUE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-08-28 09:38 | 2021-08-28 09:48 | 393 | 000:10 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON EL RECIERRE EN OFF SE VERIFICO PERSONAL FUERA DE LAS LINEAS Y SE CERRO EL INTERRUPTOR | M21082800000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 10 | 2021-08-28 | 3930 | keep | 0 | Aug | 2021 | 0.0026767 | 0.00026767 | Sustained | FALSE | TRUE | Not_TMED_Event | 393
MAYAGÃœEZ | 2021-08-28 09:38 | 2021-08-28 09:48 | 4 | 000:10 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 6007-04 CON EL RECIERRE EN OFF SE VERIFICO PERSONAL FUERA DE LAS LINEAS Y SE CERRO EL INTERRUPTOR ESTA LLEVANDO LA CARGA DEL 6007-05 | M21082800000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 10 | 2021-08-28 | 40 | keep | 0 | Aug | 2021 | 2.7244e-05 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-08-28 10:05 | 2021-08-29 13:19 | 10 | 027:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA FIJAR LINEA PRIMARIA ZAFADA | M21082800013 | New_Event | Wire Down | Include | Include | Equipment | 1634 | 2021-08-28 | 16340 | keep | 0 | Aug | 2021 | 0.011129 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-08-28 10:05 | 2021-08-28 15:15 | 6 | 005:10 | P | ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR Y SE INSTALO EN POSTE NUEVO POR POSTE EN MALAS CONDICIONES | A21082800015 | New_Event | Defective Pole | Include | Include | Equipment | 310 | 2021-08-28 | 1860 | keep | 0 | Aug | 2021 | 0.0012668 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-08-28 10:26 | 2021-08-28 14:09 | 25 | 003:43 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21082800016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 223 | 2021-08-28 | 5575 | keep | 0 | Aug | 2021 | 0.0037971 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CAGUAS | 2021-08-28 10:31 | 2021-08-28 13:13 | 7 | 002:42 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR DESGANCHARON SECUNDARIA, REPARARON Y SUBIERON TAP DEL 3 AL 5 SE DEJO EN 125 VOLTIOS POR FASE | C21082600094 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 162 | 2021-08-28 | 1134 | keep | 0 | Aug | 2021 | 0.00077236 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2021-08-28 10:55 | 2021-08-28 15:00 | 1 | 004:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN RISER MAL TIEMPO | M21082800019 | New_Event | Bad Weather | Include | Include | Weather | 245 | 2021-08-28 | 245 | keep | 0 | Aug | 2021 | 0.00016687 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-08-28 10:56 | 2021-08-28 14:30 | 80 | 003:34 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A21082800017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 214 | 2021-08-28 | 17120 | keep | 0 | Aug | 2021 | 0.01166 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-28 11:00 | 2021-08-28 11:52 | 12 | 000:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE MONTURA PARA REPARAR SECUNDARIA | S21082800015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 52 | 2021-08-28 | 624 | keep | 0 | Aug | 2021 | 0.000425 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2021-08-28 11:22 | 2021-08-28 19:44 | 15 | 008:22 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO Y 2 SECUNDARIOS | B21082100029 | New_Event | Defective Pole | Include | Include | Equipment | 502 | 2021-08-28 | 7530 | keep | 0 | Aug | 2021 | 0.0051286 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-08-28 11:40 | 2021-08-28 15:44 | 20 | 004:04 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | M21082800023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 244 | 2021-08-28 | 4880 | keep | 0 | Aug | 2021 | 0.0033237 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-08-28 11:59 | 2021-08-28 13:28 | 15 | 001:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE | S21082800022 | New_Event | Cutout Failure | Include | Include | Equipment | 89 | 2021-08-28 | 1335 | keep | 0 | Aug | 2021 | 0.00090926 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-08-28 12:10 | 2021-08-28 16:40 | 136 | 004:30 | P | DESGANCHE | 1 X 100, 1 X 80 Y 1 X 65 EN CORTES DE LINEA SE DESGANCHO E INSTALARON TIGUERO | C21082800023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 270 | 2021-08-28 | 36720 | keep | 0 | Aug | 2021 | 0.02501 | 9.2629e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 136
SAN JUAN | 2021-08-28 12:11 | 2021-08-28 14:51 | 100 | 002:40 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 100 EN CORTE DE LINEA GLOBO | S21082800024 | New_Event |  |  | Include | Wildlife | 160 | 2021-08-28 | 16000 | keep | 0 | Aug | 2021 | 0.010898 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
PONCE | 2021-08-28 12:15 | 2021-08-28 12:16 | 3718 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | P210828000XX | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-08-28 | 3718 | keep | 0 | Aug | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
PONCE | 2021-08-28 12:16 | 2021-08-28 14:35 | 5 | 002:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | P21082800048 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 139 | 2021-08-28 | 695 | keep | 0 | Aug | 2021 | 0.00047336 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2021-08-28 12:18 | 2021-08-28 21:10 | 8 | 008:52 | P | NO SE REPORTO CAUSA | CERRO CAJA DE TRANSFORMADOR | R21082800024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 532 | 2021-08-28 | 4256 | keep | 0 | Aug | 2021 | 0.0028987 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2021-08-28 12:20 | 2021-08-28 14:22 | 7 | 002:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | R21082800025 | New_Event |  |  | Include | Wildlife | 122 | 2021-08-28 | 854 | keep | 0 | Aug | 2021 | 0.00058166 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2021-08-28 12:29 | 2021-08-28 12:30 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21082800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-28 | 1352 | keep | 0 | Aug | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2021-08-28 12:29 | 2021-08-28 12:30 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6012-05 QUE ESTE LLEVANDO LA CARGA DEL 6014-03 | M21082800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-28 | 871 | keep | 0 | Aug | 2021 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2021-08-28 12:54 | 2021-08-28 12:55 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21082800000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-28 | 1352 | keep | 0 | Aug | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2021-08-28 12:54 | 2021-08-28 12:55 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6012-05 QUE ESTA LLEVANDO LA CARGA DEL 6014-03 | M21082800000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-28 | 871 | keep | 0 | Aug | 2021 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2021-08-28 13:11 | 2021-08-28 13:12 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21082800000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-28 | 1352 | keep | 0 | Aug | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2021-08-28 13:11 | 2021-08-28 13:12 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6012-05 QUE LLEVA LA CARGA DEL 6014-03 | M21082800000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-28 | 871 | keep | 0 | Aug | 2021 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2021-08-28 13:11 | 2021-08-28 17:05 | 35 | 003:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE FIJO LINEA DESPRENDIDA DEL AISLADOR | M21082800028 | New_Event | Wire Down | Include | Include | Equipment | 234 | 2021-08-28 | 8190 | keep | 0 | Aug | 2021 | 0.0055782 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
AGUADILLA | 2021-08-28 13:19 | 2021-08-28 13:20 | 569 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | M21082800032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-28 | 569 | keep | 0 | Aug | 2021 | 0.00038754 | 0.00038754 | Momentary | FALSE | FALSE | Not_TMED_Event | 569
MAYAGÃœEZ | 2021-08-28 13:21 | 2021-08-28 13:22 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21082800000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-28 | 1352 | keep | 0 | Aug | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2021-08-28 13:21 | 2021-08-28 13:22 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6012-05 QUE LLEVA LA CARGA DEL 6014-03 | M21082800000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-28 | 871 | keep | 0 | Aug | 2021 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
CAGUAS | 2021-08-28 13:24 | 2021-08-28 18:13 | 43 | 004:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C21082800046 | New_Event | Cutout Failure | Include | Include | Equipment | 289 | 2021-08-28 | 12427 | keep | 0 | Aug | 2021 | 0.008464 | 2.9287e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 43
PONCE | 2021-08-28 13:25 | 2021-08-28 14:00 | 12 | 000:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P21082800016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 35 | 2021-08-28 | 420 | keep | 0 | Aug | 2021 | 0.00028606 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
BAYAMON | 2021-08-28 13:40 | 2021-08-28 18:52 | 15 | 005:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA SE LEVANTO ALAMBRE PRIMARIO QUE VECINOS CRUZARON AL CORTAR ARBOL Y CAYO EN LAS LINEAS | B21082800048 | New_Event |  |  | Include | Wildlife | 312 | 2021-08-28 | 4680 | keep | 0 | Aug | 2021 | 0.0031875 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
ARECIBO | 2021-08-28 13:50 | 2021-08-28 17:20 | 9 | 003:30 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21082800024 | New_Event | Secondary Wire Down | Include | Include | Equipment | 210 | 2021-08-28 | 1890 | keep | 0 | Aug | 2021 | 0.0012873 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-08-28 13:55 | 2021-08-28 14:02 | 12 | 000:07 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 2 X 10 EN TRANSFORMADOR SE REMPLAZO 45 PIES DE LINEA SECUNDARIA | B21082800050 | New_Event | Secondary Wire Down | Include | Include | Equipment | 7 | 2021-08-28 | 84 | keep | 0 | Aug | 2021 | 5.7212e-05 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-08-28 14:04 | 2021-08-28 19:40 | 70 | 005:36 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA POR DESGANCHE | M21082800040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 336 | 2021-08-28 | 23520 | keep | 0 | Aug | 2021 | 0.016019 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BAYAMON | 2021-08-28 14:08 | 2021-08-28 14:22 | 20 | 000:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21082800019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 14 | 2021-08-28 | 280 | keep | 0 | Aug | 2021 | 0.00019071 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-08-28 14:13 | 2021-08-28 17:01 | 15 | 002:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO AVERIADO | C21082800042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 168 | 2021-08-28 | 2520 | keep | 0 | Aug | 2021 | 0.0017164 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-08-28 14:26 | 2021-08-28 16:20 | 380 | 001:54 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA PALOMA CRUZO FASE | P2108280057 | New_Event |  |  | Include | Wildlife | 114 | 2021-08-28 | 43320 | keep | 0 | Aug | 2021 | 0.029505 | 0.00025882 | Sustained | FALSE | TRUE | Not_TMED_Event | 380
AGUADILLA | 2021-08-28 14:26 | 2021-08-28 22:00 | 1 | 007:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO TREE WUIRE ZAFADO DE CAJA PRIMARIA | M21052800041 | New_Event | Wire Down | Include | Include | Equipment | 454 | 2021-08-28 | 454 | keep | 0 | Aug | 2021 | 0.00030922 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2021-08-28 14:40 | 2021-08-28 14:42 | 3387 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | B21082800053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-08-28 | 6774 | keep | 0 | Aug | 2021 | 0.0046137 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
MAYAGÃœEZ | 2021-08-28 14:45 | 2021-08-28 14:46 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21082800000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-28 | 1352 | keep | 0 | Aug | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2021-08-28 14:45 | 2021-08-28 14:46 | 871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21082800000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-28 | 871 | keep | 0 | Aug | 2021 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
BAYAMON | 2021-08-28 14:48 | 2021-08-28 15:36 | 20 | 000:48 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21082800054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 48 | 2021-08-28 | 960 | keep | 0 | Aug | 2021 | 0.00065385 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-08-28 14:53 | 2021-08-28 17:10 | 50 | 002:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO BAJANTE ZAFADO | A21082800027 | New_Event | Wire Down | Include | Include | Equipment | 137 | 2021-08-28 | 6850 | keep | 0 | Aug | 2021 | 0.0046655 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-08-28 14:59 | 2021-08-28 16:51 | 274 | 001:52 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA MAL TIEMPO | P21082800062 | New_Event | Bad Weather | Include | Include | Weather | 112 | 2021-08-28 | 30688 | keep | 0 | Aug | 2021 | 0.020901 | 0.00018662 | Sustained | FALSE | TRUE | Not_TMED_Event | 274
BAYAMON | 2021-08-28 15:15 | 2021-08-29 12:58 | 15 | 021:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZO 300 PIES DE SECUNDARIA | B21082800063 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1303 | 2021-08-28 | 19545 | keep | 0 | Aug | 2021 | 0.013312 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-08-28 15:18 | 2021-08-29 09:56 | 100 | 018:38 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | M21082800046 | New_Event | Bad Weather | Include | Include | Weather | 1118 | 2021-08-28 | 111800 | keep | 0 | Aug | 2021 | 0.076146 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-08-28 15:25 | 2021-08-28 15:26 | 281 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21082800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-28 | 281 | keep | 0 | Aug | 2021 | 0.00019139 | 0.00019139 | Momentary | FALSE | TRUE | Not_TMED_Event | 281
MAYAGÃœEZ | 2021-08-28 15:25 | 2021-08-28 15:26 | 1252 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21082800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-28 | 1252 | keep | 0 | Aug | 2021 | 0.00085273 | 0.00085273 | Momentary | FALSE | TRUE | Not_TMED_Event | 1252
MAYAGÃœEZ | 2021-08-28 15:25 | 2021-08-28 15:26 | 595 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21082800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-28 | 595 | keep | 0 | Aug | 2021 | 0.00040525 | 0.00040525 | Momentary | FALSE | TRUE | Not_TMED_Event | 595
MAYAGÃœEZ | 2021-08-28 15:25 | 2021-08-28 15:26 | 51 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M20828000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-28 | 51 | keep | 0 | Aug | 2021 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 51
MAYAGÃœEZ | 2021-08-28 15:25 | 2021-08-28 15:26 | 721 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M21082800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-28 | 721 | keep | 0 | Aug | 2021 | 0.00049107 | 0.00049107 | Momentary | FALSE | TRUE | Not_TMED_Event | 721
UTUADO | 2021-08-28 15:25 | 2021-08-28 15:26 | 1382 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A21082800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-28 | 1382 | keep | 0 | Aug | 2021 | 0.00094127 | 0.00094127 | Momentary | FALSE | TRUE | Not_TMED_Event | 1382
UTUADO | 2021-08-28 15:25 | 2021-08-28 15:26 | 654 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A21082800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-08-28 | 654 | keep | 0 | Aug | 2021 | 0.00044544 | 0.00044544 | Momentary | FALSE | TRUE | Not_TMED_Event | 654
MAYAGÃœEZ | 2021-08-28 15:38 | 2021-08-28 19:58 | 30 | 004:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | M21082800054 | New_Event | Bad Weather | Include | Include | Weather | 260 | 2021-08-28 | 7800 | keep | 0 | Aug | 2021 | 0.0053125 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
VEGA BAJA | 2021-08-28 15:38 | 2021-09-04 12:46 | 5 | 165:08 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE LEVANTO SECUNDARIA | B21082800065 | New_Event | Secondary Wire Down | Include | Include | Equipment | 9908 | 2021-08-28 | 49540 | keep | 0 | Aug | 2021 | 0.033741 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2021-08-28 15:41 | 2021-08-29 11:49 | 20 | 020:08 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO DEL T-114 A T-115 | B21082800066 | New_Event | UG Cable Fault | Include | Include | Equipment | 1208 | 2021-08-28 | 24160 | keep | 0 | Aug | 2021 | 0.016455 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-08-28 15:41 | 2021-08-29 17:53 | 2 | 026:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21082800032 | New_Event | Bad Weather | Include | Include | Weather | 1572 | 2021-08-28 | 3144 | keep | 0 | Aug | 2021 | 0.0021414 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2021-08-28 15:51 | 2021-08-28 17:22 | 20 | 001:31 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO Y TAPEO TRANSFORMADOR Y SE REPARO NEUTRAL SECUNDARIO | S21082700062 | New_Event | Secondary Wire Down | Include | Include | Equipment | 91 | 2021-08-28 | 1820 | keep | 0 | Aug | 2021 | 0.0012396 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-08-28 15:54 | 2021-08-29 16:25 | 30 | 024:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21082800056 | New_Event | Bad Weather | Include | Include | Weather | 1471 | 2021-08-28 | 44130 | keep | 0 | Aug | 2021 | 0.030057 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
FAJARDO | 2021-08-28 16:07 | 2021-08-28 16:32 | 15 | 000:25 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R21082800031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 25 | 2021-08-28 | 375 | keep | 0 | Aug | 2021 | 0.00025541 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-08-28 16:15 | 2021-08-28 16:16 | 2402 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVANDO 1720-08 | B21082800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-28 | 2402 | keep | 0 | Aug | 2021 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2021-08-28 16:15 | 2021-08-28 16:16 | 1 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1709-02 LLEVANDO 1720-08 | B21082800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-28 | 1 | keep | 0 | Aug | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-08-28 16:26 | 2021-08-29 13:23 | 50 | 020:57 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 25 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M21082800059 | New_Event | Wire Down | Include | Include | Equipment | 1257 | 2021-08-28 | 62850 | keep | 0 | Aug | 2021 | 0.042807 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-08-28 16:31 | 2021-08-28 18:08 | 10 | 001:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REGO 200' DE SUCUNADARIA Y SE REPARO BAJANTE | C21082800053 | New_Event | Secondary Wire Down | Include | Include | Equipment | 97 | 2021-08-28 | 970 | keep | 0 | Aug | 2021 | 0.00066066 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-08-28 17:37 | 2021-08-28 17:38 | 3438 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21082800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-28 | 3438 | keep | 0 | Aug | 2021 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
BAYAMON | 2021-08-28 18:11 | 2021-08-29 12:52 | 20 | 018:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | B21082800081 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1121 | 2021-08-28 | 22420 | keep | 0 | Aug | 2021 | 0.01527 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-08-28 18:49 | 2021-08-29 19:01 | 1 | 024:12 | P | OTRAS CAUSAS | 1 X 40 EN CORTE DE LINEA PROBLEMA DE CLIENTE | M21082800062 | New_Event | Other Causes | Include | Include | Other | 1452 | 2021-08-28 | 1452 | keep | 0 | Aug | 2021 | 0.00098895 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-08-28 19:00 | 2021-08-28 19:01 | 2231 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | A21082800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-28 | 2231 | keep | 0 | Aug | 2021 | 0.0015195 | 0.0015195 | Momentary | FALSE | FALSE | Not_TMED_Event | 2231
ARECIBO | 2021-08-28 19:01 | 2021-08-28 21:20 | 200 | 002:19 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A21082800043 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 139 | 2021-08-28 | 27800 | keep | 0 | Aug | 2021 | 0.018934 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
YAUCO | 2021-08-28 19:14 | 2021-08-29 15:40 | 4 | 020:26 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE TRANSFORMADOR 50 KVA A 4160 VOLTS AVERIADO POR 50KVA | P21082800012 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1226 | 2021-08-28 | 4904 | keep | 0 | Aug | 2021 | 0.0033401 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-08-28 19:17 | 2021-08-29 08:51 | 15 | 013:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES ROTO | A21082800048 | New_Event | Cutout Failure | Include | Include | Equipment | 814 | 2021-08-28 | 12210 | keep | 0 | Aug | 2021 | 0.0083162 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
MAYAGÃœEZ | 2021-08-28 20:02 | 2021-08-29 09:39 | 150 | 013:37 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA DESGANCHE | M21082800067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 817 | 2021-08-28 | 122550 | keep | 0 | Aug | 2021 | 0.083468 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-08-28 20:03 | 2021-08-29 11:43 | 50 | 015:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO ZAFADO EN CORTE DE LINEA | A21082800054 | New_Event | Wire Down | Include | Include | Equipment | 940 | 2021-08-28 | 47000 | keep | 0 | Aug | 2021 | 0.032011 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
HUMACAO | 2021-08-28 20:12 | 2021-08-28 20:13 | 3701 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21082800083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-28 | 3701 | keep | 0 | Aug | 2021 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
CAGUAS | 2021-08-28 21:09 | 2021-08-29 09:22 | 7 | 012:13 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR | C21082800086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 733 | 2021-08-28 | 5131 | keep | 0 | Aug | 2021 | 0.0034947 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2021-08-28 21:19 | 2021-08-29 10:25 | 11 | 013:06 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR | C21082800088 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 786 | 2021-08-28 | 8646 | keep | 0 | Aug | 2021 | 0.0058888 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2021-08-28 21:27 | 2021-08-28 21:28 | 3597 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21082800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-28 | 3597 | keep | 0 | Aug | 2021 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
PONCE | 2021-08-28 21:33 | 2021-08-28 21:34 | 1650 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210828000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-28 | 1650 | keep | 0 | Aug | 2021 | 0.0011238 | 0.0011238 | Momentary | FALSE | FALSE | Not_TMED_Event | 1650
AGUADILLA | 2021-08-28 21:36 | 2021-08-29 14:00 | 200 | 016:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO ABIERTO | M21082900004 | New_Event | Wire Down | Include | Include | Equipment | 984 | 2021-08-28 | 196800 | keep | 0 | Aug | 2021 | 0.13404 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
HUMACAO | 2021-08-28 22:05 | 2021-08-28 22:06 | 4 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21082800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-28 | 4 | keep | 0 | Aug | 2021 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2021-08-28 23:55 | 2021-08-29 10:16 | 120 | 010:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN SALIDA DEL CONVERTIDOR REEMPLAZARON DOS CAJAS QUEMADAS EN LA SALIDA DEL CONVERTIDOR | C21082800091 | New_Event | Cutout Failure | Include | Include | Equipment | 621 | 2021-08-28 | 74520 | keep | 0 | Aug | 2021 | 0.050755 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2021-08-29 00:01 | 2021-08-29 16:39 | 30 | 016:38 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21082900001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 998 | 2021-08-29 | 29940 | keep | 0 | Aug | 2021 | 0.020392 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-08-29 02:09 | 2021-08-29 09:25 | 70 | 007:16 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA PARARRAYO AVERIADO | R21082900001 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 436 | 2021-08-29 | 30520 | keep | 0 | Aug | 2021 | 0.020787 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
CANOVANAS | 2021-08-29 02:36 | 2021-08-29 10:23 | 80 | 007:47 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE Y SE RETIRO IGUANA | R21082900003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 467 | 2021-08-29 | 37360 | keep | 0 | Aug | 2021 | 0.025446 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BARRANQUITAS | 2021-08-29 02:43 | 2021-08-29 02:44 | 2410 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21082900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-29 | 2410 | keep | 0 | Aug | 2021 | 0.0016414 | 0.0016414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2410
HUMACAO | 2021-08-29 03:18 | 2021-08-29 20:36 | 46 | 017:18 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | C21082900008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1038 | 2021-08-29 | 47748 | keep | 0 | Aug | 2021 | 0.032521 | 3.133e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 46
PONCE | 2021-08-29 05:25 | 2021-08-29 15:33 | 290 | 010:08 | P | DESGANCHE | 1 X 80 Y 1 X 100 EN CORTE DE LINEA | P21082900044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 608 | 2021-08-29 | 176320 | keep | 0 | Aug | 2021 | 0.12009 | 0.00019752 | Sustained | FALSE | TRUE | Not_TMED_Event | 290
GUAYAMA | 2021-08-29 05:34 | 2021-08-29 06:59 | 4279 | 001:25 | T | PARARRAYOS DEFECTUOSO | 2 PARARRAYOS AVERIADOS EN RISER | P21082900007 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 85 | 2021-08-29 | 363715 | keep | 0 | Aug | 2021 | 0.24772 | 0.0029144 | Sustained | FALSE | FALSE | Not_TMED_Event | 4279
ARECIBO | 2021-08-29 05:42 | 2021-08-29 05:43 | 1345 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERUPTOR NO SE REPORTO CAUSA | A21052900004 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-08-29 | 1345 | keep | 0 | Aug | 2021 | 0.00091607 | 0.00091607 | Momentary | FALSE | FALSE | Not_TMED_Event | 1345
ARECIBO | 2021-08-29 05:43 | 2021-08-29 10:08 | 200 | 004:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 200 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21082900010 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 265 | 2021-08-29 | 53000 | keep | 0 | Aug | 2021 | 0.036098 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-08-29 06:29 | 2021-08-29 06:30 | 4381 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON RECIERRE EN OFF | M21082900009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-29 | 4381 | keep | 0 | Aug | 2021 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
VEGA BAJA | 2021-08-29 06:48 | 2021-08-29 06:49 | 3000 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO | B21082900009 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-08-29 | 3000 | keep | 0 | Aug | 2021 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
VEGA BAJA | 2021-08-29 06:49 | 2021-08-29 10:58 | 60 | 004:09 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B21082900015 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 249 | 2021-08-29 | 14940 | keep | 0 | Aug | 2021 | 0.010176 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
GUAYAMA | 2021-08-29 06:59 | 2021-08-29 07:45 | 3200 | 000:46 | P | PARARRAYOS DEFECTUOSO | PARARRAYOS AVERIADOS EN RISER | P21082900011 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 46 | 2021-08-29 | 147200 | keep | 0 | Aug | 2021 | 0.10026 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-08-29 07:12 | 2021-08-29 10:38 | 30 | 003:26 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REPARO PIN POLE TOP ZAFADO | A21082900013 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 206 | 2021-08-29 | 6180 | keep | 0 | Aug | 2021 | 0.0042092 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-08-29 07:29 | 2021-08-29 09:41 | 60 | 002:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B21082900012 | New_Event | Cutout Failure | Include | Include | Equipment | 132 | 2021-08-29 | 7920 | keep | 0 | Aug | 2021 | 0.0053943 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-08-29 07:32 | 2021-08-29 18:15 | 84 | 010:43 | P | CABLE SOTERRADO AVERIADO | ENERIZO CABLE NUEVO DEL T - 27 AL T - 28 E HIZO TERMINACION EN EL T - 28 | C21082900016 | New_Event | UG Cable Fault | Include | Include | Equipment | 643 | 2021-08-29 | 54012 | keep | 0 | Aug | 2021 | 0.036787 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
GUAYAMA | 2021-08-29 07:45 | 2021-08-29 12:25 | 10 | 004:40 | P | PARARRAYOS DEFECTUOSO | PARARRAYOS AVERIADOS EN RISER | P21082900012 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 280 | 2021-08-29 | 2800 | keep | 0 | Aug | 2021 | 0.0019071 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-29 08:02 | 2021-08-29 08:03 | 320 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21082900017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-29 | 320 | keep | 0 | Aug | 2021 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
PONCE | 2021-08-29 08:12 | 2021-08-29 11:06 | 327 | 002:54 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 200 Y 1 X 50 EN CORTE DE LINEA | P21082900022 | New_Event | Wire Down | Include | Include | Equipment | 174 | 2021-08-29 | 56898 | keep | 0 | Aug | 2021 | 0.038753 | 0.00022272 | Sustained | FALSE | TRUE | Not_TMED_Event | 327
VEGA BAJA | 2021-08-29 08:25 | 2021-08-29 08:26 | 3387 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21082900021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-29 | 3387 | keep | 0 | Aug | 2021 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
VEGA BAJA | 2021-08-29 08:26 | 2021-08-29 11:44 | 30 | 003:18 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21082900028 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 198 | 2021-08-29 | 5940 | keep | 0 | Aug | 2021 | 0.0040457 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-08-29 08:31 | 2021-08-29 08:32 | 1265 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21082900018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-29 | 1265 | keep | 0 | Aug | 2021 | 0.00086159 | 0.00086159 | Momentary | FALSE | FALSE | Not_TMED_Event | 1265
ARECIBO | 2021-08-29 08:33 | 2021-08-29 16:00 | 75 | 007:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A21082900019 | New_Event | Cutout Failure | Include | Include | Equipment | 447 | 2021-08-29 | 33525 | keep | 0 | Aug | 2021 | 0.022834 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
AGUADILLA | 2021-08-29 08:55 | 2021-08-29 17:10 | 50 | 008:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M21082900017 | New_Event | Cutout Failure | Include | Include | Equipment | 495 | 2021-08-29 | 24750 | keep | 0 | Aug | 2021 | 0.016857 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-08-29 08:58 | 2021-08-29 13:01 | 1 | 004:03 | P | NO SE REPORTO CAUSA | 1 X 15 EN BANCO DE TRANSFORMADOR | C21082900024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 243 | 2021-08-29 | 243 | keep | 0 | Aug | 2021 | 0.00016551 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2021-08-29 09:36 | 2021-08-29 17:17 | 6 | 007:41 | P | OTRAS CAUSAS | SE DIO RESET A TRANSFORMADOR AUTO PROTEGIDO | P21082900031 | New_Event | Other Causes | Include | Include | Other | 461 | 2021-08-29 | 2766 | keep | 0 | Aug | 2021 | 0.0018839 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2021-08-29 09:43 | 2021-08-29 09:44 | 1478 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21082900034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-29 | 1478 | keep | 0 | Aug | 2021 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
SAN JUAN | 2021-08-29 09:46 | 2021-08-29 11:52 | 8 | 002:06 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO AVERIADO | R21082700080 | New_Event | Secondary Wire Down | Include | Include | Equipment | 126 | 2021-08-29 | 1008 | keep | 0 | Aug | 2021 | 0.00068654 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-08-29 10:08 | 2021-08-29 10:12 | 1345 | 000:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR CON EL RECIERRE EN OFF SE VERIFICO PERSONAL FUERA DE LAS LINEAS Y SE CERRO EL INTERRUPTOR | A21082900027 | New_Event | Wire Down | Include | Include | Equipment | 4 | 2021-08-29 | 5380 | keep | 0 | Aug | 2021 | 0.0036643 | 0.00091607 | Momentary | FALSE | TRUE | Not_TMED_Event | 1345
CAGUAS | 2021-08-29 10:11 | 2021-08-29 13:00 | 1 | 002:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | C21082900032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 169 | 2021-08-29 | 169 | keep | 0 | Aug | 2021 | 0.00011511 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-08-29 10:12 | 2021-08-29 11:10 | 750 | 000:58 | P | DESCONECTIVO DEFECTUOSO | SE ABRE INTERRUPTOR PARA ABRIR N/O 1206-4 Y 1204-3 URB. CONQUISTADOR PARA REEMPLAZAR MACHETE EN N/O 1204-3 Y 1204-3 CARR.175 EN ORNATO TRUJILLO LLEVA 40% 1204-4 60% 1204-3 Y 60AMP DEL 1303-2 | S21082900028 | New_Event | Switch Failure | Include | Include | Equipment | 58 | 2021-08-29 | 43500 | keep | 0 | Aug | 2021 | 0.029628 | 0.00051082 | Sustained | FALSE | FALSE | Not_TMED_Event | 750
SAN JUAN | 2021-08-29 10:12 | 2021-08-29 11:10 | 1976 | 000:58 | P | DESCONECTIVO DEFECTUOSO | SE ABRE INTERRUPTOR PARA ABRIR N/O 1206-4 Y 1204-3 URB. CONQUISTADOR PARA REEMPLAZAR MACHETE EN N/O 1204-3 Y 1204-3 CARR.175 EN ORNATO TRUJILLO LLEVA 40% 1204-4 60% 1204-3 Y 60AMP DEL 1303-2 | S21082900028 | New_Event | Switch Failure | Include | Include | Equipment | 58 | 2021-08-29 | 114608 | keep | 0 | Aug | 2021 | 0.078059 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
SAN JUAN | 2021-08-29 10:12 | 2021-08-29 10:42 | 1799 | 000:30 | T | DESCONECTIVO DEFECTUOSO | SE ABRE INTERRUPTOR PARA ABRIR N/O 1206-4 Y 1204-3 URB. CONQUISTADOR PARA REEMPLAZAR MACHETE EN N/O 1204-3 Y 1204-3 CARR.175 EN ORNATO TRUJILLO LLEVA 40% 1204-4 60% 1204-3 Y 60AMP DEL 1303-2 | S21082900038 | New_Event | Switch Failure | Include | Include | Equipment | 30 | 2021-08-29 | 53970 | keep | 0 | Aug | 2021 | 0.036759 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2021-08-29 10:12 | 2021-08-29 11:10 | 600 | 000:58 | P | DESCONECTIVO DEFECTUOSO | SE ABRE INTERRUPTOR PARA ABRIR N/O 1206-4 Y 1204-3 URB. CONQUISTADOR PARA REEMPLAZAR MACHETE EN N/O 1204-3 Y 1204-3 CARR.175 EN ORNATO TRUJILLO LLEVA 40% 1204-4 60% 1204-3 Y 60AMP DEL 1303-2 | S21082900028 | New_Event | Switch Failure | Include | Include | Equipment | 58 | 2021-08-29 | 34800 | keep | 0 | Aug | 2021 | 0.023702 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
ARECIBO | 2021-08-29 10:12 | 2021-08-29 10:36 | 200 | 000:24 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 200 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21082900010 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 24 | 2021-08-29 | 4800 | keep | 0 | Aug | 2021 | 0.0032693 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-08-29 10:40 | 2021-08-29 14:44 | 300 | 004:04 | P | DESGANCHE | 1 X 100 Y 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21082900032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 244 | 2021-08-29 | 73200 | keep | 0 | Aug | 2021 | 0.049856 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
ARECIBO | 2021-08-29 10:45 | 2021-08-29 11:46 | 50 | 001:01 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | A21082900029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2021-08-29 | 3050 | keep | 0 | Aug | 2021 | 0.0020773 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-29 11:13 | 2021-08-29 17:01 | 60 | 005:48 | P | DESGANCHE | 1 X 80 Y 1 X 40 EN CORTES DE LINEA | B21082900034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 348 | 2021-08-29 | 20880 | keep | 0 | Aug | 2021 | 0.014221 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-08-29 11:18 | 2021-08-29 19:05 | 130 | 007:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21082900052 | New_Event | Bad Weather | Include | Include | Weather | 467 | 2021-08-29 | 60710 | keep | 0 | Aug | 2021 | 0.041349 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
BAYAMON | 2021-08-29 11:35 | 2021-08-29 13:48 | 150 | 002:13 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 100 EN CORTE DE LINEA SE RETIRO GLOBO DE HULE DEL 4KV | B21082900037 | New_Event |  |  | Include | Wildlife | 133 | 2021-08-29 | 19950 | keep | 0 | Aug | 2021 | 0.013588 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-08-29 11:38 | 2021-08-29 14:57 | 20 | 003:19 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | A21082900032 | New_Event |  |  | Include | Wildlife | 199 | 2021-08-29 | 3980 | keep | 0 | Aug | 2021 | 0.0027108 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
BAYAMON | 2021-08-29 11:45 | 2021-08-29 15:00 | 60 | 003:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA PERSONA ESTABA DESGANCHANDO ARBOL | B21082900036 | New_Event |  |  | Include | Wildlife | 195 | 2021-08-29 | 11700 | keep | 0 | Aug | 2021 | 0.0079688 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-08-29 11:46 | 2021-08-29 12:33 | 100 | 000:47 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21082900050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 47 | 2021-08-29 | 4700 | keep | 0 | Aug | 2021 | 0.0032011 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-08-29 12:21 | 2021-08-29 12:22 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21082900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-29 | 308 | keep | 0 | Aug | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2021-08-29 13:00 | 2021-08-29 18:20 | 12 | 005:20 | P | NO SE REPORTO CAUSA | 1 X 30 EN TRANSFORMADOR | B21082900045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 320 | 2021-08-29 | 3840 | keep | 0 | Aug | 2021 | 0.0026154 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-08-29 13:05 | 2021-08-29 15:15 | 200 | 002:10 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBÃšES SOBRE LAS LINEAS | M21082900057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2021-08-29 | 26000 | keep | 0 | Aug | 2021 | 0.017708 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-08-29 13:22 | 2021-08-29 15:53 | 50 | 002:31 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO CAUSA | C21082900047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 151 | 2021-08-29 | 7550 | keep | 0 | Aug | 2021 | 0.0051423 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-29 13:36 | 2021-08-29 18:20 | 9 | 004:44 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21082900048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 284 | 2021-08-29 | 2556 | keep | 0 | Aug | 2021 | 0.0017409 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-08-29 15:02 | 2021-08-29 17:17 | 25 | 002:15 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR | B21082900059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 135 | 2021-08-29 | 3375 | keep | 0 | Aug | 2021 | 0.0022987 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-08-29 15:15 | 2021-08-29 17:14 | 8 | 001:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A21082900028 | New_Event | Secondary Wire Down | Include | Include | Equipment | 119 | 2021-08-29 | 952 | keep | 0 | Aug | 2021 | 0.0006484 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2021-08-29 15:51 | 2021-08-29 19:24 | 150 | 003:33 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | C21082900054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2021-08-29 | 31950 | keep | 0 | Aug | 2021 | 0.021761 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-08-29 16:03 | 2021-08-29 17:30 | 30 | 001:27 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE DE CORTE DE LINEA | A21082900038 | New_Event | Wire Down | Include | Include | Equipment | 87 | 2021-08-29 | 2610 | keep | 0 | Aug | 2021 | 0.0017777 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-08-29 16:18 | 2021-08-29 17:50 | 300 | 001:32 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M21082900078 | New_Event | Bad Weather | Include | Include | Weather | 92 | 2021-08-29 | 27600 | keep | 0 | Aug | 2021 | 0.018798 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
AGUADILLA | 2021-08-29 16:39 | 2021-08-30 12:20 | 10 | 019:41 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO NEUTRAL EN TRANSFORMADOR | M21082900080 | New_Event | Wire Down | Include | Include | Equipment | 1181 | 2021-08-29 | 11810 | keep | 0 | Aug | 2021 | 0.0080437 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-29 17:03 | 2021-08-29 19:20 | 20 | 002:17 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21082900041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2021-08-29 | 2740 | keep | 0 | Aug | 2021 | 0.0018662 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
HUMACAO | 2021-08-29 17:08 | 2021-08-29 19:39 | 40 | 002:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA QUEMADA | C21082900057 | New_Event | Cutout Failure | Include | Include | Equipment | 151 | 2021-08-29 | 6040 | keep | 0 | Aug | 2021 | 0.0041138 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-08-29 17:18 | 2021-08-30 15:12 | 2 | 021:54 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR PROBO MALO SE TRANSFIRIO LA CARGA A UN TRANSFORMADOR CERCANO | C21082900060 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1314 | 2021-08-29 | 2628 | keep | 0 | Aug | 2021 | 0.0017899 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2021-08-29 17:23 | 2021-08-29 17:24 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6007-05 | M21082900078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-29 | 393 | keep | 0 | Aug | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2021-08-29 17:23 | 2021-08-29 17:24 | 4 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR EL CUAL LLEVA LA CARGA DEL 6007-05 NO SE REPORTO CAUSA | M21082900078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-29 | 4 | keep | 0 | Aug | 2021 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2021-08-29 17:25 | 2021-08-29 18:01 | 8 | 000:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21082700089 | New_Event | Secondary Wire Down | Include | Include | Equipment | 36 | 2021-08-29 | 288 | keep | 0 | Aug | 2021 | 0.00019616 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-08-29 17:40 | 2021-08-29 20:05 | 15 | 002:25 | T | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21082900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2021-08-29 | 2175 | keep | 0 | Aug | 2021 | 0.0014814 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-08-29 18:09 | 2021-08-29 19:50 | 1715 | 001:41 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1707-01 | B21082900068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 101 | 2021-08-29 | 173215 | keep | 0 | Aug | 2021 | 0.11798 | 0.0011681 | Sustained | FALSE | FALSE | Not_TMED_Event | 1715
BARRANQUITAS | 2021-08-29 18:18 | 2021-08-29 23:32 | 2362 | 005:14 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | CERRO PUENTE | C21082900064 | New_Event | Wire Down | Include | Include | Equipment | 314 | 2021-08-29 | 741668 | keep | 0 | Aug | 2021 | 0.50515 | 0.0016087 | Sustained | FALSE | FALSE | Not_TMED_Event | 2362
FAJARDO | 2021-08-29 18:50 | 2021-08-30 13:41 | 55 | 018:51 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN RISER A SU-1 Y 1 X 25 EN SU-1. SECCIONALIZO TRAMO AVERIADO T-13 A T-14 CERRO N/O T-15 A T-14 Y DEJO ABIERTO T-13 A T-14 | R21082900078 | New_Event | UG Cable Fault | Include | Include | Equipment | 1131 | 2021-08-29 | 62205 | keep | 0 | Aug | 2021 | 0.042368 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
BAYAMON | 2021-08-29 19:09 | 2021-08-29 20:50 | 1935 | 001:41 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR LLEVA LA CARGA DE 1708-02 | B21082900068 | New_Event | Wire Down | Include | Include | Equipment | 101 | 2021-08-29 | 195435 | keep | 0 | Aug | 2021 | 0.13311 | 0.0013179 | Sustained | FALSE | FALSE | Not_TMED_Event | 1935
MAYAGÃœEZ | 2021-08-29 20:14 | 2021-08-30 11:32 | 1 | 015:18 | P | OTRAS CAUSAS | 1 X 40 EN CORTE DE LINEA PROBLEMA DE CLIENTE | M21082800062 | Partial_restoration | Other Causes | Include | Include | Other | 918 | 2021-08-29 | 918 | keep | 0 | Aug | 2021 | 0.00062525 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
HUMACAO | 2021-08-29 20:36 | 2021-08-29 21:57 | 676 | 001:21 | T | NO SE REPORTO CAUSA | DISPARO, NO SE PODIA CERRAR POR EL RELEVO DE CARGA | C21082900130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2021-08-29 | 54756 | keep | 0 | Aug | 2021 | 0.037294 | 0.00046042 | Sustained | FALSE | FALSE | Not_TMED_Event | 676
CANOVANAS | 2021-08-29 20:38 | 2021-08-30 12:11 | 18 | 015:33 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR QUEMADO DE 75KVA X 75KVA Y CAJA PRIMARIA DE TRANSFORMADOR | R21082900147 | New_Event | Service Transformer Failure | Include | Include | Equipment | 933 | 2021-08-29 | 16794 | keep | 0 | Aug | 2021 | 0.011438 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2021-08-29 20:53 | 2021-08-29 21:18 | 1935 | 000:25 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR LLEVA LA CARGA DEL 1708-02 SE REPARO PUENTE ABIERTO | B21082900000 | Partial_restoration | Wire Down | Include | Include | Equipment | 25 | 2021-08-29 | 48375 | keep | 0 | Aug | 2021 | 0.032948 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-29 20:59 | 2021-08-29 23:49 | 1715 | 002:50 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR CARGA POR EL 1707-01 SE REPARO PUENTE ABIERTO Y SE CERRO AMARRE | B21082900000 | New_Event | Wire Down | Include | Include | Equipment | 170 | 2021-08-29 | 291550 | keep | 0 | Aug | 2021 | 0.19857 | 0.0011681 | Sustained | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2021-08-29 21:25 | 2021-08-29 23:37 | 1935 | 002:12 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR LLEVA LA CARGA DEL 1708-02 SE REPARO PUENTE PRIMARIO ABIERTO SE ABRIO AMARRE Y SE CERRO INTERRUPTOR | B21082900000 | Partial_restoration | Wire Down | Include | Include | Equipment | 132 | 2021-08-29 | 255420 | keep | 0 | Aug | 2021 | 0.17397 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-29 22:08 | 2021-08-29 22:13 | 2658 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE IZO PRUEBA Y QUEDO EN SERVICIO | M21082900204 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-08-29 | 13290 | keep | 0 | Aug | 2021 | 0.0090518 | 0.0018104 | Momentary | FALSE | FALSE | Not_TMED_Event | 2658
BAYAMON | 2021-08-29 22:37 | 2021-08-30 06:46 | 28 | 008:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO | B21082900142 | New_Event | Wire Down | Include | Include | Equipment | 489 | 2021-08-29 | 13692 | keep | 0 | Aug | 2021 | 0.0093256 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
VEGA BAJA | 2021-08-29 22:55 | 2021-08-30 09:41 | 10 | 010:46 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFOMADOR | B21082900147 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 646 | 2021-08-29 | 6460 | keep | 0 | Aug | 2021 | 0.0043999 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-08-29 22:58 | 2021-08-29 22:59 | 4188 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21082900149 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-29 | 4188 | keep | 0 | Aug | 2021 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
BARRANQUITAS | 2021-08-29 23:06 | 2021-08-30 15:57 | 126 | 016:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C21082900166 | New_Event | Cutout Failure | Include | Include | Equipment | 1011 | 2021-08-29 | 127386 | keep | 0 | Aug | 2021 | 0.086762 | 8.5818e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 126
MAYAGÃœEZ | 2021-08-29 23:16 | 2021-08-30 12:40 | 60 | 013:24 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M21082900233 | New_Event | Vegetation Contact | Include | Include | Vegetation | 804 | 2021-08-29 | 48240 | keep | 0 | Aug | 2021 | 0.032856 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-08-29 23:23 | 2021-08-30 08:53 | 311 | 009:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN CORTE DE LINEA CRUCE POR AVE | C21082900167 | New_Event |  |  | Include | Wildlife | 570 | 2021-08-29 | 177270 | keep | 0 | Aug | 2021 | 0.12074 | 0.00021182 | Sustained | FALSE | TRUE | Not_TMED_Event | 311
PONCE | 2021-08-29 23:24 | 2021-08-30 13:18 | 100 | 013:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLASO CAJA PRIMARIA QUEMADA | P21082900112 | New_Event | Cutout Failure | Include | Include | Equipment | 834 | 2021-08-29 | 83400 | keep | 0 | Aug | 2021 | 0.056803 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BARRANQUITAS | 2021-08-29 23:32 | 2021-08-30 14:42 | 160 | 015:10 | P | AISLADOR ROTO, PARTIDO O SAFADO | 3 X 80 EN CORTE DE LINEA SE REEMPLAZO AISLADOR Y CERRARON NEUTRAL PRIMARIO | C21082900064 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 910 | 2021-08-29 | 145600 | keep | 0 | Aug | 2021 | 0.099167 | 0.00010898 | Sustained | FALSE | TRUE | Not_TMED_Event | 160
SAN JUAN | 2021-08-29 23:41 | 2021-08-29 23:42 | 922 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA. CARGA POR EL 1401-08 | S21082900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-29 | 922 | keep | 0 | Aug | 2021 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2021-08-29 23:41 | 2021-08-29 23:42 | 135 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA. LLEVA 1346-05 | S21082900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-29 | 135 | keep | 0 | Aug | 2021 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
CANOVANAS | 2021-08-29 23:52 | 2021-08-29 23:55 | 424 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | R21082900161 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-08-29 | 1272 | keep | 0 | Aug | 2021 | 0.00086635 | 0.00028878 | Momentary | FALSE | FALSE | Not_TMED_Event | 424
PONCE | 2021-08-30 00:48 | 2021-08-30 09:54 | 100 | 009:06 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | P2108300001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 546 | 2021-08-30 | 54600 | keep | 0 | Aug | 2021 | 0.037188 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-08-30 01:13 | 2021-08-30 22:46 | 20 | 021:33 | P | CABLE SOTERRADO AVERIADO | SE CONSTUYO PROVISIONAL AEREO DEL SU-1 HACIA EL T-19 | B21083000004 | New_Event | UG Cable Fault | Include | Include | Equipment | 1293 | 2021-08-30 | 25860 | keep | 0 | Aug | 2021 | 0.017613 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-08-30 01:31 | 2021-08-30 16:10 | 95 | 014:39 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 80 EN SU-15 SE REPARO TERMINACION EN AEREO PROVISIONAL | C21083000001 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 879 | 2021-08-30 | 83505 | keep | 0 | Aug | 2021 | 0.056875 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
CAGUAS | 2021-08-30 01:55 | 2021-08-30 14:50 | 3 | 012:55 | P | PARARRAYOS DEFECTUOSO | 2 X 65 EN CORTE DE LINEA SE REEMPLAZO PARARRAYOS | C21083000002 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 775 | 2021-08-30 | 2325 | keep | 0 | Aug | 2021 | 0.0015835 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
PONCE | 2021-08-30 01:56 | 2021-08-30 01:57 | 449 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P210830000XX | New_Event |  |  | Include | Wildlife | 1 | 2021-08-30 | 449 | keep | 0 | Aug | 2021 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
PONCE | 2021-08-30 01:57 | 2021-08-30 14:00 | 2 | 012:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 50 EN RISER RATON CRUZO FASE | P21083000004 | 1st_after_momentary |  |  | Include | Wildlife | 723 | 2021-08-30 | 1446 | keep | 0 | Aug | 2021 | 0.00098486 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2021-08-30 02:10 | 2021-08-30 02:11 | 1879 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO | C21083000003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-30 | 1879 | keep | 0 | Aug | 2021 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
AGUADILLA | 2021-08-30 02:22 | 2021-08-30 19:40 | 200 | 017:18 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21083000008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1038 | 2021-08-30 | 207600 | keep | 0 | Aug | 2021 | 0.1414 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-08-30 03:16 | 2021-08-30 03:58 | 250 | 000:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 200 EN CORTE DE LINEA SE SEPARO LINEAS CRUZADAS | M21083000013 | New_Event | Wire Down | Include | Include | Equipment | 42 | 2021-08-30 | 10500 | keep | 0 | Aug | 2021 | 0.0071515 | 0.00017027 | Sustained | FALSE | TRUE | Not_TMED_Event | 250
HUMACAO | 2021-08-30 03:30 | 2021-08-30 07:13 | 1467 | 003:43 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO INTERRUPTOR SE LEVANTO CONDUCTOR PRIMARIO | C21083000006 | New_Event | Wire Down | Include | Include | Equipment | 223 | 2021-08-30 | 327141 | keep | 0 | Aug | 2021 | 0.22281 | 0.00099917 | Sustained | FALSE | FALSE | Not_TMED_Event | 1467
SAN JUAN | 2021-08-30 03:56 | 2021-08-30 05:16 | 9 | 001:20 | S | LINEA DE TRANSMISION 38KV | SECCIONALIZO LINEA 3600 | R21083000025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2021-08-30 | 720 | keep | 0 | Aug | 2021 | 0.00049039 | 6.1299e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 9
SAN JUAN | 2021-08-30 03:56 | 2021-08-30 05:16 | 6 | 001:20 | S | LINEA DE TRANSMISION 38KV | SECCIONALIZO LINEA 3600 | R21083000025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2021-08-30 | 480 | keep | 0 | Aug | 2021 | 0.00032693 | 4.0866e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 6
SAN JUAN | 2021-08-30 03:56 | 2021-08-30 05:16 | 1 | 001:20 | S | LINEA DE TRANSMISION 38KV | SECCIONALIZO LINEA 3600 | R21083000025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2021-08-30 | 80 | keep | 0 | Aug | 2021 | 5.4488e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-08-30 03:56 | 2021-08-30 05:16 | 1 | 001:20 | S | LINEA DE TRANSMISION 38KV | SECCIONALIZO LINEA 3600 | R21083000025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2021-08-30 | 80 | keep | 0 | Aug | 2021 | 5.4488e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-08-30 03:56 | 2021-08-30 05:16 | 12 | 001:20 | S | LINEA DE TRANSMISION 38KV | SECCIONALIZO LINEA 3600 | R21083000025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2021-08-30 | 960 | keep | 0 | Aug | 2021 | 0.00065385 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
SAN JUAN | 2021-08-30 03:56 | 2021-08-30 05:16 | 331 | 001:20 | S | LINEA DE TRANSMISION 38KV | SECCIONALIZO LINEA 3600 | R21083000023 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2021-08-30 | 26480 | keep | 0 | Aug | 2021 | 0.018035 | 0.00022544 | Sustained | FALSE | TRUE | Not_TMED_Event | 331
SAN JUAN | 2021-08-30 03:56 | 2021-08-30 05:16 | 1132 | 001:20 | S | LINEA DE TRANSMISION 38KV | SECCIONALIZO LINEA 3600 | R21083000023 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2021-08-30 | 90560 | keep | 0 | Aug | 2021 | 0.06168 | 0.000771 | Sustained | FALSE | TRUE | Not_TMED_Event | 1132
SAN JUAN | 2021-08-30 03:56 | 2021-08-30 05:16 | 234 | 001:20 | S | LINEA DE TRANSMISION 38KV | SECCIONALIZO LINEA 3600 | R21083000023 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2021-08-30 | 18720 | keep | 0 | Aug | 2021 | 0.01275 | 0.00015938 | Sustained | FALSE | TRUE | Not_TMED_Event | 234
SAN JUAN | 2021-08-30 03:56 | 2021-08-30 05:16 | 2179 | 001:20 | S | LINEA DE TRANSMISION 38KV | SECCIONALIZO LINEA 3600 | R21083000022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2021-08-30 | 174320 | keep | 0 | Aug | 2021 | 0.11873 | 0.0014841 | Sustained | FALSE | TRUE | Not_TMED_Event | 2179
SAN JUAN | 2021-08-30 03:56 | 2021-08-30 05:16 | 5062 | 001:20 | S | LINEA DE TRANSMISION 38KV | SECCIONALIZO LINEA 3600 | R21083000022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2021-08-30 | 404960 | keep | 0 | Aug | 2021 | 0.27582 | 0.0034477 | Sustained | FALSE | TRUE | Not_TMED_Event | 5062
MAYAGÃœEZ | 2021-08-30 03:58 | 2021-08-30 04:59 | 3458 | 001:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR POSTE EN FUEGO A PETICION DE GARETH LLEWELLEN | M21083000015 | Additional_clients | Wire Down | Include | Include | Equipment | 61 | 2021-08-30 | 210938 | keep | 0 | Aug | 2021 | 0.14367 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-30 04:05 | 2021-08-30 11:01 | 50 | 006:56 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21083000008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 416 | 2021-08-30 | 20800 | keep | 0 | Aug | 2021 | 0.014167 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-30 04:37 | 2021-08-30 19:34 | 13 | 014:57 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO SOTERRADO HACIA T-19 Y SE NORMALIZO | B21082900006 | New_Event | UG Cable Fault | Include | Include | Equipment | 897 | 2021-08-30 | 11661 | keep | 0 | Aug | 2021 | 0.0079423 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2021-08-30 04:47 | 2021-08-30 04:48 | 143 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | S21083000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-30 | 143 | keep | 0 | Aug | 2021 | 9.7397e-05 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
HUMACAO | 2021-08-30 04:47 | 2021-08-30 10:49 | 46 | 006:02 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | C21082900008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 362 | 2021-08-30 | 16652 | keep | 0 | Aug | 2021 | 0.011342 | 3.133e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 46
MAYAGÃœEZ | 2021-08-30 04:59 | 2021-08-30 10:45 | 250 | 005:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 200 EN CORTE DE LINEA SE SEPARO LINEAS CRUZADAS | M21083000013 | Partial_restoration | Wire Down | Include | Include | Equipment | 346 | 2021-08-30 | 86500 | keep | 0 | Aug | 2021 | 0.058915 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
VEGA BAJA | 2021-08-30 05:03 | 2021-08-30 05:04 | 3387 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA | B21083000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-30 | 3387 | keep | 0 | Aug | 2021 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
VEGA BAJA | 2021-08-30 05:50 | 2021-08-30 08:58 | 60 | 003:08 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21083000011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 188 | 2021-08-30 | 11280 | keep | 0 | Aug | 2021 | 0.0076828 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-08-30 05:57 | 2021-08-31 10:41 | 50 | 028:44 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21080300007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1724 | 2021-08-30 | 86200 | keep | 0 | Aug | 2021 | 0.05871 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-08-30 06:14 | 2021-08-30 10:17 | 50 | 004:03 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M21083000020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 243 | 2021-08-30 | 12150 | keep | 0 | Aug | 2021 | 0.0082753 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-08-30 06:17 | 2021-08-31 11:35 | 25 | 029:18 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S21083000009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1758 | 2021-08-30 | 43950 | keep | 0 | Aug | 2021 | 0.029934 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-08-30 06:23 | 2021-08-30 06:25 | 2179 | 000:02 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR TRAMO DE LINEA 3600 SOBRE LINEA 1619-01. | R21083000000 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2021-08-30 | 4358 | keep | 0 | Aug | 2021 | 0.0029682 | 0 | Momentary | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-08-30 06:25 | 2021-08-30 06:43 | 100 | 000:18 | P | LINEA DE TRANSMISION 38KV | SECCIONALIZARON TRAMO DEL 1619-01 POR AVERIA LINEA 3600 SOBRE EL 1619-01 Y SE TRANSFIRIO PARTE DE LA CARGA AL 1646-03 | R21083000046 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2021-08-30 | 1800 | keep | 0 | Aug | 2021 | 0.001226 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-08-30 06:31 | 2021-08-30 12:56 | 1 | 006:25 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | R21083100047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 385 | 2021-08-30 | 385 | keep | 0 | Aug | 2021 | 0.00026222 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-08-30 06:31 | 2021-08-30 09:14 | 8 | 002:43 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | A21083100003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 163 | 2021-08-30 | 1304 | keep | 0 | Aug | 2021 | 0.00088815 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2021-08-30 06:43 | 2021-08-30 11:18 | 80 | 004:35 | P | LINEA DE TRANSMISION 38KV | SE REPARO AVERIA DE LINEA 3600 SOBRE LINEA 1619-01 Y CERRARON MACHETES EN CARR 190 KM 0.1 SABANA ABAJO | R21083000046 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 275 | 2021-08-30 | 22000 | keep | 0 | Aug | 2021 | 0.014984 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-08-30 06:46 | 2021-08-30 13:39 | 35 | 006:53 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S21083000011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 413 | 2021-08-30 | 14455 | keep | 0 | Aug | 2021 | 0.0098452 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
BAYAMON | 2021-08-30 06:46 | 2021-08-30 08:10 | 2858 | 001:24 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR CONTROL, REPORTAN CONDUCTOR VIVO EN EL SUELO | B21083000014 | New_Event | Wire Down | Include | Include | Equipment | 84 | 2021-08-30 | 240072 | keep | 0 | Aug | 2021 | 0.16351 | 0.0019466 | Sustained | FALSE | FALSE | Not_TMED_Event | 2858
HUMACAO | 2021-08-30 06:47 | 2021-08-30 06:48 | 551 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR | C21083000010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-30 | 551 | keep | 0 | Aug | 2021 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
HUMACAO | 2021-08-30 06:48 | 2021-08-30 12:13 | 16 | 005:25 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21083000035 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 325 | 2021-08-30 | 5200 | keep | 0 | Aug | 2021 | 0.0035417 | 1.0898e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 16
SAN JUAN | 2021-08-30 07:02 | 2021-08-30 09:57 | 10 | 002:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21083000006 | New_Event | Secondary Wire Down | Include | Include | Equipment | 175 | 2021-08-30 | 1750 | keep | 0 | Aug | 2021 | 0.0011919 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-08-30 07:05 | 2021-08-30 11:32 | 500 | 004:27 | P | DESGANCHE | 2 X 200 EN CORTE DE LINEA REQUIERE DESGANCHE | M21082000028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 267 | 2021-08-30 | 133500 | keep | 0 | Aug | 2021 | 0.090926 | 0.00034055 | Sustained | FALSE | TRUE | Not_TMED_Event | 500
HUMACAO | 2021-08-30 07:13 | 2021-08-30 15:18 | 60 | 008:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 10 EN TRANSFORMADOR SE CERRO PUENTE DE LINEA A LINEA | C21083000027 | Partial_restoration | Wire Down | Include | Include | Equipment | 485 | 2021-08-30 | 29100 | keep | 0 | Aug | 2021 | 0.01982 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-08-30 07:15 | 2021-08-30 11:33 | 100 | 004:18 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO ENCONTRARON CAUSA | M21083000031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 258 | 2021-08-30 | 25800 | keep | 0 | Aug | 2021 | 0.017572 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-08-30 07:42 | 2021-08-30 10:55 | 40 | 003:13 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21083000023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2021-08-30 | 7720 | keep | 0 | Aug | 2021 | 0.0052581 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
PONCE | 2021-08-30 07:54 | 2021-08-30 11:58 | 10 | 004:04 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA | P21083000005 | New_Event | Wire Down | Include | Include | Equipment | 244 | 2021-08-30 | 2440 | keep | 0 | Aug | 2021 | 0.0016619 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-08-30 08:06 | 2021-08-30 16:29 | 10 | 008:23 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | R21083000050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 503 | 2021-08-30 | 5030 | keep | 0 | Aug | 2021 | 0.0034259 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BAYAMON | 2021-08-30 08:10 | 2021-08-30 12:56 | 48 | 004:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO | B21082900142 | Partial_restoration | Wire Down | Include | Include | Equipment | 286 | 2021-08-30 | 13728 | keep | 0 | Aug | 2021 | 0.0093501 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-30 08:11 | 2021-08-30 19:51 | 23 | 011:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR 50KVA | B21083000155 | New_Event | Service Transformer Failure | Include | Include | Equipment | 700 | 2021-08-30 | 16100 | keep | 0 | Aug | 2021 | 0.010966 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
GUAYAMA | 2021-08-30 08:24 | 2021-08-30 08:25 | 4132 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210830000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-30 | 4132 | keep | 0 | Aug | 2021 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
MAYAGÃœEZ | 2021-08-30 08:24 | 2021-08-30 19:36 | 1 | 011:12 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN RISER AVE CRUZO RISER | M21083000044 | New_Event |  |  | Include | Wildlife | 672 | 2021-08-30 | 672 | keep | 0 | Aug | 2021 | 0.0004577 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-08-30 08:32 | 2021-08-30 12:32 | 90 | 004:00 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R21083000010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2021-08-30 | 21600 | keep | 0 | Aug | 2021 | 0.014712 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
BAYAMON | 2021-08-30 08:39 | 2021-08-30 18:51 | 20 | 010:12 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE T-162 75KVA X 100KVA | S21083000016 | New_Event | Service Transformer Failure | Include | Include | Equipment | 612 | 2021-08-30 | 12240 | keep | 0 | Aug | 2021 | 0.0083366 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-08-30 08:54 | 2021-08-30 14:09 | 50 | 005:15 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21083000050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 315 | 2021-08-30 | 15750 | keep | 0 | Aug | 2021 | 0.010727 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-30 08:55 | 2021-08-30 13:00 | 10 | 004:05 | P | ESTRUCTURA AVERIADA | SE ABRIO CAJAS DE TRANSFORMADOR PARA PASARLO A POSTE NUEVO POSTE EN MALAS CONDICIONES | A21083000015 | New_Event | Defective Pole | Include | Include | Equipment | 245 | 2021-08-30 | 2450 | keep | 0 | Aug | 2021 | 0.0016687 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-08-30 09:01 | 2021-08-30 12:03 | 100 | 003:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 25 EN CORTE DE LINEA AVE CRUZO LINEAS | A21083000017 | New_Event |  |  | Include | Wildlife | 182 | 2021-08-30 | 18200 | keep | 0 | Aug | 2021 | 0.012396 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-08-30 09:05 | 2021-08-30 11:57 | 20 | 002:52 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR NO SE ENCONTRARON CAUSA | M21083000051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 172 | 2021-08-30 | 3440 | keep | 0 | Aug | 2021 | 0.002343 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-08-30 09:10 | 2021-08-30 12:11 | 1 | 003:01 | P | NO SE REPORTO CAUSA | 2 X 40 EN MONTURA | B21083000034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 181 | 2021-08-30 | 181 | keep | 0 | Aug | 2021 | 0.00012328 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-08-30 09:27 | 2021-08-30 09:28 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO | B21083000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-30 | 2605 | keep | 0 | Aug | 2021 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
CAGUAS | 2021-08-30 09:27 | 2021-08-30 13:30 | 10 | 004:03 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO BAJANTE SECUNDARIO, BAJARON TAP DEL 3 AL 4 Y SE REPARO SECUNADRIA EN VARIOS PUNTOS | C21083000031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 243 | 2021-08-30 | 2430 | keep | 0 | Aug | 2021 | 0.0016551 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-08-30 09:37 | 2021-08-30 09:38 | 2435 | 000:01 | P | NO SE REPORTO CAUSA | RECERRO. CARGA POR EL 1909-08 | S21083000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-30 | 2435 | keep | 0 | Aug | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-08-30 09:37 | 2021-08-30 09:38 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO. LLEVA 1907-05 | S21083000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-30 | 2956 | keep | 0 | Aug | 2021 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
SAN JUAN | 2021-08-30 09:40 | 2021-08-30 18:00 | 20 | 008:20 | P | SECUNDARIA/ESTRUCTURA AVERIADA | ABRIO TRANSFORMADOR PARA REEMPLAZAR POSTE | S21083000012 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 500 | 2021-08-30 | 10000 | keep | 0 | Aug | 2021 | 0.006811 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-08-30 09:40 | 2021-08-30 15:08 | 50 | 005:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A21083000023 | New_Event | Cutout Failure | Include | Include | Equipment | 328 | 2021-08-30 | 16400 | keep | 0 | Aug | 2021 | 0.01117 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-30 09:40 | 2021-08-30 16:55 | 45 | 007:15 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REMPLAZO POSTE PARTIDO | A21083000022 | New_Event | Defective Pole | Include | Include | Equipment | 435 | 2021-08-30 | 19575 | keep | 0 | Aug | 2021 | 0.013332 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
AGUADILLA | 2021-08-30 09:45 | 2021-08-30 13:00 | 12 | 003:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRAMSFORMADOR PARA REMPLAZAR PEDESTAL SECUNDARIO | M21083000063 | New_Event | Secondary Wire Down | Include | Include | Equipment | 195 | 2021-08-30 | 2340 | keep | 0 | Aug | 2021 | 0.0015938 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-08-30 09:54 | 2021-08-30 10:23 | 25 | 000:29 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTE SECUNDARIO | S21083000000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 29 | 2021-08-30 | 725 | keep | 0 | Aug | 2021 | 0.00049379 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-08-30 10:04 | 2021-08-30 10:05 | 4533 | 000:01 | T | CABLE SOTERRADO AVERIADO | RECERRO | B21083000046 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2021-08-30 | 4533 | keep | 0 | Aug | 2021 | 0.0030874 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
BAYAMON | 2021-08-30 10:05 | 2021-08-30 13:48 | 20 | 003:43 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO SOTERRADO AVERIADO DEL T-544 HACIA EL T-543 | B21083000050 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 223 | 2021-08-30 | 4460 | keep | 0 | Aug | 2021 | 0.0030377 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-08-30 10:10 | 2021-08-30 10:11 | 100 | 000:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | P21082900114 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-08-30 | 100 | keep | 0 | Aug | 2021 | 6.811e-05 | 6.811e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-08-30 10:13 | 2021-08-30 16:45 | 81 | 006:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | ABRIO CORTE DE LINEA PARA LEVANTAR NEUTRAL PRIMARIO | R21083000059 | New_Event | Wire Down | Include | Include | Equipment | 392 | 2021-08-30 | 31752 | keep | 0 | Aug | 2021 | 0.021626 | 5.5169e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 81
MAYAGÃœEZ | 2021-08-30 10:25 | 2021-08-31 09:30 | 80 | 023:05 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21083000320 | New_Event | Bad Weather | Include | Include | Weather | 1385 | 2021-08-30 | 110800 | keep | 0 | Aug | 2021 | 0.075465 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
VEGA BAJA | 2021-08-30 10:34 | 2021-08-31 10:35 | 10 | 024:01 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA AVERIADA | B21083000290 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1441 | 2021-08-30 | 14410 | keep | 0 | Aug | 2021 | 0.0098146 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BAYAMON | 2021-08-30 10:39 | 2021-08-31 13:24 | 30 | 026:45 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL AEREO DEL T-542 HACIA EL T-543 | B21083000050 | New_Event | UG Cable Fault | Include | Include | Equipment | 1605 | 2021-08-30 | 48150 | keep | 0 | Aug | 2021 | 0.032795 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2021-08-30 10:49 | 2021-08-30 14:36 | 50 | 003:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA, SE LEVANTO CONDUCTOR Y SE CERRO CORTE DE LINEA | B21082900000 | New_Event | Wire Down | Include | Include | Equipment | 227 | 2021-08-30 | 11350 | keep | 0 | Aug | 2021 | 0.0077304 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
ARECIBO | 2021-08-30 10:51 | 2021-08-30 18:53 | 50 | 008:02 | P | ESTRUCTURA AVERIADA | SE REMPLAZARON 2 POSTES PRIMARIOS PARTIDOS Y SE CERRO CORTE DE LINEA | A21083000042 | New_Event | Defective Pole | Include | Include | Equipment | 482 | 2021-08-30 | 24100 | keep | 0 | Aug | 2021 | 0.016414 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-30 11:04 | 2021-08-30 19:12 | 8 | 008:08 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA RELOCALIZAR EL MISMO A OTRO POSTE TRABAJOS PENDIENTES A SER REALIZADOS DESDE EL PASO DEL HURACAN MARIA | B21083000059 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 488 | 2021-08-30 | 3904 | keep | 0 | Aug | 2021 | 0.002659 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2021-08-30 11:18 | 2021-08-30 16:10 | 7 | 004:52 | P | DESGANCHE | SE DESGANCHO Y SE REPARO BAJANTE PRIMARIO | C21083000046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 292 | 2021-08-30 | 2044 | keep | 0 | Aug | 2021 | 0.0013922 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2021-08-30 11:22 | 2021-08-30 16:08 | 25 | 004:46 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21083000066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 286 | 2021-08-30 | 7150 | keep | 0 | Aug | 2021 | 0.0048698 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2021-08-30 11:36 | 2021-08-30 11:39 | 6136 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S21083000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-08-30 | 18408 | keep | 0 | Aug | 2021 | 0.012538 | 0.0041792 | Momentary | FALSE | FALSE | Not_TMED_Event | 6136
VEGA BAJA | 2021-08-30 11:44 | 2021-09-01 11:22 | 10 | 047:38 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21083000071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2858 | 2021-08-30 | 28580 | keep | 0 | Aug | 2021 | 0.019466 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2021-08-30 11:52 | 2021-08-30 14:13 | 100 | 002:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA REMPLAZO CAJA AVERIADA | R21083000066 | New_Event | Cutout Failure | Include | Include | Equipment | 141 | 2021-08-30 | 14100 | keep | 0 | Aug | 2021 | 0.0096034 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-08-30 11:52 | 2021-08-30 15:00 | 80 | 003:08 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21083000087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2021-08-30 | 15040 | keep | 0 | Aug | 2021 | 0.010244 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-08-30 12:09 | 2021-08-30 12:10 | 60 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S21083000049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-30 | 60 | keep | 0 | Aug | 2021 | 4.0866e-05 | 4.0866e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-08-30 12:22 | 2021-08-30 12:23 | 681 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1530-06 LLEVANDO LA CARGA DEL 1526-02 | S21083000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-30 | 681 | keep | 0 | Aug | 2021 | 0.00046383 | 0.00046383 | Momentary | FALSE | FALSE | Not_TMED_Event | 681
BAYAMON | 2021-08-30 12:22 | 2021-08-30 12:23 | 437 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1530-06 LLEVANDO LA CARGA DEL 1526-02 | S21083000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-30 | 437 | keep | 0 | Aug | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
SAN JUAN | 2021-08-30 12:23 | 2021-08-30 15:01 | 50 | 002:38 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21083000050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 158 | 2021-08-30 | 7900 | keep | 0 | Aug | 2021 | 0.0053807 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-30 12:46 | 2021-08-30 18:02 | 50 | 005:16 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21082900166 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 316 | 2021-08-30 | 15800 | keep | 0 | Aug | 2021 | 0.010761 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-08-30 12:49 | 2021-08-30 15:22 | 100 | 002:33 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 140 EN CORTE DE LINEA REMPLAZO AISLADOR | R21083000069 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 153 | 2021-08-30 | 15300 | keep | 0 | Aug | 2021 | 0.010421 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-08-30 12:49 | 2021-08-30 15:50 | 100 | 003:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A21083000062 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 181 | 2021-08-30 | 18100 | keep | 0 | Aug | 2021 | 0.012328 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BARRANQUITAS | 2021-08-30 12:51 | 2021-08-30 20:07 | 80 | 007:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | C21083000062 | New_Event | Wire Down | Include | Include | Equipment | 436 | 2021-08-30 | 34880 | keep | 0 | Aug | 2021 | 0.023757 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
AGUADILLA | 2021-08-30 13:08 | 2021-08-30 17:54 | 1 | 004:46 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN RISER ROEDOR CRUZO LINEAS | A21083000100 | New_Event |  |  | Include | Wildlife | 286 | 2021-08-30 | 286 | keep | 0 | Aug | 2021 | 0.00019479 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-08-30 13:18 | 2021-08-30 17:40 | 1 | 004:22 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | R21083000073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 262 | 2021-08-30 | 262 | keep | 0 | Aug | 2021 | 0.00017845 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-08-30 13:20 | 2021-08-30 13:39 | 5 | 000:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR REEMPLAZO PORTAFUSIBLE | R21083000076 | New_Event | Cutout Failure | Include | Include | Equipment | 19 | 2021-08-30 | 95 | keep | 0 | Aug | 2021 | 6.4704e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2021-08-30 13:21 | 2021-08-30 17:24 | 4 | 004:03 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21083000073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2021-08-30 | 972 | keep | 0 | Aug | 2021 | 0.00066202 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
PONCE | 2021-08-30 13:28 | 2021-08-30 17:10 | 45 | 003:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA | P21083000050 | New_Event |  |  | Include | Wildlife | 222 | 2021-08-30 | 9990 | keep | 0 | Aug | 2021 | 0.0068041 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
BAYAMON | 2021-08-30 13:48 | 2021-08-30 14:17 | 2402 | 000:29 | S | RELEVO DE CARGA POR CONTINGENCIA | CCE ABRIO ALTA DEL TRANSFORMADOR POR CONTINGENCIA L-39000 POR DISPARO L-50200 LLEVA EL 1720-08 | S21083000000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 29 | 2021-08-30 | 69658 | keep | 0 | Aug | 2021 | 0.047444 | 0.001636 | Sustained | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2021-08-30 13:48 | 2021-08-30 14:17 | 1533 | 000:29 | S | RELEVO DE CARGA POR CONTINGENCIA | CCE ABRIO ALTA DEL TRANSFORMADOR POR CONTINGENCIA L-39000 POR DISPARO L-50200. SE AFECTO EL 1720-07 | S21083000000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 29 | 2021-08-30 | 44457 | keep | 0 | Aug | 2021 | 0.030279 | 0.0010441 | Sustained | FALSE | FALSE | Not_TMED_Event | 1533
BAYAMON | 2021-08-30 13:48 | 2021-08-30 14:17 | 2364 | 000:29 | S | RELEVO DE CARGA POR CONTINGENCIA | CCE ABRIO ALTA DEL TRANSFORMADOR POR CONTINGENCIA L-39000 POR DISPARO L-50200 | S21083000000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 29 | 2021-08-30 | 68556 | keep | 0 | Aug | 2021 | 0.046693 | 0.0016101 | Sustained | FALSE | FALSE | Not_TMED_Event | 2364
BAYAMON | 2021-08-30 13:48 | 2021-08-30 14:14 | 4533 | 000:26 | S | RELEVO DE CARGA POR CONTINGENCIA | CCE ABRIO ALTA DEL TRANSFORMADOR POR PROBLEMA DE GENERACION POR CONTINGENCIA LINEA 39000 DEBIDO A DISPARO LINEA 50200 | B21083000000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 26 | 2021-08-30 | 117858 | keep | 0 | Aug | 2021 | 0.080273 | 0.0030874 | Sustained | TRUE | TRUE | Not_TMED_Event | 4533
BAYAMON | 2021-08-30 13:48 | 2021-08-30 14:14 | 911 | 000:26 | S | RELEVO DE CARGA POR CONTINGENCIA | CCE ABRIO ALTA DEL TRANSFORMADOR POR PROBLEMA DE GENERACION POR CONTINGENCIA LINEA 39000 DEBIDO A DISPARO LINEA 50200 | B21083000000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 26 | 2021-08-30 | 23686 | keep | 0 | Aug | 2021 | 0.016132 | 0.00062048 | Sustained | TRUE | TRUE | Not_TMED_Event | 911
BAYAMON | 2021-08-30 13:48 | 2021-08-30 14:14 | 4431 | 000:26 | S | RELEVO DE CARGA POR CONTINGENCIA | CCE ABRIO ALTA DEL TRANSFORMADOR POR PROBLEMA DE GENERACION POR CONTINGENCIA LINEA 39000 DEBIDO A DISPARO LINEA 50200 | B21083000000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 26 | 2021-08-30 | 115206 | keep | 0 | Aug | 2021 | 0.078466 | 0.0030179 | Sustained | TRUE | TRUE | Not_TMED_Event | 4431
BAYAMON | 2021-08-30 13:48 | 2021-08-30 14:14 | 1362 | 000:26 | S | RELEVO DE CARGA POR CONTINGENCIA | CCE ABRIO ALTA DEL TRANSFORMADOR POR PROBLEMA DE GENERACION POR CONTINGENCIA LINEA 39000 DEBIDO A DISPARO LINEA 50200 | B21083000000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 26 | 2021-08-30 | 35412 | keep | 0 | Aug | 2021 | 0.024119 | 0.00092765 | Sustained | TRUE | TRUE | Not_TMED_Event | 1362
BAYAMON | 2021-08-30 13:48 | 2021-08-30 14:14 | 341 | 000:26 | S | RELEVO DE CARGA POR CONTINGENCIA | CCE ABRIO ALTA DEL TRANSFORMADOR POR PROBLEMA DE GENERACION POR CONTINGENCIA LINEA 39000 DEBIDO A DISPARO LINEA 50200 | B21083000000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 26 | 2021-08-30 | 8866 | keep | 0 | Aug | 2021 | 0.0060386 | 0.00023225 | Sustained | TRUE | TRUE | Not_TMED_Event | 341
BAYAMON | 2021-08-30 13:48 | 2021-08-30 14:14 | 3597 | 000:26 | S | RELEVO DE CARGA POR CONTINGENCIA | CCE ABRIO ALTA DEL TRANSFORMADOR POR PROBLEMA DE GENERACION POR CONTINGENCIA LINEA 39000 DEBIDO A DISPARO LINEA 50200 | B21083000000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 26 | 2021-08-30 | 93522 | keep | 0 | Aug | 2021 | 0.063697 | 0.0024499 | Sustained | TRUE | TRUE | Not_TMED_Event | 3597
BAYAMON | 2021-08-30 13:48 | 2021-08-30 14:14 | 492 | 000:26 | S | RELEVO DE CARGA POR CONTINGENCIA | CCE ABRIO ALTA DEL TRANSFORMADOR POR PROBLEMA DE GENERACION POR CONTINGENCIA LINEA 39000 DEBIDO A DISPARO LINEA 50200 | B21083000000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 26 | 2021-08-30 | 12792 | keep | 0 | Aug | 2021 | 0.0087126 | 0.0003351 | Sustained | TRUE | TRUE | Not_TMED_Event | 492
BAYAMON | 2021-08-30 13:48 | 2021-08-30 14:14 | 4028 | 000:26 | S | RELEVO DE CARGA POR CONTINGENCIA | CCE ABRIO ALTA DEL TRANSFORMADOR POR PROBLEMA DE GENERACION POR CONTINGENCIA LINEA 39000 DEBIDO A DISPARO LINEA 50200 | B21083000000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 26 | 2021-08-30 | 104728 | keep | 0 | Aug | 2021 | 0.07133 | 0.0027435 | Sustained | TRUE | TRUE | Not_TMED_Event | 4028
BAYAMON | 2021-08-30 13:48 | 2021-08-30 14:14 | 2617 | 000:26 | S | RELEVO DE CARGA POR CONTINGENCIA | CCE ABRIO ALTA DEL TRANSFORMADOR POR PROBLEMA DE GENERACION POR CONTINGENCIA LINEA 39000 DEBIDO A DISPARO LINEA 50200 | B21083000000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 26 | 2021-08-30 | 68042 | keep | 0 | Aug | 2021 | 0.046343 | 0.0017824 | Sustained | TRUE | TRUE | Not_TMED_Event | 2617
BAYAMON | 2021-08-30 13:48 | 2021-08-30 14:17 | 1 | 000:29 | T | RELEVO DE CARGA POR CONTINGENCIA | CCE ABRIO ALTA DEL TRANSFORMADOR POR CONTINGENCIA L-39000 POR DISPARO L-50200 CARGA POR EL 1709-02 | S21083000000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 29 | 2021-08-30 | 29 | keep | 0 | Aug | 2021 | 1.9752e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-08-30 13:48 | 2021-08-30 14:16 | 2435 | 000:28 | T | RELEVO DE CARGA POR CONTINGENCIA | CCE ABRIO ALTA DE TRANSFORMADOR POR CONTINGENCIA L-39000 POR DISPARO L-50200. CARGA POR EL 1909-08 | S21083000000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 28 | 2021-08-30 | 68180 | keep | 0 | Aug | 2021 | 0.046437 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2021-08-30 13:48 | 2021-08-30 17:17 | 80 | 003:29 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S21083000072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2021-08-30 | 16720 | keep | 0 | Aug | 2021 | 0.011388 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-08-30 13:48 | 2021-08-30 14:16 | 1139 | 000:28 | S | RELEVO DE CARGA POR CONTINGENCIA | CCE ABRIO ALTA DE TRANSFORMADOR POR CONTINGENCIA L-39000 POR DISPARO L-50200 | S21083000000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 28 | 2021-08-30 | 31892 | keep | 0 | Aug | 2021 | 0.021721 | 0.00077577 | Sustained | FALSE | FALSE | Not_TMED_Event | 1139
BAYAMON | 2021-08-30 13:48 | 2021-08-30 14:16 | 2956 | 000:28 | S | RELEVO DE CARGA POR CONTINGENCIA | CCE ABRIO ALTA DE TRANSFORMADOR POR CONTINGENCIA L-39000 POR DISPARO L-50200. LLEVA 1907-05 | S21083000000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 28 | 2021-08-30 | 82768 | keep | 0 | Aug | 2021 | 0.056373 | 0.0020133 | Sustained | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2021-08-30 13:48 | 2021-08-30 14:16 | 445 | 000:28 | S | RELEVO DE CARGA POR CONTINGENCIA | CCE ABRIO ALTA DE TRANSFORMADOR POR CONTINGENCIA L-39000 POR DISPARO L-50200 | S21083000000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 28 | 2021-08-30 | 12460 | keep | 0 | Aug | 2021 | 0.0084864 | 0.00030309 | Sustained | FALSE | FALSE | Not_TMED_Event | 445
ARECIBO | 2021-08-30 13:50 | 2021-08-30 15:57 | 4 | 002:07 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 25 KVA POR LA MISMA CAPACIDAD | A21083000028 | New_Event | Service Transformer Failure | Include | Include | Equipment | 127 | 2021-08-30 | 508 | keep | 0 | Aug | 2021 | 0.000346 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2021-08-30 14:00 | 2021-08-30 14:01 | 1225 | 000:01 | T | DESGANCHE | RECIERRE | S21083000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-30 | 1225 | keep | 0 | Aug | 2021 | 0.00083434 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2021-08-30 14:01 | 2021-08-30 19:03 | 50 | 005:02 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21083000116 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 302 | 2021-08-30 | 15100 | keep | 0 | Aug | 2021 | 0.010285 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-30 14:06 | 2021-08-31 17:31 | 10 | 027:25 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA AVERIADA | S21083000320 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1645 | 2021-08-30 | 16450 | keep | 0 | Aug | 2021 | 0.011204 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-08-30 14:14 | 2021-08-30 16:27 | 20 | 002:13 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO SOTERRADO AVERIADO DEL T-544 HACIA EL T-543 | B21083000050 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 133 | 2021-08-30 | 2660 | keep | 0 | Aug | 2021 | 0.0018117 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2021-08-30 14:18 | 2021-08-30 19:00 | 16 | 004:42 | P | ESTRUCTURA AVERIADA | SE RETIRA CARGA A DOS TRANSFORMADORES PARA REMPLAZO DE POSTE PRIMARIO PARTIDO | P21083000175 | New_Event | Defective Pole | Include | Include | Equipment | 282 | 2021-08-30 | 4512 | keep | 0 | Aug | 2021 | 0.0030731 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
ARECIBO | 2021-08-30 14:30 | 2021-08-30 15:25 | 10 | 000:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | A21083000070 | New_Event | Secondary Wire Down | Include | Include | Equipment | 55 | 2021-08-30 | 550 | keep | 0 | Aug | 2021 | 0.0003746 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
HUMACAO | 2021-08-30 14:34 | 2021-08-30 19:10 | 11 | 004:36 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25 KVA X 25 KVA | C21083000083 | New_Event | Service Transformer Failure | Include | Include | Equipment | 276 | 2021-08-30 | 3036 | keep | 0 | Aug | 2021 | 0.0020678 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2021-08-30 14:39 | 2021-08-30 14:40 | 2435 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE. CARGA POR EL 1909-08 | S21083000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-30 | 2435 | keep | 0 | Aug | 2021 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2021-08-30 14:39 | 2021-08-30 14:40 | 2956 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE. LLEVA EL 1907-05 | S21083000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-30 | 2956 | keep | 0 | Aug | 2021 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
PONCE | 2021-08-30 14:50 | 2021-08-31 09:55 | 100 | 019:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LNEA DESGANCHE | P2108300061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1145 | 2021-08-30 | 114500 | keep | 0 | Aug | 2021 | 0.077985 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-08-30 15:00 | 2021-08-30 16:19 | 60 | 001:19 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21083000186 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2021-08-30 | 4740 | keep | 0 | Aug | 2021 | 0.0032284 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-08-30 15:06 | 2021-08-30 16:38 | 2 | 001:32 | P | SECUNDARIA/DESGANCHE | SE DESGANCHO Y REPARO SECUNDARIA | C21083000058 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 92 | 2021-08-30 | 184 | keep | 0 | Aug | 2021 | 0.00012532 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2021-08-30 15:30 | 2021-08-30 16:45 | 1 | 001:15 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER NO CAUSA | C21083000093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 75 | 2021-08-30 | 75 | keep | 0 | Aug | 2021 | 5.1082e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-08-30 15:44 | 2021-08-30 17:35 | 15 | 001:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR CONECTORES | S21083000022 | New_Event | Secondary Wire Down | Include | Include | Equipment | 111 | 2021-08-30 | 1665 | keep | 0 | Aug | 2021 | 0.001134 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-08-30 15:52 | 2021-08-30 17:55 | 90 | 002:03 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | S21083000170 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 123 | 2021-08-30 | 11070 | keep | 0 | Aug | 2021 | 0.0075397 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
ARECIBO | 2021-08-30 16:09 | 2021-08-30 21:30 | 1 | 005:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO ABIERTO | A21083000106 | New_Event | Wire Down | Include | Include | Equipment | 321 | 2021-08-30 | 321 | keep | 0 | Aug | 2021 | 0.00021863 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-08-30 16:17 | 2021-08-30 18:27 | 1 | 002:10 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARTO BAJANTE PRIMARIO EN TRANSFORMADOR | A21083000107 | New_Event | Wire Down | Include | Include | Equipment | 130 | 2021-08-30 | 130 | keep | 0 | Aug | 2021 | 8.8542e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-08-30 17:26 | 2021-08-30 21:04 | 9 | 003:38 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO DEL T-19 AL SU-I SE CERRO N/O EN T-18 AL T-19 TERMINACION EN SU-1 AVERIADA | C21082900063 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 218 | 2021-08-30 | 1962 | keep | 0 | Aug | 2021 | 0.0013363 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2021-08-30 17:43 | 2021-08-31 11:50 | 40 | 018:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA IGUANA CRUZANDO PARRARAYO | S21083000199 | New_Event |  |  | Include | Wildlife | 1087 | 2021-08-30 | 43480 | keep | 0 | Aug | 2021 | 0.029614 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-08-30 17:46 | 2021-08-30 19:44 | 5 | 001:58 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR PROBO MALO SE PASO LA CARGA A OTRO TRANSFORMADOR | R21083000104 | New_Event | Service Transformer Failure | Include | Include | Equipment | 118 | 2021-08-30 | 590 | keep | 0 | Aug | 2021 | 0.00040185 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2021-08-30 17:53 | 2021-08-30 20:40 | 267 | 002:47 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE ABIERTO | P21083000131 | New_Event | Wire Down | Include | Include | Equipment | 167 | 2021-08-30 | 44589 | keep | 0 | Aug | 2021 | 0.030369 | 0.00018185 | Sustained | FALSE | FALSE | Not_TMED_Event | 267
CAGUAS | 2021-08-30 18:06 | 2021-08-30 20:17 | 7 | 002:11 | P | DESGANCHE | SE DESGANCHO Y SE REPARO BAJANTE PRIMARIO | C21083000046 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 131 | 2021-08-30 | 917 | keep | 0 | Aug | 2021 | 0.00062456 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2021-08-30 18:25 | 2021-08-30 22:04 | 67 | 003:39 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | P21083000136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2021-08-30 | 14673 | keep | 0 | Aug | 2021 | 0.0099937 | 4.5633e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 67
BAYAMON | 2021-08-30 18:47 | 2021-08-30 19:41 | 25 | 000:54 | P | DESGANCHE | SE ABRIO CORTE LINEA POR FUEGO POR ARBOL ENCIMA DE LINEAS SE RETIRO RAMAS Y SE CERRO CORTE DE LINEA | B21083000221 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2021-08-30 | 1350 | keep | 0 | Aug | 2021 | 0.00091948 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CANOVANAS | 2021-08-30 18:55 | 2021-08-30 21:41 | 1 | 002:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA | R21083000162 | New_Event | Wire Down | Include | Include | Equipment | 166 | 2021-08-30 | 166 | keep | 0 | Aug | 2021 | 0.00011306 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CANOVANAS | 2021-08-30 18:55 | 2021-08-31 09:15 | 4 | 014:20 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR | R21083000176 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 860 | 2021-08-30 | 3440 | keep | 0 | Aug | 2021 | 0.002343 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2021-08-30 19:02 | 2021-08-31 16:53 | 7 | 021:51 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21083000226 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1311 | 2021-08-30 | 9177 | keep | 0 | Aug | 2021 | 0.0062504 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2021-08-30 19:03 | 2021-08-30 19:04 | 1225 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | S21083000000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-30 | 1225 | keep | 0 | Aug | 2021 | 0.00083434 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-08-30 19:04 | 2021-08-30 19:06 | 50 | 000:02 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21083000116 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2 | 2021-08-30 | 100 | keep | 0 | Aug | 2021 | 6.811e-05 | 3.4055e-05 | Momentary | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-08-30 19:04 | 2021-08-30 19:05 | 1310 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21083000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-30 | 1310 | keep | 0 | Aug | 2021 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
PONCE | 2021-08-30 19:51 | 2021-08-30 23:03 | 153 | 003:12 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | P21083000180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2021-08-30 | 29376 | keep | 0 | Aug | 2021 | 0.020008 | 0.00010421 | Sustained | FALSE | TRUE | Not_TMED_Event | 153
ARECIBO | 2021-08-30 20:37 | 2021-08-31 10:54 | 1 | 014:17 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARTO BAJANTE PRIMARIO EN TRANSFORMADOR | A21083000107 | Partial_restoration | Wire Down | Include | Include | Equipment | 857 | 2021-08-30 | 857 | keep | 0 | Aug | 2021 | 0.0005837 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-08-30 20:57 | 2021-08-31 21:20 | 50 | 024:23 | P | ESTRUCTURA AVERIADA | SE REMPLAZARON 2 POSTES PRIMARIOS PARTIDOS Y SE CERRO CORTE DE LINEA | A21083000042 | Partial_restoration | Defective Pole | Include | Include | Equipment | 1463 | 2021-08-30 | 73150 | keep | 0 | Aug | 2021 | 0.049822 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-08-30 21:02 | 2021-08-31 02:03 | 1935 | 005:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR POR FUEGO EN POSTE FRENTE A GASOLINERA SE LEVANTO CONDUCTOR Y SE CERRO INTERRUPTOR NUEVAMENTE | B21083000275 | New_Event | Wire Down | Include | Include | Equipment | 301 | 2021-08-30 | 582435 | keep | 0 | Aug | 2021 | 0.39669 | 0.0013179 | Sustained | FALSE | TRUE | Not_TMED_Event | 1935
CANOVANAS | 2021-08-30 21:10 | 2021-08-30 22:25 | 7 | 001:15 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R21083000172 | New_Event |  |  | Include | Wildlife | 75 | 2021-08-30 | 525 | keep | 0 | Aug | 2021 | 0.00035758 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
GUAYAMA | 2021-08-30 21:15 | 2021-08-30 21:34 | 16 | 000:19 | P | ESTRUCTURA AVERIADA | SE RETIRA CARGA A DOS TRANSFORMADORES PARA REMPLAZO DE POSTE PRIMARIO PARTIDO | P21083000175 | Partial_restoration | Defective Pole | Include | Include | Equipment | 19 | 2021-08-30 | 304 | keep | 0 | Aug | 2021 | 0.00020705 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-08-30 21:31 | 2021-08-30 21:35 | 1420 | 000:04 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CARGA POR EL 1530-06 | S21083000316 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-08-30 | 5680 | keep | 0 | Aug | 2021 | 0.0038686 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-08-30 21:31 | 2021-08-30 21:35 | 437 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 1526-02 | S21083000316 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-08-30 | 1748 | keep | 0 | Aug | 2021 | 0.0011906 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
GUAYAMA | 2021-08-30 21:45 | 2021-08-31 11:37 | 50 | 013:52 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEAS AVE CRUZO LINEAS | P21083000195 | New_Event |  |  | Include | Wildlife | 832 | 2021-08-30 | 41600 | keep | 0 | Aug | 2021 | 0.028334 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-08-30 22:05 | 2021-08-31 12:50 | 50 | 014:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | P21083000198 | New_Event | Cutout Failure | Include | Include | Equipment | 885 | 2021-08-30 | 44250 | keep | 0 | Aug | 2021 | 0.030138 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-08-30 22:20 | 2021-08-31 02:03 | 50 | 003:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | CERRAR PUENTE SECUNDARIO DE CAJA A LINEA | B21083000275 | New_Event | Secondary Wire Down | Include | Include | Equipment | 223 | 2021-08-30 | 11150 | keep | 0 | Aug | 2021 | 0.0075942 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-08-30 22:20 | 2021-08-31 11:50 | 100 | 013:30 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C21083000261 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 810 | 2021-08-30 | 81000 | keep | 0 | Aug | 2021 | 0.055169 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CANOVANAS | 2021-08-30 22:22 | 2021-08-30 22:23 | 539 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21083000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-30 | 539 | keep | 0 | Aug | 2021 | 0.00036711 | 0.00036711 | Momentary | FALSE | FALSE | Not_TMED_Event | 539
ARECIBO | 2021-08-30 22:37 | 2021-08-31 11:25 | 1 | 012:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO ABIERTO | A21083000106 | Partial_restoration | Wire Down | Include | Include | Equipment | 768 | 2021-08-30 | 768 | keep | 0 | Aug | 2021 | 0.00052308 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2021-08-30 22:40 | 2021-08-31 12:32 | 55 | 013:52 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C21083000265 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 832 | 2021-08-30 | 45760 | keep | 0 | Aug | 2021 | 0.031167 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
ARECIBO | 2021-08-30 23:29 | 2021-08-31 10:33 | 100 | 011:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA AVERIADA MARCA SHEEN DE 100AMP EN FID33638666 | A21083000201 | New_Event | Cutout Failure | Include | Include | Equipment | 664 | 2021-08-30 | 66400 | keep | 0 | Aug | 2021 | 0.045225 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-08-30 23:47 | 2021-08-31 11:43 | 100 | 011:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M21083000339 | New_Event | Cutout Failure | Include | Include | Equipment | 716 | 2021-08-30 | 71600 | keep | 0 | Aug | 2021 | 0.048766 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-08-31 00:31 | 2021-08-31 09:22 | 75 | 008:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES | A21083100002 | New_Event | Cutout Failure | Include | Include | Equipment | 531 | 2021-08-31 | 39825 | keep | 0 | Aug | 2021 | 0.027125 | 5.1082e-05 | Sustained | FALSE | TRUE | TMED_Event | 75
MAYAGÃœEZ | 2021-08-31 02:19 | 2021-08-31 12:30 | 1 | 010:11 | P | OTRAS CAUSAS | 2 X 80 EN CORTE DE LINEA SE HIZO BYPASS A EQUIPO DE MEDICION AVERIADO | M21083100004 | New_Event | Other Causes | Include | Include | Other | 611 | 2021-08-31 | 611 | keep | 0 | Aug | 2021 | 0.00041615 | 6.811e-07 | Sustained | FALSE | TRUE | TMED_Event | 1
ARECIBO | 2021-08-31 02:43 | 2021-08-31 10:54 | 30 | 008:11 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | A21083100003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 491 | 2021-08-31 | 14730 | keep | 0 | Aug | 2021 | 0.010033 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
CAGUAS | 2021-08-31 03:01 | 2021-08-31 19:51 | 100 | 016:50 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | C21083100004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1010 | 2021-08-31 | 101000 | keep | 0 | Aug | 2021 | 0.068791 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
ARECIBO | 2021-08-31 03:44 | 2021-08-31 16:05 | 80 | 012:21 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21083100004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 741 | 2021-08-31 | 59280 | keep | 0 | Aug | 2021 | 0.040375 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
BARRANQUITAS | 2021-08-31 04:41 | 2021-08-31 18:40 | 50 | 013:59 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA REMPLAZO PARARRAYO | C21083100008 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 839 | 2021-08-31 | 41950 | keep | 0 | Aug | 2021 | 0.028572 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
MAYAGÃœEZ | 2021-08-31 05:34 | 2021-08-31 18:30 | 100 | 012:56 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA SE CERRO PUENTES | M21083100006 | New_Event | Wire Down | Include | Include | Equipment | 776 | 2021-08-31 | 77600 | keep | 0 | Aug | 2021 | 0.052853 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
MAYAGÃœEZ | 2021-08-31 05:34 | 2021-08-31 12:36 | 150 | 007:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO PUENTE Y SE CERRO CORTE DE LINEA | M21083100006 | New_Event | Wire Down | Include | Include | Equipment | 422 | 2021-08-31 | 63300 | keep | 0 | Aug | 2021 | 0.043113 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
CANOVANAS | 2021-08-31 05:39 | 2021-08-31 12:18 | 50 | 006:39 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA REEMPLAZO AISLADOR ROTO Y SUBIO LINEA PRIMARIA | R21083100007 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 399 | 2021-08-31 | 19950 | keep | 0 | Aug | 2021 | 0.013588 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
MAYAGÃœEZ | 2021-08-31 05:59 | 2021-08-31 11:00 | 20 | 005:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA | M21083100000 | New_Event | Bad Weather | Include | Include | Weather | 301 | 2021-08-31 | 6020 | keep | 0 | Aug | 2021 | 0.0041002 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
FAJARDO | 2021-08-31 06:33 | 2021-08-31 08:44 | 95 | 002:11 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | R21083100009 | New_Event |  |  | Include | Wildlife | 131 | 2021-08-31 | 12445 | keep | 0 | Aug | 2021 | 0.0084762 | 6.4704e-05 | Sustained | FALSE | TRUE | TMED_Event | 95
CAGUAS | 2021-08-31 06:54 | 2021-08-31 06:55 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21083100013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-31 | 1702 | keep | 0 | Aug | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | TMED_Event | 1702
CAGUAS | 2021-08-31 06:55 | 2021-08-31 11:25 | 95 | 004:30 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C21083100017 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 270 | 2021-08-31 | 25650 | keep | 0 | Aug | 2021 | 0.01747 | 6.4704e-05 | Sustained | FALSE | TRUE | TMED_Event | 95
MAYAGÃœEZ | 2021-08-31 07:02 | 2021-08-31 09:48 | 500 | 002:46 | P | NO SE REPORTO CAUSA | 1 X 200 EN CONVERTIDOR | M21083100013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 166 | 2021-08-31 | 83000 | keep | 0 | Aug | 2021 | 0.056531 | 0.00034055 | Sustained | FALSE | FALSE | TMED_Event | 500
UTUADO | 2021-08-31 07:06 | 2021-08-31 14:15 | 30 | 007:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA SE CERRO CORTE DE LINEA | A21083100010 | New_Event | Wire Down | Include | Include | Equipment | 429 | 2021-08-31 | 12870 | keep | 0 | Aug | 2021 | 0.0087657 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
CAGUAS | 2021-08-31 07:12 | 2021-08-31 10:14 | 7 | 003:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR REEMPLAZO PORTAFUSIBLE | C21083100014 | New_Event | Cutout Failure | Include | Include | Equipment | 182 | 2021-08-31 | 1274 | keep | 0 | Aug | 2021 | 0.00086772 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
CAGUAS | 2021-08-31 07:24 | 2021-08-31 10:14 | 12 | 002:50 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR | C21083100016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 170 | 2021-08-31 | 2040 | keep | 0 | Aug | 2021 | 0.0013894 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
CAGUAS | 2021-08-31 07:29 | 2021-08-31 12:42 | 9 | 005:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | C21083100019 | New_Event | Secondary Wire Down | Include | Include | Equipment | 313 | 2021-08-31 | 2817 | keep | 0 | Aug | 2021 | 0.0019186 | 6.1299e-06 | Sustained | FALSE | FALSE | TMED_Event | 9
ARECIBO | 2021-08-31 07:33 | 2021-08-31 10:32 | 100 | 002:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 140 EN CORTE DE LINEA SE RETIRO TENSOR ROTO PEGANDO CON FASE VIVA | A21083100013 | New_Event |  |  | Include | Wildlife | 179 | 2021-08-31 | 17900 | keep | 0 | Aug | 2021 | 0.012192 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
BAYAMON | 2021-08-31 07:39 | 2021-08-31 14:37 | 40 | 006:58 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21083100021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 418 | 2021-08-31 | 16720 | keep | 0 | Aug | 2021 | 0.011388 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
MAYAGÃœEZ | 2021-08-31 07:44 | 2021-08-31 09:52 | 5 | 002:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA REMPLAZO AISLADOR | M21083100017 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 128 | 2021-08-31 | 640 | keep | 0 | Aug | 2021 | 0.0004359 | 3.4055e-06 | Sustained | FALSE | TRUE | TMED_Event | 5
ARECIBO | 2021-08-31 07:54 | 2021-09-04 22:45 | 80 | 110:51 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADOR PARTIDO | A21090300119 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 6651 | 2021-08-31 | 532080 | keep | 0 | Aug | 2021 | 0.3624 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
BARRANQUITAS | 2021-08-31 08:03 | 2021-08-31 12:59 | 300 | 004:56 | P | NO SE REPORTO CAUSA | 2 X 100 Y 2 X 65 EN CORTE DE LINEA | C21083100021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 296 | 2021-08-31 | 88800 | keep | 0 | Aug | 2021 | 0.060481 | 0.00020433 | Sustained | FALSE | TRUE | TMED_Event | 300
CAGUAS | 2021-08-31 08:14 | 2021-08-31 10:23 | 70 | 002:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21083100022 | New_Event |  |  | Include | Wildlife | 129 | 2021-08-31 | 9030 | keep | 0 | Aug | 2021 | 0.0061503 | 4.7677e-05 | Sustained | FALSE | TRUE | TMED_Event | 70
BARRANQUITAS | 2021-08-31 08:17 | 2021-08-31 15:10 | 80 | 006:53 | P | PARARRAYOS DEFECTUOSO | 1 X 40 Y 1 X 50 EN CORTES DE LINEA REMPLAZO PARARRAYO | C21083100023 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 413 | 2021-08-31 | 33040 | keep | 0 | Aug | 2021 | 0.022503 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
CAGUAS | 2021-08-31 08:19 | 2021-08-31 11:09 | 95 | 002:50 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR GLOBO DE HELIO | C21083100024 | New_Event |  |  | Include | Wildlife | 170 | 2021-08-31 | 16150 | keep | 0 | Aug | 2021 | 0.011 | 6.4704e-05 | Sustained | FALSE | TRUE | TMED_Event | 95
BAYAMON | 2021-08-31 08:22 | 2021-08-31 11:44 | 25 | 003:22 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21083100028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 202 | 2021-08-31 | 5050 | keep | 0 | Aug | 2021 | 0.0034395 | 1.7027e-05 | Sustained | FALSE | TRUE | TMED_Event | 25
PONCE | 2021-08-31 08:22 | 2021-08-31 08:23 | 3744 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE | P210831000XX | New_Event |  |  | Include | Wildlife | 1 | 2021-08-31 | 3744 | keep | 0 | Aug | 2021 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | TMED_Event | 3744
PONCE | 2021-08-31 08:23 | 2021-08-31 10:27 | 10 | 002:04 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR AVE CRUZO LINEAS | P21083100004 | 1st_after_momentary |  |  | Include | Wildlife | 124 | 2021-08-31 | 1240 | keep | 0 | Aug | 2021 | 0.00084456 | 6.811e-06 | Sustained | FALSE | TRUE | TMED_Event | 10
PONCE | 2021-08-31 08:24 | 2021-08-31 08:25 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210831000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-31 | 3114 | keep | 0 | Aug | 2021 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | TMED_Event | 3114
SAN JUAN | 2021-08-31 08:28 | 2021-08-31 12:02 | 1 | 003:34 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA EN CORTE DE LINEA | S21083100034 | New_Event | Wire Down | Include | Include | Equipment | 214 | 2021-08-31 | 214 | keep | 0 | Aug | 2021 | 0.00014575 | 6.811e-07 | Sustained | FALSE | TRUE | TMED_Event | 1
PONCE | 2021-08-31 08:33 | 2021-08-31 12:04 | 25 | 003:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA EN TRANSFORMADOR | P21083100014 | New_Event | Cutout Failure | Include | Include | Equipment | 211 | 2021-08-31 | 5275 | keep | 0 | Aug | 2021 | 0.0035928 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
BAYAMON | 2021-08-31 08:48 | 2021-08-31 10:48 | 15 | 002:00 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO 37.5KVA POR 37.5KVA | B21083100033 | New_Event | Service Transformer Failure | Include | Include | Equipment | 120 | 2021-08-31 | 1800 | keep | 0 | Aug | 2021 | 0.001226 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
CAGUAS | 2021-08-31 08:52 | 2021-09-01 17:58 | 55 | 033:06 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE CRITICO | C21083100086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1986 | 2021-08-31 | 109230 | keep | 0 | Aug | 2021 | 0.074396 | 3.746e-05 | Sustained | FALSE | TRUE | TMED_Event | 55
PONCE | 2021-08-31 08:59 | 2021-08-31 12:05 | 5 | 003:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE EN RISER | P21083100017 | New_Event | Wire Down | Include | Include | Equipment | 186 | 2021-08-31 | 930 | keep | 0 | Aug | 2021 | 0.00063342 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
AGUADILLA | 2021-08-31 09:00 | 2021-08-31 15:32 | 200 | 006:32 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21083100030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 392 | 2021-08-31 | 78400 | keep | 0 | Aug | 2021 | 0.053398 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
VEGA BAJA | 2021-08-31 09:06 | 2021-08-31 12:40 | 922 | 003:34 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE PRIMARIO FRENTE A PLAZA CARIBE MALL | B21083100000 | New_Event | Switch Failure | Include | Include | Equipment | 214 | 2021-08-31 | 197308 | keep | 0 | Aug | 2021 | 0.13439 | 0.00062797 | Sustained | FALSE | FALSE | TMED_Event | 922
MAYAGÃœEZ | 2021-08-31 09:07 | 2021-08-31 09:08 | 3147 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECIERRE DE INTERRUPTRO | M21083100034 | New_Event |  |  | Include | Wildlife | 1 | 2021-08-31 | 3147 | keep | 0 | Aug | 2021 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | TMED_Event | 3147
MAYAGÃœEZ | 2021-08-31 09:08 | 2021-08-31 16:25 | 150 | 007:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 80 EN CORTE DE LINEA IGUANA CRUZO LINEAS | M21083100049 | 1st_after_momentary |  |  | Include | Wildlife | 437 | 2021-08-31 | 65550 | keep | 0 | Aug | 2021 | 0.044646 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
FAJARDO | 2021-08-31 09:13 | 2021-08-31 09:59 | 1 | 000:46 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R21083100014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 46 | 2021-08-31 | 46 | keep | 0 | Aug | 2021 | 3.133e-05 | 6.811e-07 | Sustained | FALSE | TRUE | TMED_Event | 1
SAN JUAN | 2021-08-31 09:16 | 2021-09-01 14:29 | 12 | 029:13 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | S21083100044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1753 | 2021-08-31 | 21036 | keep | 0 | Aug | 2021 | 0.014328 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
ARECIBO | 2021-08-31 09:25 | 2021-08-31 10:05 | 40 | 000:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO CORTE DE LINEA PARA REPARAR NEUTRAL PRIMARIO ROTO | A21083100027 | New_Event | Wire Down | Include | Include | Equipment | 40 | 2021-08-31 | 1600 | keep | 0 | Aug | 2021 | 0.0010898 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
ARECIBO | 2021-08-31 09:27 | 2021-08-31 12:47 | 150 | 003:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA LLUVIA VIENTO Y DESCARGAS ELECTRICAS | A21083100032 | New_Event | Bad Weather | Include | Include | Weather | 200 | 2021-08-31 | 30000 | keep | 0 | Aug | 2021 | 0.020433 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
ARECIBO | 2021-08-31 09:36 | 2021-08-31 11:33 | 15 | 001:57 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21083100037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2021-08-31 | 1755 | keep | 0 | Aug | 2021 | 0.0011953 | 1.0216e-05 | Sustained | FALSE | TRUE | TMED_Event | 15
ARECIBO | 2021-08-31 09:44 | 2021-08-31 12:13 | 100 | 002:29 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21083100041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2021-08-31 | 14900 | keep | 0 | Aug | 2021 | 0.010148 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
CANOVANAS | 2021-08-31 09:48 | 2021-08-31 10:39 | 75 | 000:51 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA PARARRAYO AVERRIDO | R21083100016 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 51 | 2021-08-31 | 3825 | keep | 0 | Aug | 2021 | 0.0026052 | 5.1082e-05 | Sustained | FALSE | TRUE | TMED_Event | 75
MAYAGÃœEZ | 2021-08-31 09:57 | 2021-08-31 13:13 | 15 | 003:16 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5 | M21083100046 | New_Event | Service Transformer Failure | Include | Include | Equipment | 196 | 2021-08-31 | 2940 | keep | 0 | Aug | 2021 | 0.0020024 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
BAYAMON | 2021-08-31 09:59 | 2021-08-31 10:00 | 32 | 000:01 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | B21083100009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-08-31 | 32 | keep | 0 | Aug | 2021 | 2.1795e-05 | 2.1795e-05 | Momentary | FALSE | TRUE | TMED_Event | 32
ARECIBO | 2021-08-31 10:29 | 2021-08-31 17:00 | 100 | 006:31 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21083100046 | New_Event | Wire Down | Include | Include | Equipment | 391 | 2021-08-31 | 39100 | keep | 0 | Aug | 2021 | 0.026631 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
AGUADILLA | 2021-08-31 10:31 | 2021-08-31 10:41 | 30 | 000:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | M21083000072 | New_Event | Bad Weather | Include | Include | Weather | 10 | 2021-08-31 | 300 | keep | 0 | Aug | 2021 | 0.00020433 | 2.0433e-05 | Sustained | FALSE | TRUE | TMED_Event | 30
CAGUAS | 2021-08-31 10:33 | 2021-08-31 12:41 | 55 | 002:08 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21083100037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2021-08-31 | 7040 | keep | 0 | Aug | 2021 | 0.0047949 | 3.746e-05 | Sustained | FALSE | TRUE | TMED_Event | 55
CANOVANAS | 2021-08-31 11:00 | 2021-08-31 13:24 | 10 | 002:24 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR DE 37.5KVA X 37.5KVA | R21083100023 | New_Event | Service Transformer Failure | Include | Include | Equipment | 144 | 2021-08-31 | 1440 | keep | 0 | Aug | 2021 | 0.00098078 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
CAGUAS | 2021-08-31 11:09 | 2021-08-31 17:42 | 50 | 006:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA LEVANTO CONDUCTOR | C21083100046 | New_Event | Wire Down | Include | Include | Equipment | 393 | 2021-08-31 | 19650 | keep | 0 | Aug | 2021 | 0.013384 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
HUMACAO | 2021-08-31 11:16 | 2021-08-31 15:22 | 6 | 004:06 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SECCIONALIZO POSTE SECUNDARIO PARTIDO Y PASO LA CARGA A OTRO TRANSFORMADOR | C21083100049 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 246 | 2021-08-31 | 1476 | keep | 0 | Aug | 2021 | 0.0010053 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
ARECIBO | 2021-08-31 11:21 | 2021-08-31 13:05 | 1 | 001:44 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | A21083100057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2021-08-31 | 104 | keep | 0 | Aug | 2021 | 7.0834e-05 | 6.811e-07 | Sustained | FALSE | TRUE | TMED_Event | 1
BAYAMON | 2021-08-31 11:24 | 2021-08-31 11:57 | 98 | 000:33 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 33 | 2021-08-31 | 3234 | keep | 0 | Aug | 2021 | 0.0022027 | 6.6747e-05 | Sustained | FALSE | TRUE | TMED_Event | 98
BAYAMON | 2021-08-31 11:24 | 2021-08-31 11:57 | 74 | 000:33 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 33 | 2021-08-31 | 2442 | keep | 0 | Aug | 2021 | 0.0016632 | 5.0401e-05 | Sustained | FALSE | TRUE | TMED_Event | 74
BAYAMON | 2021-08-31 11:24 | 2021-08-31 11:57 | 776 | 000:33 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 33 | 2021-08-31 | 25608 | keep | 0 | Aug | 2021 | 0.017441 | 0.00052853 | Sustained | FALSE | TRUE | TMED_Event | 776
CAGUAS | 2021-08-31 11:33 | 2021-08-31 14:40 | 80 | 003:07 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C21083100057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2021-08-31 | 14960 | keep | 0 | Aug | 2021 | 0.010189 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
BAYAMON | 2021-08-31 11:40 | 2021-08-31 14:21 | 10 | 002:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR CONECTORES | S21083100075 | New_Event | Secondary Wire Down | Include | Include | Equipment | 161 | 2021-08-31 | 1610 | keep | 0 | Aug | 2021 | 0.0010966 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
MAYAGÃœEZ | 2021-08-31 11:53 | 2021-08-31 14:21 | 50 | 002:28 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21083100070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2021-08-31 | 7400 | keep | 0 | Aug | 2021 | 0.0050401 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
BAYAMON | 2021-08-31 11:57 | 2021-08-31 16:51 | 1210 | 004:54 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 294 | 2021-08-31 | 355740 | keep | 0 | Aug | 2021 | 0.24229 | 0.00082413 | Sustained | FALSE | TRUE | TMED_Event | 1210
BAYAMON | 2021-08-31 11:57 | 2021-08-31 16:51 | 3438 | 004:54 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 294 | 2021-08-31 | 1010772 | keep | 0 | Aug | 2021 | 0.68843 | 0.0023416 | Sustained | FALSE | TRUE | TMED_Event | 3438
BAYAMON | 2021-08-31 11:57 | 2021-08-31 16:51 | 2605 | 004:54 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 294 | 2021-08-31 | 765870 | keep | 0 | Aug | 2021 | 0.52163 | 0.0017743 | Sustained | FALSE | TRUE | TMED_Event | 2605
BAYAMON | 2021-08-31 11:57 | 2021-08-31 16:51 | 73 | 004:54 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 294 | 2021-08-31 | 21462 | keep | 0 | Aug | 2021 | 0.014618 | 4.972e-05 | Sustained | FALSE | TRUE | TMED_Event | 73
BAYAMON | 2021-08-31 11:57 | 2021-08-31 16:51 | 222 | 004:54 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | S21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 294 | 2021-08-31 | 65268 | keep | 0 | Aug | 2021 | 0.044454 | 0.0001512 | Sustained | FALSE | TRUE | TMED_Event | 222
BAYAMON | 2021-08-31 11:57 | 2021-08-31 16:51 | 2466 | 004:54 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | S21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 294 | 2021-08-31 | 725004 | keep | 0 | Aug | 2021 | 0.4938 | 0.0016796 | Sustained | FALSE | TRUE | TMED_Event | 2466
BAYAMON | 2021-08-31 11:57 | 2021-08-31 16:51 | 2435 | 004:54 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | S21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 294 | 2021-08-31 | 715890 | keep | 0 | Aug | 2021 | 0.48759 | 0.0016585 | Sustained | FALSE | TRUE | TMED_Event | 2435
SAN JUAN | 2021-08-31 11:58 | 2021-09-01 10:16 | 35 | 022:18 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S21083100438 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1338 | 2021-08-31 | 46830 | keep | 0 | Aug | 2021 | 0.031896 | 2.3838e-05 | Sustained | FALSE | TRUE | TMED_Event | 35
BAYAMON | 2021-08-31 11:58 | 2021-08-31 16:48 | 3511 | 004:50 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 290 | 2021-08-31 | 1018190 | keep | 0 | Aug | 2021 | 0.69348 | 0.0023913 | Sustained | FALSE | TRUE | TMED_Event | 3511
BAYAMON | 2021-08-31 11:58 | 2021-08-31 16:48 | 1 | 004:50 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 290 | 2021-08-31 | 290 | keep | 0 | Aug | 2021 | 0.00019752 | 6.811e-07 | Sustained | FALSE | TRUE | TMED_Event | 1
BAYAMON | 2021-08-31 11:58 | 2021-08-31 16:48 | 136 | 004:50 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 290 | 2021-08-31 | 39440 | keep | 0 | Aug | 2021 | 0.026862 | 9.2629e-05 | Sustained | FALSE | TRUE | TMED_Event | 136
BAYAMON | 2021-08-31 12:03 | 2021-08-31 16:49 | 4533 | 004:46 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 286 | 2021-08-31 | 1296438 | keep | 0 | Aug | 2021 | 0.883 | 0.0030874 | Sustained | FALSE | TRUE | TMED_Event | 4533
BAYAMON | 2021-08-31 12:03 | 2021-08-31 16:49 | 911 | 004:46 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 286 | 2021-08-31 | 260546 | keep | 0 | Aug | 2021 | 0.17746 | 0.00062048 | Sustained | FALSE | TRUE | TMED_Event | 911
BAYAMON | 2021-08-31 12:03 | 2021-08-31 16:49 | 4431 | 004:46 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 286 | 2021-08-31 | 1267266 | keep | 0 | Aug | 2021 | 0.86313 | 0.0030179 | Sustained | FALSE | TRUE | TMED_Event | 4431
BAYAMON | 2021-08-31 12:03 | 2021-08-31 16:49 | 1362 | 004:46 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 286 | 2021-08-31 | 389532 | keep | 0 | Aug | 2021 | 0.26531 | 0.00092765 | Sustained | FALSE | TRUE | TMED_Event | 1362
BAYAMON | 2021-08-31 12:03 | 2021-08-31 16:49 | 341 | 004:46 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 286 | 2021-08-31 | 97526 | keep | 0 | Aug | 2021 | 0.066425 | 0.00023225 | Sustained | FALSE | TRUE | TMED_Event | 341
BAYAMON | 2021-08-31 12:03 | 2021-08-31 16:40 | 3597 | 004:37 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 277 | 2021-08-31 | 996369 | keep | 0 | Aug | 2021 | 0.67862 | 0.0024499 | Sustained | FALSE | TRUE | TMED_Event | 3597
BAYAMON | 2021-08-31 12:03 | 2021-08-31 16:40 | 492 | 004:37 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 277 | 2021-08-31 | 136284 | keep | 0 | Aug | 2021 | 0.092822 | 0.0003351 | Sustained | FALSE | TRUE | TMED_Event | 492
BAYAMON | 2021-08-31 12:03 | 2021-08-31 16:40 | 4028 | 004:37 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 277 | 2021-08-31 | 1115756 | keep | 0 | Aug | 2021 | 0.75994 | 0.0027435 | Sustained | FALSE | TRUE | TMED_Event | 4028
BAYAMON | 2021-08-31 12:03 | 2021-08-31 16:40 | 2617 | 004:37 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 277 | 2021-08-31 | 724909 | keep | 0 | Aug | 2021 | 0.49373 | 0.0017824 | Sustained | FALSE | TRUE | TMED_Event | 2617
BAYAMON | 2021-08-31 12:04 | 2021-08-31 16:41 | 1139 | 004:37 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | S21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 277 | 2021-08-31 | 315503 | keep | 0 | Aug | 2021 | 0.21489 | 0.00077577 | Sustained | FALSE | TRUE | TMED_Event | 1139
BAYAMON | 2021-08-31 12:04 | 2021-08-31 16:41 | 2956 | 004:37 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | S21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 277 | 2021-08-31 | 818812 | keep | 0 | Aug | 2021 | 0.55769 | 0.0020133 | Sustained | FALSE | TRUE | TMED_Event | 2956
BAYAMON | 2021-08-31 12:04 | 2021-08-31 16:41 | 4456 | 004:37 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | S21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 277 | 2021-08-31 | 1234312 | keep | 0 | Aug | 2021 | 0.84068 | 0.003035 | Sustained | FALSE | TRUE | TMED_Event | 4456
BAYAMON | 2021-08-31 12:05 | 2021-08-31 16:58 | 2402 | 004:53 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 LLEVA EL 1720-08 | S21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 293 | 2021-08-31 | 703786 | keep | 0 | Aug | 2021 | 0.47935 | 0.001636 | Sustained | FALSE | TRUE | TMED_Event | 2402
BAYAMON | 2021-08-31 12:05 | 2021-08-31 16:58 | 1533 | 004:53 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | S21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 293 | 2021-08-31 | 449169 | keep | 0 | Aug | 2021 | 0.30593 | 0.0010441 | Sustained | FALSE | TRUE | TMED_Event | 1533
BAYAMON | 2021-08-31 12:05 | 2021-08-31 16:58 | 2364 | 004:53 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | S21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 293 | 2021-08-31 | 692652 | keep | 0 | Aug | 2021 | 0.47176 | 0.0016101 | Sustained | FALSE | TRUE | TMED_Event | 2364
HUMACAO | 2021-08-31 12:12 | 2021-08-31 21:03 | 200 | 008:51 | P | ANIMAL U OBJETO EXTRAÃ‘O | 3 X 140 EN RISER PEDAZO DE METAL CRUZANDO LA BARRA EN EL SU 2B2 | C21083100064 | New_Event |  |  | Include | Wildlife | 531 | 2021-08-31 | 106200 | keep | 0 | Aug | 2021 | 0.072332 | 0.00013622 | Sustained | FALSE | FALSE | TMED_Event | 200
ARECIBO | 2021-08-31 12:13 | 2021-08-31 14:26 | 2231 | 002:13 | S | RELEVO DE CARGA POR CONTINGENCIA | SE ABRIO LINEA 14700 POR SOBRE CARGA 50300 | A21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 133 | 2021-08-31 | 296723 | keep | 0 | Aug | 2021 | 0.2021 | 0.0015195 | Sustained | FALSE | TRUE | TMED_Event | 2231
ARECIBO | 2021-08-31 12:13 | 2021-08-31 14:26 | 1923 | 002:13 | S | RELEVO DE CARGA POR CONTINGENCIA | SE ABRIO LINEA 14700 POR SOBRE CARGA 50300 | A21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 133 | 2021-08-31 | 255759 | keep | 0 | Aug | 2021 | 0.1742 | 0.0013097 | Sustained | FALSE | TRUE | TMED_Event | 1923
ARECIBO | 2021-08-31 12:13 | 2021-08-31 14:26 | 1066 | 002:13 | S | RELEVO DE CARGA POR CONTINGENCIA | SE ABRIO LINEA 14700 POR SOBRE CARGA 50300 | A21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 133 | 2021-08-31 | 141778 | keep | 0 | Aug | 2021 | 0.096564 | 0.00072605 | Sustained | FALSE | TRUE | TMED_Event | 1066
ARECIBO | 2021-08-31 12:13 | 2021-08-31 14:26 | 141 | 002:13 | S | RELEVO DE CARGA POR CONTINGENCIA | SE ABRIO LINEA 14700 POR SOBRE CARGA 50300 | A21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 133 | 2021-08-31 | 18753 | keep | 0 | Aug | 2021 | 0.012773 | 9.6034e-05 | Sustained | FALSE | TRUE | TMED_Event | 141
ARECIBO | 2021-08-31 12:13 | 2021-08-31 14:26 | 2107 | 002:13 | S | RELEVO DE CARGA POR CONTINGENCIA | SE ABRIO LINEA 14700 POR SOBRE CARGA 50300 | A21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 133 | 2021-08-31 | 280231 | keep | 0 | Aug | 2021 | 0.19086 | 0.0014351 | Sustained | FALSE | TRUE | TMED_Event | 2107
ARECIBO | 2021-08-31 12:13 | 2021-08-31 14:26 | 308 | 002:13 | S | RELEVO DE CARGA POR CONTINGENCIA | SE ABRIO LINEA 14700 POR SOBRE CARGA 50300 | A21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 133 | 2021-08-31 | 40964 | keep | 0 | Aug | 2021 | 0.0279 | 0.00020978 | Sustained | FALSE | TRUE | TMED_Event | 308
ARECIBO | 2021-08-31 12:13 | 2021-08-31 14:26 | 2697 | 002:13 | S | RELEVO DE CARGA POR CONTINGENCIA | SE ABRIO LINEA 14700 POR SOBRE CARGA 50300 | A21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 133 | 2021-08-31 | 358701 | keep | 0 | Aug | 2021 | 0.24431 | 0.0018369 | Sustained | FALSE | TRUE | TMED_Event | 2697
ARECIBO | 2021-08-31 12:13 | 2021-08-31 14:26 | 67 | 002:13 | S | RELEVO DE CARGA POR CONTINGENCIA | SE ABRIO LINEA 14700 POR SOBRE CARGA 50300 | A21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 133 | 2021-08-31 | 8911 | keep | 0 | Aug | 2021 | 0.0060692 | 4.5633e-05 | Sustained | FALSE | TRUE | TMED_Event | 67
VEGA BAJA | 2021-08-31 12:28 | 2021-08-31 16:20 | 1526 | 003:52 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 232 | 2021-08-31 | 354032 | keep | 0 | Aug | 2021 | 0.24113 | 0.0010394 | Sustained | FALSE | TRUE | TMED_Event | 1526
VEGA BAJA | 2021-08-31 12:28 | 2021-08-31 16:20 | 308 | 003:52 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 232 | 2021-08-31 | 71456 | keep | 0 | Aug | 2021 | 0.048668 | 0.00020978 | Sustained | FALSE | TRUE | TMED_Event | 308
VEGA BAJA | 2021-08-31 12:28 | 2021-08-31 16:20 | 1397 | 003:52 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 232 | 2021-08-31 | 324104 | keep | 0 | Aug | 2021 | 0.22075 | 0.00095149 | Sustained | FALSE | TRUE | TMED_Event | 1397
VEGA BAJA | 2021-08-31 12:28 | 2021-08-31 16:20 | 2926 | 003:52 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 232 | 2021-08-31 | 678832 | keep | 0 | Aug | 2021 | 0.46235 | 0.0019929 | Sustained | FALSE | TRUE | TMED_Event | 2926
VEGA BAJA | 2021-08-31 12:28 | 2021-08-31 16:20 | 27 | 003:52 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 232 | 2021-08-31 | 6264 | keep | 0 | Aug | 2021 | 0.0042664 | 1.839e-05 | Sustained | FALSE | TRUE | TMED_Event | 27
VEGA BAJA | 2021-08-31 12:28 | 2021-08-31 16:20 | 603 | 003:52 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 232 | 2021-08-31 | 139896 | keep | 0 | Aug | 2021 | 0.095283 | 0.0004107 | Sustained | FALSE | TRUE | TMED_Event | 603
VEGA BAJA | 2021-08-31 12:28 | 2021-08-31 16:20 | 6 | 003:52 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 232 | 2021-08-31 | 1392 | keep | 0 | Aug | 2021 | 0.00094808 | 4.0866e-06 | Sustained | FALSE | TRUE | TMED_Event | 6
VEGA BAJA | 2021-08-31 12:28 | 2021-08-31 16:20 | 325 | 003:52 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 232 | 2021-08-31 | 75400 | keep | 0 | Aug | 2021 | 0.051355 | 0.00022136 | Sustained | FALSE | TRUE | TMED_Event | 325
VEGA BAJA | 2021-08-31 12:28 | 2021-08-31 16:20 | 172 | 003:52 | S | RELEVO DE CARGA POR CONTINGENCIA | RELEVO DE CARGA POR CONTINGENCIA POR SOBRECARGA EN LINEA DE TRANSMISION 50300 | B21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 232 | 2021-08-31 | 39904 | keep | 0 | Aug | 2021 | 0.027178 | 0.00011715 | Sustained | FALSE | TRUE | TMED_Event | 172
SAN JUAN | 2021-08-31 12:29 | 2021-08-31 17:02 | 36 | 004:33 | S | RELEVO DE CARGA POR CONTINGENCIA | SOBRECARGA LINEA 50300 | S21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 273 | 2021-08-31 | 9828 | keep | 0 | Aug | 2021 | 0.0066938 | 2.4519e-05 | Sustained | FALSE | TRUE | TMED_Event | 36
SAN JUAN | 2021-08-31 12:29 | 2021-08-31 17:02 | 3718 | 004:33 | S | RELEVO DE CARGA POR CONTINGENCIA | SOBRECARGA LINEA 50300 | S21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 273 | 2021-08-31 | 1015014 | keep | 0 | Aug | 2021 | 0.69132 | 0.0025323 | Sustained | FALSE | TRUE | TMED_Event | 3718
SAN JUAN | 2021-08-31 12:29 | 2021-08-31 17:02 | 1073 | 004:33 | S | RELEVO DE CARGA POR CONTINGENCIA | SOBRECARGA LINEA 50300 | S21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 273 | 2021-08-31 | 292929 | keep | 0 | Aug | 2021 | 0.19951 | 0.00073082 | Sustained | FALSE | TRUE | TMED_Event | 1073
SAN JUAN | 2021-08-31 12:29 | 2021-08-31 17:02 | 172 | 004:33 | S | RELEVO DE CARGA POR CONTINGENCIA | SOBRECARGA LINEA 50300 | R21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 273 | 2021-08-31 | 46956 | keep | 0 | Aug | 2021 | 0.031982 | 0.00011715 | Sustained | FALSE | TRUE | TMED_Event | 172
SAN JUAN | 2021-08-31 12:29 | 2021-08-31 17:02 | 1615 | 004:33 | S | RELEVO DE CARGA POR CONTINGENCIA | SOBRECARGA LINEA 50200 | R21083100000 | New_Event | Load Shed (Contingency) | Include | Include | Power Supply | 273 | 2021-08-31 | 440895 | keep | 0 | Aug | 2021 | 0.30029 | 0.0011 | Sustained | FALSE | TRUE | TMED_Event | 1615
AGUADILLA | 2021-08-31 13:15 | 2021-09-02 19:00 | 20 | 053:45 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | M21083100079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3225 | 2021-08-31 | 64500 | keep | 0 | Aug | 2021 | 0.043931 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
ARECIBO | 2021-08-31 13:15 | 2021-08-31 14:30 | 1 | 001:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21083100026 | New_Event | Secondary Wire Down | Include | Include | Equipment | 75 | 2021-08-31 | 75 | keep | 0 | Aug | 2021 | 5.1082e-05 | 6.811e-07 | Sustained | FALSE | TRUE | TMED_Event | 1
MAYAGÃœEZ | 2021-08-31 13:19 | 2021-08-31 18:15 | 200 | 004:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REMPLAZO PORTA FUSIBLE AVERIADO | M21083100081 | New_Event | Cutout Failure | Include | Include | Equipment | 296 | 2021-08-31 | 59200 | keep | 0 | Aug | 2021 | 0.040321 | 0.00013622 | Sustained | FALSE | TRUE | TMED_Event | 200
CAGUAS | 2021-08-31 13:25 | 2021-08-31 18:27 | 40 | 005:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21083100076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 302 | 2021-08-31 | 12080 | keep | 0 | Aug | 2021 | 0.0082276 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
ARECIBO | 2021-08-31 13:30 | 2021-08-31 14:20 | 15 | 000:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A21083100014 | New_Event | Wire Down | Include | Include | Equipment | 50 | 2021-08-31 | 750 | keep | 0 | Aug | 2021 | 0.00051082 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
GUAYAMA | 2021-08-31 13:32 | 2021-08-31 15:53 | 1 | 002:21 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER NO SE REPORTO CAUSA | P21083100033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 141 | 2021-08-31 | 141 | keep | 0 | Aug | 2021 | 9.6034e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2021-08-31 13:42 | 2021-08-31 13:43 | 1420 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 1530-06 | S21083100176 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-31 | 1420 | keep | 0 | Aug | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | TMED_Event | 1420
BAYAMON | 2021-08-31 13:42 | 2021-08-31 13:43 | 437 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA EL 1526-02 | S21083100176 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-31 | 437 | keep | 0 | Aug | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | TMED_Event | 437
CAGUAS | 2021-08-31 13:42 | 2021-08-31 13:43 | 1702 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21083100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-31 | 1702 | keep | 0 | Aug | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | TMED_Event | 1702
CANOVANAS | 2021-08-31 13:44 | 2021-08-31 16:32 | 7 | 002:48 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA X 50 KVA Y CAJA | R21083100042 | New_Event | Service Transformer Failure | Include | Include | Equipment | 168 | 2021-08-31 | 1176 | keep | 0 | Aug | 2021 | 0.00080097 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
ARECIBO | 2021-08-31 13:45 | 2021-08-31 15:16 | 12 | 001:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A21083100059 | New_Event | Cutout Failure | Include | Include | Equipment | 91 | 2021-08-31 | 1092 | keep | 0 | Aug | 2021 | 0.00074376 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
CAGUAS | 2021-08-31 13:47 | 2021-08-31 15:24 | 1 | 001:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | REPARO BAJANTE SECUNDARIO | C21083100080 | New_Event | Secondary Wire Down | Include | Include | Equipment | 97 | 2021-08-31 | 97 | keep | 0 | Aug | 2021 | 6.6066e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
UTUADO | 2021-08-31 13:47 | 2021-09-01 13:10 | 1 | 023:23 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE DE 900 AMP MARCA CHANCE | A21083100104 | New_Event | Switch Failure | Include | Include | Equipment | 1403 | 2021-08-31 | 1403 | keep | 0 | Aug | 2021 | 0.00095558 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
PONCE | 2021-08-31 13:50 | 2021-08-31 19:30 | 100 | 005:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA Y SE LEVANTO ALAMBRE PRIMARIO | P21083100035 | New_Event | Wire Down | Include | Include | Equipment | 340 | 2021-08-31 | 34000 | keep | 0 | Aug | 2021 | 0.023157 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
UTUADO | 2021-08-31 13:54 | 2021-08-31 18:05 | 10 | 004:11 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21083100107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2021-08-31 | 2510 | keep | 0 | Aug | 2021 | 0.0017095 | 6.811e-06 | Sustained | FALSE | TRUE | TMED_Event | 10
CAGUAS | 2021-08-31 14:02 | 2021-08-31 21:33 | 100 | 007:31 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21083100084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 451 | 2021-08-31 | 45100 | keep | 0 | Aug | 2021 | 0.030717 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
CAGUAS | 2021-08-31 14:09 | 2021-08-31 16:40 | 40 | 002:31 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21083100008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2021-08-31 | 6040 | keep | 0 | Aug | 2021 | 0.0041138 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
MAYAGÃœEZ | 2021-08-31 14:13 | 2021-08-31 19:00 | 100 | 004:47 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21083100100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 287 | 2021-08-31 | 28700 | keep | 0 | Aug | 2021 | 0.019547 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
AGUADILLA | 2021-08-31 14:16 | 2021-08-31 17:30 | 1 | 003:14 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M21083100090 | New_Event | Wire Down | Include | Include | Equipment | 194 | 2021-08-31 | 194 | keep | 0 | Aug | 2021 | 0.00013213 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2021-08-31 14:18 | 2021-08-31 15:12 | 15 | 000:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR CONECTORES WR-5920646 | S21083100000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 54 | 2021-08-31 | 810 | keep | 0 | Aug | 2021 | 0.00055169 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
SAN JUAN | 2021-08-31 14:21 | 2021-08-31 14:26 | 570 | 000:05 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA ATOMATICO POR PROBLEMAS DE GENEACION LLEVA EL 1328-05 | S21083100000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 5 | 2021-08-31 | 2850 | keep | 0 | Aug | 2021 | 0.0019411 | 0.00038822 | Momentary | FALSE | FALSE | TMED_Event | 570
SAN JUAN | 2021-08-31 14:21 | 2021-08-31 14:26 | 155 | 000:05 | T | RELEVO DE CARGA AUTOMATICO | RELEVO DE CARGA ATOMATICO POR PROBLEMAS DE GENEACION CARGA POR EL 1328-02 | S21083100000 | New_Event | Automatic Load Shed | Exclude | Exclude | Power supply | 5 | 2021-08-31 | 775 | keep | 0 | Aug | 2021 | 0.00052785 | 0.00010557 | Momentary | FALSE | FALSE | TMED_Event | 155
GUAYAMA | 2021-08-31 14:22 | 2021-08-31 18:00 | 50 | 003:38 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN TRANSFORMADOR Y 1 X 40 EN CORTE DE LINEA POR CONTACTO DE AVE | P21083100043 | New_Event |  |  | Include | Wildlife | 218 | 2021-08-31 | 10900 | keep | 0 | Aug | 2021 | 0.0074239 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
BAYAMON | 2021-08-31 14:26 | 2021-08-31 18:19 | 10 | 003:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR CONECTORES | S21083100075 | Partial_restoration | Secondary Wire Down | Include | Include | Equipment | 233 | 2021-08-31 | 2330 | keep | 0 | Aug | 2021 | 0.001587 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
BARRANQUITAS | 2021-08-31 14:49 | 2021-08-31 17:11 | 1604 | 002:22 | T | DESGANCHE | SE SECCIONALIZO EL ALIMENTADOR | C21083100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2021-08-31 | 227768 | keep | 0 | Aug | 2021 | 0.15513 | 0.0010925 | Sustained | FALSE | FALSE | TMED_Event | 1604
MAYAGÃœEZ | 2021-08-31 15:00 | 2021-08-31 17:15 | 5 | 002:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M21083100124 | New_Event | Wire Down | Include | Include | Equipment | 135 | 2021-08-31 | 675 | keep | 0 | Aug | 2021 | 0.00045974 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
SAN JUAN | 2021-08-31 15:06 | 2021-08-31 16:52 | 6 | 001:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA CONECTAR SECUNDARIA | R21083100077 | New_Event | Secondary Wire Down | Include | Include | Equipment | 106 | 2021-08-31 | 636 | keep | 0 | Aug | 2021 | 0.00043318 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
BARRANQUITAS | 2021-08-31 15:06 | 2021-08-31 17:32 | 90 | 002:26 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C21083100105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2021-08-31 | 13140 | keep | 0 | Aug | 2021 | 0.0089496 | 6.1299e-05 | Sustained | FALSE | TRUE | TMED_Event | 90
CAGUAS | 2021-08-31 15:10 | 2021-08-31 17:47 | 436 | 002:37 | P | DESGANCHE | RETIRO RAMAS DE LAS LINEAS | C21083100111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2021-08-31 | 68452 | keep | 0 | Aug | 2021 | 0.046622 | 0.00029696 | Sustained | FALSE | TRUE | TMED_Event | 436
CAGUAS | 2021-08-31 15:12 | 2021-08-31 15:13 | 1261 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21083100108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-31 | 1261 | keep | 0 | Aug | 2021 | 0.00085886 | 0.00085886 | Momentary | FALSE | FALSE | TMED_Event | 1261
MAYAGÃœEZ | 2021-08-31 15:14 | 2021-08-31 15:15 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6007-05 | M21083100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-31 | 393 | keep | 0 | Aug | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | TMED_Event | 393
MAYAGÃœEZ | 2021-08-31 15:14 | 2021-08-31 15:15 | 4 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6007-05 | M21083100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-31 | 4 | keep | 0 | Aug | 2021 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | TMED_Event | 4
BAYAMON | 2021-08-31 15:14 | 2021-08-31 16:56 | 100 | 001:42 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 40 EN CORTE DE LINEAS | B21083100304 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 102 | 2021-08-31 | 10200 | keep | 0 | Aug | 2021 | 0.0069472 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
CAGUAS | 2021-08-31 15:20 | 2021-08-31 16:47 | 50 | 001:27 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21083100113 | New_Event | Bad Weather | Include | Include | Weather | 87 | 2021-08-31 | 4350 | keep | 0 | Aug | 2021 | 0.0029628 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
CAGUAS | 2021-08-31 15:37 | 2021-09-01 18:20 | 19 | 026:43 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR | C21083100127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1603 | 2021-08-31 | 30457 | keep | 0 | Aug | 2021 | 0.020744 | 1.2941e-05 | Sustained | FALSE | FALSE | TMED_Event | 19
MAYAGÃœEZ | 2021-08-31 15:47 | 2021-08-31 15:48 | 1417 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21083100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-31 | 1417 | keep | 0 | Aug | 2021 | 0.00096511 | 0.00096511 | Momentary | FALSE | FALSE | TMED_Event | 1417
PONCE | 2021-08-31 15:49 | 2021-08-31 18:06 | 80 | 002:17 | P | MAL TIEMPO/RAYOS/WET ASH | 1 POR 80 EN CORTE DE LINEA POR FUERTES VIENTOS | P21083100063 | New_Event | Bad Weather | Include | Include | Weather | 137 | 2021-08-31 | 10960 | keep | 0 | Aug | 2021 | 0.0074648 | 5.4488e-05 | Sustained | FALSE | TRUE | TMED_Event | 80
BAYAMON | 2021-08-31 16:02 | 2021-08-31 17:50 | 12 | 001:48 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | B21083100336 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 108 | 2021-08-31 | 1296 | keep | 0 | Aug | 2021 | 0.0008827 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
CAGUAS | 2021-08-31 16:04 | 2021-08-31 16:05 | 1606 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21083100145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-31 | 1606 | keep | 0 | Aug | 2021 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | TMED_Event | 1606
BAYAMON | 2021-08-31 16:05 | 2021-08-31 17:24 | 25 | 001:19 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVISIONAL HACIA T-37 DE PROVISIONAL EXISTENTE | B21082900062 | New_Event | UG Cable Fault | Include | Include | Equipment | 79 | 2021-08-31 | 1975 | keep | 0 | Aug | 2021 | 0.0013452 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
YAUCO | 2021-08-31 16:25 | 2021-08-31 19:15 | 2011 | 002:50 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE HIZO DESGANCHE Y SE REEMPLAZO AISALDOR | P21083100047 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 170 | 2021-08-31 | 341870 | keep | 0 | Aug | 2021 | 0.23285 | 0.0013697 | Sustained | FALSE | FALSE | TMED_Event | 2011
MAYAGÃœEZ | 2021-08-31 16:48 | 2021-08-31 16:49 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6007-05 | M21083100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-31 | 393 | keep | 0 | Aug | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | TMED_Event | 393
MAYAGÃœEZ | 2021-08-31 16:48 | 2021-08-31 16:49 | 4 | 000:01 | T | NO SE REPORTO CAUSA | CARGA POR 6007-04 | M21083100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-31 | 4 | keep | 0 | Aug | 2021 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | TMED_Event | 4
VEGA BAJA | 2021-08-31 16:52 | 2021-08-31 16:53 | 3387 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21083100359 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-31 | 3387 | keep | 0 | Aug | 2021 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | TMED_Event | 3387
SAN JUAN | 2021-08-31 16:56 | 2021-08-31 20:05 | 100 | 003:09 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21083100123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 189 | 2021-08-31 | 18900 | keep | 0 | Aug | 2021 | 0.012873 | 6.811e-05 | Sustained | FALSE | TRUE | TMED_Event | 100
CANOVANAS | 2021-08-31 17:05 | 2021-08-31 17:35 | 20 | 000:30 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 20 EN CORTE DE LINEA Y 1 X 10 EN CORTE DE LINEA CRUCE POR REPTIL | R21083100126 | New_Event |  |  | Include | Wildlife | 30 | 2021-08-31 | 600 | keep | 0 | Aug | 2021 | 0.00040866 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
MAYAGÃœEZ | 2021-08-31 17:09 | 2021-08-31 21:48 | 50 | 004:39 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21083100070 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 279 | 2021-08-31 | 13950 | keep | 0 | Aug | 2021 | 0.0095013 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
BARRANQUITAS | 2021-08-31 17:11 | 2021-08-31 18:14 | 600 | 001:03 | P | DESGANCHE | 3 X 100 EN CORTE DE LINEA | C21083100106 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 63 | 2021-08-31 | 37800 | keep | 0 | Aug | 2021 | 0.025745 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
MAYAGÃœEZ | 2021-08-31 17:26 | 2021-08-31 17:27 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6007-05 | M21083100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-31 | 393 | keep | 0 | Aug | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | TMED_Event | 393
MAYAGÃœEZ | 2021-08-31 17:26 | 2021-08-31 17:27 | 4 | 000:01 | T | NO SE REPORTO CAUSA | CARGA POR 6007-04 | M21083100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-31 | 4 | keep | 0 | Aug | 2021 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | TMED_Event | 4
MAYAGÃœEZ | 2021-08-31 17:41 | 2021-08-31 17:42 | 393 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6007-05 | M21083100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-31 | 393 | keep | 0 | Aug | 2021 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | TMED_Event | 393
MAYAGÃœEZ | 2021-08-31 17:41 | 2021-08-31 17:42 | 4 | 000:01 | T | NO SE REPORTO CAUSA | CARGA POR 6007-04 | M21083100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-31 | 4 | keep | 0 | Aug | 2021 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | TMED_Event | 4
CAGUAS | 2021-08-31 17:49 | 2021-08-31 19:41 | 4369 | 001:52 | T | PROTECCION DEFECTUOSA | 1 X 125 SLOW SPEED FUSIBLE DE LA ALTA DE LA CAPACIDAD INCORRECTA TENIA 1 DE 65AMP SLOW SPEED | C21083100242 | New_Event | Protection Miscoordination | Include | Include | Other | 112 | 2021-08-31 | 489328 | keep | 0 | Aug | 2021 | 0.33328 | 0.0029757 | Sustained | FALSE | FALSE | TMED_Event | 4369
CAGUAS | 2021-08-31 17:49 | 2021-08-31 19:41 | 676 | 001:52 | T | PROTECCION DEFECTUOSA | 1 X 125 SLOW SPEED FUSIBLE DE LA ALTA DE LA CAPACIDAD INCORRECTA TENIA 1 DE 65AMP SLOW SPEED | C21083100242 | New_Event | Protection Miscoordination | Include | Include | Other | 112 | 2021-08-31 | 75712 | keep | 0 | Aug | 2021 | 0.051567 | 0.00046042 | Sustained | FALSE | FALSE | TMED_Event | 676
CAGUAS | 2021-08-31 17:49 | 2021-08-31 19:42 | 676 | 001:53 | T | PROTECCION DEFECTUOSA | 1 X 125 SLOW SPEED FUSIBLE DE LA ALTA DE LA CAPACIDAD INCORRECTA TENIA 1 DE 65AMP SLOW SPEED | C21083100242 | New_Event | Protection Miscoordination | Include | Include | Other | 113 | 2021-08-31 | 76388 | keep | 0 | Aug | 2021 | 0.052028 | 0.00046042 | Sustained | FALSE | FALSE | TMED_Event | 676
CAGUAS | 2021-08-31 17:49 | 2021-08-31 19:42 | 725 | 001:53 | T | PROTECCION DEFECTUOSA | 1 X 125 SLOW SPEED FUSIBLE DE LA ALTA DE LA CAPACIDAD INCORRECTA TENIA 1 DE 65AMP SLOW SPEED CARGA POR 3010-03 | C21083100242 | New_Event | Protection Miscoordination | Include | Include | Other | 113 | 2021-08-31 | 81925 | keep | 0 | Aug | 2021 | 0.055799 | 0.00049379 | Sustained | FALSE | FALSE | TMED_Event | 725
CANOVANAS | 2021-08-31 17:51 | 2021-08-31 20:09 | 50 | 002:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR REPTIL | R21083100135 | New_Event |  |  | Include | Wildlife | 138 | 2021-08-31 | 6900 | keep | 0 | Aug | 2021 | 0.0046996 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
CAGUAS | 2021-08-31 17:59 | 2021-08-31 19:11 | 50 | 001:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C21083100113 | Partial_restoration | Bad Weather | Include | Include | Weather | 72 | 2021-08-31 | 3600 | keep | 0 | Aug | 2021 | 0.0024519 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
SAN JUAN | 2021-08-31 18:00 | 2021-08-31 23:01 | 50 | 005:01 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S21083100357 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 301 | 2021-08-31 | 15050 | keep | 0 | Aug | 2021 | 0.01025 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
ARECIBO | 2021-08-31 18:01 | 2021-08-31 19:00 | 100 | 000:59 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21083100046 | Partial_restoration | Wire Down | Include | Include | Equipment | 59 | 2021-08-31 | 5900 | keep | 0 | Aug | 2021 | 0.0040185 | 0 | Sustained | FALSE | TRUE | TMED_Event | 0
ARECIBO | 2021-08-31 18:01 | 2021-08-31 20:04 | 3 | 002:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO PROTAFUSIBLE AVERIADO | A21083100203 | New_Event | Cutout Failure | Include | Include | Equipment | 123 | 2021-08-31 | 369 | keep | 0 | Aug | 2021 | 0.00025132 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
ARECIBO | 2021-08-31 18:04 | 2021-08-31 19:45 | 15 | 001:41 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21083100168 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2021-08-31 | 1515 | keep | 0 | Aug | 2021 | 0.0010319 | 1.0216e-05 | Sustained | FALSE | TRUE | TMED_Event | 15
BAYAMON | 2021-08-31 18:09 | 2021-08-31 18:10 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21083100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-31 | 2605 | keep | 0 | Aug | 2021 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | TMED_Event | 2605
BAYAMON | 2021-08-31 18:09 | 2021-08-31 18:10 | 73 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21083100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-31 | 73 | keep | 0 | Aug | 2021 | 4.972e-05 | 4.972e-05 | Momentary | FALSE | FALSE | TMED_Event | 73
CAGUAS | 2021-08-31 18:14 | 2021-09-01 12:16 | 90 | 018:02 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR IGUANA | C21083100250 | New_Event |  |  | Include | Wildlife | 1082 | 2021-08-31 | 97380 | keep | 0 | Aug | 2021 | 0.066325 | 6.1299e-05 | Sustained | FALSE | TRUE | TMED_Event | 90
VEGA BAJA | 2021-08-31 18:20 | 2021-08-31 20:16 | 8 | 001:56 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21083000150 | New_Event | Secondary Wire Down | Include | Include | Equipment | 116 | 2021-08-31 | 928 | keep | 0 | Aug | 2021 | 0.00063206 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
MAYAGÃœEZ | 2021-08-31 18:30 | 2021-08-31 21:35 | 8 | 003:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA DE TRANSFORMADOR AVERIADA | M21083100207 | New_Event | Cutout Failure | Include | Include | Equipment | 185 | 2021-08-31 | 1480 | keep | 0 | Aug | 2021 | 0.001008 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
UTUADO | 2021-08-31 18:30 | 2021-08-31 21:19 | 50 | 002:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21083100195 | New_Event | Bad Weather | Include | Include | Weather | 169 | 2021-08-31 | 8450 | keep | 0 | Aug | 2021 | 0.0057553 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
UTUADO | 2021-08-31 18:39 | 2021-08-31 20:20 | 25 | 001:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21083100196 | New_Event | Bad Weather | Include | Include | Weather | 101 | 2021-08-31 | 2525 | keep | 0 | Aug | 2021 | 0.0017198 | 1.7027e-05 | Sustained | FALSE | TRUE | TMED_Event | 25
CANOVANAS | 2021-08-31 18:50 | 2021-08-31 21:04 | 4 | 002:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR SE RETIRO AVE MUERTA | R21083100146 | New_Event |  |  | Include | Wildlife | 134 | 2021-08-31 | 536 | keep | 0 | Aug | 2021 | 0.00036507 | 2.7244e-06 | Sustained | FALSE | FALSE | TMED_Event | 4
CAGUAS | 2021-08-31 18:53 | 2021-09-01 11:05 | 60 | 016:12 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR | C21083100263 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 972 | 2021-08-31 | 58320 | keep | 0 | Aug | 2021 | 0.039721 | 4.0866e-05 | Sustained | FALSE | TRUE | TMED_Event | 60
CANOVANAS | 2021-08-31 18:54 | 2021-09-01 10:19 | 55 | 015:25 | P | DESGANCHE | 1 X 40 EN PROVISIONAL AEREO | R21083100147 | New_Event | Vegetation Contact | Include | Include | Vegetation | 925 | 2021-08-31 | 50875 | keep | 0 | Aug | 2021 | 0.034651 | 3.746e-05 | Sustained | FALSE | FALSE | TMED_Event | 55
ARECIBO | 2021-08-31 19:15 | 2021-08-31 20:30 | 1 | 001:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A21083100200 | New_Event | Wire Down | Include | Include | Equipment | 75 | 2021-08-31 | 75 | keep | 0 | Aug | 2021 | 5.1082e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
CAGUAS | 2021-08-31 19:18 | 2021-09-01 21:05 | 65 | 025:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA | C21083100276 | New_Event | Cutout Failure | Include | Include | Equipment | 1547 | 2021-08-31 | 100555 | keep | 0 | Aug | 2021 | 0.068488 | 4.4271e-05 | Sustained | FALSE | TRUE | TMED_Event | 65
AGUADILLA | 2021-08-31 19:19 | 2021-08-31 22:40 | 150 | 003:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO BAJANTE ZAFADO | M21083100180 | New_Event | Wire Down | Include | Include | Equipment | 201 | 2021-08-31 | 30150 | keep | 0 | Aug | 2021 | 0.020535 | 0.00010216 | Sustained | FALSE | TRUE | TMED_Event | 150
PONCE | 2021-08-31 19:30 | 2021-08-31 19:31 | 2689 | 000:01 | T | NO SE REPORTO CAUSA | SE CERRO MANUAL | P21083100125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-31 | 2689 | keep | 0 | Aug | 2021 | 0.0018315 | 0.0018315 | Momentary | FALSE | FALSE | TMED_Event | 2689
UTUADO | 2021-08-31 19:31 | 2021-08-31 22:55 | 20 | 003:24 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A21083100202 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2021-08-31 | 4080 | keep | 0 | Aug | 2021 | 0.0027789 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
SAN JUAN | 2021-08-31 19:37 | 2021-09-01 11:50 | 40 | 016:13 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21083100077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 973 | 2021-08-31 | 38920 | keep | 0 | Aug | 2021 | 0.026508 | 2.7244e-05 | Sustained | FALSE | TRUE | TMED_Event | 40
ARECIBO | 2021-08-31 20:22 | 2021-08-31 20:34 | 15 | 000:12 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA CRUZADA | A21083100192 | New_Event | Secondary Wire Down | Include | Include | Equipment | 12 | 2021-08-31 | 180 | keep | 0 | Aug | 2021 | 0.0001226 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
VEGA BAJA | 2021-08-31 20:39 | 2021-08-31 20:40 | 1397 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21083100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-31 | 1397 | keep | 0 | Aug | 2021 | 0.00095149 | 0.00095149 | Momentary | FALSE | FALSE | TMED_Event | 1397
PONCE | 2021-08-31 20:57 | 2021-08-31 20:58 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210831000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-31 | 3718 | keep | 0 | Aug | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | TMED_Event | 3718
PONCE | 2021-08-31 21:56 | 2021-09-01 10:02 | 50 | 012:06 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | P21083100155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 726 | 2021-08-31 | 36300 | keep | 0 | Aug | 2021 | 0.024724 | 3.4055e-05 | Sustained | FALSE | TRUE | TMED_Event | 50
VEGA BAJA | 2021-08-31 22:01 | 2021-09-01 10:21 | 20 | 012:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA PRINCIPAL Y 1 X 30 EN CORTE DE LINEA INTERMEDIO | B21083100435 | New_Event | Vegetation Contact | Include | Include | Vegetation | 740 | 2021-08-31 | 14800 | keep | 0 | Aug | 2021 | 0.01008 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
VEGA BAJA | 2021-08-31 22:01 | 2021-09-01 17:08 | 1 | 019:07 | P | NO SE REPORTO CAUSA | 1 NX 30 EN SU-1 | B21083100436 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1147 | 2021-08-31 | 1147 | keep | 0 | Aug | 2021 | 0.00078122 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
HUMACAO | 2021-08-31 22:10 | 2021-09-01 10:32 | 45 | 012:22 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21083100336 | New_Event | Vegetation Contact | Include | Include | Vegetation | 742 | 2021-08-31 | 33390 | keep | 0 | Aug | 2021 | 0.022742 | 3.0649e-05 | Sustained | FALSE | TRUE | TMED_Event | 45
CAGUAS | 2021-08-31 22:56 | 2021-09-01 15:01 | 115 | 016:05 | P | DESGANCHE | 3 X 40 EN CORTE DE LINEA | C21083100339 | New_Event | Vegetation Contact | Include | Include | Vegetation | 965 | 2021-08-31 | 110975 | keep | 0 | Aug | 2021 | 0.075585 | 7.8326e-05 | Sustained | FALSE | TRUE | TMED_Event | 115
MAYAGÃœEZ | 2021-08-31 22:59 | 2021-08-31 23:00 | 3147 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21083100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-31 | 3147 | keep | 0 | Aug | 2021 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | TMED_Event | 3147
MAYAGÃœEZ | 2021-08-31 22:59 | 2021-08-31 23:00 | 1287 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21083100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-08-31 | 1287 | keep | 0 | Aug | 2021 | 0.00087657 | 0.00087657 | Momentary | FALSE | FALSE | TMED_Event | 1287
BAYAMON | 2021-08-31 23:06 | 2021-09-01 11:34 | 20 | 012:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CERRO PUENTE DE LINEA A CAJA EN CORTE DE LINEA | S21083100480 | New_Event | Cutout Failure | Include | Include | Equipment | 748 | 2021-08-31 | 14960 | keep | 0 | Aug | 2021 | 0.010189 | 1.3622e-05 | Sustained | FALSE | TRUE | TMED_Event | 20
CANOVANAS | 2021-08-31 23:46 | 2021-09-01 09:11 | 45 | 009:25 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR CRUCE POR CULEBRA | R21083100170 | New_Event |  |  | Include | Wildlife | 565 | 2021-08-31 | 25425 | keep | 0 | Aug | 2021 | 0.017317 | 3.0649e-05 | Sustained | FALSE | TRUE | TMED_Event | 45
MAYAGÃœEZ | 2021-09-01 00:08 | 2021-09-01 00:09 | 990 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 990 | keep | 0 | Sep | 2021 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
CAGUAS | 2021-09-01 02:00 | 2021-09-02 11:25 | 90 | 033:25 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | C21090100004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2005 | 2021-09-01 | 180450 | keep | 0 | Sep | 2021 | 0.1229 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
MAYAGÃœEZ | 2021-09-01 02:13 | 2021-09-01 13:28 | 80 | 011:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21090100004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 675 | 2021-09-01 | 54000 | keep | 0 | Sep | 2021 | 0.036779 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-09-01 02:26 | 2021-09-01 09:50 | 35 | 007:24 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21090100003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 444 | 2021-09-01 | 15540 | keep | 0 | Sep | 2021 | 0.010584 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
PONCE | 2021-09-01 02:33 | 2021-09-01 02:34 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210901000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 3744 | keep | 0 | Sep | 2021 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2021-09-01 02:33 | 2021-09-01 02:34 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210901000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 3114 | keep | 0 | Sep | 2021 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
AGUADILLA | 2021-09-01 02:36 | 2021-09-01 04:51 | 3315 | 002:15 | T | DESGANCHE | DISPARO DE INTERRUTPOR SE RETIRO RAMA SOBRE LINEA | M21090100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2021-09-01 | 447525 | keep | 0 | Sep | 2021 | 0.30481 | 0.0022578 | Sustained | FALSE | TRUE | Not_TMED_Event | 3315
ARECIBO | 2021-09-01 03:01 | 2021-09-01 10:29 | 30 | 007:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | A21090100003 | New_Event | Bad Weather | Include | Include | Weather | 448 | 2021-09-01 | 13440 | keep | 0 | Sep | 2021 | 0.0091539 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-01 04:53 | 2021-09-01 14:30 | 75 | 009:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | A21090100004 | New_Event | Bad Weather | Include | Include | Weather | 577 | 2021-09-01 | 43275 | keep | 0 | Sep | 2021 | 0.029474 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
MAYAGÃœEZ | 2021-09-01 05:17 | 2021-09-01 10:15 | 4 | 004:58 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR POR DESGANCHE | M21090100009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 298 | 2021-09-01 | 1192 | keep | 0 | Sep | 2021 | 0.00081187 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2021-09-01 05:21 | 2021-09-01 05:23 | 2859 | 000:02 | T | PARARRAYOS DEFECTUOSO | RECIERRE | C21090100002 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 2 | 2021-09-01 | 5718 | keep | 0 | Sep | 2021 | 0.0038945 | 0.0019473 | Momentary | FALSE | FALSE | Not_TMED_Event | 2859
CAGUAS | 2021-09-01 05:23 | 2021-09-02 15:49 | 1 | 034:26 | P | PARARRAYOS DEFECTUOSO | 1 X 10 EN BANCO DE TRANSFORMADORES SE REEMPLAZO PARARRAYO | C21090100039 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 2066 | 2021-09-01 | 2066 | keep | 0 | Sep | 2021 | 0.0014071 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2021-09-01 05:57 | 2021-09-01 11:03 | 20 | 005:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21090100008 | New_Event | Bad Weather | Include | Include | Weather | 306 | 2021-09-01 | 6120 | keep | 0 | Sep | 2021 | 0.0041683 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-01 06:17 | 2021-09-01 19:49 | 20 | 013:32 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21090100011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 812 | 2021-09-01 | 16240 | keep | 0 | Sep | 2021 | 0.011061 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
SAN JUAN | 2021-09-01 06:33 | 2021-09-02 13:04 | 50 | 030:31 | P | NO SE REPORTO CAUSA | 1 X 20 EN SU-1 Y 1 X 65 EN RISER | S21090100007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1831 | 2021-09-01 | 91550 | keep | 0 | Sep | 2021 | 0.062354 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2021-09-01 06:38 | 2021-09-01 14:02 | 100 | 007:24 | P | DESCONECTIVO DEFECTUOSO | SE CAMBIO MACHETE QUEMADO | P21090100014 | New_Event | Switch Failure | Include | Include | Equipment | 444 | 2021-09-01 | 44400 | keep | 0 | Sep | 2021 | 0.030241 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2021-09-01 06:38 | 2021-09-01 06:39 | 2113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21092100017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 2113 | keep | 0 | Sep | 2021 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
HUMACAO | 2021-09-01 06:41 | 2021-09-01 13:39 | 65 | 006:58 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C21090100005 | New_Event |  |  | Include | Wildlife | 418 | 2021-09-01 | 27170 | keep | 0 | Sep | 2021 | 0.018505 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BAYAMON | 2021-09-01 06:51 | 2021-09-04 12:07 | 30 | 077:16 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21090100005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 4636 | 2021-09-01 | 139080 | keep | 0 | Sep | 2021 | 0.094727 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BARRANQUITAS | 2021-09-01 07:04 | 2021-09-01 07:05 | 2410 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 18400 | C21090100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-01 | 2410 | keep | 0 | Sep | 2021 | 0.0016414 | 0.0016414 | Momentary | FALSE | TRUE | Not_TMED_Event | 2410
BARRANQUITAS | 2021-09-01 07:04 | 2021-09-01 07:05 | 2826 | 000:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 18400 | C21090100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-01 | 2826 | keep | 0 | Sep | 2021 | 0.0019248 | 0.0019248 | Momentary | FALSE | TRUE | Not_TMED_Event | 2826
CAGUAS | 2021-09-01 07:11 | 2021-09-01 13:43 | 90 | 006:32 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C21090100007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 392 | 2021-09-01 | 35280 | keep | 0 | Sep | 2021 | 0.024029 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
HUMACAO | 2021-09-01 07:14 | 2021-09-01 10:21 | 65 | 003:07 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C21090100008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 187 | 2021-09-01 | 12155 | keep | 0 | Sep | 2021 | 0.0082787 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
SAN JUAN | 2021-09-01 07:22 | 2021-09-01 18:18 | 20 | 010:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | S21090100013 | New_Event | Cutout Failure | Include | Include | Equipment | 656 | 2021-09-01 | 13120 | keep | 0 | Sep | 2021 | 0.008936 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-09-01 07:35 | 2021-09-01 11:30 | 60 | 003:55 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 40 EN SU-13 CONTAMINACION | R21090100004 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 235 | 2021-09-01 | 14100 | keep | 0 | Sep | 2021 | 0.0096034 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-09-01 07:41 | 2021-09-01 18:00 | 8 | 010:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21090100013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 619 | 2021-09-01 | 4952 | keep | 0 | Sep | 2021 | 0.0033728 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-09-01 07:51 | 2021-09-01 16:10 | 30 | 008:19 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21090100014 | New_Event | Bad Weather | Include | Include | Weather | 499 | 2021-09-01 | 14970 | keep | 0 | Sep | 2021 | 0.010196 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BARRANQUITAS | 2021-09-01 08:03 | 2021-09-01 12:02 | 45 | 003:59 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | C21090100016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 239 | 2021-09-01 | 10755 | keep | 0 | Sep | 2021 | 0.0073252 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
AGUADILLA | 2021-09-01 08:11 | 2021-09-01 18:45 | 150 | 010:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M21090100020 | New_Event | Cutout Failure | Include | Include | Equipment | 634 | 2021-09-01 | 95100 | keep | 0 | Sep | 2021 | 0.064772 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
CAGUAS | 2021-09-01 08:16 | 2021-09-01 10:11 | 1 | 001:55 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | C21090100018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2021-09-01 | 115 | keep | 0 | Sep | 2021 | 7.8326e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-09-01 08:18 | 2021-09-01 11:22 | 3 | 003:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | S21090100023 | New_Event | Cutout Failure | Include | Include | Equipment | 184 | 2021-09-01 | 552 | keep | 0 | Sep | 2021 | 0.00037596 | 2.0433e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 3
ARECIBO | 2021-09-01 08:19 | 2021-09-01 12:50 | 30 | 004:31 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21090100018 | New_Event | Bad Weather | Include | Include | Weather | 271 | 2021-09-01 | 8130 | keep | 0 | Sep | 2021 | 0.0055373 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-01 08:20 | 2021-09-01 11:17 | 2391 | 002:57 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR PROBO MALO SE PATRULLO SE ABRIO MACHETE EN CARR 1 AL LADO DE LA SUB BUEN PASTOR Y SE CERRO POR SCADA 70% EN SERVICIO | S21090100026 | New_Event | Wire Down | Include | Include | Equipment | 177 | 2021-09-01 | 423207 | keep | 0 | Sep | 2021 | 0.28824 | 0.0016285 | Sustained | FALSE | FALSE | Not_TMED_Event | 2391
BAYAMON | 2021-09-01 08:20 | 2021-09-01 08:26 | 3957 | 000:06 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA SE VERIFICO PERSONAL FUERA | S21091000026 | New_Event | Wire Down | Include | Include | Equipment | 6 | 2021-09-01 | 23742 | keep | 0 | Sep | 2021 | 0.016171 | 0.0026951 | Sustained | FALSE | FALSE | Not_TMED_Event | 3957
BAYAMON | 2021-09-01 08:26 | 2021-09-01 15:37 | 50 | 007:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA Y SE LEVANTO CONDUCTOR | S21090100000 | Partial_restoration | Wire Down | Include | Include | Equipment | 431 | 2021-09-01 | 21550 | keep | 0 | Sep | 2021 | 0.014678 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CAGUAS | 2021-09-01 08:39 | 2021-09-01 16:28 | 12 | 007:49 | P | SECUNDARIA/ESTRUCTURA AVERIADA | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BARRA EN PEDESTAL Y PEDESTAL AVERIADO | C21090100024 | New_Event | Secondary Defective Pole | Include | Include | Equipment | 469 | 2021-09-01 | 5628 | keep | 0 | Sep | 2021 | 0.0038332 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2021-09-01 08:42 | 2021-09-01 11:50 | 5 | 003:08 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR DE 37.5KVA X 37.5KVA | C21090100028 | New_Event | Service Transformer Failure | Include | Include | Equipment | 188 | 2021-09-01 | 940 | keep | 0 | Sep | 2021 | 0.00064023 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2021-09-01 08:43 | 2021-09-01 13:36 | 60 | 004:53 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO BAJANTE CRUZADO CON NEUTRAL PRIMARIO | C21090100029 | New_Event | Wire Down | Include | Include | Equipment | 293 | 2021-09-01 | 17580 | keep | 0 | Sep | 2021 | 0.011974 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-09-01 08:46 | 2021-09-01 15:45 | 49 | 006:59 | P | ESTRUCTURA AVERIADA | SE ABRIO CORTE DE LINEA PARA REEMPLAZAR POSTE ROTO | C21090100030 | New_Event | Defective Pole | Include | Include | Equipment | 419 | 2021-09-01 | 20531 | keep | 0 | Sep | 2021 | 0.013984 | 3.3374e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 49
CAGUAS | 2021-09-01 08:48 | 2021-09-02 10:31 | 90 | 025:43 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C21090100032 | New_Event |  |  | Include | Wildlife | 1543 | 2021-09-01 | 138870 | keep | 0 | Sep | 2021 | 0.094584 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
YAUCO | 2021-09-01 08:49 | 2021-09-01 12:00 | 50 | 003:11 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21090100037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2021-09-01 | 9550 | keep | 0 | Sep | 2021 | 0.0065045 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-01 09:06 | 2021-09-01 10:38 | 40 | 001:32 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C21090100035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 92 | 2021-09-01 | 3680 | keep | 0 | Sep | 2021 | 0.0025064 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-01 09:33 | 2021-09-01 09:34 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 3941 | keep | 0 | Sep | 2021 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
PONCE | 2021-09-01 09:41 | 2021-09-01 16:44 | 100 | 007:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | REMPLAZO DE POSTE PARTIDO POR ACCIDENTE DE AUTO | P21090100055 | New_Event |  |  | Include | Wildlife | 423 | 2021-09-01 | 42300 | keep | 0 | Sep | 2021 | 0.02881 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2021-09-01 09:43 | 2021-09-01 15:20 | 30 | 005:37 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA DESGANCHE | A21090100029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 337 | 2021-09-01 | 10110 | keep | 0 | Sep | 2021 | 0.0068859 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
PONCE | 2021-09-01 09:45 | 2021-09-01 17:20 | 600 | 007:35 | P | DESGANCHE | SE HIZO DESGANCHE Y SE REEMPLAZO POSTE PARTIDO | P21090100058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 455 | 2021-09-01 | 273000 | keep | 0 | Sep | 2021 | 0.18594 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
PONCE | 2021-09-01 09:50 | 2021-09-01 11:59 | 3744 | 002:09 | T | ERROR HUMANO | PERSONAL DESGANCHANDO SACO ALIMENTADOR LLEVA LA CARGA DEL 5018-02 | P21090100058 | New_Event | Human Error | Include | Include | Other | 129 | 2021-09-01 | 482976 | keep | 0 | Sep | 2021 | 0.32895 | 0.00255 | Sustained | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2021-09-01 09:50 | 2021-09-01 11:59 | 3114 | 002:09 | T | ERROR HUMANO | PERSONAL DESGANCHANDO SACO ALIMENTADOR LA CARGA POR EL 5004-06 | P21090100058 | New_Event | Human Error | Include | Include | Other | 129 | 2021-09-01 | 401706 | keep | 0 | Sep | 2021 | 0.2736 | 0.0021209 | Sustained | FALSE | FALSE | Not_TMED_Event | 3114
MAYAGÃœEZ | 2021-09-01 09:51 | 2021-09-02 13:20 | 6 | 027:29 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO 15KVA. #SER-2055098957. MARCA EAPON 4160/7200V 120/240V POR LO MISMO | M21090100033 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1649 | 2021-09-01 | 9894 | keep | 0 | Sep | 2021 | 0.0067388 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2021-09-01 09:59 | 2021-09-01 19:02 | 95 | 009:03 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | C21090100043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 543 | 2021-09-01 | 51585 | keep | 0 | Sep | 2021 | 0.035134 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
ARECIBO | 2021-09-01 10:00 | 2021-09-01 10:52 | 20 | 000:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REMPLAZAR CONECTORES EN LA SECUNDARIA | A21090100031 | New_Event | Secondary Wire Down | Include | Include | Equipment | 52 | 2021-09-01 | 1040 | keep | 0 | Sep | 2021 | 0.00070834 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-09-01 10:02 | 2021-09-01 12:36 | 7 | 002:34 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR CON DERRAME DE 25KVA X 50KVA HC A GIS UPDATES | C21090100044 | New_Event | Service Transformer Failure | Include | Include | Equipment | 154 | 2021-09-01 | 1078 | keep | 0 | Sep | 2021 | 0.00073422 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2021-09-01 10:19 | 2021-09-01 13:22 | 11 | 003:03 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | C21090100047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 183 | 2021-09-01 | 2013 | keep | 0 | Sep | 2021 | 0.001371 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2021-09-01 10:28 | 2021-09-01 23:05 | 20 | 012:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21090100039 | New_Event | Bad Weather | Include | Include | Weather | 757 | 2021-09-01 | 15140 | keep | 0 | Sep | 2021 | 0.010312 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-09-01 10:49 | 2021-09-01 15:51 | 11 | 005:02 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR SECUNDARIA AVERIADA | C21090100051 | New_Event | Secondary Wire Down | Include | Include | Equipment | 302 | 2021-09-01 | 3322 | keep | 0 | Sep | 2021 | 0.0022626 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2021-09-01 10:55 | 2021-09-01 15:38 | 10 | 004:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZO SECUNDARIA AVERIADA | C21090100002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 283 | 2021-09-01 | 2830 | keep | 0 | Sep | 2021 | 0.0019275 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2021-09-01 10:55 | 2021-09-01 10:56 | 1 | 000:01 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | P2109010038 | New_Event |  |  | Include | Wildlife | 1 | 2021-09-01 | 1 | keep | 0 | Sep | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | TRUE | Not_TMED_Event | 1
PONCE | 2021-09-01 10:57 | 2021-09-01 10:58 | 25 | 000:01 | P | TRANSFORMADOR AVERIADO | TRANFORMADOR 25 KVA AVERIADO 4160 VOLT POR LA MISMA CAPACIDAD | P21090100030 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1 | 2021-09-01 | 25 | keep | 0 | Sep | 2021 | 1.7027e-05 | 1.7027e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2021-09-01 11:12 | 2021-09-01 16:23 | 20 | 005:11 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | S21090100061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 311 | 2021-09-01 | 6220 | keep | 0 | Sep | 2021 | 0.0042364 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2021-09-01 11:17 | 2021-09-01 12:15 | 718 | 000:58 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | CONDUCTOR DEL 1908-03 CAYO ENCIMA DEL 1343-05 SE CERRO MACHETES SERVICIO EL 100% | S21090000000 | New_Event | Wire Down | Include | Include | Equipment | 58 | 2021-09-01 | 41644 | keep | 0 | Sep | 2021 | 0.028364 | 0.00048903 | Sustained | FALSE | FALSE | Not_TMED_Event | 718
BAYAMON | 2021-09-01 11:23 | 2021-09-01 15:45 | 80 | 004:22 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21090100028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 262 | 2021-09-01 | 20960 | keep | 0 | Sep | 2021 | 0.014276 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-09-01 12:00 | 2021-09-01 17:44 | 40 | 005:44 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 344 | 2021-09-01 | 13760 | keep | 0 | Sep | 2021 | 0.0093719 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-01 12:12 | 2021-09-01 17:19 | 435 | 005:07 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO CONDUCTOR EN EL SUELO ABRIENDO CORTE DE LINEA | S21090100000 | New_Event | Wire Down | Include | Include | Equipment | 307 | 2021-09-01 | 133545 | keep | 0 | Sep | 2021 | 0.090957 | 0.00029628 | Sustained | FALSE | TRUE | Not_TMED_Event | 435
SAN JUAN | 2021-09-01 12:13 | 2021-09-01 12:14 | 5290 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1336-08 LLEVANDO EL 1336-09 | S21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 5290 | keep | 0 | Sep | 2021 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2021-09-01 12:13 | 2021-09-01 12:14 | 207 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO 1336-08 LLEVANDO EL 1336-09 | S21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 207 | keep | 0 | Sep | 2021 | 0.00014099 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
CANOVANAS | 2021-09-01 12:30 | 2021-09-01 12:31 | 1648 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | R21090100016 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-01 | 1648 | keep | 0 | Sep | 2021 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2021-09-01 12:30 | 2021-09-01 13:52 | 500 | 001:22 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SECCIONALIZO AVERIA POR CONDUCTOR DEL 2302-03 SOBRE EL 2403-02. SE CERRO INTERRUPTOR EN LA SUBESTACION NO TIENE RTU | R21090100017 | New_Event | Wire Down | Include | Include | Equipment | 82 | 2021-09-01 | 41000 | keep | 0 | Sep | 2021 | 0.027925 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CANOVANAS | 2021-09-01 12:31 | 2021-09-01 12:39 | 600 | 000:08 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR ROTO DEL 2302-03 SOBRE 2403-02 Y CERRO MACHETES | R21090100034 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 8 | 2021-09-01 | 4800 | keep | 0 | Sep | 2021 | 0.0032693 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2021-09-01 12:37 | 2021-09-01 16:32 | 10 | 003:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARA BAJANTE SECUNDARIO ARQUEANDO | S21090100089 | New_Event | Secondary Wire Down | Include | Include | Equipment | 235 | 2021-09-01 | 2350 | keep | 0 | Sep | 2021 | 0.0016006 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-01 12:37 | 2021-09-01 16:27 | 1 | 003:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE HACIA MACHETE | C21090100069 | New_Event | Wire Down | Include | Include | Equipment | 230 | 2021-09-01 | 230 | keep | 0 | Sep | 2021 | 0.00015665 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-09-01 12:39 | 2021-09-01 12:40 | 1648 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | R21090100016 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2021-09-01 | 1648 | keep | 0 | Sep | 2021 | 0.0011224 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-09-01 12:40 | 2021-09-01 12:47 | 600 | 000:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR ROTO DEL 2302-03 SOBRE 2403-02 Y CERRO MACHETES | R21090100034 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 7 | 2021-09-01 | 4200 | keep | 0 | Sep | 2021 | 0.0028606 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
CANOVANAS | 2021-09-01 12:47 | 2021-09-01 12:48 | 1648 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | R21090100016 | Additional_clients | Wire Down | Include | Include | Equipment | 1 | 2021-09-01 | 1648 | keep | 0 | Sep | 2021 | 0.0011224 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-09-01 12:48 | 2021-09-01 13:23 | 600 | 000:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR ROTO DEL 2302-03 SOBRE 2403-02 Y CERRO MACHETES | R21090100034 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 35 | 2021-09-01 | 21000 | keep | 0 | Sep | 2021 | 0.014303 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2021-09-01 12:52 | 2021-09-01 14:34 | 50 | 001:42 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21090100026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2021-09-01 | 5100 | keep | 0 | Sep | 2021 | 0.0034736 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
PONCE | 2021-09-01 12:55 | 2021-09-01 12:56 | 978 | 000:01 | T | DESGANCHE | RECIERRE | P21090100088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-01 | 978 | keep | 0 | Sep | 2021 | 0.00066611 | 0.00066611 | Momentary | FALSE | FALSE | Not_TMED_Event | 978
PONCE | 2021-09-01 12:56 | 2021-09-02 12:41 | 100 | 023:45 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | P21090100151 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1425 | 2021-09-01 | 142500 | keep | 0 | Sep | 2021 | 0.097056 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-01 12:58 | 2021-09-01 12:59 | 1420 | 000:01 | T | DESGANCHE | RECERRO 1530-06 LLEVANDO 1526-02 | S21090100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-01 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-01 12:58 | 2021-09-01 12:59 | 437 | 000:01 | T | OTRAS CAUSAS | RECERRO 1530-06 LLEVANDO 1526-02 DESBALANCE | S21090100000 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-09-01 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
PONCE | 2021-09-01 13:05 | 2021-09-01 17:35 | 100 | 004:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE INSTALO POSTE PARA LEVANTAR LINEA PRIMARIA LINEA ARRIADA | P21090100095 | New_Event | Wire Down | Include | Include | Equipment | 270 | 2021-09-01 | 27000 | keep | 0 | Sep | 2021 | 0.01839 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
GUAYAMA | 2021-09-01 13:07 | 2021-09-01 16:21 | 40 | 003:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR Y 1 X 40 EN CORTE DE LINEA POR CONTACTO DE AVE | P21090100096 | New_Event |  |  | Include | Wildlife | 194 | 2021-09-01 | 7760 | keep | 0 | Sep | 2021 | 0.0052853 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-09-01 13:23 | 2021-09-01 13:28 | 1648 | 000:05 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR ROTO DEL 2302-03 SOBRE 2403-02 | R21090100034 | Additional_clients | Wire Down | Include | Include | Equipment | 5 | 2021-09-01 | 8240 | keep | 0 | Sep | 2021 | 0.0056122 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-09-01 13:28 | 2021-09-01 18:37 | 600 | 005:09 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR ROTO DEL 2302-03 SOBRE 2403-02 Y CERRO MACHETES | R21090100034 | Partial_restoration | Wire Down | Include | Include | Equipment | 309 | 2021-09-01 | 185400 | keep | 0 | Sep | 2021 | 0.12628 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-09-01 13:43 | 2021-09-01 14:27 | 8 | 000:44 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21090100043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 44 | 2021-09-01 | 352 | keep | 0 | Sep | 2021 | 0.00023975 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2021-09-01 13:52 | 2021-09-01 18:29 | 80 | 004:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | REPARO AVERIA DE CONDUCTOR DEL 2302-03 SOBRE EL 2403-02 Y SE CERRO MACHETES EN CARR 187 MELILLA, LOIZA. | R21090100017 | Partial_restoration | Wire Down | Include | Include | Equipment | 277 | 2021-09-01 | 22160 | keep | 0 | Sep | 2021 | 0.015093 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-09-01 13:53 | 2021-09-01 16:26 | 11 | 002:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR SECUNDARIA AVERIADA | C21083100153 | New_Event | Secondary Wire Down | Include | Include | Equipment | 153 | 2021-09-01 | 1683 | keep | 0 | Sep | 2021 | 0.0011463 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
ARECIBO | 2021-09-01 14:00 | 2021-09-01 15:21 | 5 | 001:21 | P | SOBRECARGA | SE ABRIO TRANSFORMADOR PARA RELOCALIZARLO DEL FID-1000795748 AL FID-1000202095 | A21090100057 | New_Event | Trip Due To Overload | Include | Include | Other | 81 | 2021-09-01 | 405 | keep | 0 | Sep | 2021 | 0.00027584 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2021-09-01 14:00 | 2021-09-01 16:46 | 934 | 002:46 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 39000 SE ENERGIZO POR LA LINEA 36400 | A21090100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 166 | 2021-09-01 | 155044 | keep | 0 | Sep | 2021 | 0.1056 | 0.00063614 | Sustained | FALSE | TRUE | Not_TMED_Event | 934
UTUADO | 2021-09-01 14:00 | 2021-09-01 16:46 | 4 | 002:46 | P | LINEA DE TRANSMISION 115KV | DISPARO LINEA 39000 SE ENERGIZO POR LA LINEA 36400 | A21090100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 166 | 2021-09-01 | 664 | keep | 0 | Sep | 2021 | 0.00045225 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
UTUADO | 2021-09-01 14:00 | 2021-09-01 16:46 | 1479 | 002:46 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 39000 SE ENERGIZO POR LA LINEA 36400 | A21090100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 166 | 2021-09-01 | 245514 | keep | 0 | Sep | 2021 | 0.16722 | 0.0010073 | Sustained | FALSE | TRUE | Not_TMED_Event | 1479
UTUADO | 2021-09-01 14:00 | 2021-09-01 16:46 | 1841 | 002:46 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 39000 ENERGIZADO POR LA LINEA 36400 | A21090100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 166 | 2021-09-01 | 305606 | keep | 0 | Sep | 2021 | 0.20815 | 0.0012539 | Sustained | FALSE | TRUE | Not_TMED_Event | 1841
UTUADO | 2021-09-01 14:00 | 2021-09-01 16:46 | 1950 | 002:46 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 39000 ENERGIZADO POR LA LINEA 36400 | A21090100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 166 | 2021-09-01 | 323700 | keep | 0 | Sep | 2021 | 0.22047 | 0.0013281 | Sustained | FALSE | TRUE | Not_TMED_Event | 1950
BAYAMON | 2021-09-01 14:03 | 2021-09-01 14:04 | 1420 | 000:01 | T | DESGANCHE | RECERRO LLEVA 1526-02 | S21090100000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-01 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-01 14:03 | 2021-09-01 14:04 | 437 | 000:01 | T | OTRAS CAUSAS | RECERRO LLEVA 1526-2 DESBALANCE | S21090100000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-01 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
YAUCO | 2021-09-01 14:07 | 2021-09-01 14:08 | 2484 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21090100106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 2484 | keep | 0 | Sep | 2021 | 0.0016918 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
BAYAMON | 2021-09-01 14:09 | 2021-09-01 15:52 | 10 | 001:43 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE LE REPARO LA SECUNDARIA | B21090100002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 103 | 2021-09-01 | 1030 | keep | 0 | Sep | 2021 | 0.00070153 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-09-01 14:10 | 2021-09-01 17:48 | 30 | 003:38 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU-3MC @ SU-2MC | C21090100060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 218 | 2021-09-01 | 6540 | keep | 0 | Sep | 2021 | 0.0044544 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2021-09-01 14:10 | 2021-09-01 17:55 | 30 | 003:45 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBÃšES SOBRE LAS LINEAS | M21090100064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2021-09-01 | 6750 | keep | 0 | Sep | 2021 | 0.0045974 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-01 14:10 | 2021-09-01 16:08 | 100 | 001:58 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | A21090100062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2021-09-01 | 11800 | keep | 0 | Sep | 2021 | 0.0080369 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-09-01 14:14 | 2021-09-01 16:13 | 9 | 001:59 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR 300 PIES DE SECUNDARIA | C21081800061 | New_Event | Secondary Wire Down | Include | Include | Equipment | 119 | 2021-09-01 | 1071 | keep | 0 | Sep | 2021 | 0.00072945 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2021-09-01 14:20 | 2021-09-01 20:00 | 20 | 005:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO 75 KVA X 75 KVA | M21090100066 | New_Event | Service Transformer Failure | Include | Include | Equipment | 340 | 2021-09-01 | 6800 | keep | 0 | Sep | 2021 | 0.0046314 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2021-09-01 14:23 | 2021-09-01 16:46 | 12 | 002:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | C21083100088 | New_Event | Secondary Wire Down | Include | Include | Equipment | 143 | 2021-09-01 | 1716 | keep | 0 | Sep | 2021 | 0.0011688 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-09-01 14:32 | 2021-09-01 17:20 | 4 | 002:48 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21090100079 | New_Event | Bad Weather | Include | Include | Weather | 168 | 2021-09-01 | 672 | keep | 0 | Sep | 2021 | 0.0004577 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
BAYAMON | 2021-09-01 14:33 | 2021-09-01 14:36 | 90 | 000:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO CON R/R OFF LLEVA 75% DEL 1011-2 SE PROBO POR CONTROL QUEDO EN SERVICIO CARGA POR EL 1011-05 | S21090100112 | New_Event | Cutout Failure | Include | Include | Equipment | 3 | 2021-09-01 | 270 | keep | 0 | Sep | 2021 | 0.0001839 | 6.1299e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2021-09-01 14:33 | 2021-09-01 14:36 | 719 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA 75% DEL 1011-2 SE PROBO POR CONTROL QUEDO EN SERVICIO | S21090100112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-09-01 | 2157 | keep | 0 | Sep | 2021 | 0.0014691 | 0.00048971 | Momentary | FALSE | FALSE | Not_TMED_Event | 719
BAYAMON | 2021-09-01 14:36 | 2021-09-02 12:30 | 75 | 021:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 100 EN RISER SE REMPLAZO 3 CAJAS QUEMADAS | S21090100114 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1314 | 2021-09-01 | 98550 | keep | 0 | Sep | 2021 | 0.067122 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2021-09-01 14:45 | 2021-09-01 14:47 | 3458 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR RECIERRE EN OFF NO SE REPORTO CAUSA | M21090100095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-01 | 6916 | keep | 0 | Sep | 2021 | 0.0047105 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
AGUADILLA | 2021-09-01 14:51 | 2021-09-01 14:52 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M21090100073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 1827 | keep | 0 | Sep | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
CAGUAS | 2021-09-01 14:59 | 2021-09-01 18:40 | 10 | 003:41 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR DE 25KVA X 37.5KVA HC A GIS UPDATES | C21090100083 | New_Event | Service Transformer Failure | Include | Include | Equipment | 221 | 2021-09-01 | 2210 | keep | 0 | Sep | 2021 | 0.0015052 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-01 14:59 | 2021-09-01 15:00 | 24 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | A21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 24 | keep | 0 | Sep | 2021 | 1.6346e-05 | 1.6346e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2021-09-01 15:00 | 2021-09-01 15:01 | 3295 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO Y SE CERRO POR SCADA | B21090100000 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-01 | 3295 | keep | 0 | Sep | 2021 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2021-09-01 15:01 | 2021-09-01 22:43 | 300 | 007:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA | B21090100059 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 462 | 2021-09-01 | 138600 | keep | 0 | Sep | 2021 | 0.0944 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
MAYAGÃœEZ | 2021-09-01 15:05 | 2021-09-01 15:06 | 1287 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 1287 | keep | 0 | Sep | 2021 | 0.00087657 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
ARECIBO | 2021-09-01 15:21 | 2021-09-01 15:29 | 3431 | 000:08 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE VERIFICO PERSONAL REALIZANDO TRABAJOS EN EL AREA POR ORLANDO VELEZ. | A21090100100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2021-09-01 | 27448 | keep | 0 | Sep | 2021 | 0.018695 | 0.0023368 | Sustained | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2021-09-01 15:24 | 2021-09-01 21:00 | 60 | 005:36 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | A21090100101 | New_Event | Bad Weather | Include | Include | Weather | 336 | 2021-09-01 | 20160 | keep | 0 | Sep | 2021 | 0.013731 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
MAYAGÃœEZ | 2021-09-01 15:26 | 2021-09-01 20:40 | 80 | 005:14 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21090100085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 314 | 2021-09-01 | 25120 | keep | 0 | Sep | 2021 | 0.017109 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-09-01 15:26 | 2021-09-01 19:50 | 8 | 004:24 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | M21090100086 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 264 | 2021-09-01 | 2112 | keep | 0 | Sep | 2021 | 0.0014385 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
ARECIBO | 2021-09-01 15:29 | 2021-09-01 17:30 | 5 | 002:01 | P | SOBRECARGA | SE ABRIO TRANSFORMADOR PARA RELOCALIZARLO DEL FID-1000795748 AL FID-1000202095 | A21090100057 | Partial_restoration | Trip Due To Overload | Include | Include | Other | 121 | 2021-09-01 | 605 | keep | 0 | Sep | 2021 | 0.00041206 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-01 15:30 | 2021-09-01 15:31 | 2735 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 2735 | keep | 0 | Sep | 2021 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
YAUCO | 2021-09-01 15:31 | 2021-09-01 18:38 | 100 | 003:07 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P21090100120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2021-09-01 | 18700 | keep | 0 | Sep | 2021 | 0.012736 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-01 15:31 | 2021-09-02 18:28 | 25 | 026:57 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | B21090100208 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1617 | 2021-09-01 | 40425 | keep | 0 | Sep | 2021 | 0.027533 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CAGUAS | 2021-09-01 15:34 | 2021-09-01 17:42 | 32 | 002:08 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL SOBRE LINEA | C21090100089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2021-09-01 | 4096 | keep | 0 | Sep | 2021 | 0.0027898 | 2.1795e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 32
BAYAMON | 2021-09-01 15:35 | 2021-09-01 15:36 | 959 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 959 | keep | 0 | Sep | 2021 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
CAGUAS | 2021-09-01 15:35 | 2021-09-02 11:35 | 3 | 020:00 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | C21090100090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1200 | 2021-09-01 | 3600 | keep | 0 | Sep | 2021 | 0.0024519 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2021-09-01 15:37 | 2021-09-01 15:38 | 959 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21090100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 959 | keep | 0 | Sep | 2021 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
SAN JUAN | 2021-09-01 15:37 | 2021-09-01 15:42 | 3957 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF SE PROBO POR CONTROL QUEDO EN SERVICIO | S21090100126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-09-01 | 19785 | keep | 0 | Sep | 2021 | 0.013475 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
BAYAMON | 2021-09-01 15:42 | 2021-09-01 16:22 | 50 | 000:40 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 SE REEMPLAZO FUSIBLE EN CORTE DE LINEA Y SE LEVANTO CONDUCTOR | S21090100000 | New_Event | Wire Down | Include | Include | Equipment | 40 | 2021-09-01 | 2000 | keep | 0 | Sep | 2021 | 0.0013622 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-01 15:42 | 2021-09-01 15:44 | 2956 | 0:02 | T | NO SE REPORTO CAUSA | RECIERRE | B21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-01 | 5912 | keep | 0 | Sep | 2021 | 0.0040266 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2021-09-01 15:45 | 2021-09-01 15:46 | 959 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 9100 | B21090100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-01 | 959 | keep | 0 | Sep | 2021 | 0.00065317 | 0.00065317 | Momentary | FALSE | TRUE | Not_TMED_Event | 959
BAYAMON | 2021-09-01 15:45 | 2021-09-01 15:46 | 1382 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 9100 | B21090100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-01 | 1382 | keep | 0 | Sep | 2021 | 0.00094127 | 0.00094127 | Momentary | FALSE | TRUE | Not_TMED_Event | 1382
BAYAMON | 2021-09-01 15:45 | 2021-09-01 15:46 | 663 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 9100 | B21090100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-01 | 663 | keep | 0 | Sep | 2021 | 0.00045157 | 0.00045157 | Momentary | FALSE | TRUE | Not_TMED_Event | 663
BAYAMON | 2021-09-01 15:45 | 2021-09-01 15:46 | 3941 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 3941 | keep | 0 | Sep | 2021 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
BAYAMON | 2021-09-01 15:45 | 2021-09-01 15:46 | 3871 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 3871 | keep | 0 | Sep | 2021 | 0.0026365 | 0.0026365 | Momentary | FALSE | FALSE | Not_TMED_Event | 3871
BAYAMON | 2021-09-01 15:45 | 2021-09-01 15:46 | 1514 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 9100 | B21090100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-01 | 1514 | keep | 0 | Sep | 2021 | 0.0010312 | 0.0010312 | Momentary | FALSE | TRUE | Not_TMED_Event | 1514
BAYAMON | 2021-09-01 15:45 | 2021-09-01 15:46 | 1105 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 9100 | B21090100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-01 | 1105 | keep | 0 | Sep | 2021 | 0.00075261 | 0.00075261 | Momentary | FALSE | TRUE | Not_TMED_Event | 1105
BAYAMON | 2021-09-01 15:45 | 2021-09-01 15:46 | 4176 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 9100 | B21090100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-01 | 4176 | keep | 0 | Sep | 2021 | 0.0028443 | 0.0028443 | Momentary | FALSE | TRUE | Not_TMED_Event | 4176
BAYAMON | 2021-09-01 15:45 | 2021-09-01 15:46 | 252 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 9100 | B21090100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-01 | 252 | keep | 0 | Sep | 2021 | 0.00017164 | 0.00017164 | Momentary | FALSE | TRUE | Not_TMED_Event | 252
BAYAMON | 2021-09-01 15:45 | 2021-09-01 15:46 | 2147 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 9100 | B21090100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-01 | 2147 | keep | 0 | Sep | 2021 | 0.0014623 | 0.0014623 | Momentary | FALSE | TRUE | Not_TMED_Event | 2147
BAYAMON | 2021-09-01 15:45 | 2021-09-01 15:46 | 2858 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 9100 | B21090100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-01 | 2858 | keep | 0 | Sep | 2021 | 0.0019466 | 0.0019466 | Momentary | FALSE | TRUE | Not_TMED_Event | 2858
BAYAMON | 2021-09-01 15:46 | 2021-09-01 17:15 | 959 | 001:29 | T | NO SE REPORTO CAUSA | SE SECCIONALIZO Y SE CERRO POR SCADA | B21090100068 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 89 | 2021-09-01 | 85351 | keep | 0 | Sep | 2021 | 0.058132 | 0.00065317 | Sustained | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2021-09-01 15:46 | 2021-09-01 15:52 | 80 | 000:06 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21090100028 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 6 | 2021-09-01 | 480 | keep | 0 | Sep | 2021 | 0.00032693 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-09-01 15:51 | 2021-09-01 19:45 | 40 | 003:54 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | A21090100112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 234 | 2021-09-01 | 9360 | keep | 0 | Sep | 2021 | 0.0063751 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-01 15:52 | 2021-09-01 15:53 | 1420 | 000:01 | T | DESGANCHE | RECERRO LLEVA 1526-02 | S21090100000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-01 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-01 15:52 | 2021-09-01 15:53 | 437 | 000:01 | T | OTRAS CAUSAS | RECERRO LLEVA 1526-2 DESBALANCE | S21090100000 | 1st_after_momentary | Other Causes | Include | Include | Other | 1 | 2021-09-01 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2021-09-01 15:52 | 2021-09-01 15:53 | 4431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 4431 | keep | 0 | Sep | 2021 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
BAYAMON | 2021-09-01 15:52 | 2021-09-01 15:53 | 1514 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 9100 | B21090100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-01 | 1514 | keep | 0 | Sep | 2021 | 0.0010312 | 0.0010312 | Momentary | FALSE | TRUE | Not_TMED_Event | 1514
BAYAMON | 2021-09-01 15:52 | 2021-09-01 15:53 | 1105 | 000:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION 9100 | B21090100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2021-09-01 | 1105 | keep | 0 | Sep | 2021 | 0.00075261 | 0.00075261 | Momentary | FALSE | TRUE | Not_TMED_Event | 1105
SAN JUAN | 2021-09-01 15:53 | 2021-09-01 15:58 | 225 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO CARGA POR EL 1303-05 | S21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-09-01 | 1125 | keep | 0 | Sep | 2021 | 0.00076623 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
BAYAMON | 2021-09-01 15:53 | 2021-09-01 15:58 | 1984 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO LLEVA 1911-7 | S21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-09-01 | 9920 | keep | 0 | Sep | 2021 | 0.0067565 | 0.0013513 | Momentary | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2021-09-01 15:53 | 2021-09-01 15:54 | 2402 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 2402 | keep | 0 | Sep | 2021 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2021-09-01 15:53 | 2021-09-01 17:32 | 80 | 001:39 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21090100028 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 99 | 2021-09-01 | 7920 | keep | 0 | Sep | 2021 | 0.0053943 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-09-01 15:53 | 2021-09-01 15:58 | 577 | 000:05 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO CARGA POR EL 1529-12 | S21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-09-01 | 2885 | keep | 0 | Sep | 2021 | 0.001965 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
BAYAMON | 2021-09-01 15:56 | 2021-09-01 15:57 | 2402 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21090100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 2402 | keep | 0 | Sep | 2021 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
SAN JUAN | 2021-09-01 15:58 | 2021-09-01 15:59 | 870 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1303-4 | S21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 870 | keep | 0 | Sep | 2021 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2021-09-01 16:00 | 2021-09-01 16:01 | 3597 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 3597 | keep | 0 | Sep | 2021 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2021-09-01 16:01 | 2021-09-02 21:22 | 100 | 029:21 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | B21090100269 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1761 | 2021-09-01 | 176100 | keep | 0 | Sep | 2021 | 0.11994 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-01 16:08 | 2021-09-02 10:33 | 30 | 018:25 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21090100121 | New_Event | Bad Weather | Include | Include | Weather | 1105 | 2021-09-01 | 33150 | keep | 0 | Sep | 2021 | 0.022578 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-09-01 16:11 | 2021-09-01 18:01 | 6 | 001:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21090100045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 110 | 2021-09-01 | 660 | keep | 0 | Sep | 2021 | 0.00044952 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-09-01 16:15 | 2021-09-01 21:23 | 5961 | 005:08 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADORES PARTIDOS Y SE REPARO PRIMARIA Y SE CERRO POR SCADA LLEVA 1717-02 | B21090100104 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 308 | 2021-09-01 | 1835988 | keep | 0 | Sep | 2021 | 1.2505 | 0.00406 | Sustained | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2021-09-01 16:15 | 2021-09-01 21:23 | 850 | 005:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADORES PARTIDOS Y SE REPARO PRIMARIA Y SE CERRO POR SCADA EL 1713-05 QUE LLEVA 1717-02 | B21090100104 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 308 | 2021-09-01 | 261800 | keep | 0 | Sep | 2021 | 0.17831 | 0.00057893 | Sustained | FALSE | FALSE | Not_TMED_Event | 850
VEGA BAJA | 2021-09-01 16:17 | 2021-09-01 16:18 | 1284 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO Y SE CERRO POR CONTROL | B21090100000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-09-01 | 1284 | keep | 0 | Sep | 2021 | 0.00087453 | 0.00087453 | Momentary | FALSE | FALSE | Not_TMED_Event | 1284
VEGA BAJA | 2021-09-01 16:18 | 2021-09-02 11:01 | 20 | 018:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN RISER SE REMPLAZO CAJA PRIMARIA QUEMADA | B21090100210 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1123 | 2021-09-01 | 22460 | keep | 0 | Sep | 2021 | 0.015297 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-09-01 16:20 | 2021-09-01 16:21 | 2402 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA EL 1720-08 | B21090100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 2402 | keep | 0 | Sep | 2021 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2021-09-01 16:20 | 2021-09-01 16:21 | 1 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE LA CARGA SE ENCUENTRA POR EL 1709-02 | B21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 1 | keep | 0 | Sep | 2021 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-09-01 16:20 | 2021-09-01 17:40 | 1 | 001:20 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A21090100127 | New_Event | Bad Weather | Include | Include | Weather | 80 | 2021-09-01 | 80 | keep | 0 | Sep | 2021 | 5.4488e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-09-01 16:21 | 2021-09-01 16:26 | 6000 | 000:05 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA 90% 1336-7 Y 85% 1336-10 SE PROBO QUEDO EN SERVICIO CARGA POR EL 1620-04 | S21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2021-09-01 | 30000 | keep | 0 | Sep | 2021 | 0.020433 | 0.0040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 6000
SAN JUAN | 2021-09-01 16:21 | 2021-09-01 16:23 | 370 | 000:02 | P | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA 1620-1 LLEVA 90% 1336-7 SE PROBO QUEDO EN SERVICIO 85% DE LA CARGA SE ENCUENTRA POR EL 1620-04 | S21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-01 | 740 | keep | 0 | Sep | 2021 | 0.00050401 | 0.00025201 | Momentary | FALSE | FALSE | Not_TMED_Event | 370
SAN JUAN | 2021-09-01 16:21 | 2021-09-01 16:26 | 3718 | 000:05 | T | DESGANCHE | DISPARO CON RECIERRE EN OFF SE PROBO QUEDO EN SERVICIO | S21090100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 5 | 2021-09-01 | 18590 | keep | 0 | Sep | 2021 | 0.012662 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
SAN JUAN | 2021-09-01 16:23 | 2021-09-01 16:27 | 36 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA 90% 1336-7 Y 85% 1336-10 SE PROBO QUEDO EN SERVICIO CARGA DEL 1620-01 POR EL 1620-04 | S21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-09-01 | 144 | keep | 0 | Sep | 2021 | 9.8078e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-09-01 16:23 | 2021-09-01 16:27 | 172 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO CON R/R OFF LLEVA 1620-1 LLEVA 90% 1336-7 Y 85% 1336-10 SE PROBO QUEDO EN SERVICIO | S21090100000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-09-01 | 688 | keep | 0 | Sep | 2021 | 0.00046859 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2021-09-01 16:27 | 2021-09-02 19:33 | 20 | 027:06 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | S21090100061 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1626 | 2021-09-01 | 32520 | keep | 0 | Sep | 2021 | 0.022149 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-01 16:28 | 2021-09-01 18:10 | 1142 | 001:42 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE SECCIONALIZO LINEA PRIMARIA PARTIDA SE CERRO INTERRUPTOR | M21090100112 | New_Event | Wire Down | Include | Include | Equipment | 102 | 2021-09-01 | 116484 | keep | 0 | Sep | 2021 | 0.079337 | 0.00077781 | Sustained | FALSE | TRUE | Not_TMED_Event | 1142
ARECIBO | 2021-09-01 16:30 | 2021-09-01 19:00 | 10 | 002:30 | P | SOBRECARGA | INSTALAR TRANSFORMADOR DIVIDIR CARGA ERMCO 25 KVA 2400. OUR #668825 LOCATION-18.469384 / 66.930050 | A21090100056 | New_Event | Trip Due To Overload | Include | Include | Other | 150 | 2021-09-01 | 1500 | keep | 0 | Sep | 2021 | 0.0010216 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-09-01 16:38 | 2021-09-01 17:40 | 12 | 001:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA TRANSFORMADOR | S21090100160 | New_Event | Wire Down | Include | Include | Equipment | 62 | 2021-09-01 | 744 | keep | 0 | Sep | 2021 | 0.00050674 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-09-01 16:39 | 2021-09-01 22:20 | 7 | 005:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M21090100115 | New_Event | Bad Weather | Include | Include | Weather | 341 | 2021-09-01 | 2387 | keep | 0 | Sep | 2021 | 0.0016258 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-09-01 16:40 | 2021-09-01 16:41 | 112 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 112 | keep | 0 | Sep | 2021 | 7.6283e-05 | 7.6283e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 112
CAGUAS | 2021-09-01 16:41 | 2021-09-01 16:42 | 2608 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 2608 | keep | 0 | Sep | 2021 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
SAN JUAN | 2021-09-01 16:44 | 2021-09-01 16:45 | 837 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO CARGA POR EL 1401-07 | S21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 837 | keep | 0 | Sep | 2021 | 0.00057008 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2021-09-01 16:44 | 2021-09-01 16:45 | 908 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO LLAVA 1401-6 SE PROBO QUEDO EN SERVICIO | S21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 908 | keep | 0 | Sep | 2021 | 0.00061843 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
BAYAMON | 2021-09-01 16:46 | 2021-09-01 16:47 | 1746 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 1746 | keep | 0 | Sep | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
CAGUAS | 2021-09-01 16:48 | 2021-09-02 14:15 | 75 | 021:27 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | C21090100101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1287 | 2021-09-01 | 96525 | keep | 0 | Sep | 2021 | 0.065743 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
SAN JUAN | 2021-09-01 16:50 | 2021-09-01 22:53 | 40 | 006:03 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA Y SE REPORTA DESGANCHE | S21090100171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 363 | 2021-09-01 | 14520 | keep | 0 | Sep | 2021 | 0.0098895 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-09-01 16:52 | 2021-09-01 19:10 | 25 | 002:18 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA DESGANCHE | A21090100132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2021-09-01 | 3450 | keep | 0 | Sep | 2021 | 0.0023498 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
ARECIBO | 2021-09-01 17:00 | 2021-09-01 18:45 | 9 | 001:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES PRIMARIOS | A21090100131 | New_Event | Wire Down | Include | Include | Equipment | 105 | 2021-09-01 | 945 | keep | 0 | Sep | 2021 | 0.00064364 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2021-09-01 17:02 | 2021-09-01 21:58 | 100 | 004:56 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M21090100121 | New_Event | Bad Weather | Include | Include | Weather | 296 | 2021-09-01 | 29600 | keep | 0 | Sep | 2021 | 0.02016 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-09-01 17:08 | 2021-09-01 17:09 | 4882 | 000:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21090100000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2021-09-01 | 4882 | keep | 0 | Sep | 2021 | 0.0033251 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
VEGA BAJA | 2021-09-01 17:10 | 2021-09-01 19:39 | 25 | 002:29 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE CERRO PUENTE ABIERTO | B21090100147 | New_Event | Wire Down | Include | Include | Equipment | 149 | 2021-09-01 | 3725 | keep | 0 | Sep | 2021 | 0.0025371 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-09-01 17:12 | 2021-09-02 10:19 | 50 | 017:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA 1 X 10 EN TRANSFORMADOR Y SE REMPLAZO PORTAFUSIBLES | B21090100149 | New_Event | Cutout Failure | Include | Include | Equipment | 1027 | 2021-09-01 | 51350 | keep | 0 | Sep | 2021 | 0.034974 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-01 17:15 | 2021-09-01 17:16 | 500 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | B21090100068 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 500 | keep | 0 | Sep | 2021 | 0.00034055 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-01 17:15 | 2021-09-02 10:59 | 30 | 017:44 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA SE RETIRO AVE CRUZANDO LINEAS | S21090100185 | New_Event |  |  | Include | Wildlife | 1064 | 2021-09-01 | 31920 | keep | 0 | Sep | 2021 | 0.021741 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
VEGA BAJA | 2021-09-01 17:18 | 2021-09-01 17:49 | 6 | 000:31 | P | NO SE REPORTO CAUSA | 1 X 15 EN RISER HACIA TRANSFORMADOR | B21090100152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 31 | 2021-09-01 | 186 | keep | 0 | Sep | 2021 | 0.00012668 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2021-09-01 17:19 | 2021-09-01 17:20 | 2999 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6406-04 | M21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 2999 | keep | 0 | Sep | 2021 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
MAYAGÃœEZ | 2021-09-01 17:19 | 2021-09-01 17:20 | 1597 | 000:01 | T | NO SE REPORTO CAUSA | CARGA POR 6406-02 | M21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 1597 | keep | 0 | Sep | 2021 | 0.0010877 | 0.0010877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1597
ARECIBO | 2021-09-01 17:19 | 2021-09-01 20:45 | 10 | 003:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | A21090100136 | New_Event | Secondary Wire Down | Include | Include | Equipment | 206 | 2021-09-01 | 2060 | keep | 0 | Sep | 2021 | 0.0014031 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-01 17:20 | 2021-09-02 11:27 | 30 | 018:07 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA | B21090100155 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1087 | 2021-09-01 | 32610 | keep | 0 | Sep | 2021 | 0.022211 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
UTUADO | 2021-09-01 17:24 | 2021-09-01 21:25 | 40 | 004:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | A21090100138 | New_Event | Bad Weather | Include | Include | Weather | 241 | 2021-09-01 | 9640 | keep | 0 | Sep | 2021 | 0.0065658 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-09-01 17:26 | 2021-09-01 20:45 | 50 | 003:19 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21090100159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2021-09-01 | 9950 | keep | 0 | Sep | 2021 | 0.0067769 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-01 17:33 | 2021-09-01 23:15 | 13 | 005:42 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M21090100131 | New_Event | Bad Weather | Include | Include | Weather | 342 | 2021-09-01 | 4446 | keep | 0 | Sep | 2021 | 0.0030282 | 8.8542e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 13
BAYAMON | 2021-09-01 17:40 | 2021-09-01 17:48 | 200 | 000:08 | P | NO SE REPORTO CAUSA | SE SECCIONALIZO EN LA CALLE PASCUA Y SE CERRO MACHETE EN LA AVENIDA NOGAL | B21090100068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2021-09-01 | 1600 | keep | 0 | Sep | 2021 | 0.0010898 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-09-01 17:44 | 2021-09-01 17:45 | 776 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 776 | keep | 0 | Sep | 2021 | 0.00052853 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
CANOVANAS | 2021-09-01 17:48 | 2021-09-01 19:02 | 60 | 001:14 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R21090100057 | New_Event |  |  | Include | Wildlife | 74 | 2021-09-01 | 4440 | keep | 0 | Sep | 2021 | 0.0030241 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-09-01 17:49 | 2021-09-02 16:43 | 30 | 022:54 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA DESGANCHE | S21090100193 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1374 | 2021-09-01 | 41220 | keep | 0 | Sep | 2021 | 0.028075 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2021-09-01 17:49 | 2021-09-01 22:59 | 24 | 005:10 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA SE INSPECCIONO | R21090100058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 310 | 2021-09-01 | 7440 | keep | 0 | Sep | 2021 | 0.0050674 | 1.6346e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 24
SAN JUAN | 2021-09-01 17:50 | 2021-09-02 10:19 | 65 | 016:29 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21090100194 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 989 | 2021-09-01 | 64285 | keep | 0 | Sep | 2021 | 0.043784 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
BARRANQUITAS | 2021-09-01 17:50 | 2021-09-01 17:51 | 2635 | 000:01 | T | DESGANCHE | RECIERRE | C21090100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-01 | 2635 | keep | 0 | Sep | 2021 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2021-09-01 17:51 | 2021-09-02 16:09 | 235 | 022:18 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | C21090100108 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1338 | 2021-09-01 | 314430 | keep | 0 | Sep | 2021 | 0.21416 | 0.00016006 | Sustained | FALSE | TRUE | Not_TMED_Event | 235
PONCE | 2021-09-01 18:01 | 2021-09-01 18:04 | 3744 | 000:03 | T | ANIMAL U OBJETO EXTRAÃ‘O | DISPARO INTERRUPTOR. SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P21090100139 | New_Event |  |  | Include | Wildlife | 3 | 2021-09-01 | 11232 | keep | 0 | Sep | 2021 | 0.0076501 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2021-09-01 18:01 | 2021-09-01 18:04 | 3114 | 000:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 5004-06. SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P21090100139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2021-09-01 | 9342 | keep | 0 | Sep | 2021 | 0.0063628 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
BAYAMON | 2021-09-01 18:02 | 2021-09-01 19:12 | 60 | 001:10 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 70 | 2021-09-01 | 4200 | keep | 0 | Sep | 2021 | 0.0028606 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
PONCE | 2021-09-01 18:04 | 2021-09-02 11:45 | 33 | 017:41 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA POR AVE | P21090100141 | 1st_after_momentary |  |  | Include | Wildlife | 1061 | 2021-09-01 | 35013 | keep | 0 | Sep | 2021 | 0.023847 | 2.2476e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 33
MAYAGÃœEZ | 2021-09-01 18:06 | 2021-09-01 18:07 | 1287 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M21090100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 1287 | keep | 0 | Sep | 2021 | 0.00087657 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
BAYAMON | 2021-09-01 18:08 | 2021-09-01 21:13 | 100 | 003:05 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE ABRIO PUENTES HACIA TRAMO DE LINEA TRASPATIO EN EL SUELO QUE ALIMENTA UN TRANSFORMADOR | B21090100184 | New_Event | Wire Down | Include | Include | Equipment | 185 | 2021-09-01 | 18500 | keep | 0 | Sep | 2021 | 0.0126 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
MAYAGÃœEZ | 2021-09-01 18:10 | 2021-09-01 20:00 | 1100 | 001:50 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA ROTA SE CERRO MACHETES | M21090100142 | Partial_restoration | Wire Down | Include | Include | Equipment | 110 | 2021-09-01 | 121000 | keep | 0 | Sep | 2021 | 0.082413 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-09-01 18:17 | 2021-09-01 20:25 | 20 | 002:08 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21090100146 | New_Event | Bad Weather | Include | Include | Weather | 128 | 2021-09-01 | 2560 | keep | 0 | Sep | 2021 | 0.0017436 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-09-01 18:20 | 2021-09-01 19:20 | 10 | 001:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21090100147 | New_Event | Bad Weather | Include | Include | Weather | 60 | 2021-09-01 | 600 | keep | 0 | Sep | 2021 | 0.00040866 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-09-01 18:22 | 2021-09-01 20:11 | 25 | 001:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21090100149 | New_Event | Bad Weather | Include | Include | Weather | 109 | 2021-09-01 | 2725 | keep | 0 | Sep | 2021 | 0.001856 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
VEGA BAJA | 2021-09-01 18:24 | 2021-09-01 21:36 | 100 | 003:12 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | B21090100189 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 192 | 2021-09-01 | 19200 | keep | 0 | Sep | 2021 | 0.013077 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
CAGUAS | 2021-09-01 18:25 | 2021-09-03 15:50 | 23 | 045:25 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | C21090100109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2725 | 2021-09-01 | 62675 | keep | 0 | Sep | 2021 | 0.042688 | 1.5665e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 23
SAN JUAN | 2021-09-01 18:43 | 2021-09-02 13:03 | 40 | 018:20 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S21090100198 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1100 | 2021-09-01 | 44000 | keep | 0 | Sep | 2021 | 0.029968 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-01 18:49 | 2021-09-02 19:19 | 22 | 024:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR 50KVA | B21090100206 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1470 | 2021-09-01 | 32340 | keep | 0 | Sep | 2021 | 0.022027 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
BAYAMON | 2021-09-01 19:00 | 2021-09-01 19:01 | 4431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21090100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 4431 | keep | 0 | Sep | 2021 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
BAYAMON | 2021-09-01 19:18 | 2021-09-01 19:22 | 60 | 000:04 | P | NO SE REPORTO CAUSA | 1 X 125 EN SU-22 A FASE A SE ABRE INTERRUPTOR PARA REMPLAZAR FUSIBLE EN BOVEDA EDIFICIO LUCHETTI A PETICION ANGEL CALO LLEVA 1115-04, 1115-03 Y 50 % 1115-02 | S21090100208 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-09-01 | 240 | keep | 0 | Sep | 2021 | 0.00016346 | 4.0866e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-09-01 19:18 | 2021-09-01 19:22 | 134 | 000:04 | T | NO SE REPORTO CAUSA | 1 X 125 EN SU-22 A FASE A SE ABRE INTERRUPTOR PARA REMPLAZAR FUSIBLE EN BOVEDA EDIFICIO LUCHETTI A PETICION ANGEL CALO LLEVA 1115-04, 1115-03 Y 50 % 1115-02 | S21090100208 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-09-01 | 536 | keep | 0 | Sep | 2021 | 0.00036507 | 9.1267e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 134
BAYAMON | 2021-09-01 19:18 | 2021-09-01 19:22 | 114 | 000:04 | T | NO SE REPORTO CAUSA | 1 X 125 EN SU-22 A FASE A SE ABRE INTERRUPTOR PARA REMPLAZAR FUSIBLE EN BOVEDA EDIFICIO LUCHETTI A PETICION ANGEL CALO LLEVA 1115-04, 1115-03 Y 50 % 1115-02 | S21090100208 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-09-01 | 456 | keep | 0 | Sep | 2021 | 0.00031058 | 7.7645e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 114
BAYAMON | 2021-09-01 19:18 | 2021-09-01 19:22 | 316 | 000:04 | T | NO SE REPORTO CAUSA | 1 X 125 EN SU-22 A FASE A SE ABRE INTERRUPTOR PARA REMPLAZAR FUSIBLE EN BOVEDA EDIFICIO LUCHETTI A PETICION ANGEL CALO LLEVA 1115-04, 1115-03 Y 50 % 1115-02 | S21090100208 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-09-01 | 1264 | keep | 0 | Sep | 2021 | 0.0008609 | 0.00021523 | Momentary | FALSE | FALSE | Not_TMED_Event | 316
PONCE | 2021-09-01 19:19 | 2021-09-02 11:20 | 385 | 016:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21090100144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 961 | 2021-09-01 | 369985 | keep | 0 | Sep | 2021 | 0.252 | 0.00026222 | Sustained | FALSE | TRUE | Not_TMED_Event | 385
CANOVANAS | 2021-09-01 19:22 | 2021-09-01 19:56 | 9 | 000:34 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR | R21090100066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 34 | 2021-09-01 | 306 | keep | 0 | Sep | 2021 | 0.00020842 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2021-09-01 19:40 | 2021-09-01 19:41 | 1514 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21090100236 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 1514 | keep | 0 | Sep | 2021 | 0.0010312 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
AGUADILLA | 2021-09-01 20:08 | 2021-09-01 21:35 | 4882 | 001:27 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO INTERRUPTOR PARA REMPLAZO DE AISLADOR PARTIDO EN TRONCAL DEL ALIMENTADOR | M21090100161 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 87 | 2021-09-01 | 424734 | keep | 0 | Sep | 2021 | 0.28928 | 0.0033251 | Sustained | FALSE | FALSE | Not_TMED_Event | 4882
BAYAMON | 2021-09-01 20:19 | 2021-09-02 15:26 | 35 | 019:07 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21090100245 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1147 | 2021-09-01 | 40145 | keep | 0 | Sep | 2021 | 0.027343 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
PONCE | 2021-09-01 20:20 | 2021-09-02 10:00 | 838 | 013:40 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | P21090100153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 820 | 2021-09-01 | 687160 | keep | 0 | Sep | 2021 | 0.46802 | 0.00057076 | Sustained | FALSE | TRUE | Not_TMED_Event | 838
FAJARDO | 2021-09-01 20:55 | 2021-09-02 12:12 | 12 | 015:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | R21090100071 | New_Event | Cutout Failure | Include | Include | Equipment | 917 | 2021-09-01 | 11004 | keep | 0 | Sep | 2021 | 0.0074948 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-09-01 21:00 | 2021-09-02 09:42 | 40 | 012:42 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S21090100220 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 762 | 2021-09-01 | 30480 | keep | 0 | Sep | 2021 | 0.02076 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CANOVANAS | 2021-09-01 21:06 | 2021-09-01 23:15 | 34 | 002:09 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE DESGANCHO | R21091000072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2021-09-01 | 4386 | keep | 0 | Sep | 2021 | 0.0029873 | 2.3157e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 34
BAYAMON | 2021-09-01 21:19 | 2021-09-03 15:07 | 50 | 041:48 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE CAJA A LINEA | B21090100263 | New_Event | Wire Down | Include | Include | Equipment | 2508 | 2021-09-01 | 125400 | keep | 0 | Sep | 2021 | 0.085409 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-01 21:37 | 2021-09-02 12:26 | 10 | 014:49 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S21090100224 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 889 | 2021-09-01 | 8890 | keep | 0 | Sep | 2021 | 0.0060549 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-09-01 21:41 | 2021-09-02 10:18 | 25 | 012:37 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21090100225 | New_Event | Vegetation Contact | Include | Include | Vegetation | 757 | 2021-09-01 | 18925 | keep | 0 | Sep | 2021 | 0.01289 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BARRANQUITAS | 2021-09-01 22:24 | 2021-09-02 18:54 | 253 | 020:30 | P | ESTRUCTURA AVERIADA | 1 X 100 Y 1 X 65 EN CORTES DE LINEA SE REEMPLAZO 2 POSTES PRIMARIOS | C21090100130 | New_Event | Defective Pole | Include | Include | Equipment | 1230 | 2021-09-01 | 311190 | keep | 0 | Sep | 2021 | 0.21195 | 0.00017232 | Sustained | FALSE | TRUE | Not_TMED_Event | 253
MAYAGÃœEZ | 2021-09-01 22:35 | 2021-09-02 17:35 | 80 | 019:00 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M21090100181 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1140 | 2021-09-01 | 91200 | keep | 0 | Sep | 2021 | 0.062116 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
GUAYAMA | 2021-09-01 22:39 | 2021-09-02 15:59 | 10 | 017:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REMPLAZARON CONECTORES EN SECUNDARIA | P21090100163 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1040 | 2021-09-01 | 10400 | keep | 0 | Sep | 2021 | 0.0070834 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-09-01 22:41 | 2021-09-01 22:42 | 539 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 539 | keep | 0 | Sep | 2021 | 0.00036711 | 0.00036711 | Momentary | FALSE | FALSE | Not_TMED_Event | 539
BAYAMON | 2021-09-01 22:43 | 2021-09-01 23:47 | 3295 | 001:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA LEVANTAR LINEA PRIMARIA | B21090100059 | Additional_clients | Wire Down | Include | Include | Equipment | 64 | 2021-09-01 | 210880 | keep | 0 | Sep | 2021 | 0.14363 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
HUMACAO | 2021-09-01 23:17 | 2021-09-02 10:11 | 65 | 010:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA REEMPLAZO CAJA PRIMARIA | C21090100136 | New_Event | Cutout Failure | Include | Include | Equipment | 654 | 2021-09-01 | 42510 | keep | 0 | Sep | 2021 | 0.028953 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
CAGUAS | 2021-09-01 23:19 | 2021-09-02 12:51 | 4 | 013:32 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA ROTA | C21090100342 | New_Event | Secondary Wire Down | Include | Include | Equipment | 812 | 2021-09-01 | 3248 | keep | 0 | Sep | 2021 | 0.0022122 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2021-09-01 23:46 | 2021-09-01 23:47 | 1287 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-01 | 1287 | keep | 0 | Sep | 2021 | 0.00087657 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
UTUADO | 2021-09-02 00:01 | 2021-09-02 14:35 | 30 | 014:34 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A20190200021 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 874 | 2021-09-02 | 26220 | keep | 0 | Sep | 2021 | 0.017858 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
FAJARDO | 2021-09-02 00:22 | 2021-09-02 12:18 | 50 | 011:56 | P | DESGANCHE | 1 X 40 Y 1 X 25 EN CORTES DE LINEA SE DESGANCHO | R21090200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 716 | 2021-09-02 | 35800 | keep | 0 | Sep | 2021 | 0.024383 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CANOVANAS | 2021-09-02 01:05 | 2021-09-02 08:51 | 15 | 007:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 10 EN TRANSFORMADOR CRUCE DE LINEAS 13 KV CON 8 KV | R21090200002 | New_Event | Wire Down | Include | Include | Equipment | 466 | 2021-09-02 | 6990 | keep | 0 | Sep | 2021 | 0.0047609 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-09-02 01:30 | 2021-09-02 01:31 | 1983 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA CARGA TRANSFERIDA AL 1801-02 | B21090200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-02 | 1983 | keep | 0 | Sep | 2021 | 0.0013506 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2021-09-02 01:30 | 2021-09-02 01:31 | 186 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR SCADA LLEVA LA CARGA DEL 1711-04 | B21090200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-02 | 186 | keep | 0 | Sep | 2021 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
AGUADILLA | 2021-09-02 02:00 | 2021-09-03 00:45 | 100 | 022:45 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | M21090200227 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1365 | 2021-09-02 | 136500 | keep | 0 | Sep | 2021 | 0.09297 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-09-02 02:43 | 2021-09-02 02:44 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21090200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-02 | 308 | keep | 0 | Sep | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
CAGUAS | 2021-09-02 03:18 | 2021-09-02 10:31 | 95 | 007:13 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 40 EN CORTES DE LINEAS | C21090200004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 433 | 2021-09-02 | 41135 | keep | 0 | Sep | 2021 | 0.028017 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
SAN JUAN | 2021-09-02 03:29 | 2021-09-02 04:29 | 844 | 001:00 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO LOCAL | S21090200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 60 | 2021-09-02 | 50640 | keep | 0 | Sep | 2021 | 0.034491 | 0.00057484 | Sustained | FALSE | FALSE | Not_TMED_Event | 844
AGUADILLA | 2021-09-02 03:56 | 2021-09-02 23:10 | 100 | 019:14 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M21090200003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1154 | 2021-09-02 | 115400 | keep | 0 | Sep | 2021 | 0.078598 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-09-02 04:04 | 2021-09-02 04:05 | 6481 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S21090200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-02 | 6481 | keep | 0 | Sep | 2021 | 0.0044142 | 0.0044142 | Momentary | FALSE | FALSE | Not_TMED_Event | 6481
ARECIBO | 2021-09-02 04:25 | 2021-09-02 18:55 | 20 | 014:30 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21090200084 | New_Event | Wire Down | Include | Include | Equipment | 870 | 2021-09-02 | 17400 | keep | 0 | Sep | 2021 | 0.011851 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-09-02 04:42 | 2021-09-02 09:26 | 95 | 004:44 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C21090200005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 284 | 2021-09-02 | 26980 | keep | 0 | Sep | 2021 | 0.018376 | 6.4704e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 95
BARRANQUITAS | 2021-09-02 05:01 | 2021-09-02 20:18 | 197 | 015:17 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | C21090200006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 917 | 2021-09-02 | 180649 | keep | 0 | Sep | 2021 | 0.12304 | 0.00013418 | Sustained | FALSE | TRUE | Not_TMED_Event | 197
BAYAMON | 2021-09-02 05:25 | 2021-09-02 05:26 | 2402 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | S21090200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-02 | 2402 | keep | 0 | Sep | 2021 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2021-09-02 05:26 | 2021-09-02 20:33 | 200 | 015:07 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | S21090200017 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 907 | 2021-09-02 | 181400 | keep | 0 | Sep | 2021 | 0.12355 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-09-02 05:44 | 2021-09-02 09:20 | 1 | 003:36 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A21090200004 | New_Event | Wire Down | Include | Include | Equipment | 216 | 2021-09-02 | 216 | keep | 0 | Sep | 2021 | 0.00014712 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
SAN JUAN | 2021-09-02 05:56 | 2021-09-02 05:57 | 837 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO 1401-07 Y SE CERRO POR SCADA CARGA POR EL 1401-07 | S21090200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-02 | 837 | keep | 0 | Sep | 2021 | 0.00057008 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2021-09-02 05:56 | 2021-09-02 05:57 | 908 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA LLEVADO LA CARGA DEL 1401-06 | S21090200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-02 | 908 | keep | 0 | Sep | 2021 | 0.00061843 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
BAYAMON | 2021-09-02 06:00 | 2021-09-02 06:01 | 4089 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21090200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-02 | 4089 | keep | 0 | Sep | 2021 | 0.002785 | 0.002785 | Momentary | FALSE | FALSE | Not_TMED_Event | 4089
AGUADILLA | 2021-09-02 06:00 | 2021-09-02 20:45 | 200 | 014:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M21090200004 | New_Event | Wire Down | Include | Include | Equipment | 885 | 2021-09-02 | 177000 | keep | 0 | Sep | 2021 | 0.12055 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-09-02 06:27 | 2021-09-02 10:00 | 75 | 003:33 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21090200005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2021-09-02 | 15975 | keep | 0 | Sep | 2021 | 0.01088 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
AGUADILLA | 2021-09-02 06:57 | 2021-09-02 06:58 | 1827 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE DE INTERRUPTOR | M21090200011 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-02 | 1827 | keep | 0 | Sep | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
UTUADO | 2021-09-02 06:57 | 2021-09-02 11:10 | 25 | 004:13 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21090200007 | New_Event | Bad Weather | Include | Include | Weather | 253 | 2021-09-02 | 6325 | keep | 0 | Sep | 2021 | 0.0043079 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
MAYAGÃœEZ | 2021-09-02 06:58 | 2021-09-02 14:50 | 25 | 007:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE RETEZARON LINEAS PRIMARIAS CRUZADAS | M21090200008 | New_Event | Wire Down | Include | Include | Equipment | 472 | 2021-09-02 | 11800 | keep | 0 | Sep | 2021 | 0.0080369 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
AGUADILLA | 2021-09-02 06:58 | 2021-09-02 21:45 | 40 | 014:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | M21090200018 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 887 | 2021-09-02 | 35480 | keep | 0 | Sep | 2021 | 0.024165 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-02 07:05 | 2021-09-02 10:26 | 483 | 003:21 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 200 EN CORTE DE LINEA CRUCE POR AVE | R21090200016 | New_Event |  |  | Include | Wildlife | 201 | 2021-09-02 | 97083 | keep | 0 | Sep | 2021 | 0.066123 | 0.00032897 | Sustained | FALSE | TRUE | Not_TMED_Event | 483
BAYAMON | 2021-09-02 07:11 | 2021-09-03 17:25 | 10 | 034:14 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21090200009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2054 | 2021-09-02 | 20540 | keep | 0 | Sep | 2021 | 0.01399 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-02 07:16 | 2021-09-02 10:15 | 1 | 002:59 | P | DESGANCHE | 3 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21090200009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2021-09-02 | 179 | keep | 0 | Sep | 2021 | 0.00012192 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
AGUADILLA | 2021-09-02 07:19 | 2021-09-02 15:45 | 60 | 008:26 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | M21090200013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 506 | 2021-09-02 | 30360 | keep | 0 | Sep | 2021 | 0.020678 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-09-02 07:21 | 2021-09-02 10:39 | 90 | 003:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | R21090200008 | New_Event |  |  | Include | Wildlife | 198 | 2021-09-02 | 17820 | keep | 0 | Sep | 2021 | 0.012137 | 6.1299e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 90
ARECIBO | 2021-09-02 07:24 | 2021-09-02 11:10 | 30 | 003:46 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21090200010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2021-09-02 | 6780 | keep | 0 | Sep | 2021 | 0.0046178 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-09-02 07:30 | 2021-09-02 15:21 | 50 | 007:51 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21090200010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 471 | 2021-09-02 | 23550 | keep | 0 | Sep | 2021 | 0.01604 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-02 07:37 | 2021-09-02 12:21 | 30 | 004:44 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21090200012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 284 | 2021-09-02 | 8520 | keep | 0 | Sep | 2021 | 0.0058029 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-02 07:42 | 2021-09-02 10:00 | 1 | 002:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 2 X 30 EN RISER AVE CRUZO LINEAS | A21090200011 | New_Event |  |  | Include | Wildlife | 138 | 2021-09-02 | 138 | keep | 0 | Sep | 2021 | 9.3991e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-09-02 07:44 | 2021-09-02 10:44 | 50 | 003:00 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C21090200013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2021-09-02 | 9000 | keep | 0 | Sep | 2021 | 0.0061299 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-02 07:52 | 2021-09-02 19:47 | 10 | 011:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S21090200016 | New_Event | Secondary Wire Down | Include | Include | Equipment | 715 | 2021-09-02 | 7150 | keep | 0 | Sep | 2021 | 0.0048698 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-02 08:03 | 2021-09-02 10:34 | 30 | 002:31 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21090200012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2021-09-02 | 4530 | keep | 0 | Sep | 2021 | 0.0030854 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
MAYAGÃœEZ | 2021-09-02 08:05 | 2021-09-02 16:00 | 50 | 007:55 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | M21090200019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 475 | 2021-09-02 | 23750 | keep | 0 | Sep | 2021 | 0.016176 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
GUAYAMA | 2021-09-02 08:08 | 2021-09-02 13:00 | 10 | 004:52 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REEMPLAZARON CONECTORES EN SECUNDARIA | P21090200005 | New_Event | Secondary Wire Down | Include | Include | Equipment | 292 | 2021-09-02 | 2920 | keep | 0 | Sep | 2021 | 0.0019888 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2021-09-02 08:10 | 2021-09-02 15:40 | 80 | 007:30 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR 25MVA X 37.5MVA | S21083100026 | New_Event | Service Transformer Failure | Include | Include | Equipment | 450 | 2021-09-02 | 36000 | keep | 0 | Sep | 2021 | 0.024519 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2021-09-02 08:10 | 2021-09-02 10:45 | 5 | 002:35 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR TOMA | C21090200015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 155 | 2021-09-02 | 775 | keep | 0 | Sep | 2021 | 0.00052785 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-09-02 08:16 | 2021-09-02 16:40 | 40 | 008:24 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21090200014 | New_Event | Bad Weather | Include | Include | Weather | 504 | 2021-09-02 | 20160 | keep | 0 | Sep | 2021 | 0.013731 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-09-02 08:25 | 2021-09-04 19:07 | 1 | 058:42 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21090200018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3522 | 2021-09-02 | 3522 | keep | 0 | Sep | 2021 | 0.0023988 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2021-09-02 08:26 | 2021-09-02 11:30 | 99 | 003:04 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | P21090200007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2021-09-02 | 18216 | keep | 0 | Sep | 2021 | 0.012407 | 6.7428e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 99
MAYAGÃœEZ | 2021-09-02 08:29 | 2021-09-02 13:30 | 25 | 005:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | M21090200023 | New_Event | Bad Weather | Include | Include | Weather | 301 | 2021-09-02 | 7525 | keep | 0 | Sep | 2021 | 0.0051252 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
FAJARDO | 2021-09-02 08:35 | 2021-09-02 14:18 | 20 | 005:43 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA DESGANCHE | R21090200012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 343 | 2021-09-02 | 6860 | keep | 0 | Sep | 2021 | 0.0046723 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
MAYAGÃœEZ | 2021-09-02 08:35 | 2021-09-02 12:00 | 10 | 003:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M21090200029 | New_Event | Wire Down | Include | Include | Equipment | 205 | 2021-09-02 | 2050 | keep | 0 | Sep | 2021 | 0.0013962 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-09-02 08:42 | 2021-09-02 19:35 | 8 | 010:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21090200016 | New_Event | Bad Weather | Include | Include | Weather | 653 | 2021-09-02 | 5224 | keep | 0 | Sep | 2021 | 0.003558 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-09-02 08:53 | 2021-09-02 08:54 | 308 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21090200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-02 | 308 | keep | 0 | Sep | 2021 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
CANOVANAS | 2021-09-02 08:58 | 2021-09-02 09:35 | 8 | 000:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 15 EN TRANSFORMADOR CRUCE DE LINEAS 13 KV CON 8 KV | R21090200014 | New_Event | Wire Down | Include | Include | Equipment | 37 | 2021-09-02 | 296 | keep | 0 | Sep | 2021 | 0.0002016 | 5.4488e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 8
YAUCO | 2021-09-02 09:08 | 2021-09-02 12:45 | 80 | 003:37 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P21090200010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2021-09-02 | 17360 | keep | 0 | Sep | 2021 | 0.011824 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-09-02 09:10 | 2021-09-02 13:22 | 40 | 004:12 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | S21090200034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 252 | 2021-09-02 | 10080 | keep | 0 | Sep | 2021 | 0.0068654 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-02 09:30 | 2021-09-03 13:14 | 10 | 027:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE DE LINEA A CAJA DE TRANSFORMADOR | S21090300030 | New_Event | Wire Down | Include | Include | Equipment | 1664 | 2021-09-02 | 16640 | keep | 0 | Sep | 2021 | 0.011333 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
GUAYAMA | 2021-09-02 09:36 | 2021-09-02 15:25 | 839 | 005:49 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE REEMPLAZO POSTE PARTIDO POR ACCIDENTE DE AUTO | P21090200012 | New_Event |  |  | Include | Wildlife | 349 | 2021-09-02 | 292811 | keep | 0 | Sep | 2021 | 0.19943 | 0.00057144 | Sustained | FALSE | FALSE | Not_TMED_Event | 839
MAYAGÃœEZ | 2021-09-02 09:59 | 2021-09-02 18:30 | 75 | 008:31 | P | OTRAS CAUSAS | SE ABRIO CORTE DE LINEA PARA RELOCALIZAR LINEAS PRIMARIAS DEL FID-19533084 AL FID-1000131579 | M21090200042 | New_Event | Other Causes | Include | Include | Other | 511 | 2021-09-02 | 38325 | keep | 0 | Sep | 2021 | 0.026103 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
AGUADILLA | 2021-09-02 10:14 | 2021-09-02 19:55 | 15 | 009:41 | P | OTRAS CAUSAS | SE ABRIO PUENTE PRIMARIO PARA REGAR LINEA PRIMARIA A POSTE Y TRANSFORMADOR NUEVO | M21090200045 | New_Event | Other Causes | Include | Include | Other | 581 | 2021-09-02 | 8715 | keep | 0 | Sep | 2021 | 0.0059357 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
SAN JUAN | 2021-09-02 10:24 | 2021-09-02 18:07 | 25 | 007:43 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | S21090100225 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 463 | 2021-09-02 | 11575 | keep | 0 | Sep | 2021 | 0.0078837 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-09-02 10:25 | 2021-09-02 15:00 | 50 | 004:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA 1 X 10 EN TRANSFORMADOR Y SE REMPLAZO PORTAFUSIBLES | B21090100149 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 275 | 2021-09-02 | 13750 | keep | 0 | Sep | 2021 | 0.0093651 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
SAN JUAN | 2021-09-02 10:26 | 2021-09-03 20:06 | 40 | 033:40 | P | CABLE SOTERRADO AVERIADO | 1 X 20 EN CORTE DE LINEA SE CONSTRUYO AEREO PROVICIONAL DE T - 16 A T - 15 | R21090200009 | New_Event | UG Cable Fault | Include | Include | Equipment | 2020 | 2021-09-02 | 80800 | keep | 0 | Sep | 2021 | 0.055033 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-02 10:27 | 2021-09-02 15:39 | 269 | 005:12 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S21090200022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 312 | 2021-09-02 | 83928 | keep | 0 | Sep | 2021 | 0.057163 | 0.00018321 | Sustained | FALSE | TRUE | Not_TMED_Event | 269
AGUADILLA | 2021-09-02 10:33 | 2021-09-02 15:17 | 1047 | 004:44 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA REPARAR LINEA PRIMARIA PARTIDA | M21090200052 | New_Event | Wire Down | Include | Include | Equipment | 284 | 2021-09-02 | 297348 | keep | 0 | Sep | 2021 | 0.20252 | 0.00071311 | Sustained | FALSE | TRUE | Not_TMED_Event | 1047
BAYAMON | 2021-09-02 10:33 | 2021-09-02 13:24 | 15 | 002:51 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21090100024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 171 | 2021-09-02 | 2565 | keep | 0 | Sep | 2021 | 0.001747 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BARRANQUITAS | 2021-09-02 10:39 | 2021-09-02 21:00 | 118 | 010:21 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | C21090200064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 621 | 2021-09-02 | 73278 | keep | 0 | Sep | 2021 | 0.049909 | 8.0369e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 118
VEGA BAJA | 2021-09-02 10:42 | 2021-09-02 15:01 | 8 | 004:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | B21090200045 | New_Event | Secondary Wire Down | Include | Include | Equipment | 259 | 2021-09-02 | 2072 | keep | 0 | Sep | 2021 | 0.0014112 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-09-02 10:49 | 2021-09-02 14:00 | 25 | 003:11 | P | DESGANCHE | 1 X 20 EN CONVERTIDOR SE RETIRO RAMAS SOBRE LAS LINEAS | A21090200032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2021-09-02 | 4775 | keep | 0 | Sep | 2021 | 0.0032522 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
BAYAMON | 2021-09-02 10:58 | 2021-09-03 16:03 | 30 | 029:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE DESGANCHO | B21090200046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1745 | 2021-09-02 | 52350 | keep | 0 | Sep | 2021 | 0.035655 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-02 11:03 | 2021-09-02 17:25 | 10 | 006:22 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | A21090200035 | New_Event | Bad Weather | Include | Include | Weather | 382 | 2021-09-02 | 3820 | keep | 0 | Sep | 2021 | 0.0026018 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-02 11:24 | 2021-09-02 20:35 | 20 | 009:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A21090200036 | New_Event | Bad Weather | Include | Include | Weather | 551 | 2021-09-02 | 11020 | keep | 0 | Sep | 2021 | 0.0075057 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-09-02 11:31 | 2021-09-02 15:07 | 1 | 003:36 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO BAJANTE SECUNDARIO | C21090200075 | New_Event | Secondary Wire Down | Include | Include | Equipment | 216 | 2021-09-02 | 216 | keep | 0 | Sep | 2021 | 0.00014712 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2021-09-02 11:31 | 2021-09-02 13:42 | 10 | 002:11 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO ABIERTO | M21090200062 | New_Event | Wire Down | Include | Include | Equipment | 131 | 2021-09-02 | 1310 | keep | 0 | Sep | 2021 | 0.00089224 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-02 11:35 | 2021-09-02 11:59 | 7 | 000:24 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO TRANSFORMADOR PARA REMPLAZAR AISLADORES | A21090200070 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 24 | 2021-09-02 | 168 | keep | 0 | Sep | 2021 | 0.00011442 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2021-09-02 11:37 | 2021-09-02 19:26 | 235 | 007:49 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 2 X 80 EN SU-4, 2 X 65 EN RISER Y 2 X 30 EN CORTE DE LINEA CONTAMINACION | B21090200049 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 469 | 2021-09-02 | 110215 | keep | 0 | Sep | 2021 | 0.075067 | 0.00016006 | Sustained | FALSE | TRUE | Not_TMED_Event | 235
SAN JUAN | 2021-09-02 11:54 | 2021-09-02 17:17 | 50 | 005:23 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE FIJO LINEA | S21090200072 | New_Event | Wire Down | Include | Include | Equipment | 323 | 2021-09-02 | 16150 | keep | 0 | Sep | 2021 | 0.011 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-02 11:54 | 2021-09-02 18:19 | 4 | 006:25 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | C21090200065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 385 | 2021-09-02 | 1540 | keep | 0 | Sep | 2021 | 0.0010489 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
ARECIBO | 2021-09-02 12:00 | 2021-09-02 15:00 | 10 | 003:00 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | A21090200048 | New_Event | Secondary Wire Down | Include | Include | Equipment | 180 | 2021-09-02 | 1800 | keep | 0 | Sep | 2021 | 0.001226 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BAYAMON | 2021-09-02 12:08 | 2021-09-03 16:03 | 30 | 027:55 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21090200053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1675 | 2021-09-02 | 50250 | keep | 0 | Sep | 2021 | 0.034225 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CANOVANAS | 2021-09-02 12:12 | 2021-09-02 12:15 | 2039 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA II DE 115 KV DE CANOVANAS TC AL CERRAR BANCO DE CAPACITORES | R21090200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-09-02 | 6117 | keep | 0 | Sep | 2021 | 0.0041663 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
CANOVANAS | 2021-09-02 12:12 | 2021-09-02 12:15 | 4188 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA II DE 115 KV DE CANOVANAS TC AL CERRAR BANCO DE CAPACITORES | R21090200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-09-02 | 12564 | keep | 0 | Sep | 2021 | 0.0085573 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2021-09-02 12:12 | 2021-09-02 12:15 | 4085 | 000:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA II DE 115 KV DE CANOVANAS TC AL CERRAR BANCO DE CAPACITORES | R21090200000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2021-09-02 | 12255 | keep | 0 | Sep | 2021 | 0.0083468 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
UTUADO | 2021-09-02 12:16 | 2021-09-02 18:00 | 15 | 005:44 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21090200056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 344 | 2021-09-02 | 5160 | keep | 0 | Sep | 2021 | 0.0035145 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
GUAYAMA | 2021-09-02 12:30 | 2021-09-02 12:31 | 15 | 000:01 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | P21090200004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-02 | 15 | keep | 0 | Sep | 2021 | 1.0216e-05 | 1.0216e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2021-09-02 12:38 | 2021-09-02 14:54 | 14 | 002:16 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 25 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR CRUCE POR CULEBRA | C21090200098 | New_Event |  |  | Include | Wildlife | 136 | 2021-09-02 | 1904 | keep | 0 | Sep | 2021 | 0.0012968 | 9.5353e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 14
CAGUAS | 2021-09-02 12:49 | 2021-09-02 16:20 | 45 | 003:31 | P | ESTRUCTURA AVERIADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO POSTE PRIMARIO | C21090200100 | New_Event | Defective Pole | Include | Include | Equipment | 211 | 2021-09-02 | 9495 | keep | 0 | Sep | 2021 | 0.006467 | 3.0649e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 45
ARECIBO | 2021-09-02 12:53 | 2021-09-02 13:40 | 1212 | 000:47 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REPARO LINEA ZAFADA DE AISLADOR SE CERRO MACHETES | A21090200068 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 47 | 2021-09-02 | 56964 | keep | 0 | Sep | 2021 | 0.038798 | 0.00082549 | Sustained | FALSE | TRUE | Not_TMED_Event | 1212
BAYAMON | 2021-09-02 12:58 | 2021-09-02 14:34 | 35 | 001:36 | P | DESGANCHE | 1 X 40 EN CORETE DE LINEA SE REALIZO DESGANCHE | B21090200063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2021-09-02 | 3360 | keep | 0 | Sep | 2021 | 0.0022885 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
PONCE | 2021-09-02 13:01 | 2021-09-02 16:33 | 65 | 003:32 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P21090200029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2021-09-02 | 13780 | keep | 0 | Sep | 2021 | 0.0093855 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
CANOVANAS | 2021-09-02 13:22 | 2021-09-02 13:23 | 2106 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | R21090200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-02 | 2106 | keep | 0 | Sep | 2021 | 0.0014344 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
CANOVANAS | 2021-09-02 13:24 | 2021-09-02 13:37 | 24 | 000:13 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REEMPLAZO CONECTOR EN PEDESTAL | R21090100063 | New_Event | Secondary Wire Down | Include | Include | Equipment | 13 | 2021-09-02 | 312 | keep | 0 | Sep | 2021 | 0.0002125 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
CAGUAS | 2021-09-02 13:33 | 2021-09-02 16:05 | 10 | 002:32 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 15 KVA X 25 KVA HC @ GIS UPDATES | C21090200113 | New_Event | Service Transformer Failure | Include | Include | Equipment | 152 | 2021-09-02 | 1520 | keep | 0 | Sep | 2021 | 0.0010353 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-02 13:34 | 2021-09-02 15:09 | 140 | 001:35 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C21090200114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2021-09-02 | 13300 | keep | 0 | Sep | 2021 | 0.0090586 | 9.5353e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 140
BAYAMON | 2021-09-02 13:37 | 2021-09-02 13:38 | 5809 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | B21090200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-02 | 5809 | keep | 0 | Sep | 2021 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
BAYAMON | 2021-09-02 13:38 | 2021-09-02 20:33 | 200 | 006:55 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21090200072 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 415 | 2021-09-02 | 83000 | keep | 0 | Sep | 2021 | 0.056531 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-09-02 13:38 | 2021-09-02 16:21 | 1 | 002:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN RISER | C21090200115 | New_Event | Cutout Failure | Include | Include | Equipment | 163 | 2021-09-02 | 163 | keep | 0 | Sep | 2021 | 0.00011102 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-09-02 13:45 | 2021-09-02 16:52 | 27 | 003:07 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21090200116 | New_Event |  |  | Include | Wildlife | 187 | 2021-09-02 | 5049 | keep | 0 | Sep | 2021 | 0.0034389 | 1.839e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 27
ARECIBO | 2021-09-02 14:01 | 2021-09-02 15:19 | 20 | 001:18 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | A21090200078 | New_Event | Bad Weather | Include | Include | Weather | 78 | 2021-09-02 | 1560 | keep | 0 | Sep | 2021 | 0.0010625 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2021-09-02 14:06 | 2021-09-02 16:21 | 80 | 002:15 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P21090200040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2021-09-02 | 10800 | keep | 0 | Sep | 2021 | 0.0073558 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-09-02 14:21 | 2021-09-02 16:12 | 200 | 001:51 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIEMPO | M21090200096 | New_Event | Bad Weather | Include | Include | Weather | 111 | 2021-09-02 | 22200 | keep | 0 | Sep | 2021 | 0.01512 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-09-02 14:28 | 2021-09-02 17:05 | 50 | 002:37 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | M21090200102 | New_Event | Bad Weather | Include | Include | Weather | 157 | 2021-09-02 | 7850 | keep | 0 | Sep | 2021 | 0.0053466 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
MAYAGÃœEZ | 2021-09-02 14:32 | 2021-09-02 17:01 | 3522 | 002:29 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 | M21090200176 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 149 | 2021-09-02 | 524778 | keep | 0 | Sep | 2021 | 0.35742 | 0.0023988 | Sustained | FALSE | TRUE | Not_TMED_Event | 3522
MAYAGÃœEZ | 2021-09-02 14:32 | 2021-09-02 17:01 | 1337 | 002:29 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 | M21090200176 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 149 | 2021-09-02 | 199213 | keep | 0 | Sep | 2021 | 0.13568 | 0.00091062 | Sustained | FALSE | TRUE | Not_TMED_Event | 1337
MAYAGÃœEZ | 2021-09-02 14:32 | 2021-09-02 17:01 | 2825 | 002:29 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 | M21090200176 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 149 | 2021-09-02 | 420925 | keep | 0 | Sep | 2021 | 0.28669 | 0.0019241 | Sustained | FALSE | TRUE | Not_TMED_Event | 2825
MAYAGÃœEZ | 2021-09-02 14:32 | 2021-09-02 17:01 | 1287 | 002:29 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 | M21090200176 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 149 | 2021-09-02 | 191763 | keep | 0 | Sep | 2021 | 0.13061 | 0.00087657 | Sustained | FALSE | TRUE | Not_TMED_Event | 1287
MAYAGÃœEZ | 2021-09-02 14:32 | 2021-09-02 17:01 | 1417 | 002:29 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 | M21090200179 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 149 | 2021-09-02 | 211133 | keep | 0 | Sep | 2021 | 0.1438 | 0.00096511 | Sustained | FALSE | TRUE | Not_TMED_Event | 1417
MAYAGÃœEZ | 2021-09-02 14:32 | 2021-09-02 17:01 | 80 | 002:29 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 | M21090200179 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 149 | 2021-09-02 | 11920 | keep | 0 | Sep | 2021 | 0.0081187 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-09-02 14:42 | 2021-09-02 22:00 | 60 | 007:18 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21090100072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 438 | 2021-09-02 | 26280 | keep | 0 | Sep | 2021 | 0.017899 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CANOVANAS | 2021-09-02 15:02 | 2021-09-02 15:03 | 1648 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR | R21090200052 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-09-02 | 1648 | keep | 0 | Sep | 2021 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2021-09-02 15:03 | 2021-09-02 18:56 | 325 | 003:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | R21090200059 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 233 | 2021-09-02 | 75725 | keep | 0 | Sep | 2021 | 0.051576 | 0.00022136 | Sustained | FALSE | TRUE | Not_TMED_Event | 325
ARECIBO | 2021-09-02 15:03 | 2021-09-02 17:50 | 40 | 002:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21090200085 | New_Event | Bad Weather | Include | Include | Weather | 167 | 2021-09-02 | 6680 | keep | 0 | Sep | 2021 | 0.0045497 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-02 15:14 | 2021-09-02 19:17 | 58 | 004:03 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA PRIMARIA | S21090200103 | New_Event | Wire Down | Include | Include | Equipment | 243 | 2021-09-02 | 14094 | keep | 0 | Sep | 2021 | 0.0095994 | 3.9504e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 58
CANOVANAS | 2021-09-02 15:14 | 2021-09-02 17:35 | 7 | 002:21 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO DISCO | R21090200054 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 141 | 2021-09-02 | 987 | keep | 0 | Sep | 2021 | 0.00067224 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
CANOVANAS | 2021-09-02 15:18 | 2021-09-02 15:54 | 17 | 000:36 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR PALOMA | R21090200056 | New_Event |  |  | Include | Wildlife | 36 | 2021-09-02 | 612 | keep | 0 | Sep | 2021 | 0.00041683 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
MAYAGÃœEZ | 2021-09-02 15:18 | 2021-09-02 18:50 | 100 | 003:32 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 50 EN CORTE DE LINEA MAL TIEMPO | M21090200130 | New_Event | Bad Weather | Include | Include | Weather | 212 | 2021-09-02 | 21200 | keep | 0 | Sep | 2021 | 0.014439 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-02 15:22 | 2021-09-02 15:23 | 1420 | 000:01 | T | DESGANCHE | RECERRO 1530-06 LA CARGA DEL 1526-02 ESTA POR EL 1530-06 | S21090200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-02 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-02 15:22 | 2021-09-02 15:23 | 437 | 000:01 | T | DESGANCHE | RECERRO LLEVA 1526-2 | S21090200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-02 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2021-09-02 15:22 | 2021-09-02 21:22 | 60 | 006:00 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21090200083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 360 | 2021-09-02 | 21600 | keep | 0 | Sep | 2021 | 0.014712 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
VEGA BAJA | 2021-09-02 15:22 | 2021-09-02 18:44 | 100 | 003:22 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN CORTES DE LINEA SE REALIZO DESGANCHE | B21090200080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2021-09-02 | 20200 | keep | 0 | Sep | 2021 | 0.013758 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-02 15:26 | 2021-09-02 15:27 | 3070 | 000:01 | T | DESGANCHE | RECIERRE | B21090200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-02 | 3070 | keep | 0 | Sep | 2021 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2021-09-02 15:27 | 2021-09-02 17:38 | 35 | 002:11 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21090100245 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 131 | 2021-09-02 | 4585 | keep | 0 | Sep | 2021 | 0.0031228 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
MAYAGÃœEZ | 2021-09-02 15:34 | 2021-09-02 16:15 | 4 | 000:41 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | M21090200137 | New_Event | Bad Weather | Include | Include | Weather | 41 | 2021-09-02 | 164 | keep | 0 | Sep | 2021 | 0.0001117 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2021-09-02 15:38 | 2021-09-02 23:15 | 150 | 007:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A21090200089 | New_Event | Wire Down | Include | Include | Equipment | 457 | 2021-09-02 | 68550 | keep | 0 | Sep | 2021 | 0.046689 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-09-02 15:49 | 2021-09-02 15:50 | 1420 | 000:01 | T | DESGANCHE | RECERRO 1530-06 LA CARGA DEL 1526-02 ESTA POR EL 1530-06 | S21090200000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-02 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-02 15:49 | 2021-09-02 15:50 | 437 | 000:01 | T | DESGANCHE | RECERRO LLEVA 1526-2 | S21090200000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-02 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
ARECIBO | 2021-09-02 15:53 | 2021-09-02 16:45 | 40 | 000:52 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A21090200092 | New_Event | Bad Weather | Include | Include | Weather | 52 | 2021-09-02 | 2080 | keep | 0 | Sep | 2021 | 0.0014167 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-09-02 15:58 | 2021-09-02 21:06 | 60 | 005:08 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A21090200093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 308 | 2021-09-02 | 18480 | keep | 0 | Sep | 2021 | 0.012587 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
CAGUAS | 2021-09-02 16:05 | 2021-09-02 18:44 | 2276 | 002:39 | T | ESTRUCTURA AVERIADA | RECERRO INTERRUPTOR QUEDO FUERA SE SECCIONALIZO POSTES PRIMARIO IMPACTADOS | C21090200137 | New_Event | Defective Pole | Include | Include | Equipment | 159 | 2021-09-02 | 361884 | keep | 0 | Sep | 2021 | 0.24648 | 0.0015502 | Sustained | FALSE | FALSE | Not_TMED_Event | 2276
BAYAMON | 2021-09-02 16:10 | 2021-09-02 20:47 | 36 | 004:37 | P | DESGANCHE | 1 X 40, 1 X 30 Y 1 X 20 EN TRANSFORMADORES SE REALIZO DESGANCHE | B21090200090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 277 | 2021-09-02 | 9972 | keep | 0 | Sep | 2021 | 0.0067919 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
ARECIBO | 2021-09-02 16:10 | 2021-09-02 16:25 | 12 | 000:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA RELOCALIZAR LINEAS SECUNDARIAS | A21090200121 | New_Event | Secondary Wire Down | Include | Include | Equipment | 15 | 2021-09-02 | 180 | keep | 0 | Sep | 2021 | 0.0001226 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
FAJARDO | 2021-09-02 16:17 | 2021-09-02 17:12 | 1 | 000:55 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR MAL TIEMPO | R21090200061 | New_Event | Bad Weather | Include | Include | Weather | 55 | 2021-09-02 | 55 | keep | 0 | Sep | 2021 | 3.746e-05 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
AGUADILLA | 2021-09-02 16:18 | 2021-09-03 17:50 | 600 | 025:32 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA | M21090200157 | New_Event | Wire Down | Include | Include | Equipment | 1532 | 2021-09-02 | 919200 | keep | 0 | Sep | 2021 | 0.62606 | 0.00040866 | Sustained | FALSE | TRUE | Not_TMED_Event | 600
CANOVANAS | 2021-09-02 16:19 | 2021-09-02 19:28 | 10 | 003:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 8 EN TRANSFORMADOR CRUCE POR AVE | R21090200062 | New_Event |  |  | Include | Wildlife | 189 | 2021-09-02 | 1890 | keep | 0 | Sep | 2021 | 0.0012873 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-02 16:19 | 2021-09-02 18:46 | 1218 | 002:27 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REPARO LINEA ZAFADA DE AISLADOR | A21090200102 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 147 | 2021-09-02 | 179046 | keep | 0 | Sep | 2021 | 0.12195 | 0.00082957 | Sustained | FALSE | TRUE | Not_TMED_Event | 1218
BARRANQUITAS | 2021-09-02 16:26 | 2021-09-03 11:00 | 20 | 018:34 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | C21090200143 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1114 | 2021-09-02 | 22280 | keep | 0 | Sep | 2021 | 0.015175 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-09-02 16:29 | 2021-09-02 16:30 | 1420 | 000:01 | T | DESGANCHE | RECERRO EL 1530-06 LA CARGA DEL 1526-02 ESTA POR EL 1530-06 | S21090200000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-02 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-02 16:29 | 2021-09-02 16:30 | 437 | 000:01 | T | DESGANCHE | RECERRO LLEVA 1526-2 | S21090200000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-02 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
VEGA BAJA | 2021-09-02 16:34 | 2021-09-02 16:35 | 2216 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B21090200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-02 | 2216 | keep | 0 | Sep | 2021 | 0.0015093 | 0.0015093 | Momentary | FALSE | FALSE | Not_TMED_Event | 2216
BAYAMON | 2021-09-02 16:39 | 2021-09-02 16:40 | 1420 | 000:01 | T | DESGANCHE | RECERRO EL 1530-06 LA CARGA DEL 1526-02 ESTA POR EL 1530-06 | S21090200000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-02 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-02 16:39 | 2021-09-02 16:40 | 437 | 000:01 | T | DESGANCHE | RECERRO LLEVA CARGA 1526-2 | S21090200000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-02 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
VEGA BAJA | 2021-09-02 16:40 | 2021-09-02 16:41 | 3332 | 000:01 | T | MAL TIEMPO/RAYOS/WET ASH | RECIERRE | B21090200000 | New_Event | Bad Weather | Include | Include | Weather | 1 | 2021-09-02 | 3332 | keep | 0 | Sep | 2021 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
VEGA BAJA | 2021-09-02 16:41 | 2021-09-02 20:53 | 50 | 004:12 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA VIENTOS | B21090200093 | 1st_after_momentary | Bad Weather | Include | Include | Weather | 252 | 2021-09-02 | 12600 | keep | 0 | Sep | 2021 | 0.0085818 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
VEGA BAJA | 2021-09-02 16:41 | 2021-09-02 19:38 | 100 | 002:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 Y 1 X 50 EN CORTE DE LINEAS RAFAGAS | B21090200109 | New_Event | Bad Weather | Include | Include | Weather | 177 | 2021-09-02 | 17700 | keep | 0 | Sep | 2021 | 0.012055 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-02 16:47 | 2021-09-02 16:48 | 437 | 000:01 | T | DESGANCHE | RECERRO EL 1530-06 LA CARGA DEL 1526-02 ESTA POR EL 1530-06 | S21090200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-02 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2021-09-02 16:47 | 2021-09-02 16:48 | 437 | 000:01 | T | DESGANCHE | RECERRO LLEVA CARGA 1526-2 | S21090200000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-02 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
VEGA BAJA | 2021-09-02 16:47 | 2021-09-02 16:48 | 3000 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21090200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-02 | 3000 | keep | 0 | Sep | 2021 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
BAYAMON | 2021-09-02 16:53 | 2021-09-02 18:37 | 1420 | 001:44 | T | DESGANCHE | SE ABRIO MACHETE EN LA CALLE 13 SO ESQIUNA CALLE 10 CAPARRA Y SE CERRO N/O EN CALLE 7 SO ESQUINA CALLE 10 90% EN SERVICIO | S21090200116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2021-09-02 | 147680 | keep | 0 | Sep | 2021 | 0.10058 | 0.00096716 | Sustained | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-02 16:53 | 2021-09-02 17:57 | 437 | 001:04 | T | DESGANCHE | DISPARO SE ABRIO MACHETE N/O CONTRA 1526-2 Y SE PROBO INTERRUPTOR 100% EN SERVICIO CONTINUAN PATRULLANDO 1526-2 | S21090200116 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 64 | 2021-09-02 | 27968 | keep | 0 | Sep | 2021 | 0.019049 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
ARECIBO | 2021-09-02 17:06 | 2021-09-04 11:05 | 15 | 041:59 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A21090200114 | New_Event | Bad Weather | Include | Include | Weather | 2519 | 2021-09-02 | 37785 | keep | 0 | Sep | 2021 | 0.025735 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-09-02 17:25 | 2021-09-02 17:45 | 12 | 000:20 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21090200015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 20 | 2021-09-02 | 240 | keep | 0 | Sep | 2021 | 0.00016346 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
BAYAMON | 2021-09-02 17:26 | 2021-09-03 16:40 | 40 | 023:14 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | B21090200121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1394 | 2021-09-02 | 55760 | keep | 0 | Sep | 2021 | 0.037978 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-02 17:27 | 2021-09-03 10:04 | 169 | 016:37 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21090200156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 997 | 2021-09-02 | 168493 | keep | 0 | Sep | 2021 | 0.11476 | 0.00011511 | Sustained | FALSE | TRUE | Not_TMED_Event | 169
BAYAMON | 2021-09-02 17:30 | 2021-09-02 18:17 | 12 | 000:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 20 EN TRANSFORMADOR SE ABRIO TRANSDORMADOR PARA REPARAR SECUNDARIA | S21090200043 | New_Event | Secondary Wire Down | Include | Include | Equipment | 47 | 2021-09-02 | 564 | keep | 0 | Sep | 2021 | 0.00038414 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2021-09-02 17:53 | 2021-09-03 10:28 | 40 | 016:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA QUEMADA | S21090200126 | New_Event | Cutout Failure | Include | Include | Equipment | 995 | 2021-09-02 | 39800 | keep | 0 | Sep | 2021 | 0.027108 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-09-02 17:59 | 2021-09-03 14:51 | 30 | 020:52 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | B21090200128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1252 | 2021-09-02 | 37560 | keep | 0 | Sep | 2021 | 0.025582 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-02 18:04 | 2021-09-02 20:10 | 200 | 002:06 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A21090200125 | New_Event | Wire Down | Include | Include | Equipment | 126 | 2021-09-02 | 25200 | keep | 0 | Sep | 2021 | 0.017164 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
AGUADILLA | 2021-09-02 18:07 | 2021-09-03 12:00 | 1 | 017:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA SE REPORTO DESCARGAS ELECTRICAS | M21090200206 | New_Event | Bad Weather | Include | Include | Weather | 1073 | 2021-09-02 | 1073 | keep | 0 | Sep | 2021 | 0.00073082 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
ARECIBO | 2021-09-02 18:08 | 2021-09-03 15:08 | 50 | 021:00 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | A21090200127 | New_Event | Bad Weather | Include | Include | Weather | 1260 | 2021-09-02 | 63000 | keep | 0 | Sep | 2021 | 0.042909 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-02 18:37 | 2021-09-02 19:32 | 140 | 000:55 | P | DESGANCHE | SE PATRULLO VARIOS PUNTOS SE REALIZO DESGANCHE Y SE CERRO MACHETE EN LA CALLE 13 ESQUINA CALLE 10 100% EN SERVICIO | S21090200116 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 55 | 2021-09-02 | 7700 | keep | 0 | Sep | 2021 | 0.0052444 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-02 18:43 | 2021-09-03 14:19 | 1 | 019:36 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21090200137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1176 | 2021-09-02 | 1176 | keep | 0 | Sep | 2021 | 0.00080097 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CAGUAS | 2021-09-02 18:44 | 2021-09-03 21:20 | 1069 | 026:36 | P | ESTRUCTURA AVERIADA | SE LEVANTARON 3 POSTES PRIMARIOS Y 2 TRANSFORMADORES | C21090200165 | Partial_restoration | Defective Pole | Include | Include | Equipment | 1596 | 2021-09-02 | 1706124 | keep | 0 | Sep | 2021 | 1.162 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2021-09-02 18:58 | 2021-09-03 09:15 | 6 | 014:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | C21090200166 | New_Event |  |  | Include | Wildlife | 857 | 2021-09-02 | 5142 | keep | 0 | Sep | 2021 | 0.0035022 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2021-09-02 19:07 | 2021-09-02 21:39 | 16 | 002:32 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA X 50KVA | S21090200075 | New_Event | Service Transformer Failure | Include | Include | Equipment | 152 | 2021-09-02 | 2432 | keep | 0 | Sep | 2021 | 0.0016564 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
PONCE | 2021-09-02 19:14 | 2021-09-03 10:25 | 200 | 015:11 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | P21090200064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 911 | 2021-09-02 | 182200 | keep | 0 | Sep | 2021 | 0.1241 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
PONCE | 2021-09-02 19:15 | 2021-09-02 22:13 | 1952 | 002:58 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR. NO SE REPORTO LA CAUSA DEL DISPARO | P20902000544 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 178 | 2021-09-02 | 347456 | keep | 0 | Sep | 2021 | 0.23665 | 0.0013295 | Sustained | FALSE | FALSE | Not_TMED_Event | 1952
BAYAMON | 2021-09-02 19:18 | 2021-09-02 22:58 | 20 | 003:40 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21090200147 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 220 | 2021-09-02 | 4400 | keep | 0 | Sep | 2021 | 0.0029968 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
PONCE | 2021-09-02 19:23 | 2021-09-03 09:15 | 32 | 013:52 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | P21090200056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 832 | 2021-09-02 | 26624 | keep | 0 | Sep | 2021 | 0.018133 | 2.1795e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 32
CAGUAS | 2021-09-02 19:24 | 2021-09-03 11:03 | 30 | 015:39 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR CRUCE POR IGUANA | C21090200170 | New_Event |  |  | Include | Wildlife | 939 | 2021-09-02 | 28170 | keep | 0 | Sep | 2021 | 0.019186 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-02 19:33 | 2021-09-02 19:35 | 5619 | 000:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR 1620-4 A PETICION FERNANDO FEBRES PARA SECCIONALIZAR PUENTE PRIMARIO ARQUEANDO EN LA AVENIDA 65 DE INFANTERIA, COUNTRY CLUB EL 90% DE LA CARGA ESTA POR EL 1620-1 | S21090200109 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2021-09-02 | 11238 | keep | 0 | Sep | 2021 | 0.0076542 | 0.0038271 | Momentary | FALSE | FALSE | Not_TMED_Event | 5619
SAN JUAN | 2021-09-02 19:33 | 2021-09-02 19:35 | 350 | 000:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR 1620-4 A PETICION FERNANDO FEBRES PARA SECCIONALIZAR PUENTE PRIMARIO ARQUEANDO AVENIDA 65 DE INFANTERIA COUNTRY CLUB EL 85% DE LA CARGA ESTA POR EL 1620-1 | S21090200109 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2021-09-02 | 700 | keep | 0 | Sep | 2021 | 0.00047677 | 0.00023838 | Momentary | FALSE | FALSE | Not_TMED_Event | 350
SAN JUAN | 2021-09-02 19:33 | 2021-09-02 19:35 | 36 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR A PETICION FERNANDO FEBRES PARA SECCIONALIZAR PUENTE PRIMARIO ARQUEANDO EN AVENIDA 65 DE INFANTERIA COUNTRY CLUB LLEVA CARGA 1620-1, 85% DEL 1336-10 Y 90% DEL 1336-7 | S21090200109 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2021-09-02 | 72 | keep | 0 | Sep | 2021 | 4.9039e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-09-02 19:33 | 2021-09-02 19:35 | 172 | 000:02 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR A PETICION FERNANDO FEBRES PARA SECCIONALIZAR PUENTE PRIMARIO ARQUEANDO AVENIDA 65 DE INFANTERIA COUNTRY CLUB LLEVA CARGA 1620-1, 85% DEL 1336-10 Y 90% DEL 1336-7 | S21090200109 | New_Event | Wire Down | Include | Include | Equipment | 2 | 2021-09-02 | 344 | keep | 0 | Sep | 2021 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2021-09-02 19:35 | 2021-09-02 20:01 | 20 | 000:26 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | S21090100061 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 26 | 2021-09-02 | 520 | keep | 0 | Sep | 2021 | 0.00035417 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-02 19:37 | 2021-09-02 20:16 | 6 | 000:39 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B21090200045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 39 | 2021-09-02 | 234 | keep | 0 | Sep | 2021 | 0.00015938 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2021-09-02 19:39 | 2021-09-03 10:00 | 40 | 014:21 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | S21090200135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 861 | 2021-09-02 | 34440 | keep | 0 | Sep | 2021 | 0.023457 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2021-09-02 19:41 | 2021-09-03 11:11 | 50 | 015:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21090200230 | New_Event | Bad Weather | Include | Include | Weather | 930 | 2021-09-02 | 46500 | keep | 0 | Sep | 2021 | 0.031671 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-02 19:47 | 2021-09-03 17:25 | 40 | 021:38 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21090200157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1298 | 2021-09-02 | 51920 | keep | 0 | Sep | 2021 | 0.035362 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-02 19:57 | 2021-09-03 13:51 | 175 | 017:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 Y 1 X 30 EN CORTES DE LINEA SE REEMPLAZO CAJA PRIMARIA | C21090200179 | New_Event | Cutout Failure | Include | Include | Equipment | 1074 | 2021-09-02 | 187950 | keep | 0 | Sep | 2021 | 0.12801 | 0.00011919 | Sustained | FALSE | TRUE | Not_TMED_Event | 175
SAN JUAN | 2021-09-02 20:01 | 2021-09-02 20:16 | 5619 | 000:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR 1620-4 PARA CERRAR PUENTE PRIMARIO EN MACHETE AQUEANDO A PETICION FERNANDO FEBRES AVENIDA 65 DE INFANTERIA COUNTRY CLUB EL 90% DE LA CARGA ESTA POR EL 1620-1 | S21090200109 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 15 | 2021-09-02 | 84285 | keep | 0 | Sep | 2021 | 0.057406 | 0.0038271 | Sustained | FALSE | FALSE | Not_TMED_Event | 5619
SAN JUAN | 2021-09-02 20:01 | 2021-09-02 20:16 | 350 | 000:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR 1620-4 PARA CERRAR PUENTE PRIMARIO EN MACHETE AQUEANDO A PETICION FERNANDO FEBRES AVENIDA 65 INFANTERIA COUNTRY CLUB EL 85% DE LA CARGA ESTA POR EL 1620-1 | S21090200109 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 15 | 2021-09-02 | 5250 | keep | 0 | Sep | 2021 | 0.0035758 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
SAN JUAN | 2021-09-02 20:01 | 2021-09-02 20:16 | 36 | 000:15 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR PARA CERRAR PUENTE PRIMARIO EN MACHETE AQUEANDO A PETICION FERNANDO FEBRES AVENIDA 65 DE INFANTERIA COUNTRY CLUB LLEVA 1620-1, 85% 1336-10 , 90% 1336-7 | S21090200109 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 15 | 2021-09-02 | 540 | keep | 0 | Sep | 2021 | 0.00036779 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2021-09-02 20:01 | 2021-09-02 20:16 | 172 | 000:15 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRE INTERRUPTOR PARA CERRAR PUENTE PRIMARIO EN MACHETE AQUEANDO A PETICION FERNANDO FEBRES AVENIDA 65 INFANTERIA COUNTRY CLUB LLEVA 1620-1, 85% 1336-10 , 90% 1336-7 | S21090200109 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 15 | 2021-09-02 | 2580 | keep | 0 | Sep | 2021 | 0.0017572 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2021-09-02 20:07 | 2021-09-02 21:02 | 448 | 000:55 | T | NO SE REPORTO CAUSA | DISPARO CON RECIERRE EN OFF Y SE CERRO LOCALMENTE LLEVA 90% DEL 1420-03 | S21090200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 55 | 2021-09-02 | 24640 | keep | 0 | Sep | 2021 | 0.016782 | 0.00030513 | Sustained | FALSE | FALSE | Not_TMED_Event | 448
SAN JUAN | 2021-09-02 20:07 | 2021-09-02 21:02 | 500 | 000:55 | P | NO SE REPORTO CAUSA | DISPARO DEL 1419-13 CON RECIERRE EN OFF SE CERRO LOCALMENTE 90% DE LA CARGA ESTA POR EL 1419-13 | S21090200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 55 | 2021-09-02 | 27500 | keep | 0 | Sep | 2021 | 0.01873 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2021-09-02 20:16 | 2021-09-03 00:14 | 20 | 003:58 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | S21090100061 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 238 | 2021-09-02 | 4760 | keep | 0 | Sep | 2021 | 0.003242 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-02 22:09 | 2021-09-02 22:12 | 1420 | 000:03 | T | OTRAS CAUSAS | RECERRO EL 1530-06 LA CARGA DEL 1526-02 ESTA POR EL 1530-06. DESBALANCE | S21090200151 | New_Event | Other Causes | Include | Include | Other | 3 | 2021-09-02 | 4260 | keep | 0 | Sep | 2021 | 0.0029015 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-02 22:09 | 2021-09-02 22:12 | 437 | 000:03 | T | OTRAS CAUSAS | RECERRO LLEVA 1526-2 DESBALANCE | S21090200151 | New_Event | Other Causes | Include | Include | Other | 3 | 2021-09-02 | 1311 | keep | 0 | Sep | 2021 | 0.00089292 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
AGUADILLA | 2021-09-02 22:41 | 2021-09-03 14:40 | 50 | 015:59 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | M21090200260 | New_Event | Vegetation Contact | Include | Include | Vegetation | 959 | 2021-09-02 | 47950 | keep | 0 | Sep | 2021 | 0.032659 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
AGUADILLA | 2021-09-02 22:57 | 2021-09-02 22:58 | 1047 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21090200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-02 | 1047 | keep | 0 | Sep | 2021 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
AGUADILLA | 2021-09-02 23:27 | 2021-09-03 16:05 | 200 | 016:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA | M21090200264 | New_Event | Wire Down | Include | Include | Equipment | 998 | 2021-09-02 | 199600 | keep | 0 | Sep | 2021 | 0.13595 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
CAGUAS | 2021-09-02 23:35 | 2021-09-03 16:04 | 179 | 016:29 | P | DESGANCHE | 1 X 40 EN RISER SE DESGANCHO, RECONSTRUYERON RISER Y DIERON TERMINACIONES | C21090200190 | New_Event | Vegetation Contact | Include | Include | Vegetation | 989 | 2021-09-02 | 177031 | keep | 0 | Sep | 2021 | 0.12058 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
HUMACAO | 2021-09-02 23:54 | 2021-09-03 11:40 | 216 | 011:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C21090200191 | New_Event | Cutout Failure | Include | Include | Equipment | 706 | 2021-09-02 | 152496 | keep | 0 | Sep | 2021 | 0.10386 | 0.00014712 | Sustained | FALSE | TRUE | Not_TMED_Event | 216
SAN JUAN | 2021-09-03 00:20 | 2021-09-03 00:21 | 5062 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21090300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-03 | 5062 | keep | 0 | Sep | 2021 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
ARECIBO | 2021-09-03 01:11 | 2021-09-03 01:12 | 2697 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21090300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-03 | 2697 | keep | 0 | Sep | 2021 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
ARECIBO | 2021-09-03 01:12 | 2021-09-03 12:11 | 4 | 010:59 | P | NO SE REPORTO CAUSA | 2 X 80 Y 1 X 65 EN RAISER | A21090300017 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 659 | 2021-09-03 | 2636 | keep | 0 | Sep | 2021 | 0.0017954 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2021-09-03 01:45 | 2021-09-03 01:46 | 3838 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21090300001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-03 | 3838 | keep | 0 | Sep | 2021 | 0.002614 | 0.002614 | Momentary | FALSE | FALSE | Not_TMED_Event | 3838
MAYAGÃœEZ | 2021-09-03 02:11 | 2021-09-03 02:12 | 1352 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUTOR | M21090300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-03 | 1352 | keep | 0 | Sep | 2021 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2021-09-03 02:21 | 2021-09-03 02:22 | 2713 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRRE DE INTERRUTPOR | M21090300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-03 | 2713 | keep | 0 | Sep | 2021 | 0.0018478 | 0.0018478 | Momentary | FALSE | FALSE | Not_TMED_Event | 2713
VEGA BAJA | 2021-09-03 02:38 | 2021-09-03 02:39 | 4027 | 000:01 | T | DESGANCHE | RECIERRRE DE INTERRUPTOR | B21090300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-03 | 4027 | keep | 0 | Sep | 2021 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
VEGA BAJA | 2021-09-03 02:39 | 2021-09-03 15:20 | 80 | 012:41 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21090200176 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 761 | 2021-09-03 | 60880 | keep | 0 | Sep | 2021 | 0.041465 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
CANOVANAS | 2021-09-03 03:43 | 2021-09-03 11:10 | 6 | 007:27 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REEMPLAZAR BAJANTE SECUNDARIO QUEMADO | R21090300002 | New_Event | Secondary Wire Down | Include | Include | Equipment | 447 | 2021-09-03 | 2682 | keep | 0 | Sep | 2021 | 0.0018267 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2021-09-03 04:02 | 2021-09-03 11:42 | 40 | 007:40 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R21090300003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 460 | 2021-09-03 | 18400 | keep | 0 | Sep | 2021 | 0.012532 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-03 05:11 | 2021-09-03 05:12 | 331 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | R21090300005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-03 | 331 | keep | 0 | Sep | 2021 | 0.00022544 | 0.00022544 | Momentary | FALSE | FALSE | Not_TMED_Event | 331
SAN JUAN | 2021-09-03 05:11 | 2021-09-03 05:12 | 5062 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21090300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-03 | 5062 | keep | 0 | Sep | 2021 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
BAYAMON | 2021-09-03 05:24 | 2021-09-03 15:54 | 40 | 010:30 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21090300008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 630 | 2021-09-03 | 25200 | keep | 0 | Sep | 2021 | 0.017164 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
CAGUAS | 2021-09-03 05:52 | 2021-09-03 05:53 | 1702 | 000:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C21090300006 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2021-09-03 | 1702 | keep | 0 | Sep | 2021 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2021-09-03 06:29 | 2021-09-03 11:02 | 77 | 004:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21090300009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 273 | 2021-09-03 | 21021 | keep | 0 | Sep | 2021 | 0.014317 | 5.2444e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 77
HUMACAO | 2021-09-03 07:15 | 2021-09-03 07:16 | 1835 | 000:01 | T | DESGANCHE | RECERRO INTERRUPTOR | C21090300011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-03 | 1835 | keep | 0 | Sep | 2021 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
HUMACAO | 2021-09-03 07:16 | 2021-09-03 13:46 | 7 | 006:30 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA DESGANCHE | C21090300066 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 390 | 2021-09-03 | 2730 | keep | 0 | Sep | 2021 | 0.0018594 | 4.7677e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 7
CAGUAS | 2021-09-03 07:18 | 2021-09-03 12:00 | 19 | 004:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21090300013 | New_Event |  |  | Include | Wildlife | 282 | 2021-09-03 | 5358 | keep | 0 | Sep | 2021 | 0.0036493 | 1.2941e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 19
HUMACAO | 2021-09-03 07:20 | 2021-09-03 10:38 | 58 | 003:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR CRUCE POR CHANGO | C21090300015 | New_Event |  |  | Include | Wildlife | 198 | 2021-09-03 | 11484 | keep | 0 | Sep | 2021 | 0.0078217 | 3.9504e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 58
AGUADILLA | 2021-09-03 07:53 | 2021-09-03 17:20 | 150 | 009:27 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA DESGANCHE | M21090300007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 567 | 2021-09-03 | 85050 | keep | 0 | Sep | 2021 | 0.057927 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
FAJARDO | 2021-09-03 08:01 | 2021-09-03 19:44 | 40 | 011:43 | P | ESTRUCTURA AVERIADA | ABRIO CORTE DE LINEA PARA REEMPLAZAR POSTE PARTIDO | R21090300007 | New_Event | Defective Pole | Include | Include | Equipment | 703 | 2021-09-03 | 28120 | keep | 0 | Sep | 2021 | 0.019152 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
BAYAMON | 2021-09-03 08:09 | 2021-09-04 11:56 | 10 | 027:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN MONTURA DE TRANSFORMADORES | B21090300021 | New_Event | Cutout Failure | Include | Include | Equipment | 1667 | 2021-09-03 | 16670 | keep | 0 | Sep | 2021 | 0.011354 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-03 08:14 | 2021-09-03 08:15 | 2605 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21090300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-03 | 2605 | keep | 0 | Sep | 2021 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
AGUADILLA | 2021-09-03 08:14 | 2021-09-04 18:53 | 60 | 034:39 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA | M21090400025 | New_Event | Wire Down | Include | Include | Equipment | 2079 | 2021-09-03 | 124740 | keep | 0 | Sep | 2021 | 0.08496 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
HUMACAO | 2021-09-03 08:17 | 2021-09-03 08:18 | 3896 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C21090300018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-03 | 3896 | keep | 0 | Sep | 2021 | 0.0026535 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
MAYAGÃœEZ | 2021-09-03 08:30 | 2021-09-04 16:03 | 7 | 031:33 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO | M21090300010 | New_Event | Wire Down | Include | Include | Equipment | 1893 | 2021-09-03 | 13251 | keep | 0 | Sep | 2021 | 0.0090252 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2021-09-03 08:30 | 2021-09-03 14:21 | 60 | 005:51 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 100 EN CORTE DE LINEA SE REMPLAZO AISLADOR | B21090300027 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 351 | 2021-09-03 | 21060 | keep | 0 | Sep | 2021 | 0.014344 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
BAYAMON | 2021-09-03 08:54 | 2021-09-03 08:55 | 295 | 000:01 | T | ERROR HUMANO | SE ABRIO ALIMENTADOR ERRONEAMENTE DE EMERGENCIA A PETICION DE FERNANDO FEBRES POR CAJAS ARQUEANDO | S21090300025 | New_Event | Human Error | Include | Include | Other | 1 | 2021-09-03 | 295 | keep | 0 | Sep | 2021 | 0.00020092 | 0.00020092 | Momentary | FALSE | FALSE | Not_TMED_Event | 295
BAYAMON | 2021-09-03 08:55 | 2021-09-03 08:56 | 418 | 000:01 | T | ERROR HUMANO | SE ABRIO ALIMENTADOR ERRONEAMENTE DE EMERGENCIA A PETICION DE FERNANDO FEBRES POR CAJAS ARQUEANDO | S21090300027 | New_Event | Human Error | Include | Include | Other | 1 | 2021-09-03 | 418 | keep | 0 | Sep | 2021 | 0.0002847 | 0.0002847 | Momentary | FALSE | FALSE | Not_TMED_Event | 418
BAYAMON | 2021-09-03 08:59 | 2021-09-04 10:19 | 40 | 025:20 | P | NO SE REPORTO CAUSA | 1 X 40 EN PROVISIONAL AEREO | B21090300032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1520 | 2021-09-03 | 60800 | keep | 0 | Sep | 2021 | 0.041411 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2021-09-03 09:02 | 2021-09-03 09:03 | 75 | 000:01 | P | ERROR HUMANO | SE ABRIO ALIMENTADOR ERRONEAMENTE DE EMERGENCIA A PETICION DE FERNANDO FEBRES POR CAJAS ARQUEANDO. 75% DEL 1011-02 POR EL 1011-05. FINALMENTE EL ALIMENTADOR CORRECTO ERA EL 1012-06 | S21090300029 | New_Event | Human Error | Include | Include | Other | 1 | 2021-09-03 | 75 | keep | 0 | Sep | 2021 | 5.1082e-05 | 5.1082e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2021-09-03 09:02 | 2021-09-03 09:03 | 719 | 000:01 | T | ERROR HUMANO | SE ABRIO ALIMENTADOR ERRONEAMENTE DE EMERGENCIA A PETICION DE FERNANDO FEBRES POR CAJAS ARQUEANDO. LLEVANDO 75% DEL 1011-02 | S21090300029 | New_Event | Human Error | Include | Include | Other | 1 | 2021-09-03 | 719 | keep | 0 | Sep | 2021 | 0.00048971 | 0.00048971 | Momentary | FALSE | FALSE | Not_TMED_Event | 719
BAYAMON | 2021-09-03 09:03 | 2021-09-03 09:39 | 67 | 000:36 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO POR CONTROL EL 1012-06 LLEVANDO EL 1012-10 PARA SECCIONALIZAR CAJAS SECAS ARQUEANDO A PETICION DE FERNANDO FEBRES POR SEGURIDAD. SE QUEDARON 3 CLIENTES FUERA | S21090300000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 36 | 2021-09-03 | 2412 | keep | 0 | Sep | 2021 | 0.0016428 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2021-09-03 09:03 | 2021-09-03 09:39 | 45 | 000:36 | T | EMPALME O TERMINACION SOTERRADA AVERIADA | SE ABRIO POR CONTROL EL 1012-06 LLEVANDO EL 1012-10 PARA SECCIONALIZAR CAJAS SECAS ARQUEANDO A PETICION DE FERNANDO FEBRES POR SEGURIDAD. SE QUEDARON 3 CLIENTES FUERA | S21090300000 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 36 | 2021-09-03 | 1620 | keep | 0 | Sep | 2021 | 0.0011034 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2021-09-03 09:07 | 2021-09-03 17:11 | 30 | 008:04 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21090300034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 484 | 2021-09-03 | 14520 | keep | 0 | Sep | 2021 | 0.0098895 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-09-03 09:29 | 2021-09-03 11:03 | 10 | 001:34 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | S21090200125 | New_Event | Secondary Wire Down | Include | Include | Equipment | 94 | 2021-09-03 | 940 | keep | 0 | Sep | 2021 | 0.00064023 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-03 09:32 | 2021-09-03 09:33 | 1362 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B21090300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-03 | 1362 | keep | 0 | Sep | 2021 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
AGUADILLA | 2021-09-03 09:33 | 2021-09-03 15:10 | 12 | 005:37 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES | M21090300015 | New_Event | Secondary Wire Down | Include | Include | Equipment | 337 | 2021-09-03 | 4044 | keep | 0 | Sep | 2021 | 0.0027543 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-09-03 09:43 | 2021-09-03 16:31 | 10 | 006:48 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | A21090300013 | New_Event | Secondary Wire Down | Include | Include | Equipment | 408 | 2021-09-03 | 4080 | keep | 0 | Sep | 2021 | 0.0027789 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
BAYAMON | 2021-09-03 09:46 | 2021-09-04 12:28 | 15 | 026:42 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5KVA | B21090300044 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1602 | 2021-09-03 | 24030 | keep | 0 | Sep | 2021 | 0.016367 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-09-03 09:49 | 2021-09-03 19:51 | 100 | 010:02 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R21090300014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 602 | 2021-09-03 | 60200 | keep | 0 | Sep | 2021 | 0.041002 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-03 09:55 | 2021-09-03 13:40 | 20 | 003:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA MARCA ABB 100AMP. FID.-22681181 | A21090300015 | New_Event | Cutout Failure | Include | Include | Equipment | 225 | 2021-09-03 | 4500 | keep | 0 | Sep | 2021 | 0.0030649 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-09-03 09:59 | 2021-09-03 10:00 | 595 | 000:01 | T | DESGANCHE | RECIERRE | P210903000XX | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-03 | 595 | keep | 0 | Sep | 2021 | 0.00040525 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
PONCE | 2021-09-03 10:00 | 2021-09-03 12:32 | 100 | 002:32 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA. CLIENTE CRUZO FASES DESGANCHANDO | P21090300018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2021-09-03 | 15200 | keep | 0 | Sep | 2021 | 0.010353 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-03 10:07 | 2021-09-03 20:58 | 30 | 010:51 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21090300048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 651 | 2021-09-03 | 19530 | keep | 0 | Sep | 2021 | 0.013302 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-03 10:14 | 2021-09-04 11:12 | 1 | 024:58 | P | NO SE REPORTO CAUSA | 3 X 20 EN TRANSCLOSURE DE CLIENTE | S21090300036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1498 | 2021-09-03 | 1498 | keep | 0 | Sep | 2021 | 0.0010203 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-09-03 10:15 | 2021-09-03 11:39 | 15 | 001:24 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | C21090200079 | New_Event | Secondary Wire Down | Include | Include | Equipment | 84 | 2021-09-03 | 1260 | keep | 0 | Sep | 2021 | 0.00085818 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2021-09-03 10:28 | 2021-09-03 12:10 | 1 | 001:42 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO CONEXIONES EN TRANSFORMADOR | A21090300000 | New_Event | Secondary Wire Down | Include | Include | Equipment | 102 | 2021-09-03 | 102 | keep | 0 | Sep | 2021 | 6.9472e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-09-03 10:55 | 2021-09-04 14:25 | 1 | 027:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REPARO CAJA | C21090300050 | New_Event | Cutout Failure | Include | Include | Equipment | 1650 | 2021-09-03 | 1650 | keep | 0 | Sep | 2021 | 0.0011238 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-09-03 10:56 | 2021-09-04 10:11 | 60 | 023:15 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR PRIMARIO PARTIDO | S21090300041 | New_Event | Wire Down | Include | Include | Equipment | 1395 | 2021-09-03 | 83700 | keep | 0 | Sep | 2021 | 0.057008 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2021-09-03 11:08 | 2021-09-04 09:57 | 8 | 022:49 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHO | C21090300054 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1369 | 2021-09-03 | 10952 | keep | 0 | Sep | 2021 | 0.0074594 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-09-03 11:10 | 2021-09-04 15:13 | 100 | 028:03 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | B21090300066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1683 | 2021-09-03 | 168300 | keep | 0 | Sep | 2021 | 0.11463 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-09-03 11:24 | 2021-09-03 11:25 | 1681 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1303-04 QUE LLEVA SOLAMENTE EL 1303-01 Y 1346-06 | S21090300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-03 | 1681 | keep | 0 | Sep | 2021 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2021-09-03 11:24 | 2021-09-03 11:25 | 1598 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1303-04 QUE LLEVA SOLAMENTE EL 1303-01 Y 1346-06 | S21090300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-03 | 1598 | keep | 0 | Sep | 2021 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
AGUADILLA | 2021-09-03 11:30 | 2021-09-03 21:14 | 60 | 009:44 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | M21090300034 | New_Event | Wire Down | Include | Include | Equipment | 584 | 2021-09-03 | 35040 | keep | 0 | Sep | 2021 | 0.023866 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2021-09-03 11:32 | 2021-09-03 14:23 | 10 | 002:51 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B21090300076 | New_Event | Secondary Wire Down | Include | Include | Equipment | 171 | 2021-09-03 | 1710 | keep | 0 | Sep | 2021 | 0.0011647 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-09-03 11:37 | 2021-09-03 16:48 | 5 | 005:11 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | A21090300025 | New_Event | Bad Weather | Include | Include | Weather | 311 | 2021-09-03 | 1555 | keep | 0 | Sep | 2021 | 0.0010591 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
SAN JUAN | 2021-09-03 11:46 | 2021-09-03 17:09 | 1 | 005:23 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | R21083000019 | New_Event |  |  | Include | Wildlife | 323 | 2021-09-03 | 323 | keep | 0 | Sep | 2021 | 0.00021999 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2021-09-03 11:48 | 2021-09-03 14:18 | 146 | 002:30 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO PENCA DE LA LINEA | C21090300060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2021-09-03 | 21900 | keep | 0 | Sep | 2021 | 0.014916 | 9.944e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 146
BAYAMON | 2021-09-03 11:58 | 2021-09-03 14:00 | 10 | 002:02 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21090300052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2021-09-03 | 1220 | keep | 0 | Sep | 2021 | 0.00083094 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-03 12:08 | 2021-09-04 11:23 | 1 | 023:15 | P | NO SE REPORTO CAUSA | 2 X 25 EN MONTURA DE TRANSFORMADORES | B21090300082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1395 | 2021-09-03 | 1395 | keep | 0 | Sep | 2021 | 0.00095013 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2021-09-03 12:19 | 2021-09-04 10:07 | 10 | 021:48 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21090300085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1308 | 2021-09-03 | 13080 | keep | 0 | Sep | 2021 | 0.0089087 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-03 12:25 | 2021-09-04 18:47 | 15 | 030:22 | P | CABLE SOTERRADO AVERIADO | SE INSTALO AEREO PROVISIONAL DEL PM-4 @ PM-3 | A21090400098 | New_Event | UG Cable Fault | Include | Include | Equipment | 1822 | 2021-09-03 | 27330 | keep | 0 | Sep | 2021 | 0.018614 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-09-03 12:26 | 2021-09-03 12:27 | 3744 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21090300023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-03 | 3744 | keep | 0 | Sep | 2021 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2021-09-03 12:26 | 2021-09-03 12:27 | 3114 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P21090300023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-03 | 3114 | keep | 0 | Sep | 2021 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
VEGA BAJA | 2021-09-03 12:41 | 2021-09-03 14:25 | 1 | 001:44 | P | NO SE REPORTO CAUSA | 2 X 15 EN RISER | B21090300088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2021-09-03 | 104 | keep | 0 | Sep | 2021 | 7.0834e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-09-03 12:53 | 2021-09-03 14:39 | 7 | 001:46 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SULFATADO Y REGULARLO SUBIO TAP 3 AL 4 QUEDO 121/242V | R21090300023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 106 | 2021-09-03 | 742 | keep | 0 | Sep | 2021 | 0.00050537 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2021-09-03 12:54 | 2021-09-03 17:47 | 100 | 004:53 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | A21090300037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 293 | 2021-09-03 | 29300 | keep | 0 | Sep | 2021 | 0.019956 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-03 13:00 | 2021-09-03 16:35 | 50 | 003:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | A21090300040 | New_Event | Bad Weather | Include | Include | Weather | 215 | 2021-09-03 | 10750 | keep | 0 | Sep | 2021 | 0.0073218 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
BAYAMON | 2021-09-03 13:07 | 2021-09-03 17:00 | 10 | 003:53 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B2109030052 | New_Event | Secondary Wire Down | Include | Include | Equipment | 233 | 2021-09-03 | 2330 | keep | 0 | Sep | 2021 | 0.001587 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2021-09-03 13:29 | 2021-09-03 15:36 | 75 | 002:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA PORTAFUSIBLE | S21090300099 | New_Event | Cutout Failure | Include | Include | Equipment | 127 | 2021-09-03 | 9525 | keep | 0 | Sep | 2021 | 0.0064874 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
SAN JUAN | 2021-09-03 13:35 | 2021-09-03 17:20 | 60 | 003:45 | P | NO SE REPORTO CAUSA | 1 X 80 EN PROVISIONAL | S21090300066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 225 | 2021-09-03 | 13500 | keep | 0 | Sep | 2021 | 0.0091948 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2021-09-03 14:18 | 2021-09-03 15:05 | 9 | 000:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA EN MONTURA DE TRANSFORMADOR | A21090300051 | New_Event | Cutout Failure | Include | Include | Equipment | 47 | 2021-09-03 | 423 | keep | 0 | Sep | 2021 | 0.0002881 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
UTUADO | 2021-09-03 14:22 | 2021-09-03 15:12 | 3 | 000:50 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | A21090300007 | New_Event | Secondary Wire Down | Include | Include | Equipment | 50 | 2021-09-03 | 150 | keep | 0 | Sep | 2021 | 0.00010216 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2021-09-03 14:28 | 2021-09-03 14:37 | 1701 | 000:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRIO INTELLIRRUPTER PARA INSTALAR POSTE IMPACTADO DEL 3014-01 | C21090300071 | New_Event |  |  | Include | Wildlife | 9 | 2021-09-03 | 15309 | keep | 0 | Sep | 2021 | 0.010427 | 0.0011585 | Sustained | FALSE | FALSE | Not_TMED_Event | 1701
BAYAMON | 2021-09-03 14:31 | 2021-09-04 14:16 | 20 | 023:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO CONDUCTOR PRIMARIO | B21090300110 | New_Event | Wire Down | Include | Include | Equipment | 1425 | 2021-09-03 | 28500 | keep | 0 | Sep | 2021 | 0.019411 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2021-09-03 14:37 | 2021-09-04 16:48 | 10 | 026:11 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 15 KVA X 25 KVA HC @ GIS UPDATES | C21090200113 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1571 | 2021-09-03 | 15710 | keep | 0 | Sep | 2021 | 0.0107 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-03 14:38 | 2021-09-04 12:40 | 70 | 022:02 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | M21090300052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1322 | 2021-09-03 | 92540 | keep | 0 | Sep | 2021 | 0.063029 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
UTUADO | 2021-09-03 14:39 | 2021-09-03 21:36 | 125 | 006:57 | P | ESTRUCTURA AVERIADA | 2 X 40 EN CORTE DE LINEA SE REEMPLAZO POSTE PARTIDO | A21090300069 | New_Event | Defective Pole | Include | Include | Equipment | 417 | 2021-09-03 | 52125 | keep | 0 | Sep | 2021 | 0.035502 | 8.5137e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 125
VEGA BAJA | 2021-09-03 14:52 | 2021-09-03 14:58 | 3387 | 000:06 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL | B21090300114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 6 | 2021-09-03 | 20322 | keep | 0 | Sep | 2021 | 0.013841 | 0.0023069 | Sustained | FALSE | FALSE | Not_TMED_Event | 3387
ARECIBO | 2021-09-03 14:56 | 2021-09-03 16:55 | 40 | 001:59 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | A21090300071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2021-09-03 | 4760 | keep | 0 | Sep | 2021 | 0.003242 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-09-03 14:58 | 2021-09-03 17:55 | 75 | 002:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21090300077 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 177 | 2021-09-03 | 13275 | keep | 0 | Sep | 2021 | 0.0090415 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
BAYAMON | 2021-09-03 15:08 | 2021-09-03 17:05 | 946 | 001:57 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO MACHETE AVE. SAN PATRICIO ESQ. CALLE 3650 Y SE CERRO N/O CONTRA 1525-5 99% EN SERVICIO SE ENCONTRO ALAMBRE PRIMARIO EN EL PISO Y DESGANCHE | S21090300088 | New_Event | Wire Down | Include | Include | Equipment | 117 | 2021-09-03 | 110682 | keep | 0 | Sep | 2021 | 0.075385 | 0.00064432 | Sustained | FALSE | FALSE | Not_TMED_Event | 946
BAYAMON | 2021-09-03 15:08 | 2021-09-03 16:12 | 937 | 001:04 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE PATRULLO SE ABRIO N/O CONTRA 1525-02 Y SE CERRO INTERRUPTOR 100% EN SERVICIO CONTINUAN PATRULLANDO | S21090300076 | New_Event | Wire Down | Include | Include | Equipment | 64 | 2021-09-03 | 59968 | keep | 0 | Sep | 2021 | 0.040844 | 0.00063819 | Sustained | FALSE | FALSE | Not_TMED_Event | 937
BARRANQUITAS | 2021-09-03 15:13 | 2021-09-04 14:10 | 15 | 022:57 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 75 KVA X 75 KVA | C21090300079 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1377 | 2021-09-03 | 20655 | keep | 0 | Sep | 2021 | 0.014068 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2021-09-03 15:20 | 2021-09-05 21:00 | 10 | 053:40 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21090300122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3220 | 2021-09-03 | 32200 | keep | 0 | Sep | 2021 | 0.021931 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-03 15:24 | 2021-09-03 18:59 | 70 | 003:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | M21090300059 | New_Event | Bad Weather | Include | Include | Weather | 215 | 2021-09-03 | 15050 | keep | 0 | Sep | 2021 | 0.01025 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
VEGA BAJA | 2021-09-03 15:35 | 2021-09-03 17:15 | 30 | 001:40 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21090100180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2021-09-03 | 3000 | keep | 0 | Sep | 2021 | 0.0020433 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-03 15:40 | 2021-09-04 09:46 | 10 | 018:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A21090300098 | New_Event | Bad Weather | Include | Include | Weather | 1086 | 2021-09-03 | 10860 | keep | 0 | Sep | 2021 | 0.0073967 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2021-09-03 15:52 | 2021-09-03 19:13 | 12 | 003:21 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21090300124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 201 | 2021-09-03 | 2412 | keep | 0 | Sep | 2021 | 0.0016428 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2021-09-03 16:03 | 2021-09-03 20:56 | 200 | 004:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | A21090300101 | New_Event | Cutout Failure | Include | Include | Equipment | 293 | 2021-09-03 | 58600 | keep | 0 | Sep | 2021 | 0.039912 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2021-09-03 16:10 | 2021-09-04 15:43 | 8 | 023:33 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BARRAS DE PEDESTAL | C21090300085 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1413 | 2021-09-03 | 11304 | keep | 0 | Sep | 2021 | 0.0076991 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-09-03 16:12 | 2021-09-03 18:01 | 100 | 001:49 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 Y 1 X 40 EN CORTE DE LINEA | A21090300092 | New_Event | Bad Weather | Include | Include | Weather | 109 | 2021-09-03 | 10900 | keep | 0 | Sep | 2021 | 0.0074239 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
VEGA BAJA | 2021-09-03 16:12 | 2021-09-03 18:45 | 1 | 002:33 | P | NO SE REPORTO CAUSA | 1 X 15 EN MONTURA DE TRANSFORMADORES | B21090300126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 153 | 2021-09-03 | 153 | keep | 0 | Sep | 2021 | 0.00010421 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-09-03 16:17 | 2021-09-03 21:28 | 100 | 005:11 | P | MAL TIEMPO/RAYOS/WET ASH | 3 X 50 Y 1 X 30 EN CORTE DE LINEA MAL TIEMPO | A21090300094 | New_Event | Bad Weather | Include | Include | Weather | 311 | 2021-09-03 | 31100 | keep | 0 | Sep | 2021 | 0.021182 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-03 16:25 | 2021-09-03 16:33 | 2720 | 000:08 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | DISPARO DE INTERRUPTOR POR LINEA PARTIDA SE ABRIO CORTE DE LINEA Y SE CERRO INTERRUPTOR | A21090300100 | New_Event | Wire Down | Include | Include | Equipment | 8 | 2021-09-03 | 21760 | keep | 0 | Sep | 2021 | 0.014821 | 0.0018526 | Sustained | FALSE | TRUE | Not_TMED_Event | 2720
MAYAGÃœEZ | 2021-09-03 16:27 | 2021-09-03 18:28 | 10 | 002:01 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 8 EN TRANSFORMADOR MAL TIEMPO | M21090300071 | New_Event | Bad Weather | Include | Include | Weather | 121 | 2021-09-03 | 1210 | keep | 0 | Sep | 2021 | 0.00082413 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-09-03 16:29 | 2021-09-04 16:05 | 150 | 023:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA REMPLAZO CAJA | M21090300073 | New_Event | Cutout Failure | Include | Include | Equipment | 1416 | 2021-09-03 | 212400 | keep | 0 | Sep | 2021 | 0.14466 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-09-03 16:33 | 2021-09-03 22:15 | 150 | 005:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 3 X 80 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A21090300105 | Partial_restoration | Wire Down | Include | Include | Equipment | 342 | 2021-09-03 | 51300 | keep | 0 | Sep | 2021 | 0.03494 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-09-03 16:38 | 2021-09-04 16:40 | 15 | 024:02 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO BAJANTE PRIMARIO | A21090300102 | New_Event | Wire Down | Include | Include | Equipment | 1442 | 2021-09-03 | 21630 | keep | 0 | Sep | 2021 | 0.014732 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2021-09-03 16:44 | 2021-09-03 16:45 | 1420 | 000:01 | T | OTRAS CAUSAS | RECERRO LLEVA 1526-02 DESBALANCE | S21090300000 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-09-03 | 1420 | keep | 0 | Sep | 2021 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
BAYAMON | 2021-09-03 16:44 | 2021-09-03 16:45 | 437 | 000:01 | T | OTRAS CAUSAS | RECERRO LLEVA 1526-2 DESBALANCE | S21090300000 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-09-03 | 437 | keep | 0 | Sep | 2021 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
CANOVANAS | 2021-09-03 16:50 | 2021-09-03 18:52 | 50 | 002:02 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA REEMPLAZO PARARRAYO | R21090300033 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 122 | 2021-09-03 | 6100 | keep | 0 | Sep | 2021 | 0.0041547 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
SAN JUAN | 2021-09-03 16:56 | 2021-09-03 18:51 | 5 | 001:55 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 15 EN TRANSFORMADOR REPARARO SECUNDARIA | R21090300036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 115 | 2021-09-03 | 575 | keep | 0 | Sep | 2021 | 0.00039163 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-09-03 16:56 | 2021-09-05 13:00 | 5 | 044:04 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO 25KVA. MARCA-COOPER 2400/4160V 120/240V SER:2055094555 FID.-33703076 X 25KVA | A21090500019 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2644 | 2021-09-03 | 13220 | keep | 0 | Sep | 2021 | 0.0090041 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2021-09-03 17:01 | 2021-09-03 20:07 | 150 | 003:06 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 100 EN CORTE DE LINEA MAL TIMEPO | A21090300110 | New_Event | Bad Weather | Include | Include | Weather | 186 | 2021-09-03 | 27900 | keep | 0 | Sep | 2021 | 0.019003 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-09-03 17:05 | 2021-09-03 18:26 | 10 | 001:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO LINEA Y SE HIZO DESGANCHE SE CERRO MACHETE AVE. SAN PATRICIO ESQ. CALLE 3650 100% EN SERVICIO | S21090300088 | Partial_restoration | Wire Down | Include | Include | Equipment | 81 | 2021-09-03 | 810 | keep | 0 | Sep | 2021 | 0.00055169 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
ARECIBO | 2021-09-03 17:06 | 2021-09-04 10:21 | 80 | 017:15 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | A21090300114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1035 | 2021-09-03 | 82800 | keep | 0 | Sep | 2021 | 0.056395 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
UTUADO | 2021-09-03 17:06 | 2021-09-03 19:41 | 4 | 002:35 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 30 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR MAL TIEMPO | A21090300113 | New_Event | Bad Weather | Include | Include | Weather | 155 | 2021-09-03 | 620 | keep | 0 | Sep | 2021 | 0.00042228 | 2.7244e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 4
CAGUAS | 2021-09-03 17:13 | 2021-09-04 13:55 | 7 | 020:42 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 15 KVA X 15 KVA | C21090300089 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1242 | 2021-09-03 | 8694 | keep | 0 | Sep | 2021 | 0.0059214 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2021-09-03 17:16 | 2021-09-03 20:17 | 30 | 003:01 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | B21090300135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 181 | 2021-09-03 | 5430 | keep | 0 | Sep | 2021 | 0.0036983 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-03 17:27 | 2021-09-03 17:37 | 2379 | 000:10 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR VERIFICO PERSONAL FUERA DEL AREA SE CERRO MAL TIEMPO | A21090300000 | New_Event | Bad Weather | Include | Include | Weather | 10 | 2021-09-03 | 23790 | keep | 0 | Sep | 2021 | 0.016203 | 0.0016203 | Sustained | FALSE | FALSE | Not_TMED_Event | 2379
AGUADILLA | 2021-09-03 17:30 | 2021-09-03 19:00 | 20 | 001:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE HOWARD 50 KVA/ 4160 FID-24890995 POR 50 KVA | M21090300077 | New_Event | Service Transformer Failure | Include | Include | Equipment | 90 | 2021-09-03 | 1800 | keep | 0 | Sep | 2021 | 0.001226 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-09-03 17:36 | 2021-09-03 18:17 | 80 | 000:41 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | A21090300132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 41 | 2021-09-03 | 3280 | keep | 0 | Sep | 2021 | 0.002234 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BAYAMON | 2021-09-03 17:43 | 2021-09-03 18:03 | 25 | 000:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21090300104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 20 | 2021-09-03 | 500 | keep | 0 | Sep | 2021 | 0.00034055 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
PONCE | 2021-09-03 17:44 | 2021-09-04 09:43 | 150 | 015:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 100 EN CORTE DE LINEA CRUCE DE FASE POR AVE | P21090300035 | New_Event |  |  | Include | Wildlife | 959 | 2021-09-03 | 143850 | keep | 0 | Sep | 2021 | 0.097976 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-09-03 17:54 | 2021-09-04 10:25 | 60 | 016:31 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21090300138 | New_Event | Bad Weather | Include | Include | Weather | 991 | 2021-09-03 | 59460 | keep | 0 | Sep | 2021 | 0.040498 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
ARECIBO | 2021-09-03 17:56 | 2021-09-04 13:45 | 75 | 019:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA ABB-100 AMP | A21090300082 | New_Event | Cutout Failure | Include | Include | Equipment | 1189 | 2021-09-03 | 89175 | keep | 0 | Sep | 2021 | 0.060737 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
ARECIBO | 2021-09-03 18:05 | 2021-09-04 22:25 | 40 | 028:20 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A21090300143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1700 | 2021-09-03 | 68000 | keep | 0 | Sep | 2021 | 0.046314 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
ARECIBO | 2021-09-03 18:13 | 2021-09-03 20:28 | 20 | 002:15 | P | PARARRAYOS DEFECTUOSO | 1 X 25 EN TRANSFORMADOR SE CAMBIO PARARRAYO | A21090300146 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 135 | 2021-09-03 | 2700 | keep | 0 | Sep | 2021 | 0.001839 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2021-09-03 18:14 | 2021-09-04 18:00 | 10 | 023:46 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | A21090300147 | New_Event | Bad Weather | Include | Include | Weather | 1426 | 2021-09-03 | 14260 | keep | 0 | Sep | 2021 | 0.0097124 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
ARECIBO | 2021-09-03 18:17 | 2021-09-03 18:24 | 3431 | 000:07 | T | MAL TIEMPO/RAYOS/WET ASH | DISPARO DE INTERRUPTOR CON RE CLOSE RELAY EN OFF | A21090300149 | New_Event | Bad Weather | Include | Include | Weather | 7 | 2021-09-03 | 24017 | keep | 0 | Sep | 2021 | 0.016358 | 0.0023368 | Sustained | FALSE | FALSE | Not_TMED_Event | 3431
CANOVANAS | 2021-09-03 18:18 | 2021-09-03 19:47 | 20 | 001:29 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 20 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR MAL TIEMPO | R21090300040 | New_Event | Bad Weather | Include | Include | Weather | 89 | 2021-09-03 | 1780 | keep | 0 | Sep | 2021 | 0.0012123 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-09-03 18:24 | 2021-09-03 19:45 | 80 | 001:21 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | A21090300132 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 81 | 2021-09-03 | 6480 | keep | 0 | Sep | 2021 | 0.0044135 | 0 | Sustained | FALSE | TRUE | Not_TMED_Event | 0
CANOVANAS | 2021-09-03 18:30 | 2021-09-03 21:31 | 20 | 003:01 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHE | R21090300041 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 181 | 2021-09-03 | 3620 | keep | 0 | Sep | 2021 | 0.0024656 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2021-09-03 18:43 | 2021-09-04 17:40 | 20 | 022:57 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | A21090300164 | New_Event | Bad Weather | Include | Include | Weather | 1377 | 2021-09-03 | 27540 | keep | 0 | Sep | 2021 | 0.018757 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-09-03 18:50 | 2021-09-04 18:00 | 100 | 023:10 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 140 EN CORTE DE LINEA MAL TIEMPO | A21090300165 | New_Event | Bad Weather | Include | Include | Weather | 1390 | 2021-09-03 | 139000 | keep | 0 | Sep | 2021 | 0.094672 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-03 18:54 | 2021-09-04 16:50 | 70 | 021:56 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | A21090300166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1316 | 2021-09-03 | 92120 | keep | 0 | Sep | 2021 | 0.062743 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
MAYAGÃœEZ | 2021-09-03 18:57 | 2021-09-04 17:13 | 1000 | 022:16 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA PARTIDA Y SE CERRO CORTE DE LINEA | M21090300090 | New_Event | Wire Down | Include | Include | Equipment | 1336 | 2021-09-03 | 1336000 | keep | 0 | Sep | 2021 | 0.90994 | 0.0006811 | Sustained | FALSE | TRUE | Not_TMED_Event | 1000
ARECIBO | 2021-09-03 19:04 | 2021-09-04 11:10 | 80 | 016:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21090300167 | New_Event | Bad Weather | Include | Include | Weather | 966 | 2021-09-03 | 77280 | keep | 0 | Sep | 2021 | 0.052635 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
MAYAGÃœEZ | 2021-09-03 19:19 | 2021-09-04 12:15 | 200 | 016:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA DE 100AMP. MARCA COOPER | M21090300097 | New_Event | Cutout Failure | Include | Include | Equipment | 1016 | 2021-09-03 | 203200 | keep | 0 | Sep | 2021 | 0.1384 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-09-03 19:32 | 2021-09-04 11:43 | 1 | 016:11 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21090300156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 971 | 2021-09-03 | 971 | keep | 0 | Sep | 2021 | 0.00066134 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
BAYAMON | 2021-09-03 19:41 | 2021-09-04 10:05 | 15 | 014:24 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | B21090300158 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 864 | 2021-09-03 | 12960 | keep | 0 | Sep | 2021 | 0.008827 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2021-09-03 19:47 | 2021-09-04 12:15 | 150 | 016:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 N CORTE DE LINEA CRUCE DE FASES POR AVE | P21090300043 | New_Event |  |  | Include | Wildlife | 988 | 2021-09-03 | 148200 | keep | 0 | Sep | 2021 | 0.10094 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
SAN JUAN | 2021-09-03 19:50 | 2021-09-03 19:51 | 1271 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21090300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-03 | 1271 | keep | 0 | Sep | 2021 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
SAN JUAN | 2021-09-03 19:52 | 2021-09-03 21:07 | 65 | 001:15 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R21090300045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2021-09-03 | 4875 | keep | 0 | Sep | 2021 | 0.0033203 | 4.4271e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 65
MAYAGÃœEZ | 2021-09-03 20:05 | 2021-09-03 23:10 | 15 | 003:05 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | M21090300076 | New_Event | Secondary Wire Down | Include | Include | Equipment | 185 | 2021-09-03 | 2775 | keep | 0 | Sep | 2021 | 0.00189 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2021-09-03 20:21 | 2021-09-03 20:22 | 1271 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21090300000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-03 | 1271 | keep | 0 | Sep | 2021 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
CAGUAS | 2021-09-03 20:27 | 2021-09-04 11:04 | 40 | 014:37 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | FIJO BAJANTE DE LINEA A CAJA | C21090300098 | New_Event | Wire Down | Include | Include | Equipment | 877 | 2021-09-03 | 35080 | keep | 0 | Sep | 2021 | 0.023893 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-03 20:29 | 2021-09-03 20:30 | 1271 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21090300000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-03 | 1271 | keep | 0 | Sep | 2021 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
AGUADILLA | 2021-09-03 20:31 | 2021-09-04 23:40 | 100 | 027:09 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M21090300299 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1629 | 2021-09-03 | 162900 | keep | 0 | Sep | 2021 | 0.11095 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-03 20:33 | 2021-09-04 10:30 | 20 | 013:57 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA PRIMARIA | A21090300192 | New_Event | Vegetation Contact | Include | Include | Vegetation | 837 | 2021-09-03 | 16740 | keep | 0 | Sep | 2021 | 0.011402 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
ARECIBO | 2021-09-03 20:41 | 2021-09-04 11:48 | 40 | 015:07 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO PUENTE PRIMARIO | A21090300195 | New_Event | Wire Down | Include | Include | Equipment | 907 | 2021-09-03 | 36280 | keep | 0 | Sep | 2021 | 0.02471 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2021-09-03 20:48 | 2021-09-04 13:51 | 20 | 017:03 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 100 KVA AVERIADO X 100 KVA | A21090300197 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1023 | 2021-09-03 | 20460 | keep | 0 | Sep | 2021 | 0.013935 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2021-09-03 20:48 | 2021-09-04 09:17 | 200 | 012:29 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | B21090300169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 749 | 2021-09-03 | 149800 | keep | 0 | Sep | 2021 | 0.10203 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
MAYAGÃœEZ | 2021-09-03 21:00 | 2021-09-04 11:20 | 50 | 014:20 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE FIJO LINEA AL AISLADOR | M21090300117 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 860 | 2021-09-03 | 43000 | keep | 0 | Sep | 2021 | 0.029287 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-03 21:02 | 2021-09-04 09:49 | 234 | 012:47 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO CAUSA | C21090300100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 767 | 2021-09-03 | 179478 | keep | 0 | Sep | 2021 | 0.12224 | 0.00015938 | Sustained | FALSE | TRUE | Not_TMED_Event | 234
BARRANQUITAS | 2021-09-03 21:07 | 2021-09-04 19:21 | 150 | 022:14 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C21090300102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1334 | 2021-09-03 | 200100 | keep | 0 | Sep | 2021 | 0.13629 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
BAYAMON | 2021-09-03 21:37 | 2021-09-04 00:31 | 23 | 002:54 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA | S2109030074 | New_Event | Secondary Wire Down | Include | Include | Equipment | 174 | 2021-09-03 | 4002 | keep | 0 | Sep | 2021 | 0.0027257 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
CANOVANAS | 2021-09-03 22:12 | 2021-09-03 22:29 | 9 | 000:17 | P | DESGANCHE | 1 X 10 EN CORTE DE LINEA | R21090300047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 17 | 2021-09-03 | 153 | keep | 0 | Sep | 2021 | 0.00010421 | 6.1299e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 9
UTUADO | 2021-09-03 23:03 | 2021-09-04 12:09 | 15 | 013:06 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 10 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21090300215 | New_Event | Bad Weather | Include | Include | Weather | 786 | 2021-09-03 | 11790 | keep | 0 | Sep | 2021 | 0.0080301 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
ARECIBO | 2021-09-03 23:36 | 2021-09-04 18:40 | 700 | 019:04 | P | ESTRUCTURA AVERIADA | 3 X 100 EN CONVERTIDOR Y 3 X 140 EN CORTE DE LINEA SE REMPLAZO POSTE | A21090300227 | New_Event | Defective Pole | Include | Include | Equipment | 1144 | 2021-09-03 | 800800 | keep | 0 | Sep | 2021 | 0.54542 | 0.00047677 | Sustained | FALSE | TRUE | Not_TMED_Event | 700
CANOVANAS | 2021-09-03 23:59 | 2021-09-04 09:53 | 31 | 009:54 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO PENCA DE LA LINEA | R21090300053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 594 | 2021-09-03 | 18414 | keep | 0 | Sep | 2021 | 0.012542 | 2.1114e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 31
CAGUAS | 2021-09-04 01:23 | 2021-09-04 01:24 | 2859 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21090400005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-04 | 2859 | keep | 0 | Sep | 2021 | 0.0019473 | 0.0019473 | Momentary | FALSE | FALSE | Not_TMED_Event | 2859
GUAYAMA | 2021-09-04 02:08 | 2021-09-04 09:46 | 40 | 007:38 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA CRUCE DE FASES POR RAMA | P21090400004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 458 | 2021-09-04 | 18320 | keep | 0 | Sep | 2021 | 0.012478 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
AGUADILLA | 2021-09-04 02:56 | 2021-09-04 02:57 | 1827 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M21090400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-04 | 1827 | keep | 0 | Sep | 2021 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
CANOVANAS | 2021-09-04 03:17 | 2021-09-04 09:22 | 200 | 006:05 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | R21090400001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 365 | 2021-09-04 | 73000 | keep | 0 | Sep | 2021 | 0.04972 | 0.00013622 | Sustained | FALSE | TRUE | Not_TMED_Event | 200
ARECIBO | 2021-09-04 04:04 | 2021-09-04 04:05 | 3431 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A21090400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-04 | 3431 | keep | 0 | Sep | 2021 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
VEGA BAJA | 2021-09-04 04:14 | 2021-09-04 16:23 | 60 | 012:09 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA SE RETIRO CULEBRA | B21090400006 | New_Event |  |  | Include | Wildlife | 729 | 2021-09-04 | 43740 | keep | 0 | Sep | 2021 | 0.029791 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-09-04 06:38 | 2021-09-04 06:40 | 1615 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S21090400006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-04 | 3230 | keep | 0 | Sep | 2021 | 0.0021999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
PONCE | 2021-09-04 06:46 | 2021-09-04 11:21 | 300 | 004:35 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIERON MACHETES PARA CERRAR PUENTE PRIMARIO | P21090400006 | New_Event | Wire Down | Include | Include | Equipment | 275 | 2021-09-04 | 82500 | keep | 0 | Sep | 2021 | 0.05619 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
FAJARDO | 2021-09-04 06:59 | 2021-09-04 08:32 | 19 | 001:33 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | R21090400007 | New_Event |  |  | Include | Wildlife | 93 | 2021-09-04 | 1767 | keep | 0 | Sep | 2021 | 0.0012035 | 1.2941e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 19
ARECIBO | 2021-09-04 07:16 | 2021-09-05 10:11 | 35 | 026:55 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | A21090400012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1615 | 2021-09-04 | 56525 | keep | 0 | Sep | 2021 | 0.038499 | 2.3838e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 35
PONCE | 2021-09-04 07:24 | 2021-09-04 07:25 | 778 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR 5011-05 | P21090400007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-04 | 778 | keep | 0 | Sep | 2021 | 0.00052989 | 0.00052989 | Momentary | FALSE | FALSE | Not_TMED_Event | 778
PONCE | 2021-09-04 07:24 | 2021-09-04 07:25 | 1746 | 000:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR CARGA POR 5011-05 | P21090400007 | New_Event | Other Causes | Include | Include | Other | 1 | 2021-09-04 | 1746 | keep | 0 | Sep | 2021 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
PONCE | 2021-09-04 07:24 | 2021-09-04 07:25 | 113 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | P21090400007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-04 | 113 | keep | 0 | Sep | 2021 | 7.6964e-05 | 7.6964e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 113
SAN JUAN | 2021-09-04 07:33 | 2021-09-04 07:34 | 556 | 000:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 20% DE LA CARGA ESTA POR 1118-10 | S21090400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-04 | 556 | keep | 0 | Sep | 2021 | 0.00037869 | 0.00037869 | Momentary | FALSE | FALSE | Not_TMED_Event | 556
SAN JUAN | 2021-09-04 07:33 | 2021-09-04 07:34 | 2782 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA EL 20% DEL 1111-01 | S21090400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-04 | 2782 | keep | 0 | Sep | 2021 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
FAJARDO | 2021-09-04 07:44 | 2021-09-04 09:47 | 23 | 002:03 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 30 EN CORTE DE LINEA Y 1 X 8 EN TRANSFORMADOR CRUCE POR AVE | R21090400010 | New_Event |  |  | Include | Wildlife | 123 | 2021-09-04 | 2829 | keep | 0 | Sep | 2021 | 0.0019268 | 1.5665e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 23
ARECIBO | 2021-09-04 07:44 | 2021-09-04 16:00 | 1 | 008:16 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 10 EN TRANSFORMADOR SE REMPLAZARON CONECTORES | A21090400017 | New_Event | Secondary Wire Down | Include | Include | Equipment | 496 | 2021-09-04 | 496 | keep | 0 | Sep | 2021 | 0.00033782 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-09-04 08:00 | 2021-09-04 12:17 | 300 | 004:17 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE ABRE MACHETE Y SE CIERRA N/O CONTRA 1401-8 FRENTE A GARAJE SHELL EN CARRETERA 845 POR ACCIDENTE DE AUTO TUMBO POSTE Y LINEA | S21090400013 | New_Event |  |  | Include | Wildlife | 257 | 2021-09-04 | 77100 | keep | 0 | Sep | 2021 | 0.052512 | 0.00020433 | Sustained | TRUE | TRUE | Not_TMED_Event | 300
SAN JUAN | 2021-09-04 08:00 | 2021-09-04 17:48 | 100 | 009:48 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE LEVANTO LINEA PRIMARIA POR ACCIDENTE AUTO | S21090400014 | New_Event |  |  | Include | Wildlife | 588 | 2021-09-04 | 58800 | keep | 0 | Sep | 2021 | 0.040048 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
ARECIBO | 2021-09-04 08:00 | 2021-09-04 16:30 | 15 | 008:30 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | A21090400019 | New_Event | Bad Weather | Include | Include | Weather | 510 | 2021-09-04 | 7650 | keep | 0 | Sep | 2021 | 0.0052104 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
CAGUAS | 2021-09-04 08:13 | 2021-09-04 08:14 | 1879 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO | C21090400015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-04 | 1879 | keep | 0 | Sep | 2021 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
ARECIBO | 2021-09-04 08:16 | 2021-09-04 14:30 | 2 | 006:14 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN CORTE DE LINEA MAL TIEMPO | A21090400024 | New_Event | Bad Weather | Include | Include | Weather | 374 | 2021-09-04 | 748 | keep | 0 | Sep | 2021 | 0.00050946 | 1.3622e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 2
CAGUAS | 2021-09-04 08:36 | 2021-09-04 15:37 | 15 | 007:01 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21090400018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 421 | 2021-09-04 | 6315 | keep | 0 | Sep | 2021 | 0.0043011 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
ARECIBO | 2021-09-04 08:38 | 2021-09-04 12:00 | 80 | 003:22 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 80 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A21090400009 | New_Event | Bad Weather | Include | Include | Weather | 202 | 2021-09-04 | 16160 | keep | 0 | Sep | 2021 | 0.011007 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-09-04 08:56 | 2021-09-04 09:17 | 10 | 000:21 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARARON CONEXIONES EN SECUNDARIA | S21090300112 | New_Event | Secondary Wire Down | Include | Include | Equipment | 21 | 2021-09-04 | 210 | keep | 0 | Sep | 2021 | 0.00014303 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2021-09-04 08:58 | 2021-09-04 12:17 | 15 | 003:19 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHO Y RETEZO LINEAS | C21090400020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2021-09-04 | 2985 | keep | 0 | Sep | 2021 | 0.0020331 | 1.0216e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 15
BAYAMON | 2021-09-04 09:12 | 2021-09-04 09:14 | 1715 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL CARGA TRANSFERIDA AL 1708-03 | B21090400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-04 | 3430 | keep | 0 | Sep | 2021 | 0.0023362 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2021-09-04 09:12 | 2021-09-04 09:14 | 1498 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA LA CARGA DEL 1708-02 | B21090400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-04 | 2996 | keep | 0 | Sep | 2021 | 0.0020406 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
ARECIBO | 2021-09-04 09:12 | 2021-09-04 12:30 | 50 | 003:18 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 40 EN CORTE DE LINEA AVE CREO AVERIA | A21090400043 | New_Event |  |  | Include | Wildlife | 198 | 2021-09-04 | 9900 | keep | 0 | Sep | 2021 | 0.0067428 | 3.4055e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 50
CAGUAS | 2021-09-04 09:15 | 2021-09-04 20:14 | 1 | 010:59 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO CUASA | C21090400021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 659 | 2021-09-04 | 659 | keep | 0 | Sep | 2021 | 0.00044884 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
CANOVANAS | 2021-09-04 09:16 | 2021-09-04 16:21 | 17 | 007:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | R21090400018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 425 | 2021-09-04 | 7225 | keep | 0 | Sep | 2021 | 0.0049209 | 1.1579e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 17
BAYAMON | 2021-09-04 09:18 | 2021-09-04 09:20 | 1825 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR 1118-09 | S21090400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-04 | 3650 | keep | 0 | Sep | 2021 | 0.002486 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
BAYAMON | 2021-09-04 09:18 | 2021-09-04 09:20 | 4398 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA CARGA DEL 1118-08 | S21090400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-04 | 8796 | keep | 0 | Sep | 2021 | 0.0059909 | 0.0029955 | Momentary | FALSE | FALSE | Not_TMED_Event | 4398
SAN JUAN | 2021-09-04 09:21 | 2021-09-04 13:35 | 1 | 004:14 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR Y SE REEMPLAZARON BARRAS EN PEDESTAL | S21090400047 | New_Event | Secondary Wire Down | Include | Include | Equipment | 254 | 2021-09-04 | 254 | keep | 0 | Sep | 2021 | 0.000173 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2021-09-04 09:24 | 2021-09-06 11:03 | 8 | 049:39 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REMPLAZAR BARRAS DE PEDESTAL | C21090400023 | New_Event | Secondary Wire Down | Include | Include | Equipment | 2979 | 2021-09-04 | 23832 | keep | 0 | Sep | 2021 | 0.016232 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2021-09-04 09:30 | 2021-09-04 21:10 | 1 | 011:40 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE | A21090400047 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 700 | 2021-09-04 | 700 | keep | 0 | Sep | 2021 | 0.00047677 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2021-09-04 09:34 | 2021-09-04 10:29 | 10 | 000:55 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | R21090400019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2021-09-04 | 550 | keep | 0 | Sep | 2021 | 0.0003746 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
CANOVANAS | 2021-09-04 09:38 | 2021-09-04 09:39 | 2708 | 000:01 | T | ANIMAL U OBJETO EXTRAÃ‘O | RECERRO INTERRUPTOR | R21090400021 | New_Event |  |  | Include | Wildlife | 1 | 2021-09-04 | 2708 | keep | 0 | Sep | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2021-09-04 09:39 | 2021-09-05 06:21 | 10 | 020:42 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R21090400057 | 1st_after_momentary |  |  | Include | Wildlife | 1242 | 2021-09-04 | 12420 | keep | 0 | Sep | 2021 | 0.0084592 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2021-09-04 09:39 | 2021-09-04 12:15 | 148 | 002:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 Y 1 X 80 EN CORTES DE LINEA SE REEMPLAZO CAJA PRIMARIA Y AISLADOR | R21090400026 | New_Event | Cutout Failure | Include | Include | Equipment | 156 | 2021-09-04 | 23088 | keep | 0 | Sep | 2021 | 0.015725 | 0.0001008 | Sustained | FALSE | TRUE | Not_TMED_Event | 148
YAUCO | 2021-09-04 10:04 | 2021-09-04 13:49 | 5 | 003:45 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE DE LINEA PRIMARIA A CAJA EN TRANSFORMADOR | P21090400014 | New_Event | Wire Down | Include | Include | Equipment | 225 | 2021-09-04 | 1125 | keep | 0 | Sep | 2021 | 0.00076623 | 3.4055e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 5
CAGUAS | 2021-09-04 10:10 | 2021-09-04 17:48 | 30 | 007:38 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 30 EN CORTE DE LINEA LEVANTO NEUTRAL PRIMARIO | C21090400027 | New_Event | Wire Down | Include | Include | Equipment | 458 | 2021-09-04 | 13740 | keep | 0 | Sep | 2021 | 0.0093583 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
SAN JUAN | 2021-09-04 10:11 | 2021-09-04 12:43 | 549 | 002:32 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA LEVANTAR ALAMBRE PRIMARIO PARTIDO LLEVA LA CARGA DE 1329-02 | S21090400000 | New_Event | Wire Down | Include | Include | Equipment | 152 | 2021-09-04 | 83448 | keep | 0 | Sep | 2021 | 0.056836 | 0.00037392 | Sustained | FALSE | FALSE | Not_TMED_Event | 549
SAN JUAN | 2021-09-04 10:11 | 2021-09-04 12:43 | 644 | 002:32 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE ABRIO INTERRUPTOR PARA LEVANTAR ALAMBRE PRIMARIO PARTIDO CARGA POR 1328-04 | S21090400000 | Additional_clients | Wire Down | Include | Include | Equipment | 152 | 2021-09-04 | 97888 | keep | 0 | Sep | 2021 | 0.066671 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2021-09-04 10:12 | 2021-09-04 10:16 | 3431 | 000:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR RECIERRE EN OFF NO SE REPORTO CAUSA | A21090400051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2021-09-04 | 13724 | keep | 0 | Sep | 2021 | 0.0093474 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2021-09-04 10:19 | 2021-09-04 14:55 | 1 | 004:36 | P | MAL TIEMPO/RAYOS/WET ASH | 2 X 15 EN RISER MAL TIEMPO | A21090400054 | New_Event | Bad Weather | Include | Include | Weather | 276 | 2021-09-04 | 276 | keep | 0 | Sep | 2021 | 0.00018798 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2021-09-04 10:31 | 2021-09-04 12:13 | 40 | 001:42 | P | CABLE SOTERRADO AVERIADO | 1 X 80 EN SU-1 SE DEJO ABIERTO SU-7 A SU-6 | S21090400030 | New_Event | UG Cable Fault | Include | Include | Equipment | 102 | 2021-09-04 | 4080 | keep | 0 | Sep | 2021 | 0.0027789 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2021-09-04 10:46 | 2021-09-04 16:35 | 40 | 005:49 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 40 EN CORTE DE LINEA REPARO SECUNDARIA | C21090400032 | New_Event | Secondary Wire Down | Include | Include | Equipment | 349 | 2021-09-04 | 13960 | keep | 0 | Sep | 2021 | 0.0095081 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
SAN JUAN | 2021-09-04 11:06 | 2021-09-04 11:53 | 10 | 000:47 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | S21090300118 | New_Event | Secondary Wire Down | Include | Include | Equipment | 47 | 2021-09-04 | 470 | keep | 0 | Sep | 2021 | 0.00032011 | 6.811e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 10
MAYAGÃœEZ | 2021-09-04 11:16 | 2021-09-04 11:53 | 2225 | 000:37 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR PARA PODER ABRIR CONVERTIDOR POR LINEA DE TRANSMISION POR DEBAJO DE DISTRIBUCCION | M21090400054 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 37 | 2021-09-04 | 82325 | keep | 0 | Sep | 2021 | 0.056071 | 0.0015154 | Sustained | FALSE | TRUE | Not_TMED_Event | 2225
HUMACAO | 2021-09-04 11:27 | 2021-09-04 14:46 | 10 | 003:19 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C21090400042 | New_Event | Secondary Wire Down | Include | Include | Equipment | 199 | 2021-09-04 | 1990 | keep | 0 | Sep | 2021 | 0.0013554 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2021-09-04 11:49 | 2021-09-04 15:30 | 12 | 003:41 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A21090400072 | New_Event | Secondary Wire Down | Include | Include | Equipment | 221 | 2021-09-04 | 2652 | keep | 0 | Sep | 2021 | 0.0018063 | 8.1731e-06 | Sustained | FALSE | TRUE | Not_TMED_Event | 12
BAYAMON | 2021-09-04 11:58 | 2021-09-04 15:27 | 10 | 003:29 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | B21090400028 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 209 | 2021-09-04 | 2090 | keep | 0 | Sep | 2021 | 0.0014235 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2021-09-04 12:09 | 2021-09-04 14:55 | 70 | 002:46 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA | P21090400028 | New_Event | Wire Down | Include | Include | Equipment | 166 | 2021-09-04 | 11620 | keep | 0 | Sep | 2021 | 0.0079143 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
SAN JUAN | 2021-09-04 12:13 | 2021-09-04 13:30 | 448 | 001:17 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR AL PERSONAL DE CAMPO PARA HACER PRUEBA EN SU EN RESIDENCIAL NEMESIO CANALES SE CERRO EN SUBESTACION. LLEVA EL 90% DEL 1420-03 | S21090400000 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 77 | 2021-09-04 | 34496 | keep | 0 | Sep | 2021 | 0.023495 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-09-04 12:13 | 2021-09-04 12:31 | 1617 | 000:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21090400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2021-09-04 | 29106 | keep | 0 | Sep | 2021 | 0.019824 | 0.0011013 | Sustained | FALSE | TRUE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2021-09-04 12:13 | 2021-09-04 12:31 | 1017 | 000:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21090400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2021-09-04 | 18306 | keep | 0 | Sep | 2021 | 0.012468 | 0.00069267 | Sustained | FALSE | TRUE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2021-09-04 12:13 | 2021-09-04 12:31 | 828 | 000:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21090400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2021-09-04 | 14904 | keep | 0 | Sep | 2021 | 0.010151 | 0.00056395 | Sustained | FALSE | TRUE | Not_TMED_Event | 828
MAYAGÃœEZ | 2021-09-04 12:13 | 2021-09-04 12:31 | 863 | 000:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21090400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2021-09-04 | 15534 | keep | 0 | Sep | 2021 | 0.01058 | 0.00058779 | Sustained | FALSE | TRUE | Not_TMED_Event | 863
MAYAGÃœEZ | 2021-09-04 12:13 | 2021-09-04 12:31 | 309 | 000:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21090400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2021-09-04 | 5562 | keep | 0 | Sep | 2021 | 0.0037883 | 0.00021046 | Sustained | FALSE | TRUE | Not_TMED_Event | 309
MAYAGÃœEZ | 2021-09-04 12:13 | 2021-09-04 12:31 | 176 | 000:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M21090400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2021-09-04 | 3168 | keep | 0 | Sep | 2021 | 0.0021577 | 0.00011987 | Sustained | FALSE | TRUE | Not_TMED_Event | 176
SAN JUAN | 2021-09-04 12:17 | 2021-09-04 17:48 | 300 | 005:31 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE LEVANTO LINEA PRIMARIA Y SE CERRO MACHETE 100% EN SERIVICIO | S21090400013 | New_Event |  |  | Include | Wildlife | 331 | 2021-09-04 | 99300 | keep | 0 | Sep | 2021 | 0.067633 | 0.00020433 | Sustained | FALSE | TRUE | Not_TMED_Event | 300
BAYAMON | 2021-09-04 12:19 | 2021-09-04 14:13 | 75 | 001:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | B21090400010 | New_Event | Cutout Failure | Include | Include | Equipment | 114 | 2021-09-04 | 8550 | keep | 0 | Sep | 2021 | 0.0058234 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
BAYAMON | 2021-09-04 12:20 | 2021-09-04 17:11 | 55 | 004:51 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S21090400048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 291 | 2021-09-04 | 16005 | keep | 0 | Sep | 2021 | 0.010901 | 3.746e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 55
SAN JUAN | 2021-09-04 12:38 | 2021-09-04 13:30 | 492 | 000:52 | P | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR AL PERSONAL DE CAMPO PARA HACER PRUEBA EN SU DE RESIDENCIAL NEMESIO CANALES SE CERRO EN SUBESTACION EL 90% DEL 1420-03 ESTA POR EL 1419-13 | S21090400000 | New_Event | UG Cable Fault | Include | Include | Equipment | 52 | 2021-09-04 | 25584 | keep | 0 | Sep | 2021 | 0.017425 | 0.0003351 | Sustained | FALSE | FALSE | Not_TMED_Event | 492
SAN JUAN | 2021-09-04 13:30 | 2021-09-05 18:26 | 50 | 028:56 | P | CABLE SOTERRADO AVERIADO | 1 X 80 EN SU-6 AVERIA NUEVA DE SU-6 A T-56 SE CERRO N/O EN T-52 A T-55 SE INSTALO TAG EN SU-7 Y T-52 | S21090400030 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1736 | 2021-09-04 | 86800 | keep | 0 | Sep | 2021 | 0.059119 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-04 13:48 | 2021-09-04 17:13 | 100 | 003:25 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE LEVANTO PRIMARIA | S21090400061 | New_Event | Wire Down | Include | Include | Equipment | 205 | 2021-09-04 | 20500 | keep | 0 | Sep | 2021 | 0.013962 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
SAN JUAN | 2021-09-04 13:56 | 2021-09-04 18:59 | 180 | 005:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE DESGANCHO Y REEMPLAZARON CAJA PRIMARIA | R21090400034 | New_Event | Cutout Failure | Include | Include | Equipment | 303 | 2021-09-04 | 54540 | keep | 0 | Sep | 2021 | 0.037147 | 0.0001226 | Sustained | FALSE | TRUE | Not_TMED_Event | 180
MAYAGÃœEZ | 2021-09-04 14:25 | 2021-09-04 15:57 | 100 | 001:32 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | M21090400093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2021-09-04 | 9200 | keep | 0 | Sep | 2021 | 0.0062661 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
BAYAMON | 2021-09-04 14:30 | 2021-09-05 19:45 | 8 | 029:15 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO SECUNDARIA AVERIADA | B21090400040 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1755 | 2021-09-04 | 14040 | keep | 0 | Sep | 2021 | 0.0095626 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2021-09-04 14:31 | 2021-09-04 14:32 | 3387 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21090400041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-04 | 3387 | keep | 0 | Sep | 2021 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
VEGA BAJA | 2021-09-04 14:39 | 2021-09-04 14:40 | 3387 | 000:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B21090400043 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-04 | 3387 | keep | 0 | Sep | 2021 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
BAYAMON | 2021-09-04 14:56 | 2021-09-04 18:31 | 3597 | 003:35 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO ALIMENTADOR HACIA CIUDAD DORADA | B21090400000 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 215 | 2021-09-04 | 773355 | keep | 0 | Sep | 2021 | 0.52673 | 0.0024499 | Sustained | FALSE | FALSE | Not_TMED_Event | 3597
VEGA BAJA | 2021-09-04 15:00 | 2021-09-04 16:12 | 3387 | 001:12 | T | NO SE REPORTO CAUSA | SE SECCIONALIZO ALIMENTADOR | B21090400047 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 72 | 2021-09-04 | 243864 | keep | 0 | Sep | 2021 | 0.16609 | 0.0023069 | Sustained | FALSE | FALSE | Not_TMED_Event | 3387
MAYAGÃœEZ | 2021-09-04 15:13 | 2021-09-04 15:14 | 1287 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE DE INTERRUPTOR | M21090400104 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-04 | 1287 | keep | 0 | Sep | 2021 | 0.00087657 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
MAYAGÃœEZ | 2021-09-04 15:14 | 2021-09-05 20:35 | 150 | 029:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO LINEA PRIMARIA | M21090400173 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 1761 | 2021-09-04 | 264150 | keep | 0 | Sep | 2021 | 0.17991 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-09-04 15:33 | 2021-09-05 17:17 | 10 | 025:44 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 25 EN TRANSFORMADOR | A21090400106 | New_Event | Bad Weather | Include | Include | Weather | 1544 | 2021-09-04 | 15440 | keep | 0 | Sep | 2021 | 0.010516 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2021-09-04 15:45 | 2021-09-04 19:32 | 30 | 003:47 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C21090400058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2021-09-04 | 6810 | keep | 0 | Sep | 2021 | 0.0046383 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
GUAYAMA | 2021-09-04 16:03 | 2021-09-04 17:45 | 80 | 001:42 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO EN MACHETE | P21090400034 | New_Event | Wire Down | Include | Include | Equipment | 102 | 2021-09-04 | 8160 | keep | 0 | Sep | 2021 | 0.0055577 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2021-09-04 16:04 | 2021-09-05 10:43 | 30 | 018:39 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21090400082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1119 | 2021-09-04 | 33570 | keep | 0 | Sep | 2021 | 0.022864 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-04 16:09 | 2021-09-04 19:30 | 40 | 003:21 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | A21090400111 | New_Event | Wire Down | Include | Include | Equipment | 201 | 2021-09-04 | 8040 | keep | 0 | Sep | 2021 | 0.005476 | 2.7244e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 40
VEGA BAJA | 2021-09-04 16:12 | 2021-09-04 17:04 | 850 | 000:52 | P | NO SE REPORTO CAUSA | SE SECCIONALIZO ALIMENTADOR | B21090400047 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 52 | 2021-09-04 | 44200 | keep | 0 | Sep | 2021 | 0.030104 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2021-09-04 16:12 | 2021-09-04 17:38 | 852 | 001:26 | P | NO SE REPORTO CAUSA | SE SECCIONALIZO ALIMENTADOR Y NO SE ENCONTRO CAUSA PARA EL DISPARO | B21090400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 86 | 2021-09-04 | 73272 | keep | 0 | Sep | 2021 | 0.049905 | 0.00058029 | Sustained | FALSE | FALSE | Not_TMED_Event | 852
PONCE | 2021-09-04 16:13 | 2021-09-04 16:56 | 20 | 000:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE FIJO BAJANTE PRIMARIO A CAJA DE TRANSFORMADOR | P21090400037 | New_Event | Wire Down | Include | Include | Equipment | 43 | 2021-09-04 | 860 | keep | 0 | Sep | 2021 | 0.00058574 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2021-09-04 16:20 | 2021-09-04 19:12 | 80 | 002:52 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA CRUCE DE FASES POR RAMA | P21090400040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2021-09-04 | 13760 | keep | 0 | Sep | 2021 | 0.0093719 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
HUMACAO | 2021-09-04 17:08 | 2021-09-05 08:36 | 196 | 015:28 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C21090400061 | New_Event |  |  | Include | Wildlife | 928 | 2021-09-04 | 181888 | keep | 0 | Sep | 2021 | 0.12388 | 0.00013349 | Sustained | FALSE | TRUE | Not_TMED_Event | 196
ARECIBO | 2021-09-04 17:10 | 2021-09-04 21:00 | 80 | 003:50 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | A21090400124 | New_Event | Bad Weather | Include | Include | Weather | 230 | 2021-09-04 | 18400 | keep | 0 | Sep | 2021 | 0.012532 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
SAN JUAN | 2021-09-04 17:24 | 2021-09-05 18:50 | 12 | 025:26 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | 1 X 25 TRANSFORMADOR SE REPARO BAJANTE Y SE RETEZO TOMA | S21090400036 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1526 | 2021-09-04 | 18312 | keep | 0 | Sep | 2021 | 0.012472 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2021-09-04 17:26 | 2021-09-05 11:20 | 30 | 017:54 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21090400125 | New_Event | Bad Weather | Include | Include | Weather | 1074 | 2021-09-04 | 32220 | keep | 0 | Sep | 2021 | 0.021945 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
CAGUAS | 2021-09-04 17:33 | 2021-09-05 08:59 | 185 | 015:26 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C21090400066 | New_Event |  |  | Include | Wildlife | 926 | 2021-09-04 | 171310 | keep | 0 | Sep | 2021 | 0.11668 | 0.000126 | Sustained | FALSE | TRUE | Not_TMED_Event | 185
SAN JUAN | 2021-09-04 17:52 | 2021-09-05 12:20 | 30 | 018:28 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA | S21090400091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1108 | 2021-09-04 | 33240 | keep | 0 | Sep | 2021 | 0.02264 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
ARECIBO | 2021-09-04 17:56 | 2021-09-05 11:48 | 1 | 017:52 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE REPARO TREE WIRE PARTIDO EN TRANSFORMADOR | A21090400130 | New_Event | Wire Down | Include | Include | Equipment | 1072 | 2021-09-04 | 1072 | keep | 0 | Sep | 2021 | 0.00073013 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2021-09-04 18:00 | 2021-09-05 12:55 | 30 | 018:55 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | C21090400073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1135 | 2021-09-04 | 34050 | keep | 0 | Sep | 2021 | 0.023191 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-09-04 18:31 | 2021-09-04 19:00 | 100 | 000:29 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REMPLAZO AISLACION EN SU | B21090400000 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 29 | 2021-09-04 | 2900 | keep | 0 | Sep | 2021 | 0.0019752 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2021-09-04 18:39 | 2021-09-04 18:45 | 2225 | 000:06 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR PARA CERRAR CONVERTIDOR POR LINEA 1900 | M21090400144 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2021-09-04 | 13350 | keep | 0 | Sep | 2021 | 0.0090926 | 0.0015154 | Sustained | FALSE | TRUE | Not_TMED_Event | 2225
AGUADILLA | 2021-09-04 18:49 | 2021-09-04 21:46 | 150 | 002:57 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | M21090400149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2021-09-04 | 26550 | keep | 0 | Sep | 2021 | 0.018083 | 0.00010216 | Sustained | FALSE | TRUE | Not_TMED_Event | 150
ARECIBO | 2021-09-04 19:03 | 2021-09-04 20:50 | 75 | 001:47 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | A21090400140 | New_Event | Bad Weather | Include | Include | Weather | 107 | 2021-09-04 | 8025 | keep | 0 | Sep | 2021 | 0.0054658 | 5.1082e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 75
HUMACAO | 2021-09-04 19:10 | 2021-09-04 19:11 | 1835 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21090400083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-04 | 1835 | keep | 0 | Sep | 2021 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
GUAYAMA | 2021-09-04 19:15 | 2021-09-04 21:40 | 60 | 002:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA 100A | P21090400046 | New_Event | Cutout Failure | Include | Include | Equipment | 145 | 2021-09-04 | 8700 | keep | 0 | Sep | 2021 | 0.0059255 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
AGUADILLA | 2021-09-04 19:31 | 2021-09-05 21:30 | 10 | 025:59 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO EEI 37.5 KVA/2400 SERIE-1847007 POR 37.5 KVA | M21090400155 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1559 | 2021-09-04 | 15590 | keep | 0 | Sep | 2021 | 0.010618 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2021-09-04 19:37 | 2021-09-05 10:30 | 70 | 014:53 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | A21090400146 | New_Event | Bad Weather | Include | Include | Weather | 893 | 2021-09-04 | 62510 | keep | 0 | Sep | 2021 | 0.042575 | 4.7677e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 70
BAYAMON | 2021-09-04 19:42 | 2021-09-04 19:43 | 3597 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | B21090400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-04 | 3597 | keep | 0 | Sep | 2021 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
MAYAGÃœEZ | 2021-09-04 19:47 | 2021-09-05 09:15 | 130 | 013:28 | P | MAL TIEMPO/RAYOS/WET ASH | 1 X 80 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M21090400160 | New_Event | Bad Weather | Include | Include | Weather | 808 | 2021-09-04 | 105040 | keep | 0 | Sep | 2021 | 0.071542 | 8.8542e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 130
BAYAMON | 2021-09-04 19:51 | 2021-09-05 14:45 | 40 | 018:54 | P | EMPALME O TERMINACION SOTERRADA AVERIADA | 1 X 100 EN RISER SE REPARO TERMINACION | B21090400158 | New_Event | UG - Broken Splice / Terminal | Include | Include | Equipment | 1134 | 2021-09-04 | 45360 | keep | 0 | Sep | 2021 | 0.030894 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2021-09-04 20:09 | 2021-09-05 08:59 | 210 | 012:50 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | C21090400092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 770 | 2021-09-04 | 161700 | keep | 0 | Sep | 2021 | 0.11013 | 0.00014303 | Sustained | FALSE | TRUE | Not_TMED_Event | 210
CAGUAS | 2021-09-04 20:22 | 2021-09-05 08:33 | 187 | 012:11 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C21090400098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 731 | 2021-09-04 | 136697 | keep | 0 | Sep | 2021 | 0.093104 | 0.00012736 | Sustained | FALSE | TRUE | Not_TMED_Event | 187
BAYAMON | 2021-09-04 20:29 | 2021-09-05 11:26 | 30 | 014:57 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | B21090400169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 897 | 2021-09-04 | 26910 | keep | 0 | Sep | 2021 | 0.018328 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
BAYAMON | 2021-09-04 20:34 | 2021-09-05 15:35 | 30 | 019:01 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO CONDUCTOR | B21090400171 | New_Event | Wire Down | Include | Include | Equipment | 1141 | 2021-09-04 | 34230 | keep | 0 | Sep | 2021 | 0.023314 | 2.0433e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 30
AGUADILLA | 2021-09-04 21:01 | 2021-09-05 12:24 | 100 | 015:23 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M21090400195 | New_Event | Vegetation Contact | Include | Include | Vegetation | 923 | 2021-09-04 | 92300 | keep | 0 | Sep | 2021 | 0.062865 | 6.811e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 100
AGUADILLA | 2021-09-04 21:14 | 2021-09-05 14:37 | 20 | 017:23 | P | SECUNDARIA/CONDUCTOR ROTO, ABIERTO O CRU | SE REPARO LINEA SECUNDARIA | M21090400181 | New_Event | Secondary Wire Down | Include | Include | Equipment | 1043 | 2021-09-04 | 20860 | keep | 0 | Sep | 2021 | 0.014208 | 1.3622e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 20
CAGUAS | 2021-09-04 21:23 | 2021-09-05 09:56 | 209 | 012:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA CAJA PRIMARIA AVERIADA | C21090400118 | New_Event | Cutout Failure | Include | Include | Equipment | 753 | 2021-09-04 | 157377 | keep | 0 | Sep | 2021 | 0.10719 | 0.00014235 | Sustained | FALSE | TRUE | Not_TMED_Event | 209
BAYAMON | 2021-09-04 22:11 | 2021-09-04 23:24 | 3941 | 001:13 | T | ESTRUCTURA AVERIADA | SE ABRIO PUENTE HACIA POSTE PODRIDO/PARTIDO Y SE CERRO POR SCADA | B21090500071 | New_Event | Defective Pole | Include | Include | Equipment | 73 | 2021-09-04 | 287693 | keep | 0 | Sep | 2021 | 0.19595 | 0.0026842 | Sustained | FALSE | FALSE | Not_TMED_Event | 3941
AGUADILLA | 2021-09-04 22:13 | 2021-09-05 16:45 | 60 | 018:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA CHAINT 100 AMP | M21090400199 | New_Event | Cutout Failure | Include | Include | Equipment | 1112 | 2021-09-04 | 66720 | keep | 0 | Sep | 2021 | 0.045443 | 4.0866e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 60
SAN JUAN | 2021-09-04 22:17 | 2021-09-05 13:01 | 10 | 014:44 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | R21090400055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 884 | 2021-09-04 | 8840 | keep | 0 | Sep | 2021 | 0.0060209 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2021-09-04 23:04 | 2021-09-05 12:22 | 200 | 013:18 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE CERRO PUENTE PRIMARIO ABIERTO | M21090400204 | New_Event | Wire Down | Include | Include | Equipment | 798 | 2021-09-04 | 159600 | keep | 0 | Sep | 2021 | 0.1087 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2021-09-04 23:24 | 2021-09-05 17:17 | 10 | 017:53 | P | ESTRUCTURA AVERIADA | SE REMPLAZO POSTE PRIMARIO PARTIDO | B21090400208 | Partial_restoration | Defective Pole | Include | Include | Equipment | 1073 | 2021-09-04 | 10730 | keep | 0 | Sep | 2021 | 0.0073082 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2021-09-04 23:24 | 2021-09-05 00:20 | 20 | 000:56 | P | ESTRUCTURA AVERIADA | SE SECCONALIZO POSTE PARTIDO | B21090400000 | New_Event | Defective Pole | Include | Include | Equipment | 56 | 2021-09-04 | 1120 | keep | 0 | Sep | 2021 | 0.00076283 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2021-09-04 23:24 | 2021-09-05 00:23 | 150 | 000:59 | P | ANIMAL U OBJETO EXTRAÃ‘O | SE SECCIONALIZO POSTE PARTIDO POR VEHICULO Y SE CERRARON MACHETES CONTRA EL 1710-03 | B21090400000 | New_Event |  |  | Include | Wildlife | 59 | 2021-09-04 | 8850 | keep | 0 | Sep | 2021 | 0.0060277 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2021-09-04 23:45 | 2021-09-05 12:56 | 46 | 013:11 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN CORTES DE LINEA ENREDADERA | C21090400135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 791 | 2021-09-04 | 36386 | keep | 0 | Sep | 2021 | 0.024782 | 3.133e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 46
ARECIBO | 2021-09-05 02:36 | 2021-09-05 12:00 | 1 | 009:24 | P | OTRAS CAUSAS | 1 X 30 EN CORTE DE LINEA POR CONTAMINACION DE SALITRE EN EL AREA | A21090500002 | New_Event | Other Causes | Include | Include | Other | 564 | 2021-09-05 | 564 | keep | 0 | Sep | 2021 | 0.00038414 | 6.811e-07 | Sustained | FALSE | TRUE | Not_TMED_Event | 1
FAJARDO | 2021-09-05 02:54 | 2021-09-05 02:55 | 2286 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | R21090500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-05 | 2286 | keep | 0 | Sep | 2021 | 0.001557 | 0.001557 | Momentary | FALSE | FALSE | Not_TMED_Event | 2286
CAGUAS | 2021-09-05 04:07 | 2021-09-05 04:08 | 1510 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | C21090500006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-05 | 1510 | keep | 0 | Sep | 2021 | 0.0010285 | 0.0010285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1510
BAYAMON | 2021-09-05 04:11 | 2021-09-05 04:13 | 2735 | 000:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | B21090500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-05 | 5470 | keep | 0 | Sep | 2021 | 0.0037256 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
PONCE | 2021-09-05 04:48 | 2021-09-05 04:49 | 3718 | 000:01 | T | NO SE REPORTO CAUSA | RECIERRE | P210905000XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-05 | 3718 | keep | 0 | Sep | 2021 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
AGUADILLA | 2021-09-05 05:09 | 2021-09-05 05:10 | 650 | 000:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M21090500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2021-09-05 | 650 | keep | 0 | Sep | 2021 | 0.00044271 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
AGUADILLA | 2021-09-05 05:10 | 2021-09-05 11:12 | 80 | 006:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA PRIMARIA | M21090400208 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 362 | 2021-09-05 | 28960 | keep | 0 | Sep | 2021 | 0.019725 | 5.4488e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 80
BARRANQUITAS | 2021-09-05 05:21 | 2021-09-05 14:58 | 43 | 009:37 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | C21090500007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 577 | 2021-09-05 | 24811 | keep | 0 | Sep | 2021 | 0.016899 | 2.9287e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 43
CANOVANAS | 2021-09-05 06:21 | 2021-09-05 06:22 | 2708 | 000:01 | T | CONDUCTOR ROTO, ABIERTO O CRUZADO | RECIERRE | R21090500002 | New_Event | Wire Down | Include | Include | Equipment | 1 | 2021-09-05 | 2708 | keep | 0 | Sep | 2021 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2021-09-05 06:22 | 2021-09-05 08:42 | 10 | 002:20 | P | ANIMAL U OBJETO EXTRAÃ‘O | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R21090400057 | Partial_restoration |  |  | Include | Wildlife | 140 | 2021-09-05 | 1400 | keep | 0 | Sep | 2021 | 0.00095353 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2021-09-05 06:22 | 2021-09-05 12:05 | 60 | 005:43 | P | CONDUCTOR ROTO, ABIERTO O CRUZADO | SE LEVANTO CONDUCTOR NO FUNDIO | R21090500007 | 1st_after_momentary | Wire Down | Include | Include | Equipment | 343 | 2021-09-05 | 20580 | keep | 0 | Sep | 2021 | 0.014017 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2021-09-05 06:39 | 2021-09-05 09:32 | 726 | 002:53 | T | HERRAJE ROTO O PODRIDO | SE REMPLAZO CRUCETA PARTIDA A LA SALIDA DE ALIMENTADOR LLEVA CARGA DEL 1346-04 | S21090500000 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 173 | 2021-09-05 | 125598 | keep | 0 | Sep | 2021 | 0.085544 | 0.00049448 | Sustained | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2021-09-05 06:39 | 2021-09-05 09:32 | 3932 | 002:53 | T | HERRAJE ROTO O PODRIDO | SE REMPLAZO CRUCETA PARTIDA A LA SALIDA DE ALIMENTADOR CARGA POR 1303-03 | S21090500000 | New_Event | Broken / Rusty Hardware | Include | Include | Equipment | 173 | 2021-09-05 | 680236 | keep | 0 | Sep | 2021 | 0.46331 | 0.0026781 | Sustained | FALSE | FALSE | Not_TMED_Event | 3932
ARECIBO | 2021-09-05 06:48 | 2021-09-05 21:28 | 28 | 014:40 | P | CABLE SOTERRADO AVERIADO | AVERIA SOTERRADA DEL T-24 AL T-23 SE INSTALO AEREO PROVISIONAL | A21090500006 | New_Event | UG Cable Fault | Include | Include | Equipment | 880 | 2021-09-05 | 24640 | keep | 0 | Sep | 2021 | 0.016782 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
BAYAMON | 2021-09-05 07:00 | 2021-09-05 17:36 | 25 | 010:36 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | B21090500013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 636 | 2021-09-05 | 15900 | keep | 0 | Sep | 2021 | 0.010829 | 1.7027e-05 | Sustained | FALSE | TRUE | Not_TMED_Event | 25
CAGUAS | 2021-09-05 07:33 | 2021-09-05 11:12 | 1 | 003:39 | P | SECUNDARIA/DESGANCHE | 2 X 10 EN BANCO DE TRANSFORMADORES SE RETIRO ENREDADERA | C21090500015 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 219 | 2021-09-05 | 219 | keep | 0 | Sep | 2021 | 0.00014916 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2021-09-05 07:38 | 2021-09-05 07:40 | 3654 | 000:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | A21090500009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2021-09-05 | 7308 | keep | 0 | Sep | 2021 | 0.0049774 | 0.0024887 | Momentary | FALSE | FALSE | Not_TMED_Event | 3654
UTUADO | 2021-09-05 07:51 | 2021-09-05 10:00 | 180 | 002:09 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA POR DESGANCHE | A21090500014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2021-09-05 | 23220 | keep | 0 | Sep | 2021 | 0.015815 | 0.0001226 | Sustained | FALSE | TRUE | Not_TMED_Event | 180
BAYAMON | 2021-09-05 07:53 | 2021-09-05 07:54 | 1588 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA LA CARGA DEL 1711-03 | B21090500019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-05 | 1588 | keep | 0 | Sep | 2021 | 0.0010816 | 0.0010816 | Momentary | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2021-09-05 07:53 | 2021-09-05 07:54 | 13 | 000:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA TRANSFERIDA AL 1711-01 | B21090500019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2021-09-05 | 13 | keep | 0 | Sep | 2021 | 8.8542e-06 | 8.8542e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 13