## Info
Transmission and Distribution Quarterly Metrics
LUMA Personnel | Regulatory - Performance Metrics
Phone | 7873491241
Email | performance-metrics@lumapr.com
Generation Quarterly Metrics
Genera Personnel | Regulatory Project Manager
Phone | (787) 307-8202
Email | regulatory@genera-pr.com

## Generation
Reported by | Metric Category | Metric | Sub-Group | Unit of Measure | 2019-06-01 | 2019-07-01 | 2019-08-01 | 2019-09-01 | 2019-10-01 | 2019-11-01 | 2019-12-01 | 2020-01-01 | 2020-02-01 | 2020-03-01 | 2020-04-01 | 2020-05-01 | 2020-06-01 | 2020-07-01 | 2020-08-01 | 2020-09-01 | 2020-10-01 | 2020-11-01 | 2020-12-01 | 2021-01-01 | 2021-02-01 | 2021-03-01 | 2021-04-01 | 2021-05-01 | 2021-06-01 | 2021-07-01 | 2021-08-01 | 2021-09-01 | 2021-10-01 | 2021-11-01 | 2021-12-01 | 2022-01-01 | 2022-02-01 | 2022-03-01 | 2022-04-01 | 2022-05-01 | 2022-06-01 | 2022-07-01 | 2022-08-01 | 2022-09-01 | 2022-10-01 | 2022-11-01 | 2022-12-01 | 2023-01-01 | 2023-02-01 | 2023-03-01 | 2023-04-01 | 2023-05-01 | 2023-06-01 | 2023-07-01 | 2023-08-01 | 2023-09-01 | 2023-10-01 | 2023-11-01 | 2023-12-01 | 2024-01-01 | 2024-02-01 | 2024-03-01 | 2024-04-01 | 2024-05-01 | 2024-06-01 | 2024-07-01 | 2024-08-01 | 2024-09-01 | 2024-10-01 | 2024-11-01 | 2024-12-01 | 2025-01-01 | 2025-02-01 | 2025-03-01 | 2025-04-01 | 2025-05-01 | 2025-06-01 | 2025-07-01 | 2025-08-01 | 2025-09-01 | 2025-10-01 | 2025-11-01 | 2025-12-01 | Comments
Genera PR | Safety | OSHA Recordable Rate |  | Rate | 11.3726 | 8.3262 | 12.5135 | 9.7179 | 7.7913 | 6.5335 | 6.1737 | 10.3266 | 5.4015 | 4.7828 | 0.47399 | 1.896 | 2.4028 | 1.1865 | 1.2726 | 1.1337 | 2.2662 | 1.2595 | 1.7581 | 1.6192 | 2.0722 | 3.0586 | 1.9387 | 1.397 | 6.55 | 6.29 | 6.08 | 2.19 | 5.66 | 6.35 | 2.4 | 2.92 | 5.49 | 5.54 | 2.94 | 3.09 | 4.43 | 4.54 | 4.49 | 3.44 | 7.27 | 10.4 | 5.72 | 5.69 | 8.4 | 3.1 | 2.44 | 2.37 | 2.71 | 2.43 | 3.58 | 0 | 11.93 | 1.69 | 2.36 | 5.83 | 4.73 | 0 | 1.59 | 2.8 | 2.62 | 3.55 | 1.56 | 7.52 | 4.4 | 0 | 4.71 | 6.12 | 4.86 | 1.58 | 0 | 0 | 3.17 | 4.87 | 1.64 | 0 | 0 | 0 | 0
Genera PR | Safety | OSHA DART Rate |  | Rate | 5.4494 | 6.3671 | 7.6169 | 6.4786 | 5.12 | 3.9769 | 4.5632 | 6.3782 | 4.1444 | 4.7828 | 0.47399 | 0.94798 | 2.0596 | 1.1865 | 1.2726 | 1.1337 | 2.2662 | 1.0076 | 1.4651 | 1.3494 | 1.15 | 1.67 | 1.66 | 1.4 | 6.55 | 1.05 | 3.65 | 2.2 | 5.7 | 6.4 | 2.4 | 1.5 | 4.4 | 3.3 | 2.2 | 1 | 4.4 | 1.1 | 2.2 | 1.4 | 3.1 | 8.1 | 3.4 | 4.27 | 6.3 | 2.33 | 2.44 | 2.37 | 2.71 | 2.43 | 3.58 | 0 | 11.93 | 0 | 1.18 | 3.89 | 1.58 | 0 | 1.59 | 2.8 | 1.31 | 3.55 | 1.56 | 6.02 | 4.4 | 0 | 4.71 | 6.12 | 0 | 1.58 | 0 | 0 | 3.17 | 3.25 | 1.64 | 0 | 0 | 0 | 0
Genera PR | Safety | OSHA Severity Rate |  | Rate | 31.9856 | 28.8967 | 51.6862 | 33.7814 | 27.6034 | 23.0094 | 24.9632 | 41.9138 | 20.2614 | 51.1159 | 7.1098 | 8.0578 | 40.5046 | 11.8648 | 12.3016 | 7.4826 | 21.5285 | 10.0761 | 27.2502 | 9.7153 | 10.82 | 13.07 | 32.96 | 10.48 | 6.55 | 6.29 | 34.08 | 12.4 | 43 | 34.3 | 0 | 7.3 | 19.8 | 25.5 | 15.4 | 8.2 | 16.6 | 7.9 | 7.9 | 14.4 | 23.9 | 32.4 | 29.7 | 15.65 | 62.97 | 11.64 | 12.2 | 7.1 | 52.8 | 17.02 | 26.86 | 0 | 83.51 | 0 | 16.5 | 13.61 | 22.06 | 0 | 11.14 | 42.02 | 13.1 | 8.88 | 7.82 | 22.57 | 29.32 | 0 | 7.85 | 30.62 | 12.97 | 11.07 | 0 | 0 | 6.35 | 13 | 44.36 | 0 | 0 | 0 | 0
Genera PR | Safety | OSHA Fatality Rate |  | Rate | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Genera PR | Human Resources | Budgeted headcounts by employee type | Exempt | Number | [49 empty] | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311
Genera PR | Human Resources | Budgeted headcounts by employee type | Non-exempt | Number | [49 empty] | 492 | 492 | 492 | 492 | 492 | 492 | 492 | 492 | 492 | 492 | 492 | 492 | 492 | 492 | 492 | 492 | 492 | 492 | 492 | 492 | 492 | 492 | 492 | 492 | 492 | 492 | 492 | 492 | 492 | 492
Genera PR | Human Resources | Actual headcounts by employee type | Exempt | Number | [49 empty] | 218 | 216 | 234 | 238 | 245 | 242 | 250 | 246 | 247 | 248 | 250 | 272 | 276 | 274 | 278 | 276 | 276 | 274 | 274 | 275 | 264 | 264 | 264 | 263 | 255 | 255 | 262 | 261 | 264 | 264
Genera PR | Human Resources | Actual headcounts by employee type | Non-exempt | Number | [49 empty] | 476 | 476 | 475 | 479 | 474 | 472 | 471 | 466 | 463 | 466 | 464 | 447 | 449 | 449 | 447 | 447 | 448 | 448 | 445 | 443 | 433 | 436 | 434 | 441 | 444 | 442 | 435 | 436 | 438 | 434
Genera PR | Human Resources | Absenteeism |  | Percentage | 19.41% | 23.49% | 18.29% | 14.41% | 18.33% | 21.12% | 19.31% | 16.56% | 14.69% | 0% | 0% | 0% | 10.45% | 18.67% | 16.18% | 14.36% | 15.46% | 15.77% | 20.67% | 20.31% | 15.89% | 20.27% | 24.16% | 34.24% | 1.118% | 0.9598% | 1.865% | 23.52% | 23.59% | 24.75% | 26.54% | 26.52% | 21.63% | 14.15% | 17.6% | 19.06% | 18.24% | 22.62% | 19.35% | 17.03% | 15.41% | 19.43% | 19.89% | 19.27% | 18.15% | 17.72% | 18.65% | 24.81% | 27.11% | 0.17% | 0.47% | 1.29% | 2% | 3.41% | 3.94% | 4.4% | 3.7% | 9.9% | 7.73% | 8.95% | 8.52% | 10.9% | 11.3% | 8.04% | 6.48% | 7.26% | 9.57% | 6.42% | 5.81% | 6.42% | 6.68% | 9.63% | 11.6% | 10.45% | 7.28% | 6.56% | 6.29% | 10.08% | 10.29%
Genera PR | Finance | Operational expenses vs. budget (FYTD) | System | Percentage | 78.21% | 66.39% | 75.33% | 80.16% | 100.1% | 75.3% | 94.33% | 87.8% | 93.91% | 46.33% | 68.61% | 76.82% | 99.26% | 88.53% | 88.06% | 82.24% | 76.73% | 110.9% | 92.75% | 50.65% | 118.7% | 91.61% | 97.29% | 85.4% | 213.5% | 149% | -12.15% | 81.65% | -37.17% | -83.6% | -25.79% | -45.99% | -17.8% | -19.5% | 63.03% | -30.86% | 79.86% | -22.85% | 10.38% | -5.685% | 73.9% | 31.97% | -75.14% | 0.6721% | 39.57% | -3.344% | 10.08% | 24.47% | 116.3% | 4.811% | 10.44% | 18.72% | 25.2% | 34.59% | 44.16% | 50.03% | 55.71% | 63.68% | 72.3% | 79.86% | 91.15% | 7.41% | 14.4% | 22.38% | 30.4% | 38.15% | 46.31% | 52.86% | 59.96% | 66.45% | 72.46% | 81.17% | 93.34% | 5.58% | 12.91% | 18.69% | 25.52% | 31.4% | 38.37%
Genera PR | Finance | Operational expenses vs. budget (FYTD) | Labor | Percentage | [49 empty] | 4.227% | 9.975% | 15.53% | 21.16% | 26.86% | 38.55% | 45.46% | 51.98% | 59.22% | 69.79% | 79.82% | 89.58% | 7.876% | 15.2% | 22.66% | 31.55% | 39.1% | 46.85% | 54.95% | 62.17% | 69.08% | 75.72% | 86.39% | 98.31% | 5.47% | 15.71% | 22.54% | 30.51% | 37.01% | 44.11%
Genera PR | Finance | Operational expenses vs. budget (FYTD) | Non-Labor | Percentage | [49 empty] | 5.137% | 10.7% | 20.51% | 27.46% | 38.91% | 47.29% | 52.59% | 57.8% | 66.17% | 73.69% | 79.88% | 92.02% | 7.146% | 13.95% | 22.23% | 29.74% | 37.61% | 46% | 51.68% | 58.71% | 64.96% | 70.62% | 78.22% | 90.52% | 5.65% | 11.25% | 16.43% | 22.57% | 28.09% | 34.99%
Genera PR | Finance | Capital expenses vs. budget (FYTD) | NME | Percentage | [49 empty] | 0% | 0% | 1.049% | 3.852% | 10.06% | 17.75% | 26.05% | 34.7% | 42.99% | 53.85% | 63.01% | 91.18% | 2.299% | 4.282% | 5.664% | 10.32% | 16.2% | 27.13% | 36.69% | 45.18% | 57.45% | 64.48% | 86.63% | 99.99% | -0.52% | 1.77% | 5.16% | 9.141% | 13.38% | 17.19%
Genera PR | Finance | Capital expenses vs. budget (FYTD) | System | Percentage | 39.71% | 3.515% | 4.23% | 4.432% | 5.06% | 5.43% | 6.654% | 3.063% | 7.54% | 6.503% | 3.964% | 6.082% | 23.29% | 4.109% | 7.931% | 3.098% | 7.73% | 8.955% | 9.666% | 4.031% | 10.62% | 6.572% | 5.349% | 8.285% | 3.622% | -70.26% | 393.1% | 54.73% | 2.233% | -88.83% | -48.51% | 79.18% | -16.47% | 167.7% | 40.71% | 56.24% | 214.4% | -99.25% | -47.44% | -27.5% | -12.18% | -30.75% | 26.13% | -30.36% | 9.43% | 72.88% | -41.15% | 19.89% | 198.3%
Genera PR | Finance | Capital expenses vs. budget (FYTD) | Federally funded | Percentage | [49 empty] | 0.0619% | 2.256% | 7.972% | 9.588% | 10.57% | 23.48% | 29.9% | 54.41% | 64.65% | 72.9% | 97.6% | 110.8% | 0.5379% | 2.141% | 3.054% | 3.984% | 4.366% | 5.165% | 20.35% | 21.44% | 55.37% | 83.82% | 120.3% | 120.8% | 1.212% | 22.27% | 28.88% | 30.58% | 48.18% | 51%
Genera PR | Finance | Capital expenses vs. budget (FYTD) | Non-federally funded | Percentage | [49 empty] | 0% | 0% | 1.049% | 3.852% | 10.06% | 17.75% | 26.05% | 34.7% | 42.99% | 53.85% | 63.01% | 91.18% | 2.299% | 4.282% | 5.664% | 10.32% | 16.2% | 27.13% | 36.69% | 45.18% | 57.45% | 64.48% | 86.63% | 99.99% | -0.52% | 1.77% | 5.16% | 9.141% | 13.38% | 17.19%
Genera PR | Generation | Plant availability (system) |  | Percentage | 60.54% | 56.36% | 53.85% | 49.28% | 58.34% | 59.94% | 64.55% | 42.25% | 40.19% | 39.41% | 41.19% | 45.61% | 56.32% | 52.98% | 57.06% | 62.83% | 47.8% | 50.66% | 53.98% | 54.87% | 47.96% | 44.29% | 46.63% | 49.2% | 55.2% | 54.67% | 50.54% | 49% | 48% | 57% | 54.21% | 58.57% | 55.43% | 52.63% | 41.15% | 49.54% | 55.49% | 56.12% | 50.4% | 43.54% | 41.54% | 43.93% | 48.06% | 41% | 42.48% | 51.71% | 52.16% | 42.87% | 52.29% | 47.13% | 48.56% | 45.6% | 46.38% | 44.77% | 42.02% | 37.71% | 44.37% | 40.79% | 37.41% | 49.2% | 56.38% | 56.6% | 58.09% | 55.12% | 51% | 53% | 44% | 53.49% | 56.06% | 52.07% | 46.35% | 49.04% | 48.25% | 51.49% | 52.73% | 56.04% | 55.71% | 53.95% | 48.91%
Genera PR | Generation | Forced outages (system) |  | Percentage | 22.14% | 29.65% | 30.55% | 25.52% | 23.2% | 21.78% | 7.85% | 28.37% | 33.76% | 38.75% | 44.51% | 35.16% | 29.31% | 31.43% | 28.29% | 23.5% | 24.28% | 24.53% | 21.25% | 19.86% | 13.88% | 11.94% | 13.81% | 16.81% | 17.5% | 23.15% | 23.71% | 35% | 36% | 30% | 32.87% | 22.92% | 16.83% | 16.59% | 27.66% | 17.89% | 14.32% | 13.55% | 15.34% | 30.04% | 40.73% | 37.32% | 28.82% | 33.2% | 30.49% | 28.39% | 32.24% | 37.26% | 27.99% | 28.83% | 29.98% | 31.48% | 29.26% | 31.81% | 29.57% | 32.31% | 19.82% | 32.26% | 23.48% | 20.99% | 22.42% | 31.73% | 22.53% | 32.6% | 24% | 12% | 15% | 29.62% | 29.05% | 29.83% | 31.5% | 33.57% | 34.24% | 30.45% | 32.47% | 28.52% | 28.68% | 29.25% | 32.77%
Genera PR | Generation | Cost of generation (system total), excluding PPOA's gen |  | $/kWh | 0.13527 | 0.13492 | 0.14599 | 0.13889 | 0.13236 | 0.12868 | 0.13631 | 0.17232 | 0.18057 | 0.14554 | 0.12651 | 0.10343 | 0.091045 | 0.10703 | 0.10819 | 0.10554 | 0.11516 | 0.1122 | 0.11785 | 0.11248 | 0.1276 | 0.13247 | 0.13542 | 0.1334 | 0.13321 | 0.13496 | 0.14295 | 0.15868 | 0.16269 | 0.17215 | 0.16574 | 0.16559 | 0.18993 | 0.19203 | 0.22059 | 0.23833 | 0.24519 | 0.23001 | 0.22796 | 0.25112 | 0.2581 | 0.24163 | 0.19959 | 0.15623 | 0.17715 | 0.13362 | 0.16941 | 0.19052 | 0.1413 | 0.24232 | 0.27268 | 0.22926 | 0.22103 | 0.27829 | 0.28168 | 0.27857 | 0.29511 | 0.2619 | 0.24923 | 0.24149 | 0.24766 | 0.26446 | 0.24358 | 0.22921 | 0.22175 | 0.24404 | 0.2524 | 0.23175 | 0.25311 | 0.24412 | 0.21618 | 0.21502 | 0.21735 | 0.21901 | 0.22292 | 0.22331 | 0.22523 | 0.22799 | 0.24232 | Eliminated Palo Seco Mobile Packs from calculations.
Genera PR | Generation | Cost of generation (system: fuel) |  | $/kWh | 0.12942 | 0.12685 | 0.13746 | 0.131 | 0.12123 | 0.12113 | 0.12691 | 0.16225 | 0.17293 | 0.13385 | 0.11698 | 0.091265 | 0.086141 | 0.098912 | 0.09956 | 0.096557 | 0.10633 | 0.12592 | 0.12782 | 0.12857 | 0.13653 | 0.14167 | 0.14461 | 0.14702 | 0.12007 | 0.12317 | 0.13344 | 0.14877 | 0.15949 | 0.16389 | 0.15641 | 0.15732 | 0.1791 | 0.17998 | 0.20977 | 0.22859 | 0.22635 | 0.22136 | 0.21796 | 0.24043 | 0.24424 | 0.22888 | 0.18599 | 0.14325 | 0.16376 | 0.12287 | 0.15974 | 0.18066 | 0.13036 | 0.23572 | 0.26395 | 0.22166 | 0.21401 | 0.2636 | 0.26422 | 0.26559 | 0.28055 | 0.24624 | 0.23945 | 0.23414 | 0.23616 | 0.24796 | 0.23598 | 0.22162 | 0.21473 | 0.22744 | 0.24121 | 0.21881 | 0.23428 | 0.23245 | 0.20691 | 0.19789 | 0.20467 | 0.20786 | 0.20504 | 0.20789 | 0.21063 | 0.21288 | 0.20766 | Eliminated Palo Seco Mobile Packs from calculations.
Genera PR | Generation | Cost of generation (system: O&M), excluding PPOA's gen) |  | $/kWh | 0.0062608 | 0.0085018 | 0.0090702 | 0.008482 | 0.011584 | 0.007934 | 0.0098108 | 0.010745 | 0.0083962 | 0.012436 | 0.010232 | 0.012853 | 0.0055691 | 0.0083983 | 0.0089618 | 0.0091244 | 0.009027 | 0.0097295 | 0.013726 | 0.0070708 | 0.014823 | 0.013715 | 0.014043 | 0.0079857 | 0.01314 | 0.011792 | 0.0095121 | 0.0099153 | 0.0032087 | 0.0082598 | 0.0093299 | 0.0082619 | 0.010829 | 0.012055 | 0.010819 | 0.0097355 | 0.018833 | 0.008653 | 0.0099945 | 0.010695 | 0.013852 | 0.012752 | 0.013595 | 0.012978 | 0.013388 | 0.010751 | 0.0096717 | 0.0098608 | 0.01093 | 0.0065985 | 0.00873 | 0.0084214 | 0.012582 | 0.014692 | 0.017466 | 0.012975 | 0.014563 | 0.015655 | 0.0097777 | 0.0073515 | 0.0115 | 0.0165 | 0.0076064 | 0.0075958 | 0.0070206 | 0.016596 | 0.011185 | 0.012935 | 0.01883 | 0.011671 | 0.0092721 | 0.017128 | 0.012684 | 0.011151 | 0.017872 | 0.015419 | 0.014595 | 0.015112 | 0.034661
Genera PR | Generation | Cost of generation (by Plant Type) | Steam - Fuel | $/kWh | 0.096476 | 0.081979 | 0.079864 | 0.094476 | 0.097411 | 0.096829 | 0.097649 | 0.10647 | 0.11153 | 0.11004 | 0.098026 | 0.067075 | 0.066742 | 0.083766 | 0.08396 | 0.091013 | 0.097615 | 0.092767 | 0.10017 | 0.10207 | 0.10311 | 0.10639 | 0.10966 | 0.10935 | 0.10347 | 0.11413 | 0.11912 | 0.12487 | 0.12524 | 0.11837 | 0.11723 | 0.13622 | 0.15423 | 0.16778 | 0.19259 | 0.20812 | 0.20834 | 0.20358 | 0.19672 | 0.20239 | 0.20494 | 0.20488 | 0.16732 | 0.13016 | 0.15137 | 0.10837 | 0.14016 | 0.15228 | 0.11125 | 0.13282 | 0.131 | 0.12917 | 0.14702 | 0.14177 | 0.13353 | 0.16661 | 0.21073 | 0.11977 | 0.11905 | 0.13935 | 0.14315 | 0.15451 | 0.14659 | 0.13713 | 0.13483 | 0.12649 | 0.116 | 0.13632 | 0.13803 | 0.1252 | 0.1177 | 0.11156 | 0.13171 | 0.1301 | 0.123 | 0.1198 | 0.11327 | 0.12114 | 0.12266
Genera PR | Generation | Cost of generation (by Plant Type) | Gas - Fuel | $/kWh | 0.47289 | 0.46482 | 0.41267 | 0.23926 | 0.3958 | 0.53666 | 0.86366 | 0.2954 | 0.31426 | 0.19571 | 0.16084 | 0.14951 | 0.15294 | 0.15224 | 0.1733 | 0.14122 | 0.14943 | 0.18855 | 0.14364 | 0.17967 | 0.16684 | 0.1786 | 0.21993 | 0.2488 | 0.2772 | 0.22261 | 0.23355 | 0.23866 | 0.36043 | 0.59013 | 0.5432 | 0.96708 | 1.0048 | 0.46616 | 0.31384 | 0.3455 | 0.40483 | 0.39287 | 0.37645 | 0.40206 | 0.36884 | 0.3869 | 0.75829 | 0.74074 | 0.33532 | 0.33499 | 0.40942 | 0.31524 | 0.20596 | 0.29451 | 0.33992 | 0.24824 | 0.24529 | 0.33322 | 0.32023 | 0.30801 | 0.31047 | 0.30044 | 0.29105 | 0.27477 | 0.27602 | 0.27343 | 0.25903 | 0.24815 | 0.24651 | 0.26583 | 0.23088 | 0.25434 | 0.26372 | 0.2558 | 0.24515 | 0.23489 | 0.24671 | 0.25228 | 0.25191 | 0.25822 | 0.26158 | 0.2653 | 0.25623 | Eliminated Palo Seco Mobile Packs from calculations.
Genera PR | Generation | Cost of generation (by Plant Type) | Steam - O&M | $/kWh | 0.0059427 | 0.0077512 | 0.0087637 | 0.0089797 | 0.010151 | 0.0068316 | 0.0083276 | 0.01209 | 0.0096049 | 0.014022 | 0.01019 | 0.014844 | 0.0049856 | 0.0082746 | 0.0081909 | 0.0063919 | 0.008783 | 0.0089574 | 0.013002 | 0.0051897 | 0.013905 | 0.0098063 | 0.011989 | 0.0068934 | 0.011825 | 0.010776 | 0.0086074 | 0.0094158 | 0.00173 | 0.006538 | 0.0076328 | 0.0062587 | 0.0083152 | 0.0095237 | 0.0092015 | 0.0080546 | 0.016838 | 0.0074085 | 0.0082064 | 0.0097589 | 0.015013 | 0.011471 | 0.011585 | 0.010334 | 0.011215 | 0.010061 | 0.0071909 | 0.0093649 | 0.00983 | 0.00050376 | 0.00051237 | 0.00054334 | 0.00050612 | 0.00060166 | 0.00071011 | 0.00092218 | 0.00094902 | 0.00083916 | 0.00085917 | 0.00057475 | 0.00048835 | 0.00048398 | 0.00052257 | 0.00052373 | 0.00056924 | 0.00059113 | 0.00081352 | 0.00067472 | 0.00068132 | 0.00089405 | 0.00095218 | 0.00063042 | 0.00056594 | 0.004729 | 0.0065564 | 0.0078122 | 0.0098187 | 0.015311 | 0.016513
Genera PR | Generation | Cost of generation (by Plant Type) | Gas - O&M | $/kWh | 0.007338 | 0.012479 | 0.0093377 | 0.0061951 | 0.024093 | 0.023594 | 0.039442 | 0.0065425 | 0.0046654 | 0.0072539 | 0.0090917 | 0.0074829 | 0.0063841 | 0.0076186 | 0.010894 | 0.027208 | 0.0083952 | 0.013128 | 0.017158 | 0.037686 | 0.016833 | 0.030294 | 0.026978 | 0.013358 | 0.022693 | 0.018922 | 0.013319 | 0.010026 | 0.010023 | 0.021909 | 0.021938 | 0.071272 | 0.080577 | 0.060739 | 0.017726 | 0.016382 | 0.029505 | 0.017466 | 0.020759 | 0.012722 | 0.0092818 | 0.018533 | 0.057641 | 0.10962 | 0.037293 | 0.014481 | 0.036482 | 0.010586 | 0.01378 | 0.0060947 | 0.0082176 | 0.007878 | 0.012076 | 0.01409 | 0.016755 | 0.012053 | 0.013614 | 0.014815 | 0.0089185 | 0.0067768 | 0.011012 | 0.016016 | 0.0070838 | 0.007072 | 0.0064513 | 0.016005 | 0.010371 | 0.01226 | 0.018149 | 0.010777 | 0.0083199 | 0.016498 | 0.012118 | 0.017573 | 0.029188 | 0.023027 | 0.019372 | 0.014912 | 0.052808
Genera PR | Generation | Cost of generation (by Plant Type) | Steam - Total | $/kWh | 0.10242 | 0.08973 | 0.088628 | 0.10346 | 0.10756 | 0.10366 | 0.10598 | 0.11856 | 0.12113 | 0.12406 | 0.10822 | 0.081919 | 0.071727 | 0.09204 | 0.092151 | 0.097405 | 0.1064 | 0.10172 | 0.11317 | 0.10726 | 0.11702 | 0.1162 | 0.12165 | 0.11625 | 0.1153 | 0.12491 | 0.12772 | 0.13428 | 0.12697 | 0.12491 | 0.12486 | 0.14247 | 0.16254 | 0.1773 | 0.20179 | 0.21617 | 0.22518 | 0.21099 | 0.20493 | 0.21215 | 0.21995 | 0.21636 | 0.17891 | 0.14049 | 0.16258 | 0.11843 | 0.14735 | 0.16164 | 0.12109 | 0.13333 | 0.13151 | 0.12971 | 0.14753 | 0.14237 | 0.13424 | 0.16753 | 0.21168 | 0.12061 | 0.11991 | 0.13993 | 0.14364 | 0.15499 | 0.14711 | 0.13765 | 0.1354 | 0.12708 | 0.11681 | 0.13699 | 0.13871 | 0.1261 | 0.11865 | 0.11219 | 0.13227 | 0.13484 | 0.12958 | 0.12764 | 0.12309 | 0.13645 | 0.13917
Genera PR | Generation | Cost of generation (by Plant Type) | Gas - Total | $/kWh | 0.48022 | 0.4773 | 0.42201 | 0.24545 | 0.41989 | 0.56026 | 0.90311 | 0.30194 | 0.31892 | 0.20296 | 0.16993 | 0.15699 | 0.15933 | 0.15986 | 0.18357 | 0.16843 | 0.15782 | 0.20168 | 0.1608 | 0.21735 | 0.18367 | 0.20889 | 0.24691 | 0.26174 | 0.2999 | 0.24154 | 0.24687 | 0.24869 | 0.37045 | 0.61204 | 0.56513 | 1.0383 | 1.0854 | 0.5269 | 0.33156 | 0.36189 | 0.43433 | 0.41034 | 0.3972 | 0.41478 | 0.37813 | 0.40543 | 0.81593 | 0.85036 | 0.37262 | 0.34947 | 0.4459 | 0.32583 | 0.21974 | 0.30061 | 0.34814 | 0.25531 | 0.25174 | 0.34731 | 0.33698 | 0.32006 | 0.32408 | 0.31526 | 0.29997 | 0.28154 | 0.28703 | 0.28945 | 0.26611 | 0.25523 | 0.25297 | 0.28183 | 0.24126 | 0.26661 | 0.28187 | 0.26658 | 0.25347 | 0.25139 | 0.25883 | 0.26986 | 0.2811 | 0.28124 | 0.28095 | 0.28022 | 0.30904 | Eliminated Palo Seco Mobile Packs from calculations.
PREPA | Generation | Cost of generation (by Plant Type) | Hydro Total | $/kWh | 0.075265 | 0.068198 | 0.074286 | 0.047117 | 0.049241 | 0.033881 | 0.086829 | 0.079581 | 0.23126 | 0.080944 | 0.11505 | 0.051725 | 0.068521 | 0.081248 | 0.065496 | 0.061169 | 0.053396 | 0.097798 | 0.088933 | 0.12668 | 0.13916 | 0.2658 | 0.18536 | 0.11109 | 0.08769 | 0.12419 | 0.10389 | 0.087211 | 0.044734 | 0.08886 | 0.13652 | 0.082866 | 0.16505 | 0.12828 | 0.11988 | 0.21701 | 0.42444 | 0.20387 | 0.11088 | 0.069554 | 0.049619 | 0.048186 | 0.10804 | 0.12134 | 0.11322 | 0.17037 | 0.077841 | 0.09117 | 0.13492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Genera PR | Generation | Monthly thermal generation (system), excluding PPOA's gen |  | GWh | 999.6632 | 1018.2134 | 1027.8909 | 1133.6933 | 1019.053 | 944.889 | 929.2833 | 930.379 | 881.3591 | 795.6137 | 807.386 | 989.369 | 1157.1811 | 1245.7424 | 1220.7623 | 1083.716 | 1020.0813 | 890.248 | 884.166 | 831.091 | 732.0577 | 870.3106 | 846.684 | 1006.7009 | 1085.4157 | 1158.1078 | 1209.5088 | 1081.43 | 1081.64 | 1130.68 | 1026.7164 | 965.9764 | 876.4683 | 869.5856 | 808.3326 | 991.2872 | 1059.019 | 1144.343 | 1195.3774 | 908.6459 | 992.4891 | 927.1809 | 857.7887 | 797.921 | 804.2617 | 1001.0207 | 953.9735 | 1053.4137 | 1167.9813 | 1245.9079 | 1195.0855 | 1152.7604 | 1002.3194 | 845.6864 | 715.7038 | 609.7847 | 580.6293 | 723.515 | 914.0804 | 1231.4727 | 1250.9471 | 1180.5743 | 1243.509 | 1258.4983 | 1193.818 | 1005.605 | 866.914 | 757.379 | 708.588 | 600.741 | 602.8702 | 765.1151 | 878.0035 | 951.389 | 970.815 | 948.9247 | 1107.8001 | 957.9234 | 788.8531
Genera PR | Generation | Monthly thermal generation (by plant) | San Juan - Steam | GWh | 47.289 | 37.962 | 37.121 | 55.823 | 52.77 | 54.271 | 44.914 | 70.421 | 94.347 | 110.956 | 66.038 | 72.844 | 61.081 | 102.585 | 81.28 | 80.076 | 55.562 | 51.289 | 50.705 | 0 | 0 | 0 | 0 | 0 | 40.874 | 58.923 | 61.97 | 37.89 | 80.62 | 91.1 | 79.742 | 69.916 | 64.711 | 67.603 | 84.77 | 89.322 | 93.914 | 75.955 | 79.573 | 81.712 | 109.613 | 88.441 | 66.08 | 82.664 | 67.583 | 0 | 0 | 0 | 29.631 | 62.845 | 51.924 | 51.561 | 57.817 | 71.453 | 94.094 | 99.612 | 62.96 | 30.987 | 49.53 | 50.091 | 50.407 | 59.123 | 104.819 | 103.577 | 53.63 | 48.47 | 0 | 16.27 | 48.6 | 53.948 | 48.787 | 50.69 | 54.105 | 46.973 | 55.18 | 42.58 | 55.447 | 51.136 | 46.31
Genera PR | Generation | Monthly thermal generation (by plant) | Palo Seco - Steam | GWh | 148.442 | 46.14 | 113.789 | 108.929 | 169.121 | 122.444 | 127.217 | 183.826 | 216.401 | 222.098 | 231.147 | 182.034 | 236.091 | 240.779 | 170.47 | 130.789 | 87.511 | 43.304 | 33.254 | 0 | 79.618 | 86.577 | 107.023 | 106.685 | 100.811 | 157.054 | 162.319 | 161.07 | 163.86 | 173.78 | 146.099 | 144.46 | 81.936 | 123.964 | 194.289 | 234.595 | 219.072 | 206.126 | 204.693 | 80.6112 | 110.605 | 108.932 | 191.923 | 178.018 | 175.71 | 179.27 | 163.649 | 219.653 | 147.229 | 193.858 | 97.489 | 101.995 | 109.626 | 77.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.306 | 103.15 | 107.723 | 108.31 | 87.8 | 88.17 | 106.87 | 102.7 | 97.513 | 85.786 | 108.042 | 72.811 | 87.348 | 88.69 | 80.721 | 156.103 | 107.745 | 160.79
Genera PR | Generation | Monthly thermal generation (by plant) | Costa Sur - Steam | GWh | 394.69 | 347.12 | 226.93 | 327.46 | 353.41 | 381.91 | 391.02 | 75.13 | 0 | 0 | 0 | 0 | 0 | 0 | 175.04 | 203.34 | 190.96 | 194.62 | 185.82 | 206.38 | 257.11 | 310.81 | 217.96 | 275.55 | 405.08 | 447.2 | 389.25 | 98.83 | 184.49 | 206.92 | 179.58 | 280.98 | 300.86 | 319.94 | 183.01 | 272.83 | 346.64 | 341.77 | 360.27 | 280.58 | 214.1 | 353.07 | 340.91 | 317.9 | 281.03 | 341.27 | 318.25 | 307.91 | 306.23 | 155.14 | 234.32 | 198.08 | 228.14 | 212.89 | 209.22 | 25.84 | 2.32 | 72.4 | 190.91 | 262.39 | 341.33 | 355.28 | 323.2 | 386.97 | 365.32 | 350.44 | 309.91 | 333.7 | 299.94 | 201.95 | 190.9 | 372.39 | 368.44 | 354.16 | 413.15 | 392.35 | 413.38 | 368.83 | 344.77
Genera PR | Generation | Monthly thermal generation (by plant) | Aguirre - Steam | GWh | 160.93 | 205.97 | 209.465 | 166.1 | 224.555 | 206.925 | 209.135 | 173.24 | 157.73 | 176.74 | 184.19 | 235.685 | 398.65 | 406.945 | 337.82 | 290 | 262.665 | 332.965 | 348.61 | 355.845 | 146.365 | 193.04 | 306.85 | 333.23 | 176.64 | 143.945 | 172.525 | 290.01 | 251.4 | 342.48 | 345.7 | 328.73 | 301.03 | 177.66 | 105.085 | 146.325 | 205.575 | 208.41 | 171.09 | 111.11 | 110.1 | 63.885 | 184.89 | 62.48 | 0 | 143.195 | 161.955 | 59.61 | 170.595 | 172.27 | 192.1 | 179.385 | 214.85 | 137.655 | 112.44 | 25.84 | 196.5 | 175.275 | 155.425 | 313.065 | 336.42 | 260.96 | 175.155 | 91.705 | 112.27 | 137.99 | 0 | 67.29 | 70.02 | 0 | 0 | 0 | 43.425 | 147.64 | 144.74 | 180.84 | 156.06 | 163.525 | 98.055
Genera PR | Generation | Monthly thermal generation (by plant) | San Juan - Combined Cycle | GWh | 160.945 | 261.72 | 263.027 | 188.555 | 136.148 | 126.342 | 121.411 | 152.976 | 148.301 | 66.529 | 86.12 | 212.856 | 204.878 | 218.272 | 239.032 | 251.812 | 240.844 | 174.264 | 176.687 | 229.783 | 133.186 | 128.819 | 122.589 | 172.043 | 255.79 | 250.851 | 267.612 | 259.76 | 239.54 | 206.41 | 177.736 | 112.821 | 99.858 | 140.84 | 119.764 | 91.189 | 92.397 | 201.159 | 231.928 | 170.708 | 190.446 | 175.186 | 41.308 | 135.973 | 220.808 | 269.581 | 234.826 | 275.805 | 272.69 | 286.869 | 280.508 | 276.511 | 256.494 | 230.156 | 202.127 | 253.841 | 200.554 | 244.201 | 114.817 | 137.854 | 170.311 | 192.997 | 116.725 | 131.251 | 116.04 | 102.89 | 130.61 | 113.398 | 101.853 | 127.658 | 126.228 | 150.393 | 221.196 | 200.816 | 165.37 | 192.618 | 207.31 | 168.586 | 77.447
Genera PR | Generation | Monthly thermal generation (by plant) | Aguirre - Combined Cycle | GWh | 57.121 | 72.825 | 116.954 | 142.621 | 54.894 | 39.899 | 24.206 | 110.592 | 123.829 | 100.493 | 130.685 | 138.732 | 127.962 | 132.05 | 111.859 | 66.007 | 108.199 | 65.587 | 57.171 | 28.574 | 82.986 | 99.309 | 65.469 | 67.868 | 56.74 | 48.003 | 51.432 | 114.91 | 78.03 | 50.69 | 48.565 | 17.504 | 17.707 | 22.87 | 53.011 | 87.645 | 64.429 | 71.784 | 82.949 | 56.667 | 108.032 | 52.925 | 3.216 | 0 | 15.116 | 19.405 | 24.71 | 75.735 | 62.75 | 80.928 | 60.409 | 41.727 | 53.625 | 52.895 | 33.288 | 36.172 | 28.132 | 25.708 | 56.469 | 74.388 | 52.214 | 33.926 | 84.013 | 85.835 | 109.93 | 41.55 | 61.774 | 27.7 | 19.875 | 29.16 | 48.774 | 47.17 | 75.839 | 73.09 | 59.935 | 37.56 | 65.814 | 59.939 | 37.857
Genera PR | Generation | Monthly thermal generation (by plant) | Mayagüez - Gas | GWh | 1.3322 | 5.547 | 12.271 | 49.751 | 3.202 | 1.087 | 0.491 | 22.976 | 21.839 | 14.571 | 19.308 | 27.182 | 33.506 | 38.609 | 35.669 | 21.318 | 24.113 | 5.638 | 12.235 | 3.306 | 4.4587 | 15.8596 | 8.055 | 12.0989 | 16.6076 | 17.3528 | 30.1968 | 36.36 | 26.16 | 16.66 | 13.274 | 2.5464 | 2.1243 | 4.1326 | 27.2131 | 31.5159 | 16.2145 | 19.1134 | 21.394 | 38.2141 | 41.4716 | 36.4931 | 12.5807 | 5.9195 | 15.4342 | 12.3974 | 19.542 | 41.2282 | 40.0883 | 64.3674 | 47.6791 | 31.9134 | 23.8626 | 16.092 | 36.3508 | 57.5632 | 49.8893 | 42.9459 | 57.7883 | 67.2337 | 46.3662 | 35.1318 | 50.2952 | 48.2593 | 48.34 | 32.25 | 42.28 | 42.005 | 18.529 | 21.629 | 21.5727 | 5.5961 | 7.5985 | 5.301 | 5.207 | 1.8097 | 6.0711 | 11.2324 | 11.6061
Genera PR | Generation | Monthly thermal generation (by plant) | Palo Seco - Gas | GWh | 10.839 | 15.57 | 16.778 | 32.809 | 14.918 | 5.215 | 8.318 | 61.993 | 58.063 | 79.694 | 56.692 | 69.146 | 71.3071 | 69.118 | 36.5163 | 9.135 | 15.3043 | 6.775 | 2.974 | 1.892 | 4.815 | 7.687 | 5.744 | 9.367 | 6.4 | 6.375 | 12.329 | 13.49 | 5.41 | 5.09 | 4.891 | 1.178 | 0.875 | 1.061 | 6.272 | 1.857 | 3.304 | 4.8446 | 5.263 | 28.372 | 45.536 | 14.337 | 3.2355 | 5.5555 | 11.977 | 13.0243 | 11.383 | 27.661 | 6.846 | 8.478 | 11.392 | 11.119 | 18.706 | 6.644 | 6.443 | 6.298 | 8.965 | 11.545 | 8.579 | 14.959 | 8.139 | 4.874 | 10.97 | 12.607 | 13.1 | 3.671 | 5.719 | 6.876 | 3.873 | 9.523 | 10.951 | 3.219 | 3.559 | 6.139 | 3.882 | 1.972 | 5.175 | 3.882 | 2.476
Genera PR | Generation | Monthly thermal generation (by plant) | Costa Sur - Gas | GWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.482 | 0.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033 | 0.037 | 0.1822 | 0.85 | 0.12 | 0.06 | 0.393 | 7.8 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Genera PR | Generation | Monthly thermal generation (by plant) | Aguirre - Gas | GWh | 0 | 0 | 0.0974 | 0 | 0 | 0 | 0 | 0 | 2.5351 | 1.746 | 3.447 | 3.084 | 0 | 0 | 0 | 1.269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043 | 0 | 0.723 | 3.73 | 1.8 | 0.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.169 | 1.113 | 0 | 0.033 | 0 | 0.202 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Genera PR | Generation | Monthly thermal generation (by plant) | Yabucoa - Gas | GWh | 0.577 | 1.296 | 2.15 | 5.674 | 2.669 | 0.186 | 0.393 | 5.885 | 2.572 | 0.9447 | 1.88 | 1.824 | 1.675 | 1.67 | 1.163 | 1.968 | 2.511 | 0.554 | 1.757 | 0.072 | 1.041 | 0.76 | 0 | 0 | 0 | 0 | 0.03 | 0.01 | 0.46 | 1.77 | 2.3 | 0.41 | 0.37 | 0.36 | 2.17 | 2.11 | 0.72 | 0.12 | 1.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.213 | 3.694 | 2.015 | 3.3 | 1.899 | 3.07 | 0.912 | 1.553 | 1.085 | 0.957 | 1.845 | 3.336 | 1.081 | 0.601 | 2.615 | 2.291 | 1.32 | 0.26 | 0.49 | 1.498 | 1.003 | 2.496 | 3.222 | 1.252 | 1.867 | 1.773 | 2.477 | 1.019 | 3.405 | 2.791 | 1.533
Genera PR | Generation | Monthly thermal generation (by plant) | Daguao - Gas | GWh | 1.124 | 1.495 | 1.663 | 5.934 | 2.193 | 0.511 | 0.748 | 10.02 | 5.43 | 1.257 | 3.63 | 4.103 | 2.078 | 4.853 | 3.947 | 4.354 | 4.182 | 2.563 | 1.721 | 0.401 | 0.864 | 1.925 | 2.057 | 4.137 | 3.127 | 2.974 | 4.878 | 9.32 | 6.01 | 5.16 | 3.989 | 0.586 | 0.48 | 0.795 | 3.987 | 3.581 | 0.715 | 0.583 | 2.822 | 5.702 | 9.45 | 5.564 | 0.828 | 0.324 | 0.753 | 2.435 | 1.27 | 4.478 | 4.506 | 7.26 | 4.872 | 8.338 | 5.523 | 8.168 | 2.782 | 4.93 | 3.402 | 3.47 | 5.753 | 8.916 | 1.644 | 1.014 | 3.423 | 3.19 | 2.74 | 0.67 | 1.25 | 3.267 | 3.211 | 6.437 | 7.754 | 3.172 | 5.328 | 3.28 | 5.218 | 3.098 | 7.13 | 4.507 | 2.893
Genera PR | Generation | Monthly thermal generation (by plant) | Jobos - Gas | GWh | 0.324 | 0.7704 | 2.2495 | 6.2223 | 2.768 | 0.181 | 0.2523 | 5.864 | 3.712 | 1.389 | 2.308 | 4.784 | 2.77 | 2.7164 | 2.429 | 4.302 | 6.496 | 0.775 | 1.148 | 0.219 | 2.759 | 4.403 | 2.187 | 4.2 | 3.372 | 4.74 | 8.084 | 10.4 | 5.04 | 4.32 | 4.24 | 0.464 | 0.393 | 0.122 | 2.046 | 4.829 | 1.66 | 0.974 | 3.392 | 2.89 | 7.155 | 5.049 | 0.625 | 0.463 | 0.436 | 2.523 | 0.42 | 2.344 | 2.478 | 3.602 | 2.274 | 4.058 | 3.592 | 4.513 | 1.469 | 2.074 | 1.323 | 1.162 | 2.413 | 3.75 | 1.692 | 0.756 | 3.078 | 3.127 | 2.63 | 0.39 | 0.81 | 1.813 | 1.307 | 3.621 | 5.274 | 2.014 | 3.106 | 3.227 | 3.261 | 1.441 | 4.478 | 3.688 | 0.36
Genera PR | Generation | Monthly thermal generation (by plant) | Vega Baja - Gas | GWh | 1.877 | 3.16 | 2.144 | 1.103 | 0 | 0 | 0 | 0.014 | 2.21 | 1.159 | 1.788 | 1.51 | 0.805 | 0.994 | 0.67 | 2.228 | 3.019 | 1.115 | 1.115 | 0.657 | 0.965 | 0.534 | 0.992 | 2.299 | 1.135 | 0 | 1.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Plant decommissioning in progress for Storage Batteries installation project.
Genera PR | Generation | Monthly thermal generation (by plant) | Cambalache - Gas | GWh | 14.173 | 18.597 | 23.252 | 42.711 | 2.404 | 5.918 | 1.178 | 57.387 | 44.39 | 18.037 | 20.153 | 35.585 | 16.378 | 27.151 | 24.841 | 17.118 | 18.715 | 10.799 | 10.969 | 3.957 | 17.887 | 20.587 | 7.758 | 19.223 | 18.796 | 20.69 | 46.91 | 45.67 | 38.82 | 25.56 | 17.699 | 2.491 | 4.057 | 7.662 | 24.024 | 19.122 | 12.279 | 11.718 | 25.9 | 45.677 | 38.248 | 16.001 | 7.643 | 5.476 | 12.701 | 15.477 | 14.065 | 32.509 | 31.666 | 61.045 | 51.712 | 60.403 | 24.114 | 21.126 | 13.06 | 22.944 | 23.999 | 20.82 | 42.32 | 53.346 | 26.618 | 19.62 | 49.473 | 51.84 | 49.03 | 13.66 | 31.68 | 36.299 | 29.877 | 46.566 | 53.553 | 21.177 | 20.729 | 21.642 | 23.705 | 12.916 | 27.427 | 11.87 | 4.756
Genera PR | Generation | Monthly thermal generation (by plant) | Vieques - Diesel | GWh | 0 | 0.021 | 0 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017 | 0 | 0 | 0 | 0 | 0.005 | 0.001 | 0 | 0 | 0 | 6.15e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.026 | 0.012309 | 0.003 | 0 | 0.003 | 0.091 | 0 | 0.034 | 0 | 0.034 | 0.0015 | 0 | 0.0055 | 0.0715 | 0.0033 | 0.0826 | 0.056 | 0.104 | 0.12 | 0.0285 | 0.001 | 0.004 | 0.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Genera PR | Generation | Monthly thermal generation (by plant) | Culebra - Diesel | GWh | 0 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013 | 0 | 0 | 0 | 0.77592 | 0 | 0.005819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0076 | 0 | 0.045 | 0.084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0.192 | 0
Genera PR | Generation | Average heat rate (system) |  | BTU/kWh | 11382.5573 | 10910.7146 | 11114.4524 | 11399 | 11164 | 10966 | 11111.0932 | 11640.992 | 12038.1892 | 12104 | 11824 | 11472 | 11173.2147 | 11269.6791 | 10962.2617 | 11009.5364 | 11201.2142 | 11044.8828 | 10966 | 10854 | 11329 | 11302.773 | 11192.838 | 11163.6174 | 10660 | 10695 | 10830 | 10827.8 | 10832.66 | 11096.94 | 11239 | 11197 | 11250 | 10868 | 11376 | 11727 | 11390 | 10919 | 11239 | 11589 | 11708 | 11419 | 11338 | 11266 | 11072 | 10650 | 10978 | 10985 | 10960 | 11041.99 | 10929.1 | 10850.33 | 11101 | 11585 | 11147 | 10752 | 11488 | 11058 | 11122 | 11413 | 11506 | 11569 | 11698 | 11626 | 11474 | 11500 | 11183 | 13093.9546 | 12915.6546 | 12053.48 | 12812.6727 | 12838.1068 | 12955.99 | 10974.7491 | 10920.1648 | 10802.5117 | 9514.7496 | 10959.8918 | 10872.6802
Genera PR | Generation | Average heat rate (by plant) | San Juan - Steam | BTU/kWh | 12195 | 12457 | 12792 | 12205 | 11948 | 12220 | 12259.69 | 12082.1283 | 11954.3956 | 12133 | 12245 | 12418 | 15513.4395 | 12213.8577 | 12290.3526 | 12367.2726 | 12317.3594 | 12007.0811 | 12553 | 0 | 0 | 0 | 0 | 0 | 11331.7554 | 11215.1081 | 11560.2119 | 12490.56 | 11540.05 | 11397.09 | 11577 | 11684 | 11811 | 11466 | 11184.5352 | 11466.5296 | 11601 | 12212 | 11855 | 12409 | 12277 | 12111 | 12064 | 12181 | 12030 | 0 | 0 | 0 | 11524 | 11719 | 12017 | 12148 | 12304 | 12497 | 11917 | 12041 | 12522 | 13293 | 11951 | 12059 | 12153 | 11632 | 11593 | 11691 | 11828 | 12222 | 0 | 11369.63 | 10998.02 | 11261.76 | 10987.32 | 11117.36 | 11241.16 | 11429.77 | 10955.47 | 11437.19 | 10134.66 | 11331.82 | 11173.94
Genera PR | Generation | Average heat rate (by plant) | Palo Seco - Steam | BTU/kWh | 11864 | 12434 | 10963 | 11114 | 11129 | 11367 | 11787.8857 | 11314.0388 | 11505.9012 | 11304 | 11291 | 11437.3422 | 11279.5354 | 11530.2652 | 11492.8129 | 11729.7067 | 11433.5803 | 11663.4317 | 11577 | 0 | 11057 | 10918.393 | 10731.4504 | 10900.1374 | 10969.8623 | 11042.0352 | 11069.988 | 10986.34 | 10586.36 | 10948.44 | 11109 | 11413 | 11128 | 10859 | 10847.6534 | 10646 | 10675 | 10725 | 11236 | 11011 | 11546 | 10546 | 10741 | 11223 | 10957 | 10933 | 11154 | 11196 | 11382 | 11054 | 11323 | 10799 | 11468 | 10843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11977 | 10637 | 10561 | 10168 | 10542 | 10753 | 10302 | 10145 | 10292 | 10414 | 10321 | 10815 | 10783 | 10790 | 11457 | 11209 | 11298 | 11186
Genera PR | Generation | Average heat rate (by plant) | Costa Sur - Steam | BTU/kWh | 11915 | 12076 | 11973 | 12172 | 11903 | 11694 | 11721.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11544.8641 | 11594.7353 | 11925.9907 | 11632.0612 | 11509 | 12307 | 11866 | 11496.5189 | 11057.2721 | 11350.2812 | 11194.1028 | 11109.7369 | 11273.3804 | 11437.42 | 11273.77 | 11057.71 | 11711 | 11712 | 11471 | 11480 | 12295.5838 | 12217.9665 | 11486 | 11281 | 11756 | 11962 | 11833 | 11346 | 11549 | 11738 | 12128 | 11751 | 12037 | 12271 | 11828 | 14282 | 11658 | 11950 | 11969 | 11973 | 12034 | 12632 | 41871 | 12748 | 10800 | 11977 | 11639 | 11331 | 11836 | 11671 | 11921 | 12110 | 12118 | 11707.2 | 11583 | 11439 | 11338 | 11478.5 | 11256 | 11681.08 | 11528 | 11649 | 11493 | 11831 | 11337
Genera PR | Generation | Average heat rate (by plant) | Aguirre - Steam | BTU/kWh | 10805 | 10891 | 10955 | 11242 | 10531 | 10573 | 10712.6127 | 11141.6933 | 11142.5985 | 11107 | 11150 | 11720 | 10669.4696 | 10826.6704 | 11107.2904 | 11209.9347 | 12161.5601 | 11024.5379 | 11175 | 11116 | 11227 | 11488.639 | 11458.079 | 11263.9933 | 11299.4222 | 11356.8862 | 11187.9529 | 11234.68 | 11540.2 | 11307.57 | 11344 | 11362 | 11103 | 11277 | 11545.4915 | 11434.121 | 10990 | 10973 | 11470 | 11541 | 11526 | 11519 | 11166 | 11300 | 0 | 11423 | 11661 | 11658 | 11406 | 12057 | 11371 | 11337 | 11537 | 13561 | 12156 | 12319 | 12338 | 12462 | 11968 | 11703 | 11662 | 12113 | 12497 | 11628 | 12465 | 11799 | 0 | 14309.57 | 12860.96 | 0 | 0 | 0 | 13853.62 | 11611.82 | 12071.87 | 11505.27 | 11644.69 | 11431.03 | 11928.47
Genera PR | Generation | Average heat rate (by plant) | Ciclo Combinado San Juan | BTU/kWh | 9059 | 7994 | 8587 | 7224 | 8512 | 7894 | 7972.661 | 8919.0891 | 10774.3132 | 10766 | 9226 | 9266.4094 | 9301.7569 | 9373.4577 | 8443.8524 | 8304.917 | 8326.0516 | 8322.1178 | 8386 | 8311 | 8235 | 8121.4541 | 8238.5348 | 8334.2288 | 8191.3574 | 8158.9071 | 8278.9339 | 8160.27 | 8309.71 | 9315.02 | 9108 | 7983 | 9854 | 8044 | 8225.9748 | 11140.1547 | 10935 | 9418 | 9331 | 9903 | 10955 | 10928 | 11094 | 9658 | 9140 | 8227 | 8548 | 8227 | 8466 | 8120 | 8196 | 8172 | 8159 | 8923 | 8257 | 8378 | 9051 | 8527 | 9351 | 9253 | 10227 | 11105 | 11363 | 8666 | 8753 | 9103 | 8346 | 11700.8 | 11192.63 | 10890.01 | 10996.39 | 9547.085 | 9719.48 | 9149.83 | 8999.58 | 9231.39 | 9179.21 | 9565.94 | 10183.91
Genera PR | Generation | Average heat rate (by plant) | Ciclo Combinado - Aguirre | BTU/kWh | 12868 | 12897 | 13963 | 14114 | 13240 | 12709 | 13937.8444 | 14523.1194 | 14749.0943 | 15176 | 14278 | 13290 | 13182.9768 | 13505.8566 | 13902.8522 | 14666.1524 | 14728.7842 | 14758.0591 | 13418 | 15805 | 14112 | 13795.4703 | 15639.3751 | 15649.2021 | 13292.9268 | 14588.4705 | 14458.9364 | 13195.39 | 13600.81 | 15448.93 | 14663 | 15835 | 15535 | 14298 | 15139.438 | 13948.5852 | 14181 | 12073 | 12359 | 13441 | 12133 | 13225 | 16249 | 0 | 14956 | 14281 | 14963 | 15139 | 15083 | 14612 | 15246 | 14833.85 | 15155 | 15224 | 15336 | 14910 | 15202 | 14079 | 12107 | 11918 | 12693 | 14055 | 12201 | 12520 | 12074 | 13062 | 12533 | 14912.54 | 15387.28 | 15259.73 | 15046.7 | 15363.68 | 14829.99 | 14761.27 | 15108.34 | 15133.24 | 15274.97 | 15071.49 | 15035.28
Genera PR | Generation | Average heat rate (by plant) | Mayagüez - Gas | BTU/kWh | 9562 | 10511 | 10591 | 10439.5226 | 10284.7164 | 9627.5974 | 9289.0168 | 10962.5942 | 10808.1565 | 10801 | 10724 | 10239 | 9633.5417 | 10487.3858 | 9961.4197 | 9941.28 | 9977.5986 | 9860.5893 | 10649 | 10503 | 10603 | 10643.3214 | 10405.5902 | 10472.8015 | 10865.2546 | 10317.1207 | 10454.8583 | 10605.48 | 10971.07 | 9828.28 | 10510 | 10945 | 10333 | 10684 | 10670.2039 | 10747.3956 | 10541 | 10656 | 10439 | 10729 | 10774 | 10600 | 10617 | 10467 | 10514 | 10477 | 10738 | 10758 | 10861 | 10776 | 10873 | 10892 | 10965 | 10863 | 11123 | 10923 | 10974 | 11067 | 11160 | 10919 | 11080 | 10889 | 10960 | 10913 | 10908 | 10957 | 10866 | 10259 | 10062 | 10108 | 9895 | 9906 | 10910.97 | 10833.18 | 10729.94 | 11109.71 | 10984.5 | 10511.57 | 10767.3965
Genera PR | Generation | Average heat rate (by plant) | Palo Seco - Gas | BTU/kWh | 14856 | 14892 | 14871 | 15046.1627 | 15473.9708 | 14626.3162 | 15208.3705 | 12820.6064 | 15245.0949 | 12205 | 13175 | 12333 | 12042.1281 | 12439.1226 | 8616.3538 | 15133.2031 | 15042.4335 | 15581.086 | 15178 | 15430 | 15303 | 15561.7574 | 15288.0896 | 15266.4181 | 15341.987 | 15679.1182 | 15447.4085 | 15625.11 | 15931.68 | 15819.82 | 15838 | 16219 | 14904 | 15550 | 15817.1274 | 16053.0062 | 15742 | 11032 | 15931 | 12203 | 11454 | 11491 | 11301 | 11370 | 12485 | 11195 | 10935 | 0 | 16278 | 16079 | 16585 | 15734.96 | 15131 | 16114 | 15222 | 15081 | 16642 | 15607 | 15902 | 15879 | 16013 | 15868 | 15522 | 15608 | 15448 | 16135 | 15665 | 14604.46 | 15761.99 | 15443.84 | 15142.34 | 14990.27 | 15145.75 | 15030.23 | 14343.32 | 15139.96 | 15009.46 | 15011.19 | 15034.0123
Genera PR | Generation | Average heat rate (by plant) | Costa Sur - Gas | BTU/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18230 | 19980 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19267 | 18223 | 16243 | 15643 | 15965 | 26060.18 | 14079.78 | 11327.23 | 14709.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Genera PR | Generation | Average heat rate (by plant) | Aguirre - Gas | BTU/kWh | 0 | 0 | 16700 | 0 | 0 | 0 | 0 | 0 | 15353.9295 | 15173 | 14258 | 15398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15618.9184 | 0 | 15272.1893 | 0 | 15796.14 | 15804.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15384 | 16562 | 0 | 25559 | 0 | 15362 | 0 | 0 | 0 | 0 | 0 | 0 | 15137 | 17782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Genera PR | Generation | Average heat rate (by plant) | Yabucoa - Gas | BTU/kWh | 14354 | 15262 | 15011 | 14800.0468 | 14967.537 | 14761.1052 | 15225.6888 | 14762.8175 | 14884.375 | 14393 | 14351 | 14305 | 14639.0534 | 16113.058 | 14266.9066 | 17498.3978 | 0 | 15315.6948 | 15826 | 16300 | 16286 | 16113.6321 | 0 | 0 | 0 | 0 | 15327.3273 | 15965.97 | 16271.37 | 0 | 15950 | 16253 | 15978 | 15558.5919 | 15078.6638 | 16587.3523 | 15949 | 16943 | 14974 | 16417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14481 | 14234 | 15556 | 15777.61 | 15982 | 15657 | 16239 | 16122 | 16144 | 15829 | 15970 | 16292 | 16904 | 16046 | 15866 | 16082 | 16872 | 20566 | 15541 | 15233.63 | 16640.68 | 15765.06 | 15784.43 | 16712.25 | 15968.35 | 14986.78 | 16307.64 | 15854.17 | 15816.78 | 15813.47 | 15395.85
Genera PR | Generation | Average heat rate (by plant) | Daguao - Gas | BTU/kWh | 15480 | 15520 | 15829 | 15904.4756 | 16051.963 | 15696.2559 | 14421.9469 | 16182.7647 | 15784.0286 | 15831 | 15771 | 15671 | 15015.321 | 15806.855 | 15737.5876 | 15879.4571 | 0 | 15543.2283 | 15585 | 20273 | 15234 | 15808.7655 | 15426.424 | 15476.3429 | 15289.8087 | 15478.0948 | 15082.6975 | 15564.12 | 7006.22 | 15718.12 | 15516 | 16274 | 15958 | 15909.213 | 15457.5617 | 15936.9728 | 16088 | 15921 | 15542 | 15227 | 15268 | 15189 | 15584 | 15847 | 15533 | 15084 | 15359 | 15618 | 15263 | 15912.53 | 15515 | 15859.77 | 15826 | 15766 | 15690 | 15459 | 15239 | 15237 | 15399 | 15260 | 15201 | 15592 | 15141 | 15019 | 15521 | 14741 | 15263 | 15138.24 | 14783.15 | 15167.2 | 15239.17 | 15513.53 | 15550.34 | 15618.81 | 15952.11 | 16215.58 | 16951.19 | 17288.48 | 16086.499
Genera PR | Generation | Average heat rate (by plant) | Jobos - Gas | BTU/kWh | 15082 | 15010 | 15036 | 14842.7378 | 15430.2713 | 14287.7352 | 15720.0692 | 15365.8116 | 15342.7177 | 15331 | 14795 | 15327 | 14472.479 | 15621.7489 | 14677.9089 | 15477.7493 | 0 | 15013.0647 | 14681 | 15844 | 14886 | 14783.9577 | 14764.6128 | 14708.3731 | 14687.0186 | 14834.6912 | 14839.6296 | 14780.22 | 14960.69 | 15069.82 | 14866 | 14966 | 15343 | 15831.2903 | 15120.5487 | 14676.9184 | 15220 | 15274 | 15284 | 15633 | 15588 | 15231 | 15674 | 15857 | 15513 | 15155 | 15489 | 15167 | 15263 | 15303 | 15330 | 15116.76 | 15178 | 14868 | 15443 | 14958 | 15277 | 15016 | 15021 | 15199 | 15159 | 14334 | 15054 | 15579 | 14662 | 17398 | 14526 | 13912.15 | 14316.54 | 13583.6 | 13655.66 | 13322.3 | 13854.66 | 14222.77 | 13292 | 13912.27 | 15302.75 | 13981.29 | 13950.82
Genera PR | Generation | Average heat rate (by plant) | Vega Baja - Gas | BTU/kWh | 15549 | 15695 | 17746 | 13020.2696 | 0 | 0 | 0 | 33727.5847 | 16878.1868 | 16231 | 15774 | 17221 | 18219.9889 | 17102.3035 | 15885.2913 | 13163.935 | 0 | 0 | 14175 | 0 | 15921 | 16062.7294 | 15901.5871 | 15873.0327 | 16371.247 | 0 | 16212.9217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Plant decommissioning in progress for Storage Batteries installation project.
Genera PR | Generation | Average heat rate (by plant) | Cambalache - Gas | BTU/kWh | 12794 | 12416 | 12622 | 12098 | 14613 | 12094 | 14144.0492 | 11961.8392 | 12279.3426 | 12263 | 11555 | 11806 | 11926.9017 | 12111.1533 | 12221.5829 | 12265.1054 | 12293.037 | 13412.0296 | 13009 | 14262 | 13340 | 13380.8414 | 13763.2948 | 13436.1426 | 12812.6234 | 12703.8823 | 12496.6022 | 12190.32 | 12924.23 | 13050.52 | 12711 | 14830 | 13699 | 13304.5767 | 12526.8579 | 12717.4024 | 13191 | 13207 | 12643 | 12488 | 12618 | 12896 | 13927 | 14185 | 13417 | 13131 | 13439 | 12562 | 12698 | 12232 | 12661 | 12605.6 | 12471 | 12575 | 13466 | 13019 | 12950 | 13061 | 12761 | 12521 | 12929 | 13100 | 12471 | 12439 | 12466 | 13475 | 12944 | 12692.41 | 12845.03 | 12775.76 | 12440.39 | 12947.2 | 12326.56 | 12502.39 | 12474.02 | 12884.62 | 12404.45 | 12722.312 | 13005.86
Genera PR | Generation | Average heat rate (by plant) | Vieques - Diesel | BTU/kWh | 0 | 9380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Genera PR | Generation | Average heat rate (by plant) | Culebra - Diesel | BTU/kWh | 0 | 8092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Genera PR | Generation | Plant availability (by plant) | San Juan - Steam | Percentage | 18.87% | 25.57% | 26.95% | 34.42% | 19.98% | 27.87% | 45.12% | 31.58% | 35.07% | 40.54% | 34.65% | 42.57% | 31.28% | 32.16% | 31.95% | 42.6% | 23.79% | 33.91% | 31.58% | 28.62% | 22.96% | 21.35% | 21.36% | 23.38% | 30.86% | 27.3% | 28.42% | 27% | 53% | 62.8% | 65.32% | 62.28% | 46.28% | 51.27% | 40% | 47.1% | 59.3% | 37.1% | 48.9% | 54% | 66.5% | 58.1% | 40.06% | 47.49% | 47.42% | 0% | 0% | 0% | 17.1% | 33.3% | 30.6% | 32.9% | 36.4% | 53.1% | 59.9% | 65.68% | 46.46% | 40.59% | 27.59% | 23.61% | 30.79% | 50.2% | 93.82% | 88.96% | 46% | 46% | 0% | 14.85% | 100% | 100% | 44% | 50% | 50% | 41.93% | 49.09% | 40.32% | 40.77% | 41% | 35.24%
Genera PR | Generation | Plant availability (by plant) | Palo Seco - Steam | Percentage | 46.29% | 12.53% | 30.55% | 30.46% | 47.06% | 36.96% | 45.32% | 55.43% | 69.05% | 65.75% | 68.11% | 51.79% | 66.53% | 51.24% | 46.35% | 36.62% | 24.48% | 12.19% | 9.38% | 0% | 25.61% | 24.93% | 31.8% | 30.21% | 28.72% | 44.08% | 44.92% | 51% | 53% | 62% | 50.09% | 67.47% | 46.06% | 58.27% | 91.04% | 95.77% | 95.4% | 78.8% | 31.7% | 32.36% | 47.6% | 9.7% | 85.62% | 58.06% | 54.02% | 87.57% | 85.8% | 72.18% | 60.8% | 70.8% | 36.76% | 37.99% | 41.1% | 28.4% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 6.9% | 42.4% | 46.18% | 45% | 43% | 39% | 45% | 45.91% | 41.44% | 35.5% | 45.06% | 27.78% | 28.42% | 27.19% | 28.08% | 56.46% | 51.63% | 71.88%
Genera PR | Generation | Plant availability (by plant) | Costa Sur - Steam | Percentage | 100% | 80.58% | 50.74% | 70.9% | 86.22% | 97.15% | 99.33% | 19.62% | 0% | 0% | 0% | 0% | 0% | 0% | 44.89% | 48.47% | 31.99% | 32.99% | 33.8% | 37.9% | 59.52% | 51.48% | 51.67% | 50.34% | 87.08% | 97.11% | 80.24% | 20% | 41% | 48% | 43.15% | 76.41% | 73.66% | 74.4% | 49.03% | 71.03% | 73.7% | 73.8% | 71.2% | 57.5% | 38.8% | 73.1% | 72.58% | 64.85% | 64.66% | 75.6% | 69.9% | 51.34% | 62.6% | 28.3% | 50% | 36.25% | 40.9% | 44.7% | 34.29% | 6.5% | 2.51% | 17.27% | 38.6% | 54.84% | 73.1% | 73.8% | 68.48% | 79.93% | 71% | 74% | 64% | 95% | 97.5% | 50% | 41% | 81.17% | 70.54% | 64.04% | 90.12% | 91.5% | 84.34% | 91.12% | 92.15%
Genera PR | Generation | Plant availability (by plant) | Aguirre - Steam | Percentage | 37.99% | 50% | 47.65% | 27.99% | 50% | 50% | 49.93% | 32.06% | 32.83% | 33.33% | 41.94% | 41.2% | 96.04% | 91.67% | 73.99% | 75% | 48.86% | 82.22% | 87.84% | 94.69% | 43.75% | 41.47% | 56.53% | 65.39% | 39.86% | 39.11% | 35.69% | 61% | 50% | 72% | 67.34% | 62.5% | 64.21% | 37.16% | 19.72% | 27.89% | 38.9% | 36.6% | 28.5% | 19.44% | 21.4% | 13.5% | 38.91% | 13.78% | 0% | 29.03% | 37.3% | 10.35% | 36% | 30% | 34.21% | 33.47% | 38% | 29.4% | 27.6% | 29.2% | 60.56% | 38.71% | 31.5% | 60.75% | 71% | 51.88% | 41.87% | 20% | 19% | 29% | 0% | 19.7% | 24.18% | 0% | 0% | 0% | 11.12% | 34.78% | 28.81% | 37.4% | 35.81% | 27.61% | 17.78%
Genera PR | Generation | Plant availability (by plant) | Ciclo Combinado San Juan | Percentage | 75.62% | 99.46% | 100% | 79.03% | 57.73% | 50% | 48.05% | 65.12% | 87.07% | 34.01% | 42.5% | 95.03% | 92.01% | 95.9% | 94.29% | 99.44% | 89.99% | 71.67% | 71.91% | 93.01% | 59.15% | 48.72% | 48.33% | 65.93% | 97.78% | 90.59% | 98.66% | 97% | 92% | 85.2% | 84.5% | 61.2% | 45.2% | 50% | 44.5% | 36.4% | 36% | 76.4% | 85.14% | 68.7% | 70.6% | 65.8% | 18.28% | 53.6% | 91.2% | 97.8% | 96.4% | 98.5% | 97.6% | 98.9% | 95.3% | 98.5% | 94.4% | 86.9% | 69.99% | 96.9% | 74.2% | 95.19% | 40.4% | 46.4% | 62.3% | 68.8% | 50.7% | 41.43% | 35% | 40% | 49% | 42% | 43% | 48% | 45% | 57.62% | 84.04% | 75.3% | 63.23% | 87.07% | 75.7% | 65.66% | 29.16%
Genera PR | Generation | Plant availability (by plant) | Ciclo Combinado - Aguirre | Percentage | 70.77% | 50.92% | 58.27% | 40.95% | 54.85% | 59.98% | 62.32% | 48.9% | 41.13% | 44.74% | 45.01% | 60.33% | 53.39% | 40.81% | 41.53% | 61.73% | 46.54% | 49.48% | 50.78% | 50.78% | 47.95% | 52.5% | 35.82% | 31.15% | 40.86% | 31.16% | 21.2% | 42% | 32% | 25% | 29.44% | 31.19% | 33.25% | 37.17% | 25.95% | 38.83% | 48.6% | 42.6% | 43.5% | 27.67% | 28.7% | 34.1% | 15.37% | 0% | 9.79% | 14.1% | 19.5% | 18.58% | 25.6% | 24.5% | 26.08% | 20.08% | 22.4% | 25.3% | 26.5% | 20.09% | 45.07% | 21.22% | 31.4% | 34.96% | 36.3% | 36.1% | 41.14% | 32.62% | 41% | 47% | 40% | 28.1% | 51.01% | 24.05% | 18.9% | 42.72% | 50.36% | 47.12% | 40.07% | 42.8% | 37.5% | 37.79% | 38.91%
Genera PR | Generation | Plant availability (by plant) | Mayagüez - Gas | Percentage | 61.26% | 78.39% | 76.58% | 49.15% | 72.99% | 86.69% | 86.96% | 42.09% | 28.95% | 38.2% | 34.79% | 20.1% | 66.92% | 66.46% | 65% | 72.9% | 73.77% | 85.43% | 52.4% | 52.37% | 72.52% | 51.36% | 65.02% | 61.36% | 45.03% | 42.09% | 27.12% | 53% | 35% | 49% | 51.9% | 49.57% | 70.8% | 71.38% | 53.2% | 48% | 61.5% | 59.7% | 44% | 69.2% | 64.6% | 83.6% | 73.4% | 86.28% | 85.3% | 86.1% | 85.5% | 89.2% | 79.5% | 84.7% | 93.31% | 95% | 94.1% | 94.9% | 91.26% | 90.8% | 91.2% | 91.06% | 70.6% | 75.18% | 75.3% | 69.5% | 64% | 64.9% | 66% | 67% | 67% | 75% | 33.75% | 35.67% | 47.1% | 50% | 43.06% | 26.06% | 25.37% | 26.01% | 24.72% | 26.06% | 25.82%
Genera PR | Generation | Plant availability (by plant) | Palo Seco - Gas | Percentage | 64.03% | 62.78% | 65.85% | 63.46% | 64.91% | 53.21% | 49.44% | 41.93% | 18.17% | 35.04% | 42.31% | 28.83% | 30.74% | 30.24% | 30.94% | 32.37% | 31.8% | 32.49% | 33.12% | 33.12% | 27.62% | 28.5% | 33.44% | 33.4% | 32.77% | 32.14% | 31.39% | 30% | 19% | 24% | 32.1% | 32.44% | 31.1% | 32.87% | 32.4% | 33% | 32.9% | 31.7% | 32.7% | 31% | 17.3% | 25.9% | 33.3% | 33.19% | 31.9% | 28.22% | 32.6% | 32.1% | 63.5% | 51.7% | 54% | 40.6% | 46.3% | 42.3% | 43.5% | 49.8% | 66.5% | 74.9% | 55.5% | 86.2% | 95.9% | 96.1% | 96.9% | 88.6% | 95% | 97% | 96% | 88.7% | 61.1% | 88% | 57.6% | 33% | 33.33% | 55.91% | 33.33% | 33.2% | 33.33% | 32.34% | 33.33%
Genera PR | Generation | Plant availability (by plant) | Costa Sur - Gas | Percentage | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 7.5% | 6.4% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.1% | 0.2% | 0.6% | 2.7% | 0.4% | 0.2% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Genera PR | Generation | Plant availability (by plant) | Aguirre - Gas | Percentage | 0% | 0% | 0.3117% | 0% | 0% | 0% | 0% | 0% | 29.81% | 50% | 50% | 44.22% | 0% | 0% | 0% | 36.67% | 10.89% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.389% | 2.957% | 23.15% | 25% | 36% | 26% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 9.4% | 24.1% | 0% | 0% | 0% | 12.7% | 0% | 0% | 0% | 0% | 0% | 0% | 0.35% | 0.022% | 0.045% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Genera PR | Generation | Plant availability (by plant) | Yabucoa - Gas | Percentage | 49.69% | 49.17% | 48.95% | 46.89% | 48.6% | 49.92% | 49.78% | 45.24% | 48.6% | 49.8% | 49.27% | 50.19% | 49.9% | 49.03% | 50% | 48.04% | 50.78% | 0% | 99.04% | 99.04% | 49.73% | 11.17% | 0% | 0% | 0% | 0% | 0.09601% | 0% | 11% | 99% | 42% | 49.77% | 49.7% | 49.81% | 48.7% | 48.8% | 49.6% | 49.9% | 49.2% | 29.2% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 11.6% | 49.4% | 48.32% | 46.5% | 48% | 33.4% | 49.1% | 48.4% | 48.8% | 49.03% | 48% | 46.6% | 48.9% | 49.4% | 47.4% | 39.2% | 37% | 50% | 50% | 51.6% | 50% | 50% | 50% | 50% | 50% | 100% | 100% | 100% | 100% | 100% | 100%
Genera PR | Generation | Plant availability (by plant) | Daguao - Gas | Percentage | 49.41% | 44.42% | 49.27% | 48.1% | 96.53% | 99.51% | 99.4% | 82.75% | 84.87% | 99.18% | 97% | 96.87% | 98.33% | 96.31% | 96.97% | 96.55% | 97.46% | 98.34% | 98.79% | 98.79% | 59.15% | 84.99% | 98.68% | 97.51% | 98.26% | 98.29% | 98.47% | 95% | 77% | 97% | 98% | 86.82% | 99.7% | 99.52% | 66.1% | 91% | 81.4% | 99.6% | 98.5% | 97.7% | 65.8% | 98.1% | 99.8% | 99.89% | 99.8% | 99.32% | 99.6% | 97.5% | 98% | 96.5% | 97.5% | 94.7% | 96.2% | 95.8% | 98.8% | 98.1% | 99% | 98.87% | 97.8% | 96.8% | 99.3% | 49.5% | 48.7% | 10.5% | 49% | 100% | 99% | 100% | 100% | 100% | 99.3% | 100% | 100% | 100% | 100% | 100% | 94.29% | 84.44% | 90.17%
Genera PR | Generation | Plant availability (by plant) | Jobos - Gas | Percentage | 43.85% | 46.69% | 49.4% | 48.91% | 48.71% | 49.9% | 49.8% | 45.98% | 47.68% | 49.2% | 46.66% | 84.4% | 73.12% | 73.01% | 73.97% | 89.3% | 93.77% | 99.79% | 95.33% | 95.33% | 95.39% | 62.48% | 72.12% | 99.26% | 99.33% | 98.3% | 80.91% | 80% | 82% | 93% | 92.7% | 62.83% | 96.6% | 74.45% | 99.5% | 98.2% | 97.7% | 99.7% | 95.5% | 89.3% | 65% | 93.8% | 90.6% | 84.01% | 96.3% | 96.78% | 50.3% | 49.4% | 49.2% | 48.2% | 49.28% | 48.8% | 48.9% | 48.8% | 49.7% | 49.5% | 47.4% | 49.75% | 49.4% | 49.1% | 49.5% | 49.7% | 49.2% | 49.1% | 49% | 50% | 50% | 50% | 47.6% | 50% | 50% | 50% | 50% | 100% | 100% | 100% | 99.38% | 100% | 8.199%
Genera PR | Generation | Plant availability (by plant) | Vega Baja - Gas | Percentage | 49.05% | 47.55% | 48.06% | 28.44% | 29.84% | 0% | 0% | 0.2464% | 47.29% | 49.61% | 49.04% | 48.78% | 41.06% | 26.57% | 14.38% | 49.31% | 48.37% | 42.09% | 43.76% | 43.76% | 50% | 12.66% | 49.46% | 48.55% | 48.82% | 0% | 70.47% | 70% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Plant decommissioning in progress for Storage Batteries installation project.
Genera PR | Generation | Plant availability (by plant) | Cambalache - Gas | Percentage | 100% | 100% | 99.46% | 97.43% | 100% | 77.71% | 86.69% | 99.26% | 86.21% | 97.72% | 99.93% | 99.26% | 75% | 96.44% | 100% | 98.33% | 50.01% | 55.14% | 100% | 100% | 100% | 98.12% | 83.82% | 87.43% | 99.79% | 73.05% | 79.1% | 83% | 100% | 99% | 100% | 100% | 100% | 100% | 80.63% | 50% | 71.2% | 96.2% | 91% | 98.89% | 99.1% | 95.7% | 100% | 96.91% | 86.83% | 86.02% | 78.1% | 99.66% | 96% | 100% | 92.2% | 92.08% | 48% | 49.9% | 68.5% | 98% | 100% | 98.45% | 99.2% | 99.87% | 99.6% | 100% | 99.4% | 99.65% | 99% | 73% | 100% | 99.4% | 99% | 98% | 99.49% | 74.11% | 50% | 50.46% | 50.86% | 100% | 50.2% | 50.12% | 50.86%
Genera PR | Generation | Plant availability (by plant) | Vieques - Diesel | Percentage | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 57% | 57% | 57% | 100% | 42.86% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 66% | 27.5% | 50% | 50% | 42.86% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 100% | 85.7% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Genera PR | Generation | Plant availability (by plant) | Culebra - Diesel | Percentage | 0% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 66.7% | 100% | 66.7% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 85.7% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
PREPA | Generation | Plant availability (by plant) | Hydro | Percentage | 21.27% | 18.13% | 21.49% | 21.81% | 26.5% | 27.47% | 25.71% | 22.37% | 9.594% | 18.4% | 19.59% | 25.86% | 25.61% | 25.36% | 25.36% | 26.26% | 31.98% | 31.98% | 31.05% | 31.05% | 31.25% | 31.3% | 29.22% | 30.48% | 32.7% | 32.7% | 32.7% | 31% | 28% | 23% | 24.05% | 28.38% | 31.27% | 34.91% | 32.7% | 32.7% | 32.7% | 27.2% | 32.7% | 29.94% | 50% | 26.1% | 28.8% | 27.13% | 26.5% | 25.13% | 28.2% | 30.39% | 30.4% | 23.2% | 23.19% | 34.91% | 34.9% | 36% | 31% | 32% | 31.98% | 31.98% | 32.5% | 31.98% | 32% | 30.6% | 30.58% | 30.58% | 31% | 26% | 18% | 23.3% | 26.6% | 26.6% | 26.6% | 26.6% | 31.6% | 31.6% | 31.6% | 28.2% | 28.2% | 28.2% | 21.6%
Genera PR | Generation | Forced outages (by plant) | San Juan - Steam | Percentage | 10.86% | 4.163% | 2.779% | 6.16% | 22.28% | 13.87% | 0.5013% | 16.89% | 11.95% | 9.1% | 27.96% | 15.33% | 22.97% | 26.37% | 25.36% | 14.23% | 16.47% | 18.91% | 3.49% | 0.09% | 0.54% | 0% | 0% | 1.177% | 9.294% | 14.4% | 13.88% | 29% | 41% | 0% | 34.68% | 37.72% | 53.72% | 38.44% | 40% | 47.09% | 40.74% | 40.05% | 47.54% | 45.97% | 33.33% | 41.3% | 35.39% | 44.09% | 40.87% | 66.67% | 33.33% | 33.33% | 33.33% | 33.33% | 35.93% | 33.33% | 33.69% | 41.39% | 36.11% | 33.42% | 10.25% | 26.08% | 35.46% | 34.5% | 34.86% | 29.53% | 3.41% | 0.37% | 32% | 25.01% | 0% | 0% | 0% | 0% | 3.09% | 0% | 0% | 2% | 0.9073% | 6.733% | 0% | 0% | 0%
Genera PR | Generation | Forced outages (by plant) | Palo Seco - Steam | Percentage | 22.84% | 80.81% | 42.4% | 41.78% | 9.04% | 27.5% | 8.536% | 2.134% | 7.463% | 3.59% | 4.12% | 3.43% | 0% | 3.26% | 28.82% | 16.44% | 21.89% | 38.78% | 16.44% | 0% | 19.55% | 17.96% | 16.44% | 16.44% | 16.85% | 36.21% | 36.83% | 31% | 36% | 20% | 32.28% | 1.08% | 3.05% | 6.38% | 5.69% | 0% | 0% | 0.3% | 1.2% | 49% | 50% | 47.7% | 2.08% | 3.36% | 6.47% | 0% | 6.74% | 3.02% | 24.72% | 14.8% | 54.03% | 54.4% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 60.2% | 54.44% | 50% | 51% | 53% | 58% | 50.4% | 50.42% | 51.4% | 50.97% | 50% | 62.44% | 55% | 54.82% | 47.12% | 13.22% | 18.66% | 1.815%
Genera PR | Generation | Forced outages (by plant) | Costa Sur - Steam | Percentage | 0% | 11.76% | 47.45% | 0.21% | 10.48% | 0% | 0.5376% | 80.38% | 100% | 100% | 100% | 100% | 100% | 100% | 55.11% | 51.53% | 52.76% | 0% | 52.22% | 44.62% | 16.37% | 3.36% | 0% | 0.5376% | 1.736% | 1.21% | 14.65% | 78% | 59% | 51% | 56.85% | 13.58% | 0.74% | 0% | 32.29% | 7% | 1.1% | 0% | 0.1% | 18.4% | 22.38% | 0% | 0% | 0% | 11.31% | 0% | 0% | 7.73% | 4.31% | 9.5% | 0% | 6.39% | 0% | 0% | 0% | 0% | 0% | 21.43% | 0% | 18.82% | 9.38% | 13% | 15.66% | 0% | 6% | 0% | 10% | 4.81% | 0.53% | 0% | 1.96% | 5.16% | 1.37% | 8% | 6.549% | 4.499% | 4.926% | 4.788% | 6.65%
Genera PR | Generation | Forced outages (by plant) | Aguirre - Steam | Percentage | 50% | 50% | 50.2% | 51.11% | 50% | 50% | 0% | 4.099% | 0% | 50% | 52.15% | 20.09% | 0% | 0% | 5.98% | 19.44% | 5.44% | 3.54% | 0.87% | 0% | 0% | 0.7392% | 0% | 0.4704% | 2.917% | 10.89% | 2.352% | 7% | 27% | 11% | 10.35% | 9.54% | 0.15% | 8.87% | 21.46% | 12.7% | 0% | 0% | 5.2% | 20.8% | 70.9% | 81.9% | 50% | 100% | 50% | 50% | 54.03% | 81.59% | 57.22% | 61.2% | 53.82% | 54.17% | 50% | 58.2% | 60.4% | 70.83% | 26.65% | 49.33% | 56.11% | 18.82% | 5.63% | 22.72% | 38.37% | 70.42% | 41% | 50% | 0% | 24.22% | 25.82% | 0% | 0% | 100% | 84.86% | 65.22% | 62.98% | 56.39% | 64.19% | 61.35% | 66.36%
Genera PR | Generation | Forced outages (by plant) | Ciclo Combinado San Juan | Percentage | 19.1% | 0.5376% | 0% | 20.97% | 0.54% | 0% | 1.882% | 5.108% | 3.305% | 15.3% | 29.53% | 16.18% | 4.38% | 4.1% | 1.28% | 0.56% | 0.07% | 0.76% | 1.01% | 0.2% | 0.67% | 0% | 0% | 27.55% | 0.9722% | 0% | 0.2016% | 3% | 8% | 0% | 15.49% | 12.32% | 2.38% | 0% | 4.17% | 13.64% | 14.04% | 17.7% | 14.19% | 31.31% | 29.37% | 27.27% | 27.32% | 37.13% | 8.55% | 2.2% | 3.59% | 0.32% | 0% | 1.06% | 4.69% | 1.48% | 5.6% | 12.15% | 0% | 0.75% | 15.53% | 5.93% | 59.56% | 50.09% | 37.66% | 28.2% | 49.32% | 51.23% | 1% | 0.9% | 1.56% | 4.25% | 7.13% | 1.79% | 0.8% | 12.49% | 0.31% | 6.347% | 56.81% | 14.48% | 7.255% | 19.02% | 46.43%
Genera PR | Generation | Forced outages (by plant) | Ciclo Combinado - Aguirre | Percentage | 1.759% | 8.515% | 2.417% | 12.45% | 1.99% | 0.28% | 3.041% | 10.95% | 20.01% | 17.43% | 17.47% | 12.75% | 6.2% | 14.49% | 22.15% | 2.59% | 18.66% | 8.89% | 13.53% | 13.53% | 15.58% | 4.767% | 36.13% | 44.47% | 37.99% | 40.11% | 42.1% | 16% | 22% | 35% | 33.12% | 41.6% | 33.23% | 26.46% | 36.6% | 21.36% | 10.8% | 8.9% | 9.7% | 23.8% | 15.9% | 17.1% | 42.24% | 58.45% | 44.9% | 42.71% | 67.31% | 59.6% | 33.7% | 33.2% | 33.2% | 42.36% | 37.4% | 33.5% | 33.1% | 33.11% | 9.05% | 34.4% | 22.63% | 19.19% | 16.5% | 14.2% | 11.62% | 31.63% | 17% | 2.1% | 12.3% | 59.34% | 9.8% | 45.18% | 41.98% | 22.82% | 16.5% | 17% | 18.38% | 15.65% | 20.94% | 17.94% | 18.04%
Genera PR | Generation | Forced outages (by plant) | Mayagüez - Gas | Percentage | 0% | 0% | 0% | 0% | 12.03% | 0% | 0% | 25% | 50% | 0% | 47.92% | 49.09% | 0% | 0% | 0% | 0% | 0% | 0% | 37.5% | 37.5% | 25% | 31.72% | 6.944% | 19.22% | 37.78% | 44.49% | 49.43% | 45% | 38% | 38% | 37.5% | 37.5% | 27.2% | 25.3% | 25.2% | 27.4% | 25% | 25% | 38.7% | 24.9% | 12.5% | 12.5% | 12.5% | 13.04% | 12.9% | 13% | 12.5% | 6.9% | 14.6% | 8.2% | 0.13% | 0% | 0.82% | 0.8% | 1.55% | 1.65% | 1.7% | 2.69% | 14.9% | 12.7% | 12.5% | 23.2% | 26.51% | 26.7% | 25% | 25% | 26.35% | 0% | 4.1% | 25% | 47.1% | 50% | 50% | 40% | 69.15% | 73.99% | 75.28% | 73.94% | 74.18%
Genera PR | Generation | Forced outages (by plant) | Palo Seco - Gas | Percentage | 35.56% | 36.02% | 33.33% | 33.33% | 33.33% | 46.39% | 50% | 55.53% | 81.61% | 64.36% | 54.81% | 68.08% | 68.31% | 67.03% | 66.87% | 66.67% | 66.67% | 66.67% | 66.67% | 66.67% | 72.27% | 64.92% | 57.89% | 65.68% | 66.67% | 67.2% | 67.38% | 69% | 75% | 76% | 67.47% | 67.47% | 68.8% | 67% | 66.8% | 66.8% | 66.7% | 68.2% | 66.7% | 66.7% | 67.7% | 73.7% | 66.7% | 66.67% | 67.9% | 66% | 67.1% | 66.9% | 0.37% | 10.7% | 39.07% | 22.2% | 40.9% | 56.4% | 55.6% | 49.06% | 29.8% | 12.28% | 41% | 7.53% | 0.74% | 1.79% | 0% | 0% | 0% | 1% | 1% | 11.3% | 45.2% | 33.17% | 38.9% | 66.67% | 66.67% | 44.09% | 66.67% | 66.81% | 66.67% | 67.66% | 66.67%
Genera PR | Generation | Forced outages (by plant) | Costa Sur - Gas | Percentage | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 92.1% | 93.5% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.87% | 99.7% | 99.31% | 96.79% | 99.6% | 99.1% | 98.55% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Genera PR | Generation | Forced outages (by plant) | Aguirre - Gas | Percentage | 100% | 100% | 99.6% | 100% | 100% | 100% | 100% | 100% | 70.19% | 50% | 50% | 55.78% | 100% | 100% | 100% | 63.33% | 89.11% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 98.61% | 97.04% | 76.81% | 74% | 57% | 74% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 90.1% | 75.3% | 100% | 99.9% | 100% | 87.3% | 100% | 100% | 100% | 100% | 100% | 100% | 99.6% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Genera PR | Generation | Forced outages (by plant) | Yabucoa - Gas | Percentage | 50% | 50% | 49.87% | 50% | 50% | 50% | 50% | 51.61% | 50% | 49.73% | 49.79% | 49.33% | 49.65% | 50% | 50% | 50% | 48.12% | 50% | 0% | 0% | 50% | 88.37% | 100% | 0% | 100% | 100% | 99.87% | 100% | 87% | 0% | 56.72% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 70.3% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 50% | 50% | 50% | 50% | 50% | 63.3% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.3% | 11% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Genera PR | Generation | Forced outages (by plant) | Daguao - Gas | Percentage | 50% | 50% | 49.8% | 41.67% | 0% | 0% | 0% | 8.065% | 10.34% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 40.32% | 13.44% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 12.9% | 0% | 0% | 31.7% | 6.9% | 18.3% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 50% | 50% | 88.3% | 50% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 5.71% | 15.56% | 9.835%
Genera PR | Generation | Forced outages (by plant) | Jobos - Gas | Percentage | 56.11% | 53.23% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 52.22% | 12.9% | 25.83% | 25% | 25% | 7.43% | 3.7% | 0% | 4.57% | 4.57% | 4.57% | 36.69% | 27.71% | 0.336% | 0.3472% | 1.008% | 17.74% | 18% | 1% | 7% | 6.45% | 37.1% | 3.3% | 25.5% | 0% | 0% | 1.7% | 0% | 2.8% | 8.3% | 8% | 3.8% | 9.1% | 15.86% | 3.5% | 3% | 49.5% | 50% | 50% | 50.8% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 0% | 48.4% | 50% | 50% | 50% | 50% | 50% | 50% | 0% | 0% | 0% | 0.6183% | 0% | 91.8%
Genera PR | Generation | Forced outages (by plant) | Vega Baja - Gas | Percentage | 50% | 50.81% | 50% | 70.83% | 70.16% | 100% | 100% | 99.66% | 51.72% | 50% | 50% | 50% | 58.13% | 72.38% | 85.28% | 50.14% | 50.13% | 57.78% | 55.98% | 55.98% | 50% | 86.96% | 50% | 50% | 50% | 100% | 28.56% | 30% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 96.8% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Plant decommissioning in progress for Storage Batteries installation project.
Genera PR | Generation | Forced outages (by plant) | Cambalache - Gas | Percentage | 0.5556% | 0% | 0% | 2.22% | 0% | 0% | 0% | 0.7392% | 4.454% | 0% | 0.07% | 0.4% | 1.11% | 0.2% | 0% | 1.67% | 0% | 0.69% | 0% | 0% | 4.17% | 0% | 15.56% | 12.57% | 0.2083% | 0.0672% | 0% | 1% | 0% | 1% | 0% | 0% | 0% | 0% | 0% | 0% | 3.1% | 3.8% | 3.4% | 1.11% | 0.4% | 0% | 0% | 3.09% | 0% | 0% | 1.39% | 0.34% | 0% | 0% | 1.61% | 0% | 2.9% | 0.1% | 5.78% | 2.02% | 0% | 1.21% | 0.69% | 0.13% | 0% | 0% | 0% | 0.35% | 1.3% | 10.6% | 0.36% | 0.6% | 0.92% | 0.51% | 0.69% | 13.61% | 50% | 50% | 49.14% | 49.14% | 49.33% | 49.88% | 49.14%
Genera PR | Generation | Forced outages (by plant) | Vieques - Diesel | Percentage | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 43% | 43% | 43% | 0% | 42.86% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 34% | 50% | 50% | 50% | 42.86% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Genera PR | Generation | Forced outages (by plant) | Culebra - Diesel | Percentage | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 33.3% | 0% | 33.3% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
PREPA | Generation | Forced outages (by plant) | Hydro | Percentage | 45.01% | 51.76% | 48.4% | 48.09% | 43.39% | 42.42% | 40.58% | 46.13% | 60.3% | 51.49% | 50.31% | 44.03% | 44.29% | 44.53% | 44.53% | 38% | 42.97% | 37.92% | 38.85% | 38.85% | 38.65% | 43.65% | 40.67% | 40.38% | 37.19% | 37.19% | 37.19% | 39% | 42% | 47% | 42.24% | 41.52% | 43.68% | 40.03% | 62.2% | 37.19% | 62.2% | 42.7% | 37.2% | 39.96% | 42.4% | 42.3% | 37.31% | 42.74% | 43.4% | 40.26% | 66.73% | 64.54% | 37.5% | 70.4% | 70.36% | 58.64% | 63.7% | 61.8% | 60% | 68.02% | 68.02% | 68.02% | 69.07% | 68.02% | 68% | 68% | 69.41% | 69.41% | 69% | 75% | 82% | 8.3% | 8.3% | 5% | 10.8% | 10% | 8.5% | 12.5% | 15.3% | 16.6% | 11.6% | 11.6% | 18.3%
Genera PR | Fuel | MMBTU consumed | Diesel #2 | Million MMBTU | 2.5828 | 3.626 | 4.6465 | 5.1736 | 2.269 | 1.6723 | 1.4733 | 5.0425 | 5.1075 | 3.6603 | 3.528 | 5.0147 | 4.4745 | 4.091 | 3.5691 | 1.7729 | 2.684 | 1.681 | 1.1772 | 0.61109 | 1.6258 | 2.0362 | 1.4978 | 1.998 | 1.8743 | 1.3786 | 2.222 | 3.3 | 3.1 | 3.42 | 2.9232 | 1.2496 | 1.2616 | 0.8056 | 1.7403 | 1.9953 | 1.3442 | 1.4783 | 1.924 | 2.5467 | 3.0305 | 1.6296 | 0.79826 | 0.49401 | 0.7078 | 0.86041 | 1.1856 | 2.564 | 2.2936 | 3.2131 | 3.0096 | 2.7789 | 3.1602 | 2.4544 | 1.3516 | 1.7184 | 1.5114 | 1.5651 | 2.1973 | 2.8826 | 1.8935 | 1.5491 | 2.8948 | 2.7031 | 3.19 | 1.36 | 1.97 | 1.8325 | 1.8123 | 3.1515 | 3.2779 | 1.53 | 2.08 | 2.417 | 1.99 | 1.344 | 3.029 | 1.914 | 1.016 | Consumed Units in TBtu.
Genera PR | Fuel | MMBTU consumed | #6 | Million MMBTU | 3.7376 | 3.0489 | 3.7338 | 3.4338 | 4.5085 | 3.9213 | 3.944 | 4.4398 | 8.2414 | 5.3729 | 5.0381 | 5.2273 | 7.3061 | 7.8231 | 6.1927 | 5.3561 | 4.432 | 4.4534 | 4.5557 | 3.716 | 2.3334 | 2.9401 | 4.314 | 4.5694 | 3.4184 | 3.7792 | 4.7392 | 5.08 | 5.15 | 5.15 | 6.3697 | 7.6966 | 6.9617 | 5.7785 | 5.415 | 6.8782 | 7.2852 | 7.5179 | 7.4342 | 4.8551 | 5.9685 | 6.1561 | 7.5023 | 5.5882 | 4.2767 | 5.762 | 4.8228 | 5.9028 | 5.6618 | 4.8832 | 4.1974 | 3.5487 | 4.3254 | 3.1033 | 3.0075 | 2.1748 | 2.9469 | 2.3303 | 2.3692 | 6.1524 | 6.8539 | 6.6841 | 5.7243 | 5.6843 | 4.27 | 3.29 | 2.09 | 2.4801 | 2.875 | 2.038 | 1.7577 | 3.28 | 4.45 | 4.682 | 3.484 | 3.411 | 5.189 | 4.323 | 5.388 | Consumed Units in TBtu.
Genera PR | Fuel | MMBTU consumed | NG | Million MMBTU | 4.3696 | 3.8784 | 2.4892 | 3.6572 | 3.9081 | 4.1744 | 4.2765 | 0.84345 | 0 | 0 | 0.47711 | 0.53627 | 0.55989 | 1.4724 | 3.3915 | 4.3607 | 3.3635 | 3.3131 | 3.5823 | 4.3694 | 4.0093 | 4.4533 | 3.3187 | 4.1932 | 5.6751 | 6.566 | 5.5028 | 5.26 | 5.38 | 5.38 | 3.4856 | 3.0812 | 2.9665 | 4.7126 | 3.4615 | 4.332 | 5.0066 | 5.34 | 5.7035 | 4.2262 | 4.0167 | 4.4885 | 3.0604 | 4.447 | 5.4512 | 4.9479 | 5.702 | 4.9635 | 5.7874 | 6.1502 | 6.3839 | 6.435 | 5.4441 | 5.726 | 5.4757 | 4.6748 | 3.9848 | 5.9787 | 7.4962 | 6.5215 | 7.4155 | 4.3918 | 6.598 | 6.7207 | 7.69 | 8.33 | 7.28 | 6.9463 | 4.9258 | 5.3897 | 5.71 | 7.16 | 6.44 | 6.745 | 8.965 | 8.679 | 6.971 | 6.181 | 4.889 | Consumed Units in TBtu.
Genera PR | Fuel | Average fuel price | Diesel #2 | $ / MMBTU | 15.9962 | 15.2935 | 15.7697 | 13.283 | 14.4947 | 17.0085 | 20.879 | 16.107 | 16.3059 | 11.726 | 10.9411 | 8.5464 | 8.7695 | 10.3297 | 10.5491 | 10.1914 | 10.169 | 10.5419 | 10.8981 | 11.5721 | 11.8873 | 13.2801 | 14.1005 | 14.8291 | 15.847 | 16.1456 | 16.3439 | 18.44 | 18.7 | 18.94 | 17.93 | 19.26 | 20.7851 | 21.6948 | 21.5191 | 26.2893 | 29.5515 | 29.04 | 28.65 | 31.4217 | 30.1817 | 30.7669 | 26.4585 | 26.2923 | 26.3042 | 25.1542 | 24.2891 | 22.6645 | 21.9207 | 21.5212 | 22.7325 | 24.1062 | 23.8458 | 23.1552 | 22.0155 | 21.3269 | 21.4287 | 21.2263 | 21.6056 | 19.9383 | 19.4483 | 19.6 | 19.0981 | 18.8448 | 18.76 | 18.59 | 18.08 | 18.5647 | 18.3917 | 17.0869 | 16.1276 | 15.8935 | 17.4117 | 18.467 | 17.312 | 17.73 | 17.64 | 18.84 | 16.72
Genera PR | Fuel | Average fuel price | #6 | $ / MMBTU | 12.9223 | 12.8311 | 12.3021 | 13.8314 | 12.4498 | 12.3739 | 12.3782 | 14.02 | 13.9117 | 11.7988 | 10.0551 | 7.9211 | 7.4224 | 8.3811 | 8.978 | 8.7663 | 8.911 | 9.173 | 9.6234 | 10.6068 | 10.9873 | 11.6949 | 12.0717 | 12.3997 | 10.515 | 12.728 | 12.6132 | 13.39 | 14.33 | 13.75 | 13.65 | 14.74 | 16.6848 | 18.7698 | 19.935 | 20.5296 | 21.354 | 21.05 | 19.98 | 18.6693 | 18.1474 | 17.0305 | 16.5694 | 15.7283 | 15.8045 | 15.42 | 15.4124 | 14.7094 | 14.6413 | 14.581 | 15.2765 | 15.6778 | 15.6741 | 15.5771 | 14.4396 | 14.7127 | 15.2812 | 15.7243 | 15.9816 | 15.6867 | 15.8857 | 15.7524 | 15.465 | 14.8237 | 14.75 | 14.44 | 14.23 | 14.3725 | 13.8335 | 12.9971 | 11.8217 | 11.7597 | 13.1613 | 12.723 | 12.49 | 12.23 | 11.37 | 11.9 | 10.97
Genera PR | Fuel | Average fuel price | NG | $ / MMBTU | 9.0868 | 8.9126 | 8.8288 | 8.8902 | 8.9665 | 9.0608 | 8.99 | 8.8885 | 0 | 0 | 10.3791 | 10.5631 | 10.4803 | 10.1918 | 8.3297 | 9.1902 | 8.8763 | 9.932 | 9.9032 | 9.658 | 9.4156 | 9.4484 | 8.9857 | 9.6275 | 10.0717 | 10.8684 | 11.4804 | 12.34 | 13.52 | 13.36 | 12.46 | 10.65 | 14.2548 | 12.3032 | 13.1864 | 15.4071 | 18.2349 | 14.58 | 16.54 | 17.306 | 15.113 | 12.5139 | 13.3188 | 11.9154 | 10.0754 | 9.3187 | 8.7897 | 8.9346 | 9.0082 | 9.4935 | 8.8657 | 8.9394 | 9.1786 | 9.6386 | 9.1119 | 9.0119 | 8.8635 | 7.8571 | 7.8113 | 9.8111 | 10.4963 | 11.2536 | 10.2281 | 9.5179 | 10.19 | 9.95 | 10.71 | 10.7089 | 9.8189 | 10.4625 | 10.4952 | 9.9368 | 9.4065 | 10.55 | 10.18 | 9.83 | 9.1 | 9.11 | 10.98
Genera PR | Fuel | Average fuel price vs. forecast price | Diesel #2 | Percentage | 0.1384% | -4.549% | -1.915% | -12.72% | -6.234% | 9.75% | 34.59% | 4.826% | 5.188% | -23.96% | 30.84% | -6.473% | 0.5003% | 0.811% | 1.636% | -2.651% | 6.081% | 9.971% | 12.2% | -11.08% | -9.685% | -15.67% | -10.76% | -6.063% | 0.542% | 2.437% | 57.47% | 46.79% | -4.43% | -4.58% | 1.39% | 10.47% | 17.81% | 23.67% | 24.17% | 52.13% | 22.08% | -10.35% | -8.89% | 2.05% | 8.52% | 12.81% | -0.94% | 0.41% | 2.7% | 10.49% | 6.88% | 1.24% | 5.68% | 4.03% | -9.685% | 16.02% | -2.295% | -1.705% | -3.822% | 8.753% | 8.68% | 9.171% | 12.72% | 5.005% | 3.372% | -0.86% | -3.87% | 12.04% | 8.96% | 8.24% | 7.1% | 5.72% | 5.31% | -1.83% | -13.64% | -14.43% | -5.854% | 8.972% | 3.211% | 6.189% | -1.66% | 6.51% | -4.58%
Genera PR | Fuel | Average fuel price vs. forecast price | #6 | Percentage | -4.358% | -4.086% | -7.315% | 1.851% | 1.506% | 1.096% | 0.5837% | -1.882% | 20.51% | 1.993% | 48.18% | 13.42% | -0.1045% | -3.082% | 2.633% | -0.3649% | 3.046% | 5.59% | 12.84% | -4.266% | -1.927% | -12.64% | -7.794% | -4.653% | -19.14% | -2.128% | 46.85% | 29.13% | -6.19% | -7.86% | -1.38% | 9.87% | 25.03% | 41.01% | 50.51% | 55.69% | 3.52% | -9.08% | -13.08% | -18.05% | 9.92% | 3.3% | 0.68% | -4.18% | -3.55% | -4.35% | -5.07% | -9.13% | -5.03% | -5.15% | -3.346% | 2.166% | 3.213% | 3.646% | -3.255% | -2.039% | 0.6181% | 3.775% | 5.683% | 3.962% | 4.109% | -1.73% | -2.61% | 7.049% | 0.01% | -1.1% | 4.37% | 2.38% | 0.09% | -6.39% | -15.82% | -15.52% | -5.888% | -11.71% | -12.44% | -13.54% | -12.94% | -8.22% | -14.8%
Genera PR | Fuel | Average fuel price vs. forecast price | NG | Percentage | -0.4732% | -0.3065% | -1.244% | -4.299% | 9.121% | 8.734% | 5.269% | -6.702% | -100% |  | -8.997% |  | 0.1319% | -0.2693% | -19.81% | -11.94% | -20.44% | -14.75% | -8.168% | -2.809% | -8.036% | -8.993% | -7.423% | -1.255% | 2.647% | 10.77% | 27.03% | 23.55% | -2.18% | 0.87% | -5.71% | -5.87% | 26.43% | 10.09% | 19.1% | 39.04% | 52.02% | -10.8% | 0.21% | 6.24% | -2.92% | -19.97% | -15.65% | -24.74% | 0.26% | 0% | -7.06% | -7.31% | 0.72% | 1.38% | -5.34% | 0.1613% | 1.03% | -0.4277% | -10.4% | 1.66% | -4.969% | 13.28% | 12.98% | 8.911% | 0.06514% | 1.92% | -8.07% | -8.839% | 2.04% | -2.13% | -0.28% | 20.26% | 6.76% | 13.27% | 5.94% | 1.296% | -4.474% | -2.054% | -3.044% | -6.494% | -10.62% | -12.34% | 0.67%
Genera PR | Planning and Enviromental | Total Emissions (system) | Total | tons | [43 empty] | 2880.06 | 2613.01 | 3454.61 | 2697.95 | 3870.46 | 3798.85 | 3444.61 | 3285.24 | 2910.13 | 2919 | 2629.99 | 2210.3 | 1622.23 | 1839.82 | 2020.51 | 2141.87 | 3968.68 | 4056.61 | 3399.52 | 3656.61 | 3500.52 | 3435.7 | 2692.22 | 2086.89 | 2563.52 | 2544.54 | 1875.88 | 1947.31 | 2559.92 | 3283.41 | 3395.23 | 3065.48 | 2809.25 | 4080.77 | 3263.28 | 3206.22
Genera PR | Planning and Enviromental | Total Emissions (system) | CO2 | tons | [43 empty] | 76.64 | 76.45 | 95.98 | 80.37 | 92.47 | 106.86 | 183.53 | 111.99 | 110.67 | 81.53 | 83.97 | 68.48 | 65.96 | 74.99 | 71.26 | 66.42 | 98.38 | 108.05 | 81.94 | 105.2 | 74.67 | 82.91 | 79.28 | 46.49 | 63.73 | 63.41 | 51.42 | 51.81 | 59.29 | 70.69 | 86.81 | 92.8 | 95.15 | 108.57 | 95.77 | 79.48
Genera PR | Planning and Enviromental | Total Emissions (system) | SO2 | tons | [43 empty] | 1494.12 | 1109.7 | 1516.22 | 1078.62 | 1536.72 | 1453.53 | 1102.86 | 1113.58 | 936.12 | 846.77 | 840.69 | 794.24 | 569.1 | 762.27 | 723.48 | 618.58 | 1601.01 | 1720.73 | 1467.64 | 1347.69 | 1251.83 | 1107.16 | 882.32 | 557.92 | 894.79 | 1007.55 | 586.02 | 522.38 | 877.02 | 1176.91 | 1228.98 | 909.3 | 864.23 | 1348.63 | 1071.61 | 1324.28
Genera PR | Planning and Enviromental | Total Emissions (system) | Nox | tons | [43 empty] | 1042.71 | 1190.7 | 1550.43 | 1333.73 | 1909.35 | 1938.06 | 1934.76 | 1822.09 | 1649.74 | 1781.24 | 1522.78 | 1181.57 | 0.28 | 876.87 | 1077.43 | 1315.47 | 1950.89 | 1897.26 | 1530.37 | 1933.2 | 1983.95 | 1550.19 | 1314.43 | 1314.43 | 1401.61 | 1255.97 | 1077.15 | 1222.18 | 1411.34 | 1752.19 | 1813.25 | 1865.1 | 1666.07 | 2317.27 | 1870.1 | 1539.89
Genera PR | Planning and Enviromental | Total Emissions (system) | PM | tons | [43 empty] | 228.49 | 191.82 | 248.81 | 177.88 | 280.99 | 259.31 | 198.66 | 210.17 | 191.18 | 189.34 | 165.94 | 146.73 | 105.58 | 113.74 | 131.47 | 127.59 | 274.57 | 285.4 | 271.68 | 239.48 | 257.82 | 228.49 | 162.66 | 144.56 | 175.97 | 188.44 | 141.29 | 132.18 | 182.29 | 240.75 | 230.86 | 178.26 | 166.69 | 269.46 | 200.21 | 225.49
Genera PR | Planning and Enviromental | Total Emissions (system) | VOC | tons | [43 empty] | 13.21 | 24.12 | 15.02 | 11.09 | 16.61 | 17.86 | 20.62 | 19.97 | 21.14 | 17.54 | 15.81 | 10.51 | 10.34 | 11.93 | 11.51 | 12.03 | 18.72 | 18.1 | 14.59 | 19.51 | 14.79 | 16.31 | 12.21 | 9 | 12.33 | 13.12 | 13.73 | 13.84 | 10.32 | 12.47 | 15.73 | 14.89 | 14.6 | 20.21 | 14.79 | 12.35
Genera PR | Planning and Enviromental | Total Emissions (system) | Pb | tons | [43 empty] | 0.03 | 0.02 | 0.02 | 0.02 | 0.04 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.02 | 0.03 | 0.02 | 0.01 | 0.01 | 0.03 | 0.05 | 0.03 | 0.01 | 0.06 | 0.05 | 0.03 | 0.02 | 0.04 | 0.03 | 0.02 | 0.04 | 0.04 | 0.02 | 0.02 | 0.03 | 0.02 | 0.01 | 0.04 | 0.03 | 0.02
Genera PR | Planning and Enviromental | Emissions rates (system) | CO2 | lb / MMBTU | [43 empty] | 0.01 | 0.01 | 0.02 | 0.01 | 0.01 | 0.02 | 0.03 | 0.02 | 0.02 | 0.01 | 0.01 | 0.01 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.01 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
Genera PR | Planning and Enviromental | Emissions rates (system) | SO2 | lb / MMBTU | [43 empty] | 0.28 | 0.21 | 0.26 | 0.18 | 0.23 | 0.21 | 0.15 | 0.16 | 0.15 | 0.13 | 0.15 | 0.16 | 0.18 | 0.24 | 0.19 | 0.17 | 0.3 | 0.3 | 0.27 | 0.23 | 0.22 | 0.21 | 0.2 | 0.15 | 0.21 | 0.26 | 0.18 | 0.15 | 0.21 | 0.25 | 0.24 | 0.17 | 0.17 | 0.22 | 0.2 | 0.31
Genera PR | Planning and Enviromental | Emissions rates (system) | Nox | lb / MMBTU | [43 empty] | 0.2 | 0.23 | 27 | 0.23 | 0.28 | 0.28 | 0.27 | 0.27 | 0.26 | 0.28 | 0.27 | 0.24 | 0.28 | 0.28 | 0.28 | 0.36 | 0.36 | 0.33 | 0.28 | 0.33 | 0.33 | 0.37 | 0.35 | 0.36 | 0.34 | 0.33 | 0.33 | 0.36 | 0.34 | 0.37 | 0.35 | 0.35 | 0.32 | 0.38 | 0.35 | 0.36
Genera PR | Planning and Enviromental | Emissions rates (system) | PM | lb / MMBTU | [43 empty] | 0.04 | 0.04 | 0.04 | 0.03 | 0.04 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.03 | 0.03 | 0.04 | 0.04 | 0.05
Genera PR | Planning and Enviromental | Emissions rates (system) | VOC | lb / MMBTU | [43 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Genera PR | Planning and Enviromental | Emissions rates (system) | Pb | lb / MMBTU | [43 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Genera PR | Planning and Enviromental | Carbon intensity of fossil generation |  | tons / MWH | [43 empty] | 0.72 | 0.73 | 0.76 | 0.65 | 0.82 | 0.83 | 0.67 | 0.7 | 0.68 | 0.73 | 0.78 | 0.76 | 0.73 | 0.8 | 0.83 | 0.79 | 0.86 | 0.85 | 0.77 | 0.8 | 0.75 | 0.66 | 0.64 | 0.61 | 0.84 | 0.8 | 0.89 | 0.8 | 0.77 | 0.85 | 0.81 | 0.77 | 0.75 | 0.86 | 0.8 | 0.84
Genera PR | Fleet | Fleet out of service (system) |  | Percentage | N/A | N/A | 20.89% | 17.28% | 18.1% | 18.1% | 17.28% | 17.28% | 17.87% | 17.53% | 0% | 18.1% | 15.3% | 17.99% | 18.98% | 19.55% | 20.61% | 17.78% | 16.6% | 17.79% | 18.4% | N/A | N/A | N/A | Not available | Not available | Not available | Not available | Not available | Not available | Not available | Not available | 88% | 63% | 71% | 77% | 67% | 35% | 36% | 37% | 33% | 33% | 32% | 31% | 31% | 32% | 33% | 33% | 31% | 19.84% | 17.6% | 17.6% | 17.6% | 19.2% | 18.4% | 19.2% | 24% | 20.8% | 25.6% | 26.4% | 24.8% | 22.4% | 17.6% | 17.6% | 17% | 17% | 18% | 17% | 26% | 27% | 31% | 28% | 27%% | 27% | 4% | 4%% | 4% | 4% | 4%
Genera PR | Fleet | Total available vehicles in service (system) |  | Number of vehicles | N/A | N/A | 2925 | 2925 | 2896 | 2896 | 2925 | 2925 | 2904 | 3516 | 0 | 2896 | 2995 | 2900 | 2865 | 2818 | 2781 | 2880 | 3171 | 3142 | 3117 | N/A | N/A | N/A | 125 | 125 | 125 | Not available | Not available | Not available | Not available | Not available | 313 | 336 | 336 | 338 | 338 | 220 | 216 | 213 | 225 | 226 | 229 | 232 | 232 | 230 | 227 | 227 | 248 | 101 | 103 | 103 | 103 | 101 | 102 | 101 | 95 | 99 | 93 | 92 | 94 | 97 | 103 | 103 | 104 | 104 | 103 | 104 | 92 | 91 | 89 | 90 | 91 | 91 | 100 | 100 | 100 | 100 | 100

## Genera Incentive Metrics
Reported by | Metric Category | Metric | Definition | Sub-Group | Unit of Measure | 2023-07-01 | 2023-08-01 | 2023-09-01 | 2023-10-01 | 2023-11-01 | 2023-12-01 | 2024-01-01 | 2024-02-01 | 2024-03-01 | 2024-04-01 | 2024-05-01 | 2024-06-01 | 2024-07-01 | 2024-08-01 | 2024-09-01 | 2024-10-01 | 2024-11-01 | 2024-12-01 | 2025-01-01 | 2025-02-01 | 2025-03-01 | 2025-04-01 | 2025-05-01 | 2025-06-01 | 2025-07-01 | 2025-08-01 | 2025-09-01 | 2025-10-01 | 2025-11-01 | 2025-12-01
Genera PR | Operation Cost Efficiency | Operation Cost Efficiency | Actual expenditures as a percentage (%) of the Efficiency approved Operating Budget, where actual savings equal the Operating Budget minus actual expenditures |  | Percentage | 3.17% | 6.88% | 12.69% | 18.19% | 27.16% | 36.52% | 43.13% | 49.89% | 57.96% | 67.1% | 75.23% | 91.5% | 5.817% | 11.68% | 17.94% | 25.95% | 33.26% | 42.66% | 48.99% | 56.86% | 64.94% | 70.56% | 83.3% | 95.36% | 4.217% | 8.487% | 13.21% | 19% | 24.5% | 30.07%
Genera PR | Equivalent Availability Factor | Equivalent Availability Factor (EAF) for Baseload Units | Equivalent Availability Factor for Baseload Units EAF= [(Available Hours - Equivalent Unplanned Derated Hours - Hours or Number of hours that the Legacy Generation Asset was in active state]x100% |  | Percentage | 48.13% | 49.71% | 46.37% | 49.41% | 46.42% | 39.57% | 29.59% | 36.95% | 35.22% | 30.84% | 45.53% | 57.49% | 53.87% | 54.82% | 51.63% | 43.92% | 53.17% | 32.57% | 25.75% | 43.5% | 30.95% | 28.62% | 44.37% | 46.57% | 49.12% | 52.97% | 57.38% | 59.47% | 56.4% | 50.45%
Genera PR | Equivalent Availability Factor | Equivalent Availability Factor (EAF) for Peaking Units | Equivalent Availability Factor for Baseload Units EAF= [(Available Hours - Equivalent Unplanned Derated Hours - Hours or Number of hours that the Legacy Generation Asset was in active state]x100% |  | Percentage | 54.1% | 58.04% | 52.87% | 49.79% | 50.7% | 52.85% | 54.1% | 66.2% | 55.49% | 64.62% | 71.4% | 58.6% | 68.13% | 70.91% | 69.85% | 74.69% | 69.53% | 68.89% | 55.93% | 56.43% | 53.85% | 53.77% | 54.95% | 57.52% | 55.36% | 52.34% | 53.85% | 49.56% | 49.96% | 46.4%
Genera PR | Environmental Compliance | Number of Consent Decrees Violations | Violation of Consent Decrees and/or Notice of Violations (NOVs) |  | Number | 85 | 28 | 35 | 28 | 18 | 19 | 36 | 13 | 11 | 27 | 66 | 77 | 89 | 126 | 50 | 32 | 29 | 21 | 36 | 13 | 11 | 16 | 11 | 35 | 35 | 22 | 23 | 44 | 38 | 26
Genera PR | Environmental Compliance | Number of NOVs | Violation of Consent Decrees and/or Notice of Violations (NOVs) |  | Number | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Genera PR | Reporting Obligations | Reporting Obligations | For every fifteen (15) sequential days during which Operator fails to respond to Administrator, Operator shall pay a penalty of US$100,000 (the "Reporting Obligation Charge") |  | Number | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Genera PR | Decommissioning Costs Efficiency | Decommissioning Costs Efficiency | Please refer to Genera's Motion |  | Percentage | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 59.4% | N/A | N/A | N/A | N/A | N/A

## Definitions
Metric | Units_En | Definition | Metric_Es | Units_Es | Definition_Es
OSHA DART Rate | Rate | The Occupational Safety and Health Administration (OSHA) Days Away/Restricted or Transfer Rate (DART) describes the number of recordable injuries and illnesses that resulted in days away from work, restricted worked activity, or job transfer, multiplied by 200,000 and divided by the total number of hours worked by employees in the year. The metric represents the number of applicable injuries for every 100 employees working full-time per year. | Índice DART de OSHA | Tasa | Los días de ausencia/restringidos o tasa de transferencia (DART, de lesiones registrables de la Administración de Seguridad y Salud Ocupacional (OSHA, por sus siglas en inglés) describe el número de lesiones y enfermedades registrables que resultaron en días de ausencia del trabajo, actividad laboral restringida o transferencia de trabajo, multiplicado por 200,000 y dividido por el número total de horas trabajadas por los empleados en el año. La métrica representa la cantidad de lesiones aplicables por cada 100 empleados que trabajan a tiempo completo por año.
OSHA Severity Rate | Rate | The Occupational Safety and Health Administration (OSHA) Severity Rate describes the total number of days away from work, restricted worked activity, or job transfer asa result of a recordable injury, multiplied by 200,000 and divided by the total number of hours worked by employees in the year. The metric is used to compare the severity of occupational injuries in different time periods. | Índice de gravedad de OSHA | Tasa | La tasa de gravedad de la Administración de Seguridad y Salud Ocupacional (OSHA) describe la cantidad total de días fuera del trabajo, actividad laboral restringida o transferencia de trabajo como resultado de una lesión registrable, multiplicada por 200,000 y dividida por la cantidad total de horas trabajadas por los empleados. en el año. La métrica se utiliza para comparar la gravedad de las lesiones laborales en diferentes períodos de tiempo.
OSHA Fatality | Rate | The Occupational Safety and Health Administration (OSHA) number of fatalities is defined as the total number of workers fatally injured from an occupational injury. | Número de fatalidad de OSHA | Tasa | El número de fatalidades de la Administración de Seguridad y Salud Ocupacional (OSHA, por sus siglas en inglés) se define como el número total de trabajadores fatalmente lesionados por una lesión ocupacional.
OSHA Recordable Rate | Rate | The Occupational Safety and Health Administration (OSHA) recordable rate is defined as the number of employees per 100 full-time employees or 200,000 hours that have been involved in an OSHA-recordable injury or illness. | Tasa incidencia de OSHA | Tasa | La tasa de incidencia de la Administración de Seguridad y Salud Ocupacional (OSHA) se define como el número de empleados por cada 100 empleados a tiempo completo o 200,000 horas que han tenido una lesión o enfermedad.
12-Month Rolling OSHA Recordable Rate | Rate | A weighted 12-month rolling average of the OSHA Recordable Injury Rate. | Índice de lesiones registrables de OSHA de los últimos 12 meses | Tasa | Un promedio de los ultimos 12 meses de la tasa de lesiones registrables de OSHA.
12-Month Rolling OSHA Fatality Rate | Rate | The Occupational Safety and Health Administration (OSHA) fatality rate is defined as the number of fatally injured worked divided by the number of employed workers, multiplied by 100,000. This value is the average of the past 12 months. | Tasa de fatalidad de los últimos 12 meses de la OSHA | Tasa | La tasa de fatalidad de la Administración de Seguridad y Salud Ocupacional (OSHA) se define como el número de lesiones fatales trabajadas divididas por el número de trabajadores, multiplicado por 100,000. Este valor es el promedio de los últimos 12 meses.
12-Month Rolling OSHA Severity Rate | Rate | A weighted 12-month rolling average of the OSHA Severity Rate. | Índice de gravedad de OSHA de los últimos 12 meses | Tasa | Un promedio de los ultimos 12 meses de la tasa de gravedad de OSHA.
12-Month Rolling OSHA DART Rate | Rate | A weighted 12-month rolling average of the OSHA DART Rate. | Índice de incidencia DART de OSHA de los últimos 12 meses | Tasa | Un promedio de los ultimos 12 meses de la tasa de gravedad de DART.
Budgeted headcounts by employee type | Number | This metric measures the budgeted number of employees. | Puestos presupuestados por tipo de empleado | Número | Esta métrica mide la cantidad presupuestada de empleados.
Actual headcounts by employee type | Number | This metric measures the actual number of employees. | Número actual de empleados por tipo de empleado | Número | Esta métrica mide el número real de empleados al momento.
Turnover rate | Percentage | The rate at which employees move in and out of a company, it measures the percentage of employees during a specific period. | Tasa de cambio de personal | Porcentaje | Es la tasa en la que los empleados entran y salen de una empresa, mide el porcentaje de empleados durante un período específico.
Monthly CAIDI | Minutes | The Customer Average Interruption Duration Index (CAIDI) represents the average outage duration experienced by customers over the given month. It is calculated by dividing the System Average Interruption Duration Index (SAIDI) by the System Average Interruption Frequency Index (SAIDI). | CAIDI | Minutos | El índice de duración de interrupción promedio del cliente (CAIDI por sus siglas en inglés) representa la duración promedio de la interrupción experimentada por los clientes durante el mes dado. Se calcula dividiendo el índice de duración de interrupción promedio del sistema (SAIDI) por el índice de frecuencia de interrupción promedio del sistema (SAIFI).
Operational expenses vs. budget | Percentage | Operational expenses v. budget represents the actual amount of money spent on operational expenses as a percentage of the budget. | Gastos operativos en relación al presupuesto | Porcentaje | Gastos operativos en relación al presupuesto representa la cantidad real de dinero gastado en gastos operativos como porcentaje del presupuesto.
Capital expenses vs. budget | Percentage | Capital expenses v. budget represents the actual amount of money spent on capital expenses as a percentage of the budget. | Gastos de capital en relación al presupuesto | Porcentaje | Los gastos de capital en relación al presupuesto representa la cantidad real de dinero gastado en gastos de capital como porcentaje del presupuesto.
Number of customers by customer class | Number of customers | This metric represents the total number of active customers at the end of the period. | Número de clientes por clase de clientes | Número de clientes | Esta métrica representa el número total de clientes activos al final del período
Monthly system sales by customer class | GWh | This metric represents the total number of GWh of energy sold across all customer classes. | Ventas mensuales por clase de clientes | GWh | Esta métrica representa el número total de GWh de energía vendida en todas las clases de clientes.
Monthly sales by Municipality | GWh | This metric represents the total number of GWh of energy sold across all municipalities. | Ventas mensuales por municipio | GWh | Esta métrica representa el número total de GWh de energía vendida en todos los municipios.
Monthly system peak | MW | This metric represents the highest electrical power demand in MWh on the system overall per month, measured across rolling 60-minute averages. | Demanda pico del sistema en el mes | MW | Esta métrica representa la mayor demanda de energía eléctrica en MWh en el sistema por mes, medida a través de promedios móviles de 60 minutos.
Monthly peak by customer class | MW | This metric represents the highest electrical power demand in MW for each customer class per month, measured across rolling 15-minute averages. PREPA/LUMA currently do not have this information available. | Pico mensual por clase de clientes | MW | Esta métrica representa la mayor demanda de energía eléctrica en MW para cada clase de cliente durante el mes, medida en promedios de 15 minutos. PREPA/LUMA actualmente no tiene esta información disponible.
Monthly peak by district | MW | This metric represents the highest electrical power demand in MW for each district per month, measured across rolling 15-minute averages. PREPA/LUMA currently do not have this information available. | Pico mensual por distrito | MW | Esta métrica representa la mayor demanda de energía eléctrica en MW para cada distrito por mes, medido en promedios de 15 minutos. PREPA/LUMA actualmente no tiene esta información disponible.
Cost of generation per customer (system) | $/customer | The metric represents total generation costs including cost of fuel and fuel shipping,divided by total number of customers. | Costo de generación por cliente (sistema) | $/cliente | La métrica representa los costos totales de generación, incluido el costo del combustible y el envío de combustible. dividido por el número total de clientes.
Average revenue per kilowatt-hour sold | $/kWh | This metric measures the amount ($) billed by LUMA divided by billed (kWh) sales. | Ingreso promedio por kilovatio-hora vendido | $/kWh | Esta métrica mide la cantidad ($) facturada por LUMA dividida por las ventas facturadas (kWh).
Purchased energy from thermal PPOA's | GWh | This metric represents the total number of GWh of energy across the whole system aquired by PREPA from Purchase Power and Operating Agreement (PPOA) contracts. | Energía comprada por los acuerdo de compra de energía (“PPOA”, en inglés) térmico | MWh | Esta métrica representa el número total de GWH de energía termica en todo el sistema adquirido por PREPA por los acuerdo de compra de energía (“PPOA”, en inglés).
Cost of capacity purchased from thermal PPOA's | $ / kW-month | The cost of capacity represents the amount PREPA is paying for thermal generation (fossil fuel powered) capacity purchased from EcoEléctrica, measured in $ per kW-month. | Costo de capacidad comprado por acuerdo de compra de energía (“PPOA”, en inglés) térmico | $ / kW-month | El costo de la capacidad representa la cantidad de PREPA está pagando por la capacidad de generación térmica (combustible con combustible fósil) comprada en Ecoeléctrica, medida en $ por kW-mes.
Cost of energy (base + excess) purchased from thermal PPOA's | $ / MWh | The cost of energy represents the total cost paid by PREPA, including base and excess charges, for aquiring energy from EcoEléctrica, measured in $ per kWh. | Costo de energía (base + exceso) comprado por acuerdo de compra de energía (“PPOA”, en inglés) térmico | $ / MWh | El costo de la energía representa el costo total pagado por la PREPA, incluidos los cargos de base y exceso, por la energía adquirida de Ecoeléctrica, medido en $ por kWh.
Monthly SAIDI (T&D) | Minutes | The System Average Interruption Duration Index (SAIDI) represents the average duration of power outages for the system for a given time period. This metric reports outages for the whole system as a monthly number in minutes. It is calculated by dividing the sum total of all customer interruption durations by the number of customers served by the system. | SAIDI (T&D) Mensual | Minutos | El índice de duración de interrupción promedio del sistema (SAIDI en inglés) representa la duración promedio de las interrupciones de energía para el sistema durante un período de tiempo determinado. Esta métrica informa interrupciones para todo el sistema con un número mensual en minutos. Se calcula dividiendo la suma total de todas las interrupciones eléctricas al cliente por el número de clientes atendidos por el sistema.
SAIDI (T&D) 12-month rolling average | Minutes | The System Average Interruption Duration Index (SAIDI) represents the average duration of power outages for the system for a given time period. This metric reports outages for the whole system as an annualized number in minutes. It is calculated by dividing the sum total of all customer interruption durations by the number of customers served by the system. | Promedio de SAIDI (T&D) de los últimos 12 meses | Minutos | El índice de duración de interrupción promedio del sistema (SAIDI en inglés) representa la duración promedio de interrupciones del servicio de energía para el sistema durante un período de tiempo determinado. Esta métrica informa interrupciones para todo el sistema como un número anualizado en minutos. Se calcula dividiendo la suma total de todas las interrupciones del cliente por el número de clientes atendidos por el sistema.
Monthly SAIFI (T&D) | Interruptions per customer | The System Average Interruption Frequency Index (SAIFI) provides the average number of interruptions experienced by the sytem for a given time period. This metric reports outage frequency for the whole system as a monthly number of interruptions per customer. It is calculated by dividing the total number of customer interruptions by the number of customers. | SAIFI (T&D) Mensual | Interrupciones por clientes | El índice de frecuencia de interrupción promedio del sistema (SAIFI en inglés) proporciona el número promedio de interrupciones experimentadas por el sistema durante un período de tiempo determinado. Esta métrica informa de la frecuencia de interrupción para todo el sistema como un número mensual de interrupciones por cliente. Se calcula dividiendo el número total de interrupciones del cliente por el número de clientes.
SAIFI (T&D) 12-month rolling average | Interruptions per customer | The System Average Interruption Frequency Index (SAIFI) provides the average number of interruptions experienced by the sytem for a given time period. This metric reports outage frequency for the whole system as an annualized number of interruptions per customer. It is calculated by dividing the total number of customer interruptions over the past 12 months by the number of customers. | Promedio de SAIFI (T&D) de los últimos 12 meses | Interrupciones por clientes | El índice de frecuencia de interrupción promedio del sistema (SAIFI en inglés) proporciona el número promedio de interrupciones experimentadas por el sistema durante un período de tiempo determinado. Esta métrica informa de la frecuencia de interrupción para todo el sistema como un número de interrupciones del cliente por 12 meses. Se calcula dividiendo el número total de interrupciones del cliente por el número de clientes.
Net monthly work orders balance | Number of work orders | The metric documents the amount of maintenance work that will be performed. The balance represents the number of open work orders remaining at the end of the month. | Saldo de órdenes de trabajo mensuales netos | Número de ordenes | La métrica documenta la cantidad de trabajo de mantenimiento que se realizará. El saldo representa el número de órdenes de trabajo abiertas que quedan al final del mes.
Monthly MAIFI | Percentage | The Momentary Average Interruption Frequency Index (MAIFI) represents the average number of momentary interruptions a customer would experience over a given time interval. It is defined as the total number of customer interruptions less than a defined amount of time, divided by the total number of customers served. PREPA/LUMA currently do not have this information available. | MAIFI | Porcentaje | El índice de frecuencia de interrupción promedio momentánea (MAIFI en inglés) representa el número promedio de interrupciones momentáneas que un cliente experimentaría durante un intervalo de tiempo determinado. Se define como el número total de interrupciones de los clientes menores de un tiempo definido, dividido por el número total de clientes atendidos. PREPA/LUMA actualmente no tiene esta información disponible.
MAIFI 12-month rolling average | Percentage | The Momentary Average Interruption Frequency Index (MAIFI) represents the average number of momentary interruptions a customer would experience over a given time interval. It is defined as the total number of customer interruptions less than a defined amount of time, divided by the total number of customers served. PREPA/LUMA currently do not have this information available. | MAIFI | Porcentaje | El índice de frecuencia de interrupción promedio momentánea (MAIFI en inglés) representa el número promedio de interrupciones momentáneas que un cliente experimentaría durante un intervalo de tiempo determinado. Se define como el número total de interrupciones de los clientes menores de un tiempo definido, dividido por el número total de clientes atendidos. PREPA/LUMA actualmente no tiene esta información disponible.
Monthly SAIDI Distribution | Minutes | The System Average Interruption Duration Index (SAIDI) represents the average duration of power outages for the system for a given time period. This metric reports outages at the distribution level as a monthly number in minutes. It is calculated by dividing the sum total of all customer interruption durations by the number of customers served by the system. | SAIDI Distribución Mensual | Minutos | El índice de duración de interrupción eléctrica promedio del sistema (SAIDI en inglés) representa la duración promedio de las cortes de energía para el sistema durante un período de tiempo determinado. Esta métrica informa las interrupciones en el nivel de distribución como un número mensual en minutos. Se calcula dividiendo la suma total de todas las duraciones de interrupción de energía del cliente por el número de clientes atendidos por el sistema.
Monthly SAIDI Transmission Substation | Minutes | The System Average Interruption Duration Index (SAIDI) represents the average duration of power outages for the system for a given time period. This metric reports outages at the transmission level as a monthly number in minutes. It is calculated by dividing the sum total of all customer interruption durations by the number of customers served by the system. | SAIDI Mensual Subestación de Transmisión | Minutos | El índice de duración de interrupción promedio del sistema (SAIDI en inglés) representa la duración promedio de las cortes de energía para el sistema durante un período de tiempo determinado. Esta métrica informa las interrupciones en el nivel de transmisión como número mensual en minutos. Se calcula dividiendo la suma total de todas las duraciones de interrupción del cliente por el número de clientes atendidos por el sistema.
Monthly SAIFI Distribution | Interruptions per customer | The System Average Interruption Frequency Index (SAIFI) provides the average number of interruptions experienced by the sytem for a given time period. This metric reports outage frequency at the distribution level as a monthly number of interruptions per customer. It is calculated by dividing the total number of customer interruptions by the number of customers. | Distribución SAIFI Mensual | Interrupciones por cliente | El índice de frecuencia de interrupción promedio del sistema (SAIFI) proporciona el número promedio de interrupciones experimentadas por el sistema durante un período de tiempo determinado. Esta métrica informa de la frecuencia de interrupción en el nivel de distribución como un número mensual de interrupciones por cliente. Se calcula dividiendo el número total de interrupciones del cliente por el número de clientes.
Monthly SAIFI Transmission Substation | Interruptions per customer | The System Average Interruption Frequency Index (SAIFI) provides the average number of interruptions experienced by the sytem for a given time period. This metric reports outage frequency at the transmission level as a monthly number of interruptions per customer. It is calculated by dividing the total number of customer interruptions by the number of customers. | SAIFI Mensual Subestación de transmisión | Interrupciones por cliente | El índice de frecuencia de interrupción promedio del sistema (SAIFI) proporciona el número promedio de interrupciones experimentadas por el sistema durante un período de tiempo determinado. Esta métrica informa de la frecuencia de interrupción en el nivel de transmisión como un número mensual de interrupciones por cliente. Se calcula dividiendo el número total de interrupciones del cliente por el número de clientes.
Technical losses as % of net generation | Percentage | This metric represents technical losses as a percentage of net generation. Technical losses include energy dissipation that occur in cables, transformers and other equipment. | Pérdidas técnicas como % de la generación neta | Porcentaje | Esta métrica representa las pérdidas técnicas como un porcentaje de generación neta. Las pérdidas técnicas incluyen disipación de energía que ocurre en cables, transformadores y otros equipos.
DSO (Days Sales Outstanding) | Days | Days Sales Outstanding measures LUMA's ability to collect payment for clients' customer billings. | DSO (días de ventas pendientes de cobro) | Dias | Días de ventas pendientes de cobro mide el número promedio de días que LUMA tarda en cobrar el pago después de que se haya realizado una venta.
NTL as a % of net generation | Percentage | This metric represents the non technical losses (NTL) as a percentage of total generation. These might include defective meters, un-metered supply and theft. | NTL como % de generación neta | Porcentaje | Esta métrica representa las pérdidas no técnicas (NTL por sus siglas en inglés) como un porcentaje de generación total. Estos pueden incluir medidores defectuosos, suministro sin medidores y hurto.
Total number of calls received | Number | This metric measures the total number of customer service calls received by LUMA during the period. | Número total de llamadas recibidas | Numero | Esta métrica mide el número total de llamadas de servicio al cliente recibidas por LUMA durante el período.
Number of customer calls answered | Number of calls | This metric represents the number of customer service calls answered by LUMA. | Número de llamadas de clientes atendidas | Numero de llamadas | Esta métrica representa el número de llamadas de servicio al cliente respondidas por LUMA.
Percent of customer calls answered | Percentage | This metric measures the percent of calls answered by LUMA. This metric is calculated by the total number of calls answered in the month divided by the total number of calls received that month. | Porcentaje de llamadas de clientes atendidas | Porcentaje | Esta métrica mide el porcentaje de llamadas atendidas por LUMA. Esta métrica se calcula por el número total de llamadas atendida en el mes dividida por el número total de llamadas recibidas ese mes.
Average speed to answer | Minutes | Average speed to answer represents the average amout of time to answer a call to LUMA's call center. | Velocidad promedio para responder llamadas | Minutos | La velocidad promedio de respuesta representa la cantidad promedio de tiempo para responder una llamada al centro de llamadas de Luma.
Wait time in Customer Service Centers | Minutes | This measures the average wait time of customers in minutes at customer service centers. | Tiempo de espera en los centros de servicio al cliente | Minutos | Esto mide el tiempo de espera promedio de los clientes en minutos en los centros de servicio al cliente.
Number of Act 57 Claims Opened | Number of cases | The metric measures opened Act 57 claims, which are cases and disputes related to the review of the electricity bills sent by PREPA (LUMA as the Operator) to its customers. | Número de reclamos de la Ley 57 abiertas | Número de casos | Esta métrica mide las reclamaciones abiertas asociadas a reclamaciones de la Ley 57, que son casos y disputas relacionadas con la revisión de las facturas de electricidad enviadas por PREPA (LUMA como operador) a sus clientes.
Average time to resolve billing disputes (Act 57 Claims) | Days | The metric measures the average time to resolve Act 57 claims, which are cases and disputes related to the review of the electricity bills sent by PREPA (LUMA as the Operator) to its customers. | Tiempo promedio para resolver disputas de facturación (reclamos de la Ley 57 -) | Dias | La métrica mide el tiempo promedio para resolver los reclamos de la Ley 57, que son casos y disputas relacionadas con la revisión de las facturas de electricidad enviadas por PREPA (LUMA como operador) a sus clientes.
Number of customer complaints closed by class (Act 57 Claims) | Number of cases | The metric measures closed Act 57 claims, which are cases and disputes related to the review of the electricity bills sent by PREPA (LUMA as the Operator) to commercial customers. | Número de quejas de los clientes, resueltas por clase (Reclamaciones Ley 57) | Número de casos | La métricas mide los reclamos resueltos relacionados a la Ley 57 , que son casos y disputas relacionadas con la revisión de las facturas de electricidad enviadas por PREPA (LUMA como operador) a clientes comerciales.
Percent of customers on AMI | Percentage | This metric represents the total percentage of customers on advanced metering infrastructure (AMI). AMI allows for two-way communication and enhanced data gathering by the utility. | Porcentaje de los clientes en AMI (según sus siglas en ingles) | Porcentaje | Esta métrica representa el porcentaje total de clientes en la infraestructura de medición avanzada (AMI en ingles). AMI permite la comunicación bidireccional y la recopilación de datos mejorados por parte de la utilidad.
Percent of customers billed | Percentage | This metric measures the percentage of customers billed in a given month. | Porcentaje de los clientes facturados | Porcentaje | Esta métrica mide el porcentaje de clientes facturados en un mes determinado.
Percent of bills estimated vs. read | Percentage | This metric measures the percentage of customers whose bills are estimated. The metric is calculated by taking the number of customers whose bill is estimated in a given time period divided by the total number of customers. | Porcentaje de facturas estimadas comparadas con facturas con información de lectura real | Porcentaje | Esta métrica mide el porcentaje de clientes cuyas facturas se estiman. La métrica se calcula tomando el número de clientes cuya factura se estima en un período de tiempo determinado dividido por el número total de clientes.
Percent of automatically-generated NTL leads found to be occurrences of theft | Percentage | This metric represents the percentage of non technical losses (NTL) that were found to be occurrences of theft. | El porcentaje de los cables de NTL (según sus siglas en inglés) que son ocurrencias de robo | Porcentaje | Esta métrica representa el porcentaje de pérdidas no técnicas (NTL en inglés) que se encontraron que eran ocurrencias de robo.
Average time to respond to service and outage complaints | Days | This metric measures the amount of time to respond to a service and outage complaint filed with LUMA. | Tiempo promedio para responder a las quejas de servicio y interrupción | Días | Esta métrica mide la cantidad de tiempo para responder a una queja de servicio y/o interrupción notificada a LUMA.
Number of disconnections by customer class | Number of disconnections | This metric represents the total number of customer disconnections across all customer classes. Note that there was a moratorium on disconnections due to the COVID-19 pandemic that began May 2020. | Número de desconexiones por clase de cliente | Numero de desconexiones. | Esta métrica representa el número total de desconexiones de los clientes en todas las clases de clientes. Tenga en cuenta que hubo una moratoria en las desconexiones debido a la pandemia Covid-19 que comenzó en mayo de 2020.
Number of disconnections by Area | Number of disconnections | This metric represents the total number of customer disconnections across all areas. Note that there was a moratorium on disconnections due to the COVID-19 pandemic that began May 2020. | Número de desconexiones por área | Numero de desconexiones. | Esta métrica representa el número total de desconexiones de los clientes por áreas. Tenga en cuenta que hubo una moratoria en las desconexiones debido a la pandemia Covid-19 que comenzó en mayo de 2020.
Number of customers enrolled in extended payment plans by class | Number of customers | The metric measures the number of residential customers enrolled in financial assistance plans. | Número de clientes inscritos en planes de pago por clase | Número de clientes | La métrica mide el número de clientes residenciales inscritos en los planes de asistencia financiera.
Number of customers defaulting on extended payment plans by class | Number of customers | The metric measures the number of residential customers enrolled in financial assistance plans that have defaulted on their payments. | Número de clientes que incumplen los planes de pago, por clase | Número de clientes | La métrica mide el número de clientes residenciales inscritos en planes de asistencia financiera que han incumplido sus pagos.
Number of customers completing extended payment plans by class | Number of customers | The metric measures the number of residential customers who have enrolled in financial assistance plans and have completed their payment plan. | Número de clientes que completan planes de pago, por clase | Número de clientes | La métrica mide el número de clientes residenciales que se han inscrito en planes de asistencia financiera y han completado su plan de pago.
Accounts Payable days outstanding | Days | This metric measures the number of days it takes for LUMA to pay its bills. | Días de cuentas por pagar pendientes | Dias | Esta métrica mide la cantidad de días que LUMA tarda en pagar sus facturas.
Fleet out of service (system) | Percentage | This metric represents the percentage of the vehicle fleet that is out of service. | Flota de vehículos fuera de servicio (sistema) | Porcentaje | Esta métrica representa el porcentaje de la flota de vehículo que está fuera de servicio.
Total available vehicles in service (system) | Number of vehicles | This metric represents the number of vehicles that are available and in service. | Total de vehículos disponibles en servicio (sistema) | numero de vehiculos | Esta métrica representa el número de vehículos disponibles y en servicio.
Fuel Expenditure vs Forecast | Percentage | Fuel expenditure vs forecast represents the percentage difference of the actual fuel cost from the forecast fuel cost. | Gasto de Combustible vs Pronóstico | Porcentaje | El gasto de combustible vs el pronóstico, representa la diferencia porcentual del costo real del combustible con respecto al costo pronosticado.
MMBTU consumed vs. forecast | Percentage | This metric represents the percentage difference of the actual fuel consumed in MMBTUs from the forecast fuel consumption in MMBTUs. MMBTUs stands for Metric Million British Thermal Units and is the industry standard used to describe a volume of fuel. | MMBTU consumido vs pronóstico | Porcentaje | Esta métrica representa la diferencia porcentual del combustible real consumido en MMBTU del consumo de combustible pronosticado en MMBTU. MMBTU significa Métrica de Millones Británicos de Unidades Térmicas y es el estándar de la industria utilizado para describir un volumen de combustible.
Number of curtailed hours from RPS-eligible capacity | Hours | The number of curtailed hours refers to the numbers of hours during which the output of a renewable resource was reduced from what it could potentially have produced. | Número de horas reducidas desde la capacidad elegible para RPS (en ingles) | Horas | El número de horas reducidas se refiere al número de horas durante las cuales la producción de un recurso renovable se redujo de lo que podría haber producido.
Operational RPS-eligible capacity | MW | This metric represents the total operational energy generation capacity in MW that qualifies under Puerto Rico's Renewable Portfolio Standard (RPS). | Capacidad de generación operacional considerada como RPS (en ingles) | MW | Esta métrica representa la capacidad total de generación de energía operativa en MW que cualifica bajo el estándar de la cartera renovable (RPS según sus siglas en ingles) de Puerto Rico.
Contracted but not operational RPS-eligible capacity | MW | This metric represents the capacity of renewable resources that were contracted for but not actually dispatched to generate energy. | Capacidad contratada pero no operativa de RPS (en ingles) | MW | Esta métrica representa la capacidad de generación de los recursos renovables que fueron contratados pero que en realidad no se despacharon para generar energía.
Average delay in anticipated online date of RPS-eligible projects | Days | This metric measures the number of days of when RPS-eligible projects are actually commercially operational compared to the project's scheduled commercially operational date. | Retraso promedio en la fecha anticipada de los proyectos elegibles para RPS (en ingles) | Dias | Esta métrica mide el número de días de cuando los proyectos elegibles para RPS están realmente en operación comercial en comparación con la fecha programada del proyecto.
Average capacity factor of RPS-eligible capacity | Percentage | This metric quantifies the utilization of the given renewable resource. Capacity factors represent the percentage of time that a generation facility operated for relative to the total number of hours in a given time period. 'RPS-eligible facility' indicates that this resource qualifies under Puerto Rico's Renewable Portfolio Standard. | Factor promedio de la capacidad elegible para RPS (en ingles) | Porcentaje | Esta métrica cuantifica la utilización del recurso renovable. Los factores representan el porcentaje de tiempo que una instalación de generación operaba durante el número total de horas, durante un período de tiempo determinado. 'Instalaciónes elegible para RPS' indica que este recurso es considerado bajo el estándar de cartera renovable de Puerto Rico.
Generation from RPS-eligible PPOA's (percent of sales) | Percentage | This metric represents the percentage of all electricity sold that is aquired from renewable resources that qualify under Puerto Rico's Renewable Portfolio Standard (RPS) via Power Purchase and Operating Agreement (PPOA) contracts. | PPOA (en ingles) elegibles para RPS (porcentaje de ventas) | Porcentaje | Esta métrica representa el porcentaje de toda la electricidad vendida que se surgió de los recursos renovables que califican bajo el estándar de cartera renovable (RPS en inglés) de Puerto Rico a través de contratos de compra de energía y acuerdo operativo (PPOA en inglés).
Generation from RPS-eligible PPOA's (by unit) | GWh | This metric represents the total generation in GWh of all renewable resources contracted under Power Purchase and Operating Agreements (PPOAs) with PREPA. | Generación de electricidad de PPOA de RPS (por unidad) | MWh | Esta métrica representa la generación total en GWh de todos los recursos renovables contratados bajo la compra de energía y los acuerdos operativos (PPOA en inglés) con PREPA.
Total installed distributed generation capacity - Photovoltaic | MW | This metric represents the total capacity in MW of photovoltaic generation installed on the system overall. | Capacidad de generación total instalada: Fotovoltaica | MW | Esta métrica representa la capacidad total en MW de generación fotovoltaica en el sistema en general.
Total installed distributed generation capacity - Wind | MW | This metric represents the total capacity in MW of wind generation installed on the system overall. | Capacidad de generación total instalada: viento | MW | Esta métrica representa la capacidad total en MW de generación de viento en el sistema en general.
Total number of distributed generation installations - Photovoltaic | Number of facilities | This metric represents the total number of photovoltaic facilities installed across the system overall. | Número total de instalaciones de generación: Fotovoltaica | Numero de facilidades | Esta métrica representa el número total de instalaciones fotovoltaicas en todo el sistema en general.
Total number of distributed generation installations - Wind | Number of facilities | This metric represents the total number of wind facilities installed across the system overall. | Número total de instalaciones de generación: viento | Numero de facilidades | Esta métrica representa el número total de instalaciones de viento en todo el sistema en general.
Total installed BESS capacity | Kwh | This metric represents the installed capacity in kWh of Battery Energy Storage Systems (BESS) in the selected region. | Capacidad total de BESS (por sus siglas en ingles) instalada | Kwh | Esta métrica representa la capacidad instalada en KWH de los sistemas de almacenamiento de energía de batería (BESS en inglés) en la región seleccionada.
Total number of BESS installations | Number of facilities | This metric represents the number of Battery Energy Storage System (BESS) facilities in the selected region. | Número total de instalaciones de BESS (en ingles) | Numero de facilidades | Esta métrica representa el número de instalaciones del sistema de almacenamiento de energía de batería (BESS en inglés) en la región seleccionada.
Total budgeted head counts by employee type | Number | This metric measures the budgeted number of employees | Total de plantilla presupuestada por tipo de plantilla | Número | Esta métrica mide el número presupuestado de empleados
Total actual head counts by employee type | Number | This metric measures the actual number of employees | Plantilla actual por tipo | Numero | Esta métrica mide el número real de empleados
Absenteeism | Percentage | Absences are defined as instances when persons who usually work 35 or more hours per week (full time) worked less than 35 hours during the reference week for one of the following reasons: own illness, injury, or medical problems; child care problems; other family or personal obligations; civic or military duty; and maternity or paternity leave. Excluded are situations in which work was missed due to vacation or personal days, holiday, labor dispute, and other reasons. For multiple jobholders, absence data refer only to work missed at their main jobs. The absence rate is the ratio of workers with absences to total full-time wage and salary employment. | Ausentismo | Porcentaje | Las ausencias se definen como casos en que las personas que generalmente trabajan 35 o más horas por semana (a tiempo completo) trabajaron menos de 35 horas durante la semana de referencia por una de las siguientes razones: enfermedad propia, lesiones o problemas médicos; problemas de cuidado infantil; otras obligaciones familiares o personales; deber cívico o militar; y licencia de maternidad o paternidad. Se excluyen situaciones en las que se perdió el trabajo debido a vacaciones o días personales, vacaciones, disputas laborales y otras razones. Para empleados con múltiples trabajos, los datos de ausencia se refieren solo al trabajo perdido en sus principales trabajos. La tasa de ausencia es la proporción de trabajadores con ausencias dividido entre el total de tiempo completo.
Plant availability (system) | Percentage | Plant availablity for the system represents the amount of time all the plants can generate electricity divided by the time period. High plant availability indicates effectiveness of the generating plants. | Disponibilidad de la planta (sistema) | Porcentaje | La disponibilidad de las plantas para el sistema representa la cantidad de tiempo que todas las plantas pueden generar electricidad dividida en el período de tiempo. La disponibilidad de plantas indica la efectividad de las plantas generadoras.
Forced outages (system) | Percentage | Forced outages are when a power plant must be shut down for emergency reasons or due to equipment failure. This metric is calculated by taking the time the plant is unavailable during a time period divided by the total time for the period. | Paro forzadas (sistema) | Porcentaje | Las interrupciones forzadas (o paro forzado) son cuando una planta de energía debe interrumpir servicio por razones de emergencia o debido a la falla del equipo. Esta métrica se calcula tomando el tiempo que la planta no está disponible durante un período de tiempo dividido por el tiempo total para el período.
Cost of generation (system total) AEE, exc. PPOA's gen | $/kWh | The metric represents total generation costs, excluding purchased power costs, divided by total generation. | Costo de generación (Sistema Total) AEE, Excluyendo Generación de PPOA (por sus siglas en ingles) | $/kWh | La métrica representa los costos de generación total, excluyendo los costos de energía comprada, divididos por la generación total.
Cost of generation (system: fuel) | $/kWh | This metric represents the average fuel costs associated with energy generation across all powerplants. It is calculated on a $ per KWh basis for the amount of generation during the time period. | Costo de generación (sistema: combustible) | $/kWh | Esta métrica representa los costos promedio de combustible asociados con la generación de energía en todas las plantas de energía. Se calcula en base de $ por kWh para la cantidad de generación durante el período de tiempo.
Cost of generation (system: O&M AEE, exc. PPOA's gen) | $/kWh | This metric represents the total O&M costs associated with energy generation from the system for a time period, but excluding costs from power purchase agreements with AES and EcoElectrica. | Costo de generación (Sistema: O&M AEE, Excluyendo generación a través de PPOA's) | $/kWh | Esta métrica representa los costos totales de O&M asociados con la generación de energía del sistema durante un período de tiempo, pero excluyendo los costos de los acuerdos de compra de energía con AES y Ecoelectrica.
Cost of generation (by Plant Type) | $/kWh | This metric represents the total costs per kWh of generation for all the plants of this type over the time period. | Costo de generación (por tipo de planta) | $/kWh | Esta métrica representa los costos totales por kWh de generación para todas las plantas de ese tipo durante un período de tiempo.
Monthly thermal generation (system) AEE, excluding PPOA's gen | GWh | This metric represents the GWh of energy generated per month via thermal generation (fossil fuel powered generation) across all power plants on the system, including purchased power. | Generación térmica mensual (Sistema) AEE, excluyendo la generación de PPOA | GWh | Esta métrica representa los GWh de energía generada por mes a través de la generación térmica (generación de combustible fósil) en todas las centrales eléctricas del sistema, incluyendo la energía comprada.
Monthly thermal generation (by plant) | GWh | This metric represents the GWh of energy generated per month by the selected power plant. | Generación térmica mensual (por planta) | GWh | Esta métrica representa los GWh de energía generada por mes por la planta de energía seleccionada.
Average heat rate (system) | BTU/kWh | This metric represents the average heat rate across the whole system. Heat rate is a measure of efficiency for power plants that convert fuel into electricity. It is defined as the number of British thermal units (effectively a unit of fuel) required to generate one kilowatt hour of energy. Note that a lower heat rate corresponds to a higher efficiency. | Tasa de calor promedio (sistema) | BTU/kWh | Esta métrica representa la tasa de consumo de calor promedio en todo el sistema. El consumo de calor es una medida de eficiencia para las centrales eléctricas que convierten combustible en electricidad. Se define como el número de unidades térmicas británicas (efectivamente una unidad de combustible) requeridas para generar una hora de energía kilovatio (kWh). Nota: una tasa de calor más baja corresponde a una mayor eficiencia.
Average heat rate (by plant) | BTU/kWh | Heat rate is a measure of efficiency for power plants that convert fuel into electricity. It is defined as the number of British thermal units (effectively a unit of fuel) required to generate one kilowatt hour of energy. Note that a lower heat rate corresponds to a more efficient plant. | Tasa de calor promedio (por planta) | BTU/kWh | El consumo de calor es una medida de eficiencia para las centrales eléctricas que convierten combustible en electricidad. Se define como el número de unidades térmicas británicas (efectivamente una unidad de combustible) requeridas para generar una hora de energía kilovatio (kWh). Nota: una tasa de calor más baja corresponde a una planta más eficiente.
Plant availability (by plant) | Percentage | Plant availability is the amount of time that the plant is able to produce electricity over a certain period, divided by the amount of the time in the period. | Disponibilidad de la planta (por planta) | Porcentaje | La disponibilidad de la planta es la cantidad de tiempo que la planta puede producir electricidad durante un cierto período, dividido por la cantidad de tiempo en el período.
Forced outages (by plant) | Percentage | Forced outage percentage represents when a power plant has shut down for emergency reasons or due to equipment failure during a time period divided by the amount of time the plant should be operating over the same time period. | Interrupciones forzadas (por planta) | Porcentaje | El porcentaje de interrupción forzada (o paro forzado) representa cuando una planta de energía interrumpe su producción de energía por razones de emergencia o debido a una falla del equipo durante un período de tiempo dividido por la cantidad de tiempo que la planta debe operar durante el mismo período de tiempo.
MMBTU consumed | Million MMBTU | This metric represents the MMBtu of fuel consumed across the whole system. | MMBTU consumido | Millon MMBTU | Esta métrica representa el MMBTU de combustible consumido por todo el sistema.
Average fuel price | $ / MMBTU | This metric represents the average price paid by PREPA for fuel in $ per MMBtu. | Precio promedio de combustible | $ / MMBTU | Esta métrica representa el precio promedio pagado por PREPA por combustible en $ por MMBTU.
Average fuel price vs. forecast price | Percentage | This metric represents the actual average price paid by PREPA as a percentage of the predicted fuel price. | Precio promedio de combustible comparado con el precio de pronóstico | Porcentaje | Esta métrica representa el precio promedio real pagado por PREPA como porcentaje del precio estimado del combustible.
Total Emissions | tons | This metric represents the total amount of emissions in tons of sulphur dioxide, nitrogen oxides, carbon dioxide, particulate matter and other regulated pollutants released by the system overall. | Emisiones de SO2, NOX, CO2, PM, HG y otros contaminantes regulados (Sistema) | tons | Esta métrica representa la cantidad total de emisiones en toneladas de dióxido de azufre, óxidos de nitrógeno, dióxido de carbono, partículas y otros contaminantes regulados liberados al medio ambiente por el sistema en general.
Emissions rates | lb / MMBTU | This metric represents the average emission rate across the whole system of sulphur dioxide, nitrogen oxides, carbon dioxide, particulate matter and other regulated pollutants released by the system overall. It is measured in pounds of pollutants released per MMBtu of fossil fuel combusted. | Tasas de emisiones de SO2, NOX, CO2, PM, HG y otros contaminantes regulados (Sistema) | lb / MMBTU | Esta métrica representa la tasa de emisión promedio en todo el sistema de dióxido de azufre, óxidos de nitrógeno, dióxido de carbono, partículas y otros contaminantes regulados liberados al medio ambiente por el sistema en general. Se mide en libras de contaminantes liberados por MMBTU de combustible fósil utilizado.
Distribution line inspections | Number of inspections | The number of distribution line inspections completed, with data recorded in a database for analysis. Inspections of all 13.2 kV, 8.3 kV, and 4.16 kV mainline, 3 phase, overhead circuits to assess the physical integrality of the poles, structures, components, and equipment to be completed. | Inspecciones de líneas de distribución | Numero | El número de inspecciones de líneas de distribución completadas, con los datos registrados en una base de datos para su análisis. Se deben completar las inspecciones de todos los circuitos principales de 13,2 kV, 8,3 kV y 4,16 kV, trifásicos, aéreos, para evaluar la integralidad física de los postes, estructuras, componentes y equipos.
Transmission line inspections | Number of inspections | The number of transmission line inspections completed, with data recorded in a database for analysis. Inspections of all 230 kV, 115 kV, and 38 kV transmission circuits to assess the physical integratity of the poles, structures, components, and equipment to be completed. | Inspecciones de líneas de transmisión | Numero | El número de inspecciones de líneas de transmisión completadas, con los datos registrados en una base de datos para su análisis. Se deben completar las inspecciones de todos los circuitos de transmisión de 230 kV, 115 kV y 38 kV para evaluar la integralidad física de los postes, estructuras, componentes y equipos.
T&D substation inspections | Number of inspections | The number of distribution and transmission substation inspections completed, with data recorded in a database for analysis. Inspections of all distribution and transmission substation structures, components, and equipment to be completed. | Inspecciones de subestaciones de T&D | Numero | El número de inspecciones de subestaciones de distribución y transmisión completadas, con los datos registrados en una base de datos para su análisis. Se deben completar las inspecciones de todas las estructuras, componentes y equipos de las subestaciones de distribución y transmisión.
Overtime | Percentage | Measures ability to manage overtime costs. | Horas extras | Porcentaje | Mide la abilidad con que se administran los costes de horas extra.
Call abandonment rate | Percentage | The percentage of callers who hang up (abandon) while the call is still in the IVR queue. | Tasa de abandono de llamadas | Porcentaje | Porcentaje de abonados que cuelgan, o abandonan una llamada mientras aún esperan en el cuadro telefónico.
Carbon intensity of fossil generation | tons / MWH | The carbon intensity of fossil generation represents the number of tons of carbon dioxide released per MWh of energy generated. | Intensidad de carbon de la generación fósil | tons / MWH | La intensidad de carbón de la generación por combustibles fósiles representa el número de toneladas de dióxido de carbono liberado por MWH de energía generada.
Vegetation Maintenance Miles Completed | Miles | This metric represents the number of line miles completed for vegetation maintenance each fiscal year along 230kV, 115kV, 38kV, and primary Distribution lines. | Millas de mantenimiento de vegetación completadas | Millas | Esta métrica representa el número de millas de mantenimiento de vegetación completadas cada año fiscal a lo largo de las líneas de distribución primaria, 38kV, 115kV y 230kV.
Monthly CEMI | Percentage | Indicates the ratio of individual customers experiencing multiple interruptions or more sustained interruptions to the total number of customers served. | CEMI Mensual | Porcentaje | Indica la proporción de clientes individuales que experimentan múltiples interrupciones o más interrupciones sostenidas con respecto al número total de clientes atendidos.
CEMI 12-month rolling average | Percentage | Indicates the ratio of individual customers experiencing multiple interruptions or more sustained interruptions to the total number of customers served over the past twelve months. | Promedio de CEMI de los últimos 12 meses | Porcentaje | Indica la proporción de clientes individuales que experimentan múltiple interrupciones o más interrupciones sostenidas con respecto al número total de clientes atendidos en los últimos doce meses.
Customer Complaint Rate | Rate | This metric measures the total number of customer complaints registered with PREB under NEPR-QR and NEPR-RV dockets. | Tasa de querellas de clientes | Tasa | Esta métrica mide el número total de quejas de clientes registradas ante el PREB bajo los expedientes NEPR-QR y NEPR-RV.
First Call Resolution | Percentage | This metric represents the percentage of calls where the customer was able to resolve their needs on the first attempt. | Resolución en la primera llamada | Porcentaje | Esta métrica representa el porcentaje de llamadas en las que el cliente pudo resolver sus necesidades en el primer intento.
J.D. Power Customer Satisfaction Survey | Points | Industry standard third-party customer satisfaction survey. | Encuesta de satisfacción del cliente de J.D. Power | Puntos | Diseñado por un tercero, es una medida de satisfacción del cliente para clientes residenciales y comerciales.
NEM Project Activation Duration | Days | This metric measures the average duration in days for completing all activities (within the utility’s control) required to activate the NEM tariff on the customer’s bill. | Duración promedio de activación de proyectos de NEM | Días | Este indicador mide la duración promedio en días para completar todas las actividades (dentro del control de la utilidad) necesarias para activar la tarifa NEM en la factura del cliente.

## Methodology
Metric | Methodology
OSHA DART Rate | Data is gathered from three (3) sources: hours worked from Kronos; incidents data from Intelex; and active employees from Workday. This metric is calculated by the total number of DART cases reported during the month multiplied by the OSHA scaling factor and divided by the total number of hours worked by all employees. The OSHA scaling factor is 200,000 and equals one hundred (100) employees working forty (40) hours per week, fifty (50) weeks per year.
OSHA Severity Rate | Data is gathered from three (3) sources: hours worked from Kronos; incidents data from Intelex; and active employees from Workday. This metric is calculated using the following formula, the total number of Lost and Restricted Days cases reported during the month multiply by the OSHA scaling factor and divided by the total number of hours worked by all employees. The OSHA scaling factor is 200,000 and equals one hundred (100) employees working forty (40) hours per week, fifty (50) weeks per year.
OSHA Fatality | Data is gathered from Intelex. This metric is calculated as the sum of the number of work-related fatalities reported during the month.
OSHA Recordable Rate | Data is gathered from three (3) sources: hours worked from Kronos; incidents data from Intelex; and active employees from Workday. This metric is calculated using the following formula, the total number of OSHA Recordable injuries and illnesses cases reported during the month multiply by the OSHA scaling factor and divided by the total number of hours worked by all employees. The OSHA scaling factor is 200,000 and equals one hundred (100) employees working forty (40) hours per week, fifty (50) weeks per year.
12-Month Rolling OSHA DART Rate | Data is gathered from three (3) sources: hours worked from Kronos; incidents data from Intelex; and active employees from Workday. This metric is calculated by the total number of DART cases reported fiscal year-to-date multiply by the OSHA scaling factor and divided by the total number of hours worked fiscal year-to-date by all employees. The OSHA scaling factor is 200,000 and equals one hundred (100) employees working forty (40) hours per week, fifty (50) weeks per year.
12-Month Rolling OSHA Severity Rate | Data is gathered from three (3) sources: hours worked from Kronos; incidents data from Intelex; and active employees from Workday. This metric is calculated using the following formula, the total number of Lost and Restricted Days cases reported fiscal year-to-date multiply by the OSHA scaling factor and divided by the total number of hours worked by all employees fiscal year-to-date. The OSHA scaling factor is 200,000 and equals one hundred (100) employees working forty (40) hours per week, fifty (50) weeks per year.
12-Month Rolling OSHA Fatality Rate | Data is gathered from Intelex. This metric s calculated as the sum of the number of work-related fatalities reported fiscal year-to-date.
12-Month Rolling OSHA Recordable Rate | Data is gathered from three (3) sources: hours worked from Kronos; incidents data from Intelex; and active employees from Workday. This metric is calculated using the following formula, the total number of OSHA Recordable injuries and illnesses cases reported fiscal year-to-date multiply by the OSHA scaling factor and divided by the total number of hours worked by all employees fiscal year-to-date. The OSHA scaling factor is 200,000 and equals one hundred (100) employees working forty (40) hours per week, fifty (50) weeks per year.
Budgeted headcounts by employee type | Data is extracted from Oracle EBS LUMA Budget Online, using the Cost Center View - Labor Details Report. The metric represents the total budgeted number of employees.
Actual headcounts by employee type | Data is gathered from Workday, using the PREB Monthly Report, which generates an employee headcount report per month. The metric represents the total number of active employees during the period.
Turnover Rate | Data is gathered from Workday, using the Termination by Range of Dates Report. The metric is calculated by dividing the total number of terminations during the period by the total number of active employees at the end of the period.
Monthly CAIDI | Data is gathered from the Interruptions Database. The Customer Average Interruption Duration Index (CAIDI) metric is calculated by dividing the total outage duration for the average customer in a given period by the average number of interruptions per customer in a given period. The period used for calculation is per month. Formula: CAIDI = SAIDI/SAIFI
Operational expenses vs. budget | Data gathered from the spreadsheet Mth-Yr-Executive Summary. This metric is calculated by dividing the actual operating expenditures for a given fiscal year by the approved T&D operating budget for the same fiscal year, including 2% excess expenditures. Metric is reported as a fiscal year-to-date value.
Capital expenses vs. budget | Data gathered from the spreadsheet Mth-Yr-Executive Summary. This metric is calculated by dividing the actual capital expenses (Federally or Non Federally funded) for a given fiscal year by the approved budget (Federally or Non Federally funded) for the same fiscal year, including 2% excess expenditures. Metric is reported as a fiscal year-to-date value.
Number of customers by customer class | Data is gathered from the Customer Care & Billing System (CC&B) Report. The data is derived from the billing system; therefore, no modifications are required.
Monthly system sales by customer class | Data is gathered from the CC&B Report, Sales by Type Report, Fuel Consumption Report (as per data received from GeneraPR), and Invoices from Purchased Power Suppliers. Billing adjustments are performed aligned with the revenue recognition process that includes: the net unbilled and the riders for Fuel, Purchased Power, CILT, Subsidy, and Energy Efficiency. The results after adjustments are proportionally applied across all customer classes and to revenue types as registered.
Monthly sales by Municipality | Data is gathered from the CC&B Report and the Official Summary Sales of Electric Energy of LUMA Finance,. A data clean-up process is performed to reflect the official monthly sales for each municipality. For this metric, the Sales by customer class raw billed data totals is distributed proportionally by municipality and aligned according to the official Summary Sales of Electric Energy of LUMA Finance. The metric is calculated by dividing the monthly billing per municipality by the Total Monthly Billing and then multiplying by the Official Monthly Sales.
Monthly system peak | The data for this metric is gathered from the Operational Dispatch database; therefore, no modifications are required.
Monthly peak by customer class | N/A
Monthly peak by district | N/A
Cost of generation per customer (system) | GeneraPR provides the fuel purchase and consumption data. Using that data, LUMA prepares the Fuel Report and the Sales by Rate Report, which included the total numbers of customer using the system at the end of the month. LUMA also retrieves PREPA's monthly 725 Report, which includes the actual expenses data for all departments and all operating expense data identified as Generation. The metric is calculated by adding the Cost of Fuel, Shipping Cost, Purchased Fuel to Ecoeléctrica Costs, Excess Nomination and Operation and Management Generation costs, and dividing the result by total customers using the system at the end of the month.
Average revenue per kilowatt-hour sold | Data is gathered from the Official Summary Sales of Electric Energy of LUMA Finance, and the metric is calculated by dividing the Revenue by Class by Sales by Customer Class.
Purchased energy from thermal PPOA's | Data received from each Independent Power Producer (IPP) meter. A data validation process and meter calibration is performed monthly by LUMA. This metric is calculated by adding the hourly generation for each IPP to obtain the monthly purchased energy.
Cost of capacity purchased from thermal PPOA's | The contracted capacity is established in the IPP's agreements. Data is gathered from a dispatch report which includes the available capacity each IPP provided hourly during the month. This metric is calculated by dividing the total amount of capacity paid ($) by the contracted capacity of the IPP. A reconciliation process between LUMA and the IPPs is held monthly to make adjustments (if needed).
Cost of energy (base + excess) purchased from thermal PPOA's | Data is gathered from each IPP meter. This metric is calculated by dividing the total amount paid by the total purchased energy each IPP provided each hour per month, which is known as the Net Electrical Output (NEO).
Distribution line inspections | Data is gathered from two sources: the High-Level Assessments tracker and the Assessment Viewer App. A validation process is performed to confirm the entire feeder was assessed. The metric represents the total number of distribution lines (circuits) inspected during the period. Metric is reported as a Fiscal Year-to-Date value.
Transmission line inspections | Data is gathered from two sources: the Transmission Power Line Inspections (PLI) Tracker and the Transmission Reliability Work Assessments FY2025 tracker. A validation process is performed to confirm the entire line (breaker-to-breaker) was assessed. The metric represents the total number of transmission lines inspected during the period. Metric is reported as a Fiscal Year-to-Date value.
T&D substation inspections | Data is gathered from the Facility Assessment Dashboard file. A validation process is performed to remove duplicates of substations that were visited multiple times during the same month. The metric represents the total number of T&D substations inspected during the period. Metric is reported as a Fiscal Year-to-Date value.
Vegetation Maintenance Miles Completed | Data is gathered from internal database, which includes corrective, reactive, and preventive work orders for vegetation management. The metric is calculated by adding together the total number of vegetation maintenance miles completed along 230kV, 115kV, 38kV, and primary Distribution lines. Metric is reported as a Fiscal Year-to-Date value.
Monthly SAIDI Distribution | Data is gathered from the Interruptions Database. To determine the System Average Interruption Duration Index (SAIDI) Distribution, the Customer minutes of interruption (CMI) is computed and the System Customers Served (CN) is defined, considering distribution outage events (partial and total). CMI is calculated as the product of the customers interrupted during an event, times the duration, in minutes, of the event. CN is the value representing the total number of customers served by the utility in a reporting period. This metric is calculated by dividing the total duration of all distribution power outages experienced by all customers during a specific period (CMI) by the total number of customers served during that same period (CN). The period used for calculation is per month. Formula: SAIDI = ∑CMI/CN
Monthly SAIDI Transmission Substation | Data is gathered from the Interruptions Database. To determine the System Average Interruption Duration Index (SAIDI) Transmission Substation, the Customer minutes of interruption (CMI) is computed and the System Customers Served (CN) is defined, considering only transmission and substation outage events. CMI is calculated as the product of the customers interrupted during an event, times the duration, in minutes, of the event. CN is the value representing the total number of customers served by the utility in a reporting period. This metric is calculated by dividing the total duration of all transmission and substation power outages experienced by all customers during a specific period (CMI) by the total number of customers served during that same period (CN). The period used for calculation is per month. Formula:SAIDI = ∑CMI/CN
Monthly SAIDI (T&D) | Data gathered from the Interruptions Database. To determine the System Average Interruption Duration Index (SAIDI) Transmission and Distribution (T&D),the Customer minutes of interruption (CMI) is computed and the System Customers Served (CN) is defined, considering transmission, substation, and distribution outage events. CMI is calculated as the product of the customers interrupted during an event, times the duration, in minutes, of the event. CN is the value representing the total number of customers served by the utility in a reporting period. This metric is calculated by dividing the total duration of all power outages experienced by all customers during a specific period (CMI) by the total number of customers served during that same period (CN). The period used for calculation is per month. Formula:SAIDI = ∑CMI/CN
SAIDI (T&D) 12-month rolling average | Data gathered from the Interruptions Database. To determine the System Average Interruption Duration Index (SAIDI) Transmission and Distribution (T&D), the Customer minutes of interruption (CMI) is computed and the System Customers Served (CN) is defined, considering transmission, substation, and distribution outage events. CMI is calculated as the product of the customers interrupted during an event, times the duration, in minutes, of the event. CN is the value representing the total number of customers served by the utility in a reporting period. This metric is calculated by dividing the total duration of all power outages experienced by all customers during a specific period (CMI) by the total number of customers served during that same period (CN). The period used for calculation is Fiscal Year-to-Date (FYTD). Formula:SAIDI = ∑CMI/CN
Monthly SAIFI Distribution | Data gathered from the Interruptions Database. To determine the System Average Interruption Frequency Index (SAIFI) Distribution, the Customer interrupted (CI) is computed and the System Customers Served (CN) is defined, considering distribution outage events (partial and total). CI is calculated as the product of the customers interrupted during an event, times the duration, in minutes, of the event. CN is the value representing the total number of customers served by the utility in a reporting period. This metric is calculated by summing the product of the length of each interruption and the number of customers affected by that interruption for all sustained interruptions during a specific period (CI), then dividing by the total number of customers served (CN). The period used for calculation is per month. Formula: SAIFI = ∑CI/CN
Monthly SAIFI Transmission Substation | Data gathered from the Interruptions Database . To determine the System Average Interruption Frequency Index (SAIFI) Transmission Substation, the Customer interrupted (CI) is computed and the System Customers Served (CN) is defined, considering only transmission and substation outage events. CI is calculated as the product of the customers interrupted during an event, times the duration, in minutes, of the event. CN is the value representing the total number of customers served by the utility in a reporting period. This metric is calculated by summing the product of the length of each interruption and the number of customers affected by that interruption for all sustained interruptions during a specific period (CI), then dividing by the total number of customers served (CN). The period used for calculation is per month. Formula: SAIFI = ∑CI/CN
Monthly SAIFI (T&D) | Data gathered from the Interruptions Database. To determine the System Average Interruption Frequency Index (SAIFI) Transmission and Distribution (T&D), the Customer interrupted (CI) is computed and the System Customers Served (CN) is defined, considering transmission, substation, and distribution outage events. CI is calculated as the product of the customers interrupted during an event, times the duration, in minutes, of the event. CN is the value representing the total number of customers served by the utility in a reporting period. This metric is calculated by summing the product of the length of each interruption and the number of customers affected by that interruption for all sustained interruptions during a specific period (CI), then dividing by the total number of customers served (CN). The period used for calculation is per month. Formula: SAIFI = ∑CI/CN
SAIFI (T&D) 12-month rolling average | Data gathered from the Interruptions Database. To determine the System Average Interruption Frequency Index (SAIFI) Transmission and Distribution (T&D), the Customer interrupted (CI) is computed and the System Customers Served (CN) is defined, considering transmission, substation, and distribution outage events. CI is calculated as the product of the customers interrupted during an event, times the duration, in minutes, of the event. CN is the value representing the total number of customers served by the utility in a reporting period. This metric is calculated by summing the product of the length of each interruption and the number of customers affected by that interruption for all sustained interruptions during a specific period (CI), then dividing by the total number of customers served (CN). The period used for calculation is Fiscal Year-to-Date (FYTD). Formula: SAIFI = ∑CI/CN
Net monthly work orders balance | Data is gathered from the Outage Management System (OMS) and the Severant Trent Operational Resources Management System (STORMS). The metric is calculated by adding the number of work requests open in both systems at the end of the period. The prior quarter is restated based on a reconciliation.
Monthly MAIFI | N/A
MAIFI 12-month rolling average | N/A
Monthly CEMI | N/A
CEMI 12-month rolling average | N/A
Technical losses as % of net generation | Data is gathered from the CC&B Report and Generation (as per data received from GeneraPR). Technical losses are equal to the total Transmission System Energy, Distribution Substation Energy, and Primary Distribution and Secondary Distribution Losses. The percentage of technical losses are applied according to studies carried out by PREPA in mid-2000. Losses are determined based on the rolling accumulation of data over 12-months to mitigate the mismatch of billing cycles with the calendar month.
DSO (Days Sales Outstanding) | For DSO General Customers, data is gathered from the Finance Report Income Statement and Exhibit A: YTD Billed Revenue from the Income Statement per GAAP tab and YTD General Accounts Receivables (A/R) from the Exhibit A tab. For DSO Government Customers, data is gathered from the Finance Report Income Statement and Exhibit A and the Billed Sales and Collections Report: YTD Government A/R from Exhibit A tab and YTD Government Revenue from FY2025 tab. This metric is calculated by dividing the total amount receivables Fiscal Year-to-Date (FYTD) by the total credit sales FYTD and multiplying the result by the number of days in the period.
Overtime | Data retrieved monthly through the Splash Reporting Tool to gather Hourly Salary and Overtime expenses data. This metric represents the total overtime expenses divided by the total non-exempt base compensation expenses. Metric is reported as a fiscal year-to-date value.
Total number of calls received | Data is gathered from the Genesys system via the Queue Performance report. This metric is the sum of all calls received per month and represents the total number of interactions routed into the queue for an advisor to answer. Interactions counted towards this metrics are all inbound calls received through the following queues: Billing and Payments, Emergencies, Outages, and Service Orders.
Number of customer calls answered | Data is gathered from the Genesys system via the Queue Performance report. This metric is the sum of all calls answered per month and represents the total number of interactions answered by an advisor. Interactions counted towards this metrics are all inbound calls receive through the following queues: Billing and Payments, Emergencies, Outages, and Service Orders.
Percent of customer calls answered | Data is gathered from the Genesys system via the Queue Performance report. This metric is calculated by dividing the total number of calls answered by an advisor by the total number of calls received. Interactions counted towards this metrics are all inbound calls receive through the following queues: Billing and Payments, Emergencies, Outages, and Service Orders.
Call abandonment rate | Data gathered from the Genesys system via the Queue Performance report. This metric represents the percentage of offered interactions in which the customer disconnected before connecting with an agent. Interactions counted towards this metrics are all inbound calls offered in the following queues: Billing and Payments, Emergencies, Outages, and Service Orders. This metric is calculated by dividing the FYTD abandoned count by the FYTD offered count and then multiplying it by one hundred.
Average speed to answer | Data gathered from the Genesys system via the Queue Performance report. This metric represents the average amount of time an interaction waits in queue before an agent answers it. Interactions counted towards this metrics are all inbound calls receive through the following queues: Billing and Payments, Emergencies, Outages, and Service Orders. This metric is calculated by dividing the FYTD total amount of time that interactions wait on queue by the FYTD total count of calls received.
Wait time in Customer Service Centers | Data gathered from TurnosPR website. The report is generated by selecting the month and the offices. Once the report is generated, the data needed is provided as the average wait time, no further manipulation is required.
Number of Act 57 Claims Opened | Data gathered from the "Enlace Formulario Ley 57" Report from the Customer Care & Billing (CC&B) System. Once the total of objections registered is exported, a Pivot table is used to obtain the total per period. This metric represents the total Act 57 claims registered by month.
Average time to resolve billing disputes (Act 57 Claims) | Data gathered from the "Registro de Objeciones Ley 57 (2)" Report from the CC&B System. The time of closing for each billing dispute is computed by the difference in days from the day the objection was registered minus the day it was closed.; then a monthly average of days for all billing disputes is computed.
Customer Complaint Rate | Data gathered from the Puerto Rico Energy Bureau's (PREB) website. This metric measures the FYTD customer complaints registered with the PREB under NEPR-QR and NEPR-RV dockets. This metric is calculated by dividing the total number of complaints by the total utility customer population and multiplying the result by 100,000.
First Call Resolution | N/A
Number of customer complaints closed by class (Act 57 Claims) | Data gathered from the "Registro de Objeciones Ley 57 (2)" Report from the CC&B System. This metric is the total objections closed by month, distributed by customer class.
J.D. Power Customer Satisfaction Survey (Residential Customers) | Industry standard third-party customer satisfaction survey. Customer Satisfaction will be measured by surveys in four phases per year for residential customers. Data for this metric is gathered through J.D. Power online platform Power Source and survey results are published in March, June, September, and December. J.D. Power sends the online survey to 100,000 randomly selected customers with emails registered in the CC&B database. Values are reported as FYTD.
J.D. Power Customer Satisfaction Survey (Business Customers) | Industry standard third-party customer satisfaction survey. Customer Satisfaction will be measured by following up with surveys in two phases per year for business customers. Data for this metric is gathered through J.D. Power online platform Power Source and survey results are published in July and November J.D. Power sends the online survey to 10,000 randomly selected customers with emails registered in the CC&B database. Values are reported as FYTD.
Percent of customers on AMI | Data gathered from the CC&B system. This metric is calculated by dividing the total number of meters with Advanced Metering Infrastructure (AMI) by the total number of active customers.
Percent of customers billed | Data gathered from the CC&B system. This metric is calculated by dividing the total number of non-billed customers by the total number of active service agreements and the result then is subtracted from 100%.
Percent of bills estimated vs. read | Data gathered from the CC&B system. This metric is calculated by dividing the total number of meters estimated by the total number of meters read.
Percent of automatically-generated NTL leads found to be occurrences of theft | Data is gathered from the Energy Irregularities Office's Tracker. This metric is calculated by dividing the total number of field visits by the total number of cases found to be occurrences of theft.
Average time to respond to service and outage complaints | Data gathered from the CC&B system. To compute this metric, the reports are filtered to select the possible field works related to customers' request. This metric is calculated by the difference in days from the field activity creation date and the field activity completion date, then a monthly average is calculated.
Number of disconnections by customer class | Data gathered from the Monthly FA-COMPLETED-DATE-EDITED Report. This metric is the sum off all number of disconnections, distributed by customer class.
Number of disconnections by Area | Data gathered from the Monthly FA-ALL-STATUS_LAST_3_MONTHS Report. This metric is the sum of all the number of disconnections, distributed by area.
Number of customers enrolled in extended payment plans by class | Data gathered from the Monthly PP001 Report. This metric is the sum of all the number of customers enrolled in financial assistance plans, distributed by customer class.
Number of customers defaulting on extended payment plans by class | Data gathered from the Monthly PP001 Report. This metric is the sum of all the number of customers enrolled in financial assistance plans that have defaulted on their payments, distributed by customer class.
Number of customers completing extended payment plans by class | Data gathered from the Monthly PP001 Report. This metric is the sum of all the number of customers who have enrolled in financial assistance plans and have completed their payment plan, distributed by customer class.
Accounts Payable days outstanding | Data compiled from the Monthly Cash Flow, Monthy aging of vouchered accounts payable, and non payroll disbursements reports. This metric is calculated by the Total Accounts Payable (excluding disputed amounts) divided by the total amount paid per day (which is the total non payroll disbursements divided by the number of business days in the month).
Fleet out of service (system) | Data is gathered from the Fleet Management Software AssetWorks. The metric is calculated by dividing the total number of units out of service by the total number of active units.
Total available vehicles in service (system) | Data is gathered from the Fleet Management Software AssetWorks. The metric represents the total number of active units.
Fuel Expenditure vs Forecast | Data gathered from the Fuel Cost Adjustment (FCA) and Purchased Power Charge Adjustment (PPCA) forecasted results and the Fuel Report. The metric is calculated by dividing the actual fuel expenditure (actual costs plus barrel handling costs) by the forecasted costs. The result is then subtracted by 1 to expressed value as percentage.
MMBTU consumed vs. forecast | Data gathered from the Fuel Cost Adjustment (FCA) and Purchased Power Charge Adjustment (PPCA) forecasted results and the Fuel Report. The metric is calculated by dividing the actual consumption (MMBTU) by the forecasted consumption (MMBTU). The result is then subtracted by 1 to expressed value as percentage.
Number of curtailed hours from RPS-eligible capacity | Data is gathered from Operational Dispatch Database; therefore, no modifications are required.
Operational RPS-eligible capacity | Data provided by all generation projects that qualify under Puerto Rico's Renewable Portfolio Standards (RPS) requirements and have achieved their commercial operation date. This metric is calculated by adding the total nameplate capacity of all projects.
Contracted but not operational RPS-eligible capacity | Data provided by all generation projects that qualify under RPS requirements that have a signed Power Purchase Operating Agreement (PPOA) but have not achieved their commercial operation date, as confirmed by an executed Commercial Operation Date (COD) certificate. This metric is calculated by adding the total nameplate capacity of all projects.
Average delay in anticipated online date of RPS-eligible projects | This metric represents the average delay (in days) between the Guaranteed Commercial Operation Date and the actual COD achieved, based on a 12-month rolling basis.
Mean time to interconnect utility-scale RPS-eligible projects | N/A
NEM Project Activation Duration | Data is gathered from the "Portal Conexión LUMA" and "Portal de Radicaciones Electrónicas para Proyectos" (PREP LUMA) interfaces. The metric is calculated as the average duration in days, between the filling date of a complete application and the date when the Net Energy Metering (NEM) tariff is activated on the customer’s account, across all expedited projects activated during the fiscal year.
Average capacity factor of RPS-eligible capacity | This metric represents the ratio of the actual electricity output of the IPP each month relative to the maximum electricity output of the IPP over a period of time. This metric is calculated by dividing the NEO of each IPP by product of each IPP installed capacity and the number of hours of the corresponding month, expressed as a percentage.
Generation from RPS-eligible PPOA's (percent of sales) | Data gathered from the NEO, the Customer Care & Billing (CC&B) Report, Sales by Rate data, Fuel Consumption Report, and invoices from Purchased Power Suppliers. This metric is calculated by dividing the total hourly NEO of all RPS projects by the total system consumption, expressed as a percentage.
Generation from RPS-eligible PPOA's (by unit) | Data gathered from the NEO, which determines the Purchased Energy each IPP provided each hour per month. This metric represents the monthly total generation provided by all IPPs.
Total installed distributed generation capacity - Photovoltaic | Data is gathered from the "Portal Conexión LUMA" and PREP LUMA interphases and the Customer Care and Billing (CC&B) Report. NEM active customers data is retrieved from the CC&B report and is matched with the generation capacity retrieved from the sources. This metric is the sum of all installed generation capacity of Photovoltaic NEM projects during the period.
Total installed distributed generation capacity - Wind | Data is gathered from the "Portal Conexión LUMA" and PREP LUMA interphases and the CC&B Report. NEM active customers data is retrieved from the CC&B report and is match with the generation capacity retrieved from the sources. This metric is the sum of all the installed generation capacity of Wind NEM projects during the period.
Total number of distributed generation installations - Photovoltaic | Data is gathered from the "Portal Conexión LUMA" and PREP LUMA interphases and the CC&B Report. This metric is the sum of the number of photovoltaic facilities installed (active) across the system during the period.
Total number of distributed generation installations - Wind | Data is gathered from the "Portal Conexión LUMA" and PREP LUMA interphases and the CC&B Report. This metric is the sum of all the number of wind facilities installed (active) across the system during the period.
Total installed BESS capacity | Data is gathered from the "Portal Conexión LUMA" and PREP LUMA interphases extracting the Registered Projects and Equipment Report. Registered projects data is match with the battery capacity and municipality. This metric is the sum of all Battery Energy Storage Systems (BESS) installed capacity during the period.
Total number of BESS installations | Data is gathered from the "Portal Conexión LUMA" and PREP LUMA interphases, extracting the Registered Projects and Equipment Report. Registered projects data is match with its battery capacity and municipality. This metric is the sum of all BESS facilities installed during the period.
OSHA Fatality Rate | [See GenCo Methodology Tab]
Absenteeism | [See GenCo Methodology Tab]
Plant availability (system) | [See GenCo Methodology Tab]
Forced outages (system) | [See GenCo Methodology Tab]
Cost of generation (system total), excluding PPOA's gen | [See GenCo Methodology Tab]
Cost of generation (system: fuel) | [See GenCo Methodology Tab]
Cost of generation (system: O&M), excluding PPOA's gen) | [See GenCo Methodology Tab]
Cost of generation (by Plant Type) | [See GenCo Methodology Tab]
Monthly thermal generation (system), excluding PPOA's gen | [See GenCo Methodology Tab]
Monthly thermal generation (by plant) | [See GenCo Methodology Tab]
Average heat rate (system) | [See GenCo Methodology Tab]
Average heat rate (by plant) | [See GenCo Methodology Tab]
Plant availability (by plant) | [See GenCo Methodology Tab]
Forced outages (by plant) | [See GenCo Methodology Tab]
MMBTU consumed | [See GenCo Methodology Tab]
Average fuel price | [See GenCo Methodology Tab]
Average fuel price vs. forecast price | [See GenCo Methodology Tab]
Total Emissions (system) | [See GenCo Methodology Tab]
Emissions rates (system) | [See GenCo Methodology Tab]
Carbon intensity of fossil generation | [See GenCo Methodology Tab]

## GenCo Methodology
METRIC | CALCULATION METHODOLOGY
OSHA DART Rate | Formula: (Number of injuries and illnesses with days lost (absence) x 200,000)/Hours Worked
OSHA Severity Rate | Formula: (Number of injuries and illnesses x 200,000)/Hours Worked
OSHA Fatality | (Number of Deaths/Total Active Employees)
OSHA Recordable Rate | Formula: (Number of Injuries/Total Active Employees) x 100
Budgeted headcount by employee type | Formula: Exempt: The total sum of exempt employees planned by each leader. The indicated number of employees to take on the responsibility needs to meet relevant goals and challenges. Formula: Non-exempt: The total sum of non-exempt employees planned by each leader. The indicated number of employees to take on the responsibility required by their respective knowledge, skills, education, and business needs to meet relevant goals and challenges.
Actual headcounts by employee type | Formula: Exempt: Total sum of active classified as exempt. It also includes active employees who are on proactive leave. Excludes inactive exempt employees who are on protective leave. Excludes inactive exempt employees for whatever reason applies on payroll and records for the month being reported. The data is extracted from the human resources system – ADP. Formula: Non-exempt: Total sum of active employees classified as non-exempt, also includes active employees but on protective leave. Excludes inactive exempt employees for whatever reason applies based on payroll and records for the month being reported. Data is extracted from the human resources system – ADP.
Absenteeism | Formula: Hours classified as absentee within ADPs “Time data” system. The percentage is based on a comparison of the month by the period being reported. All employees (exempt and non-exempt) are included; the information is extracted from ADP.
Operational expenses vs. budget | Formula: This metric shows the actual operating expenses for a given Fiscal Year divided by the approved GenCo operating budget for the same Fiscal Year as incurred.
Capital expenses vs. budget | Formula: This metric shows the actual Federally or Non-Funded Capital expenses for a Fiscal Year, as incurred, divided by approved Capita/Budget: Federally or Non-Federally Funded for the same Fiscal Year.
Fleet out of service (system) | Formula: Fleet Out of Service (%) = (Total Vehicles Out of Services / Total Fleet Size) x 100 Where: • Total Vehicles Out of Service is the number of vehicles in the workshop for maintenance or repair at the end of each month (on the 30th or 31st) • Total Felet Size is the total number of vehicles available in each power plant.
Operational expense vs budget | Formula: This metric shows the actual oprating expenses for a given Fiscal Year divided by the approved GenCo operating budget for the same Fiscal Year as incurred
Capital expenses vs budget (Non-funded) | Formula: This metric shows the actual Non-Funded Capital expenses for a Fiscal Year, as incurred, divided by approved Budget for the same Fiscal year
Capital expenses vs budget (Federal) | Formula: This metric shows the actual Federally Capital expenses for a Fiscal Year, as incurred, divided by Projected Federal Funds for the same Fiscal year
Total available vehicles in service (system) | Total available Vehicles in Services = Total Fleet Size - Total Vehicles Out of Service Where: * Total Fleet Size is the total number of vehicles in the fleet. * Total Vehicles Out of Service is the number of vehicles that are currently not operational.
Plant availability (system) | Plant Availability (%) = ((Total Available Hours - Equivalent Unplanned Derated Hours) / Total Month Hours)) x 100
Plant availability (by plant) | Plant Availability (%) = ((Total Available Hours - Equivalent Unplanned Derated Hours) / Total Month Hours)) x 100
Forced outages (system) | Forced Outage Factor (FOF) % = (Forced Outages Hours / Total Month Hours) x 100
Forced outages (by plant) | Forced Outage Factor (FOF) % = (Forced Outages Hours / Total Month Hours) x 100
Monthly thermal generation (system) = | Sum of Total thermal generation
Monthly thermal generation (by plant) = | Total Fuel Consumption (MMBtu) / Heat Rate (MMBtu/kWh)
Average heat rate (system) = | Total Fuel Consumption (Btu) / Total Generation (kWh)
Average heat rate (by plant) = | Total Fuel Consumption (Btu) / Total Generation (kWh)
Average fuel price | Average Cost in MMBtu = Purchase of Fuel ($) / MMBtu
Average fuel price vs forecast price = | (Current Purchases - Budgeted Purchases) / Budgeted Purchases
Total Emissions (system) = | Sum per pollutant per unit of Fuel Consumption x Calorific value of the fuel used x AP42 Emission Factor of the pollutant. The formula inputs include: Fuel Consumption data from operations, reflecting the total fuel utilized; Calorific Value of Fuel, which is a fixed value assigned to each type of fuel of energy content assessment; AP42 Emission Factor, a fixed value per combustible determined by the EPA for accurate emissions qualification.