## KPI_FY 25-26
JULY 2025 | [16 empty] | AUGUST 2025 | [16 empty] | SEPTEMBER 2025 | [16 empty] | OCTOBER 2025 | [16 empty] | NOVEMBER 2025 | [16 empty] | DECEMBER 2025
MONTH HOURS: | 744 | [15 empty] | MONTH HOURS: | 744 | [15 empty] | MONTH HOURS: | 720 | [15 empty] | MONTH HOURS: | 744 | [15 empty] | MONTH HOURS: | 720 | [15 empty] | MONTH HOURS: | 744
PLANT | UNIT | Available Hours | Service Hours | Reserve Shutdown Hours | Forced Outage Hours | Forced Outage Factor | Planned Outage Hours | Planned Outage Factor | Maintenance Outage Hours | Maintenance Outage Factor | Equivalent Unplanned Derated Hours | Equivalent Availability Factor | Capacity Factor | Gross Generation | Nameplate Capacity | APT Capacity | PLANT | UNIT | Available Hours | Service Hours | Reserve Shutdown Hours | Forced Outage Hours | Forced Outage Factor | Planned Outage Hours | Planned Outage Factor | Maintenance Outage Hours | Maintenance Outage Factor | Equivalent Unplanned Derated Hours | Equivalent Availability Factor | Capacity Factor | Gross Generation | Nameplate Capacity | APT Capacity | PLANT | UNIT | Available Hours | Service Hours | Reserve Shutdown Hours | Forced Outage Hours | Forced Outage Factor | Planned Outage Hours | Planned Outage Factor | Maintenance Outage Hours | Maintenance Outage Factor | Equivalent Unplanned Derated Hours | Equivalent Availability Factor | Capacity Factor | Gross Generation | Nameplate Capacity | APT Capacity | PLANT | UNIT | Available Hours | Service Hours | Reserve Shutdown Hours | Forced Outage Hours | Forced Outage Factor | Planned Outage Hours | Planned Outage Factor | Maintenance Outage Hours | Maintenance Outage Factor | Equivalent Unplanned Derated Hours | Equivalent Availability Factor | Capacity Factor | Gross Generation | Nameplate Capacity | APT Capacity | PLANT | UNIT | Available Hours | Service Hours | Reserve Shutdown Hours | Forced Outage Hours | Forced Outage Factor | Planned Outage Hours | Planned Outage Factor | Maintenance Outage Hours | Maintenance Outage Factor | Equivalent Unplanned Derated Hours | Equivalent Availability Factor | Capacity Factor | Gross Generation | Nameplate Capacity | APT Capacity | PLANT | UNIT | Available Hours | Service Hours | Reserve Shutdown Hours | Forced Outage Hours | Forced Outage Factor | Planned Outage Hours | Planned Outage Factor | Maintenance Outage Hours | Maintenance Outage Factor | Equivalent Unplanned Derated Hours | Equivalent Availability Factor | Capacity Factor | Gross Generation | Nameplate Capacity | APT Capacity
SAN | CT 5 | 726.4 | 726.4 | 0 | 0 | 0% | 0 | 0% | 17.6 | 2.366% | 57.773 | 89.87% | 82.42% | 93816 | 160 | 153 | SAN | CT 5 | 667.4 | 667.4 | 0 | 0 | 0% | 0 | 0% | 76.6 | 10.3% | 0 | 89.7% | 72.68% | 82735 | 160 | 153 | SAN | CT 5 | 653.83 | 653.83 | 0 | 18.7 | 2.597% | 0 | 0% | 47.47 | 6.593% | 0 | 90.81% | 76.11% | 83848 | 160 | 153 | SAN | CT 5 | 656.1 | 656.1 | 0 | 87.9 | 11.81% | 0 | 0% | 0 | 0% | 35.99 | 83.35% | 73.8% | 84004 | 160 | 153 | SAN | CT 5 | 432.8 | 432.8 | 0 | 264.1 | 36.68% | 0 | 0% | 23.1 | 3.208% | 7.96 | 59.01% | 50.16% | 55261 | 160 | 153 | SAN | CT 5 | 198.6 | 175.72 | 22.88 | 545.4 | 73.31% | 0 | 0% | 0 | 0% | 14.91 | 24.69% | 19.08% | 21719 | 160 | 153
JUAN | ST 5 | 724.9 | 724.9 | 0 | 0 | 0% | 0 | 0% | 19.1 | 2.567% | 48.165 | 90.96% | 81.02% | 31345 | 60 | 52 | JUAN | ST 5 | 656.5 | 656.5 | 0 | 6.1 | 0.8199% | 0 | 0% | 81.4 | 10.94% | 0 | 88.24% | 75.27% | 29122 | 60 | 52 | JUAN | ST 5 | 636.9 | 636.9 | 0 | 21.2 | 2.944% | 0 | 0% | 61.9 | 8.597% | 0 | 88.46% | 78.83% | 29514 | 60 | 52 | JUAN | ST 5 | 647.9 | 647.9 | 0 | 96.1 | 12.92% | 0 | 0% | 0 | 0% | 32.96 | 82.65% | 74.3% | 28747 | 60 | 52 | JUAN | ST 5 | 424.8 | 424.8 | 0 | 264.4 | 36.72% | 0 | 0% | 30.8 | 4.278% | 0 | 59% | 51.74% | 19373 | 60 | 52 | JUAN | ST 5 | 182.32 | 151.64 | 30.68 | 561.68 | 75.49% | 0 | 0% | 0 | 0% | 59.09 | 16.56% | 16.49% | 6381 | 60 | 52
| CT 6 | 610.1 | 550 | 60.1 | 133.9 | 18% | 0 | 0% | 0 | 0% | 3.568 | 81.52% | 72.63% | 75655 | 160 | 140 |  | CT 6 | 360.7 | 300.6 | 60.1 | 383.3 | 51.52% | 0 | 0% | 0 | 0% | 0 | 48.48% | 51.38% | 53514 | 160 | 140 |  | CT 6 | 583.7 | 581.3 | 2.4 | 0 | 0% | 0 | 0% | 136.3 | 18.93% | 0 | 81.07% | 78.63% | 79256 | 160 | 140 |  | CT 6 | 722.7 | 722.7 | 0 | 21.3 | 2.863% | 0 | 0% | 0 | 0% | 31.74 | 92.87% | 90.78% | 94559 | 160 | 140 |  | CT 6 | 718.5 | 718.5 | 0 | 1.5 | 0.2083% | 0 | 0% | 0 | 0% | 0 | 99.79% | 93.21% | 93952 | 160 | 140 |  | CT 6 | 368.62 | 359.82 | 8.8 | 175 | 23.52% | 200.38 | 26.93% | 0 | 0% | 0 | 49.55% | 47.14% | 49106 | 160 | 140
| ST 6 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 60 | 52 |  | ST 6 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 60 | 52 |  | ST 6 | 0 | 0 | 0 | 0 | 0% | 720 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 60 | 52 |  | ST 6 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 60 | 52 |  | ST 6 | 0 | 0 | 0 | 0 | 0% | 720 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 60 | 52 |  | ST 6 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 60 | 52
| 7 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 100 | 100 |  | 7 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 100 | 100 |  | 7 | 0 | 0 | 0 | 0 | 0% | 720 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 100 | 100 |  | 7 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 100 | 100 |  | 7 | 0 | 0 | 0 | 0 | 0% | 720 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 100 | 100 |  | 7 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 100 | 100
| 9 | 645.7 | 645.7 | 0 | 30.7 | 4.126% | 0 | 0% | 67.6 | 9.086% | 21.804 | 83.86% | 63.14% | 46973 | 100 | 100 |  | 9 | 730.5 | 730.5 | 0 | 13.5 | 1.815% | 0 | 0% | 0 | 0% | 0 | 98.19% | 74.17% | 55182 | 100 | 100 |  | 9 | 623.05 | 623.05 | 0 | 96.95 | 13.47% | 0 | 0% | 0 | 0% | 42.48 | 80.63% | 59.14% | 42580 | 100 | 100 |  | 9 | 744 | 744 | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 137.29 | 81.55% | 74.53% | 55447 | 100 | 100 |  | 9 | 720 | 720 | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 129.6 | 82% | 71.02% | 51136 | 100 | 100 |  | 9 | 655.37 | 655.37 | 0 | 0 | 0% | 0 | 0% | 88.63 | 11.91% | 131.07 | 70.47% | 62.24% | 46310 | 100 | 100
| Total | 2707.1 | 2647 | 60.1 | 164.6 | 4.912% | 1488 | 25.46% | 104.3 | 2.352% | 131.31 | 64.48% | 55.79% | 247789 | 640 | 597 |  | Total | 2415.1 | 2355 | 60.1 | 402.9 | 12.46% | 1488 | 25.46% | 158 | 3.592% | 0 | 58.49% | 49.66% | 220553 | 640 | 597 |  | Total | 2497.48 | 2495.08 | 2.4 | 136.85 | 3.178% | 1440 | 25.46% | 245.67 | 6.878% | 42.48 | 63.5% | 54.72% | 235198 | 640 | 597 |  | Total | 2770.7 | 2770.7 | 0 | 205.3 | 4.824% | 1488 | 25.46% | 0 | 0% | 237.98 | 64% | 59.16% | 262757 | 640 | 597 |  | Total | 2296.1 | 2296.1 | 0 | 530 | 12.65% | 1440 | 25.46% | 53.9 | 1.195% | 137.56 | 57.4% | 51.12% | 219722 | 640 | 597 |  | Total | 1404.91 | 1342.55 | 62.36 | 1282.08 | 30.88% | 1688.38 | 31.78% | 88.63 | 1.995% | 205.07 | 31.19% | 27.81% | 123516 | 640 | 597
PALO | 3 | 739.33 | 739.33 | 0 | 4.67 | 0.6277% | 0 | 0% | 0 | 0% | 271.25 | 62.91% | 65.96% | 87348 | 216 | 178 | PALO | 3 | 744 | 744 | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 296.22 | 60.19% | 66.97% | 88691 | 216 | 178 | PALO | 3 | 704.52 | 704.52 | 0 | 15.48 | 2.15% | 0 | 0% | 0 | 0% | 314.11 | 54.22% | 56.81% | 72802 | 216 | 178 | PALO | 3 | 640.45 | 640.45 | 0 | 103.55 | 13.92% | 0 | 0% | 0 | 0% | 264.55 | 50.52% | 53.92% | 71413 | 216 | 178 | PALO | 3 | 628.18 | 628.18 | 0 | 91.82 | 12.75% | 0 | 0% | 0 | 0% | 206.5 | 58.57% | 55.87% | 71599 | 216 | 178 | PALO | 3 | 744 | 660 | 84 | 0 | 0% | 0 | 0% | 0 | 0% | 212.99 | 71.37% | 60.88% | 80621 | 216 | 178
SECO | 4 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 216 | 216 | SECO | 4 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 216 | 216 | SECO | 4 | 113.88 | 113.88 | 0 | 606.12 | 84.18% | 0 | 0% | 0 | 0% | 66.84 | 6.533% | 5.092% | 7919 | 216 | 216 | SECO | 4 | 649.99 | 649.99 | 0 | 94.01 | 12.64% | 0 | 0% | 0 | 0% | 193.48 | 61.36% | 52.7% | 84690 | 216 | 216 | SECO | 4 | 480.92 | 394.44 | 86.48 | 169.45 | 23.53% | 0 | 0% | 69.63 | 9.671% | 150.4 | 45.91% | 23.24% | 36146 | 216 | 216 | SECO | 4 | 719.37 | 692.87 | 26.5 | 24.63 | 3.31% | 0 | 0% | 0 | 0% | 181.51 | 72.29% | 49.89% | 80169.67 | 216 | 216
| Total | 739.33 | 739.33 | 0 | 748.67 | 55.11% | 0 | 0% | 0 | 0% | 271.25 | 28.42% | 29.8% | 87348 | 432 | 394 |  | Total | 744 | 744 | 0 | 744 | 54.82% | 0 | 0% | 0 | 0% | 296.22 | 27.19% | 30.26% | 88691 | 432 | 394 |  | Total | 818.4 | 818.4 | 0 | 621.6 | 47.12% | 0 | 0% | 0 | 0% | 380.95 | 28.08% | 28.45% | 80721 | 432 | 394 |  | Total | 1290.44 | 1290.44 | 0 | 197.56 | 13.22% | 0 | 0% | 0 | 0% | 458.03 | 56.46% | 53.25% | 156103 | 432 | 394 |  | Total | 1109.1 | 1022.62 | 86.48 | 261.27 | 18.66% | 0 | 0% | 69.63 | 5.302% | 356.9 | 51.63% | 37.98% | 107745 | 432 | 394 |  | Total | 1463.37 | 1352.87 | 110.5 | 24.63 | 1.815% | 0 | 0% | 0 | 0% | 394.5 | 71.88% | 54.85% | 160790.67 | 432 | 394
COSTA | 5 | 628.75 | 628.75 | 0 | 115.25 | 15.49% | 0 | 0% | 0 | 0% | 71.64 | 74.88% | 69.09% | 179910 | 410 | 350 | COSTA | 5 | 744 | 744 | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 87.57% | 228030 | 410 | 350 | COSTA | 5 | 720 | 720 | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 28.92 | 95.98% | 83.96% | 211590 | 410 | 350 | COSTA | 5 | 670.7 | 670.7 | 0 | 73.3 | 9.852% | 0 | 0% | 0 | 0% | 6.8 | 89.23% | 84.02% | 218790 | 410 | 350 | COSTA | 5 | 720 | 720 | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 79.52% | 200400 | 410 | 350 | COSTA | 5 | 736.45 | 621.45 | 115 | 0 | 0% | 0 | 0% | 7.55 | 1.015% | 0 | 98.99% | 66.08% | 172070 | 410 | 350
SUR | 6 | 744 | 744 | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 348.17 | 53.2% | 66.92% | 174250 | 410 | 350 | SUR | 6 | 646.55 | 646.55 | 0 | 97.45 | 13.1% | 0 | 0% | 0 | 0% | 49.49 | 80.25% | 71.09% | 185120 | 410 | 350 | SUR | 6 | 655.21 | 655.21 | 0 | 64.79 | 8.999% | 0 | 0% | 0 | 0% | 28.75 | 87.01% | 71.73% | 180760 | 410 | 350 | SUR | 6 | 744 | 744 | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 152.87 | 79.45% | 74.73% | 194590 | 410 | 350 | SUR | 6 | 651.05 | 651.05 | 0 | 68.95 | 9.576% | 0 | 0% | 0 | 0% | 58.85 | 82.25% | 66.84% | 168430 | 410 | 350 | SUR | 6 | 645.05 | 645.05 | 0 | 98.95 | 13.3% | 0 | 0% | 0 | 0% | 10.32 | 85.31% | 66.32% | 172700 | 410 | 350
| Total | 1372.75 | 1372.75 | 0 | 115.25 | 7.745% | 0 | 0% | 0 | 0% | 419.81 | 64.04% | 68% | 354160 | 820 | 700 |  | Total | 1390.55 | 1390.55 | 0 | 97.45 | 6.549% | 0 | 0% | 0 | 0% | 49.49 | 90.12% | 79.33% | 413150 | 820 | 700 |  | Total | 1375.21 | 1375.21 | 0 | 64.79 | 4.499% | 0 | 0% | 0 | 0% | 57.67 | 91.5% | 77.85% | 392350 | 820 | 700 |  | Total | 1414.7 | 1414.7 | 0 | 73.3 | 4.926% | 0 | 0% | 0 | 0% | 159.67 | 84.34% | 79.37% | 413380 | 820 | 700 |  | Total | 1371.05 | 1371.05 | 0 | 68.95 | 4.788% | 0 | 0% | 0 | 0% | 58.85 | 91.12% | 73.18% | 368830 | 820 | 700 |  | Total | 1381.5 | 1266.5 | 115 | 98.95 | 6.65% | 0 | 0% | 7.55 | 0.5074% | 10.32 | 92.15% | 66.2% | 344770 | 820 | 700
AGUIRRE | 1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 450 | 450 | AGUIRRE | 1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 450 | 450 | AGUIRRE | 1 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 450 | 450 | AGUIRRE | 1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 450 | 450 | AGUIRRE | 1 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 450 | 450 | AGUIRRE | 1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 450 | 450
| 2 | 591.52 | 591.52 | 0 | 152.48 | 20.49% | 0 | 0% | 0 | 0% | 0 | 79.51% | 56.7% | 147640 | 450 | 350 |  | 2 | 629.51 | 629.51 | 0 | 114.49 | 15.39% | 0 | 0% | 0 | 0% | 139.62 | 65.85% | 55.58% | 144740 | 450 | 350 |  | 2 | 717.63 | 717.63 | 0 | 2.37 | 0.3292% | 0 | 0% | 0 | 0% | 102.2 | 85.48% | 71.76% | 180840 | 450 | 350 |  | 2 | 608.95 | 608.95 | 0 | 135.05 | 18.15% | 0 | 0% | 0 | 0% | 0 | 81.85% | 59.93% | 156060 | 450 | 350 |  | 2 | 636.07 | 636.07 | 0 | 83.93 | 11.66% | 0 | 0% | 0 | 0% | 181.7 | 63.11% | 64.89% | 163525 | 450 | 350 |  | 2 | 472.67 | 393.05 | 79.62 | 171.85 | 23.1% | 0 | 0% | 99.48 | 13.37% | 170.3 | 40.64% | 37.66% | 98055 | 450 | 350
| Total | 591.52 | 591.52 | 0 | 896.48 | 65.22% | 0 | 0% | 0 | 0% | 0 | 34.78% | 24.81% | 147640 | 900 | 800 |  | Total | 629.51 | 629.51 | 0 | 858.49 | 62.98% | 0 | 0% | 0 | 0% | 139.62 | 28.81% | 24.32% | 144740 | 900 | 800 |  | Total | 717.63 | 717.63 | 0 | 722.37 | 56.39% | 0 | 0% | 0 | 0% | 102.2 | 37.4% | 31.4% | 180840 | 900 | 800 |  | Total | 608.95 | 608.95 | 0 | 879.05 | 64.19% | 0 | 0% | 0 | 0% | 0 | 35.81% | 26.22% | 156060 | 900 | 800 |  | Total | 636.07 | 636.07 | 0 | 803.93 | 61.35% | 0 | 0% | 0 | 0% | 181.7 | 27.61% | 28.39% | 163525 | 900 | 800 |  | Total | 472.67 | 393.05 | 79.62 | 915.85 | 66.36% | 0 | 0% | 99.48 | 5.85% | 170.3 | 17.78% | 16.47% | 98055 | 900 | 800
| Total Baseloads | 5410.7 | 5350.6 | 60.1 | 1925 | 33.01% | 1488 | 6.102% | 104.3 | 0.5636% | 822.37 | 49.12% | 45.16% | 836937 | 2792 | 2491 |  | Total Baseloads | 5179.16 | 5119.06 | 60.1 | 2102.84 | 33.72% | 1488 | 6.102% | 158 | 0.8608% | 485.33 | 52.9% | 46.79% | 867134 | 2792 | 2491 |  | Total Baseloads | 5408.72 | 5406.32 | 2.4 | 1545.61 | 27.59% | 1440 | 6.102% | 245.67 | 1.648% | 583.3 | 57.38% | 49.57% | 889109 | 2792 | 2491 |  | Total Baseloads | 6084.79 | 6084.79 | 0 | 1355.21 | 25.25% | 1488 | 6.102% | 0 | 0% | 855.68 | 59.47% | 53.33% | 988300 | 2792 | 2491 |  | Total Baseloads | 5412.32 | 5325.84 | 86.48 | 1664.15 | 27.03% | 1440 | 6.102% | 123.53 | 1.125% | 735.01 | 56.4% | 47.94% | 859822 | 2792 | 2491 |  | Total Baseloads | 4722.45 | 4354.97 | 367.48 | 2321.51 | 30.87% | 1688.38 | 7.616% | 195.66 | 2.5% | 780.19 | 50.45% | 39.23% | 727131.67 | 2792 | 2491
AGUIRRE CC | V-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 96 | 96 | AGUIRRE CC | V-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 96 | 96 | AGUIRRE CC | V-1 | 27.3 | 0 | 27.3 | 692.7 | 96.21% | 0 | 0% | 0 | 0% | 0 | 3.792% | 0% | 0 | 96 | 96 | AGUIRRE CC | V-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 96 | 96 | AGUIRRE CC | V-1 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 96 | 96 | AGUIRRE CC | V-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 96 | 96
| 1-1 | 744 | 298 | 446 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 36.97% | 13752 | 50 | 50 |  | 1-1 | 741.3 | 393 | 348.3 | 2.7 | 0.3629% | 0 | 0% | 0 | 0% | 0 | 99.64% | 34.46% | 12818 | 50 | 50 |  | 1-1 | 720 | 252 | 468 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 22.27% | 8017 | 50 | 50 |  | 1-1 | 744 | 510 | 234 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 44.95% | 16722 | 50 | 50 |  | 1-1 | 699.2 | 427 | 272.2 | 20.8 | 2.889% | 0 | 0% | 0 | 0% | 0 | 97.11% | 39.57% | 14247 | 50 | 50 |  | 1-1 | 688.9 | 241 | 447.9 | 0 | 0% | 55.1 | 7.406% | 0 | 0% | 0 | 92.59% | 21.52% | 8007 | 50 | 50
| 1-2 | 742.8 | 338 | 404.8 | 1.2 | 0.1613% | 0 | 0% | 0 | 0% | 0 | 99.84% | 29.71% | 11051 | 50 | 50 |  | 1-2 | 729.5 | 335 | 394.5 | 14.5 | 1.949% | 0 | 0% | 0 | 0% | 0 | 98.05% | 28.95% | 10771 | 50 | 50 |  | 1-2 | 718.1 | 176 | 542.1 | 1.9 | 0.2639% | 0 | 0% | 0 | 0% | 0 | 99.74% | 15.41% | 5547 | 50 | 50 |  | 1-2 | 727.5 | 425 | 302.5 | 16.5 | 2.218% | 0 | 0% | 0 | 0% | 0 | 97.78% | 36.86% | 13713 | 50 | 50 |  | 1-2 | 720 | 366 | 354 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 32.71% | 11774 | 50 | 50 |  | 1-2 | 734.7 | 200 | 534.7 | 9.3 | 1.25% | 0 | 0% | 0 | 0% | 0 | 98.75% | 16.52% | 6146 | 50 | 50
| 1-3 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 50 | 50 |  | 1-3 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 50 | 50 |  | 1-3 | 0 | 0 | 0 | 0 | 0% | 720 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 50 | 50 |  | 1-3 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 50 | 50 |  | 1-3 | 0 | 0 | 0 | 0 | 0% | 720 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 50 | 50 |  | 1-3 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 50 | 50
| 1-4 | 488.3 | 273 | 215.3 | 23.8 | 3.199% | 231.9 | 31.17% | 0 | 0% | 0 | 65.63% | 24.63% | 9164 | 50 | 50 |  | 1-4 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 50 | 50 |  | 1-4 | 0 | 0 | 0 | 0 | 0% | 720 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 50 | 50 |  | 1-4 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 50 | 50 |  | 1-4 | 0 | 0 | 0 | 0 | 0% | 720 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 50 | 50 |  | 1-4 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 50 | 50
| V-2 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 96 | 96 |  | V-2 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 96 | 96 |  | V-2 | 0 | 0 | 0 | 0 | 0% | 720 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 96 | 96 |  | V-2 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 96 | 96 |  | V-2 | 0 | 0 | 0 | 0 | 0% | 720 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 96 | 96 |  | V-2 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 96 | 96
| 2-1 | 744 | 424.7 | 319.3 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 37.26% | 13859 | 50 | 50 |  | 2-1 | 690.6 | 397.5 | 293.1 | 53.4 | 7.177% | 0 | 0% | 0 | 0% | 0 | 92.82% | 34.19% | 12720 | 50 | 50 |  | 2-1 | 720 | 297.6 | 422.4 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 26.08% | 9389 | 50 | 50 |  | 2-1 | 450.1 | 322.9 | 127.2 | 293.9 | 39.5% | 0 | 0% | 0 | 0% | 0 | 60.5% | 28.6% | 10638 | 50 | 50 |  | 2-1 | 707.5 | 397.8 | 309.7 | 0 | 0% | 0 | 0% | 12.5 | 1.736% | 0 | 98.26% | 35.3% | 12709 | 50 | 50 |  | 2-1 | 710.3 | 259.7 | 450.6 | 33.7 | 4.53% | 0 | 0% | 0 | 0% | 0 | 95.47% | 23.38% | 8699 | 50 | 50
| 2-2 | 744 | 453.3 | 290.7 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 39.52% | 14702 | 50 | 50 |  | 2-2 | 707.8 | 424.4 | 283.4 | 36.2 | 4.866% | 0 | 0% | 0 | 0% | 0 | 95.13% | 36.43% | 13551 | 50 | 50 |  | 2-2 | 718.1 | 242 | 476.1 | 1.9 | 0.2639% | 0 | 0% | 0 | 0% | 0 | 99.74% | 20.93% | 7533 | 50 | 50 |  | 2-2 | 638.2 | 293.8 | 344.4 | 105.8 | 14.22% | 0 | 0% | 0 | 0% | 0 | 85.78% | 25.09% | 9335 | 50 | 50 |  | 2-2 | 581.6 | 320.7 | 260.9 | 125.9 | 17.49% | 0 | 0% | 12.5 | 1.736% | 0 | 80.78% | 28.2% | 10152 | 50 | 50 |  | 2-2 | 722.4 | 314.9 | 407.5 | 21.6 | 2.903% | 0 | 0% | 0 | 0% | 0 | 97.1% | 27.6% | 10267 | 50 | 50
| 2-3 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 50 | 50 |  | 2-3 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 50 | 50 |  | 2-3 | 0 | 0 | 0 | 0 | 0% | 720 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 50 | 50 |  | 2-3 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 50 | 50 |  | 2-3 | 0 | 0 | 0 | 0 | 0% | 720 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 50 | 50 |  | 2-3 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0 | 50 | 50
| 2-4 | 687.6 | 316.6 | 371 | 56.4 | 7.581% | 0 | 0% | 0 | 0% | 0 | 92.42% | 28.2% | 10491 | 50 | 50 |  | 2-4 | 660.5 | 321.3 | 339.2 | 83.5 | 11.22% | 0 | 0% | 0 | 0% | 0 | 88.78% | 27.08% | 10075 | 50 | 50 |  | 2-4 | 720 | 213.9 | 506.1 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 19.65% | 7074 | 50 | 50 |  | 2-4 | 744 | 464.1 | 279.9 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 41.41% | 15406 | 50 | 50 |  | 2-4 | 513 | 334 | 179 | 0 | 0% | 207 | 28.75% | 0 | 0% | 0 | 71.25% | 30.71% | 11057 | 50 | 50 |  | 2-4 | 571.7 | 146.4 | 425.3 | 96.2 | 12.93% | 76.1 | 10.23% | 0 | 0% | 0 | 76.84% | 12.74% | 4738 | 50 | 50
| Total | 4150.7 | 2103.6 | 2047.1 | 825.4 | 17.14% | 2463.9 | 35.74% | 0 | 0% | 0 | 47.12% | 16.58% | 73019 | 592 | 592 |  | Total | 3529.7 | 1871.2 | 1658.5 | 934.3 | 18.38% | 2976 | 41.55% | 0 | 0% | 0 | 40.07% | 13.61% | 59935 | 592 | 592 |  | Total | 3623.5 | 1181.5 | 2442 | 696.5 | 15.65% | 2880 | 41.55% | 0 | 0% | 0 | 42.8% | 8.812% | 37560 | 592 | 592 |  | Total | 3303.8 | 2015.8 | 1288 | 1160.2 | 20.94% | 2976 | 41.55% | 0 | 0% | 0 | 37.5% | 14.94% | 65814 | 592 | 592 |  | Total | 3221.3 | 1845.5 | 1375.8 | 866.7 | 17.94% | 3087 | 43.98% | 25 | 0.2933% | 0 | 37.79% | 14.06% | 59939 | 592 | 592 |  | Total | 3428 | 1162 | 2266 | 904.8 | 18.04% | 3107.2 | 43.04% | 0 | 0% | 0 | 38.91% | 8.595% | 37857 | 592 | 592
PALO | 1-1 | 504 | 128.6 | 375.4 | 240 | 32.26% | 0 | 0% | 0 | 0% | 0 | 67.74% | 14.7% | 2297 | 21 | 21 | PALO | 1-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 21 | 21 | PALO | 1-1 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 21 | 21 | PALO | 1-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 21 | 21 | PALO | 1-1 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 21 | 21 | PALO | 1-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 21 | 21
SECO | 1-2 | 744 | 213.44 | 530.56 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 24.59% | 3842 | 21 | 21 | SECO | 1-2 | 744 | 180.76 | 563.24 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 24.85% | 3882 | 21 | 21 | SECO | 1-2 | 717.2 | 107.6 | 609.6 | 2.8 | 0.3889% | 0 | 0% | 0 | 0% | 0 | 99.61% | 13.04% | 1972 | 21 | 21 | SECO | 1-2 | 744 | 275.3 | 468.7 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 33.12% | 5175 | 21 | 21 | SECO | 1-2 | 698.5 | 205.3 | 493.2 | 21.5 | 2.986% | 0 | 0% | 0 | 0% | 0 | 97.01% | 25.67% | 3882 | 21 | 21 | SECO | 1-2 | 744 | 131.6 | 612.4 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 15.85% | 2476 | 21 | 21
| 2-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 21 | 21 |  | 2-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 21 | 21 |  | 2-1 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 21 | 21 |  | 2-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 21 | 21 |  | 2-1 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 21 | 21 |  | 2-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 21 | 21
| Total | 1248 | 342.04 | 905.96 | 984 | 44.09% | 0 | 0% | 0 | 0% | 0 | 55.91% | 13.1% | 6139 | 63 | 63 |  | Total | 744 | 180.76 | 563.24 | 1488 | 66.67% | 0 | 0% | 0 | 0% | 0 | 33.33% | 8.282% | 3882 | 63 | 63 |  | Total | 717.2 | 107.6 | 609.6 | 1442.8 | 66.8% | 0 | 0% | 0 | 0% | 0 | 33.2% | 4.347% | 1972 | 63 | 63 |  | Total | 744 | 275.3 | 468.7 | 1488 | 66.67% | 0 | 0% | 0 | 0% | 0 | 33.33% | 11.04% | 5175 | 63 | 63 |  | Total | 698.5 | 205.3 | 493.2 | 1461.5 | 67.66% | 0 | 0% | 0 | 0% | 0 | 32.34% | 8.558% | 3882 | 63 | 63 |  | Total | 744 | 131.6 | 612.4 | 1488 | 66.67% | 0 | 0% | 0 | 0% | 0 | 33.33% | 5.282% | 2476 | 63 | 63
YABUCOA | 1-2 | 744 | 117.8 | 626.2 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 15.89% | 1773 | 21 | 15 | YABUCOA | 1-2 | 744 | 164.8 | 579.2 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 22.2% | 2477 | 21 | 15 | YABUCOA | 1-2 | 720 | 68 | 652 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | #REF! | 1019 | 21 | 15 | YABUCOA | 1-2 | 744 | 226.6 | 517.4 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 30.51% | 3405 | 21 | 15 | YABUCOA | 1-2 | 720 | 185.7 | 534.3 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 25.84% | 2791 | 21 | 15 | YABUCOA | 1-2 | 744 | 101.9 | 642.1 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 13.74% | 1533 | 21 | 15
| Total | 744 | 117.8 | 626.2 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 15.89% | 1773 | 21 | 15 |  | Total | 744 | 164.8 | 579.2 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 22.2% | 2477 | 21 | 15 |  | Total | 720 | 68 | 652 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | #REF! | 1019 | 21 | 15 |  | Total | 744 | 226.6 | 517.4 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 30.51% | 3405 | 21 | 15 |  | Total | 720 | 185.7 | 534.3 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 25.84% | 2791 | 21 | 15 |  | Total | 744 | 101.9 | 642.1 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 13.74% | 1533 | 21 | 15
JOBOS | 1-2 | 744 | 169.1 | 574.9 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 21.69% | 3227 | 21 | 20 | JOBOS | 1-2 | 744 | 169.7 | 574.3 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 21.92% | 3261 | 21 | 20 | JOBOS | 1-2 | 720 | 79 | 641 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | #REF! | 1441 | 21 | 20 | JOBOS | 1-2 | 739.4 | 235.2 | 504.2 | 4.6 | 0.6183% | 0 | 0% | 0 | 0% | 0 | 99.38% | 30.09% | 4478 | 21 | 20 | JOBOS | 1-2 | 720 | 193.1 | 526.9 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 25.61% | 3688 | 21 | 20 | JOBOS | 1-2 | 61 | 18.7 | 42.3 | 683 | 91.8% | 0 | 0% | 0 | 0% | 0 | 8.199% | 2.419% | 360 | 21 | 20
| Total | 744 | 169.1 | 574.9 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 21.69% | 3227 | 21 | 20 |  | Total | 744 | 169.7 | 574.3 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 21.92% | 3261 | 21 | 20 |  | Total | 720 | 79 | 641 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | #REF! | 1441 | 21 | 20 |  | Total | 739.4 | 235.2 | 504.2 | 4.6 | 0.6183% | 0 | 0% | 0 | 0% | 0 | 99.38% | 30.09% | 4478 | 21 | 20 |  | Total | 720 | 193.1 | 526.9 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 25.61% | 3688 | 21 | 20 |  | Total | 61 | 18.7 | 42.3 | 683 | 91.8% | 0 | 0% | 0 | 0% | 0 | 8.199% | 2.419% | 360 | 21 | 20
DAGUAO | 1-1 | 744 | 180.7 | 563.3 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 21.72% | 3232 | 21 | 20 | DAGUAO | 1-1 | 744 | 203 | 541 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 24.31% | 3618 | 21 | 20 | DAGUAO | 1-1 | 720 | 96 | 624 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 12.01% | 1730 | 21 | 20 | DAGUAO | 1-1 | 712.56 | 243.2 | 469.36 | 31.44 | 4.226% | 0 | 0% | 0 | 0% | 0 | 95.77% | 29.72% | 4422 | 21 | 20 | DAGUAO | 1-1 | 630.9 | 163 | 467.9 | 89.1 | 12.38% | 0 | 0% | 0 | 0% | 0 | 87.62% | 20.58% | 2964 | 21 | 20 | DAGUAO | 1-1 | 720 | 95 | 625 | 24 | 3.226% | 0 | 0% | 0 | 0% | 0 | 96.77% | 11.68% | 1738 | 21 | 20
| 1-2 | 744 | 2.9 | 741.1 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0.3072% | 48 | 21 | 21 |  | 1-2 | 744 | 95.9 | 648.1 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 10.24% | 1600 | 21 | 21 |  | 1-2 | 720 | 94.5 | 625.5 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 9.048% | 1368 | 21 | 21 |  | 1-2 | 691 | 231.5 | 459.5 | 53 | 7.124% | 0 | 0% | 0 | 0% | 0 | 92.88% | 17.33% | 2708 | 21 | 21 |  | 1-2 | 586.11 | 149.4 | 436.71 | 133.89 | 18.6% | 0 | 0% | 0 | 0% | 0 | 81.4% | 10.21% | 1543 | 21 | 21 |  | 1-2 | 624 | 84.5 | 539.5 | 120 | 16.13% | 0 | 0% | 0 | 0% | 0 | 83.87% | 7.392% | 1155 | 21 | 21
| Total | 1488 | 183.6 | 1304.4 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 10.75% | 3280 | 42 | 41 |  | Total | 1488 | 298.9 | 1189.1 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 17.11% | 5218 | 42 | 41 |  | Total | 1440 | 190.5 | 1249.5 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 10.49% | 3098 | 42 | 41 |  | Total | 1403.56 | 474.7 | 928.86 | 84.44 | 5.71% | 0 | 0% | 0 | 0% | 0 | 94.29% | 23.37% | 7130 | 42 | 41 |  | Total | 1217.01 | 312.4 | 904.61 | 222.99 | 15.56% | 0 | 0% | 0 | 0% | 0 | 84.44% | 15.27% | 4507 | 42 | 41 |  | Total | 1344 | 179.5 | 1164.5 | 144 | 9.835% | 0 | 0% | 0 | 0% | 0 | 90.17% | 9.484% | 2893 | 42 | 41
CAMBALACHE | 2 | 738.13 | 370.63 | 367.5 | 5.87 | 0.789% | 0 | 0% | 0 | 0% | 0 | 99.21% | 37.68% | 21642 | 82.5 | 77.2 | CAMBALACHE | 2 | 744 | 415.28 | 328.72 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 41.27% | 23705 | 82.5 | 77.2 | CAMBALACHE | 2 | 720 | 234.78 | 485.22 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 23.24% | 12916 | 82.5 | 77.2 | CAMBALACHE | 2 | 734.42 | 475.3 | 259.12 | 2.7 | 0.3629% | 0 | 0% | 6.88 | 0.9247% | 0 | 98.71% | 47.75% | 27427 | 82.5 | 77.2 | CAMBALACHE | 2 | 709.52 | 208.72 | 500.8 | 10.48 | 1.456% | 0 | 0% | 0 | 0% | 0 | 98.54% | 21.36% | 11870 | 82.5 | 77.2 | CAMBALACHE | 2 | 744 | 82.9 | 661.1 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 8.28% | 4756 | 82.5 | 77.2
| 3 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 82.5 | 74.6 |  | 3 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 82.5 | 74.6 |  | 3 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 82.5 | 74.6 |  | 3 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 82.5 | 74.6 |  | 3 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 82.5 | 74.6 |  | 3 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 82.5 | 74.6
| Total | 738.13 | 370.63 | 367.5 | 749.87 | 49.54% | 0 | 0% | 0 | 0% | 0 | 50.46% | 19.16% | 21642 | 165 | 151.8 |  | Total | 744 | 415.28 | 328.72 | 744 | 49.14% | 0 | 0% | 0 | 0% | 0 | 50.86% | 20.99% | 23705 | 165 | 151.8 |  | Total | 720 | 234.78 | 485.22 | 720 | 49.14% | 0 | 0% | 0 | 0% | 0 | 50.86% | 11.82% | 12916 | 165 | 151.8 |  | Total | 734.42 | 475.3 | 259.12 | 746.7 | 49.33% | 0 | 0% | 6.88 | 0.4703% | 0 | 50.2% | 24.28% | 27427 | 165 | 151.8 |  | Total | 709.52 | 208.72 | 500.8 | 730.48 | 49.88% | 0 | 0% | 0 | 0% | 0 | 50.12% | 10.86% | 11870 | 165 | 151.8 |  | Total | 744 | 82.9 | 661.1 | 744 | 49.14% | 0 | 0% | 0 | 0% | 0 | 50.86% | 4.211% | 4756 | 165 | 151.8
MAYAGUEZ | 1 | 0 | 0 | 0 | 432 | 58.06% | 0 | 0% | 312 | 41.94% | 0 | 0% | 0% | 0 | 55 | 47.7 | MAYAGUEZ | 1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 55 | 47.7 | MAYAGUEZ | 1 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 55 | 47.7 | MAYAGUEZ | 1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 55 | 47.7 | MAYAGUEZ | 1 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 55 | 47.7 | MAYAGUEZ | 1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 55 | 47.7
| 2 | 0 | 0 | 0 | 0 | 0% | 0 | 0% | 744 | 100% | 0 | 0% | 0% | 0 | 55 | 49 |  | 2 | 0 | 0 | 0 | 576 | 77.42% | 0 | 0% | 168 | 22.58% | 0 | 0% | 0% | 0 | 55 | 49 |  | 2 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 55 | 49 |  | 2 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 55 | 49 |  | 2 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 55 | 49 |  | 2 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0 | 55 | 49
| 3 | 372 | 59.2 | 312.8 | 372 | 50% | 0 | 0% | 0 | 0% | 0 | 50% | 6.269% | 2565.2 | 55 | 55 |  | 3 | 353 | 59.2 | 293.8 | 391 | 52.55% | 0 | 0% | 0 | 0% | 0 | 47.45% | 6.247% | 2556.3 | 55 | 55 |  | 3 | 360 | 21.35 | 338.65 | 360 | 50% | 0 | 0% | 0 | 0% | 0 | 50% | 2.048% | 810.9 | 55 | 55 |  | 3 | 359.125 | 68.25 | 290.875 | 384.875 | 51.73% | 0 | 0% | 0 | 0% | 0 | 48.27% | 7.232% | 2959.5 | 55 | 55 |  | 3 | 360 | 123.35 | 236.65 | 360 | 50% | 0 | 0% | 0 | 0% | 0 | 50% | 14.02% | 5550.1 | 55 | 55 |  | 3 | 367.815 | 127.3 | 240.515 | 376.185 | 50.56% | 0 | 0% | 0 | 0% | 0 | 49.44% | 14% | 5728.5 | 55 | 55
| 4 | 372 | 59.65 | 312.35 | 372 | 50% | 0 | 0% | 0 | 0% | 0 | 50% | 7.312% | 2736.2 | 55 | 50.3 |  | 4 | 372 | 58.5 | 313.5 | 372 | 50% | 0 | 0% | 0 | 0% | 0 | 50% | 7.084% | 2651.1 | 55 | 50.3 |  | 4 | 358.375 | 22.45 | 335.925 | 361.625 | 50.23% | 0 | 0% | 0 | 0% | 0 | 49.77% | 2.758% | 998.8 | 55 | 50.3 |  | 4 | 345.785 | 69.95 | 275.835 | 398.215 | 53.52% | 0 | 0% | 0 | 0% | 0 | 46.48% | 8.315% | 3111.6 | 55 | 50.3 |  | 4 | 359.9335 | 121.4985 | 238.435 | 360.0665 | 50.01% | 0 | 0% | 0 | 0% | 0 | 49.99% | 15.69% | 5682.3 | 55 | 50.3 |  | 4 | 369.365 | 127.8 | 241.565 | 374.635 | 50.35% | 0 | 0% | 0 | 0% | 0 | 49.65% | 15.71% | 5877.6 | 55 | 50.3
| Total | 744 | 118.85 | 625.15 | 1176 | 39.78% | 0 | 0% | 1056 | 34.16% | 0 | 26.06% | 3.527% | 5301.4 | 220 | 202 |  | Total | 725 | 117.7 | 607.3 | 2083 | 69.15% | 0 | 0% | 168 | 5.477% | 0 | 25.37% | 3.465% | 5207.4 | 220 | 202 |  | Total | 718.375 | 43.8 | 674.575 | 2161.625 | 73.99% | 0 | 0% | 0 | 0% | 0 | 26.01% | 1.244% | 1809.7 | 220 | 202 |  | Total | 704.91 | 138.2 | 566.71 | 2271.09 | 75.28% | 0 | 0% | 0 | 0% | 0 | 24.72% | 4.04% | 6071.1 | 220 | 202 |  | Total | 719.9335 | 244.8485 | 475.085 | 2160.0665 | 73.94% | 0 | 0% | 0 | 0% | 0 | 26.06% | 7.723% | 11232.4 | 220 | 202 |  | Total | 737.18 | 255.1 | 482.08 | 2238.82 | 74.18% | 0 | 0% | 0 | 0% | 0 | 25.82% | 7.723% | 11606.1 | 220 | 202
| Total Peakers | 9856.83 | 3405.62 | 6451.21 | 3735.27 | 26.25% | 2463.9 | 19.5% | 1056 | 6.361% | 0 | 47.88% | 14.17% | 114381.4 | 1124 | 1084.8 |  | Total Peakers | 8718.7 | 3218.34 | 5500.36 | 5249.3 | 33.65% | 2976 | 22.68% | 168 | 1.02% | 0 | 42.65% | 12.85% | 103685.4 | 1124 | 1084.8 |  | Total Peakers | 8659.075 | 1905.18 | 6753.895 | 5020.925 | 33.07% | 2880 | 22.68% | 0 | 0% | 0 | 44.25% | #REF! | 59815.7 | 1124 | 1084.8 |  | Total Peakers | 8374.09 | 3841.1 | 4532.99 | 5755.03 | 36.45% | 2976 | 22.68% | 6.88 | 0.06581% | 0 | 40.81% | 14.81% | 119500.1 | 1124 | 1084.8 |  | Total Peakers | 8006.2635 | 3195.5685 | 4810.695 | 5441.7365 | 35.05% | 3087 | 24% | 25 | 0.16% | 0 | 40.78% | 12.54% | 97909.4 | 1124 | 1084.8 |  | Total Peakers | 7802.18 | 1931.7 | 5870.48 | 6202.62 | 36.47% | 3107.2 | 23.49% | 0 | 0% | 0 | 40.04% | 7.618% | 61481.1 | 1124 | 1084.8
| Total System | 15267.53 | 8756.22 | 6511.31 | 5660.27 | 30.96% | 3951.9 | 10.17% | 1160.3 | 2.322% | 822.37 | 48.74% | 35.76% | 951318.4 | 3916 | 3575.8 |  | Total System | 13897.86 | 8337.4 | 5560.46 | 7352.14 | 33.7% | 4464 | 11.13% | 326 | 0.9091% | 485.33 | 49.79% | 36.49% | 970819.4 | 3916 | 3575.8 |  | Total System | 14067.795 | 7311.5 | 6756.295 | 6566.535 | 29.25% | 4320 | 11.13% | 245.67 | 1.148% | 583.3 | 53.4% | #REF! | 948924.7 | 3916 | 3575.8 |  | Total System | 14458.88 | 9925.89 | 4532.99 | 7110.24 | 28.64% | 4464 | 11.13% | 6.88 | 0.01996% | 855.68 | 53.81% | 41.64% | 1107800.1 | 3916 | 3575.8 |  | Total System | 13418.5835 | 8521.4085 | 4897.175 | 7105.8865 | 29.47% | 4527 | 11.53% | 148.53 | 0.8322% | 735.01 | 51.66% | 37.2% | 957731.4 | 3916 | 3575.8 |  | Total System | 12524.63 | 6286.67 | 6237.96 | 8524.13 | 32.57% | 4795.58 | 12.43% | 195.66 | 1.741% | 780.19 | 47.29% | 29.64% | 788612.77 | 3916 | 3575.8
VIEQUES | 1 | 744 | 1.5 | 742.5 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 3.3 | 3.3 | VIEQUES | 1 | 744 | 1.5 | 742.5 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 3.3 | 3.3 | VIEQUES | 1 | 720 | 1 | 719 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 3.3 | 3.3 | VIEQUES | 1 | 565 | 1 | 564 | 179 | 24.06% | 0 | 0% | 0 | 0% | 0 | 75.94% | 0% | 0 | 3.3 | 3.3 | VIEQUES | 1 | 720 | 1 | 719 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 3.3 | 3.3 | VIEQUES | 1 | 744 | 0 | 744 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 3.3 | 3.3
| 2 | 744 | 1.5 | 742.5 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 3.3 | 3.3 |  | 2 | 744 | 1.5 | 742.5 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 3.3 | 3.3 |  | 2 | 720 | 1 | 719 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 3.3 | 3.3 |  | 2 | 565 | 1 | 564 | 179 | 24.06% | 0 | 0% | 0 | 0% | 0 | 75.94% | 0% | 0 | 3.3 | 3.3 |  | 2 | 720 | 1 | 719 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 3.3 | 3.3 |  | 2 | 744 | 0 | 744 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 3.3 | 3.3
| Total | 1488 | 3 | 1485 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 6.6 | 6.6 |  | Total | 1488 | 3 | 1485 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 6.6 | 6.6 |  | Total | 1440 | 2 | 1438 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 6.6 | 6.6 |  | Total | 1130 | 2 | 1128 | 358 | 24.06% | 0 | 0% | 0 | 0% | 0 | 75.94% | 0% | 0 | 6.6 | 6.6 |  | Total | 1440 | 2 | 1438 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 6.6 | 6.6 |  | Total | 1488 | 0 | 1488 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 6.6 | 6.6
CULEBRA | 1 | 744 | 1.1 | 742.9 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 2.2 | 2.2 | CULEBRA | 1 | 744 | 1.27 | 742.73 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 2.2 | 2.2 | CULEBRA | 1 | 720 | 1.61 | 718.39 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 2.2 | 2.2 | CULEBRA | 1 | 744 | 1.1 | 742.9 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 2.2 | 2.2 | CULEBRA | 1 | 720 | 55.12 | 664.88 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 3.662% | 58 | 2.2 | 2.2 | CULEBRA | 1 | 744 | 1.03 | 742.97 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 3.543% | 58 | 2.2 | 2.2
| 2 | 744 | 1.1 | 742.9 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 2.2 | 2.2 |  | 2 | 744 | 1.27 | 742.73 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 2.2 | 2.2 |  | 2 | 720 | 1.21 | 718.79 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 2.2 | 2.2 |  | 2 | 744 | 1.1 | 742.9 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 2.2 | 2.2 |  | 2 | 720 | 79.42 | 640.58 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 5.303% | 84 | 2.2 | 2.2 |  | 2 | 744 | 1 | 743 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 5.132% | 84 | 2.2 | 2.2
| 3 | 744 | 1.1 | 742.9 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 2.2 | 2.2 |  | 3 | 744 | 1.27 | 742.73 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 2.2 | 2.2 |  | 3 | 720 | 1.18 | 718.82 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 2.2 | 2.2 |  | 3 | 744 | 1 | 743 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 2.2 | 2.2 |  | 3 | 720 | 51.12 | 668.88 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 3.157% | 50 | 2.2 | 2.2 |  | 3 | 744 | 1.06 | 742.94 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 3.055% | 50 | 2.2 | 2.2
| Total | 2232 | 3.3 | 2228.7 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 6.6 | 6.6 |  | Total | 2232 | 3.81 | 2228.19 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 6.6 | 6.6 |  | Total | 2160 | 4 | 2156 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 6.6 | 6.6 |  | Total | 2232 | 3.2 | 2228.8 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 0% | 0 | 6.6 | 6.6 |  | Total | 2160 | 185.66 | 1974.34 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 4.04% | 192 | 6.6 | 6.6 |  | Total | 2232 | 3.09 | 2228.91 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 3.91% | 192 | 6.6 | 6.6

## Metrics ACUM (OMC) (2) (hidden)
FISCAL YEAR 2025-26 HOURS: | #REF!
PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Gross Generation | Net Capacity | APT Capacity | KPI Acum
SAN | CT 5 | #REF! | #REF! | #REF! | 106.6 | #REF! | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 160 | 153 | #REF!
JUAN | ST 5 | #REF! | #REF! | #REF! | 123.4 | #REF! | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 60 | 52 | #REF!
| CT 6 | #REF! | #REF! | #REF! | 538.5 | #REF! | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 160 | 140 | #REF!
| ST 6 | #REF! | #REF! | #REF! | 0 | #REF! | 2952 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 60 | 52 | #REF!
| 7 | #REF! | #REF! | #REF! | 0 | #REF! | 2952 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 100 | 100 | #REF!
| 9 | #REF! | #REF! | #REF! | 141.15 | #REF! | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 100 | 100 | #REF!
San Juan | Total | #REF! | #REF! | #REF! | 909.65 | #REF! | 5904 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 640 | 597
PALO | 3 | #REF! | #REF! | #REF! | 123.7 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 216 | 178 | #REF!
SECO | 4 | #REF! | #REF! | #REF! | 2188.13 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 216 | 216 | #REF!
PS | Total | #REF! | #REF! | #REF! | 2311.83 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 432 | 394
COSTA | 5 | #REF! | #REF! | #REF! | 188.55 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 410 | 350 | #REF!
SUR | 6 | #REF! | #REF! | #REF! | 162.24 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 410 | 350 | #REF!
CS | Total | #REF! | #REF! | #REF! | 350.79 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 820 | 700
AGUIRRE | 1 | #REF! | #REF! | #REF! | 2952 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 450 | 450 | #REF!
AGUIRRE | 2 | #REF! | #REF! | #REF! | 404.39 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 450 | 350 | #REF!
AGUIRRE | Total | #REF! | #REF! | #REF! | 3356.39 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 900 | 800
| Total Baseloads | #REF! | #REF! | #REF! | 6928.66 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2792 | 2491
AGUIRRE CC | V-1 | #REF! | #REF! | #REF! | 2924.7 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 96 | 96 | #REF!
AGUIRRE CC | 1-1 | #REF! | #REF! | #REF! | 2.7 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 50 | 50 | #REF!
AGUIRRE CC | 1-2 | #REF! | #REF! | #REF! | 34.1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 50 | 50 | #REF!
AGUIRRE CC | 1-3 | #REF! | #REF! | #REF! | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 50 | 50 | #REF!
AGUIRRE CC | 1-4 | #REF! | #REF! | #REF! | 23.8 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 50 | 50 | #REF!
AGUIRRE CC | V-2 | #REF! | #REF! | #REF! | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 96 | 96 | #REF!
AGUIRRE CC | 2-1 | #REF! | #REF! | #REF! | 347.3 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 50 | 50 | #REF!
AGUIRRE CC | 2-2 | #REF! | #REF! | #REF! | 143.9 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 50 | 50 | #REF!
AGUIRRE CC | 2-3 | #REF! | #REF! | #REF! | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 50 | 50 | #REF!
AGUIRRE CC | 2-4 | #REF! | #REF! | #REF! | 139.9 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 50 | 50 | #REF!
AGUIRRE CC | Total | #REF! | #REF! | #REF! | 3616.4 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 592 | 592
PALO | 1-1 | #REF! | #REF! | #REF! | 2448 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 21 | 21 | #REF!
SECO | 1-2 | #REF! | #REF! | #REF! | 2.8 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 21 | 21 | #REF!
| 2-1 | #REF! | #REF! | #REF! | 2952 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 21 | 21 | #REF!
Palo Seco | Total | #REF! | #REF! | #REF! | 5402.8 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 63 | 63
COSTA SUR | 1-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 21 | 21 | #REF!
CS | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 21 | 21
YABUCOA | 1-2 | #REF! | #REF! | #REF! | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 21 | 15 | #REF!
YABUCOA | Total | #REF! | #REF! | #REF! | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 21 | 15
JOBOS | 1-2 | #REF! | #REF! | #REF! | 4.6 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 21 | 20 | #REF!
JOBOS | Total | #REF! | #REF! | #REF! | 4.6 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 21 | 20
DAGUAO | 1-1 | #REF! | #REF! | #REF! | 31.44 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 21 | 20 | #REF!
DAGUAO | 1-2 | #REF! | #REF! | #REF! | 53 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 21 | 21 | #REF!
DAGUAO | Total | #REF! | #REF! | #REF! | 84.44 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 42 | 41
PALO SECO PW | MP 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 27 | 27 | #REF!
PALO SECO PW | MP 2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 27 | 27 | #REF!
PALO SECO PW | MP 3 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 27 | 27 | #REF!
PALO SECO PW | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 81 | 81
CAMBALACHE | 2 | #REF! | #REF! | #REF! | 8.57 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 82.5 | 77.2 | #REF!
CAMBALACHE | 3 | #REF! | #REF! | #REF! | 2952 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 82.5 | 74.6 | #REF!
CAMBALACHE | Total | #REF! | #REF! | #REF! | 2960.57 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 165 | 151.8
MAYAGUEZ | 1 | #REF! | #REF! | #REF! | 2640 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 55 | 47.7 | #REF!
MAYAGUEZ | 2 | #REF! | #REF! | #REF! | 2040 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 55 | 49 | #REF!
MAYAGUEZ | 3 | #REF! | #REF! | #REF! | 1507.875 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 55 | 55 | #REF!
MAYAGUEZ | 4 | #REF! | #REF! | #REF! | 1503.84 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 55 | 50.3 | #REF!
MAYAGUEZ | Total | #REF! | #REF! | #REF! | 7691.715 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 220 | 202
SJ PS TM | TM 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 25 | 25 | #REF!
SJ PS TM | TM 2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 25 | 25 | #REF!
SJ PS TM | TM 3 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 25 | 25 | #REF!
SJ PS TM | TM 4 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 25 | 25 | #REF!
SJ PS TM | TM 5 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 25 | 25 | #REF!
SJ PS TM | TM 6 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 25 | 25 | #REF!
SJ PS TM | TM 7 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 25 | 25 | #REF!
SJ PS TM | TM 8 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 25 | 25 | #REF!
SJ PS TM | TM 9 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 25 | 25 | #REF!
SJ PS TM | TM 10 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 25 | 25 | #REF!
SJ PS TM | TM 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 25 | 25 | #REF!
SJ PS TM | TM 2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 25 | 25 | #REF!
SJ PS TM | TM 3 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 20 | 20 | #REF!
SJ PS TM | TM 4 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 20 | 20 | #REF!
SJ PS TM | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 340 | 340
| Total Peakers | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1566 | 1526.8
| Total System | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4358 | 4017.8

## KPI_FY 25-26 (OMC) (2) (hidden)
JULY 2025 | [23 empty] | AUGUST 2025 | [24 empty] | SEPTEMBER 2025 | [24 empty] | OCTOBER 2025 | [23 empty] | NOVEMBER 2025 | [23 empty] | DECEMBER 2025 | [23 empty] | JANUARY 2026 | [23 empty] | FEBRUARY 2026 | [23 empty] | MARCH 2026 | [23 empty] | APRIL 2026 | [23 empty] | MAY 2026 | [23 empty] | JUNE 2026
MONTH HOURS: | 744 | [22 empty] | MONTH HOURS: | 744 | [23 empty] | MONTH HOURS: | 720 | [23 empty] | MONTH HOURS: | 744 | [22 empty] | MONTH HOURS: | [23 empty] | MONTH HOURS: | [23 empty] | MONTH HOURS: | [23 empty] | MONTH HOURS: | [23 empty] | MONTH HOURS: | [23 empty] | MONTH HOURS: | [23 empty] | MONTH HOURS: | [23 empty] | MONTH HOURS:
PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum |  | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum |  | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum |  | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum
SAN | CT 5 | 726.4 | 726.4 | 0 | 0 | 0 | 0 | 0 | 17.6 | 2.3656 | 57.773 | 97.6344 | 89.8692 | 7.3674 | 82.4162 | 0.077652 | 744 | 93816 | 160 | 153 | 156 | 92.3125 |  | SAN | CT 5 | 667.4 | 667.4 | 0 | 0 | 0 | 0 | 0 | 76.6 | 0.10296 | 0 | 0.89704 | 0.89704 | 0 | 0.72682 | 0 | 0 | 744 | 82735 | 160 | 153 | 151 | 100% |  | SAN | CT 5 | 653.83 | 653.83 | 0 | 18.7 | 0.025972 | 0 | 0 | 47.47 | 0.065931 | 0 | 0.9081 | 0.9081 | 0.027805 | 0.76115 | 0 | 1 | 720 | 83848 | 160 | 153 | 150 | 100% |  | SAN | CT 5 | 656.1 | 656.1 | 0 | 87.9 | 0.11815 | 0 | 0 | 0 | 0 | 35.99 | 0.88185 | 0.83348 | 0.15884 | 0.73796 | 0.048374 | 2 | 744 | 84004 | 160 | 153 | 150 | 100% | SAN | CT 5 | [16 empty] | 0 |  | 160 | 153 |  | 0% | SAN | CT 5 | [16 empty] | 0 |  | 160 | 153 |  | 0% | SAN | CT 5 | [16 empty] | 0 |  | 160 | 153 |  | 0% | SAN | CT 5 | [16 empty] | 0 |  | 160 | 153 |  | 0% | SAN | CT 5 | [16 empty] | 0 |  | 160 | 153 |  | 0% | SAN | CT 5 | [16 empty] | 0 |  | 160 | 153 |  | 0% | SAN | CT 5 | [16 empty] | 0 |  | 160 | 153 |  | 0% | SAN | CT 5 | [16 empty] | 0 |  | 160 | 153 |  | 0%
JUAN | ST 5 | 724.9 | 724.9 | 0 | 0 | 0 | 0 | 0 | 19.1 | 2.5672 | 48.165 | 97.4328 | 90.959 | 6.2304 | 81.02 | 0.064738 | 744 | 31345 | 60 | 52 | 53 | 93.5909 |  | JUAN | ST 5 | 656.5 | 656.5 | 0 | 6.1 | 0.0081989 | 0 | 0 | 81.4 | 0.10941 | 0 | 0.88239 | 0.88239 | 0.0092062 | 0.75274 | 0 | 1 | 744 | 29122 | 60 | 52 | 53 | 100% |  | JUAN | ST 5 | 636.9 | 636.9 | 0 | 21.2 | 0.029444 | 0 | 0 | 61.9 | 0.085972 | 0 | 0.88458 | 0.88458 | 0.032214 | 0.7883 | 0 | 1 | 720 | 29514 | 60 | 52 | 50 | 100% |  | JUAN | ST 5 | 647.9 | 647.9 | 0 | 96.1 | 0.12917 | 0 | 0 | 0 | 0 | 32.96 | 0.87083 | 0.82653 | 0.16611 | 0.74305 | 0.044301 | 1 | 744 | 28747 | 60 | 52 | 50 | 100% | JUAN | ST 5 | [16 empty] | 0 |  | 60 | 52 |  | 0% | JUAN | ST 5 | [16 empty] | 0 |  | 60 | 52 |  | 0% | JUAN | ST 5 | [16 empty] | 0 |  | 60 | 52 |  | 0% | JUAN | ST 5 | [16 empty] | 0 |  | 60 | 52 |  | 0% | JUAN | ST 5 | [16 empty] | 0 |  | 60 | 52 |  | 0% | JUAN | ST 5 | [16 empty] | 0 |  | 60 | 52 |  | 0% | JUAN | ST 5 | [16 empty] | 0 |  | 60 | 52 |  | 0% | JUAN | ST 5 | [16 empty] | 0 |  | 60 | 52 |  | 0%
| CT 6 | 610.1 | 550 | 60.1 | 133.9 | 17.9973 | 0 | 0 | 0 | 0 | 3.568 | 82.0027 | 81.5231 | 19.9963 | 72.6334 | 0.0047957 | 744 | 75655 | 160 | 140 | 160 | 99.5252 |  |  | CT 6 | 360.7 | 300.6 | 60.1 | 383.3 | 0.51519 | 0 | 0 | 0 | 0 | 0 | 0.48481 | 0.48481 | 0.56046 | 0.51377 | 0 | 3 | 744 | 53514 | 160 | 140 | 160 | 100% |  |  | CT 6 | 583.7 | 581.3 | 2.4 | 0 | 0 | 0 | 0 | 136.3 | 0.18931 | 0 | 0.81069 | 0.81069 | 0 | 0.78627 | 0 | 0 | 720 | 79256 | 160 | 140 | 160 | 100% | 14.48% |  | CT 6 | 722.7 | 722.7 | 0 | 21.3 | 0.028629 | 0 | 0 | 0 | 0 | 31.74 | 0.97137 | 0.92871 | 0.068373 | 0.90782 | 0.042661 | 2 | 744 | 94559 | 160 | 140 | 160 | 100% |  | CT 6 | [16 empty] | 0 |  | 160 | 140 |  | 0% |  | CT 6 | [16 empty] | 0 |  | 160 | 140 |  | 0% |  | CT 6 | [16 empty] | 0 |  | 160 | 140 |  | 0% |  | CT 6 | [16 empty] | 0 |  | 160 | 140 |  | 0% |  | CT 6 | [16 empty] | 0 |  | 160 | 140 |  | 0% |  | CT 6 | [16 empty] | 0 |  | 160 | 140 |  | 0% |  | CT 6 | [16 empty] | 0 |  | 160 | 140 |  | 0% |  | CT 6 | [16 empty] | 0 |  | 160 | 140 |  | 0%
| ST 6 | 0 | 0 | 0 | 0 | 0 | 744 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 60 | 52 | 0 | 100 | 634.7% |  | ST 6 | 0 | 0 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 60 | 52 | 0 | 100% |  |  | ST 6 | 0 | 0 | 0 | 0 | 0 | 720 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 0 | 60 | 52 | 0 | 100% | 88.27% |  | ST 6 | 0 | 0 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 60 | 52 | 0 | 100% |  | ST 6 | [16 empty] | 0 |  | 60 | 52 |  | 0% |  | ST 6 | [16 empty] | 0 |  | 60 | 52 |  | 0% |  | ST 6 | [16 empty] | 0 |  | 60 | 52 |  | 0% |  | ST 6 | [16 empty] | 0 |  | 60 | 52 |  | 0% |  | ST 6 | [16 empty] | 0 |  | 60 | 52 |  | 0% |  | ST 6 | [16 empty] | 0 |  | 60 | 52 |  | 0% |  | ST 6 | [16 empty] | 0 |  | 60 | 52 |  | 0% |  | ST 6 | [16 empty] | 0 |  | 60 | 52 |  | 0%
| 7 | 0 | 0 | 0 | 0 | 0 | 744 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 100 | 100 | 0 | 100 |  |  | 7 | 0 | 0 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 100 | 100 | 0 | 100% | 56.81% |  | 7 | 0 | 0 | 0 | 0 | 0 | 720 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 0 | 100 | 100 | 0 | 100% |  |  | 7 | 0 | 0 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 100 | 100 | 0 | 100% |  | 7 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 7 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 7 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 7 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 7 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 7 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 7 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 7 | [16 empty] | 0 |  | 100 | 100 |  | 0%
| 9 | 645.7 | 645.7 | 0 | 30.7 | 4.1263 | 0 | 0 | 67.6 | 9.086 | 21.804 | 86.7876 | 83.857 | 7.5199 | 63.1358 | 0.029306 | 744 | 46973 | 100 | 100 | 57 | 97.0987 | 7530% |  | 9 | 744 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.74169 | 0 | 1 | 744 | 55182 | 100 | 100 | 93 | 100% | 63.23% |  | 9 | 623.05 | 623.05 | 0 | 96.95 | 0.13465 | 0 | 0 | 0 | 0 | 42.48 | 0.86535 | 0.80635 | 0.18286 | 0.59139 | 0.059 | 1 | 720 | 42580 | 100 | 100 | 81 | 100% | 6.733% |  | 9 | 744 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.29 | 1 | 0.81547 | 0.15578 | 0.74526 | 0.18453 | 0 | 744 | 55447 | 100 | 100 | 82 | 100% |  | 9 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 9 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 9 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 9 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 9 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 9 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 9 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 9 | [16 empty] | 0 |  | 100 | 100 |  | 0%
| Total | 2707.1 | 2647 | 60.1 | 164.6 | 22.1237 | 1488 | 200 | 104.3 | 14.0188 | 131.31 | 363.8575 | 346.2083 | 27.1775 | 65.9569 | 0.031573 | 4464 | 247789 | 640 | 597 | 426 |  | 4193% |  | Total | 2428.6 | 2368.5 | 60.1 | 389.4 | 0.12153 | 1488 | 0.25461 | 158 | 0.035916 | 0 | 0.58795 | 0.58795 | 0.13223 | 0.49655 | 0 | 5 | 4464 | 220553 | 640 | 597 | 457 |  | 50% |  | Total | 2497.48 | 2495.08 | 2.4 | 136.85 | 0.031776 | 1440 | 0.25461 | 245.67 | 0.068778 | 42.48 | 0.64484 | 0.63496 | 0.040562 | 0.54718 | 0.0098827 | 3 | 4320 | 235198 | 640 | 597 | 441 |  | 40.32% |  | Total | 2770.7 | 2770.7 | 0 | 205.3 | 0.048243 | 1488 | 0.25461 | 0 | 0 | 237.98 | 0.69715 | 0.63998 | 0.097303 | 0.59157 | 0.05717 | 5 | 4464 | 262757 | 640 | 597 | 442 |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 640 | 597 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 640 | 597 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 640 | 597 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 640 | 597 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 640 | 597 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 640 | 597 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 640 | 597 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 640 | 597
PALO | 3 | 739.33 | 739.33 | 0 | 4.67 | 0.62769 | 0 | 0 | 0 | 0 | 271.25 | 99.3723 | 62.914 | 100 | 0 | 0.36458 | 744 | 87348 | 216 | 178 | 130 | 63.9062 |  | PALO | 3 | 744 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296.22 | 1 | 0.60185 | 0.28477 | 0.66971 | 0.39815 | 0 | 744 | 88691 | 216 | 178 | 130 | 100% | 0% | PALO | 3 | 704.52 | 704.52 | 0 | 15.48 | 0.0215 | 0 | 0 | 0 | 0 | 314.11 | 0.9785 | 0.54224 | 0.31872 | 0.56806 | 0.43626 | 2 | 720 | 72802 | 216 | 178 | 100 | 100% |  | PALO | 3 | 640.45 | 640.45 | 0 | 103.55 | 0.13918 | 0 | 0 | 0 | 0 | 264.55 | 0.86082 | 0.50524 | 0.36498 | 0.53924 | 0.35558 | 1 | 744 | 71413 | 216 | 178 | 145 | 100% | PALO | 3 | [16 empty] | 0 |  | 216 | 178 |  | 0% | PALO | 3 | [16 empty] | 0 |  | 216 | 178 |  | 0% | PALO | 3 | [16 empty] | 0 |  | 216 | 178 |  | 0% | PALO | 3 | [16 empty] | 0 |  | 216 | 178 |  | 0% | PALO | 3 | [16 empty] | 0 |  | 216 | 178 |  | 0% | PALO | 3 | [16 empty] | 0 |  | 216 | 178 |  | 0% | PALO | 3 | [16 empty] | 0 |  | 216 | 178 |  | 0% | PALO | 3 | [16 empty] | 0 |  | 216 | 178 |  | 0%
SECO | 4 | 0 | 0 | 0 | 744 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9133 | 69.0899 | 0 | 744 | 0 | 216 | 216 | 0 | 100 |  | SECO | 4 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 744 | 0 | 216 | 216 | 0 | 100% |  | SECO | 4 | 113.88 | 113.88 | 0 | 606.12 | 0.84183 | 0 | 0 | 0 | 0 | 66.84 | 0.15817 | 0.065333 | 0.85527 | 0.050919 | 0.092833 | 1 | 720 | 7919 | 216 | 216 | 80 | 100% |  | SECO | 4 | 649.99 | 649.99 | 0 | 94.01 | 0.12636 | 0 | 0 | 0 | 0 | 193.48 | 0.87364 | 0.61359 | 0.30666 | 0.52699 | 0.26005 | 6 | 744 | 84690 | 216 | 216 | 170 | 100% | SECO | 4 | [16 empty] | 0 |  | 216 | 216 |  | 0% | SECO | 4 | [16 empty] | 0 |  | 216 | 216 |  | 0% | SECO | 4 | [16 empty] | 0 |  | 216 | 216 |  | 0% | SECO | 4 | [16 empty] | 0 |  | 216 | 216 |  | 0% | SECO | 4 | [16 empty] | 0 |  | 216 | 216 |  | 0% | SECO | 4 | [16 empty] | 0 |  | 216 | 216 |  | 0% | SECO | 4 | [16 empty] | 0 |  | 216 | 216 |  | 0% | SECO | 4 | [16 empty] | 0 |  | 216 | 216 |  | 0%
| Total | 739.33 | 739.33 | 0 | 748.67 | 100.6277 | 0 | 0 | 0 | 0 | 271.25 | 99.3723 | 62.914 | 31.8787 | 66.9163 | 0.16471 | 1488 | 87348 | 432 | 394 | 130 |  |  |  | Total | 744 | 744 | 0 | 744 | 0.54822 | 0 | 0 | 0 | 0 | 296.22 | 0.45178 | 0.2719 | 0.67687 | 0.30256 | 0.17987 | 0 | 1488 | 88691 | 432 | 394 | 130 |  |  |  | Total | 818.4 | 818.4 | 0 | 621.6 | 0.47123 | 0 | 0 | 0 | 0 | 380.95 | 0.52877 | 0.28079 | 0.61287 | 0.28455 | 0.24799 | 3 | 1440 | 80721 | 432 | 394 | 180 |  |  |  | Total | 1290.44 | 1290.44 | 0 | 197.56 | 0.13215 | 0 | 0 | 0 | 0 | 458.03 | 86.78% | 56.46% | 33.3% | 53.25% | 30.32% | 7 | 1488 | 156103 | 432 | 394 | 315 |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 432 | 394 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 432 | 394 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 432 | 394 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 432 | 394 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 432 | 394 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 432 | 394 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 432 | 394 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 432 | 394
COSTA | 5 | 628.75 | 628.75 | 0 | 115.25 | 15.4906 | 0 | 0 | 0 | 0 | 71.64 | 84.5094 | 74.8804 | 100 | 0 | 0.09629 | 744 | 179910 | 410 | 350 | 0 | 90.4673 |  | COSTA | 5 | 744 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.87569 | 0 | 0 | 744 | 228030 | 410 | 350 | 410 | 100% |  | COSTA | 5 | 720 | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.92 | 1 | 0.95983 | 0.038616 | 0.83964 | 0.040167 | 0 | 720 | 211590 | 410 | 350 | 290 | 100% |  | COSTA | 5 | 670.7 | 670.7 | 0 | 73.3 | 0.098522 | 0 | 0 | 0 | 0 | 6.8 | 0.90148 | 0.89234 | 0.10669 | 0.84021 | 0.0091398 | 0 | 744 | 218790 | 410 | 350 | 410 | 100% | COSTA | 5 | [16 empty] | 0 |  | 410 | 350 |  | 0% | COSTA | 5 | [16 empty] | 0 |  | 410 | 350 |  | 0% | COSTA | 5 | [16 empty] | 0 |  | 410 | 350 |  | 0% | COSTA | 5 | [16 empty] | 0 |  | 410 | 350 |  | 0% | COSTA | 5 | [16 empty] | 0 |  | 410 | 350 |  | 0% | COSTA | 5 | [16 empty] | 0 |  | 410 | 350 |  | 0% | COSTA | 5 | [16 empty] | 0 |  | 410 | 350 |  | 0% | COSTA | 5 | [16 empty] | 0 |  | 410 | 350 |  | 0%
SUR | 6 | 744 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348.17 | 100 | 53.203 | 20.4946 | 56.6974 | 0.46797 | 744 | 174250 | 410 | 350 | 350 | 53.6709 |  | SUR | 6 | 646.55 | 646.55 | 0 | 97.45 | 0.13098 | 0 | 0 | 0 | 0 | 49.49 | 0.86902 | 0.8025 | 0.18518 | 0.71091 | 0.066519 | 2 | 744 | 185120 | 410 | 350 | 360 | 100% |  | SUR | 6 | 655.21 | 655.21 | 0 | 64.79 | 0.089986 | 0 | 0 | 0 | 0 | 28.75 | 0.91001 | 0.87008 | 0.12493 | 0.7173 | 0.039931 | 2 | 720 | 180760 | 410 | 350 | 252 | 100% |  | SUR | 6 | 744 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152.87 | 1 | 0.79453 | 0.17045 | 0.74727 | 0.20547 | 0 | 744 | 194590 | 410 | 350 | 292 | 100% | SUR | 6 | [16 empty] | 0 |  | 410 | 350 |  | 0% | SUR | 6 | [16 empty] | 0 |  | 410 | 350 |  | 0% | SUR | 6 | [16 empty] | 0 |  | 410 | 350 |  | 0% | SUR | 6 | [16 empty] | 0 |  | 410 | 350 |  | 0% | SUR | 6 | [16 empty] | 0 |  | 410 | 350 |  | 0% | SUR | 6 | [16 empty] | 0 |  | 410 | 350 |  | 0% | SUR | 6 | [16 empty] | 0 |  | 410 | 350 |  | 0% | SUR | 6 | [16 empty] | 0 |  | 410 | 350 |  | 0%
| Total | 1372.75 | 1372.75 | 0 | 115.25 | 15.4906 | 0 | 0 | 0 | 0 | 419.81 | 184.5094 | 128.0833 | 100 | 0 | 0.28213 | 1488 | 354160 | 820 | 700 | 350 |  |  |  | Total | 1390.55 | 1390.55 | 0 | 97.45 | 0.065491 | 0 | 0 | 0 | 0 | 49.49 | 0.93451 | 0.90125 | 0.092591 | 0.7933 | 0.033259 | 2 | 1488 | 413150 | 820 | 700 | 770 |  |  |  | Total | 1375.21 | 1375.21 | 0 | 64.79 | 0.044993 | 0 | 0 | 0 | 0 | 57.67 | 0.95501 | 0.91496 | 0.081772 | 0.77847 | 0.040049 | 2 | 1440 | 392350 | 820 | 700 | 542 |  |  |  | Total | 1414.7 | 1414.7 | 0 | 73.3 | 0.049261 | 0 | 0 | 0 | 0 | 159.67 | 0.95074 | 0.84343 | 0.13857 | 0.79374 | 0.10731 | 0 | 1488 | 413380 | 820 | 700 | 702 |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 820 | 700 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 820 | 700 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 820 | 700 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 820 | 700 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 820 | 700 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 820 | 700 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 820 | 700 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 820 | 700
AGUIRRE | 1 | 0 | 0 | 0 | 744 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.9677 | 0 | 744 | 0 | 450 | 450 | 410 | 100 |  | AGUIRRE | 1 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 744 | 0 | 450 | 450 | 0 | 100% |  | AGUIRRE | 1 | 0 | 0 | 0 | 720 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 720 | 0 | 450 | 450 | 0 | 100% |  | AGUIRRE | 1 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 744 | 0 | 450 | 450 | 0 | 100% | AGUIRRE | 1 | [16 empty] | 0 |  | 450 | 450 |  | 0% | AGUIRRE | 1 | [16 empty] | 0 |  | 450 | 450 |  | 0% | AGUIRRE | 1 | [16 empty] | 0 |  | 450 | 450 |  | 0% | AGUIRRE | 1 | [16 empty] | 0 |  | 450 | 450 |  | 0% | AGUIRRE | 1 | [16 empty] | 0 |  | 450 | 450 |  | 0% | AGUIRRE | 1 | [16 empty] | 0 |  | 450 | 450 |  | 0% | AGUIRRE | 1 | [16 empty] | 0 |  | 450 | 450 |  | 0% | AGUIRRE | 1 | [16 empty] | 0 |  | 450 | 450 |  | 0%
| 2 | 591.52 | 591.52 | 0 | 152.48 | 20.4946 | 0 | 0 | 0 | 0 | 0 | 79.5054 | 79.5054 | 0.35377 | 29.707 | 0 | 744 | 147640 | 450 | 350 | 256 | 100 |  |  | 2 | 629.51 | 629.51 | 0 | 114.49 | 0.15388 | 0 | 0 | 0 | 0 | 139.62 | 0.84612 | 0.65845 | 0.28758 | 0.55584 | 0.18766 | 4 | 744 | 144740 | 450 | 350 | 350 | 100% |  |  | 2 | 717.63 | 717.63 | 0 | 2.37 | 0.0032917 | 0 | 0 | 0 | 0 | 102.2 | 0.99671 | 0.85476 | 0.12718 | 0.71762 | 0.14194 | 1 | 720 | 180840 | 450 | 350 | 350 | 100% |  |  | 2 | 608.95 | 608.95 | 0 | 135.05 | 0.18152 | 0 | 0 | 0 | 0 | 0 | 0.81848 | 0.81848 | 0.18152 | 0.59931 | 0 | 1 | 744 | 156060 | 450 | 350 | 350 | 100% |  | 2 | [16 empty] | 0 |  | 450 | 350 |  | 0% |  | 2 | [16 empty] | 0 |  | 450 | 350 |  | 0% |  | 2 | [16 empty] | 0 |  | 450 | 350 |  | 0% |  | 2 | [16 empty] | 0 |  | 450 | 350 |  | 0% |  | 2 | [16 empty] | 0 |  | 450 | 350 |  | 0% |  | 2 | [16 empty] | 0 |  | 450 | 350 |  | 0% |  | 2 | [16 empty] | 0 |  | 450 | 350 |  | 0% |  | 2 | [16 empty] | 0 |  | 450 | 350 |  | 0%
| Total | 591.52 | 591.52 | 0 | 896.48 | 120.4946 | 0 | 0 | 0 | 0 | 0 | 79.5054 | 79.5054 | 0 | 0 | 0 | 1488 | 147640 | 900 | 800 | 666 |  |  |  | Total | 629.51 | 629.51 | 0 | 858.49 | 0.62982 | 0 | 0 | 0 | 0 | 139.62 | 0.37018 | 0.28807 | 0.68832 | 0.24318 | 0.082102 | 4 | 1488 | 144740 | 900 | 800 | 350 |  |  |  | Total | 717.63 | 717.63 | 0 | 722.37 | 0.56394 | 0 | 0 | 0 | 0 | 102.2 | 0.43606 | 0.37396 | 0.61814 | 0.31396 | 0.062101 | 1 | 1440 | 180840 | 900 | 800 | 350 |  |  |  | Total | 608.95 | 608.95 | 0 | 879.05 | 0.64191 | 0 | 0 | 0 | 0 | 0 | 0.35809 | 0.35809 | 0.64191 | 0.2622 | 0 | 1 | 1488 | 156060 | 900 | 800 | 350 |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 900 | 800 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 900 | 800 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 900 | 800 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 900 | 800 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 900 | 800 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 900 | 800 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 900 | 800 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 900 | 800
| Total Baseloads | 5410.7 | 5350.6 | 60.1 | 1925 | 258.7366 | 1488 | 200 | 104.3 | 14.0188 | 822.37 | 727.2446 | 616.711 | 8.0189 | 24.6344 | 0.1129 |  | 836937 | 2792 | 2491 | 1572 |  |  |  | Total Baseloads | 5192.66 | 5132.56 | 60.1 | 2089.34 | 0.33651 | 1488 | 0.06102 | 158 | 0.0086077 | 485.33 | 0.59386 | 0.52969 | 0.38583 | 0.46789 | 0.064164 | 11 | 8928 | 867134 | 2792 | 2491 | 1707 |  |  |  | Total Baseloads | 5408.72 | 5406.32 | 2.4 | 1545.61 | 0.27591 | 1440 | 0.06102 | 245.67 | 0.016484 | 583.3 | 0.64659 | 0.5738 | 0.32816 | 0.49573 | 0.072791 | 9 | 8640 | 889109 | 2792 | 2491 | 1513 |  |  |  | Total Baseloads | 6084.79 | 6084.79 | 0 | 1355.21 | 0.25246 | 1488 | 0.06102 | 0 | 0 | 855.68 | 0.68652 | 0.5947 | 0.32109 | 0.53326 | 0.091814 | 13 | 8928 | 988300 | 2792 | 2491 | 1809 |  |  | Total Baseloads | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 2792 | 2491 |  |  |  | Total Baseloads | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 2792 | 2491 |  |  |  | Total Baseloads | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 2792 | 2491 |  |  |  | Total Baseloads | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 2792 | 2491 |  |  |  | Total Baseloads | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 2792 | 2491 |  |  |  | Total Baseloads | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 2792 | 2491 |  |  |  | Total Baseloads | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 2792 | 2491 |  |  |  | Total Baseloads | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 2792 | 2491
AGUIRRE CC | V-1 | 0 | 0 | 0 | 744 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 96 | 96 | 0 | 100 |  | AGUIRRE CC | V-1 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 744 | 0 | 96 | 96 | 0 | 100% |  | AGUIRRE CC | V-1 | 27.3 | 0 | 27.3 | 692.7 | 0.96208 | 0 | 0 | 0 | 0 | 0 | 0.037917 | 0.037917 | 1 | 0 | 0 | 0 | 720 | 0 | 96 | 96 | 0 | 100% |  | AGUIRRE CC | V-1 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 744 | 0 | 96 | 96 | 0 | 100% | AGUIRRE CC | V-1 | [16 empty] | 0 |  | 96 | 96 |  | 0% | AGUIRRE CC | V-1 | [16 empty] | 0 |  | 96 | 96 |  | 0% | AGUIRRE CC | V-1 | [16 empty] | 0 |  | 96 | 96 |  | 0% | AGUIRRE CC | V-1 | [16 empty] | 0 |  | 96 | 96 |  | 0% | AGUIRRE CC | V-1 | [16 empty] | 0 |  | 96 | 96 |  | 0% | AGUIRRE CC | V-1 | [16 empty] | 0 |  | 96 | 96 |  | 0% | AGUIRRE CC | V-1 | [16 empty] | 0 |  | 96 | 96 |  | 0% | AGUIRRE CC | V-1 | [16 empty] | 0 |  | 96 | 96 |  | 0%
| 1-1 | 744 | 298 | 446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 37.2554 | 0 | 744 | 13752 | 50 | 50 | 50 | 100 |  |  | 1-1 | 741.3 | 393 | 348.3 | 2.7 | 0.003629 | 0 | 0 | 0 | 0 | 0 | 0.99637 | 0.99637 | 0.0068234 | 0.34457 | 0 | 1 | 744 | 12818 | 50 | 50 | 50 | 100% |  |  | 1-1 | 720 | 252 | 468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.22269 | 0 | 0 | 720 | 8017 | 50 | 50 | 50 | 100% |  |  | 1-1 | 744 | 510 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.44952 | 0 | 0 | 744 | 16722 | 50 | 50 | 50 | 100% |  | 1-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-1 | [16 empty] | 0 |  | 50 | 50 |  | 0%
| 1-2 | 742.8 | 338 | 404.8 | 1.2 | 0.16129 | 0 | 0 | 0 | 0 | 0 | 99.8387 | 99.8387 | 0 | 39.5215 | 0 | 744 | 11051 | 50 | 50 | 50 | 100 |  |  | 1-2 | 729.5 | 335 | 394.5 | 14.5 | 0.019489 | 0 | 0 | 0 | 0 | 0 | 0.98051 | 0.98051 | 0.041488 | 0.28954 | 0 | 0 | 744 | 10771 | 50 | 50 | 50 | 100% |  |  | 1-2 | 718.1 | 176 | 542.1 | 1.9 | 0.0026389 | 0 | 0 | 0 | 0 | 0 | 0.99736 | 0.99736 | 0.01068 | 0.15408 | 0 | 0 | 720 | 5547 | 50 | 50 | 48 | 100% |  |  | 1-2 | 727.5 | 425 | 302.5 | 16.5 | 0.022177 | 0 | 0 | 0 | 0 | 0 | 0.97782 | 0.97782 | 0.037373 | 0.36863 | 0 | 1 | 744 | 13713 | 50 | 50 | 50 | 100% |  | 1-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 50 | 50 |  | 0%
| 1-3 | 0 | 0 | 0 | 0 | 0 | 744 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 50 | 50 | 0 | 100 |  |  | 1-3 | 0 | 0 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 50 | 50 | 0 | 100% |  |  | 1-3 | 0 | 0 | 0 | 0 | 0 | 720 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 0 | 50 | 50 | 0 | 100% |  |  | 1-3 | 0 | 0 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 50 | 50 | 0 | 100% |  | 1-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-3 | [16 empty] | 0 |  | 50 | 50 |  | 0%
| 1-4 | 488.3 | 273 | 215.3 | 23.8 | 3.1989 | 231.9 | 31.1694 | 0 | 0 | 0 | 65.6317 | 65.6317 | 15.1206 | 28.2016 | 0 | 744 | 9164 | 50 | 50 | 50 | 100 |  |  | 1-4 | 0 | 0 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 50 | 50 | 0 | 100% |  |  | 1-4 | 0 | 0 | 0 | 0 | 0 | 720 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 0 | 50 | 50 | 0 | 100% |  |  | 1-4 | 0 | 0 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 50 | 50 | 0 | 100% |  | 1-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-4 | [16 empty] | 0 |  | 50 | 50 |  | 0%
| V-2 | 0 | 0 | 0 | 0 | 0 | 744 | 100 | 0 | 0 | 0 | 0 | 0 | 65.1112 | 14.7017 | 0 | 744 | 0 | 96 | 96 | 0 | 100 |  |  | V-2 | 0 | 0 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 96 | 96 | 0 | 100% |  |  | V-2 | 0 | 0 | 0 | 0 | 0 | 720 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 0 | 96 | 96 | 0 | 100% |  |  | V-2 | 0 | 0 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 96 | 96 | 0 | 100% |  | V-2 | [16 empty] | 0 |  | 96 | 96 |  | 0% |  | V-2 | [16 empty] | 0 |  | 96 | 96 |  | 0% |  | V-2 | [16 empty] | 0 |  | 96 | 96 |  | 0% |  | V-2 | [16 empty] | 0 |  | 96 | 96 |  | 0% |  | V-2 | [16 empty] | 0 |  | 96 | 96 |  | 0% |  | V-2 | [16 empty] | 0 |  | 96 | 96 |  | 0% |  | V-2 | [16 empty] | 0 |  | 96 | 96 |  | 0% |  | V-2 | [16 empty] | 0 |  | 96 | 96 |  | 0%
| 2-1 | 744 | 424.7 | 319.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 24.5904 | 0 | 744 | 13859 | 50 | 50 | 50 | 100 |  |  | 2-1 | 690.6 | 397.5 | 293.1 | 53.4 | 0.071774 | 0 | 0 | 0 | 0 | 0 | 0.92823 | 0.92823 | 0.11843 | 0.34194 | 0 | 2 | 744 | 12720 | 50 | 50 | 50 | 100% |  |  | 2-1 | 720 | 297.6 | 422.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.26081 | 0 | 0 | 720 | 9389 | 50 | 50 | 50 | 100% |  |  | 2-1 | 450.1 | 322.9 | 127.2 | 293.9 | 0.39503 | 0 | 0 | 0 | 0 | 0 | 0.60497 | 0.60497 | 0.47649 | 0.28597 | 0 | 5 | 744 | 10638 | 50 | 50 | 50 | 100% |  | 2-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 50 | 50 |  | 0%
| 2-2 | 744 | 453.3 | 290.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 0 | 0 | 744 | 14702 | 50 | 50 | 50 | 100 |  |  | 2-2 | 707.8 | 424.4 | 283.4 | 36.2 | 0.048656 | 0 | 0 | 0 | 0 | 0 | 0.95134 | 0.95134 | 0.078593 | 0.36427 | 0 | 3 | 744 | 13551 | 50 | 50 | 50 | 100% |  |  | 2-2 | 718.1 | 242 | 476.1 | 1.9 | 0.0026389 | 0 | 0 | 0 | 0 | 0 | 0.99736 | 0.99736 | 0.0077901 | 0.20925 | 0 | 0 | 720 | 7533 | 50 | 50 | 50 | 100% |  |  | 2-2 | 638.2 | 293.8 | 344.4 | 105.8 | 0.1422 | 0 | 0 | 0 | 0 | 0 | 0.8578 | 0.8578 | 0.26476 | 0.25094 | 0 | 1 | 744 | 9335 | 50 | 50 | 50 | 100% |  | 2-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-2 | [16 empty] | 0 |  | 50 | 50 |  | 0%
| 2-3 | 0 | 0 | 0 | 0 | 0 | 744 | 100 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 744 | 0 | 50 | 50 | 0 | 100 |  |  | 2-3 | 0 | 0 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 50 | 50 | 0 | 100% |  |  | 2-3 | 0 | 0 | 0 | 0 | 0 | 720 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 0 | 50 | 50 | 0 | 100% |  |  | 2-3 | 0 | 0 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 50 | 50 | 0 | 100% |  | 2-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-3 | [16 empty] | 0 |  | 50 | 50 |  | 0%
| 2-4 | 687.6 | 316.6 | 371 | 56.4 | 7.5806 | 0 | 0 | 0 | 0 | 0 | 92.4194 | 92.4194 | 0 | 15.8871 | 0 | 744 | 10491 | 50 | 50 | 50 | 100 |  |  | 2-4 | 660.5 | 321.3 | 339.2 | 83.5 | 0.11223 | 0 | 0 | 0 | 0 | 0 | 0.88777 | 0.88777 | 0.20627 | 0.27083 | 0 | 0 | 744 | 10075 | 50 | 50 | 50 | 100% |  |  | 2-4 | 720 | 213.9 | 506.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.1965 | 0 | 0 | 720 | 7074 | 50 | 50 | 50 | 100% |  |  | 2-4 | 744 | 464.1 | 279.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.41414 | 0 | 0 | 744 | 15406 | 50 | 50 | 50 | 100% |  | 2-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-4 | [16 empty] | 0 |  | 50 | 50 |  | 0%
| Total | 4150.7 | 2103.6 | 2047.1 | 825.4 | 110.9409 | 2463.9 | 331.1694 | 0 | 0 | 0 | 557.8898 | 557.8898 | 0 | 21.6868 | 0 | 7440 | 73019 | 592 | 592 | 300 |  |  |  | Total | 3529.7 | 1871.2 | 1658.5 | 934.3 | 0.18377 | 2976 | 0.41554 | 0 | 0 | 0 | 0.40069 | 0.40069 | 0.2003 | 0.13608 | 0 | 6 | 7440 | 59935 | 592 | 592 | 250 |  |  |  | Total | 3623.5 | 1181.5 | 2442 | 696.5 | 0.15646 | 2880 | 0.41554 | 0 | 0 | 0 | 0.428 | 0.428 | 0.16372 | 0.088119 | 0 | 0 | 7200 | 37560 | 592 | 592 | 248 |  |  |  | Total | 3303.8 | 2015.8 | 1288 | 1160.2 | 0.20941 | 2976 | 0.41554 | 0 | 0 | 0 | 0.37505 | 0.37505 | 0.22792 | 0.14943 | 0 | 7 | 7440 | 65814 | 592 | 592 | 250 |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 592 | 592 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 592 | 592 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 592 | 592 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 592 | 592 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 592 | 592 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 592 | 592 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 592 | 592 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 592 | 592
PALO | 1-1 | 504 | 128.6 | 375.4 | 240 | 32.2581 | 0 | 0 | 0 | 0 | 0 | 67.7419 | 67.7419 | 0 | 21.7204 | 0 | 744 | 2297 | 21 | 21 | 18 | 100 |  | PALO | 1-1 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 744 | 0 | 21 | 21 | 0 | 100% |  | PALO | 1-1 | 0 | 0 | 0 | 720 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 720 | 0 | 21 | 21 | 0 | 100% |  | PALO | 1-1 | 744 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 744 | 0 | 21 | 21 | 0 | 100% | PALO | 1-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% | PALO | 1-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% | PALO | 1-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% | PALO | 1-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% | PALO | 1-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% | PALO | 1-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% | PALO | 1-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% | PALO | 1-1 | [16 empty] | 0 |  | 21 | 21 |  | 0%
SECO | 1-2 | 744 | 213.4 | 530.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 0.30722 | 0 | 744 | 3842 | 21 | 21 | 18 | 100 |  | SECO | 1-2 | 744 | 180.76 | 563.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.24846 | 0 | 0 | 744 | 3882 | 21 | 21 | 21 | 100% |  | SECO | 1-2 | 717.2 | 107.6 | 609.6 | 2.8 | 0.0038889 | 0 | 0 | 0 | 0 | 0 | 0.99611 | 0.99611 | 0.025362 | 0.13042 | 0 | 1 | 720 | 1972 | 21 | 21 | 18.3613 | 100% |  | SECO | 1-2 | 275.3 | -193.4 | 468.7 | 468.7 | 0.62997 | 0 | 0 | 0 | 0 | 0 | 0.37003 | 0.37003 | 1.7025 | 0.33122 | 0 | 0 | 744 | 5175 | 21 | 21 | 19 | 100% | SECO | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | SECO | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | SECO | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | SECO | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | SECO | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | SECO | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | SECO | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | SECO | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0%
| 2-1 | 0 | 0 | 0 | 744 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.0518 | 0 | 744 | 0 | 21 | 21 | 0 | 100 |  |  | 2-1 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 744 | 0 | 21 | 21 | 0 | 100% |  |  | 2-1 | 0 | 0 | 0 | 720 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 720 | 0 | 21 | 21 | 0 | 100% |  |  | 2-1 | 744 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 744 | 0 | 21 | 21 | 0 | 100% |  | 2-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 21 | 21 |  | 0%
| Total | 1248 | 342 | 906 | 984 | 132.2581 | 0 | 0 | 0 | 0 | 0 | 167.7419 | 167.7419 | 0 | 19.9423 | 0 | 2232 | 6139 | 63 | 63 | 36 |  |  |  | Total | 744 | 180.76 | 563.24 | 1488 | 0.66667 | 0 | 0 | 0 | 0 | 0 | 0.33333 | 0.33333 | 0.66667 | 0.082821 | 0 | 0 | 2232 | 3882 | 63 | 63 | 21 |  |  |  | Total | 717.2 | 107.6 | 609.6 | 1442.8 | 0.66796 | 0 | 0 | 0 | 0 | 0 | 0.33204 | 0.33204 | 0.67512 | 0.043474 | 0 | 1 | 2160 | 1972 | 63 | 63 | 18.3613 |  |  |  | Total | 1763.3 | 1294.6 | 468.7 | 468.7 | 0.20999 | 0 | 0 | 0 | 0 | 0 | 0.79001 | 0.79001 | 0.5675 | 0.11041 | 0 | 0 | 2232 | 5175 | 63 | 63 | 19 |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 63 | 63 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 63 | 63 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 63 | 63 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 63 | 63 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 63 | 63 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 63 | 63 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 63 | 63 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 63 | 63
COSTA SUR | 1-2 | 0 | 0 | 0 | 744 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.7021 | 0 | 744 | 0 | 21 | 21 | 0 | 100 |  | COSTA SUR | 1-2 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 744 | 0 | 21 | 21 | 0 | 100% |  | COSTA SUR | 1-2 | 0 | 0 | 0 | 720 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 0 | 21 | 21 | 0 | 100% |  | COSTA SUR | 1-2 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 744 | 0 | 21 | 21 | 0 | 100% | COSTA SUR | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | COSTA SUR | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | COSTA SUR | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | COSTA SUR | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | COSTA SUR | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | COSTA SUR | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | COSTA SUR | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | COSTA SUR | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0%
| Total | 0 | 0 | 0 | 744 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5591 | 37.6797 | 0 | 744 | 0 | 21 | 21 | 0 |  |  |  | Total | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 744 | 0 | 21 | 21 | 0 |  |  |  | Total | 0 | 0 | 0 | 720 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 0 | 21 | 21 | 0 |  |  |  | Total | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 744 | 0 | 21 | 21 | 0 |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 21 | 21 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 21 | 21 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 21 | 21 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 21 | 21 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 21 | 21 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 21 | 21 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 21 | 21 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 21 | 21
YABUCOA | 1-2 | 744 | 117.8 | 626.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 0 | 0 | 744 | 1773 | 21 | 15 | 15 | 100 |  | YABUCOA | 1-2 | 744 | 164.8 | 579.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.22195 | 0 | 0 | 744 | 2477 | 21 | 15 | 15 | 100% |  | YABUCOA | 1-2 | 720 | 68 | 652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.0013889 | 1.929e-06 | 2.6792e-09 | 0 | 720 | 1019 | 21 | 15 | 14.9853 | 100% |  | YABUCOA | 1-2 | 744 | 226.6 | 517.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.30511 | 0 | 0 | 744 | 3405 | 21 | 15 | 15 | 100% | YABUCOA | 1-2 | [16 empty] | 0 |  | 21 | 15 |  | 0% | YABUCOA | 1-2 | [16 empty] | 0 |  | 21 | 15 |  | 0% | YABUCOA | 1-2 | [16 empty] | 0 |  | 21 | 15 |  | 0% | YABUCOA | 1-2 | [16 empty] | 0 |  | 21 | 15 |  | 0% | YABUCOA | 1-2 | [16 empty] | 0 |  | 21 | 15 |  | 0% | YABUCOA | 1-2 | [16 empty] | 0 |  | 21 | 15 |  | 0% | YABUCOA | 1-2 | [16 empty] | 0 |  | 21 | 15 |  | 0% | YABUCOA | 1-2 | [16 empty] | 0 |  | 21 | 15 |  | 0%
| Total | 744 | 117.8 | 626.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 0 | 0 | 744 | 1773 | 21 | 15 | 15 |  |  |  | Total | 744 | 164.8 | 579.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.22195 | 0 | 0 | 744 | 2477 | 21 | 15 | 15 |  |  |  | Total | 720 | 68 | 652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.0013889 | 1.929e-06 | 2.6792e-09 | 0 | 720 | 1019 | 21 | 15 | 14.9853 |  |  |  | Total | 744 | 226.6 | 517.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.30511 | 0 | 0 | 744 | 3405 | 21 | 15 | 15 |  |  | Total | [16 empty] | 0 |  | 21 | 15 |  |  |  | Total | [16 empty] | 0 |  | 21 | 15 |  |  |  | Total | [16 empty] | 0 |  | 21 | 15 |  |  |  | Total | [16 empty] | 0 |  | 21 | 15 |  |  |  | Total | [16 empty] | 0 |  | 21 | 15 |  |  |  | Total | [16 empty] | 0 |  | 21 | 15 |  |  |  | Total | [16 empty] | 0 |  | 21 | 15 |  |  |  | Total | [16 empty] | 0 |  | 21 | 15
JOBOS | 1-2 | 744 | 169.1 | 574.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 0 | 0 | 744 | 3227 | 21 | 20 | 20 | 100 |  | JOBOS | 1-2 | 744 | 169.7 | 574.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.21915 | 0 | 0 | 744 | 3261 | 21 | 20 | 20 | 100% |  | JOBOS | 1-2 | 720 | 79 | 641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.0013889 | 1.929e-06 | 2.6792e-09 | 0 | 720 | 1441 | 21 | 20 | 20 | 100% |  | JOBOS | 1-2 | 744 | 239.8 | 504.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.30094 | 0 | 0 | 744 | 4478 | 21 | 20 | 20 | 100% | JOBOS | 1-2 | [16 empty] | 0 |  | 21 | 20 |  | 0% | JOBOS | 1-2 | [16 empty] | 0 |  | 21 | 20 |  | 0% | JOBOS | 1-2 | [16 empty] | 0 |  | 21 | 20 |  | 0% | JOBOS | 1-2 | [16 empty] | 0 |  | 21 | 20 |  | 0% | JOBOS | 1-2 | [16 empty] | 0 |  | 21 | 20 |  | 0% | JOBOS | 1-2 | [16 empty] | 0 |  | 21 | 20 |  | 0% | JOBOS | 1-2 | [16 empty] | 0 |  | 21 | 20 |  | 0% | JOBOS | 1-2 | [16 empty] | 0 |  | 21 | 20 |  | 0%
| Total | 744 | 169.1 | 574.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 86.2709 | 6.2688 | 0 | 744 | 3227 | 21 | 20 | 20 |  |  |  | Total | 744 | 169.7 | 574.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.21915 | 0 | 0 | 744 | 3261 | 21 | 20 | 20 |  |  |  | Total | 720 | 79 | 641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.0013889 | 1.929e-06 | 2.6792e-09 | 0 | 720 | 1441 | 21 | 20 | 20 |  |  |  | Total | 744 | 239.8 | 504.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.30094 | 0 | 0 | 744 | 4478 | 21 | 20 | 20 |  |  | Total | [16 empty] | 0 |  | 21 | 20 |  |  |  | Total | [16 empty] | 0 |  | 21 | 20 |  |  |  | Total | [16 empty] | 0 |  | 21 | 20 |  |  |  | Total | [16 empty] | 0 |  | 21 | 20 |  |  |  | Total | [16 empty] | 0 |  | 21 | 20 |  |  |  | Total | [16 empty] | 0 |  | 21 | 20 |  |  |  | Total | [16 empty] | 0 |  | 21 | 20 |  |  |  | Total | [16 empty] | 0 |  | 21 | 20
DAGUAO | 1-1 | 744 | 180.7 | 563.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 86.1809 | 7.3115 | 0 | 744 | 3232 | 21 | 20 | 20 | 100 |  | DAGUAO | 1-1 | 744 | 203 | 541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.24315 | 0 | 0 | 744 | 3618 | 21 | 20 | 20 | 100% |  | DAGUAO | 1-1 | 720 | 96 | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.12014 | 0 | 0 | 720 | 1730 | 21 | 20 | 20 | 100% |  | DAGUAO | 1-1 | 712.56 | 243.2 | 469.36 | 31.44 | 0.042258 | 0 | 0 | 0 | 0 | 0 | 0.95774 | 0.95774 | 0.11448 | 0.29718 | 0 | 1 | 744 | 4422 | 21 | 20 | 20 | 100% | DAGUAO | 1-1 | [16 empty] | 0 |  | 21 | 20 |  | 0% | DAGUAO | 1-1 | [16 empty] | 0 |  | 21 | 20 |  | 0% | DAGUAO | 1-1 | [16 empty] | 0 |  | 21 | 20 |  | 0% | DAGUAO | 1-1 | [16 empty] | 0 |  | 21 | 20 |  | 0% | DAGUAO | 1-1 | [16 empty] | 0 |  | 21 | 20 |  | 0% | DAGUAO | 1-1 | [16 empty] | 0 |  | 21 | 20 |  | 0% | DAGUAO | 1-1 | [16 empty] | 0 |  | 21 | 20 |  | 0% | DAGUAO | 1-1 | [16 empty] | 0 |  | 21 | 20 |  | 0%
| 1-2 | 744 | 2.9 | 741.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 11.8294 | 0 | 744 | 48 | 21 | 21 | 17 | 100 |  |  | 1-2 | 744 | 95.9 | 648.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.10241 | 0 | 0 | 744 | 1600 | 21 | 21 | 16.684 | 100% |  |  | 1-2 | 720 | 94.5 | 625.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.090476 | 0 | 0 | 720 | 1368 | 21 | 21 | 14.4762 | 100% |  |  | 1-2 | 691 | 231.5 | 459.5 | 53 | 0.071237 | 0 | 0 | 0 | 0 | 0 | 0.92876 | 0.92876 | 0.18629 | 0.17332 | 0 | 1 | 744 | 2708 | 21 | 21 | 12 | 100% |  | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0%
| Total | 1488 | 183.6 | 1304.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 32.6084 | 49.3769 | 0 | 1488 | 3280 | 42 | 41 | 37 |  |  |  | Total | 1488 | 298.9 | 1189.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.17106 | 0 | 0 | 1488 | 5218 | 42 | 41 | 36.684 |  |  |  | Total | 1440 | 190.5 | 1249.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.10495 | 0 | 0 | 1440 | 3098 | 42 | 41 | 34.4762 |  |  |  | Total | 1403.56 | 474.7 | 928.86 | 84.44 |  | 0 |  | 0 |  | 0 | 0.9429 | 0.9429 | 0.15126 | 0.23374 | 0 | 2 | 1488 | 7130 | 42 | 41 | 32 |  |  | Total | [16 empty] | 0 |  | 42 | 41 |  |  |  | Total | [16 empty] | 0 |  | 42 | 41 |  |  |  | Total | [16 empty] | 0 |  | 42 | 41 |  |  |  | Total | [16 empty] | 0 |  | 42 | 41 |  |  |  | Total | [16 empty] | 0 |  | 42 | 41 |  |  |  | Total | [16 empty] | 0 |  | 42 | 41 |  |  |  | Total | [16 empty] | 0 |  | 42 | 41 |  |  |  | Total | [16 empty] | 0 |  | 42 | 41
PALO SECO PW | MP 1 | 744 | 153.6 | 590.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 32.144 | 47.908 | 0 | 744 | 4028 | 27 | 27 | 27 | 100 |  | PALO SECO PW | MP 1 | 744 | 159.3 | 584.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.20565 | 0 | 0 | 744 | 4131 | 27 | 27 | 27 | 100% |  | PALO SECO PW | MP 1 | 720 | 64.3 | 655.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.083539 | 0 | 0 | 720 | 1624 | 27 | 27 | 27 | 100% |  | PALO SECO PW | MP 1 | 744 | 207.1 | 536.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.26508 | 0 | 0 | 744 | 5325 | 27 | 27 | 27 | 100% | PALO SECO PW | MP 1 | [16 empty] | 0 |  | 27 | 27 |  | 0% | PALO SECO PW | MP 1 | [16 empty] | 0 |  | 27 | 27 |  | 0% | PALO SECO PW | MP 1 | [16 empty] | 0 |  | 27 | 27 |  | 0% | PALO SECO PW | MP 1 | [16 empty] | 0 |  | 27 | 27 |  | 0% | PALO SECO PW | MP 1 | [16 empty] | 0 |  | 27 | 27 |  | 0% | PALO SECO PW | MP 1 | [16 empty] | 0 |  | 27 | 27 |  | 0% | PALO SECO PW | MP 1 | [16 empty] | 0 |  | 27 | 27 |  | 0% | PALO SECO PW | MP 1 | [16 empty] | 0 |  | 27 | 27 |  | 0%
FT-8 | MP 2 | 744 | 153.1 | 590.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 0 | 0 | 744 | 4006 | 27 | 27 | 27 | 100 |  | FT-8 | MP 2 | 744 | 158.9 | 585.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.20744 | 0 | 0 | 744 | 4167 | 27 | 27 | 27 | 100% |  | FT-8 | MP 2 | 720 | 64.3 | 655.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.083385 | 0 | 0 | 720 | 1621 | 27 | 27 | 27 | 100% |  | FT-8 | MP 2 | 744 | 207.5 | 536.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.27141 | 0 | 0 | 744 | 5452 | 27 | 27 | 27 | 100% | FT-8 | MP 2 | [16 empty] | 0 |  | 27 | 27 |  | 0% | FT-8 | MP 2 | [16 empty] | 0 |  | 27 | 27 |  | 0% | FT-8 | MP 2 | [16 empty] | 0 |  | 27 | 27 |  | 0% | FT-8 | MP 2 | [16 empty] | 0 |  | 27 | 27 |  | 0% | FT-8 | MP 2 | [16 empty] | 0 |  | 27 | 27 |  | 0% | FT-8 | MP 2 | [16 empty] | 0 |  | 27 | 27 |  | 0% | FT-8 | MP 2 | [16 empty] | 0 |  | 27 | 27 |  | 0% | FT-8 | MP 2 | [16 empty] | 0 |  | 27 | 27 |  | 0%
| MP 3 | 744 | 152 | 592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 58.3695 | 0 | 744 | 3556 | 27 | 27 | 27 | 100 |  |  | MP 3 | 744 | 149 | 595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.17692 | 0 | 0 | 744 | 3554 | 27 | 27 | 27 | 100% |  |  | MP 3 | 720 | 65.2 | 654.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.079733 | 0 | 0 | 720 | 1550 | 27 | 27 | 27 | 100% |  |  | MP 3 | 744 | 208.4 | 535.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.25075 | 0 | 0 | 744 | 5037 | 27 | 27 | 27 | 100% |  | MP 3 | [16 empty] | 0 |  | 27 | 27 |  | 0% |  | MP 3 | [16 empty] | 0 |  | 27 | 27 |  | 0% |  | MP 3 | [16 empty] | 0 |  | 27 | 27 |  | 0% |  | MP 3 | [16 empty] | 0 |  | 27 | 27 |  | 0% |  | MP 3 | [16 empty] | 0 |  | 27 | 27 |  | 0% |  | MP 3 | [16 empty] | 0 |  | 27 | 27 |  | 0% |  | MP 3 | [16 empty] | 0 |  | 27 | 27 |  | 0% |  | MP 3 | [16 empty] | 0 |  | 27 | 27 |  | 0%
| Total | 2232 | 458.7 | 1773.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 31.2515 | 53.6528 | 0 | 2232 | 11590 | 81 | 81 | 81 |  |  |  | Total | 2232 | 467.2 | 1764.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.19667 | 0 | 0 | 2232 | 11852 | 81 | 81 | 81 |  |  |  | Total | 2160 | 193.8 | 1966.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.082219 | 0 | 0 | 2160 | 4795 | 81 | 81 | 81 |  |  |  | Total | 2232 | 623 | 1609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.26241 | 0 | 0 | 2232 | 15814 | 81 | 81 | 81 |  |  | Total | [16 empty] | 0 |  | 81 | 81 |  |  |  | Total | [16 empty] | 0 |  | 81 | 81 |  |  |  | Total | [16 empty] | 0 |  | 81 | 81 |  |  |  | Total | [16 empty] | 0 |  | 81 | 81 |  |  |  | Total | [16 empty] | 0 |  | 81 | 81 |  |  |  | Total | [16 empty] | 0 |  | 81 | 81 |  |  |  | Total | [16 empty] | 0 |  | 81 | 81 |  |  |  | Total | [16 empty] | 0 |  | 81 | 81
CAMBALACHE | 2 | 738.13 | 370.63 | 367.5 | 5.87 | 0.78898 | 0 | 0 | 0 | 0 | 0 | 99.211 | 99.211 | 0 | 66.7054 | 0 | 744 | 21642 | 82.5 | 77.2 | 77.2 | 100 |  | CAMBALACHE | 2 | 744 | 415.28 | 328.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.41271 | 0 | 0 | 744 | 23705 | 82.5 | 77.2 | 77.2 | 100% |  | CAMBALACHE | 2 | 720 | 234.78 | 485.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.23237 | 0 | 0 | 720 | 12916 | 82.5 | 77.2 | 77.2 | 100% |  | CAMBALACHE | 2 | 734.42 | 475.3 | 259.12 | 2.7 | 0.003629 | 0 | 0 | 6.88 | 0.0092473 | 0 | 0.98712 | 0.98712 | 0.0056485 | 0.47752 | 0 | 1 | 744 | 27427 | 82.5 | 77.2 | 77 | 100% | CAMBALACHE | 2 | [16 empty] | 0 |  | 82.5 | 77.2 |  | 0% | CAMBALACHE | 2 | [16 empty] | 0 |  | 82.5 | 77.2 |  | 0% | CAMBALACHE | 2 | [16 empty] | 0 |  | 82.5 | 77.2 |  | 0% | CAMBALACHE | 2 | [16 empty] | 0 |  | 82.5 | 77.2 |  | 0% | CAMBALACHE | 2 | [16 empty] | 0 |  | 82.5 | 77.2 |  | 0% | CAMBALACHE | 2 | [16 empty] | 0 |  | 82.5 | 77.2 |  | 0% | CAMBALACHE | 2 | [16 empty] | 0 |  | 82.5 | 77.2 |  | 0% | CAMBALACHE | 2 | [16 empty] | 0 |  | 82.5 | 77.2 |  | 0%
| 3 | 0 | 0 | 0 | 744 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.855 | 0 | 744 | 0 | 82.5 | 74.6 | 0 | 100 |  |  | 3 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 744 | 0 | 82.5 | 74.6 | 0 | 100% |  |  | 3 | 0 | 0 | 0 | 720 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 720 | 0 | 82.5 | 74.6 | 0 | 100% |  |  | 3 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 744 | 0 | 82.5 | 74.6 | 0 | 100% |  | 3 | [16 empty] | 0 |  | 82.5 | 74.6 |  | 0% |  | 3 | [16 empty] | 0 |  | 82.5 | 74.6 |  | 0% |  | 3 | [16 empty] | 0 |  | 82.5 | 74.6 |  | 0% |  | 3 | [16 empty] | 0 |  | 82.5 | 74.6 |  | 0% |  | 3 | [16 empty] | 0 |  | 82.5 | 74.6 |  | 0% |  | 3 | [16 empty] | 0 |  | 82.5 | 74.6 |  | 0% |  | 3 | [16 empty] | 0 |  | 82.5 | 74.6 |  | 0% |  | 3 | [16 empty] | 0 |  | 82.5 | 74.6 |  | 0%
| Total | 738.13 | 370.63 | 367.5 | 749.87 | 100.789 | 0 | 0 | 0 | 0 | 0 | 99.211 | 99.211 | 100 | 0 | 0 | 1488 | 21642 | 165 | 151.8 | 77.2 |  |  |  | Total | 744 | 415.28 | 328.72 | 744 | 0.49144 | 0 | 0 | 0 | 0 | 0 | 0.50856 | 0.50856 | 0.49144 | 0.20989 | 0 | 0 | 1488 | 23705 | 165 | 151.8 | 77.2 |  |  |  | Total | 720 | 234.78 | 485.22 | 720 | 0.49144 | 0 | 0 | 0 | 0 | 0 | 0.50856 | 0.50856 | 0.49144 | 0.11817 | 0 | 0 | 1440 | 12916 | 165 | 151.8 | 77.2 |  |  |  | Total | 734.42 | 475.3 | 259.12 | 746.7 | 0.49328 | 0 | 0 | 6.88 | 0.0047028 | 0 | 0.50202 | 0.50202 | 0.49431 | 0.24285 | 0 | 1 | 1488 | 27427 | 165 | 151.8 | 77 |  |  | Total | [16 empty] | 0 |  | 165 | 151.8 |  |  |  | Total | [16 empty] | 0 |  | 165 | 151.8 |  |  |  | Total | [16 empty] | 0 |  | 165 | 151.8 |  |  |  | Total | [16 empty] | 0 |  | 165 | 151.8 |  |  |  | Total | [16 empty] | 0 |  | 165 | 151.8 |  |  |  | Total | [16 empty] | 0 |  | 165 | 151.8 |  |  |  | Total | [16 empty] | 0 |  | 165 | 151.8 |  |  |  | Total | [16 empty] | 0 |  | 165 | 151.8
MAYAGUEZ | 1 | 0 | 0 | 0 | 432 | 58.0645 | 0 | 0 | 312 | 41.9355 | 0 | 0 | 0 | 38.4451 | 46.4558 | 0 | 744 | 0 | 55 | 47.7 | 0 | 100 |  | MAYAGUEZ | 1 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 744 | 0 | 55 | 47.7 | 0 | 100% |  | MAYAGUEZ | 1 | 0 | 0 | 0 | 720 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 720 | 0 | 55 | 47.7 | 0 | 100% |  | MAYAGUEZ | 1 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 744 | 0 | 55 | 47.7 | 0 | 100% | MAYAGUEZ | 1 | [16 empty] | 0 |  | 55 | 47.7 |  | 0% | MAYAGUEZ | 1 | [16 empty] | 0 |  | 55 | 47.7 |  | 0% | MAYAGUEZ | 1 | [16 empty] | 0 |  | 55 | 47.7 |  | 0% | MAYAGUEZ | 1 | [16 empty] | 0 |  | 55 | 47.7 |  | 0% | MAYAGUEZ | 1 | [16 empty] | 0 |  | 55 | 47.7 |  | 0% | MAYAGUEZ | 1 | [16 empty] | 0 |  | 55 | 47.7 |  | 0% | MAYAGUEZ | 1 | [16 empty] | 0 |  | 55 | 47.7 |  | 0% | MAYAGUEZ | 1 | [16 empty] | 0 |  | 55 | 47.7 |  | 0%
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 100 | 0 | 0 | 0 | 0.23357 | 69.3556 | 0 | 744 | 0 | 55 | 49 | 0 | 100 |  |  | 2 | 0 | 0 | 0 | 576 | 0.77419 | 0 | 0 | 168 | 0.22581 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 744 | 0 | 55 | 49 | 0 | 100% |  |  | 2 | 0 | 0 | 0 | 720 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 720 | 0 | 55 | 49 | 0 | 100% |  |  | 2 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 744 | 0 | 55 | 49 | 0 | 100% |  | 2 | [16 empty] | 0 |  | 55 | 49 |  | 0% |  | 2 | [16 empty] | 0 |  | 55 | 49 |  | 0% |  | 2 | [16 empty] | 0 |  | 55 | 49 |  | 0% |  | 2 | [16 empty] | 0 |  | 55 | 49 |  | 0% |  | 2 | [16 empty] | 0 |  | 55 | 49 |  | 0% |  | 2 | [16 empty] | 0 |  | 55 | 49 |  | 0% |  | 2 | [16 empty] | 0 |  | 55 | 49 |  | 0% |  | 2 | [16 empty] | 0 |  | 55 | 49 |  | 0%
| 3 | 372 | 59.2 | 312.8 | 372 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 0.32041 | 74.0511 | 0 | 744 | 2565.2 | 55 | 55 | 23.5 | 100 |  |  | 3 | 353 | 59.2 | 293.8 | 391 | 0.52554 | 0 | 0 | 0 | 0 | 0 | 0.47446 | 0.47446 | 0.8685 | 0.062471 | 0 | 1 | 744 | 2556.3 | 55 | 55 | 23 | 100% |  |  | 3 | 360 | 21.35 | 338.65 | 360 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.94401 | 0.020477 | 0 | 0 | 720 | 810.9 | 55 | 55 | 23 | 100% |  |  | 3 | 359.125 | 68.25 | 290.875 | 384.875 | 0.51731 | 0 | 0 | 0 | 0 | 0 | 0.48269 | 0.48269 | 0.84938 | 0.072324 | 0 | 0.5 | 744 | 2959.5 | 55 | 55 | 23 | 100% |  | 3 | [16 empty] | 0 |  | 55 | 55 |  | 0% |  | 3 | [16 empty] | 0 |  | 55 | 55 |  | 0% |  | 3 | [16 empty] | 0 |  | 55 | 55 |  | 0% |  | 3 | [16 empty] | 0 |  | 55 | 55 |  | 0% |  | 3 | [16 empty] | 0 |  | 55 | 55 |  | 0% |  | 3 | [16 empty] | 0 |  | 55 | 55 |  | 0% |  | 3 | [16 empty] | 0 |  | 55 | 55 |  | 0% |  | 3 | [16 empty] | 0 |  | 55 | 55 |  | 0%
| 4 | 372 | 59.65 | 312.35 | 372 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 0 | 53.5838 | 0 | 744 | 2736.2 | 55 | 50.3 | 23.5 | 100 |  |  | 4 | 372 | 58.5 | 313.5 | 372 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.86411 | 0.070841 | 0 | 0 | 744 | 2651.1 | 55 | 50.3 | 24 | 100% |  |  | 4 | 358.375 | 22.45 | 335.925 | 361.625 | 0.50226 | 0 | 0 | 0 | 0 | 0 | 0.49774 | 0.49774 | 0.94155 | 0.027579 | 0 | 2 | 720 | 998.8 | 55 | 50.3 | 24 | 100% |  |  | 4 | 345.785 | 69.95 | 275.835 | 398.215 | 0.53524 | 0 | 0 | 0 | 0 | 0 | 0.46476 | 0.46476 | 0.85059 | 0.083146 | 0 | 0.5 | 744 | 3111.6 | 55 | 50.3 | 24 | 100% |  | 4 | [16 empty] | 0 |  | 55 | 50.3 |  | 0% |  | 4 | [16 empty] | 0 |  | 55 | 50.3 |  | 0% |  | 4 | [16 empty] | 0 |  | 55 | 50.3 |  | 0% |  | 4 | [16 empty] | 0 |  | 55 | 50.3 |  | 0% |  | 4 | [16 empty] | 0 |  | 55 | 50.3 |  | 0% |  | 4 | [16 empty] | 0 |  | 55 | 50.3 |  | 0% |  | 4 | [16 empty] | 0 |  | 55 | 50.3 |  | 0% |  | 4 | [16 empty] | 0 |  | 55 | 50.3 |  | 0%
| Total | 744 | 118.85 | 625.15 | 1176 | 158.0645 | 0 | 0 | 1056 | 141.9355 | 0 | 100 | 100 | 100 | 0 | 0 | 2976 | 5301.4 | 220 | 202 | 47 |  |  |  | Total | 725 | 117.7 | 607.3 | 2083 | 0.69153 | 0 | 0 | 168 | 0.054775 | 0 | 0.25369 | 0.25369 | 0.69422 | 0.034649 | 0 | 1 | 2976 | 5207.4 | 220 | 202 | 47 |  |  |  | Total | 718.375 | 43.8 | 674.575 | 2161.625 | 0.73992 | 0 | 0 | 0 | 0 | 0 | 0.26008 | 0.26008 | 0.9702 | 0.012443 | 0 | 2 | 2880 | 1809.7 | 220 | 202 | 47 |  |  |  | Total | 704.91 | 138.2 | 566.71 | 2271.09 | 0.75284 | 0 | 0 | 0 | 0 | 0 | 0.24716 | 0.24716 | 0.92178 | 0.040396 | 0 | 1 | 2976 | 6071.1 | 220 | 202 | 47 |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 220 | 202 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 220 | 202 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 220 | 202 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 220 | 202 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 220 | 202 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 220 | 202 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 220 | 202 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 220 | 202
SAN JUAN TM | TM 1 | 744 | 88.03 | 655.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 11.8294 | 0 | 744 | 2200.272 | 25 | 25 | 25 | 100 |  | SAN JUAN TM | TM 1 | 716.15 | 467.15 | 249 | 15.85 | 0.021304 | 12 | 0.016129 | 0 | 0 | 0 | 0.96257 | 0.96257 | 0.032816 | 0.60456 | 0 | 1 | 744 | 11244.853 | 25 | 25 | 25 | 100% |  | SAN JUAN TM | TM 1 | 713.13 | 374.17 | 338.96 | 6.87 | 0.0095417 | 0 | 0 | 0 | 0 | 0 | 0.99046 | 0.99046 | 0.01803 | 0.49469 | 0 | 2 | 720 | 8904.47 | 25 | 25 | 25 | 100% |  | SAN JUAN TM | TM 1 | 387.1 | 260.51 | 126.59 | 356.9 | 0.4797 | 0 | 0 | 0 | 0 | 0 | 0.5203 | 0.5203 | 0.57806 | 0.32195 | 0 | 1 | 744 | 5988.231 | 25 | 25 | 25 | 100% | SAN JUAN TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | SAN JUAN TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | SAN JUAN TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | SAN JUAN TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | SAN JUAN TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | SAN JUAN TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | SAN JUAN TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | SAN JUAN TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 2 | 568.87 | 361.94 | 206.93 | 175.13 | 23.539 | 0 | 0 | 0 | 0 | 0 | 76.461 | 76.461 | 0.32608 | 0.49377 | 0 | 744 | 9184.111 | 25 | 25 | 25 | 100 |  |  | TM 2 | 730.52 | 451.25 | 279.27 | 1.48 | 0.0019892 | 12 | 0.016129 | 0 | 0 | 0 | 0.98188 | 0.98188 | 0.0032691 | 0.61525 | 0 | 1 | 744 | 11443.562 | 25 | 25 | 25 | 100% |  |  | TM 2 | 704.3 | 336.15 | 368.15 | 15.7 | 0.021806 | 0 | 0 | 0 | 0 | 0 | 0.97819 | 0.97819 | 0.044621 | 0.4723 | 0 | 2 | 720 | 8501.49 | 25 | 25 | 25 | 100% |  |  | TM 2 | 705.92 | 237.19 | 468.73 | 38.08 | 0.051183 | 0 | 0 | 0 | 0 | 0 | 0.94882 | 0.94882 | 0.13834 | 0.2643 | 0 | 1 | 744 | 4916.05 | 25 | 25 | 25 | 100% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 3 | 568.86 | 369.72 | 199.14 | 175.14 | 23.5403 | 0 | 0 | 0 | 0 | 0 | 76.4597 | 76.4597 | 0.32144 | 0.47908 | 0 | 744 | 8910.887 | 25 | 25 | 25 | 100 |  |  | TM 3 | 730.52 | 474.92 | 255.6 | 1.48 | 0.0019892 | 12 | 0.016129 | 0 | 0 | 0 | 0.98188 | 0.98188 | 0.0031066 | 0.61094 | 0 | 1 | 744 | 11363.546 | 25 | 25 | 25 | 100% |  |  | TM 3 | 717.73 | 358.96 | 358.77 | 2.27 | 0.0031528 | 0 | 0 | 0 | 0 | 0 | 0.99685 | 0.99685 | 0.0062841 | 0.47026 | 0 | 1 | 720 | 8464.74 | 25 | 25 | 25 | 100% |  |  | TM 3 | 705.92 | 240.81 | 465.11 | 38.08 | 0.051183 | 0 | 0 | 0 | 0 | 0 | 0.94882 | 0.94882 | 0.13654 | 0.26226 | 0 | 1 | 744 | 4878.091 | 25 | 25 | 25 | 100% |  | TM 3 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 4 | 0 | 0 | 0 | 744 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 744 | 0 | 25 | 25 | 0 | 100 |  |  | TM 4 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 744 | 0 | 25 | 25 | 25 | 100% |  |  | TM 4 | 0 | 0 | 0 | 720 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 720 | 0 | 25 | 25 | 25 | 100% |  |  | TM 4 | 263.9 | 38.37 | 225.53 | 480.1 | 0.6453 | 0 | 0 | 0 | 0 | 0 | 0.3547 | 0.3547 | 0.92599 | 0.048808 | 0 | 0 | 744 | 907.829 | 25 | 25 | 25 | 100% |  | TM 4 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 5 | 744 | 478.33 | 265.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 0.5837 | 0 | 744 | 10856.733 | 25 | 25 | 25 | 100 |  |  | TM 5 | 732 | 448.06 | 283.94 | 0 | 0 | 12 | 0.016129 | 0 | 0 | 0 | 0.98387 | 0.98387 | 0 | 0.60642 | 0 | 0 | 744 | 11279.501 | 25 | 25 | 25 | 100% |  |  | TM 5 | 717.73 | 345.77 | 371.96 | 2.27 | 0.0031528 | 0 | 0 | 0 | 0 | 0 | 0.99685 | 0.99685 | 0.0065222 | 0.48855 | 0 | 1 | 720 | 8793.94 | 25 | 25 | 25 | 100% |  |  | TM 5 | 705.92 | 356.17 | 349.75 | 38.08 | 0.051183 | 0 | 0 | 0 | 0 | 0 | 0.94882 | 0.94882 | 0.096588 | 0.27333 | 0 | 1 | 744 | 5083.874 | 25 | 25 | 25 | 100% |  | TM 5 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 5 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 5 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 5 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 5 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 5 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 5 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 5 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 6 | 566.91 | 389.57 | 177.34 | 177.09 | 23.8024 | 0 | 0 | 0 | 0 | 0 | 76.1976 | 76.1976 | 0.31252 | 0.53653 | 0 | 744 | 9979.412 | 25 | 25 | 25 | 100 |  |  | TM 6 | 730.52 | 459.3 | 271.22 | 1.48 | 0.0019892 | 12 | 0.016129 | 0 | 0 | 0 | 0.98188 | 0.98188 | 0.0032119 | 0.61951 | 0 | 1 | 744 | 11522.883 | 25 | 25 | 25 | 100% |  |  | TM 6 | 717.73 | 378.32 | 339.41 | 2.27 | 0.0031528 | 0 | 0 | 0 | 0 | 0 | 0.99685 | 0.99685 | 0.0059644 | 0.54524 | 0 | 1 | 720 | 9814.27 | 25 | 25 | 25 | 100% |  |  | TM 6 | 705.92 | 251.86 | 454.06 | 38.08 | 0.051183 | 0 | 0 | 0 | 0 | 0 | 0.94882 | 0.94882 | 0.13134 | 0.29503 | 0 | 1 | 744 | 5487.486 | 25 | 25 | 25 | 100% |  | TM 6 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 6 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 6 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 6 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 6 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 6 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 6 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 6 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 7 | 744 | 528.95 | 215.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 0.66705 | 0 | 744 | 12407.201 | 25 | 25 | 25 | 100 |  |  | TM 7 | 732 | 556.95 | 175.05 | 0 | 0 | 12 | 0.016129 | 0 | 0 | 0 | 0.98387 | 0.98387 | 0 | 0.71246 | 0 | 0 | 744 | 13251.838 | 25 | 25 | 25 | 100% |  |  | TM 7 | 504.25 | 262.83 | 241.42 | 215.75 | 0.29965 | 0 | 0 | 0 | 0 | 0 | 0.70035 | 0.70035 | 0.45081 | 0.3727 | 0 | 1 | 720 | 6708.55 | 25 | 25 | 25 | 100% |  |  | TM 7 | 705.92 | 450.66 | 255.26 | 38.08 | 0.051183 | 0 | 0 | 0 | 0 | 0 | 0.94882 | 0.94882 | 0.077915 | 0.47727 | 0 | 1 | 744 | 8877.24 | 25 | 25 | 25 | 100% |  | TM 7 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 7 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 7 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 7 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 7 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 7 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 7 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 7 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 8 | 744 | 393.03 | 350.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 0.49855 | 0 | 744 | 9273.033 | 25 | 25 | 25 | 100 |  |  | TM 8 | 732 | 508.39 | 223.61 | 0 | 0 | 12 | 0.016129 | 0 | 0 | 0 | 0.98387 | 0.98387 | 0 | 0.65643 | 0 | 0 | 744 | 12209.617 | 25 | 25 | 25 | 100% |  |  | TM 8 | 717.73 | 448.79 | 268.94 | 2.27 | 0.0031528 | 0 | 0 | 0 | 0 | 0 | 0.99685 | 0.99685 | 0.0050326 | 0.59491 | 0 | 1 | 720 | 10708.47 | 25 | 25 | 25 | 100% |  |  | TM 8 | 705.92 | 454.19 | 251.73 | 38.08 | 0.051183 | 0 | 0 | 0 | 0 | 0 | 0.94882 | 0.94882 | 0.077356 | 0.4873 | 0 | 1 | 744 | 9063.705 | 25 | 25 | 25 | 100% |  | TM 8 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 8 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 8 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 8 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 8 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 8 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 8 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 8 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 9 | 0 | 0 | 0 | 744 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 744 | 0 | 25 | 25 | 0 | 100 |  |  | TM 9 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 744 | 0 | 25 | 25 | 25 | 100% |  |  | TM 9 | 0 | 0 | 0 | 720 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 720 | 0 | 25 | 25 | 25 | 100% |  |  | TM 9 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 744 | 0 | 25 | 25 | 25 | 100% |  | TM 9 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 9 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 9 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 9 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 9 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 9 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 9 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 9 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 10 | 522.96 | 353.91 | 169.05 | 221.04 | 29.7097 | 0 | 0 | 0 | 0 | 0 | 70.2903 | 70.2903 | 0.38445 | 0.46456 | 0 | 744 | 8640.77 | 25 | 25 | 25 | 100 |  |  | TM 10 | 732 | 495.5 | 236.5 | 0 | 0 | 12 | 0.016129 | 0 | 0 | 0 | 0.98387 | 0.98387 | 0 | 0.64641 | 0 | 0 | 744 | 12023.171 | 25 | 25 | 25 | 100% |  |  | TM 10 | 717.73 | 444.61 | 273.12 | 2.27 | 0.0031528 | 0 | 0 | 0 | 0 | 0 | 0.99685 | 0.99685 | 0.0050797 | 0.5907 | 0 | 1 | 720 | 10632.67 | 25 | 25 | 25 | 100% |  |  | TM 10 | 705.92 | 434.89 | 271.03 | 38.08 | 0.051183 | 0 | 0 | 0 | 0 | 0 | 0.94882 | 0.94882 | 0.080513 | 0.49181 | 0 | 1 | 744 | 9147.605 | 25 | 25 | 25 | 100% |  | TM 10 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 10 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 10 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 10 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 10 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 10 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 10 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 10 | [16 empty] | 0 |  | 25 | 25 |  | 0%
PALO SECO TM | TM 1 | 742.72 | 546.73 | 195.99 | 1.28 | 0.17204 | 0 | 0 | 0 | 0 | 0 | 99.828 | 99.828 | 0.0023357 | 0.69356 | 0 | 744 | 12900.142 | 25 | 25 | 25 | 100 |  | PALO SECO TM | TM 1 | 732 | 617.53 | 114.47 | 0 | 0 | 12 | 0.016129 | 0 | 0 | 0 | 0.98387 | 0.98387 | 0 | 0.77737 | 0 | 0 | 744 | 14459.08 | 25 | 25 | 25 | 100% |  | PALO SECO TM | TM 1 | 718.28 | 40.88 | 677.4 | 1.72 | 0.0023889 | 0 | 0 | 0 | 0 | 0 | 0.99761 | 0.99761 | 0.040376 | 0.055969 | 0 | 1 | 720 | 1007.45 | 25 | 25 | 25 | 100% |  | PALO SECO TM | TM 1 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 744 | 0 | 25 | 25 | 25 | 100% | PALO SECO TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | PALO SECO TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | PALO SECO TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | PALO SECO TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | PALO SECO TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | PALO SECO TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | PALO SECO TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | PALO SECO TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 2 | 742.24 | 547.53 | 194.71 | 1.76 | 0.23656 | 0 | 0 | 0 | 0 | 0 | 99.7634 | 99.7634 | 0.0032041 | 0.74051 | 0 | 744 | 13773.508 | 25 | 25 | 25 | 100 |  |  | TM 2 | 732 | 683.72 | 48.28 | 0 | 0 | 12 | 0.016129 | 0 | 0 | 0 | 0.98387 | 0.98387 | 0 | 0.49632 | 0 | 0 | 744 | 9231.643 | 25 | 25 | 25 | 100% |  |  | TM 2 | 720 | 447.67 | 272.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.59687 | 0 | 0 | 720 | 10743.7 | 25 | 25 | 25 | 100% |  |  | TM 2 | 744 | 595.33 | 148.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.67214 | 0 | 0 | 744 | 12501.852 | 25 | 25 | 25 | 100% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 3 | 744 | 394.75 | 349.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 0.53584 | 0 | 744 | 7973.27 | 20 | 20 | 20 | 100 |  |  | TM 3 | 732 | 599.2 | 132.8 | 0 | 0 | 12 | 0.016129 | 0 | 0 | 0 | 0.98387 | 0.98387 | 0 | 0.78399 | 0 | 0 | 744 | 11665.805 | 20 | 20 | 20 | 100% |  |  | TM 3 | 715.28 | 437.54 | 277.74 | 4.72 | 0.0065556 | 0 | 0 | 0 | 0 | 0 | 0.99344 | 0.99344 | 0.010672 | 0.59857 | 0 | 1 | 720 | 8619.48 | 20 | 20 | 20 | 100% |  |  | TM 3 | 744 | 589.02 | 154.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.63603 | 0 | 0 | 744 | 9464.193 | 20 | 20 | 20 | 100% |  | TM 3 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 20 | 20 |  | 0%
| TM 4 | 0 | 0 | 0 | 744 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 744 | 0 | 20 | 20 | 0 | 100 |  |  | TM 4 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 744 | 0 | 20 | 20 | 20 | 100% |  |  | TM 4 | 0 | 0 | 0 | 720 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 720 | 0 | 20 | 20 | 20 | 100% |  |  | TM 4 | 0 | 0 | 0 | 744 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 744 | 0 | 20 | 20 | 20 | 100% |  | TM 4 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 20 | 20 |  | 0%
| Total | 7432.56 | 4452.49 | 2980.07 | 2983.44 | 2801% | 0 | 0% | 0 | 0% | 0 | 7199% | 7199% | 612.9% | 128.1% | 0% | 10416 | 106099.339 | 340 | 340 | 270 |  |  |  | Total | 8031.71 | 5761.97 | 2269.74 | 2252.29 | 20.79% | 132 | 1.281% | 0 | 0% | 0 | 77.93% | 77.93% | 20.9% | 51.27% | 0% | 4 | 10416 | 129695.499 | 340 | 340 | 340 |  |  |  | Total | 7663.89 | 3875.69 | 3788.2 | 2416.11 | 23.19% | 0 | 0% | 0 | 0% | 0 | 76.81% | 76.81% | 24.94% | 37.95% | 0% | 12 | 10080 | 92899.23 | 340 | 340 | 340 |  |  |  | Total | 7080.44 | 3909 | 3171.44 | 3335.56 | 31.49% | 0 | 0% | 0 | 0% | 0 | 68.51% | 68.51% | 37.08% | 30.17% | 0% | 8 | 10416 | 76316.156 | 340 | 340 | 340 |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 340 | 340 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 340 | 340 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 340 | 340 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 340 | 340 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 340 | 340 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 340 | 340 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 340 | 340 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 340 | 340
| Total Peakers | 19521.39 | 8316.77 | 11204.62 | 7462.71 | 8702% | 2463.9 | 12841% | 1056 | 1878% | 0 | 28594% | 28594% | 2921% | 1429% | 0% |  | 232070.739 | 1566 | 1526.8 | 883.2 |  |  |  | Total Peakers | 18982.41 | 9447.51 | 9534.9 | 8245.59 | 29.92% | 3108 | 16.4% | 168 | 0.7247% | 0 | 52.96% | 52.96% | 30.62% | 21.59% | 0% | 11 | 30504 | 245232.899 | 1566 | 1526.8 | 887.884 |  |  |  | Total Peakers | 18482.965 | 5974.67 | 12508.295 | 8157.035 | 30.04% | 2880 | 16.11% | 0 | 0% | 0 | 51.56% | 53.85% | 32.41% | 14.1% | 6.142e-09% | 15 | 29520 | 157509.93 | 1566 | 1526.8 | 881.0228 |  |  |  | Total Peakers | 18710.43 | 9397 | 9313.43 | 8810.69 | 32.24% | 2976 | 16.11% | 6.88 | 0.04676% | 0 | 51.45% | 51.45% | 38.33% | 18.63% | 0% | 19 | 30504 | 211630.256 | 1566 | 1526.8 | 881 |  |  | Total Peakers | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 1566 | 1526.8 | 0 |  |  | Total Peakers | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 1566 | 1526.8 | 0 |  |  | Total Peakers | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 1566 | 1526.8 | 0 |  |  | Total Peakers | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 1566 | 1526.8 | 0 |  |  | Total Peakers | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 1566 | 1526.8 | 0 |  |  | Total Peakers | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 1566 | 1526.8 | 0 |  |  | Total Peakers | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 1566 | 1526.8 | 0 |  |  | Total Peakers | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 1566 | 1526.8 | 0
| Total System | 24932.09 | 13667.37 | 11264.72 | 9387.71 | 19348% | 3951.9 | 17279% | 1160.3 | 1583% | 822.37 | 55955% | 49102% | 1607% | 2070% | 7% |  | 1069007.739 | 4358 | 4017.8 | 2455.2 |  |  |  | Total System | 24175.07 | 14580.07 | 9595 | 10334.93 | 32.23% | 4596 | 10.01% | 326 | 0.8091% | 485.33 | 56.94% | 52.97% | 35.56% | 37.21% | 3.978% | 22 | 39432 | 1112366.899 | 4358 | 4017.8 | 2594.884 |  |  |  | Total System | 23891.685 | 11380.99 | 12510.695 | 9702.645 | 28.52% | 4320 | 9.906% | 245.67 | 1.022% | 583.3 | 59.68% | 56.04% | 32.66% | 36.09% | 4.513% | 24 | 38160 | 1046618.93 | 4358 | 4017.8 | 2394.0228 |  |  |  | Total System | 24795.22 | 15481.79 | 9313.43 | 10165.9 | 27.9% | 4464 | 9.906% | 6.88 | 0.01777% | 855.68 | 62.11% | 56.42% | 34.47% | 40.14% | 5.692% | 32 | 39432 | 1199930.256 | 4358 | 4017.8 | 2690 |  |  | Total System | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 0 | 0 | 4358 | 4017.8 | 0 |  |  | Total System | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 0 | 0 | 4358 | 4017.8 | 0 |  |  | Total System | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 0 | 0 | 4358 | 4017.8 | 0 |  |  | Total System | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 0 | 0 | 4358 | 4017.8 | 0 |  |  | Total System | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 0 | 0 | 4358 | 4017.8 | 0 |  |  | Total System | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 0 | 0 | 4358 | 4017.8 | 0 |  |  | Total System | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 0 | 0 | 4358 | 4017.8 | 0 |  |  | Total System | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 0 | 0 | 4358 | 4017.8 | 0
[17 empty] | Total Generation | 1069007.739
Note on AD42: Jan C Rodriguez Velazquez: It was later reported an outage of 11.57 hours on August 18th due to a free way by LUMA Energy.
Note on CB42: Jan C Rodriguez Velazquez: Fuel conservation 4.6 hours eliminated and transferred to Available hours.
Note on CB60: Jan C Rodriguez Velazquez: Fuel conservation 28.20 hours eliminated and transferred to Available hours.
Note on CB61: Jan C Rodriguez Velazquez: Fuel conservation 27.30 hours eliminated and transferred to Available hours.
Note on CB63: Jan C Rodriguez Velazquez: Fuel conservation 148.97 hours eliminated and transferred to Available hours.
Note on CB64: Jan C Rodriguez Velazquez: Fuel conservation 27.82 hours eliminated and transferred to Available hours.
Note on CB65: Jan C Rodriguez Velazquez: Fuel conservation 48.84 hours eliminated and transferred to Available hours.
Note on CB66: Jan C Rodriguez Velazquez: Fuel conservation 48.83 hours eliminated and transferred to Available hours.
Note on CB68: Jan C Rodriguez Velazquez: Fuel conservation 48.92 hours eliminated and transferred to Available hours.
Note on CB71: Jan C Rodriguez Velazquez: Fuel conservation 75.1 and 75 hours eliminated respectively and transferred to Available hours.

## KPI_FY 25-26 (OMC) (3) (hidden)
JULY 2025 | [24 empty] | AUGUST 2025 | [24 empty] | SEPTEMBER 2025 | [24 empty] | OCTOBER 2025 | [23 empty] | NOVEMBER 2025 | [23 empty] | DECEMBER 2025 | [23 empty] | JANUARY 2026 | [23 empty] | FEBRUARY 2026 | [23 empty] | MARCH 2026 | [23 empty] | APRIL 2026 | [23 empty] | MAY 2026 | [23 empty] | JUNE 2026
MONTH HOURS: | 744 | [23 empty] | MONTH HOURS: | 744 | [23 empty] | MONTH HOURS: | 720 | [23 empty] | MONTH HOURS: | 744 | [22 empty] | MONTH HOURS: | [23 empty] | MONTH HOURS: | [23 empty] | MONTH HOURS: | [23 empty] | MONTH HOURS: | [23 empty] | MONTH HOURS: | [23 empty] | MONTH HOURS: | [23 empty] | MONTH HOURS: | [23 empty] | MONTH HOURS:
PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum |  | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum |  | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum |  | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum
SAN | CT 5 | 726.4 | 726.4 | 0 | 0 | 0% | 0 | 0% | 17.6 | 2.366% | 57.773 | 97.63% | 89.87% | 7.367% | 82.42% | 7.765% | 0 | 744 | 93816 | 160 | 153 | 156 | 100% |  | SAN | CT 5 | 667.4 | 667.4 | 0 | 0 | 0% | 0 | 0% | 76.6 | 10.3% | 0 | 89.7% | 89.7% | 0% | 72.68% | 0% | 0 | 744 | 82735 | 160 | 153 | 151 | 100% |  | SAN | CT 5 | 653.83 | 653.83 | 0 | 18.7 | 2.597% | 0 | 0% | 47.47 | 6.593% | 0 | 90.81% | 90.81% | 2.781% | 76.11% | 0% | 1 | 720 | 83848 | 160 | 153 | 150 | 100% |  | SAN | CT 5 | 656.1 | 656.1 | 0 | 87.9 | 11.81% | 0 | 0% | 0 | 0% | 35.99 | 88.19% | 83.35% | 15.88% | 73.8% | 4.837% | 2 | 744 | 84004 | 160 | 153 | 150 | 100% | SAN | CT 5 | [16 empty] | 0 |  | 160 | 153 |  | 0% | SAN | CT 5 | [16 empty] | 0 |  | 160 | 153 |  | 0% | SAN | CT 5 | [16 empty] | 0 |  | 160 | 153 |  | 0% | SAN | CT 5 | [16 empty] | 0 |  | 160 | 153 |  | 0% | SAN | CT 5 | [16 empty] | 0 |  | 160 | 153 |  | 0% | SAN | CT 5 | [16 empty] | 0 |  | 160 | 153 |  | 0% | SAN | CT 5 | [16 empty] | 0 |  | 160 | 153 |  | 0% | SAN | CT 5 | [16 empty] | 0 |  | 160 | 153 |  | 0%
JUAN | ST 5 | 724.9 | 724.9 | 0 | 0 | 0% | 0 | 0% | 19.1 | 2.567% | 48.165 | 97.43% | 90.96% | 6.23% | 81.02% | 6.474% | 0 | 744 | 31345 | 60 | 52 | 53 | 100% |  | JUAN | ST 5 | 656.5 | 656.5 | 0 | 6.1 | 0.8199% | 0 | 0% | 81.4 | 10.94% | 0 | 88.24% | 88.24% | 0.9206% | 75.27% | 0% | 1 | 744 | 29122 | 60 | 52 | 53 | 100% |  | JUAN | ST 5 | 636.9 | 636.9 | 0 | 21.2 | 2.944% | 0 | 0% | 61.9 | 8.597% | 0 | 88.46% | 88.46% | 3.221% | 78.83% | 0% | 1 | 720 | 29514 | 60 | 52 | 50 | 100% |  | JUAN | ST 5 | 647.9 | 647.9 | 0 | 96.1 | 12.92% | 0 | 0% | 0 | 0% | 32.96 | 87.08% | 82.65% | 16.61% | 74.3% | 4.43% | 1 | 744 | 28747 | 60 | 52 | 50 | 100% | JUAN | ST 5 | [16 empty] | 0 |  | 60 | 52 |  | 0% | JUAN | ST 5 | [16 empty] | 0 |  | 60 | 52 |  | 0% | JUAN | ST 5 | [16 empty] | 0 |  | 60 | 52 |  | 0% | JUAN | ST 5 | [16 empty] | 0 |  | 60 | 52 |  | 0% | JUAN | ST 5 | [16 empty] | 0 |  | 60 | 52 |  | 0% | JUAN | ST 5 | [16 empty] | 0 |  | 60 | 52 |  | 0% | JUAN | ST 5 | [16 empty] | 0 |  | 60 | 52 |  | 0% | JUAN | ST 5 | [16 empty] | 0 |  | 60 | 52 |  | 0%
| CT 6 | 610.1 | 550 | 60.1 | 133.9 | 18% | 0 | 0% | 0 | 0% | 3.568 | 82% | 81.52% | 20% | 72.63% | 0.4796% | 8 | 744 | 75655 | 160 | 140 | 160 | 100% |  |  | CT 6 | 360.7 | 300.6 | 60.1 | 383.3 | 51.52% | 0 | 0% | 0 | 0% | 0 | 48.48% | 48.48% | 56.05% | 51.38% | 0% | 3 | 744 | 53514 | 160 | 140 | 160 | 100% |  |  | CT 6 | 583.7 | 581.3 | 2.4 | 0 | 0% | 0 | 0% | 136.3 | 18.93% | 0 | 81.07% | 81.07% | 0% | 78.63% | 0% | 0 | 720 | 79256 | 160 | 140 | 160 | 100% | 14.48% |  | CT 6 | 722.7 | 722.7 | 0 | 21.3 | 2.863% | 0 | 0% | 0 | 0% | 31.74 | 97.14% | 92.87% | 6.837% | 90.78% | 4.266% | 2 | 744 | 94559 | 160 | 140 | 160 | 100% |  | CT 6 | [16 empty] | 0 |  | 160 | 140 |  | 0% |  | CT 6 | [16 empty] | 0 |  | 160 | 140 |  | 0% |  | CT 6 | [16 empty] | 0 |  | 160 | 140 |  | 0% |  | CT 6 | [16 empty] | 0 |  | 160 | 140 |  | 0% |  | CT 6 | [16 empty] | 0 |  | 160 | 140 |  | 0% |  | CT 6 | [16 empty] | 0 |  | 160 | 140 |  | 0% |  | CT 6 | [16 empty] | 0 |  | 160 | 140 |  | 0% |  | CT 6 | [16 empty] | 0 |  | 160 | 140 |  | 0%
| ST 6 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 60 | 52 | 0 | 100% | 6.347% |  | ST 6 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 60 | 52 | 0 | 100% |  |  | ST 6 | 0 | 0 | 0 | 0 | 0% | 720 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 720 | 0 | 60 | 52 | 0 | 100% | 88.27% |  | ST 6 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 60 | 52 | 0 | 100% |  | ST 6 | [16 empty] | 0 |  | 60 | 52 |  | 0% |  | ST 6 | [16 empty] | 0 |  | 60 | 52 |  | 0% |  | ST 6 | [16 empty] | 0 |  | 60 | 52 |  | 0% |  | ST 6 | [16 empty] | 0 |  | 60 | 52 |  | 0% |  | ST 6 | [16 empty] | 0 |  | 60 | 52 |  | 0% |  | ST 6 | [16 empty] | 0 |  | 60 | 52 |  | 0% |  | ST 6 | [16 empty] | 0 |  | 60 | 52 |  | 0% |  | ST 6 | [16 empty] | 0 |  | 60 | 52 |  | 0%
| 7 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 100 | 100 | 0 | 100% |  |  | 7 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 100 | 100 | 0 | 100% | 56.81% |  | 7 | 0 | 0 | 0 | 0 | 0% | 720 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 720 | 0 | 100 | 100 | 0 | 100% |  |  | 7 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 100 | 100 | 0 | 100% |  | 7 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 7 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 7 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 7 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 7 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 7 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 7 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 7 | [16 empty] | 0 |  | 100 | 100 |  | 0%
| 9 | 645.7 | 645.7 | 0 | 30.7 | 4.126% | 0 | 0% | 67.6 | 9.086% | 21.804 | 86.79% | 83.86% | 7.52% | 63.14% | 2.931% | 3 | 744 | 46973 | 100 | 100 | 57 | 100% | 75.3% |  | 9 | 744 | 744 | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 74.17% | 0% | 1 | 744 | 55182 | 100 | 100 | 93 | 100% | 63.23% |  | 9 | 623.05 | 623.05 | 0 | 96.95 | 13.47% | 0 | 0% | 0 | 0% | 42.48 | 86.53% | 80.63% | 18.29% | 59.14% | 5.9% | 1 | 720 | 42580 | 100 | 100 | 81 | 100% | 6.733% |  | 9 | 744 | 744 | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 137.29 | 100% | 81.55% | 15.58% | 74.53% | 18.45% | 0 | 744 | 55447 | 100 | 100 | 82 | 100% |  | 9 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 9 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 9 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 9 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 9 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 9 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 9 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 9 | [16 empty] | 0 |  | 100 | 100 |  | 0%
| Total | 2707.1 | 2647 | 60.1 | 164.6 | 4.912% | 1488 | 25.46% | 104.3 | 2.352% | 131.31 | 67.28% | 64.48% | 8.38% | 55.79% | 3.157% | 11 | 4464 | 247789 | 640 | 597 | 426 |  | 41.93% |  | Total | 2428.6 | 2368.5 | 60.1 | 389.4 | 12.15% | 1488 | 25.46% | 158 | 3.592% | 0 | 58.79% | 58.79% | 13.22% | 49.66% | 0% | 5 | 4464 | 220553 | 640 | 597 | 457 |  | 50% |  | Total | 2497.48 | 2495.08 | 2.4 | 136.85 | 3.178% | 1440 | 25.46% | 245.67 | 6.878% | 42.48 | 64.48% | 63.5% | 4.056% | 54.72% | 0.9883% | 3 | 4320 | 235198 | 640 | 597 | 441 |  | 40.32% |  | Total | 2770.7 | 2770.7 | 0 | 205.3 | 4.824% | 1488 | 25.46% | 0 | 0% | 237.98 | 69.72% | 64% | 9.73% | 59.16% | 5.717% | 5 | 4464 | 262757 | 640 | 597 | 442 |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 640 | 597 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 640 | 597 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 640 | 597 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 640 | 597 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 640 | 597 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 640 | 597 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 640 | 597 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 640 | 597
PALO | 3 | 739.33 | 739.33 | 0 | 4.67 | 0.6277% | 0 | 0% | 0 | 0% | 271.25 | 99.37% | 62.91% | 27.18% | 65.96% | 36.46% | 1 | 744 | 87348 | 216 | 178 | 130 | 100% |  | PALO | 3 | 744 | 744 | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 296.22 | 100% | 60.19% | 28.48% | 66.97% | 39.81% | 0 | 744 | 88691 | 216 | 178 | 130 | 100% | 0% | PALO | 3 | 704.52 | 704.52 | 0 | 15.48 | 2.15% | 0 | 0% | 0 | 0% | 314.11 | 97.85% | 54.22% | 31.87% | 56.81% | 43.63% | 2 | 720 | 72802 | 216 | 178 | 100 | 100% |  | PALO | 3 | 640.45 | 640.45 | 0 | 103.55 | 13.92% | 0 | 0% | 0 | 0% | 264.55 | 86.08% | 50.52% | 36.5% | 53.92% | 35.56% | 1 | 744 | 71413 | 216 | 178 | 145 | 100% | PALO | 3 | [16 empty] | 0 |  | 216 | 178 |  | 0% | PALO | 3 | [16 empty] | 0 |  | 216 | 178 |  | 0% | PALO | 3 | [16 empty] | 0 |  | 216 | 178 |  | 0% | PALO | 3 | [16 empty] | 0 |  | 216 | 178 |  | 0% | PALO | 3 | [16 empty] | 0 |  | 216 | 178 |  | 0% | PALO | 3 | [16 empty] | 0 |  | 216 | 178 |  | 0% | PALO | 3 | [16 empty] | 0 |  | 216 | 178 |  | 0% | PALO | 3 | [16 empty] | 0 |  | 216 | 178 |  | 0%
SECO | 4 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 216 | 216 | 0 | 100% |  | SECO | 4 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 216 | 216 | 0 | 100% |  | SECO | 4 | 113.88 | 113.88 | 0 | 606.12 | 84.18% | 0 | 0% | 0 | 0% | 66.84 | 15.82% | 6.533% | 85.53% | 5.092% | 9.283% | 1 | 720 | 7919 | 216 | 216 | 80 | 100% |  | SECO | 4 | 649.99 | 649.99 | 0 | 94.01 | 12.64% | 0 | 0% | 0 | 0% | 193.48 | 87.36% | 61.36% | 30.67% | 52.7% | 26.01% | 6 | 744 | 84690 | 216 | 216 | 170 | 100% | SECO | 4 | [16 empty] | 0 |  | 216 | 216 |  | 0% | SECO | 4 | [16 empty] | 0 |  | 216 | 216 |  | 0% | SECO | 4 | [16 empty] | 0 |  | 216 | 216 |  | 0% | SECO | 4 | [16 empty] | 0 |  | 216 | 216 |  | 0% | SECO | 4 | [16 empty] | 0 |  | 216 | 216 |  | 0% | SECO | 4 | [16 empty] | 0 |  | 216 | 216 |  | 0% | SECO | 4 | [16 empty] | 0 |  | 216 | 216 |  | 0% | SECO | 4 | [16 empty] | 0 |  | 216 | 216 |  | 0%
| Total | 739.33 | 739.33 | 0 | 748.67 | 55.11% | 0 | 0% | 0 | 0% | 271.25 | 44.89% | 28.42% | 67.1% | 29.8% | 16.47% | 1 | 1488 | 87348 | 432 | 394 | 130 |  |  |  | Total | 744 | 744 | 0 | 744 | 54.82% | 0 | 0% | 0 | 0% | 296.22 | 45.18% | 27.19% | 67.69% | 30.26% | 17.99% | 0 | 1488 | 88691 | 432 | 394 | 130 |  |  |  | Total | 818.4 | 818.4 | 0 | 621.6 | 47.12% | 0 | 0% | 0 | 0% | 380.95 | 52.88% | 28.08% | 61.29% | 28.45% | 24.8% | 3 | 1440 | 80721 | 432 | 394 | 180 |  |  |  | Total | 1290.44 | 1290.44 | 0 | 197.56 | 13.22% | 0 | 0% | 0 | 0% | 458.03 | 86.78% | 56.46% | 33.3% | 53.25% | 30.32% | 7 | 1488 | 156103 | 432 | 394 | 315 |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 432 | 394 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 432 | 394 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 432 | 394 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 432 | 394 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 432 | 394 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 432 | 394 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 432 | 394 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 432 | 394
COSTA | 5 | 628.75 | 628.75 | 0 | 115.25 | 15.49% | 0 | 0% | 0 | 0% | 71.64 | 84.51% | 74.88% | 22.91% | 69.09% | 9.629% | 1 | 744 | 179910 | 410 | 350 | 0 | 100% |  | COSTA | 5 | 744 | 744 | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 87.57% | 0% | 0 | 744 | 228030 | 410 | 350 | 410 | 100% |  | COSTA | 5 | 720 | 720 | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 28.92 | 100% | 95.98% | 3.862% | 83.96% | 4.017% | 0 | 720 | 211590 | 410 | 350 | 290 | 100% |  | COSTA | 5 | 670.7 | 670.7 | 0 | 73.3 | 9.852% | 0 | 0% | 0 | 0% | 6.8 | 90.15% | 89.23% | 10.67% | 84.02% | 0.914% | 0 | 744 | 218790 | 410 | 350 | 410 | 100% | COSTA | 5 | [16 empty] | 0 |  | 410 | 350 |  | 0% | COSTA | 5 | [16 empty] | 0 |  | 410 | 350 |  | 0% | COSTA | 5 | [16 empty] | 0 |  | 410 | 350 |  | 0% | COSTA | 5 | [16 empty] | 0 |  | 410 | 350 |  | 0% | COSTA | 5 | [16 empty] | 0 |  | 410 | 350 |  | 0% | COSTA | 5 | [16 empty] | 0 |  | 410 | 350 |  | 0% | COSTA | 5 | [16 empty] | 0 |  | 410 | 350 |  | 0% | COSTA | 5 | [16 empty] | 0 |  | 410 | 350 |  | 0%
SUR | 6 | 744 | 744 | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 348.17 | 100% | 53.2% | 31.88% | 66.92% | 46.8% | 0 | 744 | 174250 | 410 | 350 | 350 | 100% |  | SUR | 6 | 646.55 | 646.55 | 0 | 97.45 | 13.1% | 0 | 0% | 0 | 0% | 49.49 | 86.9% | 80.25% | 18.52% | 71.09% | 6.652% | 2 | 744 | 185120 | 410 | 350 | 360 | 100% |  | SUR | 6 | 655.21 | 655.21 | 0 | 64.79 | 8.999% | 0 | 0% | 0 | 0% | 28.75 | 91% | 87.01% | 12.49% | 71.73% | 3.993% | 2 | 720 | 180760 | 410 | 350 | 252 | 100% |  | SUR | 6 | 744 | 744 | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 152.87 | 100% | 79.45% | 17.04% | 74.73% | 20.55% | 0 | 744 | 194590 | 410 | 350 | 292 | 100% | SUR | 6 | [16 empty] | 0 |  | 410 | 350 |  | 0% | SUR | 6 | [16 empty] | 0 |  | 410 | 350 |  | 0% | SUR | 6 | [16 empty] | 0 |  | 410 | 350 |  | 0% | SUR | 6 | [16 empty] | 0 |  | 410 | 350 |  | 0% | SUR | 6 | [16 empty] | 0 |  | 410 | 350 |  | 0% | SUR | 6 | [16 empty] | 0 |  | 410 | 350 |  | 0% | SUR | 6 | [16 empty] | 0 |  | 410 | 350 |  | 0% | SUR | 6 | [16 empty] | 0 |  | 410 | 350 |  | 0%
| Total | 1372.75 | 1372.75 | 0 | 115.25 | 7.745% | 0 | 0% | 0 | 0% | 419.81 | 92.25% | 64.04% | 27.4% | 68% | 28.21% | 1 | 1488 | 354160 | 820 | 700 | 350 |  |  |  | Total | 1390.55 | 1390.55 | 0 | 97.45 | 6.549% | 0 | 0% | 0 | 0% | 49.49 | 93.45% | 90.12% | 9.259% | 79.33% | 3.326% | 2 | 1488 | 413150 | 820 | 700 | 770 |  |  |  | Total | 1375.21 | 1375.21 | 0 | 64.79 | 4.499% | 0 | 0% | 0 | 0% | 57.67 | 95.5% | 91.5% | 8.177% | 77.85% | 4.005% | 2 | 1440 | 392350 | 820 | 700 | 542 |  |  |  | Total | 1414.7 | 1414.7 | 0 | 73.3 | 4.926% | 0 | 0% | 0 | 0% | 159.67 | 95.07% | 84.34% | 13.86% | 79.37% | 10.73% | 0 | 1488 | 413380 | 820 | 700 | 702 |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 820 | 700 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 820 | 700 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 820 | 700 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 820 | 700 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 820 | 700 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 820 | 700 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 820 | 700 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 820 | 700
AGUIRRE | 1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 450 | 450 | 410 | 100% |  | AGUIRRE | 1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 450 | 450 | 0 | 100% |  | AGUIRRE | 1 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 720 | 0 | 450 | 450 | 0 | 100% |  | AGUIRRE | 1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 450 | 450 | 0 | 100% | AGUIRRE | 1 | [16 empty] | 0 |  | 450 | 450 |  | 0% | AGUIRRE | 1 | [16 empty] | 0 |  | 450 | 450 |  | 0% | AGUIRRE | 1 | [16 empty] | 0 |  | 450 | 450 |  | 0% | AGUIRRE | 1 | [16 empty] | 0 |  | 450 | 450 |  | 0% | AGUIRRE | 1 | [16 empty] | 0 |  | 450 | 450 |  | 0% | AGUIRRE | 1 | [16 empty] | 0 |  | 450 | 450 |  | 0% | AGUIRRE | 1 | [16 empty] | 0 |  | 450 | 450 |  | 0% | AGUIRRE | 1 | [16 empty] | 0 |  | 450 | 450 |  | 0%
| 2 | 591.52 | 591.52 | 0 | 152.48 | 20.49% | 0 | 0% | 0 | 0% | 0 | 79.51% | 79.51% | 20.49% | 56.7% | 0% | 1 | 744 | 147640 | 450 | 350 | 256 | 100% |  |  | 2 | 629.51 | 629.51 | 0 | 114.49 | 15.39% | 0 | 0% | 0 | 0% | 139.62 | 84.61% | 65.85% | 28.76% | 55.58% | 18.77% | 4 | 744 | 144740 | 450 | 350 | 350 | 100% |  |  | 2 | 717.63 | 717.63 | 0 | 2.37 | 0.3292% | 0 | 0% | 0 | 0% | 102.2 | 99.67% | 85.48% | 12.72% | 71.76% | 14.19% | 1 | 720 | 180840 | 450 | 350 | 350 | 100% |  |  | 2 | 608.95 | 608.95 | 0 | 135.05 | 18.15% | 0 | 0% | 0 | 0% | 0 | 81.85% | 81.85% | 18.15% | 59.93% | 0% | 1 | 744 | 156060 | 450 | 350 | 350 | 100% |  | 2 | [16 empty] | 0 |  | 450 | 350 |  | 0% |  | 2 | [16 empty] | 0 |  | 450 | 350 |  | 0% |  | 2 | [16 empty] | 0 |  | 450 | 350 |  | 0% |  | 2 | [16 empty] | 0 |  | 450 | 350 |  | 0% |  | 2 | [16 empty] | 0 |  | 450 | 350 |  | 0% |  | 2 | [16 empty] | 0 |  | 450 | 350 |  | 0% |  | 2 | [16 empty] | 0 |  | 450 | 350 |  | 0% |  | 2 | [16 empty] | 0 |  | 450 | 350 |  | 0%
| Total | 591.52 | 591.52 | 0 | 896.48 | 65.22% | 0 | 0% | 0 | 0% | 0 | 34.78% | 34.78% | 65.22% | 24.81% | 0% | 1 | 1488 | 147640 | 900 | 800 | 666 |  |  |  | Total | 629.51 | 629.51 | 0 | 858.49 | 62.98% | 0 | 0% | 0 | 0% | 139.62 | 37.02% | 28.81% | 68.83% | 24.32% | 8.21% | 4 | 1488 | 144740 | 900 | 800 | 350 |  |  |  | Total | 717.63 | 717.63 | 0 | 722.37 | 56.39% | 0 | 0% | 0 | 0% | 102.2 | 43.61% | 37.4% | 61.81% | 31.4% | 6.21% | 1 | 1440 | 180840 | 900 | 800 | 350 |  |  |  | Total | 608.95 | 608.95 | 0 | 879.05 | 64.19% | 0 | 0% | 0 | 0% | 0 | 35.81% | 35.81% | 64.19% | 26.22% | 0% | 1 | 1488 | 156060 | 900 | 800 | 350 |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 900 | 800 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 900 | 800 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 900 | 800 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 900 | 800 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 900 | 800 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 900 | 800 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 900 | 800 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 900 | 800
| Total Baseloads | 5410.7 | 5350.6 | 60.1 | 1925 | 33.01% | 1488 | 6.102% | 104.3 | 0.5636% | 822.37 | 60.32% | 49.12% | 41.26% | 45.16% | 11.29% | 14 |  | 836937 | 2792 | 2491 | 1572 |  |  |  | Total Baseloads | 5192.66 | 5132.56 | 60.1 | 2089.34 | 33.65% | 1488 | 6.102% | 158 | 0.8608% | 485.33 | 59.39% | 52.97% | 38.58% | 46.79% | 6.416% | 11 | 8928 | 867134 | 2792 | 2491 | 1707 |  |  |  | Total Baseloads | 5408.72 | 5406.32 | 2.4 | 1545.61 | 27.59% | 1440 | 6.102% | 245.67 | 1.648% | 583.3 | 64.66% | 57.38% | 32.82% | 49.57% | 7.279% | 9 | 8640 | 889109 | 2792 | 2491 | 1513 |  |  |  | Total Baseloads | 6084.79 | 6084.79 | 0 | 1355.21 | 25.25% | 1488 | 6.102% | 0 | 0% | 855.68 | 68.65% | 59.47% | 32.11% | 53.33% | 9.181% | 13 | 8928 | 988300 | 2792 | 2491 | 1809 |  |  | Total Baseloads | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 2792 | 2491 |  |  |  | Total Baseloads | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 2792 | 2491 |  |  |  | Total Baseloads | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 2792 | 2491 |  |  |  | Total Baseloads | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 2792 | 2491 |  |  |  | Total Baseloads | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 2792 | 2491 |  |  |  | Total Baseloads | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 2792 | 2491 |  |  |  | Total Baseloads | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 2792 | 2491 |  |  |  | Total Baseloads | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 2792 | 2491
AGUIRRE CC | V-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 96 | 96 | 0 | 100% |  | AGUIRRE CC | V-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 96 | 96 | 0 | 100% |  | AGUIRRE CC | V-1 | 27.3 | 0 | 27.3 | 692.7 | 96.21% | 0 | 0% | 0 | 0% | 0 | 3.792% | 3.792% | 100% | 0% | 0% | 0 | 720 | 0 | 96 | 96 | 0 | 100% |  | AGUIRRE CC | V-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 96 | 96 | 0 | 100% | AGUIRRE CC | V-1 | [16 empty] | 0 |  | 96 | 96 |  | 0% | AGUIRRE CC | V-1 | [16 empty] | 0 |  | 96 | 96 |  | 0% | AGUIRRE CC | V-1 | [16 empty] | 0 |  | 96 | 96 |  | 0% | AGUIRRE CC | V-1 | [16 empty] | 0 |  | 96 | 96 |  | 0% | AGUIRRE CC | V-1 | [16 empty] | 0 |  | 96 | 96 |  | 0% | AGUIRRE CC | V-1 | [16 empty] | 0 |  | 96 | 96 |  | 0% | AGUIRRE CC | V-1 | [16 empty] | 0 |  | 96 | 96 |  | 0% | AGUIRRE CC | V-1 | [16 empty] | 0 |  | 96 | 96 |  | 0%
| 1-1 | 744 | 298 | 446 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 36.97% | 0% | 0 | 744 | 13752 | 50 | 50 | 50 | 100% |  |  | 1-1 | 741.3 | 393 | 348.3 | 2.7 | 0.3629% | 0 | 0% | 0 | 0% | 0 | 99.64% | 99.64% | 0.6823% | 34.46% | 0% | 1 | 744 | 12818 | 50 | 50 | 50 | 100% |  |  | 1-1 | 720 | 252 | 468 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 22.27% | 0% | 0 | 720 | 8017 | 50 | 50 | 50 | 100% |  |  | 1-1 | 744 | 510 | 234 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 44.95% | 0% | 0 | 744 | 16722 | 50 | 50 | 50 | 100% |  | 1-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-1 | [16 empty] | 0 |  | 50 | 50 |  | 0%
| 1-2 | 742.8 | 338 | 404.8 | 1.2 | 0.1613% | 0 | 0% | 0 | 0% | 0 | 99.84% | 99.84% | 0.3538% | 29.71% | 0% | 1 | 744 | 11051 | 50 | 50 | 50 | 100% |  |  | 1-2 | 729.5 | 335 | 394.5 | 14.5 | 1.949% | 0 | 0% | 0 | 0% | 0 | 98.05% | 98.05% | 4.149% | 28.95% | 0% | 0 | 744 | 10771 | 50 | 50 | 50 | 100% |  |  | 1-2 | 718.1 | 176 | 542.1 | 1.9 | 0.2639% | 0 | 0% | 0 | 0% | 0 | 99.74% | 99.74% | 1.068% | 15.41% | 0% | 0 | 720 | 5547 | 50 | 50 | 48 | 100% |  |  | 1-2 | 727.5 | 425 | 302.5 | 16.5 | 2.218% | 0 | 0% | 0 | 0% | 0 | 97.78% | 97.78% | 3.737% | 36.86% | 0% | 1 | 744 | 13713 | 50 | 50 | 50 | 100% |  | 1-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 50 | 50 |  | 0%
| 1-3 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 50 | 50 | 0 | 100% |  |  | 1-3 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 50 | 50 | 0 | 100% |  |  | 1-3 | 0 | 0 | 0 | 0 | 0% | 720 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 720 | 0 | 50 | 50 | 0 | 100% |  |  | 1-3 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 50 | 50 | 0 | 100% |  | 1-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-3 | [16 empty] | 0 |  | 50 | 50 |  | 0%
| 1-4 | 488.3 | 273 | 215.3 | 23.8 | 3.199% | 231.9 | 31.17% | 0 | 0% | 0 | 65.63% | 65.63% | 8.019% | 24.63% | 0% | 0 | 744 | 9164 | 50 | 50 | 50 | 100% |  |  | 1-4 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 50 | 50 | 0 | 100% |  |  | 1-4 | 0 | 0 | 0 | 0 | 0% | 720 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 720 | 0 | 50 | 50 | 0 | 100% |  |  | 1-4 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 50 | 50 | 0 | 100% |  | 1-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-4 | [16 empty] | 0 |  | 50 | 50 |  | 0%
| V-2 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 96 | 96 | 0 | 100% |  |  | V-2 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 96 | 96 | 0 | 100% |  |  | V-2 | 0 | 0 | 0 | 0 | 0% | 720 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 720 | 0 | 96 | 96 | 0 | 100% |  |  | V-2 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 96 | 96 | 0 | 100% |  | V-2 | [16 empty] | 0 |  | 96 | 96 |  | 0% |  | V-2 | [16 empty] | 0 |  | 96 | 96 |  | 0% |  | V-2 | [16 empty] | 0 |  | 96 | 96 |  | 0% |  | V-2 | [16 empty] | 0 |  | 96 | 96 |  | 0% |  | V-2 | [16 empty] | 0 |  | 96 | 96 |  | 0% |  | V-2 | [16 empty] | 0 |  | 96 | 96 |  | 0% |  | V-2 | [16 empty] | 0 |  | 96 | 96 |  | 0% |  | V-2 | [16 empty] | 0 |  | 96 | 96 |  | 0%
| 2-1 | 744 | 424.7 | 319.3 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 37.26% | 0% | 0 | 744 | 13859 | 50 | 50 | 50 | 100% |  |  | 2-1 | 690.6 | 397.5 | 293.1 | 53.4 | 7.177% | 0 | 0% | 0 | 0% | 0 | 92.82% | 92.82% | 11.84% | 34.19% | 0% | 2 | 744 | 12720 | 50 | 50 | 50 | 100% |  |  | 2-1 | 720 | 297.6 | 422.4 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 26.08% | 0% | 0 | 720 | 9389 | 50 | 50 | 50 | 100% |  |  | 2-1 | 450.1 | 322.9 | 127.2 | 293.9 | 39.5% | 0 | 0% | 0 | 0% | 0 | 60.5% | 60.5% | 47.65% | 28.6% | 0% | 5 | 744 | 10638 | 50 | 50 | 50 | 100% |  | 2-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 50 | 50 |  | 0%
| 2-2 | 744 | 453.3 | 290.7 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 39.52% | 0% | 0 | 744 | 14702 | 50 | 50 | 50 | 100% |  |  | 2-2 | 707.8 | 424.4 | 283.4 | 36.2 | 4.866% | 0 | 0% | 0 | 0% | 0 | 95.13% | 95.13% | 7.859% | 36.43% | 0% | 3 | 744 | 13551 | 50 | 50 | 50 | 100% |  |  | 2-2 | 718.1 | 242 | 476.1 | 1.9 | 0.2639% | 0 | 0% | 0 | 0% | 0 | 99.74% | 99.74% | 0.779% | 20.93% | 0% | 0 | 720 | 7533 | 50 | 50 | 50 | 100% |  |  | 2-2 | 638.2 | 293.8 | 344.4 | 105.8 | 14.22% | 0 | 0% | 0 | 0% | 0 | 85.78% | 85.78% | 26.48% | 25.09% | 0% | 1 | 744 | 9335 | 50 | 50 | 50 | 100% |  | 2-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-2 | [16 empty] | 0 |  | 50 | 50 |  | 0%
| 2-3 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 50 | 50 | 0 | 100% |  |  | 2-3 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 50 | 50 | 0 | 100% |  |  | 2-3 | 0 | 0 | 0 | 0 | 0% | 720 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 720 | 0 | 50 | 50 | 0 | 100% |  |  | 2-3 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 50 | 50 | 0 | 100% |  | 2-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-3 | [16 empty] | 0 |  | 50 | 50 |  | 0%
| 2-4 | 687.6 | 316.6 | 371 | 56.4 | 7.581% | 0 | 0% | 0 | 0% | 0 | 92.42% | 92.42% | 15.12% | 28.2% | 0% | 1 | 744 | 10491 | 50 | 50 | 50 | 100% |  |  | 2-4 | 660.5 | 321.3 | 339.2 | 83.5 | 11.22% | 0 | 0% | 0 | 0% | 0 | 88.78% | 88.78% | 20.63% | 27.08% | 0% | 0 | 744 | 10075 | 50 | 50 | 50 | 100% |  |  | 2-4 | 720 | 213.9 | 506.1 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 19.65% | 0% | 0 | 720 | 7074 | 50 | 50 | 50 | 100% |  |  | 2-4 | 744 | 464.1 | 279.9 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 41.41% | 0% | 0 | 744 | 15406 | 50 | 50 | 50 | 100% |  | 2-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-4 | [16 empty] | 0 |  | 50 | 50 |  | 0%
| Total | 4150.7 | 2103.6 | 2047.1 | 825.4 | 17.14% | 2463.9 | 35.74% | 0 | 0% | 0 | 47.12% | 47.12% | 18.2% | 16.58% | 0% | 2 | 7440 | 73019 | 592 | 592 | 300 |  |  |  | Total | 3529.7 | 1871.2 | 1658.5 | 934.3 | 18.38% | 2976 | 41.55% | 0 | 0% | 0 | 40.07% | 40.07% | 20.03% | 13.61% | 0% | 6 | 7440 | 59935 | 592 | 592 | 250 |  |  |  | Total | 3623.5 | 1181.5 | 2442 | 696.5 | 15.65% | 2880 | 41.55% | 0 | 0% | 0 | 42.8% | 42.8% | 16.37% | 8.812% | 0% | 0 | 7200 | 37560 | 592 | 592 | 248 |  |  |  | Total | 3303.8 | 2015.8 | 1288 | 1160.2 | 20.94% | 2976 | 41.55% | 0 | 0% | 0 | 37.5% | 37.5% | 22.79% | 14.94% | 0% | 7 | 7440 | 65814 | 592 | 592 | 250 |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 592 | 592 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 592 | 592 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 592 | 592 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 592 | 592 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 592 | 592 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 592 | 592 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 592 | 592 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 592 | 592
PALO | 1-1 | 504 | 128.6 | 375.4 | 240 | 32.26% | 0 | 0% | 0 | 0% | 0 | 67.74% | 67.74% | 65.11% | 14.7% | 0% | 0 | 744 | 2297 | 21 | 21 | 18 | 100% |  | PALO | 1-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 21 | 21 | 0 | 100% |  | PALO | 1-1 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 720 | 0 | 21 | 21 | 0 | 100% |  | PALO | 1-1 | 744 | 744 | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 0% | 0% | 0 | 744 | 0 | 21 | 21 | 0 | 100% | PALO | 1-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% | PALO | 1-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% | PALO | 1-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% | PALO | 1-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% | PALO | 1-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% | PALO | 1-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% | PALO | 1-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% | PALO | 1-1 | [16 empty] | 0 |  | 21 | 21 |  | 0%
SECO | 1-2 | 744 | 213.4 | 530.6 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 24.59% | 0% | 0 | 744 | 3842 | 21 | 21 | 18 | 100% |  | SECO | 1-2 | 744 | 180.76 | 563.24 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 24.85% | 0% | 0 | 744 | 3882 | 21 | 21 | 21 | 100% |  | SECO | 1-2 | 717.2 | 107.6 | 609.6 | 2.8 | 0.3889% | 0 | 0% | 0 | 0% | 0 | 99.61% | 99.61% | 2.536% | 13.04% | 0% | 1 | 720 | 1972 | 21 | 21 | 18.3613 | 100% |  | SECO | 1-2 | 275.3 | -193.4 | 468.7 | 468.7 | 63% | 0 | 0% | 0 | 0% | 0 | 37% | 37% | 170.3% | 33.12% | 0% | 0 | 744 | 5175 | 21 | 21 | 19 | 100% | SECO | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | SECO | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | SECO | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | SECO | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | SECO | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | SECO | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | SECO | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | SECO | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0%
| 2-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 21 | 21 | 0 | 100% |  |  | 2-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 21 | 21 | 0 | 100% |  |  | 2-1 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 720 | 0 | 21 | 21 | 0 | 100% |  |  | 2-1 | 744 | 744 | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 0% | 0% | 0 | 744 | 0 | 21 | 21 | 0 | 100% |  | 2-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 21 | 21 |  | 0%
| Total | 1248 | 342 | 906 | 984 | 44.09% | 0 | 0% | 0 | 0% | 0 | 55.91% | 55.91% | 55.04% | 13.1% | 0% | 0 | 2232 | 6139 | 63 | 63 | 36 |  |  |  | Total | 744 | 180.76 | 563.24 | 1488 | 66.67% | 0 | 0% | 0 | 0% | 0 | 33.33% | 33.33% | 66.67% | 8.282% | 0% | 0 | 2232 | 3882 | 63 | 63 | 21 |  |  |  | Total | 717.2 | 107.6 | 609.6 | 1442.8 | 66.8% | 0 | 0% | 0 | 0% | 0 | 33.2% | 33.2% | 67.51% | 4.347% | 0% | 1 | 2160 | 1972 | 63 | 63 | 18.3613 |  |  |  | Total | 1763.3 | 1294.6 | 468.7 | 468.7 | 21% | 0 | 0% | 0 | 0% | 0 | 79% | 79% | 56.75% | 11.04% | 0% | 0 | 2232 | 5175 | 63 | 63 | 19 |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 63 | 63 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 63 | 63 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 63 | 63 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 63 | 63 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 63 | 63 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 63 | 63 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 63 | 63 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 63 | 63
COSTA SUR | 1-2 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 21 | 21 | 0 | 100% |  | COSTA SUR | 1-2 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 21 | 21 | 0 | 100% |  | COSTA SUR | 1-2 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 720 | 0 | 21 | 21 | 0 | 100% |  | COSTA SUR | 1-2 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 21 | 21 | 0 | 100% | COSTA SUR | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | COSTA SUR | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | COSTA SUR | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | COSTA SUR | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | COSTA SUR | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | COSTA SUR | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | COSTA SUR | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | COSTA SUR | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0%
| Total | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 21 | 21 | 0 |  |  |  | Total | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 21 | 21 | 0 |  |  |  | Total | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 720 | 0 | 21 | 21 | 0 |  |  |  | Total | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 21 | 21 | 0 |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 21 | 21 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 21 | 21 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 21 | 21 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 21 | 21 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 21 | 21 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 21 | 21 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 21 | 21 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 21 | 21
YABUCOA | 1-2 | 744 | 117.8 | 626.2 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 15.89% | 0% | 0 | 744 | 1773 | 21 | 15 | 15 | 100% |  | YABUCOA | 1-2 | 744 | 164.8 | 579.2 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 22.2% | 0% | 0 | 744 | 2477 | 21 | 15 | 15 | 100% |  | YABUCOA | 1-2 | 720 | 68 | 652 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 100% | 0.1389% | 0.0001929% | 2.679e-07% | 0 | 720 | 1019 | 21 | 15 | 14.9853 | 100% |  | YABUCOA | 1-2 | 744 | 226.6 | 517.4 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 30.51% | 0% | 0 | 744 | 3405 | 21 | 15 | 15 | 100% | YABUCOA | 1-2 | [16 empty] | 0 |  | 21 | 15 |  | 0% | YABUCOA | 1-2 | [16 empty] | 0 |  | 21 | 15 |  | 0% | YABUCOA | 1-2 | [16 empty] | 0 |  | 21 | 15 |  | 0% | YABUCOA | 1-2 | [16 empty] | 0 |  | 21 | 15 |  | 0% | YABUCOA | 1-2 | [16 empty] | 0 |  | 21 | 15 |  | 0% | YABUCOA | 1-2 | [16 empty] | 0 |  | 21 | 15 |  | 0% | YABUCOA | 1-2 | [16 empty] | 0 |  | 21 | 15 |  | 0% | YABUCOA | 1-2 | [16 empty] | 0 |  | 21 | 15 |  | 0%
| Total | 744 | 117.8 | 626.2 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 15.89% | 0% | 0 | 744 | 1773 | 21 | 15 | 15 |  |  |  | Total | 744 | 164.8 | 579.2 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 22.2% | 0% | 0 | 744 | 2477 | 21 | 15 | 15 |  |  |  | Total | 720 | 68 | 652 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 100% | 0.1389% | 0.0001929% | 2.679e-07% | 0 | 720 | 1019 | 21 | 15 | 14.9853 |  |  |  | Total | 744 | 226.6 | 517.4 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 30.51% | 0% | 0 | 744 | 3405 | 21 | 15 | 15 |  |  | Total | [16 empty] | 0 |  | 21 | 15 |  |  |  | Total | [16 empty] | 0 |  | 21 | 15 |  |  |  | Total | [16 empty] | 0 |  | 21 | 15 |  |  |  | Total | [16 empty] | 0 |  | 21 | 15 |  |  |  | Total | [16 empty] | 0 |  | 21 | 15 |  |  |  | Total | [16 empty] | 0 |  | 21 | 15 |  |  |  | Total | [16 empty] | 0 |  | 21 | 15 |  |  |  | Total | [16 empty] | 0 |  | 21 | 15
JOBOS | 1-2 | 744 | 169.1 | 574.9 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 21.69% | 0% | 0 | 744 | 3227 | 21 | 20 | 20 | 100% |  | JOBOS | 1-2 | 744 | 169.7 | 574.3 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 21.92% | 0% | 0 | 744 | 3261 | 21 | 20 | 20 | 100% |  | JOBOS | 1-2 | 720 | 79 | 641 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 100% | 0.1389% | 0.0001929% | 2.679e-07% | 0 | 720 | 1441 | 21 | 20 | 20 | 100% |  | JOBOS | 1-2 | 744 | 239.8 | 504.2 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 30.09% | 0% | 0 | 744 | 4478 | 21 | 20 | 20 | 100% | JOBOS | 1-2 | [16 empty] | 0 |  | 21 | 20 |  | 0% | JOBOS | 1-2 | [16 empty] | 0 |  | 21 | 20 |  | 0% | JOBOS | 1-2 | [16 empty] | 0 |  | 21 | 20 |  | 0% | JOBOS | 1-2 | [16 empty] | 0 |  | 21 | 20 |  | 0% | JOBOS | 1-2 | [16 empty] | 0 |  | 21 | 20 |  | 0% | JOBOS | 1-2 | [16 empty] | 0 |  | 21 | 20 |  | 0% | JOBOS | 1-2 | [16 empty] | 0 |  | 21 | 20 |  | 0% | JOBOS | 1-2 | [16 empty] | 0 |  | 21 | 20 |  | 0%
| Total | 744 | 169.1 | 574.9 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 21.69% | 0% | 0 | 744 | 3227 | 21 | 20 | 20 |  |  |  | Total | 744 | 169.7 | 574.3 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 21.92% | 0% | 0 | 744 | 3261 | 21 | 20 | 20 |  |  |  | Total | 720 | 79 | 641 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 100% | 0.1389% | 0.0001929% | 2.679e-07% | 0 | 720 | 1441 | 21 | 20 | 20 |  |  |  | Total | 744 | 239.8 | 504.2 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 30.09% | 0% | 0 | 744 | 4478 | 21 | 20 | 20 |  |  | Total | [16 empty] | 0 |  | 21 | 20 |  |  |  | Total | [16 empty] | 0 |  | 21 | 20 |  |  |  | Total | [16 empty] | 0 |  | 21 | 20 |  |  |  | Total | [16 empty] | 0 |  | 21 | 20 |  |  |  | Total | [16 empty] | 0 |  | 21 | 20 |  |  |  | Total | [16 empty] | 0 |  | 21 | 20 |  |  |  | Total | [16 empty] | 0 |  | 21 | 20 |  |  |  | Total | [16 empty] | 0 |  | 21 | 20
DAGUAO | 1-1 | 744 | 180.7 | 563.3 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 21.72% | 0% | 0 | 744 | 3232 | 21 | 20 | 20 | 100% |  | DAGUAO | 1-1 | 744 | 203 | 541 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 24.31% | 0% | 0 | 744 | 3618 | 21 | 20 | 20 | 100% |  | DAGUAO | 1-1 | 720 | 96 | 624 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 12.01% | 0% | 0 | 720 | 1730 | 21 | 20 | 20 | 100% |  | DAGUAO | 1-1 | 712.56 | 243.2 | 469.36 | 31.44 | 4.226% | 0 | 0% | 0 | 0% | 0 | 95.77% | 95.77% | 11.45% | 29.72% | 0% | 1 | 744 | 4422 | 21 | 20 | 20 | 100% | DAGUAO | 1-1 | [16 empty] | 0 |  | 21 | 20 |  | 0% | DAGUAO | 1-1 | [16 empty] | 0 |  | 21 | 20 |  | 0% | DAGUAO | 1-1 | [16 empty] | 0 |  | 21 | 20 |  | 0% | DAGUAO | 1-1 | [16 empty] | 0 |  | 21 | 20 |  | 0% | DAGUAO | 1-1 | [16 empty] | 0 |  | 21 | 20 |  | 0% | DAGUAO | 1-1 | [16 empty] | 0 |  | 21 | 20 |  | 0% | DAGUAO | 1-1 | [16 empty] | 0 |  | 21 | 20 |  | 0% | DAGUAO | 1-1 | [16 empty] | 0 |  | 21 | 20 |  | 0%
| 1-2 | 744 | 2.9 | 741.1 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 0.3072% | 0% | 0 | 744 | 48 | 21 | 21 | 17 | 100% |  |  | 1-2 | 744 | 95.9 | 648.1 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 10.24% | 0% | 0 | 744 | 1600 | 21 | 21 | 16.684 | 100% |  |  | 1-2 | 720 | 94.5 | 625.5 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 9.048% | 0% | 0 | 720 | 1368 | 21 | 21 | 14.4762 | 100% |  |  | 1-2 | 691 | 231.5 | 459.5 | 53 | 7.124% | 0 | 0% | 0 | 0% | 0 | 92.88% | 92.88% | 18.63% | 17.33% | 0% | 1 | 744 | 2708 | 21 | 21 | 12 | 100% |  | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0%
| Total | 1488 | 183.6 | 1304.4 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 10.75% | 0% | 0 | 1488 | 3280 | 42 | 41 | 37 |  |  |  | Total | 1488 | 298.9 | 1189.1 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 17.11% | 0% | 0 | 1488 | 5218 | 42 | 41 | 36.684 |  |  |  | Total | 1440 | 190.5 | 1249.5 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 10.49% | 0% | 0 | 1440 | 3098 | 42 | 41 | 34.4762 |  |  |  | Total | 1403.56 | 474.7 | 928.86 | 84.44 |  | 0 |  | 0 |  | 0 | 94.29% | 94.29% | 15.13% | 23.37% | 0% | 2 | 1488 | 7130 | 42 | 41 | 32 |  |  | Total | [16 empty] | 0 |  | 42 | 41 |  |  |  | Total | [16 empty] | 0 |  | 42 | 41 |  |  |  | Total | [16 empty] | 0 |  | 42 | 41 |  |  |  | Total | [16 empty] | 0 |  | 42 | 41 |  |  |  | Total | [16 empty] | 0 |  | 42 | 41 |  |  |  | Total | [16 empty] | 0 |  | 42 | 41 |  |  |  | Total | [16 empty] | 0 |  | 42 | 41 |  |  |  | Total | [16 empty] | 0 |  | 42 | 41
PALO SECO PW | MP 1 | 744 | 153.6 | 590.4 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 20.05% | 0% | 0 | 744 | 4028 | 27 | 27 | 27 | 100% |  | PALO SECO PW | MP 1 | 744 | 159.3 | 584.7 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 20.56% | 0% | 0 | 744 | 4131 | 27 | 27 | 27 | 100% |  | PALO SECO PW | MP 1 | 720 | 64.3 | 655.7 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 8.354% | 0% | 0 | 720 | 1624 | 27 | 27 | 27 | 100% |  | PALO SECO PW | MP 1 | 744 | 207.1 | 536.9 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 26.51% | 0% | 0 | 744 | 5325 | 27 | 27 | 27 | 100% | PALO SECO PW | MP 1 | [16 empty] | 0 |  | 27 | 27 |  | 0% | PALO SECO PW | MP 1 | [16 empty] | 0 |  | 27 | 27 |  | 0% | PALO SECO PW | MP 1 | [16 empty] | 0 |  | 27 | 27 |  | 0% | PALO SECO PW | MP 1 | [16 empty] | 0 |  | 27 | 27 |  | 0% | PALO SECO PW | MP 1 | [16 empty] | 0 |  | 27 | 27 |  | 0% | PALO SECO PW | MP 1 | [16 empty] | 0 |  | 27 | 27 |  | 0% | PALO SECO PW | MP 1 | [16 empty] | 0 |  | 27 | 27 |  | 0% | PALO SECO PW | MP 1 | [16 empty] | 0 |  | 27 | 27 |  | 0%
FT-8 | MP 2 | 744 | 153.1 | 590.9 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 19.94% | 0% | 0 | 744 | 4006 | 27 | 27 | 27 | 100% |  | FT-8 | MP 2 | 744 | 158.9 | 585.1 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 20.74% | 0% | 0 | 744 | 4167 | 27 | 27 | 27 | 100% |  | FT-8 | MP 2 | 720 | 64.3 | 655.7 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 8.338% | 0% | 0 | 720 | 1621 | 27 | 27 | 27 | 100% |  | FT-8 | MP 2 | 744 | 207.5 | 536.5 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 27.14% | 0% | 0 | 744 | 5452 | 27 | 27 | 27 | 100% | FT-8 | MP 2 | [16 empty] | 0 |  | 27 | 27 |  | 0% | FT-8 | MP 2 | [16 empty] | 0 |  | 27 | 27 |  | 0% | FT-8 | MP 2 | [16 empty] | 0 |  | 27 | 27 |  | 0% | FT-8 | MP 2 | [16 empty] | 0 |  | 27 | 27 |  | 0% | FT-8 | MP 2 | [16 empty] | 0 |  | 27 | 27 |  | 0% | FT-8 | MP 2 | [16 empty] | 0 |  | 27 | 27 |  | 0% | FT-8 | MP 2 | [16 empty] | 0 |  | 27 | 27 |  | 0% | FT-8 | MP 2 | [16 empty] | 0 |  | 27 | 27 |  | 0%
| MP 3 | 744 | 152 | 592 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 17.7% | 0% | 0 | 744 | 3556 | 27 | 27 | 27 | 100% |  |  | MP 3 | 744 | 149 | 595 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 17.69% | 0% | 0 | 744 | 3554 | 27 | 27 | 27 | 100% |  |  | MP 3 | 720 | 65.2 | 654.8 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 7.973% | 0% | 0 | 720 | 1550 | 27 | 27 | 27 | 100% |  |  | MP 3 | 744 | 208.4 | 535.6 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 25.07% | 0% | 0 | 744 | 5037 | 27 | 27 | 27 | 100% |  | MP 3 | [16 empty] | 0 |  | 27 | 27 |  | 0% |  | MP 3 | [16 empty] | 0 |  | 27 | 27 |  | 0% |  | MP 3 | [16 empty] | 0 |  | 27 | 27 |  | 0% |  | MP 3 | [16 empty] | 0 |  | 27 | 27 |  | 0% |  | MP 3 | [16 empty] | 0 |  | 27 | 27 |  | 0% |  | MP 3 | [16 empty] | 0 |  | 27 | 27 |  | 0% |  | MP 3 | [16 empty] | 0 |  | 27 | 27 |  | 0% |  | MP 3 | [16 empty] | 0 |  | 27 | 27 |  | 0%
| Total | 2232 | 458.7 | 1773.3 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 19.23% | 0% | 0 | 2232 | 11590 | 81 | 81 | 81 |  |  |  | Total | 2232 | 467.2 | 1764.8 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 19.67% | 0% | 0 | 2232 | 11852 | 81 | 81 | 81 |  |  |  | Total | 2160 | 193.8 | 1966.2 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 8.222% | 0% | 0 | 2160 | 4795 | 81 | 81 | 81 |  |  |  | Total | 2232 | 623 | 1609 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 26.24% | 0% | 0 | 2232 | 15814 | 81 | 81 | 81 |  |  | Total | [16 empty] | 0 |  | 81 | 81 |  |  |  | Total | [16 empty] | 0 |  | 81 | 81 |  |  |  | Total | [16 empty] | 0 |  | 81 | 81 |  |  |  | Total | [16 empty] | 0 |  | 81 | 81 |  |  |  | Total | [16 empty] | 0 |  | 81 | 81 |  |  |  | Total | [16 empty] | 0 |  | 81 | 81 |  |  |  | Total | [16 empty] | 0 |  | 81 | 81 |  |  |  | Total | [16 empty] | 0 |  | 81 | 81
CAMBALACHE | 2 | 738.13 | 370.63 | 367.5 | 5.87 | 0.789% | 0 | 0% | 0 | 0% | 0 | 99.21% | 99.21% | 1.559% | 37.68% | 0% | 1 | 744 | 21642 | 82.5 | 77.2 | 77.2 | 100% |  | CAMBALACHE | 2 | 744 | 415.28 | 328.72 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 41.27% | 0% | 0 | 744 | 23705 | 82.5 | 77.2 | 77.2 | 100% |  | CAMBALACHE | 2 | 720 | 234.78 | 485.22 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 23.24% | 0% | 0 | 720 | 12916 | 82.5 | 77.2 | 77.2 | 100% |  | CAMBALACHE | 2 | 734.42 | 475.3 | 259.12 | 2.7 | 0.3629% | 0 | 0% | 6.88 | 0.9247% | 0 | 98.71% | 98.71% | 0.5649% | 47.75% | 0% | 1 | 744 | 27427 | 82.5 | 77.2 | 77 | 100% | CAMBALACHE | 2 | [16 empty] | 0 |  | 82.5 | 77.2 |  | 0% | CAMBALACHE | 2 | [16 empty] | 0 |  | 82.5 | 77.2 |  | 0% | CAMBALACHE | 2 | [16 empty] | 0 |  | 82.5 | 77.2 |  | 0% | CAMBALACHE | 2 | [16 empty] | 0 |  | 82.5 | 77.2 |  | 0% | CAMBALACHE | 2 | [16 empty] | 0 |  | 82.5 | 77.2 |  | 0% | CAMBALACHE | 2 | [16 empty] | 0 |  | 82.5 | 77.2 |  | 0% | CAMBALACHE | 2 | [16 empty] | 0 |  | 82.5 | 77.2 |  | 0% | CAMBALACHE | 2 | [16 empty] | 0 |  | 82.5 | 77.2 |  | 0%
| 3 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 82.5 | 74.6 | 0 | 100% |  |  | 3 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 82.5 | 74.6 | 0 | 100% |  |  | 3 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 720 | 0 | 82.5 | 74.6 | 0 | 100% |  |  | 3 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 82.5 | 74.6 | 0 | 100% |  | 3 | [16 empty] | 0 |  | 82.5 | 74.6 |  | 0% |  | 3 | [16 empty] | 0 |  | 82.5 | 74.6 |  | 0% |  | 3 | [16 empty] | 0 |  | 82.5 | 74.6 |  | 0% |  | 3 | [16 empty] | 0 |  | 82.5 | 74.6 |  | 0% |  | 3 | [16 empty] | 0 |  | 82.5 | 74.6 |  | 0% |  | 3 | [16 empty] | 0 |  | 82.5 | 74.6 |  | 0% |  | 3 | [16 empty] | 0 |  | 82.5 | 74.6 |  | 0% |  | 3 | [16 empty] | 0 |  | 82.5 | 74.6 |  | 0%
| Total | 738.13 | 370.63 | 367.5 | 749.87 | 49.54% | 0 | 0% | 0 | 0% | 0 | 49.61% | 50.46% | 49.94% | 19.16% | 0% | 1 | 1488 | 21642 | 165 | 151.8 | 77.2 |  |  |  | Total | 744 | 415.28 | 328.72 | 744 | 49.14% | 0 | 0% | 0 | 0% | 0 | 50.86% | 50.86% | 49.14% | 20.99% | 0% | 0 | 1488 | 23705 | 165 | 151.8 | 77.2 |  |  |  | Total | 720 | 234.78 | 485.22 | 720 | 49.14% | 0 | 0% | 0 | 0% | 0 | 50.86% | 50.86% | 49.14% | 11.82% | 0% | 0 | 1440 | 12916 | 165 | 151.8 | 77.2 |  |  |  | Total | 734.42 | 475.3 | 259.12 | 746.7 | 49.33% | 0 | 0% | 6.88 | 0.4703% | 0 | 50.2% | 50.2% | 49.43% | 24.28% | 0% | 1 | 1488 | 27427 | 165 | 151.8 | 77 |  |  | Total | [16 empty] | 0 |  | 165 | 151.8 |  |  |  | Total | [16 empty] | 0 |  | 165 | 151.8 |  |  |  | Total | [16 empty] | 0 |  | 165 | 151.8 |  |  |  | Total | [16 empty] | 0 |  | 165 | 151.8 |  |  |  | Total | [16 empty] | 0 |  | 165 | 151.8 |  |  |  | Total | [16 empty] | 0 |  | 165 | 151.8 |  |  |  | Total | [16 empty] | 0 |  | 165 | 151.8 |  |  |  | Total | [16 empty] | 0 |  | 165 | 151.8
MAYAGUEZ | 1 | 0 | 0 | 0 | 432 | 58.06% | 0 | 0% | 312 | 41.94% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 55 | 47.7 | 0 | 100% |  | MAYAGUEZ | 1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 55 | 47.7 | 0 | 100% |  | MAYAGUEZ | 1 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 720 | 0 | 55 | 47.7 | 0 | 100% |  | MAYAGUEZ | 1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 55 | 47.7 | 0 | 100% | MAYAGUEZ | 1 | [16 empty] | 0 |  | 55 | 47.7 |  | 0% | MAYAGUEZ | 1 | [16 empty] | 0 |  | 55 | 47.7 |  | 0% | MAYAGUEZ | 1 | [16 empty] | 0 |  | 55 | 47.7 |  | 0% | MAYAGUEZ | 1 | [16 empty] | 0 |  | 55 | 47.7 |  | 0% | MAYAGUEZ | 1 | [16 empty] | 0 |  | 55 | 47.7 |  | 0% | MAYAGUEZ | 1 | [16 empty] | 0 |  | 55 | 47.7 |  | 0% | MAYAGUEZ | 1 | [16 empty] | 0 |  | 55 | 47.7 |  | 0% | MAYAGUEZ | 1 | [16 empty] | 0 |  | 55 | 47.7 |  | 0%
| 2 | 0 | 0 | 0 | 0 | 0% | 0 | 0% | 744 | 100% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 55 | 49 | 0 | 100% |  |  | 2 | 0 | 0 | 0 | 576 | 77.42% | 0 | 0% | 168 | 22.58% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 55 | 49 | 0 | 100% |  |  | 2 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 720 | 0 | 55 | 49 | 0 | 100% |  |  | 2 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 55 | 49 | 0 | 100% |  | 2 | [16 empty] | 0 |  | 55 | 49 |  | 0% |  | 2 | [16 empty] | 0 |  | 55 | 49 |  | 0% |  | 2 | [16 empty] | 0 |  | 55 | 49 |  | 0% |  | 2 | [16 empty] | 0 |  | 55 | 49 |  | 0% |  | 2 | [16 empty] | 0 |  | 55 | 49 |  | 0% |  | 2 | [16 empty] | 0 |  | 55 | 49 |  | 0% |  | 2 | [16 empty] | 0 |  | 55 | 49 |  | 0% |  | 2 | [16 empty] | 0 |  | 55 | 49 |  | 0%
| 3 | 372 | 59.2 | 312.8 | 372 | 50% | 0 | 0% | 0 | 0% | 0 | 50% | 50% | 86.27% | 6.269% | 0% | 0 | 744 | 2565.2 | 55 | 55 | 23.5 | 100% |  |  | 3 | 353 | 59.2 | 293.8 | 391 | 52.55% | 0 | 0% | 0 | 0% | 0 | 47.45% | 47.45% | 86.85% | 6.247% | 0% | 1 | 744 | 2556.3 | 55 | 55 | 23 | 100% |  |  | 3 | 360 | 21.35 | 338.65 | 360 | 50% | 0 | 0% | 0 | 0% | 0 | 50% | 50% | 94.4% | 2.048% | 0% | 0 | 720 | 810.9 | 55 | 55 | 23 | 100% |  |  | 3 | 359.125 | 68.25 | 290.875 | 384.875 | 51.73% | 0 | 0% | 0 | 0% | 0 | 48.27% | 48.27% | 84.94% | 7.232% | 0% | 0.5 | 744 | 2959.5 | 55 | 55 | 23 | 100% |  | 3 | [16 empty] | 0 |  | 55 | 55 |  | 0% |  | 3 | [16 empty] | 0 |  | 55 | 55 |  | 0% |  | 3 | [16 empty] | 0 |  | 55 | 55 |  | 0% |  | 3 | [16 empty] | 0 |  | 55 | 55 |  | 0% |  | 3 | [16 empty] | 0 |  | 55 | 55 |  | 0% |  | 3 | [16 empty] | 0 |  | 55 | 55 |  | 0% |  | 3 | [16 empty] | 0 |  | 55 | 55 |  | 0% |  | 3 | [16 empty] | 0 |  | 55 | 55 |  | 0%
| 4 | 372 | 59.65 | 312.35 | 372 | 50% | 0 | 0% | 0 | 0% | 0 | 50% | 50% | 86.18% | 7.312% | 0% | 0 | 744 | 2736.2 | 55 | 50.3 | 23.5 | 100% |  |  | 4 | 372 | 58.5 | 313.5 | 372 | 50% | 0 | 0% | 0 | 0% | 0 | 50% | 50% | 86.41% | 7.084% | 0% | 0 | 744 | 2651.1 | 55 | 50.3 | 24 | 100% |  |  | 4 | 358.375 | 22.45 | 335.925 | 361.625 | 50.23% | 0 | 0% | 0 | 0% | 0 | 49.77% | 49.77% | 94.15% | 2.758% | 0% | 2 | 720 | 998.8 | 55 | 50.3 | 24 | 100% |  |  | 4 | 345.785 | 69.95 | 275.835 | 398.215 | 53.52% | 0 | 0% | 0 | 0% | 0 | 46.48% | 46.48% | 85.06% | 8.315% | 0% | 0.5 | 744 | 3111.6 | 55 | 50.3 | 24 | 100% |  | 4 | [16 empty] | 0 |  | 55 | 50.3 |  | 0% |  | 4 | [16 empty] | 0 |  | 55 | 50.3 |  | 0% |  | 4 | [16 empty] | 0 |  | 55 | 50.3 |  | 0% |  | 4 | [16 empty] | 0 |  | 55 | 50.3 |  | 0% |  | 4 | [16 empty] | 0 |  | 55 | 50.3 |  | 0% |  | 4 | [16 empty] | 0 |  | 55 | 50.3 |  | 0% |  | 4 | [16 empty] | 0 |  | 55 | 50.3 |  | 0% |  | 4 | [16 empty] | 0 |  | 55 | 50.3 |  | 0%
| Total | 744 | 118.85 | 625.15 | 1176 | 39.78% | 0 | 0% | 1056 | 34.16% | 0 | 26.06% | 26.06% | 68.56% | 3.527% | 0% | 0 | 2976 | 5301.4 | 220 | 202 | 47 |  |  |  | Total | 725 | 117.7 | 607.3 | 2083 | 69.15% | 0 | 0% | 168 | 5.477% | 0 | 25.37% | 25.37% | 69.42% | 3.465% | 0% | 1 | 2976 | 5207.4 | 220 | 202 | 47 |  |  |  | Total | 718.375 | 43.8 | 674.575 | 2161.625 | 73.99% | 0 | 0% | 0 | 0% | 0 | 26.01% | 26.01% | 97.02% | 1.244% | 0% | 2 | 2880 | 1809.7 | 220 | 202 | 47 |  |  |  | Total | 704.91 | 138.2 | 566.71 | 2271.09 | 75.28% | 0 | 0% | 0 | 0% | 0 | 24.72% | 24.72% | 92.18% | 4.04% | 0% | 1 | 2976 | 6071.1 | 220 | 202 | 47 |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 220 | 202 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 220 | 202 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 220 | 202 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 220 | 202 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 220 | 202 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 220 | 202 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 220 | 202 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 220 | 202
SAN JUAN TM | TM 1 | 744 | 88.03 | 655.97 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 11.83% | 0% | 0 | 744 | 2200.272 | 25 | 25 | 25 | 100% |  | SAN JUAN TM | TM 1 | 716.15 | 467.15 | 249 | 15.85 | 2.13% | 12 | 1.613% | 0 | 0% | 0 | 96.26% | 96.26% | 3.282% | 60.46% | 0% | 1 | 744 | 11244.853 | 25 | 25 | 25 | 100% |  | SAN JUAN TM | TM 1 | 713.13 | 374.17 | 338.96 | 6.87 | 0.9542% | 0 | 0% | 0 | 0% | 0 | 99.05% | 99.05% | 1.803% | 49.47% | 0% | 2 | 720 | 8904.47 | 25 | 25 | 25 | 100% |  | SAN JUAN TM | TM 1 | 387.1 | 260.51 | 126.59 | 356.9 | 47.97% | 0 | 0% | 0 | 0% | 0 | 52.03% | 52.03% | 57.81% | 32.19% | 0% | 1 | 744 | 5988.231 | 25 | 25 | 25 | 100% | SAN JUAN TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | SAN JUAN TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | SAN JUAN TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | SAN JUAN TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | SAN JUAN TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | SAN JUAN TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | SAN JUAN TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | SAN JUAN TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 2 | 568.87 | 361.94 | 206.93 | 175.13 | 23.54% | 0 | 0% | 0 | 0% | 0 | 76.46% | 76.46% | 32.61% | 49.38% | 0% | 0 | 744 | 9184.111 | 25 | 25 | 25 | 100% |  |  | TM 2 | 730.52 | 451.25 | 279.27 | 1.48 | 0.1989% | 12 | 1.613% | 0 | 0% | 0 | 98.19% | 98.19% | 0.3269% | 61.52% | 0% | 1 | 744 | 11443.562 | 25 | 25 | 25 | 100% |  |  | TM 2 | 704.3 | 336.15 | 368.15 | 15.7 | 2.181% | 0 | 0% | 0 | 0% | 0 | 97.82% | 97.82% | 4.462% | 47.23% | 0% | 2 | 720 | 8501.49 | 25 | 25 | 25 | 100% |  |  | TM 2 | 705.92 | 237.19 | 468.73 | 38.08 | 5.118% | 0 | 0% | 0 | 0% | 0 | 94.88% | 94.88% | 13.83% | 26.43% | 0% | 1 | 744 | 4916.05 | 25 | 25 | 25 | 100% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 3 | 568.86 | 369.72 | 199.14 | 175.14 | 23.54% | 0 | 0% | 0 | 0% | 0 | 76.46% | 76.46% | 32.14% | 47.91% | 0% | 0 | 744 | 8910.887 | 25 | 25 | 25 | 100% |  |  | TM 3 | 730.52 | 474.92 | 255.6 | 1.48 | 0.1989% | 12 | 1.613% | 0 | 0% | 0 | 98.19% | 98.19% | 0.3107% | 61.09% | 0% | 1 | 744 | 11363.546 | 25 | 25 | 25 | 100% |  |  | TM 3 | 717.73 | 358.96 | 358.77 | 2.27 | 0.3153% | 0 | 0% | 0 | 0% | 0 | 99.68% | 99.68% | 0.6284% | 47.03% | 0% | 1 | 720 | 8464.74 | 25 | 25 | 25 | 100% |  |  | TM 3 | 705.92 | 240.81 | 465.11 | 38.08 | 5.118% | 0 | 0% | 0 | 0% | 0 | 94.88% | 94.88% | 13.65% | 26.23% | 0% | 1 | 744 | 4878.091 | 25 | 25 | 25 | 100% |  | TM 3 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 4 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 25 | 25 | 0 | 100% |  |  | TM 4 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 25 | 25 | 25 | 100% |  |  | TM 4 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 720 | 0 | 25 | 25 | 25 | 100% |  |  | TM 4 | 263.9 | 38.37 | 225.53 | 480.1 | 64.53% | 0 | 0% | 0 | 0% | 0 | 35.47% | 35.47% | 92.6% | 4.881% | 0% | 0 | 744 | 907.829 | 25 | 25 | 25 | 100% |  | TM 4 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 5 | 744 | 478.33 | 265.67 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 58.37% | 0% | 0 | 744 | 10856.733 | 25 | 25 | 25 | 100% |  |  | TM 5 | 732 | 448.06 | 283.94 | 0 | 0% | 12 | 1.613% | 0 | 0% | 0 | 98.39% | 98.39% | 0% | 60.64% | 0% | 0 | 744 | 11279.501 | 25 | 25 | 25 | 100% |  |  | TM 5 | 717.73 | 345.77 | 371.96 | 2.27 | 0.3153% | 0 | 0% | 0 | 0% | 0 | 99.68% | 99.68% | 0.6522% | 48.86% | 0% | 1 | 720 | 8793.94 | 25 | 25 | 25 | 100% |  |  | TM 5 | 705.92 | 356.17 | 349.75 | 38.08 | 5.118% | 0 | 0% | 0 | 0% | 0 | 94.88% | 94.88% | 9.659% | 27.33% | 0% | 1 | 744 | 5083.874 | 25 | 25 | 25 | 100% |  | TM 5 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 5 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 5 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 5 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 5 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 5 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 5 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 5 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 6 | 566.91 | 389.57 | 177.34 | 177.09 | 23.8% | 0 | 0% | 0 | 0% | 0 | 76.2% | 76.2% | 31.25% | 53.65% | 0% | 0 | 744 | 9979.412 | 25 | 25 | 25 | 100% |  |  | TM 6 | 730.52 | 459.3 | 271.22 | 1.48 | 0.1989% | 12 | 1.613% | 0 | 0% | 0 | 98.19% | 98.19% | 0.3212% | 61.95% | 0% | 1 | 744 | 11522.883 | 25 | 25 | 25 | 100% |  |  | TM 6 | 717.73 | 378.32 | 339.41 | 2.27 | 0.3153% | 0 | 0% | 0 | 0% | 0 | 99.68% | 99.68% | 0.5964% | 54.52% | 0% | 1 | 720 | 9814.27 | 25 | 25 | 25 | 100% |  |  | TM 6 | 705.92 | 251.86 | 454.06 | 38.08 | 5.118% | 0 | 0% | 0 | 0% | 0 | 94.88% | 94.88% | 13.13% | 29.5% | 0% | 1 | 744 | 5487.486 | 25 | 25 | 25 | 100% |  | TM 6 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 6 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 6 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 6 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 6 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 6 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 6 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 6 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 7 | 744 | 528.95 | 215.05 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 66.71% | 0% | 0 | 744 | 12407.201 | 25 | 25 | 25 | 100% |  |  | TM 7 | 732 | 556.95 | 175.05 | 0 | 0% | 12 | 1.613% | 0 | 0% | 0 | 98.39% | 98.39% | 0% | 71.25% | 0% | 0 | 744 | 13251.838 | 25 | 25 | 25 | 100% |  |  | TM 7 | 504.25 | 262.83 | 241.42 | 215.75 | 29.97% | 0 | 0% | 0 | 0% | 0 | 70.03% | 70.03% | 45.08% | 37.27% | 0% | 1 | 720 | 6708.55 | 25 | 25 | 25 | 100% |  |  | TM 7 | 705.92 | 450.66 | 255.26 | 38.08 | 5.118% | 0 | 0% | 0 | 0% | 0 | 94.88% | 94.88% | 7.791% | 47.73% | 0% | 1 | 744 | 8877.24 | 25 | 25 | 25 | 100% |  | TM 7 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 7 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 7 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 7 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 7 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 7 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 7 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 7 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 8 | 744 | 393.03 | 350.97 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 49.86% | 0% | 0 | 744 | 9273.033 | 25 | 25 | 25 | 100% |  |  | TM 8 | 732 | 508.39 | 223.61 | 0 | 0% | 12 | 1.613% | 0 | 0% | 0 | 98.39% | 98.39% | 0% | 65.64% | 0% | 0 | 744 | 12209.617 | 25 | 25 | 25 | 100% |  |  | TM 8 | 717.73 | 448.79 | 268.94 | 2.27 | 0.3153% | 0 | 0% | 0 | 0% | 0 | 99.68% | 99.68% | 0.5033% | 59.49% | 0% | 1 | 720 | 10708.47 | 25 | 25 | 25 | 100% |  |  | TM 8 | 705.92 | 454.19 | 251.73 | 38.08 | 5.118% | 0 | 0% | 0 | 0% | 0 | 94.88% | 94.88% | 7.736% | 48.73% | 0% | 1 | 744 | 9063.705 | 25 | 25 | 25 | 100% |  | TM 8 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 8 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 8 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 8 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 8 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 8 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 8 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 8 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 9 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 25 | 25 | 0 | 100% |  |  | TM 9 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 25 | 25 | 25 | 100% |  |  | TM 9 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 720 | 0 | 25 | 25 | 25 | 100% |  |  | TM 9 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 25 | 25 | 25 | 100% |  | TM 9 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 9 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 9 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 9 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 9 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 9 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 9 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 9 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 10 | 522.96 | 353.91 | 169.05 | 221.04 | 29.71% | 0 | 0% | 0 | 0% | 0 | 70.29% | 70.29% | 38.45% | 46.46% | 0% | 0 | 744 | 8640.77 | 25 | 25 | 25 | 100% |  |  | TM 10 | 732 | 495.5 | 236.5 | 0 | 0% | 12 | 1.613% | 0 | 0% | 0 | 98.39% | 98.39% | 0% | 64.64% | 0% | 0 | 744 | 12023.171 | 25 | 25 | 25 | 100% |  |  | TM 10 | 717.73 | 444.61 | 273.12 | 2.27 | 0.3153% | 0 | 0% | 0 | 0% | 0 | 99.68% | 99.68% | 0.508% | 59.07% | 0% | 1 | 720 | 10632.67 | 25 | 25 | 25 | 100% |  |  | TM 10 | 705.92 | 434.89 | 271.03 | 38.08 | 5.118% | 0 | 0% | 0 | 0% | 0 | 94.88% | 94.88% | 8.051% | 49.18% | 0% | 1 | 744 | 9147.605 | 25 | 25 | 25 | 100% |  | TM 10 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 10 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 10 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 10 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 10 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 10 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 10 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 10 | [16 empty] | 0 |  | 25 | 25 |  | 0%
PALO SECO TM | TM 1 | 742.72 | 546.73 | 195.99 | 1.28 | 0.172% | 0 | 0% | 0 | 0% | 0 | 99.83% | 99.83% | 0.2336% | 69.36% | 0% | 0 | 744 | 12900.142 | 25 | 25 | 25 | 100% |  | PALO SECO TM | TM 1 | 732 | 617.53 | 114.47 | 0 | 0% | 12 | 1.613% | 0 | 0% | 0 | 98.39% | 98.39% | 0% | 77.74% | 0% | 0 | 744 | 14459.08 | 25 | 25 | 25 | 100% |  | PALO SECO TM | TM 1 | 718.28 | 40.88 | 677.4 | 1.72 | 0.2389% | 0 | 0% | 0 | 0% | 0 | 99.76% | 99.76% | 4.038% | 5.597% | 0% | 1 | 720 | 1007.45 | 25 | 25 | 25 | 100% |  | PALO SECO TM | TM 1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 25 | 25 | 25 | 100% | PALO SECO TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | PALO SECO TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | PALO SECO TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | PALO SECO TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | PALO SECO TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | PALO SECO TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | PALO SECO TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | PALO SECO TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 2 | 742.24 | 547.53 | 194.71 | 1.76 | 0.2366% | 0 | 0% | 0 | 0% | 0 | 99.76% | 99.76% | 0.3204% | 74.05% | 0% | 0 | 744 | 13773.508 | 25 | 25 | 25 | 100% |  |  | TM 2 | 732 | 683.72 | 48.28 | 0 | 0% | 12 | 1.613% | 0 | 0% | 0 | 98.39% | 98.39% | 0% | 49.63% | 0% | 0 | 744 | 9231.643 | 25 | 25 | 25 | 100% |  |  | TM 2 | 720 | 447.67 | 272.33 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 59.69% | 0% | 0 | 720 | 10743.7 | 25 | 25 | 25 | 100% |  |  | TM 2 | 744 | 595.33 | 148.67 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 67.21% | 0% | 0 | 744 | 12501.852 | 25 | 25 | 25 | 100% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 3 | 744 | 394.75 | 349.25 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 53.58% | 0% | 0 | 744 | 7973.27 | 20 | 20 | 20 | 100% |  |  | TM 3 | 732 | 599.2 | 132.8 | 0 | 0% | 12 | 1.613% | 0 | 0% | 0 | 98.39% | 98.39% | 0% | 78.4% | 0% | 0 | 744 | 11665.805 | 20 | 20 | 20 | 100% |  |  | TM 3 | 715.28 | 437.54 | 277.74 | 4.72 | 0.6556% | 0 | 0% | 0 | 0% | 0 | 99.34% | 99.34% | 1.067% | 59.86% | 0% | 1 | 720 | 8619.48 | 20 | 20 | 20 | 100% |  |  | TM 3 | 744 | 589.02 | 154.98 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 63.6% | 0% | 0 | 744 | 9464.193 | 20 | 20 | 20 | 100% |  | TM 3 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 20 | 20 |  | 0%
| TM 4 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 20 | 20 | 0 | 100% |  |  | TM 4 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 20 | 20 | 20 | 100% |  |  | TM 4 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 720 | 0 | 20 | 20 | 20 | 100% |  |  | TM 4 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 20 | 20 | 20 | 100% |  | TM 4 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 20 | 20 |  | 0%
| Total | 7432.56 | 4452.49 | 2980.07 | 2983.44 | 28.01% | 0 | 0% | 0 | 0% | 0 | 71.99% | 71.99% | 30.51% | 41.94% | 0% | 0 | 10416 | 106099.339 | 340 | 340 | 270 |  |  |  | Total | 8031.71 | 5761.97 | 2269.74 | 2252.29 | 20.79% | 132 | 1.281% | 0 | 0% | 0 | 77.93% | 77.93% | 20.9% | 51.27% | 0% | 4 | 10416 | 129695.499 | 340 | 340 | 340 |  |  |  | Total | 7663.89 | 3875.69 | 3788.2 | 2416.11 | 23.19% | 0 | 0% | 0 | 0% | 0 | 76.81% | 76.81% | 24.94% | 37.95% | 0% | 12 | 10080 | 92899.23 | 340 | 340 | 340 |  |  |  | Total | 7080.44 | 3909 | 3171.44 | 3335.56 | 31.49% | 0 | 0% | 0 | 0% | 0 | 68.51% | 68.51% | 37.08% | 30.17% | 0% | 8 | 10416 | 76316.156 | 340 | 340 | 340 |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 340 | 340 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 340 | 340 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 340 | 340 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 340 | 340 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 340 | 340 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 340 | 340 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 340 | 340 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 340 | 340
| Total Peakers | 19521.39 | 8316.77 | 11204.62 | 7462.71 | 26.27% | 2463.9 | 13.86% | 1056 | 4.519% | 0 | 55.27% | 55.36% | 31.53% | 20.43% | 0% | 3 |  | 232070.739 | 1566 | 1526.8 | 883.2 |  |  |  | Total Peakers | 18982.41 | 9447.51 | 9534.9 | 8245.59 | 29.92% | 3108 | 16.4% | 168 | 0.7247% | 0 | 52.96% | 52.96% | 30.62% | 21.59% | 0% | 11 | 30504 | 245232.899 | 1566 | 1526.8 | 887.884 |  |  |  | Total Peakers | 18482.965 | 5974.67 | 12508.295 | 8157.035 | 30.04% | 2880 | 16.11% | 0 | 0% | 0 | 51.56% | 53.85% | 32.41% | 14.1% | 6.142e-09% | 15 | 29520 | 157509.93 | 1566 | 1526.8 | 881.0228 |  |  |  | Total Peakers | 18710.43 | 9397 | 9313.43 | 8810.69 | 32.24% | 2976 | 16.11% | 6.88 | 0.04676% | 0 | 51.45% | 51.45% | 38.33% | 18.63% | 0% | 19 | 30504 | 211630.256 | 1566 | 1526.8 | 881 |  |  | Total Peakers | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 1566 | 1526.8 | 0 |  |  | Total Peakers | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 1566 | 1526.8 | 0 |  |  | Total Peakers | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 1566 | 1526.8 | 0 |  |  | Total Peakers | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 1566 | 1526.8 | 0 |  |  | Total Peakers | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 1566 | 1526.8 | 0 |  |  | Total Peakers | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 1566 | 1526.8 | 0 |  |  | Total Peakers | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 1566 | 1526.8 | 0 |  |  | Total Peakers | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 1566 | 1526.8 | 0
| Total System | 24932.09 | 13667.37 | 11264.72 | 9387.71 | 30.45% | 3951.9 | 9.049% | 1160.3 | 2.067% | 822.37 | 58.4% | 51.49% | 37.57% | 35.76% | 7% | 17 |  | 1069007.739 | 4358 | 4017.8 | 2455.2 |  |  |  | Total System | 24175.07 | 14580.07 | 9595 | 10334.93 | 32.23% | 4596 | 10.01% | 326 | 0.8091% | 485.33 | 56.94% | 52.97% | 35.56% | 37.21% | 3.978% | 22 | 39432 | 1112366.899 | 4358 | 4017.8 | 2594.884 |  |  |  | Total System | 23891.685 | 11380.99 | 12510.695 | 9702.645 | 28.52% | 4320 | 9.906% | 245.67 | 1.022% | 583.3 | 59.68% | 56.04% | 32.66% | 36.09% | 4.513% | 24 | 38160 | 1046618.93 | 4358 | 4017.8 | 2394.0228 |  |  |  | Total System | 24795.22 | 15481.79 | 9313.43 | 10165.9 | 27.9% | 4464 | 9.906% | 6.88 | 0.01777% | 855.68 | 62.11% | 56.42% | 34.47% | 40.14% | 5.692% | 32 | 39432 | 1199930.256 | 4358 | 4017.8 | 2690 |  |  | Total System | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 0 | 0 | 4358 | 4017.8 | 0 |  |  | Total System | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 0 | 0 | 4358 | 4017.8 | 0 |  |  | Total System | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 0 | 0 | 4358 | 4017.8 | 0 |  |  | Total System | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 0 | 0 | 4358 | 4017.8 | 0 |  |  | Total System | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 0 | 0 | 4358 | 4017.8 | 0 |  |  | Total System | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 0 | 0 | 4358 | 4017.8 | 0 |  |  | Total System | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 0 | 0 | 4358 | 4017.8 | 0 |  |  | Total System | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 0 | 0 | 4358 | 4017.8 | 0
[18 empty] | Total Generation | 1069007.739
Note on AE42: Jan C Rodriguez Velazquez: It was later reported an outage of 11.57 hours on August 18th due to a free way by LUMA Energy.
Note on CC42: Jan C Rodriguez Velazquez: Fuel conservation 4.6 hours eliminated and transferred to Available hours.
Note on CC60: Jan C Rodriguez Velazquez: Fuel conservation 28.20 hours eliminated and transferred to Available hours.
Note on CC61: Jan C Rodriguez Velazquez: Fuel conservation 27.30 hours eliminated and transferred to Available hours.
Note on CC63: Jan C Rodriguez Velazquez: Fuel conservation 148.97 hours eliminated and transferred to Available hours.
Note on CC64: Jan C Rodriguez Velazquez: Fuel conservation 27.82 hours eliminated and transferred to Available hours.
Note on CC65: Jan C Rodriguez Velazquez: Fuel conservation 48.84 hours eliminated and transferred to Available hours.
Note on CC66: Jan C Rodriguez Velazquez: Fuel conservation 48.83 hours eliminated and transferred to Available hours.
Note on CC68: Jan C Rodriguez Velazquez: Fuel conservation 48.92 hours eliminated and transferred to Available hours.
Note on CC71: Jan C Rodriguez Velazquez: Fuel conservation 75.1 and 75 hours eliminated respectively and transferred to Available hours.

## KPI_FY 25-26 (3) (hidden)
JULY 2025 | [24 empty] | AUGUST 2025 | [24 empty] | SEPTEMBER 2025 | [24 empty] | OCTOBER 2025 | [24 empty] | NOVEMBER 2025 | [23 empty] | DECEMBER 2025 | [23 empty] | JANUARY 2026 | [23 empty] | FEBRUARY 2026 | [23 empty] | MARCH 2026 | [23 empty] | APRIL 2026 | [23 empty] | MAY 2026 | [23 empty] | JUNE 2026
MONTH HOURS: | 744 | [23 empty] | MONTH HOURS: | 744 | [23 empty] | MONTH HOURS: | 720 | [23 empty] | MONTH HOURS: | 744 | [23 empty] | MONTH HOURS: | 720 | [22 empty] | MONTH HOURS: | [23 empty] | MONTH HOURS: | [23 empty] | MONTH HOURS: | [23 empty] | MONTH HOURS: | [23 empty] | MONTH HOURS: | [23 empty] | MONTH HOURS: | [23 empty] | MONTH HOURS:
PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum |  | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum |  | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum |  | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum |  | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum | PLANT | UNIT | AH | SH | RSH | FOH | FOF | POH | POF | MOH | MOF | EUDH | OA | EAF | EFOR | CF | EOF | FOO | Total Hours | Gross Generation | Nameplate Capacity | APT Capacity | Available Capacity | KPI Acum
SAN | CT 5 | 726.4 | 726.4 | 0 | 0 | 0% | 0 | 0% | 17.6 | 2.366% | 57.773 | 97.63% | 89.87% | 7.367% | 82.42% | 7.765% | 0 | 744 | 93816 | 160 | 153 | 156 | 100% |  | SAN | CT 5 | 667.4 | 667.4 | 0 | 0 | 0% | 0 | 0% | 76.6 | 10.3% | 0 | 89.7% | 89.7% | 0% | 72.68% | 0% | 0 | 744 | 82735 | 160 | 153 | 151 | 100% |  | SAN | CT 5 | 653.83 | 653.83 | 0 | 18.7 | 2.597% | 0 | 0% | 47.47 | 6.593% | 0 | 90.81% | 90.81% | 2.781% | 76.11% | 0% | 1 | 720 | 83848 | 160 | 153 | 150 | 100% |  | SAN | CT 5 | 656.1 | 656.1 | 0 | 87.9 | 11.81% | 0 | 0% | 0 | 0% | 35.99 | 88.19% | 83.35% | 15.88% | 73.8% | 4.837% | 2 | 744 | 84004 | 160 | 153 | 150 | 100% |  | SAN | CT 5 | 432.8 | 432.8 | 0 | 264.1 | 36.6806 | 0 | 0 | 23.1 | 3.2083 | 7.96 | 60.1111 | 59.0056 | 38.5977 | 50.1643 | 1.106% | 1 | 720 | 55261 | 160 | 153 | 153 | 9891% | SAN | CT 5 | [16 empty] | 0 |  | 160 | 153 |  | 0% | SAN | CT 5 | [16 empty] | 0 |  | 160 | 153 |  | 0% | SAN | CT 5 | [16 empty] | 0 |  | 160 | 153 |  | 0% | SAN | CT 5 | [16 empty] | 0 |  | 160 | 153 |  | 0% | SAN | CT 5 | [16 empty] | 0 |  | 160 | 153 |  | 0% | SAN | CT 5 | [16 empty] | 0 |  | 160 | 153 |  | 0% | SAN | CT 5 | [16 empty] | 0 |  | 160 | 153 |  | 0%
JUAN | ST 5 | 724.9 | 724.9 | 0 | 0 | 0% | 0 | 0% | 19.1 | 2.567% | 48.165 | 97.43% | 90.96% | 6.23% | 81.02% | 6.474% | 0 | 744 | 31345 | 60 | 52 | 53 | 100% |  | JUAN | ST 5 | 656.5 | 656.5 | 0 | 6.1 | 0.8199% | 0 | 0% | 81.4 | 10.94% | 0 | 88.24% | 88.24% | 0.9206% | 75.27% | 0% | 1 | 744 | 29122 | 60 | 52 | 53 | 100% |  | JUAN | ST 5 | 636.9 | 636.9 | 0 | 21.2 | 2.944% | 0 | 0% | 61.9 | 8.597% | 0 | 88.46% | 88.46% | 3.221% | 78.83% | 0% | 1 | 720 | 29514 | 60 | 52 | 50 | 100% |  | JUAN | ST 5 | 647.9 | 647.9 | 0 | 96.1 | 12.92% | 0 | 0% | 0 | 0% | 32.96 | 87.08% | 82.65% | 16.61% | 74.3% | 4.43% | 1 | 744 | 28747 | 60 | 52 | 50 | 100% |  | JUAN | ST 5 | 424.8 | 424.8 | 0 | 264.4 | 36.7222 | 0 | 0 | 30.8 | 4.2778 | 0 | 59 | 59 | 38.3633 | 51.7441 | 0% | 1 | 720 | 19373 | 60 | 52 | 52 | 10000% | JUAN | ST 5 | [16 empty] | 0 |  | 60 | 52 |  | 0% | JUAN | ST 5 | [16 empty] | 0 |  | 60 | 52 |  | 0% | JUAN | ST 5 | [16 empty] | 0 |  | 60 | 52 |  | 0% | JUAN | ST 5 | [16 empty] | 0 |  | 60 | 52 |  | 0% | JUAN | ST 5 | [16 empty] | 0 |  | 60 | 52 |  | 0% | JUAN | ST 5 | [16 empty] | 0 |  | 60 | 52 |  | 0% | JUAN | ST 5 | [16 empty] | 0 |  | 60 | 52 |  | 0%
| CT 6 | 610.1 | 550 | 60.1 | 133.9 | 18% | 0 | 0% | 0 | 0% | 3.568 | 82% | 81.52% | 20% | 72.63% | 0.4796% | 8 | 744 | 75655 | 160 | 140 | 160 | 100% |  |  | CT 6 | 360.7 | 300.6 | 60.1 | 383.3 | 51.52% | 0 | 0% | 0 | 0% | 0 | 48.48% | 48.48% | 56.05% | 51.38% | 0% | 3 | 744 | 53514 | 160 | 140 | 160 | 100% |  |  | CT 6 | 583.7 | 581.3 | 2.4 | 0 | 0% | 0 | 0% | 136.3 | 18.93% | 0 | 81.07% | 81.07% | 0% | 78.63% | 0% | 0 | 720 | 79256 | 160 | 140 | 160 | 100% | 14.48% |  | CT 6 | 722.7 | 722.7 | 0 | 21.3 | 2.863% | 0 | 0% | 0 | 0% | 31.74 | 97.14% | 92.87% | 6.837% | 90.78% | 4.266% | 2 | 744 | 94559 | 160 | 140 | 160 | 100% |  |  | CT 6 | 718.5 | 718.5 | 0 | 1.5 | 0.20833 | 0 | 0 | 0 | 0 | 0 | 99.7917 | 99.7917 | 0.20833 | 93.2063 | 0% | 1 | 720 | 93952 | 160 | 140 | 160 | 10000% |  | CT 6 | [16 empty] | 0 |  | 160 | 140 |  | 0% |  | CT 6 | [16 empty] | 0 |  | 160 | 140 |  | 0% |  | CT 6 | [16 empty] | 0 |  | 160 | 140 |  | 0% |  | CT 6 | [16 empty] | 0 |  | 160 | 140 |  | 0% |  | CT 6 | [16 empty] | 0 |  | 160 | 140 |  | 0% |  | CT 6 | [16 empty] | 0 |  | 160 | 140 |  | 0% |  | CT 6 | [16 empty] | 0 |  | 160 | 140 |  | 0%
| ST 6 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 60 | 52 | 0 | 100% | 6.347% |  | ST 6 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 60 | 52 | 0 | 100% |  |  | ST 6 | 0 | 0 | 0 | 0 | 0% | 720 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 720 | 0 | 60 | 52 | 0 | 100% | 88.27% |  | ST 6 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 60 | 52 | 0 | 100% | 75.7% |  | ST 6 | 0 | 0 | 0 | 0 | 0 | 720 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 720 | 0 | 60 | 52 | 0 | 10000% |  | ST 6 | [16 empty] | 0 |  | 60 | 52 |  | 0% |  | ST 6 | [16 empty] | 0 |  | 60 | 52 |  | 0% |  | ST 6 | [16 empty] | 0 |  | 60 | 52 |  | 0% |  | ST 6 | [16 empty] | 0 |  | 60 | 52 |  | 0% |  | ST 6 | [16 empty] | 0 |  | 60 | 52 |  | 0% |  | ST 6 | [16 empty] | 0 |  | 60 | 52 |  | 0% |  | ST 6 | [16 empty] | 0 |  | 60 | 52 |  | 0%
| 7 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 100 | 100 | 0 | 100% |  |  | 7 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 100 | 100 | 0 | 100% | 56.81% |  | 7 | 0 | 0 | 0 | 0 | 0% | 720 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 720 | 0 | 100 | 100 | 0 | 100% |  |  | 7 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 100 | 100 | 0 | 100% | 7.255% |  | 7 | 0 | 0 | 0 | 0 | 0 | 720 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 720 | 0 | 100 | 100 | 0 | 10000% |  | 7 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 7 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 7 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 7 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 7 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 7 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 7 | [16 empty] | 0 |  | 100 | 100 |  | 0%
| 9 | 645.7 | 645.7 | 0 | 30.7 | 4.126% | 0 | 0% | 67.6 | 9.086% | 21.804 | 86.79% | 83.86% | 7.52% | 63.14% | 2.931% | 3 | 744 | 46973 | 100 | 100 | 57 | 100% | 75.3% |  | 9 | 730.5 | 730.5 | 0 | 13.5 | 1.815% | 0 | 0% | 0 | 0% | 0 | 98.19% | 98.19% | 1.815% | 74.17% | 0% | 1 | 744 | 55182 | 100 | 100 | 93 | 100% | 63.23% |  | 9 | 623.05 | 623.05 | 0 | 96.95 | 13.47% | 0 | 0% | 0 | 0% | 42.48 | 86.53% | 80.63% | 18.29% | 59.14% | 5.9% | 1 | 720 | 42580 | 100 | 100 | 81 | 100% | 6.733% |  | 9 | 744 | 744 | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 137.29 | 100% | 81.55% | 15.58% | 74.53% | 18.45% | 0 | 744 | 55447 | 100 | 100 | 82 | 100% | 40.77% |  | 9 | 720 | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.6 | 100 | 82 | 15.2542 | 71.0222 | 18% | 0 | 720 | 51136 | 100 | 100 | 82 | 8218% |  | 9 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 9 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 9 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 9 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 9 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 9 | [16 empty] | 0 |  | 100 | 100 |  | 0% |  | 9 | [16 empty] | 0 |  | 100 | 100 |  | 0%
| Total | 2707.1 | 2647 | 60.1 | 164.6 | 4.912% | 1488 | 25.46% | 104.3 | 2.352% | 131.31 | 67.28% | 64.48% | 8.38% | 55.79% | 3.157% | 11 | 4464 | 247789 | 640 | 597 | 426 |  | 41.93% |  | Total | 2415.1 | 2355 | 60.1 | 402.9 | 12.46% | 1488 | 25.46% | 158 | 3.592% | 0 | 58.49% | 58.49% | 13.53% | 49.66% | 0% | 5 | 4464 | 220553 | 640 | 597 | 457 |  | 49.09% |  | Total | 2497.48 | 2495.08 | 2.4 | 136.85 | 3.178% | 1440 | 25.46% | 245.67 | 6.878% | 42.48 | 64.48% | 63.5% | 4.056% | 54.72% | 0.9883% | 3 | 4320 | 235198 | 640 | 597 | 441 |  | 40.32% |  | Total | 2770.7 | 2770.7 | 0 | 205.3 | 4.824% | 1488 | 25.46% | 0 | 0% | 237.98 | 69.72% | 64% | 9.73% | 59.16% | 5.717% | 5 | 4464 | 262757 | 640 | 597 | 442 |  |  |  | Total | 2296.1 | 2296.1 | 0 | 530 | 73.6111 | 1440 | 200 | 53.9 | 7.4861 | 137.56 | 318.9028 | 299.7972 | 22.5249 | 51.1172 | 3.298% | 3 | 4320 | 219722 | 640 | 597 | 447 |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 640 | 597 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 640 | 597 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 640 | 597 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 640 | 597 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 640 | 597 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 640 | 597 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 640 | 597
PALO | 3 | 739.33 | 739.33 | 0 | 4.67 | 0.6277% | 0 | 0% | 0 | 0% | 271.25 | 99.37% | 62.91% | 27.18% | 65.96% | 36.46% | 1 | 744 | 87348 | 216 | 178 | 130 | 100% |  | PALO | 3 | 744 | 744 | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 296.22 | 100% | 60.19% | 28.48% | 66.97% | 39.81% | 0 | 744 | 88691 | 216 | 178 | 130 | 100% | 0.9073% | PALO | 3 | 704.52 | 704.52 | 0 | 15.48 | 2.15% | 0 | 0% | 0 | 0% | 314.11 | 97.85% | 54.22% | 31.87% | 56.81% | 43.63% | 2 | 720 | 72802 | 216 | 178 | 100 | 100% |  | PALO | 3 | 640.45 | 640.45 | 0 | 103.55 | 13.92% | 0 | 0% | 0 | 0% | 264.55 | 86.08% | 50.52% | 36.5% | 53.92% | 35.56% | 1 | 744 | 71413 | 216 | 178 | 145 | 100% |  | PALO | 3 | 628.18 | 628.18 | 0 | 91.82 | 12.7528 | 0 | 0 | 0 | 0 | 206.5 | 87.2472 | 58.5667 | 32.1986 | 55.8669 | 28.68% | 2 | 720 | 71599 | 216 | 178 | 145 | 7161% | PALO | 3 | [16 empty] | 0 |  | 216 | 178 |  | 0% | PALO | 3 | [16 empty] | 0 |  | 216 | 178 |  | 0% | PALO | 3 | [16 empty] | 0 |  | 216 | 178 |  | 0% | PALO | 3 | [16 empty] | 0 |  | 216 | 178 |  | 0% | PALO | 3 | [16 empty] | 0 |  | 216 | 178 |  | 0% | PALO | 3 | [16 empty] | 0 |  | 216 | 178 |  | 0% | PALO | 3 | [16 empty] | 0 |  | 216 | 178 |  | 0%
SECO | 4 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 216 | 216 | 0 | 100% |  | SECO | 4 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 216 | 216 | 0 | 100% |  | SECO | 4 | 113.88 | 113.88 | 0 | 606.12 | 84.18% | 0 | 0% | 0 | 0% | 66.84 | 15.82% | 6.533% | 85.53% | 5.092% | 9.283% | 1 | 720 | 7919 | 216 | 216 | 80 | 100% |  | SECO | 4 | 649.99 | 649.99 | 0 | 94.01 | 12.64% | 0 | 0% | 0 | 0% | 193.48 | 87.36% | 61.36% | 30.67% | 52.7% | 26.01% | 6 | 744 | 84690 | 216 | 216 | 170 | 100% |  | SECO | 4 | 480.92 | 394.44 | 86.48 | 169.45 | 23.5347 | 0 | 0 | 69.63 | 9.6708 | 150.4 | 66.7944 | 45.9056 | 44.7787 | 23.242 | 20.89% | 2 | 720 | 36146 | 216 | 216 | 85 | 7932% | SECO | 4 | [16 empty] | 0 |  | 216 | 216 |  | 0% | SECO | 4 | [16 empty] | 0 |  | 216 | 216 |  | 0% | SECO | 4 | [16 empty] | 0 |  | 216 | 216 |  | 0% | SECO | 4 | [16 empty] | 0 |  | 216 | 216 |  | 0% | SECO | 4 | [16 empty] | 0 |  | 216 | 216 |  | 0% | SECO | 4 | [16 empty] | 0 |  | 216 | 216 |  | 0% | SECO | 4 | [16 empty] | 0 |  | 216 | 216 |  | 0%
| Total | 739.33 | 739.33 | 0 | 748.67 | 55.11% | 0 | 0% | 0 | 0% | 271.25 | 44.89% | 28.42% | 67.1% | 29.8% | 16.47% | 1 | 1488 | 87348 | 432 | 394 | 130 |  |  |  | Total | 744 | 744 | 0 | 744 | 54.82% | 0 | 0% | 0 | 0% | 296.22 | 45.18% | 27.19% | 67.69% | 30.26% | 17.99% | 0 | 1488 | 88691 | 432 | 394 | 130 |  |  |  | Total | 818.4 | 818.4 | 0 | 621.6 | 47.12% | 0 | 0% | 0 | 0% | 380.95 | 52.88% | 28.08% | 61.29% | 28.45% | 24.8% | 3 | 1440 | 80721 | 432 | 394 | 180 |  |  |  | Total | 1290.44 | 1290.44 | 0 | 197.56 | 13.22% | 0 | 0% | 0 | 0% | 458.03 | 86.78% | 56.46% | 33.3% | 53.25% | 30.32% | 7 | 1488 | 156103 | 432 | 394 | 315 |  |  |  | Total | 1109.1 | 1022.62 | 86.48 | 261.27 | 36.2875 | 0 | 0 | 69.63 | 9.6708 | 356.9 | 154.0417 | 104.4722 | 37.6751 | 37.9812 | 24.41% | 4 | 1440 | 107745 | 432 | 394 | 230 |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 432 | 394 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 432 | 394 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 432 | 394 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 432 | 394 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 432 | 394 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 432 | 394 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 432 | 394
COSTA | 5 | 628.75 | 628.75 | 0 | 115.25 | 15.49% | 0 | 0% | 0 | 0% | 71.64 | 84.51% | 74.88% | 22.91% | 69.09% | 9.629% | 1 | 744 | 179910 | 410 | 350 | 0 | 100% |  | COSTA | 5 | 744 | 744 | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 87.57% | 0% | 0 | 744 | 228030 | 410 | 350 | 410 | 100% |  | COSTA | 5 | 720 | 720 | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 28.92 | 100% | 95.98% | 3.862% | 83.96% | 4.017% | 0 | 720 | 211590 | 410 | 350 | 290 | 100% |  | COSTA | 5 | 670.7 | 670.7 | 0 | 73.3 | 9.852% | 0 | 0% | 0 | 0% | 6.8 | 90.15% | 89.23% | 10.67% | 84.02% | 0.914% | 0 | 744 | 218790 | 410 | 350 | 410 | 100% |  | COSTA | 5 | 720 | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 79.5238 | 0% | 0 | 720 | 200400 | 410 | 350 | 410 | 10000% | COSTA | 5 | [16 empty] | 0 |  | 410 | 350 |  | 0% | COSTA | 5 | [16 empty] | 0 |  | 410 | 350 |  | 0% | COSTA | 5 | [16 empty] | 0 |  | 410 | 350 |  | 0% | COSTA | 5 | [16 empty] | 0 |  | 410 | 350 |  | 0% | COSTA | 5 | [16 empty] | 0 |  | 410 | 350 |  | 0% | COSTA | 5 | [16 empty] | 0 |  | 410 | 350 |  | 0% | COSTA | 5 | [16 empty] | 0 |  | 410 | 350 |  | 0%
SUR | 6 | 744 | 744 | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 348.17 | 100% | 53.2% | 31.88% | 66.92% | 46.8% | 0 | 744 | 174250 | 410 | 350 | 350 | 100% |  | SUR | 6 | 646.55 | 646.55 | 0 | 97.45 | 13.1% | 0 | 0% | 0 | 0% | 49.49 | 86.9% | 80.25% | 18.52% | 71.09% | 6.652% | 2 | 744 | 185120 | 410 | 350 | 360 | 100% |  | SUR | 6 | 655.21 | 655.21 | 0 | 64.79 | 8.999% | 0 | 0% | 0 | 0% | 28.75 | 91% | 87.01% | 12.49% | 71.73% | 3.993% | 2 | 720 | 180760 | 410 | 350 | 252 | 100% |  | SUR | 6 | 744 | 744 | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 152.87 | 100% | 79.45% | 17.04% | 74.73% | 20.55% | 0 | 744 | 194590 | 410 | 350 | 292 | 100% |  | SUR | 6 | 651.05 | 651.05 | 0 | 68.95 | 9.5764 | 0 | 0 | 0 | 0 | 58.85 | 90.4236 | 82.25 | 16.4088 | 66.8373 | 8.174% | 1 | 720 | 168430 | 410 | 350 | 360 | 9191% | SUR | 6 | [16 empty] | 0 |  | 410 | 350 |  | 0% | SUR | 6 | [16 empty] | 0 |  | 410 | 350 |  | 0% | SUR | 6 | [16 empty] | 0 |  | 410 | 350 |  | 0% | SUR | 6 | [16 empty] | 0 |  | 410 | 350 |  | 0% | SUR | 6 | [16 empty] | 0 |  | 410 | 350 |  | 0% | SUR | 6 | [16 empty] | 0 |  | 410 | 350 |  | 0% | SUR | 6 | [16 empty] | 0 |  | 410 | 350 |  | 0%
| Total | 1372.75 | 1372.75 | 0 | 115.25 | 7.745% | 0 | 0% | 0 | 0% | 419.81 | 92.25% | 64.04% | 27.4% | 68% | 28.21% | 1 | 1488 | 354160 | 820 | 700 | 350 |  |  |  | Total | 1390.55 | 1390.55 | 0 | 97.45 | 6.549% | 0 | 0% | 0 | 0% | 49.49 | 93.45% | 90.12% | 9.259% | 79.33% | 3.326% | 2 | 1488 | 413150 | 820 | 700 | 770 |  |  |  | Total | 1375.21 | 1375.21 | 0 | 64.79 | 4.499% | 0 | 0% | 0 | 0% | 57.67 | 95.5% | 91.5% | 8.177% | 77.85% | 4.005% | 2 | 1440 | 392350 | 820 | 700 | 542 |  |  |  | Total | 1414.7 | 1414.7 | 0 | 73.3 | 4.926% | 0 | 0% | 0 | 0% | 159.67 | 95.07% | 84.34% | 13.86% | 79.37% | 10.73% | 0 | 1488 | 413380 | 820 | 700 | 702 |  |  |  | Total | 1371.05 | 1371.05 | 0 | 68.95 | 9.5764 | 0 | 0 | 0 | 0 | 58.85 | 190.4236 | 182.25 | 8.5265 | 73.1806 | 4.087% | 1 | 1440 | 368830 | 820 | 700 | 770 |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 820 | 700 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 820 | 700 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 820 | 700 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 820 | 700 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 820 | 700 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 820 | 700 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 820 | 700
AGUIRRE | 1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 450 | 450 | 0 | 100% |  | AGUIRRE | 1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 450 | 450 | 0 | 100% |  | AGUIRRE | 1 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 720 | 0 | 450 | 450 | 0 | 100% |  | AGUIRRE | 1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 450 | 450 | 0 | 100% |  | AGUIRRE | 1 | 0 | 0 | 0 | 720 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0% | 0 | 720 | 0 | 450 | 450 | 0 | 10000% | AGUIRRE | 1 | [16 empty] | 0 |  | 450 | 450 |  | 0% | AGUIRRE | 1 | [16 empty] | 0 |  | 450 | 450 |  | 0% | AGUIRRE | 1 | [16 empty] | 0 |  | 450 | 450 |  | 0% | AGUIRRE | 1 | [16 empty] | 0 |  | 450 | 450 |  | 0% | AGUIRRE | 1 | [16 empty] | 0 |  | 450 | 450 |  | 0% | AGUIRRE | 1 | [16 empty] | 0 |  | 450 | 450 |  | 0% | AGUIRRE | 1 | [16 empty] | 0 |  | 450 | 450 |  | 0%
| 2 | 591.52 | 591.52 | 0 | 152.48 | 20.49% | 0 | 0% | 0 | 0% | 0 | 79.51% | 79.51% | 20.49% | 56.7% | 0% | 1 | 744 | 147640 | 450 | 350 | 256 | 100% |  |  | 2 | 629.51 | 629.51 | 0 | 114.49 | 15.39% | 0 | 0% | 0 | 0% | 139.62 | 84.61% | 65.85% | 28.76% | 55.58% | 18.77% | 4 | 744 | 144740 | 450 | 350 | 350 | 100% |  |  | 2 | 717.63 | 717.63 | 0 | 2.37 | 0.3292% | 0 | 0% | 0 | 0% | 102.2 | 99.67% | 85.48% | 12.72% | 71.76% | 14.19% | 1 | 720 | 180840 | 450 | 350 | 350 | 100% |  |  | 2 | 608.95 | 608.95 | 0 | 135.05 | 18.15% | 0 | 0% | 0 | 0% | 0 | 81.85% | 81.85% | 18.15% | 59.93% | 0% | 1 | 744 | 156060 | 450 | 350 | 350 | 100% |  |  | 2 | 636.07 | 636.07 | 0 | 83.93 | 11.6569 | 0 | 0 | 0 | 0 | 181.7 | 88.3431 | 63.1069 | 29.4588 | 64.8909 | 25.24% | 3 | 720 | 163525 | 450 | 350 | 350 | 7502% |  | 2 | [16 empty] | 0 |  | 450 | 350 |  | 0% |  | 2 | [16 empty] | 0 |  | 450 | 350 |  | 0% |  | 2 | [16 empty] | 0 |  | 450 | 350 |  | 0% |  | 2 | [16 empty] | 0 |  | 450 | 350 |  | 0% |  | 2 | [16 empty] | 0 |  | 450 | 350 |  | 0% |  | 2 | [16 empty] | 0 |  | 450 | 350 |  | 0% |  | 2 | [16 empty] | 0 |  | 450 | 350 |  | 0%
| Total | 591.52 | 591.52 | 0 | 896.48 | 65.22% | 0 | 0% | 0 | 0% | 0 | 34.78% | 34.78% | 65.22% | 24.81% | 0% | 1 | 1488 | 147640 | 900 | 800 | 256 |  |  |  | Total | 629.51 | 629.51 | 0 | 858.49 | 62.98% | 0 | 0% | 0 | 0% | 139.62 | 37.02% | 28.81% | 68.83% | 24.32% | 8.21% | 4 | 1488 | 144740 | 900 | 800 | 350 |  |  |  | Total | 717.63 | 717.63 | 0 | 722.37 | 56.39% | 0 | 0% | 0 | 0% | 102.2 | 43.61% | 37.4% | 61.81% | 31.4% | 6.21% | 1 | 1440 | 180840 | 900 | 800 | 350 |  |  |  | Total | 608.95 | 608.95 | 0 | 879.05 | 64.19% | 0 | 0% | 0 | 0% | 0 | 35.81% | 35.81% | 64.19% | 26.22% | 0% | 1 | 1488 | 156060 | 900 | 800 | 350 |  |  |  | Total | 636.07 | 636.07 | 0 | 803.93 | 111.6569 | 0 | 0 | 0 | 0 | 181.7 | 88.3431 | 63.1069 | 60.7776 | 28.3898 | 11.04% | 3 | 1440 | 163525 | 900 | 800 | 350 |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 900 | 800 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 900 | 800 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 900 | 800 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 900 | 800 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 900 | 800 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 900 | 800 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 900 | 800
| Total Baseloads | 5410.7 | 5350.6 | 60.1 | 1925 | 33.01% | 1488 | 6.102% | 104.3 | 0.5636% | 822.37 | 60.32% | 49.12% | 41.26% | 45.16% | 11.29% | 14 | 8928 | 836937 | 2792 | 2491 | 1162 |  |  |  | Total Baseloads | 5179.16 | 5119.06 | 60.1 | 2102.84 | 33.72% | 1488 | 6.102% | 158 | 0.8608% | 485.33 | 59.31% | 52.9% | 38.66% | 46.79% | 6.416% | 11 | 8928 | 867134 | 2792 | 2491 | 1707 |  |  |  | Total Baseloads | 5408.72 | 5406.32 | 2.4 | 1545.61 | 27.59% | 1440 | 6.102% | 245.67 | 1.648% | 583.3 | 64.66% | 57.38% | 32.82% | 49.57% | 7.279% | 9 | 8640 | 889109 | 2792 | 2491 | 1513 |  |  |  | Total Baseloads | 6084.79 | 6084.79 | 0 | 1355.21 | 25.25% | 1488 | 6.102% | 0 | 0% | 855.68 | 68.65% | 59.47% | 32.11% | 53.33% | 9.181% | 13 | 8928 | 988300 | 2792 | 2491 | 1809 |  |  |  | Total Baseloads | 5412.32 | 5325.84 | 86.48 | 1664.15 | 231.1319 | 1440 | 200 | 123.53 | 17.1569 | 735.01 | 751.7111 | 649.6264 | 31.0571 | 47.9405 | 9.346% | 11 | 8640 | 859822 | 2792 | 2491 | 1797 |  |  | Total Baseloads | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 2792 | 2491 |  |  |  | Total Baseloads | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 2792 | 2491 |  |  |  | Total Baseloads | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 2792 | 2491 |  |  |  | Total Baseloads | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 2792 | 2491 |  |  |  | Total Baseloads | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 2792 | 2491 |  |  |  | Total Baseloads | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 2792 | 2491 |  |  |  | Total Baseloads | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 2792 | 2491
AGUIRRE CC | V-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 96 | 96 | 0 | 100% |  | AGUIRRE CC | V-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 96 | 96 | 0 | 100% |  | AGUIRRE CC | V-1 | 27.3 | 0 | 27.3 | 692.7 | 96.21% | 0 | 0% | 0 | 0% | 0 | 3.792% | 3.792% | 100% | 0% | 0% | 0 | 720 | 0 | 96 | 96 | 0 | 100% |  | AGUIRRE CC | V-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 96 | 96 | 0 | 100% |  | AGUIRRE CC | V-1 | 0 | 0 | 0 | 720 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0% | 0 | 720 | 0 | 96 | 96 | 0 | 10000% | AGUIRRE CC | V-1 | [16 empty] | 0 |  | 96 | 96 |  | 0% | AGUIRRE CC | V-1 | [16 empty] | 0 |  | 96 | 96 |  | 0% | AGUIRRE CC | V-1 | [16 empty] | 0 |  | 96 | 96 |  | 0% | AGUIRRE CC | V-1 | [16 empty] | 0 |  | 96 | 96 |  | 0% | AGUIRRE CC | V-1 | [16 empty] | 0 |  | 96 | 96 |  | 0% | AGUIRRE CC | V-1 | [16 empty] | 0 |  | 96 | 96 |  | 0% | AGUIRRE CC | V-1 | [16 empty] | 0 |  | 96 | 96 |  | 0%
| 1-1 | 744 | 298 | 446 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 36.97% | 0% | 0 | 744 | 13752 | 50 | 50 | 50 | 100% |  |  | 1-1 | 741.3 | 393 | 348.3 | 2.7 | 0.3629% | 0 | 0% | 0 | 0% | 0 | 99.64% | 99.64% | 0.6823% | 34.46% | 0% | 1 | 744 | 12818 | 50 | 50 | 50 | 100% |  |  | 1-1 | 720 | 252 | 468 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 22.27% | 0% | 0 | 720 | 8017 | 50 | 50 | 50 | 100% |  |  | 1-1 | 744 | 510 | 234 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 44.95% | 0% | 0 | 744 | 16722 | 50 | 50 | 50 | 100% |  |  | 1-1 | 699.2 | 427 | 272.2 | 20.8 | 2.8889 | 0 | 0 | 0 | 0 | 0 | 97.1111 | 97.1111 | 4.6449 | 39.575 | 0% | 0 | 720 | 14247 | 50 | 50 | 50 | 10000% |  | 1-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-1 | [16 empty] | 0 |  | 50 | 50 |  | 0%
| 1-2 | 742.8 | 338 | 404.8 | 1.2 | 0.1613% | 0 | 0% | 0 | 0% | 0 | 99.84% | 99.84% | 0.3538% | 29.71% | 0% | 1 | 744 | 11051 | 50 | 50 | 50 | 100% |  |  | 1-2 | 729.5 | 335 | 394.5 | 14.5 | 1.949% | 0 | 0% | 0 | 0% | 0 | 98.05% | 98.05% | 4.149% | 28.95% | 0% | 0 | 744 | 10771 | 50 | 50 | 50 | 100% |  |  | 1-2 | 718.1 | 176 | 542.1 | 1.9 | 0.2639% | 0 | 0% | 0 | 0% | 0 | 99.74% | 99.74% | 1.068% | 15.41% | 0% | 0 | 720 | 5547 | 50 | 50 | 48 | 100% |  |  | 1-2 | 727.5 | 425 | 302.5 | 16.5 | 2.218% | 0 | 0% | 0 | 0% | 0 | 97.78% | 97.78% | 3.737% | 36.86% | 0% | 1 | 744 | 13713 | 50 | 50 | 50 | 100% |  |  | 1-2 | 720 | 366 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 32.7056 | 0% | 0 | 720 | 11774 | 50 | 50 | 50 | 10000% |  | 1-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 50 | 50 |  | 0%
| 1-3 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 50 | 50 | 0 | 100% |  |  | 1-3 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 50 | 50 | 0 | 100% |  |  | 1-3 | 0 | 0 | 0 | 0 | 0% | 720 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 720 | 0 | 50 | 50 | 0 | 100% |  |  | 1-3 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 50 | 50 | 0 | 100% |  |  | 1-3 | 0 | 0 | 0 | 0 | 0 | 720 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 720 | 0 | 50 | 50 | 0 | 10000% |  | 1-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-3 | [16 empty] | 0 |  | 50 | 50 |  | 0%
| 1-4 | 488.3 | 273 | 215.3 | 23.8 | 3.199% | 231.9 | 31.17% | 0 | 0% | 0 | 65.63% | 65.63% | 8.019% | 24.63% | 0% | 0 | 744 | 9164 | 50 | 50 | 50 | 100% |  |  | 1-4 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 50 | 50 | 0 | 100% |  |  | 1-4 | 0 | 0 | 0 | 0 | 0% | 720 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 720 | 0 | 50 | 50 | 0 | 100% |  |  | 1-4 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 50 | 50 | 0 | 100% |  |  | 1-4 | 0 | 0 | 0 | 0 | 0 | 720 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 720 | 0 | 50 | 50 | 0 | 10000% |  | 1-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 1-4 | [16 empty] | 0 |  | 50 | 50 |  | 0%
| V-2 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 96 | 96 | 0 | 100% |  |  | V-2 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 96 | 96 | 0 | 100% |  |  | V-2 | 0 | 0 | 0 | 0 | 0% | 720 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 720 | 0 | 96 | 96 | 0 | 100% |  |  | V-2 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 96 | 96 | 0 | 100% |  |  | V-2 | 0 | 0 | 0 | 0 | 0 | 720 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 720 | 0 | 96 | 96 | 0 | 10000% |  | V-2 | [16 empty] | 0 |  | 96 | 96 |  | 0% |  | V-2 | [16 empty] | 0 |  | 96 | 96 |  | 0% |  | V-2 | [16 empty] | 0 |  | 96 | 96 |  | 0% |  | V-2 | [16 empty] | 0 |  | 96 | 96 |  | 0% |  | V-2 | [16 empty] | 0 |  | 96 | 96 |  | 0% |  | V-2 | [16 empty] | 0 |  | 96 | 96 |  | 0% |  | V-2 | [16 empty] | 0 |  | 96 | 96 |  | 0%
| 2-1 | 744 | 424.7 | 319.3 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 37.26% | 0% | 0 | 744 | 13859 | 50 | 50 | 50 | 100% |  |  | 2-1 | 690.6 | 397.5 | 293.1 | 53.4 | 7.177% | 0 | 0% | 0 | 0% | 0 | 92.82% | 92.82% | 11.84% | 34.19% | 0% | 2 | 744 | 12720 | 50 | 50 | 50 | 100% |  |  | 2-1 | 720 | 297.6 | 422.4 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 26.08% | 0% | 0 | 720 | 9389 | 50 | 50 | 50 | 100% |  |  | 2-1 | 450.1 | 322.9 | 127.2 | 293.9 | 39.5% | 0 | 0% | 0 | 0% | 0 | 60.5% | 60.5% | 47.65% | 28.6% | 0% | 5 | 744 | 10638 | 50 | 50 | 50 | 100% |  |  | 2-1 | 707.5 | 397.8 | 309.7 | 0 | 0 | 0 | 0 | 12.5 | 1.7361 | 0 | 98.2639 | 98.2639 | 0 | 35.3028 | 0% | 0 | 720 | 12709 | 50 | 50 | 50 | 10000% |  | 2-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 50 | 50 |  | 0%
| 2-2 | 744 | 453.3 | 290.7 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 39.52% | 0% | 0 | 744 | 14702 | 50 | 50 | 50 | 100% |  |  | 2-2 | 707.8 | 424.4 | 283.4 | 36.2 | 4.866% | 0 | 0% | 0 | 0% | 0 | 95.13% | 95.13% | 7.859% | 36.43% | 0% | 3 | 744 | 13551 | 50 | 50 | 50 | 100% |  |  | 2-2 | 718.1 | 242 | 476.1 | 1.9 | 0.2639% | 0 | 0% | 0 | 0% | 0 | 99.74% | 99.74% | 0.779% | 20.93% | 0% | 0 | 720 | 7533 | 50 | 50 | 50 | 100% |  |  | 2-2 | 638.2 | 293.8 | 344.4 | 105.8 | 14.22% | 0 | 0% | 0 | 0% | 0 | 85.78% | 85.78% | 26.48% | 25.09% | 0% | 1 | 744 | 9335 | 50 | 50 | 50 | 100% |  |  | 2-2 | 581.6 | 320.7 | 260.9 | 125.9 | 17.4861 | 0 | 0 | 12.5 | 1.7361 | 0 | 80.7778 | 80.7778 | 28.1908 | 28.2 | 0% | 1 | 720 | 10152 | 50 | 50 | 50 | 10000% |  | 2-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-2 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-2 | [16 empty] | 0 |  | 50 | 50 |  | 0%
| 2-3 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 50 | 50 | 0 | 100% |  |  | 2-3 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 50 | 50 | 0 | 100% |  |  | 2-3 | 0 | 0 | 0 | 0 | 0% | 720 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 720 | 0 | 50 | 50 | 0 | 100% |  |  | 2-3 | 0 | 0 | 0 | 0 | 0% | 744 | 100% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 50 | 50 | 0 | 100% |  |  | 2-3 | 0 | 0 | 0 | 0 | 0 | 720 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 720 | 0 | 50 | 50 | 0 | 10000% |  | 2-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-3 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-3 | [16 empty] | 0 |  | 50 | 50 |  | 0%
| 2-4 | 687.6 | 316.6 | 371 | 56.4 | 7.581% | 0 | 0% | 0 | 0% | 0 | 92.42% | 92.42% | 15.12% | 28.2% | 0% | 1 | 744 | 10491 | 50 | 50 | 50 | 100% |  |  | 2-4 | 660.5 | 321.3 | 339.2 | 83.5 | 11.22% | 0 | 0% | 0 | 0% | 0 | 88.78% | 88.78% | 20.63% | 27.08% | 0% | 0 | 744 | 10075 | 50 | 50 | 50 | 100% |  |  | 2-4 | 720 | 213.9 | 506.1 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 19.65% | 0% | 0 | 720 | 7074 | 50 | 50 | 50 | 100% |  |  | 2-4 | 744 | 464.1 | 279.9 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 41.41% | 0% | 0 | 744 | 15406 | 50 | 50 | 50 | 100% |  |  | 2-4 | 513 | 334 | 179 | 0 | 0 | 207 | 28.75 | 0 | 0 | 0 | 71.25 | 71.25 | 0 | 30.7139 | 0% | 0 | 720 | 11057 | 50 | 50 | 50 | 10000% |  | 2-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-4 | [16 empty] | 0 |  | 50 | 50 |  | 0% |  | 2-4 | [16 empty] | 0 |  | 50 | 50 |  | 0%
| Total | 4150.7 | 2103.6 | 2047.1 | 825.4 | 17.14% | 2463.9 | 35.74% | 0 | 0% | 0 | 47.12% | 47.12% | 18.2% | 16.58% | 0% | 2 | 7440 | 73019 | 592 | 592 | 300 |  |  |  | Total | 3529.7 | 1871.2 | 1658.5 | 934.3 | 18.38% | 2976 | 41.55% | 0 | 0% | 0 | 40.07% | 40.07% | 20.03% | 13.61% | 0% | 6 | 7440 | 59935 | 592 | 592 | 250 |  |  |  | Total | 3623.5 | 1181.5 | 2442 | 696.5 | 15.65% | 2880 | 41.55% | 0 | 0% | 0 | 42.8% | 42.8% | 16.37% | 8.812% | 0% | 0 | 7200 | 37560 | 592 | 592 | 248 |  |  |  | Total | 3303.8 | 2015.8 | 1288 | 1160.2 | 20.94% | 2976 | 41.55% | 0 | 0% | 0 | 37.5% | 37.5% | 22.79% | 14.94% | 0% | 7 | 7440 | 65814 | 592 | 592 | 250 |  |  |  | Total | 3221.3 | 1845.5 | 1375.8 | 866.7 | 120.375 | 3087 | 428.75 | 25 | 3.4722 | 0 | 447.4028 | 447.4028 | 31.9556 | 14.0623 | 0% | 1 | 7200 | 59939 | 592 | 592 | 250 |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 592 | 592 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 592 | 592 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 592 | 592 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 592 | 592 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 592 | 592 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 592 | 592 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 592 | 592
PALO | 1-1 | 504 | 128.6 | 375.4 | 240 | 32.26% | 0 | 0% | 0 | 0% | 0 | 67.74% | 67.74% | 65.11% | 14.7% | 0% | 0 | 744 | 2297 | 21 | 21 | 18 | 100% |  | PALO | 1-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 21 | 21 | 0 | 100% |  | PALO | 1-1 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 720 | 0 | 21 | 21 | 0 | 100% |  | PALO | 1-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 21 | 21 | 0 | 100% |  | PALO | 1-1 | 0 | 0 | 0 | 720 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0% | 0 | 720 | 0 | 21 | 21 | 0 | 10000% | PALO | 1-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% | PALO | 1-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% | PALO | 1-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% | PALO | 1-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% | PALO | 1-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% | PALO | 1-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% | PALO | 1-1 | [16 empty] | 0 |  | 21 | 21 |  | 0%
SECO | 1-2 | 744 | 213.4 | 530.6 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 24.59% | 0% | 0 | 744 | 3842 | 21 | 21 | 18 | 100% |  | SECO | 1-2 | 744 | 180.76 | 563.24 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 24.85% | 0% | 0 | 744 | 3882 | 21 | 21 | 21 | 100% |  | SECO | 1-2 | 717.2 | 107.6 | 609.6 | 2.8 | 0.3889% | 0 | 0% | 0 | 0% | 0 | 99.61% | 99.61% | 2.536% | 13.04% | 0% | 1 | 720 | 1972 | 21 | 21 | 18.3613 | 100% |  | SECO | 1-2 | 744 | 275.3 | 468.7 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 33.12% | 0% | 0 | 744 | 5175 | 21 | 21 | 19 | 100% |  | SECO | 1-2 | 698.5 | 205.3 | 493.2 | 21.5 | 2.9861 | 0 | 0 | 0 | 0 | 0 | 97.0139 | 97.0139 | 9.4797 | 25.6746 | 0% | 1 | 720 | 3882 | 21 | 21 | 19 | 10000% | SECO | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | SECO | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | SECO | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | SECO | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | SECO | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | SECO | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | SECO | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0%
| 2-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 21 | 21 | 0 | 100% |  |  | 2-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 21 | 21 | 0 | 100% |  |  | 2-1 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 720 | 0 | 21 | 21 | 0 | 100% |  |  | 2-1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 21 | 21 | 0 | 100% |  |  | 2-1 | 0 | 0 | 0 | 720 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0% | 0 | 720 | 0 | 21 | 21 | 0 | 10000% |  | 2-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 2-1 | [16 empty] | 0 |  | 21 | 21 |  | 0%
| Total | 1248 | 342 | 906 | 984 | 44.09% | 0 | 0% | 0 | 0% | 0 | 55.91% | 55.91% | 55.04% | 13.1% | 0% | 0 | 2232 | 6139 | 63 | 63 | 36 |  |  |  | Total | 744 | 180.76 | 563.24 | 1488 | 66.67% | 0 | 0% | 0 | 0% | 0 | 33.33% | 33.33% | 66.67% | 8.282% | 0% | 0 | 2232 | 3882 | 63 | 63 | 21 |  |  |  | Total | 717.2 | 107.6 | 609.6 | 1442.8 | 66.8% | 0 | 0% | 0 | 0% | 0 | 33.2% | 33.2% | 67.51% | 4.347% | 0% | 1 | 2160 | 1972 | 63 | 63 | 18.3613 |  |  |  | Total | 744 | 275.3 | 468.7 | 1488 | 66.67% | 0 | 0% | 0 | 0% | 0 | 33.33% | 33.33% | 66.67% | 11.04% | 0% | 0 | 2232 | 5175 | 63 | 63 | 19 |  |  |  | Total | 698.5 | 205.3 | 493.2 | 1461.5 | 202.9861 | 0 | 0 | 0 | 0 | 0 | 97.0139 | 97.0139 | 87.683 | 8.5582 | 0% | 1 | 2160 | 3882 | 63 | 63 | 19 |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 63 | 63 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 63 | 63 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 63 | 63 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 63 | 63 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 63 | 63 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 63 | 63 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 63 | 63
COSTA SUR | 1-2 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 21 | 21 | 0 | 100% |  | COSTA SUR | 1-2 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 21 | 21 | 0 | 100% |  | COSTA SUR | 1-2 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 720 | 0 | 21 | 21 | 0 | 100% |  | COSTA SUR | 1-2 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 21 | 21 | 0 | 100% |  | COSTA SUR | 1-2 | 0 | 0 | 0 | 720 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0% | 0 | 720 | 0 | 21 | 21 | 0 | 10000% | COSTA SUR | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | COSTA SUR | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | COSTA SUR | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | COSTA SUR | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | COSTA SUR | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | COSTA SUR | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% | COSTA SUR | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0%
| Total | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 21 | 21 | 0 |  |  |  | Total | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 21 | 21 | 0 |  |  |  | Total | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 720 | 0 | 21 | 21 | 0 |  |  |  | Total | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 21 | 21 | 0 |  |  |  | Total | 0 | 0 | 0 | 720 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0% | 0 | 720 | 0 | 21 | 21 | 0 |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 21 | 21 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 21 | 21 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 21 | 21 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 21 | 21 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 21 | 21 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 21 | 21 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 21 | 21
YABUCOA | 1-2 | 744 | 117.8 | 626.2 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 15.89% | 0% | 0 | 744 | 1773 | 21 | 15 | 15 | 100% |  | YABUCOA | 1-2 | 744 | 164.8 | 579.2 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 22.2% | 0% | 0 | 744 | 2477 | 21 | 15 | 15 | 100% |  | YABUCOA | 1-2 | 720 | 68 | 652 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 100% | 0.1389% | 0.0001929% | 2.679e-07% | 0 | 720 | 1019 | 21 | 15 | 14.9853 | 100% |  | YABUCOA | 1-2 | 744 | 226.6 | 517.4 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 30.51% | 0% | 0 | 744 | 3405 | 21 | 15 | 15 | 100% |  | YABUCOA | 1-2 | 720 | 185.7 | 534.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 25.8426 | 0% | 0 | 720 | 2791 | 21 | 15 | 15 | 10000% | YABUCOA | 1-2 | [16 empty] | 0 |  | 21 | 15 |  | 0% | YABUCOA | 1-2 | [16 empty] | 0 |  | 21 | 15 |  | 0% | YABUCOA | 1-2 | [16 empty] | 0 |  | 21 | 15 |  | 0% | YABUCOA | 1-2 | [16 empty] | 0 |  | 21 | 15 |  | 0% | YABUCOA | 1-2 | [16 empty] | 0 |  | 21 | 15 |  | 0% | YABUCOA | 1-2 | [16 empty] | 0 |  | 21 | 15 |  | 0% | YABUCOA | 1-2 | [16 empty] | 0 |  | 21 | 15 |  | 0%
| Total | 744 | 117.8 | 626.2 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 15.89% | 0% | 0 | 744 | 1773 | 21 | 15 | 15 |  |  |  | Total | 744 | 164.8 | 579.2 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 22.2% | 0% | 0 | 744 | 2477 | 21 | 15 | 15 |  |  |  | Total | 720 | 68 | 652 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 100% | 0.1389% | 0.0001929% | 2.679e-07% | 0 | 720 | 1019 | 21 | 15 | 14.9853 |  |  |  | Total | 744 | 226.6 | 517.4 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 30.51% | 0% | 0 | 744 | 3405 | 21 | 15 | 15 |  |  |  | Total | 720 | 185.7 | 534.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 25.8426 | 0% | 0 | 720 | 2791 | 21 | 15 | 15 |  |  | Total | [16 empty] | 0 |  | 21 | 15 |  |  |  | Total | [16 empty] | 0 |  | 21 | 15 |  |  |  | Total | [16 empty] | 0 |  | 21 | 15 |  |  |  | Total | [16 empty] | 0 |  | 21 | 15 |  |  |  | Total | [16 empty] | 0 |  | 21 | 15 |  |  |  | Total | [16 empty] | 0 |  | 21 | 15 |  |  |  | Total | [16 empty] | 0 |  | 21 | 15
JOBOS | 1-2 | 744 | 169.1 | 574.9 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 21.69% | 0% | 0 | 744 | 3227 | 21 | 20 | 20 | 100% |  | JOBOS | 1-2 | 744 | 169.7 | 574.3 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 21.92% | 0% | 0 | 744 | 3261 | 21 | 20 | 20 | 100% |  | JOBOS | 1-2 | 720 | 79 | 641 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 100% | 0.1389% | 0.0001929% | 2.679e-07% | 0 | 720 | 1441 | 21 | 20 | 20 | 100% |  | JOBOS | 1-2 | 739.4 | 235.2 | 504.2 | 4.6 | 0.6183% | 0 | 0% | 0 | 0% | 0 | 99.38% | 99.38% | 1.918% | 30.09% | 0% | 0 | 744 | 4478 | 21 | 20 | 20 | 100% |  | JOBOS | 1-2 | 720 | 193.1 | 526.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 25.6111 | 0% | 0 | 720 | 3688 | 21 | 20 | 20 | 10000% | JOBOS | 1-2 | [16 empty] | 0 |  | 21 | 20 |  | 0% | JOBOS | 1-2 | [16 empty] | 0 |  | 21 | 20 |  | 0% | JOBOS | 1-2 | [16 empty] | 0 |  | 21 | 20 |  | 0% | JOBOS | 1-2 | [16 empty] | 0 |  | 21 | 20 |  | 0% | JOBOS | 1-2 | [16 empty] | 0 |  | 21 | 20 |  | 0% | JOBOS | 1-2 | [16 empty] | 0 |  | 21 | 20 |  | 0% | JOBOS | 1-2 | [16 empty] | 0 |  | 21 | 20 |  | 0%
| Total | 744 | 169.1 | 574.9 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 21.69% | 0% | 0 | 744 | 3227 | 21 | 20 | 20 |  |  |  | Total | 744 | 169.7 | 574.3 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 21.92% | 0% | 0 | 744 | 3261 | 21 | 20 | 20 |  |  |  | Total | 720 | 79 | 641 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 100% | 0.1389% | 0.0001929% | 2.679e-07% | 0 | 720 | 1441 | 21 | 20 | 20 |  |  |  | Total | 739.4 | 235.2 | 504.2 | 4.6 | 0.6183% | 0 | 0% | 0 | 0% | 0 | 99.38% | 99.38% | 1.918% | 30.09% | 0% | 0 | 744 | 4478 | 21 | 20 | 20 |  |  |  | Total | 720 | 193.1 | 526.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 25.6111 | 0% | 0 | 720 | 3688 | 21 | 20 | 20 |  |  | Total | [16 empty] | 0 |  | 21 | 20 |  |  |  | Total | [16 empty] | 0 |  | 21 | 20 |  |  |  | Total | [16 empty] | 0 |  | 21 | 20 |  |  |  | Total | [16 empty] | 0 |  | 21 | 20 |  |  |  | Total | [16 empty] | 0 |  | 21 | 20 |  |  |  | Total | [16 empty] | 0 |  | 21 | 20 |  |  |  | Total | [16 empty] | 0 |  | 21 | 20
DAGUAO | 1-1 | 744 | 180.7 | 563.3 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 21.72% | 0% | 0 | 744 | 3232 | 21 | 20 | 20 | 100% |  | DAGUAO | 1-1 | 744 | 203 | 541 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 24.31% | 0% | 0 | 744 | 3618 | 21 | 20 | 20 | 100% |  | DAGUAO | 1-1 | 720 | 96 | 624 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 12.01% | 0% | 0 | 720 | 1730 | 21 | 20 | 20 | 100% |  | DAGUAO | 1-1 | 712.56 | 243.2 | 469.36 | 31.44 | 4.226% | 0 | 0% | 0 | 0% | 0 | 95.77% | 95.77% | 11.45% | 29.72% | 0% | 1 | 744 | 4422 | 21 | 20 | 20 | 100% |  | DAGUAO | 1-1 | 630.9 | 163 | 467.9 | 89.1 | 12.375 | 0 | 0 | 0 | 0 | 0 | 87.625 | 87.625 | 35.3431 | 20.5833 | 0% | 1 | 720 | 2964 | 21 | 20 | 20 | 10000% | DAGUAO | 1-1 | [16 empty] | 0 |  | 21 | 20 |  | 0% | DAGUAO | 1-1 | [16 empty] | 0 |  | 21 | 20 |  | 0% | DAGUAO | 1-1 | [16 empty] | 0 |  | 21 | 20 |  | 0% | DAGUAO | 1-1 | [16 empty] | 0 |  | 21 | 20 |  | 0% | DAGUAO | 1-1 | [16 empty] | 0 |  | 21 | 20 |  | 0% | DAGUAO | 1-1 | [16 empty] | 0 |  | 21 | 20 |  | 0% | DAGUAO | 1-1 | [16 empty] | 0 |  | 21 | 20 |  | 0%
| 1-2 | 744 | 2.9 | 741.1 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 0.3072% | 0% | 0 | 744 | 48 | 21 | 21 | 17 | 100% |  |  | 1-2 | 744 | 95.9 | 648.1 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 10.24% | 0% | 0 | 744 | 1600 | 21 | 21 | 16.684 | 100% |  |  | 1-2 | 720 | 94.5 | 625.5 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 9.048% | 0% | 0 | 720 | 1368 | 21 | 21 | 14.4762 | 100% |  |  | 1-2 | 691 | 231.5 | 459.5 | 53 | 7.124% | 0 | 0% | 0 | 0% | 0 | 92.88% | 92.88% | 18.63% | 17.33% | 0% | 1 | 744 | 2708 | 21 | 21 | 12 | 100% |  |  | 1-2 | 586.11 | 149.4 | 436.71 | 133.89 | 18.5958 | 0 | 0 | 0 | 0 | 0 | 81.4042 | 81.4042 | 47.2625 | 10.205 | 0% | 3 | 720 | 1543 | 21 | 21 | 10 | 10000% |  | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0% |  | 1-2 | [16 empty] | 0 |  | 21 | 21 |  | 0%
| Total | 1488 | 183.6 | 1304.4 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 10.75% | 0% | 0 | 1488 | 3280 | 42 | 41 | 37 |  |  |  | Total | 1488 | 298.9 | 1189.1 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 17.11% | 0% | 0 | 1488 | 5218 | 42 | 41 | 36.684 |  |  |  | Total | 1440 | 190.5 | 1249.5 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 10.49% | 0% | 0 | 1440 | 3098 | 42 | 41 | 34.4762 |  |  |  | Total | 1403.56 | 474.7 | 928.86 | 84.44 | 5.71% | 0 | 0% | 0 | 0% | 0 | 94.29% | 94.29% | 15.13% | 23.37% | 0% | 2 | 1488 | 7130 | 42 | 41 | 32 |  |  |  | Total | 1217.01 | 312.4 | 904.61 | 222.99 | 30.9708 | 0 | 0 | 0 | 0 | 0 | 169.0292 | 169.0292 | 41.65 | 15.2676 | 0% | 4 | 1440 | 4507 | 42 | 41 | 30 |  |  | Total | [16 empty] | 0 |  | 42 | 41 |  |  |  | Total | [16 empty] | 0 |  | 42 | 41 |  |  |  | Total | [16 empty] | 0 |  | 42 | 41 |  |  |  | Total | [16 empty] | 0 |  | 42 | 41 |  |  |  | Total | [16 empty] | 0 |  | 42 | 41 |  |  |  | Total | [16 empty] | 0 |  | 42 | 41 |  |  |  | Total | [16 empty] | 0 |  | 42 | 41
PALO SECO PW | MP 1 | 744 | 153.6 | 590.4 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 20.05% | 0% | 0 | 744 | 4028 | 27 | 27 | 27 | 100% |  | PALO SECO PW | MP 1 | 744 | 159.3 | 584.7 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 20.56% | 0% | 0 | 744 | 4131 | 27 | 27 | 27 | 100% |  | PALO SECO PW | MP 1 | 720 | 64.3 | 655.7 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 8.354% | 0% | 0 | 720 | 1624 | 27 | 27 | 27 | 100% |  | PALO SECO PW | MP 1 | 744 | 207.1 | 536.9 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 26.51% | 0% | 0 | 744 | 5325 | 27 | 27 | 27 | 100% |  | PALO SECO PW | MP 1 | 720 | 173.1 | 546.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 22.9321 | 0% | 0 | 720 | 4458 | 27 | 27 | 27 | 10000% | PALO SECO PW | MP 1 | [16 empty] | 0 |  | 27 | 27 |  | 0% | PALO SECO PW | MP 1 | [16 empty] | 0 |  | 27 | 27 |  | 0% | PALO SECO PW | MP 1 | [16 empty] | 0 |  | 27 | 27 |  | 0% | PALO SECO PW | MP 1 | [16 empty] | 0 |  | 27 | 27 |  | 0% | PALO SECO PW | MP 1 | [16 empty] | 0 |  | 27 | 27 |  | 0% | PALO SECO PW | MP 1 | [16 empty] | 0 |  | 27 | 27 |  | 0% | PALO SECO PW | MP 1 | [16 empty] | 0 |  | 27 | 27 |  | 0%
FT-8 | MP 2 | 744 | 153.1 | 590.9 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 19.94% | 0% | 0 | 744 | 4006 | 27 | 27 | 27 | 100% |  | FT-8 | MP 2 | 744 | 158.9 | 585.1 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 20.74% | 0% | 0 | 744 | 4167 | 27 | 27 | 27 | 100% |  | FT-8 | MP 2 | 720 | 64.3 | 655.7 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 8.338% | 0% | 0 | 720 | 1621 | 27 | 27 | 27 | 100% |  | FT-8 | MP 2 | 744 | 207.5 | 536.5 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 27.14% | 0% | 0 | 744 | 5452 | 27 | 27 | 27 | 100% |  | FT-8 | MP 2 | 602.67 | 141.2 | 461.47 | 117.33 | 16.2958 | 0 | 0 | 0 | 0 | 0 | 83.7042 | 83.7042 | 45.3835 | 17.999 | 0% | 1 | 720 | 3499 | 27 | 27 | 27 | 10000% | FT-8 | MP 2 | [16 empty] | 0 |  | 27 | 27 |  | 0% | FT-8 | MP 2 | [16 empty] | 0 |  | 27 | 27 |  | 0% | FT-8 | MP 2 | [16 empty] | 0 |  | 27 | 27 |  | 0% | FT-8 | MP 2 | [16 empty] | 0 |  | 27 | 27 |  | 0% | FT-8 | MP 2 | [16 empty] | 0 |  | 27 | 27 |  | 0% | FT-8 | MP 2 | [16 empty] | 0 |  | 27 | 27 |  | 0% | FT-8 | MP 2 | [16 empty] | 0 |  | 27 | 27 |  | 0%
| MP 3 | 744 | 152 | 592 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 17.7% | 0% | 0 | 744 | 3556 | 27 | 27 | 27 | 100% |  |  | MP 3 | 744 | 149 | 595 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 17.69% | 0% | 0 | 744 | 3554 | 27 | 27 | 27 | 100% |  |  | MP 3 | 720 | 65.2 | 654.8 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 7.973% | 0% | 0 | 720 | 1550 | 27 | 27 | 27 | 100% |  |  | MP 3 | 744 | 208.4 | 535.6 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 25.07% | 0% | 0 | 744 | 5037 | 27 | 27 | 27 | 100% |  |  | MP 3 | 720 | 176.3 | 543.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 21.857 | 0% | 0 | 720 | 4249 | 27 | 27 | 27 | 10000% |  | MP 3 | [16 empty] | 0 |  | 27 | 27 |  | 0% |  | MP 3 | [16 empty] | 0 |  | 27 | 27 |  | 0% |  | MP 3 | [16 empty] | 0 |  | 27 | 27 |  | 0% |  | MP 3 | [16 empty] | 0 |  | 27 | 27 |  | 0% |  | MP 3 | [16 empty] | 0 |  | 27 | 27 |  | 0% |  | MP 3 | [16 empty] | 0 |  | 27 | 27 |  | 0% |  | MP 3 | [16 empty] | 0 |  | 27 | 27 |  | 0%
| Total | 2232 | 458.7 | 1773.3 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 19.23% | 0% | 0 | 2232 | 11590 | 81 | 81 | 81 |  |  |  | Total | 2232 | 467.2 | 1764.8 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 19.67% | 0% | 0 | 2232 | 11852 | 81 | 81 | 81 |  |  |  | Total | 2160 | 193.8 | 1966.2 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 8.222% | 0% | 0 | 2160 | 4795 | 81 | 81 | 81 |  |  |  | Total | 2232 | 623 | 1609 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 26.24% | 0% | 0 | 2232 | 15814 | 81 | 81 | 81 |  |  |  | Total | 2042.67 | 490.6 | 1552.07 | 117.33 | 16.2958 | 0 | 0 | 0 | 0 | 0 | 283.7042 | 283.7042 | 19.2999 | 20.9294 | 0% | 1 | 2160 | 12206 | 81 | 81 | 81 |  |  | Total | [16 empty] | 0 |  | 81 | 81 |  |  |  | Total | [16 empty] | 0 |  | 81 | 81 |  |  |  | Total | [16 empty] | 0 |  | 81 | 81 |  |  |  | Total | [16 empty] | 0 |  | 81 | 81 |  |  |  | Total | [16 empty] | 0 |  | 81 | 81 |  |  |  | Total | [16 empty] | 0 |  | 81 | 81 |  |  |  | Total | [16 empty] | 0 |  | 81 | 81
CAMBALACHE | 2 | 738.13 | 370.63 | 367.5 | 5.87 | 0.789% | 0 | 0% | 0 | 0% | 0 | 99.21% | 99.21% | 1.559% | 37.68% | 0% | 1 | 744 | 21642 | 82.5 | 77.2 | 77.2 | 100% |  | CAMBALACHE | 2 | 744 | 415.28 | 328.72 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 41.27% | 0% | 0 | 744 | 23705 | 82.5 | 77.2 | 77.2 | 100% |  | CAMBALACHE | 2 | 720 | 234.78 | 485.22 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 23.24% | 0% | 0 | 720 | 12916 | 82.5 | 77.2 | 77.2 | 100% |  | CAMBALACHE | 2 | 734.42 | 475.3 | 259.12 | 2.7 | 0.3629% | 0 | 0% | 6.88 | 0.9247% | 0 | 98.71% | 98.71% | 0.5649% | 47.75% | 0% | 1 | 744 | 27427 | 82.5 | 77.2 | 77 | 100% |  | CAMBALACHE | 2 | 709.52 | 208.72 | 500.8 | 10.48 | 1.4556 | 0 | 0 | 0 | 0 | 0 | 98.5444 | 98.5444 | 4.781 | 21.3551 | 0% | 1 | 720 | 11870 | 82.5 | 77.2 | 77 | 10000% | CAMBALACHE | 2 | [16 empty] | 0 |  | 82.5 | 77.2 |  | 0% | CAMBALACHE | 2 | [16 empty] | 0 |  | 82.5 | 77.2 |  | 0% | CAMBALACHE | 2 | [16 empty] | 0 |  | 82.5 | 77.2 |  | 0% | CAMBALACHE | 2 | [16 empty] | 0 |  | 82.5 | 77.2 |  | 0% | CAMBALACHE | 2 | [16 empty] | 0 |  | 82.5 | 77.2 |  | 0% | CAMBALACHE | 2 | [16 empty] | 0 |  | 82.5 | 77.2 |  | 0% | CAMBALACHE | 2 | [16 empty] | 0 |  | 82.5 | 77.2 |  | 0%
| 3 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 82.5 | 74.6 | 0 | 100% |  |  | 3 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 82.5 | 74.6 | 0 | 100% |  |  | 3 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 720 | 0 | 82.5 | 74.6 | 0 | 100% |  |  | 3 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 82.5 | 74.6 | 0 | 100% |  |  | 3 | 0 | 0 | 0 | 720 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0% | 0 | 720 | 0 | 82.5 | 74.6 | 0 | 10000% |  | 3 | [16 empty] | 0 |  | 82.5 | 74.6 |  | 0% |  | 3 | [16 empty] | 0 |  | 82.5 | 74.6 |  | 0% |  | 3 | [16 empty] | 0 |  | 82.5 | 74.6 |  | 0% |  | 3 | [16 empty] | 0 |  | 82.5 | 74.6 |  | 0% |  | 3 | [16 empty] | 0 |  | 82.5 | 74.6 |  | 0% |  | 3 | [16 empty] | 0 |  | 82.5 | 74.6 |  | 0% |  | 3 | [16 empty] | 0 |  | 82.5 | 74.6 |  | 0%
| Total | 738.13 | 370.63 | 367.5 | 749.87 | 49.54% | 0 | 0% | 0 | 0% | 0 | 49.61% | 50.46% | 49.94% | 19.16% | 0% | 1 | 1488 | 21642 | 165 | 151.8 | 77.2 |  |  |  | Total | 744 | 415.28 | 328.72 | 744 | 49.14% | 0 | 0% | 0 | 0% | 0 | 50.86% | 50.86% | 49.14% | 20.99% | 0% | 0 | 1488 | 23705 | 165 | 151.8 | 77.2 |  |  |  | Total | 720 | 234.78 | 485.22 | 720 | 49.14% | 0 | 0% | 0 | 0% | 0 | 50.86% | 50.86% | 49.14% | 11.82% | 0% | 0 | 1440 | 12916 | 165 | 151.8 | 77.2 |  |  |  | Total | 734.42 | 475.3 | 259.12 | 746.7 | 49.33% | 0 | 0% | 6.88 | 0.4703% | 0 | 50.2% | 50.2% | 49.43% | 24.28% | 0% | 1 | 1488 | 27427 | 165 | 151.8 | 77 |  |  |  | Total | 709.52 | 208.72 | 500.8 | 730.48 | 101.4556 | 0 | 0 | 0 | 0 | 0 | 98.5444 | 98.5444 | 77.7768 | 10.8604 | 0% | 1 | 1440 | 11870 | 165 | 151.8 | 77 |  |  | Total | [16 empty] | 0 |  | 165 | 151.8 |  |  |  | Total | [16 empty] | 0 |  | 165 | 151.8 |  |  |  | Total | [16 empty] | 0 |  | 165 | 151.8 |  |  |  | Total | [16 empty] | 0 |  | 165 | 151.8 |  |  |  | Total | [16 empty] | 0 |  | 165 | 151.8 |  |  |  | Total | [16 empty] | 0 |  | 165 | 151.8 |  |  |  | Total | [16 empty] | 0 |  | 165 | 151.8
MAYAGUEZ | 1 | 0 | 0 | 0 | 432 | 58.06% | 0 | 0% | 312 | 41.94% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 55 | 47.7 | 0 | 100% |  | MAYAGUEZ | 1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 55 | 47.7 | 0 | 100% |  | MAYAGUEZ | 1 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 720 | 0 | 55 | 47.7 | 0 | 100% |  | MAYAGUEZ | 1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 55 | 47.7 | 0 | 100% |  | MAYAGUEZ | 1 | 0 | 0 | 0 | 720 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0% | 0 | 720 | 0 | 55 | 47.7 | 0 | 10000% | MAYAGUEZ | 1 | [16 empty] | 0 |  | 55 | 47.7 |  | 0% | MAYAGUEZ | 1 | [16 empty] | 0 |  | 55 | 47.7 |  | 0% | MAYAGUEZ | 1 | [16 empty] | 0 |  | 55 | 47.7 |  | 0% | MAYAGUEZ | 1 | [16 empty] | 0 |  | 55 | 47.7 |  | 0% | MAYAGUEZ | 1 | [16 empty] | 0 |  | 55 | 47.7 |  | 0% | MAYAGUEZ | 1 | [16 empty] | 0 |  | 55 | 47.7 |  | 0% | MAYAGUEZ | 1 | [16 empty] | 0 |  | 55 | 47.7 |  | 0%
| 2 | 0 | 0 | 0 | 0 | 0% | 0 | 0% | 744 | 100% | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 744 | 0 | 55 | 49 | 0 | 100% |  |  | 2 | 0 | 0 | 0 | 576 | 77.42% | 0 | 0% | 168 | 22.58% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 55 | 49 | 0 | 100% |  |  | 2 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 720 | 0 | 55 | 49 | 0 | 100% |  |  | 2 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 55 | 49 | 0 | 100% |  |  | 2 | 0 | 0 | 0 | 720 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0% | 0 | 720 | 0 | 55 | 49 | 0 | 10000% |  | 2 | [16 empty] | 0 |  | 55 | 49 |  | 0% |  | 2 | [16 empty] | 0 |  | 55 | 49 |  | 0% |  | 2 | [16 empty] | 0 |  | 55 | 49 |  | 0% |  | 2 | [16 empty] | 0 |  | 55 | 49 |  | 0% |  | 2 | [16 empty] | 0 |  | 55 | 49 |  | 0% |  | 2 | [16 empty] | 0 |  | 55 | 49 |  | 0% |  | 2 | [16 empty] | 0 |  | 55 | 49 |  | 0%
| 3 | 372 | 59.2 | 312.8 | 372 | 50% | 0 | 0% | 0 | 0% | 0 | 50% | 50% | 86.27% | 6.269% | 0% | 0 | 744 | 2565.2 | 55 | 55 | 23.5 | 100% |  |  | 3 | 353 | 59.2 | 293.8 | 391 | 52.55% | 0 | 0% | 0 | 0% | 0 | 47.45% | 47.45% | 86.85% | 6.247% | 0% | 1 | 744 | 2556.3 | 55 | 55 | 23 | 100% |  |  | 3 | 360 | 21.35 | 338.65 | 360 | 50% | 0 | 0% | 0 | 0% | 0 | 50% | 50% | 94.4% | 2.048% | 0% | 0 | 720 | 810.9 | 55 | 55 | 23 | 100% |  |  | 3 | 359.125 | 68.25 | 290.875 | 384.875 | 51.73% | 0 | 0% | 0 | 0% | 0 | 48.27% | 48.27% | 84.94% | 7.232% | 0% | 1 | 744 | 2959.5 | 55 | 55 | 23 | 100% |  |  | 3 | 360 | 123.35 | 236.65 | 360 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 74.4802 | 14.0154 | 0% | 0 | 720 | 5550.1 | 55 | 55 | 22.5 | 10000% |  | 3 | [16 empty] | 0 |  | 55 | 55 |  | 0% |  | 3 | [16 empty] | 0 |  | 55 | 55 |  | 0% |  | 3 | [16 empty] | 0 |  | 55 | 55 |  | 0% |  | 3 | [16 empty] | 0 |  | 55 | 55 |  | 0% |  | 3 | [16 empty] | 0 |  | 55 | 55 |  | 0% |  | 3 | [16 empty] | 0 |  | 55 | 55 |  | 0% |  | 3 | [16 empty] | 0 |  | 55 | 55 |  | 0%
| 4 | 372 | 59.65 | 312.35 | 372 | 50% | 0 | 0% | 0 | 0% | 0 | 50% | 50% | 86.18% | 7.312% | 0% | 0 | 744 | 2736.2 | 55 | 50.3 | 23.5 | 100% |  |  | 4 | 372 | 58.5 | 313.5 | 372 | 50% | 0 | 0% | 0 | 0% | 0 | 50% | 50% | 86.41% | 7.084% | 0% | 0 | 744 | 2651.1 | 55 | 50.3 | 24 | 100% |  |  | 4 | 358.375 | 22.45 | 335.925 | 361.625 | 50.23% | 0 | 0% | 0 | 0% | 0 | 49.77% | 49.77% | 94.15% | 2.758% | 0% | 2 | 720 | 998.8 | 55 | 50.3 | 24 | 100% |  |  | 4 | 345.785 | 69.95 | 275.835 | 398.215 | 53.52% | 0 | 0% | 0 | 0% | 0 | 46.48% | 46.48% | 85.06% | 8.315% | 0% | 1 | 744 | 3111.6 | 55 | 50.3 | 24 | 100% |  |  | 4 | 359.9335 | 121.4985 | 238.435 | 360.0665 | 50.0092 | 0 | 0 | 0 | 0 | 0 | 49.9908 | 49.9908 | 74.7701 | 15.69 | 0% | 0 | 720 | 5682.3 | 55 | 50.3 | 24 | 10000% |  | 4 | [16 empty] | 0 |  | 55 | 50.3 |  | 0% |  | 4 | [16 empty] | 0 |  | 55 | 50.3 |  | 0% |  | 4 | [16 empty] | 0 |  | 55 | 50.3 |  | 0% |  | 4 | [16 empty] | 0 |  | 55 | 50.3 |  | 0% |  | 4 | [16 empty] | 0 |  | 55 | 50.3 |  | 0% |  | 4 | [16 empty] | 0 |  | 55 | 50.3 |  | 0% |  | 4 | [16 empty] | 0 |  | 55 | 50.3 |  | 0%
| Total | 744 | 118.85 | 625.15 | 1176 | 39.78% | 0 | 0% | 1056 | 34.16% | 0 | 26.06% | 26.06% | 68.56% | 3.527% | 0% | 0 | 2976 | 5301.4 | 220 | 202 | 47 |  |  |  | Total | 725 | 117.7 | 607.3 | 2083 | 69.15% | 0 | 0% | 168 | 5.477% | 0 | 25.37% | 25.37% | 69.42% | 3.465% | 0% | 1 | 2976 | 5207.4 | 220 | 202 | 47 |  |  |  | Total | 718.375 | 43.8 | 674.575 | 2161.625 | 73.99% | 0 | 0% | 0 | 0% | 0 | 26.01% | 26.01% | 97.02% | 1.244% | 0% | 2 | 2880 | 1809.7 | 220 | 202 | 47 |  |  |  | Total | 704.91 | 138.2 | 566.71 | 2271.09 | 75.28% | 0 | 0% | 0 | 0% | 0 | 24.72% | 24.72% | 92.18% | 4.04% | 0% | 2 | 2976 | 6071.1 | 220 | 202 | 47 |  |  |  | Total | 719.9335 | 244.8485 | 475.085 | 2160.0665 | 300.0092 | 0 | 0 | 0 | 0 | 0 | 99.9908 | 99.9908 | 89.8188 | 7.723 | 0% | 0 | 2880 | 11232.4 | 220 | 202 | 46.5 |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 220 | 202 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 220 | 202 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 220 | 202 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 220 | 202 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 220 | 202 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 220 | 202 |  |  |  | Total | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 |  | 220 | 202
SAN JUAN TM | TM 1 | 744 | 88.03 | 655.97 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 11.83% | 0% | 0 | 744 | 2200.272 | 25 | 25 | 25 | 100% |  | SAN JUAN TM | TM 1 | 716.15 | 467.15 | 249 | 15.85 | 2.13% | 12 | 1.613% | 0 | 0% | 0 | 96.26% | 96.26% | 3.282% | 60.46% | 0% | 1 | 744 | 11244.853 | 25 | 25 | 25 | 100% |  | SAN JUAN TM | TM 1 | 713.13 | 374.17 | 338.96 | 6.87 | 0.9542% | 0 | 0% | 0 | 0% | 0 | 99.05% | 99.05% | 1.803% | 49.47% | 0% | 2 | 720 | 8904.47 | 25 | 25 | 25 | 100% |  | SAN JUAN TM | TM 1 | 387.1 | 260.51 | 126.59 | 356.9 | 47.97% | 0 | 0% | 0 | 0% | 0 | 52.03% | 52.03% | 57.81% | 32.19% | 0% | 1 | 744 | 5988.231 | 25 | 25 | 25 | 100% |  | SAN JUAN TM | TM 1 | 0 | 0 | 0 | 720 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0% | 0 | 720 | 0 | 25 | 25 | 25 | 10000% | SAN JUAN TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | SAN JUAN TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | SAN JUAN TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | SAN JUAN TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | SAN JUAN TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | SAN JUAN TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | SAN JUAN TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 2 | 568.87 | 361.94 | 206.93 | 175.13 | 23.54% | 0 | 0% | 0 | 0% | 0 | 76.46% | 76.46% | 32.61% | 49.38% | 0% | 0 | 744 | 9184.111 | 25 | 25 | 25 | 100% |  |  | TM 2 | 730.52 | 451.25 | 279.27 | 1.48 | 0.1989% | 12 | 1.613% | 0 | 0% | 0 | 98.19% | 98.19% | 0.3269% | 61.52% | 0% | 1 | 744 | 11443.562 | 25 | 25 | 25 | 100% |  |  | TM 2 | 704.3 | 336.15 | 368.15 | 15.7 | 2.181% | 0 | 0% | 0 | 0% | 0 | 97.82% | 97.82% | 4.462% | 47.23% | 0% | 2 | 720 | 8501.49 | 25 | 25 | 25 | 100% |  |  | TM 2 | 677.72 | 208.99 | 468.73 | 66.28 | 8.909% | 0 | 0% | 0 | 0% | 0 | 91.09% | 91.09% | 24.08% | 26.43% | 0% | 1 | 744 | 4916.05 | 25 | 25 | 25 | 100% |  |  | TM 2 | 719.83 | 17.11 | 702.72 | 0.17 | 0.023611 | 0 | 0 | 0 | 0 | 0 | 99.9764 | 99.9764 | 0.9838 | 2.0447 | 0% | 0 | 720 | 368.053 | 25 | 25 | 25 | 10000% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 3 | 568.86 | 369.72 | 199.14 | 175.14 | 23.54% | 0 | 0% | 0 | 0% | 0 | 76.46% | 76.46% | 32.14% | 47.91% | 0% | 0 | 744 | 8910.887 | 25 | 25 | 25 | 100% |  |  | TM 3 | 730.52 | 474.92 | 255.6 | 1.48 | 0.1989% | 12 | 1.613% | 0 | 0% | 0 | 98.19% | 98.19% | 0.3107% | 61.09% | 0% | 1 | 744 | 11363.546 | 25 | 25 | 25 | 100% |  |  | TM 3 | 717.73 | 358.96 | 358.77 | 2.27 | 0.3153% | 0 | 0% | 0 | 0% | 0 | 99.68% | 99.68% | 0.6284% | 47.03% | 0% | 1 | 720 | 8464.74 | 25 | 25 | 25 | 100% |  |  | TM 3 | 678.62 | 213.51 | 465.11 | 65.38 | 8.788% | 0 | 0% | 0 | 0% | 0 | 91.21% | 91.21% | 23.44% | 26.23% | 0% | 1 | 744 | 4878.091 | 25 | 25 | 25 | 100% |  |  | TM 3 | 719.83 | 17.91 | 701.92 | 0.17 | 0.023611 | 0 | 0 | 0 | 0 | 0 | 99.9764 | 99.9764 | 0.94027 | 2.1665 | 0% | 0 | 720 | 389.971 | 25 | 25 | 25 | 10000% |  | TM 3 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 4 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 25 | 25 | 0 | 100% |  |  | TM 4 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 25 | 25 | 25 | 100% |  |  | TM 4 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 720 | 0 | 25 | 25 | 25 | 100% |  |  | TM 4 | 263.9 | 38.37 | 225.53 | 480.1 | 64.53% | 0 | 0% | 0 | 0% | 0 | 35.47% | 35.47% | 92.6% | 4.881% | 0% | 0 | 744 | 907.829 | 25 | 25 | 25 | 100% |  |  | TM 4 | 719.83 | 26.47 | 693.36 | 0.17 | 0.023611 | 0 | 0 | 0 | 0 | 0 | 99.9764 | 99.9764 | 0.63814 | 3.523 | 0% | 0 | 720 | 634.14 | 25 | 25 | 25 | 10000% |  | TM 4 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 5 | 744 | 478.33 | 265.67 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 58.37% | 0% | 0 | 744 | 10856.733 | 25 | 25 | 25 | 100% |  |  | TM 5 | 732 | 448.06 | 283.94 | 0 | 0% | 12 | 1.613% | 0 | 0% | 0 | 98.39% | 98.39% | 0% | 60.64% | 0% | 0 | 744 | 11279.501 | 25 | 25 | 25 | 100% |  |  | TM 5 | 717.73 | 345.77 | 371.96 | 2.27 | 0.3153% | 0 | 0% | 0 | 0% | 0 | 99.68% | 99.68% | 0.6522% | 48.86% | 0% | 1 | 720 | 8793.94 | 25 | 25 | 25 | 100% |  |  | TM 5 | 556.95 | 207.2 | 349.75 | 187.05 | 25.14% | 0 | 0% | 0 | 0% | 0 | 74.86% | 74.86% | 47.44% | 27.33% | 0% | 1 | 744 | 5083.874 | 25 | 25 | 25 | 100% |  |  | TM 5 | 719.83 | 39.72 | 680.11 | 0.17 | 0.023611 | 0 | 0 | 0 | 0 | 0 | 99.9764 | 99.9764 | 0.42617 | 4.9496 | 0% | 0 | 720 | 890.926 | 25 | 25 | 25 | 10000% |  | TM 5 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 5 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 5 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 5 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 5 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 5 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 5 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 6 | 566.91 | 389.57 | 177.34 | 177.09 | 23.8% | 0 | 0% | 0 | 0% | 0 | 76.2% | 76.2% | 31.25% | 53.65% | 0% | 0 | 744 | 9979.412 | 25 | 25 | 25 | 100% |  |  | TM 6 | 730.52 | 459.3 | 271.22 | 1.48 | 0.1989% | 12 | 1.613% | 0 | 0% | 0 | 98.19% | 98.19% | 0.3212% | 61.95% | 0% | 1 | 744 | 11522.883 | 25 | 25 | 25 | 100% |  |  | TM 6 | 717.73 | 378.32 | 339.41 | 2.27 | 0.3153% | 0 | 0% | 0 | 0% | 0 | 99.68% | 99.68% | 0.5964% | 54.52% | 0% | 1 | 720 | 9814.27 | 25 | 25 | 25 | 100% |  |  | TM 6 | 678.11 | 224.05 | 454.06 | 65.89 | 8.856% | 0 | 0% | 0 | 0% | 0 | 91.14% | 91.14% | 22.73% | 29.5% | 0% | 1 | 744 | 5487.486 | 25 | 25 | 25 | 100% |  |  | TM 6 | 719.83 | 22.64 | 697.19 | 0.17 | 0.023611 | 0 | 0 | 0 | 0 | 0 | 99.9764 | 99.9764 | 0.74529 | 2.8851 | 0% | 0 | 720 | 519.314 | 25 | 25 | 25 | 10000% |  | TM 6 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 6 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 6 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 6 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 6 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 6 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 6 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 7 | 744 | 528.95 | 215.05 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 66.71% | 0% | 0 | 744 | 12407.201 | 25 | 25 | 25 | 100% |  |  | TM 7 | 732 | 556.95 | 175.05 | 0 | 0% | 12 | 1.613% | 0 | 0% | 0 | 98.39% | 98.39% | 0% | 71.25% | 0% | 0 | 744 | 13251.838 | 25 | 25 | 25 | 100% |  |  | TM 7 | 504.25 | 262.83 | 241.42 | 215.75 | 29.97% | 0 | 0% | 0 | 0% | 0 | 70.03% | 70.03% | 45.08% | 37.27% | 0% | 1 | 720 | 6708.55 | 25 | 25 | 25 | 100% |  |  | TM 7 | 657.08 | 401.82 | 255.26 | 86.92 | 11.68% | 0 | 0% | 0 | 0% | 0 | 88.32% | 88.32% | 17.78% | 47.73% | 0% | 1 | 744 | 8877.24 | 25 | 25 | 25 | 100% |  |  | TM 7 | 707.5 | 33.66 | 673.84 | 12.5 | 1.7361 | 0 | 0 | 0 | 0 | 0 | 98.2639 | 98.2639 | 27.0797 | 3.8029 | 0% | 1 | 720 | 684.525 | 25 | 25 | 25 | 10000% |  | TM 7 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 7 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 7 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 7 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 7 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 7 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 7 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 8 | 744 | 393.03 | 350.97 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 49.86% | 0% | 0 | 744 | 9273.033 | 25 | 25 | 25 | 100% |  |  | TM 8 | 732 | 508.39 | 223.61 | 0 | 0% | 12 | 1.613% | 0 | 0% | 0 | 98.39% | 98.39% | 0% | 65.64% | 0% | 0 | 744 | 12209.617 | 25 | 25 | 25 | 100% |  |  | TM 8 | 717.73 | 448.79 | 268.94 | 2.27 | 0.3153% | 0 | 0% | 0 | 0% | 0 | 99.68% | 99.68% | 0.5033% | 59.49% | 0% | 1 | 720 | 10708.47 | 25 | 25 | 25 | 100% |  |  | TM 8 | 657.09 | 405.36 | 251.73 | 86.91 | 11.68% | 0 | 0% | 0 | 0% | 0 | 88.32% | 88.32% | 17.65% | 48.73% | 0% | 1 | 744 | 9063.705 | 25 | 25 | 25 | 100% |  |  | TM 8 | 717.95 | 34.14 | 683.81 | 2.05 | 0.28472 | 0 | 0 | 0 | 0 | 0 | 99.7153 | 99.7153 | 5.6645 | 4.1404 | 0% | 1 | 720 | 745.265 | 25 | 25 | 25 | 10000% |  | TM 8 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 8 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 8 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 8 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 8 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 8 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 8 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 9 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 25 | 25 | 0 | 100% |  |  | TM 9 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 25 | 25 | 25 | 100% |  |  | TM 9 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 720 | 0 | 25 | 25 | 25 | 100% |  |  | TM 9 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 25 | 25 | 25 | 100% |  |  | TM 9 | 0 | 0 | 0 | 720 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0% | 0 | 720 | 0 | 25 | 25 | 25 | 10000% |  | TM 9 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 9 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 9 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 9 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 9 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 9 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 9 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 10 | 522.96 | 353.91 | 169.05 | 221.04 | 29.71% | 0 | 0% | 0 | 0% | 0 | 70.29% | 70.29% | 38.45% | 46.46% | 0% | 0 | 744 | 8640.77 | 25 | 25 | 25 | 100% |  |  | TM 10 | 732 | 495.5 | 236.5 | 0 | 0% | 12 | 1.613% | 0 | 0% | 0 | 98.39% | 98.39% | 0% | 64.64% | 0% | 0 | 744 | 12023.171 | 25 | 25 | 25 | 100% |  |  | TM 10 | 717.73 | 444.61 | 273.12 | 2.27 | 0.3153% | 0 | 0% | 0 | 0% | 0 | 99.68% | 99.68% | 0.508% | 59.07% | 0% | 1 | 720 | 10632.67 | 25 | 25 | 25 | 100% |  |  | TM 10 | 657 | 385.97 | 271.03 | 87 | 11.69% | 0 | 0% | 0 | 0% | 0 | 88.31% | 88.31% | 18.39% | 49.18% | 0% | 1 | 744 | 9147.605 | 25 | 25 | 25 | 100% |  |  | TM 10 | 703.61 | 41.92 | 661.69 | 16.39 | 2.2764 | 0 | 0 | 0 | 0 | 0 | 97.7236 | 97.7236 | 28.1084 | 5.1306 | 0% | 1 | 720 | 923.501 | 25 | 25 | 25 | 10000% |  | TM 10 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 10 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 10 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 10 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 10 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 10 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 10 | [16 empty] | 0 |  | 25 | 25 |  | 0%
PALO SECO TM | TM 1 | 742.72 | 546.73 | 195.99 | 1.28 | 0.172% | 0 | 0% | 0 | 0% | 0 | 99.83% | 99.83% | 0.2336% | 69.36% | 0% | 0 | 744 | 12900.142 | 25 | 25 | 25 | 100% |  | PALO SECO TM | TM 1 | 732 | 617.53 | 114.47 | 0 | 0% | 12 | 1.613% | 0 | 0% | 0 | 98.39% | 98.39% | 0% | 77.74% | 0% | 0 | 744 | 14459.08 | 25 | 25 | 25 | 100% |  | PALO SECO TM | TM 1 | 718.28 | 40.88 | 677.4 | 1.72 | 0.2389% | 0 | 0% | 0 | 0% | 0 | 99.76% | 99.76% | 4.038% | 5.597% | 0% | 1 | 720 | 1007.45 | 25 | 25 | 25 | 100% |  | PALO SECO TM | TM 1 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 25 | 25 | 25 | 100% |  | PALO SECO TM | TM 1 | 0 | 0 | 0 | 720 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0% | 0 | 720 | 0 | 25 | 25 | 25 | 10000% | PALO SECO TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | PALO SECO TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | PALO SECO TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | PALO SECO TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | PALO SECO TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | PALO SECO TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0% | PALO SECO TM | TM 1 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 2 | 742.24 | 547.53 | 194.71 | 1.76 | 0.2366% | 0 | 0% | 0 | 0% | 0 | 99.76% | 99.76% | 0.3204% | 74.05% | 0% | 0 | 744 | 13773.508 | 25 | 25 | 25 | 100% |  |  | TM 2 | 449.73 | 401.45 | 48.28 | 282.27 | 37.94% | 12 | 1.613% | 0 | 0% | 0 | 60.45% | 60.45% | 41.28% | 49.63% | 0% | 1 | 744 | 9231.643 | 25 | 25 | 25 | 100% |  |  | TM 2 | 720 | 447.67 | 272.33 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 59.69% | 0% | 0 | 720 | 10743.7 | 25 | 25 | 25 | 100% |  |  | TM 2 | 669 | 520.33 | 148.67 | 75 | 10.08% | 0 | 0% | 0 | 0% | 0 | 89.92% | 89.92% | 12.6% | 67.21% | 0% | 0 | 744 | 12501.852 | 25 | 25 | 25 | 100% |  |  | TM 2 | 704.88 | 460.59 | 244.29 | 15.12 | 2.1 | 0 | 0 | 0 | 0 | 0 | 97.9 | 97.9 | 3.1784 | 62.3928 | 0% | 0 | 720 | 11230.71 | 25 | 25 | 25 | 10000% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0% |  | TM 2 | [16 empty] | 0 |  | 25 | 25 |  | 0%
| TM 3 | 744 | 394.75 | 349.25 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 100% | 100% | 0% | 53.58% | 0% | 0 | 744 | 7973.27 | 20 | 20 | 20 | 100% |  |  | TM 3 | 732 | 599.2 | 132.8 | 0 | 0% | 12 | 1.613% | 0 | 0% | 0 | 98.39% | 98.39% | 0% | 78.4% | 0% | 0 | 744 | 11665.805 | 20 | 20 | 20 | 100% |  |  | TM 3 | 715.28 | 437.54 | 277.74 | 4.72 | 0.6556% | 0 | 0% | 0 | 0% | 0 | 99.34% | 99.34% | 1.067% | 59.86% | 0% | 1 | 720 | 8619.48 | 20 | 20 | 20 | 100% |  |  | TM 3 | 668.9 | 513.92 | 154.98 | 75.1 | 10.09% | 0 | 0% | 0 | 0% | 0 | 89.91% | 89.91% | 12.75% | 63.6% | 0% | 0 | 744 | 9464.193 | 20 | 20 | 20 | 100% |  |  | TM 3 | 713.47 | 455.65 | 257.82 | 6.53 | 0.90694 | 0 | 0 | 0 | 0 | 0 | 99.0931 | 99.0931 | 1.4129 | 59.281 | 0% | 2 | 720 | 8536.469 | 20 | 20 | 20 | 10000% |  | TM 3 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 3 | [16 empty] | 0 |  | 20 | 20 |  | 0%
| TM 4 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 20 | 20 | 0 | 100% |  |  | TM 4 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 20 | 20 | 20 | 100% |  |  | TM 4 | 0 | 0 | 0 | 720 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 720 | 0 | 20 | 20 | 20 | 100% |  |  | TM 4 | 0 | 0 | 0 | 744 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0% | 100% | 0% | 0% | 0 | 744 | 0 | 20 | 20 | 20 | 100% |  |  | TM 4 | 0 | 0 | 0 | 720 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0% | 0 | 720 | 0 | 20 | 20 | 20 | 10000% |  | TM 4 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 20 | 20 |  | 0% |  | TM 4 | [16 empty] | 0 |  | 20 | 20 |  | 0%
| Total | 7432.56 | 4452.49 | 2980.07 | 2983.44 | 28.01% | 0 | 0% | 0 | 0% | 0 | 71.99% | 71.99% | 30.51% | 41.94% | 0% | 0 | 10416 | 106099.339 | 340 | 340 | 270 |  |  |  | Total | 7749.44 | 5479.7 | 2269.74 | 2534.56 | 23.58% | 132 | 1.281% | 0 | 0% | 0 | 75.14% | 75.14% | 23.94% | 51.27% | 0% | 5 | 10416 | 129695.499 | 340 | 340 | 340 |  |  |  | Total | 7663.89 | 3875.69 | 3788.2 | 2416.11 | 23.19% | 0 | 0% | 0 | 0% | 0 | 76.81% | 76.81% | 24.94% | 37.95% | 0% | 12 | 10080 | 92899.23 | 340 | 340 | 340 |  |  |  | Total | 6551.47 | 3380.03 | 3171.44 | 3864.53 | 36.57% | 0 | 0% | 0 | 0% | 0 | 63.43% | 63.43% | 45.94% | 30.17% | 0% | 8 | 10416 | 76316.156 | 340 | 340 | 340 |  |  |  | Total | 7146.56 | 1149.81 | 5996.75 | 2933.44 | 2847% | 0 | 0% | 0 | 0% | 0 | 7153% | 7153% | 3301% | 1018% | 0% | 5 | 10080 | 24922.874 | 340 | 340 | 340 |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 340 | 340 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 340 | 340 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 340 | 340 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 340 | 340 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 340 | 340 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 340 | 340 |  |  |  | Total | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 340 | 340
| Total Peakers | 19521.39 | 8316.77 | 11204.62 | 7462.71 | 26.27% | 2463.9 | 13.86% | 1056 | 4.519% | 0 | 55.27% | 55.36% | 31.53% | 20.43% | 0% | 3 |  | 232070.739 | 1566 | 1526.8 | 883.2 |  |  |  | Total Peakers | 18700.14 | 9165.24 | 9534.9 | 8527.86 | 30.54% | 3108 | 16.4% | 168 | 0.7247% | 0 | 52.34% | 52.34% | 31.29% | 21.59% | 0% | 12 | 30504 | 245232.899 | 1566 | 1526.8 | 887.884 |  |  |  | Total Peakers | 18482.965 | 5974.67 | 12508.295 | 8157.035 | 30.04% | 2880 | 16.11% | 0 | 0% | 0 | 51.56% | 53.85% | 32.41% | 14.1% | 6.142e-09% | 15 | 29520 | 157509.93 | 1566 | 1526.8 | 881.0228 |  |  |  | Total Peakers | 17157.56 | 7844.13 | 9313.43 | 10363.56 | 35.42% | 2976 | 16.11% | 6.88 | 0.04676% | 0 | 48.42% | 48.42% | 40.73% | 18.63% | 0% | 20 | 30504 | 211630.256 | 1566 | 1526.8 | 881 |  |  |  | Total Peakers | 17195.4935 | 4835.9785 | 12359.515 | 9212.5065 | 11424% | 3087 | 16624% | 25 | 134.6% | 0 | 23832% | 23832% | 4649% | 1228% | 0% | 13 | 29520 | 135038.274 | 1566 | 1526.8 | 878.5 |  |  | Total Peakers | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 1566 | 1526.8 | 0 |  |  | Total Peakers | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 1566 | 1526.8 | 0 |  |  | Total Peakers | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 1566 | 1526.8 | 0 |  |  | Total Peakers | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 1566 | 1526.8 | 0 |  |  | Total Peakers | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 1566 | 1526.8 | 0 |  |  | Total Peakers | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 1566 | 1526.8 | 0 |  |  | Total Peakers | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 1566 | 1526.8 | 0
| Total System | 24932.09 | 13667.37 | 11264.72 | 9387.71 | 30.45% | 3951.9 | 9.049% | 1160.3 | 2.067% | 822.37 | 58.4% | 51.49% | 37.57% | 35.76% | 7% | 17 |  | 1069007.739 | 4358 | 4017.8 | 2045.2 |  |  |  | Total System | 23879.3 | 14284.3 | 9595 | 10630.7 | 32.51% | 4596 | 10.01% | 326 | 0.8091% | 485.33 | 56.66% | 52.69% | 35.86% | 37.21% | 3.978% | 23 | 39432 | 1112366.899 | 4358 | 4017.8 | 2594.884 |  |  |  | Total System | 23891.685 | 11380.99 | 12510.695 | 9702.645 | 28.52% | 4320 | 9.906% | 245.67 | 1.022% | 583.3 | 59.68% | 56.04% | 32.66% | 36.09% | 4.513% | 24 | 38160 | 1046618.93 | 4358 | 4017.8 | 2394.0228 |  |  |  | Total System | 23242.35 | 13928.92 | 9313.43 | 11718.77 | 29.11% | 4464 | 9.906% | 6.88 | 0.01777% | 855.68 | 60.97% | 55.27% | 35.39% | 40.14% | 5.692% | 33 | 39432 | 1199930.256 | 4358 | 4017.8 | 2690 |  |  |  | Total System | 22607.8135 | 10161.8185 | 12445.995 | 10876.6565 | 18671% | 4527 | 18717% | 148.53 | 1115% | 735.01 | 55662% | 49332% | 3692% | 3439% | 5.794% | 24 | 38160 | 994860.274 | 4358 | 4017.8 | 2675.5 |  |  | Total System | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 0 | 0 | 4358 | 4017.8 | 0 |  |  | Total System | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 0 | 0 | 4358 | 4017.8 | 0 |  |  | Total System | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 0 | 0 | 4358 | 4017.8 | 0 |  |  | Total System | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 0 | 0 | 4358 | 4017.8 | 0 |  |  | Total System | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 0 | 0 | 4358 | 4017.8 | 0 |  |  | Total System | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 0 | 0 | 4358 | 4017.8 | 0 |  |  | Total System | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 0 | 0 | 4358 | 4017.8 | 0
[75 empty] | VIEQUES | 1 | 744 | 1 | 564 | 179 | 24.06% | [18 empty] | VIEQUES | 1
[76 empty] | 2 | 744 | 1 | 564 | 179 | 24.06% | [19 empty] | 2
[76 empty] | Total | 1488 | 2 | 1128 | 358 | [20 empty] | Total
[75 empty] | CULEBRA | 1 | 744 | 1.1 | 742.9 | 0 | 0% | [18 empty] | CULEBRA | 1
[76 empty] | 2 | 744 | 1.1 | 742.9 | 0 | 0% | [19 empty] | 2
[76 empty] | 3 | 744 | 1 | 743 | 0 | 0% | [19 empty] | 3
[76 empty] | Total | 2232 | 3.2 | 2228.8 | 0 | [20 empty] | Total