## San Juan
October 2025 | [8 empty] | Comments
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
San Juan 5 | ULSD | 56840.67 | 5819964.36 | 330810673598.5212 | 112751000 | 110835000 | 8095.2115 | 8235.1531
| LNG |  | 5851646.4474 | 581932516482.71
San Juan 6 | ULSD | 78697.23 | 5819964.36 | 456453534690.97 | 94559000 | 92012000 | 10488.6158 | 10778.9529
| LNG |  | 5851646.4474 | 535339483517.29
Total San Juan CC |  |  |  | 1.9045e+12 | 207310000 | 202847000 | 9186.8999 | 9389.0282 | Heat rate includes Natural Gas invoiced consumption, which is the correct value.
Current month Heating value used not the previous month.
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
San Juan 7 | Bunker C | 0 | 0 | 0 | 0 | 0 | 0 | 0
San Juan 9 | Bunker C | 87763.54 | 6244149.91 | 548008700392.2814 | 55447000 | 54770785 | 9883.4689 | 10005.4929
Total San Juan - Steam |  | 87763.54 |  | 548008700392.2814 | 55447000 | 54770785 | 9883.4689 | 10005.4929 | Value doesn't include auxiliaries of units 7, 8, & 10 out of service.
November 2025
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
San Juan 5 | ULSD | 16891.51 | 5819957.22 | 98307865581.2022 | 74634000 | 73173000 | 8232.8184 | 8397.198
| LNG | 88989.708 | 5800000 | 516140306168.2402
San Juan 6 | ULSD | 38022.45 | 5819957.22 | 221289032399.589 | 93952000 | 91224000 | 10636.62 | 10954.7019
| LNG | 134145.292 | 5800000 | 778042693831.7598
Total San Juan CC |  | 278048.96 |  | 1.6138e+12 | 168586000 | 164397000 | 9572.4431 | 9816.3586 | Heat rate includes Natural Gas invoiced consumption, which is the correct value.
Current month Heating value used not the previous month.
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
San Juan 7 | Bunker C | 0 | 0 | 0 | 0 | 0 | 0 | 0
San Juan 9 | Bunker C | 90643.44 | 6238057.35 | 565438977121.2839 | 51136000 | 50484685 | 11057.552 | 11200.2081
Total San Juan - Steam |  | 90643.44 |  | 565438977121.2839 | 51136000 | 50484685 | 11057.552 | 11200.2081 | Value doesn't include auxiliaries of units 7, 8, & 10 out of service.
December 2025
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
San Juan 5 | ULSD | 1419.96 | 5797803.77 | 8232649441.2492 | 28100000 | 27236000 | 8595.1154 | 8867.7758
| LNG | 40222.4297 | 5800000 | 233290092154.8615
San Juan 6 | ULSD | 7557.06 | 5797803.77 | 43814350958.1162 | 49106000 | 48252000 | 10736.7788 | 10926.8063
| LNG | 83349.2945 | 5800000 | 483425907845.1385
Total San Juan CC |  | 132548.7441 |  | 768763000399.3655 | 77206000 | 75488000 | 9957.2961 | 10183.91
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
San Juan 7 | Bunker C | 0 | 0 | 0 | 0 | 0 | 0 | 0
San Juan 9 | Bunker C | 81831.47 | 6233364.16 | 510085352258.1152 | 46310000 | 45649567 | 11014.5833 | 11173.9363
Total San Juan - Steam |  | 81831.47 |  | 510085352258.1152 | 46310000 | 45649567 | 11014.5833 | 11173.9363

## Palo Seco
October 2025
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
Palo Seco 3 | ULSD | 150.64 | 5800830 | 873837031.2 | 71413000 | 65543923.89 | 10004.797 | 10900.6682
| Bunker C | 111426.33 | 6404220 | 713598731112.6
Palo Seco 4 | ULSD | 3210.57 | 5800830 | 18623970773.1 | 84690000 | 76029092.11 | 10270.0238 | 11439.9408
| Bunker C | 132903.67 | 6404220 | 851144341487.4
Total Palo Seco - Steam |  | 247691.21 |  | 1.5842e+12 | 156103000 | 141573016 | 10148.6895 | 11190.2743 | Propane consumption not included in total calculation.
November 2025
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
Palo Seco 3 | ULSD | 1176.91 | 5796098 | 6821485697.18 | 71599000 | 66637445.046 | 9848.2913 | 10581.5552
| Bunker C | 110818.79 | 6301335 | 698306320084.6499
Palo Seco 4 | ULSD | 2992.28 | 5796098 | 17343548123.44 | 36146000 | 32721514.59 | 11480.2582 | 12681.7299
| Bunker C | 63101.21 | 6301335 | 397621863115.35
Total Palo Seco - Steam |  | 178089.19 |  | 1.1201e+12 | 107745000 | 99358959.636 | 10395.7791 | 11273.1979 | Propane consumption not included in total calculation.
December 2025
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
Palo Seco 3 | ULSD | 469.47 | 5758128 | 2703268352.16 | 80621000 | 73525721.277 | 9673.5838 | 10607.0908
| Bunker C | 123812.34 | 6277167 | 777190734840.78
Palo Seco 4 | ULSD | 306.13 | 5758128 | 1762735724.64 | 80169670 | 71644183.723 | 10487.5768 | 11735.5734
| Bunker C | 133662.66 | 6277167 | 839022838484.22
Total Palo Seco - Steam |  | 258250.6 |  | 1.6207e+12 | 160790670 | 145169905 | 10079.4379 | 11164.019 | Propane consumption not included in total calculation.

## Aguirre
October 2025
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
Aguirre 1 | ULSD | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bunker C | 0 | 0 | 0
Aguirre 2 | ULSD | 626.72 | 5774817 | 3619193310.24 | 156060000 | 145882430 | 10884.7024 | 11644.0798
| Bunker C | 271547.44 | 6242178 | 1.695e+12
Total Aguirre - Steam |  | 272174.16 |  | 1.6987e+12 | 156060000 | 145882430 | 10884.7024 | 11644.0798 | Rounding issue.
November 2025
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
Aguirre 1 | ULSD | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bunker C | 0 | 0 | 0
Aguirre 2 | ULSD | 166.81 | 5779664 | 964105751.84 | 163525000 | 152897530 | 10687.4044 | 11430.2553
| Bunker C | 279961.08 | 6239059 | 1.7467e+12
Total Aguirre - Steam |  | 280127.89 |  | 1.7477e+12 | 163525000 | 152897530 | 10687.4044 | 11430.2553 | Rounding issue.
December 2025
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
Aguirre 1 | ULSD | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bunker C | 0 | 0 | 0
Aguirre 2 | ULSD | 771.14 | 5779925 | 4457131364.5 | 98055000 | 91079130 | 11079.1219 | 11927.6864
| Bunker C | 173368.59 | 6240497 | 1.0819e+12
Total Aguirre - Steam |  | 174139.73 |  | 1.0864e+12 | 98055000 | 91079130 | 11079.1219 | 11927.6864

## Aguirre CC
October 2025
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
1-1 | ULSD | 44792.01 | 5774817 | 258665660812.17 | 16722000 | 16655112 | 15468.584 | 15530.7068
1-2 | ULSD | 36369.9 | 5774817 | 210029516808.3 | 13713000 | 13658148 | 15316.0882 | 15377.5985
1-3 | ULSD | 0 | 0 | 0 | 0 | 0 | 0 | 0
1-4 | ULSD | 0 | 0 | 0 | 0 | 0 | 0 | 0
2-1 | ULSD | 27723.54 | 5774817 | 160098370092.18 | 10638000 | 10595448 | 15049.6682 | 15110.1086
2-2 | ULSD | 23986.21 | 5774817 | 138515973273.57 | 9335000 | 9297660 | 14838.3474 | 14897.9392
2-3 | ULSD | 0 | 0 | 0 | 0 | 0 | 0 | 0
2-4 | ULSD | 40516.65 | 5774817 | 233976239203.05 | 15406000 | 15344376 | 15187.3451 | 15248.3385
Total Aguirre CC |  | 173388.31 |  | 1.0013e+12 | 65814000 | 65550744 | 15213.8718 | 15274.9717
November 2025
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
1-1 | ULSD | 37268.48 | 5779664 | 215399292190.72 | 14247000 | 14190012 | 15118.9227 | 15179.6413
1-2 | ULSD | 31455.4 | 5779664 | 181801642985.6 | 11774000 | 11726904 | 15440.9413 | 15502.9531
1-3 | ULSD | 0 | 0 | 0 | 0 | 0 | 0 | 0
1-4 | ULSD | 0 | 0 | 0 | 0 | 0 | 0 | 0
2-1 | ULSD | 32861.05 | 5779664 | 189925827687.2 | 12709000 | 12658164 | 14944.1992 | 15004.2161
2-2 | ULSD | 25502.03 | 5779664 | 147393164717.92 | 10152000 | 10111392 | 14518.6332 | 14576.941
2-3 | ULSD | 0 | 0 | 0 | 0 | 0 | 0 | 0
2-4 | ULSD | 28589.32 | 5779664 | 165236663588.48 | 11057000 | 11012772 | 14944.0774 | 15004.0938
Total Aguirre CC |  | 155676.28 |  | 899756591169.9199 | 59939000 | 59699244 | 15011.2046 | 15071.4905
December 2025
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
1-1 | ULSD | 21050.7 | 5779925 | 121671467197.5 | 8007000 | 7974972 | 15195.6372 | 15256.6639
1-2 | ULSD | 16788.28 | 5779925 | 97034999279 | 6146000 | 6121416 | 15788.3175 | 15851.7244
1-3 | ULSD | 0 | 0 | 0 | 0 | 0 | 0 | 0
1-4 | ULSD | 0 | 0 | 0 | 0 | 0 | 0 | 0
2-1 | ULSD | 22231.91 | 5779925 | 128498772406.75 | 8699000 | 8664204 | 14771.6717 | 14830.9957
2-2 | ULSD | 25595.42 | 5779925 | 147939607943.5 | 10267000 | 10225932 | 14409.2342 | 14467.1027
2-3 | ULSD | 0 | 0 | 0 | 0 | 0 | 0 | 0
2-4 | ULSD | 12416.91 | 5779925 | 71768808531.75 | 4738000 | 4719048 | 15147.4902 | 15208.3235
Total Aguirre CC |  | 98083.22 |  | 566913655358.5 | 37857000 | 37705572 | 14975.1342 | 15035.2753

## Costa Sur
October 2025
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
Costa Sur 5 | LNG | 312969.0143 | 6266614.74 | 1961256238100 | 218790000 | 205907000 | 10897.0028 | 11578.7965
| Bunker C | 67733.36 | 6243585.336 | 422899013254.009
Costa Sur 6 | LNG | 178699.8746 | 6266614.7746 | 1119843274400 | 194590000 | 181735000 | 10643.0547 | 11395.8897
| Bunker C | 152346.56 | 6243585.336 | 951188748006.0442
Total Costa Sur - Steam |  | 711748.8089 |  | 4.4552e+12 | 413380000 | 387642000 | 10777.4621 | 11493.0458
November 2025
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
Costa Sur 5 | LNG | 293631.6944 | 6442014.7705 | 1891579712280 | 200400000 | 187356000 | 10960.321 | 11723.3947
| Bunker C | 48616.15 | 6270933.021 | 304868620388.8892
Costa Sur 6 | LNG | 201660.8453 | 6442014.7705 | 1.2991e+12 | 168430000 | 157402000 | 11176.2538 | 11959.2917
| Bunker C | 93018.74 | 6270933.021 | 583314288237.8136
Total Costa Sur - Steam |  | 636927.4297 |  | 4.0789e+12 | 368830000 | 344758000 | 11058.929 | 11831.0953
December 2025
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
Costa Sur 5 | LNG | 189320.1736 | 6303340.5834 | 1193349533400 | 172070000 | 161074000 | 10775.5906 | 11511.2052
| Bunker C | 105725.58 | 6250203 | 660806337292.74
Costa Sur 6 | LNG | 51317.2867 | 6303340.5834 | 323470336099.9999 | 172700000 | 161605000 | 10446.4121 | 11163.611
| Bunker C | 236892.31 | 6250203 | 1.4806e+12
Total Costa Sur - Steam |  | 583255.3503 |  | 3.6583e+12 | 344770000 | 322679000 | 10610.7006 | 11337.1221

## Cambalache
October 2025
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
Cambalache 2 | ULSD | 57709.58 | 5828303 | 336348918242.74 | 27427000 | 27115179 | 12263.4236 | 12404.4513
Cambalache 3 | ULSD | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Cambalache - Gas |  | 57709.58 |  | 336348918242.74 | 27427000 | 27115179 | 12263.4236 | 12404.4513
November 2025
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
Cambalache 2 | ULSD | 25470.55 | 5812773 | 148054525335.15 | 11870000 | 11637390 | 12473.0013 | 12722.3136
Cambalache 3 | ULSD | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Cambalache - Gas |  | 25470.55 |  | 148054525335.15 | 11870000 | 11637390 | 12473.0013 | 12722.3136
December 2025
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
Cambalache 2 | ULSD | 10399.02 | 5812773 | 60447142682.46 | 4756000 | 4586770 | 12709.6599 | 13178.586
Cambalache 3 | ULSD | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Cambalache - Gas |  | 10399.02 |  | 60447142682.46 | 4756000 | 4586770 | 12709.6599 | 13178.586

## Mayaguez
October 2025
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
Mayaguez 1 | ULSD | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mayaguez 2 | ULSD | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mayaguez 3 | ULSD | 5752.06 | 5798130.66 | 33351195444.1596 | 2959500 | 2955948.6 | 11269.1993 | 11282.7386
Mayaguez 4 | ULSD | 5895.34 | 5798130.66 | 34181951605.1244 | 3111600 | 3107866.1 | 10985.3296 | 10998.5278
Total Mayaguez - Gas |  | 11647.4 |  | 67533147049.284 | 6071100 | 6063814.7 | 11123.7086 | 11137.073 | Reported in the Quarterly Report a Gross Heat Rate for one unit instead of the entire plant.
November 2025
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
Mayaguez 1 | ULSD | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mayaguez 2 | ULSD | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mayaguez 3 | ULSD | 10591 | 5798130.66 | 61408001820.06 | 5550100 | 5543439.88 | 11064.3055 | 11077.5986
Mayaguez 4 | ULSD | 10432.15 | 5798130.66 | 60486968764.719 | 5682300 | 5675481.24 | 10644.8038 | 10657.5929
Total Mayaguez - Gas |  | 21023.15 |  | 121894970584.779 | 11232400 | 11218921.12 | 10852.086 | 10865.1241 | Updated fuel consumption and Heating value to calculate the Net Heat Rate for entire plant.
Gross Heat rate was being reported.
December 2025
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
Mayaguez 1 | ULSD | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mayaguez 2 | ULSD | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mayaguez 3 | ULSD | 10766.3 | 5854091.61 | 63026906500.743 | 5728500 | 5721625.8 | 11002.3403 | 11015.559
Mayaguez 4 | ULSD | 10808.59 | 5854091.61 | 63274476034.9299 | 5877600 | 5870546 | 10765.3593 | 10778.2949
Total Mayaguez - Gas |  | 21574.89 |  | 126301382535.6729 | 11606100 | 11592171.8 | 10882.3276 | 10895.4029 | Updated fuel consumption and Heating value to calculate the Net Heat Rate for entire plant.
Gross Heat rate was being reported.

## TMs
October 2025
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
San Juan TMs | LNG | 67784.2466 | 5800000 | 393148630000 | 54350111 | 54348869 | 11008.9555 | 11009.2071
| ULSD | 35377.47 | 5800000 | 205189326000
Palo Seco TMs | LNG | 19149.9483 | 5800000 | 111069700000 | 21966045 | 21965778 | 10698.0969 | 10698.2269
| ULSD | 21366.41 | 5800000 | 123925178000
Total TMs |  | 143678.0748 |  | 833332834000 | 76316156 | 76314647 | 10919.4812 | 10919.6972
November 2025
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
San Juan TMs | LNG | 7092.0603 | 5800000 | 41133950000 | 5155695 | 5154327 | 10883.451 | 10886.3396
| ULSD | 2582.38 | 5800000 | 14977804000
Palo Seco TMs | LNG | 32499.4983 | 5800000 | 188497090000 | 19767179 | 19766907 | 11256.3223 | 11256.4772
| ULSD | 5863.56 | 5800000 | 34008648000
Total TMs |  | 48037.4986 |  | 278617492000 | 24922874 | 24921234 | 11179.1879 | 11179.9236
December 2025
Unit | Fuel type | Fuel consumed (Barrels) | Heating Value (Btu/Barrels) | Btu | Gross Generation (kWh) | Net Generation (kWh) | Gross Heat Rate (Btu/kWh) | Net Heat Rate (Btu/kWh)
San Juan TMs | LNG | 56247.4345 | 5800000 | 326235120000.0001 | 27872081 | 27870546 | 11704.7278 | 11705.3724
| ULSD | 0 | 5800000 | 0
Palo Seco TMs | LNG | 21141.6897 | 5800000 | 122621800000 | 11137851 | 11137584 | 11009.4667 | 11009.7307
| ULSD | 0 | 5800000 | 0
Total TMs |  | 77389.1241 |  | 448856920000.0001 | 39009932 | 39008130 | 11506.2215 | 11506.7531