## June 2026
June 2026 Forced Outages Report
Unit | Description | Date Out | Time Out | Date In | Time In | Duration (Hrs) | Corrective Action | Root Cause Analysis
Aguirre CC 1-1 | Unit trip over temperature exahust gases (spread trip). | 2026-06-01 | 16:34 | 2026-06-01 | 18:42 | 2.1 | Themocouples #4 and #12 they crossed the signal with thermocouple #5 and #1, respectively. Another day they were changed. | RCA CC 1-1 June 1, 2026.pdf
Aguirre CC 2-1 | It was not a unit trip. When taking baterry bank 2-1 out of service, breaker 0012 and 0014 opened on the 230kv. | 2026-06-04 | 14:16 | 2026-06-04 | 17:00 | 2.7 | Battery bank 2-1 was put into service, 2 fuses on the UPS were replaced, and the trip coil on the incomming breaker 2A (4.16kv) was changed. | RCA CC 2-1 June 4. 2026.pdf
Aguirre CC 2-1 | Unit trip with output bars explore. | 2026-06-13 | 8:42 | 2026-06-18 | 20:28 | 131.8 | Completed, the output bars were removed, the insulation was changed and bars were cleaned. A test was perfomed on the transformer. | RCA CC 2-1 Jun 13, 2026.pdf
Aguirre CC 2-1 | Unit trip due to generator and exciter fault. Generator and transfomer lockout activated, relay 87T-2 and 87G-2. | 2026-06-22 | 22:47 | 2026-06-30 | 24:00 | 193.2 | The unit was disconnected from the transformer to isolate the fault. | RCA CC 2-1 Jun 22, 2026.pdf
Aguirre CC 2-2 | It was not a unit trip. When taking baterry bank 2-1 out of service, breaker 0012 and 0014 opened on the 230kv. | 2026-06-04 | 14:16 | 2026-06-04 | 17:00 | 2.7 | Battery bank 2-1 was put into service, 2 fuses on the UPS were replaced, and the trip coil on the incomming breaker 2A (4.16kv) was changed. | RCA CC 2-2 June 4, 2026.pdf
Aguirre CC 2-2 | Unit trip when U2-1 output bars explode. Lockout generator. | 2026-06-13 | 8:42 | 2026-06-14 | 18:36 | 33.9 | The U2-1 output bars were diconnected to isolate the fault. | RCA CC 2-2 June 13, 2026.pdf
Aguirre CC 2-2 | Unit trips when it syncs U2-1 for generator lockkout and relay 64G-2. Only one unit can be in service, going out through MPT 2-1/2-2. | 2026-06-18 | 20:58 | 2026-06-24 | 16:49 | 139.9 | After the U2-1 exciter explosion, it disconnected from the transformer and the relays of the U2-2 generator were calibrated. | RCA CC 2-2 June 18, 2026.pdf
Aguirre CC 2-4 | It was not a unit trip. When taking baterry bank 2-1 out of service, breaker 0012 and 0014 opened on the 230kv. | 2026-06-04 | 14:16 | 2026-06-04 | 17:00 | 2.7 | Battery bank 2-1 was put into service, 2 fuses on the UPS were replaced, and the trip coil on the incomming breaker 2A (4.16kv) was changed. | RCA CC 2-4 Jun 4, 2026.pdf
Aguirre CC 2-4 | It was not a unit trip, it was out of service when the fault occurred in the U2-1 output bars. | 2026-06-13 | 8:42 | 2026-06-13 | 11:20 | 2.6 | Completed, MOD 0015 was opened to isolate the fault and be able to energize the 230kv. | RCA CC 2-4 Jun 13, 2026.pdf
Aguirre CC 2-4 | Unit trips due to the area exciter U2-1 explotion when the 230kv goes out. | 2026-06-22 | 22:47 | 2026-06-23 | 8:50 | 10.1 | Completed, MOD 0015 was opened to isolate the fault and be able to energize the 230kv. | RCA CC 2-4 Jun 22, 2026.pdf
Cambalache 2 | Unavailability of the turbine's CO2 fire protection system. For safety reasons, the unit cannot operate without a fire protection system. | 2026-06-18 | 9:55 | 2026-06-26 | 16:32 | 198.61 | Repair on compressor and filling of the CO2 tank of the turbine fire protection system. | RCA Cambalache U2 & U3_Failure of the CO₂ cooling unit compressor_18-06-2026.pdf
Cambalache 3 | Unavailability of the turbine's CO2 fire protection system. For safety reasons, the unit cannot operate without a fire protection system. | 2026-06-18 | 9:55 | 2026-06-26 | 16:32 | 198.61 | Repair on compressor and filling of the CO2 tank of the turbine fire protection system. | RCA Cambalache U2 & U3_Failure of the CO₂ cooling unit compressor_18-06-2026.pdf
Mayaguez 3A | Inspection revealed that the starter of Unit 3B was damaged. Prior to this finding, the operators had shutted down both units 3A & 3B due to abnormal noise originating from within the equipment. | 2026-06-01 | 17:35 | 2026-06-01 | 18:06 | 0.52 | After confirming that the source of the noise was the starter of Unit 3B, Unit 3A was released for operation and placed back into service. | RCA Unit 3B_Ignition Speed Failure_01-06-26.pdf
Mayaguez 3A | One of the PLC cards failed, resulting in erroneous readings from PT501/PT502, which caused the unit to trip, as well as incorrect readings from other pressure transmitters, including PT1011 and PT1012. | 2026-06-09 | 5:31 | 2026-06-09 | 10:15 | 4.73 | The defective card was identified and replaced, restoring normal operation. | RCA Unit 3A_3B_PLC Card Failed_09-06-2026 (1).pdf
Mayaguez 3A | Switchyard breaker 0010 opened while the unit was in operation, resulting in a unit shutdown/trip. | 2026-06-13 | 18:16 | 2026-06-13 | 19:13 | 0.95 | LUMA was requested to reclose the breaker, as it falls under their area of responsibility. A subject matter expert later identified that the issue was caused by an Main Power Transformer relay associated with the step-up transformer (13.8 kV/115 kV). The issue was successfully resolved. | RCA MPT Unit 3_Breaker 0010 Trip_13-06-2026.pdf
Mayaguez 3B | Inspection revealed that the starter of Unit 3B was damaged. Prior to this finding, the operators had shutted down both units 3A & 3B due to abnormal noise originating from within the equipment. | 2026-06-01 | 16:53 | 2026-06-02 | 8:00 | 15.12 | Starter was replaced. | RCA Unit 3B_Ignition Speed Failure_01-06-26.pdf
Mayaguez 3B | One of the PLC cards failed, resulting in erroneous readings from PT501/PT502, which caused the unit to trip, as well as incorrect readings from other pressure transmitters, including PT1011 and PT1012. | 2026-06-09 | 5:06 | 2026-06-09 | 10:15 | 5.15 | The defective card was identified and replaced, restoring normal operation. | RCA Unit 3A_3B_PLC Card Failed_09-06-2026 (1).pdf
Mayaguez 3B | Switchyard breaker 0010 opened while the unit was in operation, resulting in a unit shutdown/trip. | 2026-06-13 | 18:16 | 2026-06-13 | 19:13 | 0.95 | LUMA was requested to reclose the breaker, as it falls under their area of responsibility. A subject matter expert later identified that the issue was caused by an MPT relay associated with the step-up transformer (13.8 kV/115 kV). The issue was successfully resolved. | RCA MPT Unit 3_Breaker 0010 Trip_13-06-2026.pdf
Palo Seco 1-2 | Igniter issues. | 2026-06-25 | 17:00 | 2026-06-27 | 10:56 | 41.93 | Reset igniter.
Palo Seco 1-2 | Igniter issues. | 2026-06-28 | 18:15 | 2026-06-29 | 20:00 | 25.75 | Reset igniter.
Palo Seco 1-2 | Fuel leak. | 2026-06-29 | 20:52 | 2026-06-30 | 24:00 | 27.12 | Corrected.
Palo Seco 1-2 | Fuel leak. | 2026-06-30 | 16:46 | 2026-06-30 | 17:15 | 0.48 | Corrected.
Palo Seco 3 | Broken Boiler. | 2026-06-01 | 22:21 | 2026-06-04 | 11:56 | 61.58 | Leaks corrected. | No RCA is required for this event, boiler tubes were repaired and hidrostatic test was performed.
Palo Seco 3 | Real air flow indicator bad signal caused trip. | 2026-06-24 | 11:40 | 2026-06-24 | 15:28 | 3.8 | Indicator corrected. | PS 3 AIRFLOW SIGNAL FAILURE
San Juan TM 2 | Node n-1 issues. | 2026-06-04 | 10:17 | 2026-06-09 | 10:50 | 120.55 | System inspected and reset.
San Juan TM 6 | Synchronizer fail. | 2026-06-02 | 18:19 | 2026-06-02 | 19:09 | 0.83 | Synchonizer fixed.
San Juan TM 7 | High temperature spread. | 2026-06-22 | 22:25 | 2026-06-23 | 15:30 | 17.08 | Technician replaced bolts.
San Juan TM 10 | Instrumentation fail. | 2026-06-23 | 15:47 | 2026-06-23 | 16:06 | 0.32 | System inspected and reset.
San Juan 9 | Fire on burner corner C. | 2026-06-17 | 4:40 | 2026-06-30 | 24:00 | 331.33 | Repairs in progress. | No RCA is required for this event, all burners components were inspected, replaced if neccesary and calibrated as part of current Major Maintenance/Environmetal Outage.
Jobos 1-2 | The turbine does not slow down enought to start. | 2026-06-07 | 18:47 | 2026-06-09 | 16:25 | 45.63 | Valve replacement 20 TU.
Daguao 1-1 | Generator Voltage Control trouble. | 2026-06-03 | 17:48 | 2026-06-03 | 18:00 | 0.2 | The Unit was repaired and brought back online.
Daguao 1-2 | Diesel leak at nozzle number 5. | 2026-06-09 | 15:27 | 2026-06-09 | 16:00 | 0.55 | The leak was repaired and brought back online.
Daguao 1-2 | High exhaust temperature spread. | 2026-06-11 | 17:05 | 2026-06-14 | 16:36 | 71.52 | The nozzles were replaced with new nozzles.
Daguao 1-2 | The water supply line to the speed reducer broke. | 2026-06-14 | 20:08 | 2026-06-14 | 23:55 | 3.78 | The water line was repaired and returned to service.
Daguao 1-2 | Flame detector failure the unit was cycling on and off. | 2026-06-15 | 17:02 | 2026-06-15 | 20:17 | 3.25 | The flame detector cable was found broke, it was replaced.
Daguao 1-2 | Flame detector fault, causing the unit to trip. | 2026-06-18 | 17:25 | 2026-06-18 | 24:00 | 6.58 | The flame detector were removed, cleaned and the unit was returned to service.
Daguao 1-1 | Ignition cable broke, preventing the unit from starting. | 2026-06-19 | 19:40 | 2026-06-19 | 23:30 | 3.83 | The ignition cables were replaced, and the unit was returned to service.
Daguao 1-1 | High exhaust temperature spread. | 2026-06-20 | 15:20 | 2026-06-20 | 18:10 | 2.83 | Fuel check valves were replaced,and the unit was returned to service.
Daguao 1-2 | Cooling system fan drive failure, causing the unit to trip on high temperature. | 2026-06-21 | 13:30 | 2026-06-21 | 16:30 | 3 | The fan system pins were repaired, and the unit was returned to service.

## April 2026
April 2026 Forced Outages Report
Unit | Cause | Out Date | Time Out | In Date | Time In | Duration (Hrs) | Corrective Action | Root Cause Analysis // Comments
Aguirre 2 | Unit tripped due to loss of condenser vacuum - Vacuum Pump 2-1 coupling failure. | 2026-04-12 | 19:18 | 2026-04-12 | 21:54 | 2.6 | Unit was returned to service limited to 20MW due to low condenser operating vacuum conditions. | Vacuum Pump 2-1 coupling failure. Apr 2026.pdf
Aguirre 2 | Unit tripped due to loss of condenser vacuum - Vacuum Pump 2-1 operating issues. | 2026-04-13 | 14:12 | 2026-04-13 | 16:45 | 2.55 | Vacuump Pump 2-1 was troubleshooted in order to normalize the main condenser vacuum operating conditions. | Vacuum Pump 2-1 coupling failure. Apr 2026.pdf
Aguirre CC 2-1 | Trip unit by fuel control. | 2026-04-01 | 18:00 | 2026-04-02 | 16:25 | 22.4 | Changed the TCQC board, which had low voltage and did not reach the fuel bypass valve control (LVDT). From the terminal block (QTBA), all cables associated with the natrual gas system were removed. | RCA CC 2-1- Trip unit by fuel control-Apr, 2026.pdf
Aguirre CC 2-1 | Trip unit by fuel control. | 2026-04-06 | 22:05 | 2026-04-07 | 15:22 | 17.3 | Changed the solenoid of the fuel bypass valve. Finished removing the cables associated with natural gas on the terminal block (QTBA). | RCA CC 2-1- Trip unit by fuel control-Apr, 2026.pdf
Aguirre CC 2-1 | Trip unit by fuel control. | 2026-04-07 | 19:24 | 2026-04-08 | 14:03 | 18.7 | Changed the solenoid block. | RCA CC 2-1- Trip unit by fuel control-Apr, 2026.pdf
Aguirre CC 2-1 | Trip unit by fuel control. | 2026-04-08 | 16:25 | 2026-04-08 | 18:19 | 1.9 | Disconnected RVDT #1 from the inlet guide vanes that was affecting the circuit. | RCA CC 2-1- Trip unit by fuel control-Apr, 2026.pdf
Daguao 1-1 | Circuit breaker 0010 opened. | 2026-04-18 | 2:00 | 2026-04-19 | 15:48 | 37.8 | Luma staff reset breaker and closed it. | Luma staff reset breaker and closed it.
Daguao 1-1 | Ground fault main power transformer. Water ingress in connection box. | 2026-04-22 | 12:40 | 2026-04-24 | 17:49 | 53.15 | Cleaned, painted and replaced lid gasket preventive maintenace was performed. | Cleaned, painted and replaced lid gasket preventive maintenace was performed.
Daguao 1-1 | Tripped due to fuel flow divider issues. | 2026-04-30 | 21:04 | 2026-04-30 | 21:32 | 0.47 | Calibrate and Master reset. | Calibrate and Master reset.
Daguao 1-2 | Ground fault main power transformer. Water ingress in connection box. | 2026-04-22 | 12:40 | 2026-04-24 | 17:49 | 53.15 | Cleaning, Painting and replaced cover gasket. | Cleaning, Painting and replaced cover gasket.
Daguao 1-2 | Circuit breaker 0010 opened. | 2026-04-18 | 2:00 | 2026-04-19 | 15:48 | 37.8 | Luma staff reset breaker and closed. | Luma staff reset breaker and closed.
Mayaguez 2A | Unit trip due a erratic pressure differential in a scavange line. | 2026-04-28 | 19:23 | 2026-04-30 | 0:00 | 52.62 | Unit 2A was disengaged in order to have online 2B. | Unit 2A was disengaged in order to have online 2B.
Mayaguez 2B | Because Unit 2A PT621 trip. Unit 2B can’t be online due to a high oil leak on 2A. | 2026-04-28 | 19:37 | 2026-04-30 | 0:00 | 24.1 | Unit 2A decoupled to keep Unit 2B available. | The Unit was uncoupled to have available unit 2B. The Unit was sent PW for in a Hot Gas Inspection
Mayaguez 3A | Unit was out due to a flame trip. | 2026-04-06 | 16:39 | 2026-04-06 | 19:51 | 3.2 | A software reset was made. | Evaluation of the area was made and the repair was a quick fix.
Mayaguez 4A | The unit exhibited a back pressure issue. This is typically caused by the fuel injection system, water injection system, or bleed valves that may or may not have opened at a specific point in time. A trendline analysis was performed to graphically identify the problem, and no discrepancies were found. | 2026-04-11 | 19:58 | 2026-04-30 | 24:00 | 460.03 | The data was sent to Mitsubishi. They instructed to calibrate the pressure transmitters and temperature sensors (TE). The process was been completed, and we are pending approval from Mitsubishi. Also, a boroscope inspection was made. | 0705_MAYAQUEZ_Eng A PB Dot 04-11-26.pdf
Mayaguez 4B | Unit trip due to a no light. | 2026-04-06 | 17:01 | 2026-04-07 | 17:07 | 24.1 | A replacement of the igniters was made. | RCA_Unit 4B_04_06_2026_Trip due to failure establish flame.pdf
Mayaguez 4B | The secondary fans located in the pump compartments have failed. | 2026-04-10 | 16:42 | 2026-04-10 | 16:57 | 0.25 | A software reset was made. | No RCA is required for this event. The secondary fans experienced a temporary failure and returned to normal operation after a software reset. No additional abnormalities were observed after the reset.
Mayaguez 4B | Because Unit A was under a boroscope inspection, unit B was not available. | 2026-04-14 | 9:26 | 2026-04-14 | 17:08 | 7.7 | Because Unit A was under a boroscope inspection, unit B was not available. | 0705_MAYAQUEZ_Eng A PB Dot 04-11-26.pdf
Mayaguez 4B | Because Unit A was under a boroscope inspection, unit B was not available. | 2026-04-15 | 9:03 | 2026-04-15 | 17:59 | 8.93 | Because Unit A was under a boroscope inspection, unit B was not available. | 0705_MAYAQUEZ_Eng A PB Dot 04-11-26.pdf
Mayaguez 4B | Unit was out due to a LUMA Switchyard open 0080 breaker. | 2026-04-19 | 18:02 | 2026-04-19 | 21:30 | 3.47 | LUMA personnel worked on Breaker 0080. | LUMA personnel worked on Breaker 0080. An RCA is not required.
Mayaguez 4B | Unit 4A was under a pressure transmiter and temperature sensor calibration. Therefore Unit 4B was out. | 2026-04-22 | 15:22 | 2026-04-22 | 15:53 | 0.52 | Pressure transmitter and temperature sensor calibrated. | 0705_MAYAQUEZ_Eng A PB Dot 04-11-26.pdf
Mayaguez 4B | Unit out of service due to a permissive alarm on 4A. The alarm is related to metal and carbon particles in the filters and chip detectors. | 2026-04-28 | 22:05 | 2026-04-29 | 15:22 | 17.28 | Unit 4A was disengaged in order to have unit 4B online. | The metal and carbon particles was identified and originating from the power turbine. The engine was decoupled, and the engine will be swapped. An RCA is not required since the power turbine will be sent out to repair.
Costa Sur 5 | Platen superheater issue. | 2026-04-11 | 0:36 | 2026-04-15 | 0:30 | 95.89 | Boiler repaired, hydrostatic performed and unit synchronized. | Platen superheater issue 11_24_26
Costa Sur 5 | Rotor collector rings issue. | 2026-04-15 | 0:55 | 2026-04-15 | 13:13 | 12.3 | Brush holder area cleaning performed and unit synchronized. | Rotor collector rings issue 15_4_26
Costa Sur 6 | Main stop valves issue. | 2026-04-20 | 16:42 | 2026-04-30 | 24:00 | 247.3 | Pending repair of main steam inlet valves to the turbine. | Main stop valves issues 20_4_26
San Juan TM 2 | Node fault. | 2026-04-28 | 18:30 | 2026-04-30 | 24:00 | 53.48 | System cleaned. | System cleaned.
San Juan TM 2 | Node fault. | 2026-04-02 | 17:44 | 2026-04-02 | 19:05 | 1.35 | System cleaned. | System cleaned.
San Juan TM 2 | Regas working relief valve. | 2026-04-25 | 7:45 | 2026-04-25 | 10:21 | 2.6 | Regas finished work. | Regas finished work.
San Juan TM 2 | Node fault. | 2026-04-28 | 14:12 | 2026-04-28 | 14:26 | 0.73 | System cleaned. | System cleaned.
San Juan TM 3 | Regas working relief valve. | 2026-04-25 | 7:45 | 2026-04-25 | 10:21 | 2.6 | Regas finished work. | Regas finished work.
San Juan TM 4 | Regas working relief valve. | 2026-04-25 | 7:45 | 2026-04-25 | 10:21 | 2.6 | Regas finished work. | Regas finished work.
San Juan TM 7 | Undiagnostic trip. | 2026-04-02 | 18:46 | 2026-04-02 | 22:17 | 3.52 | Unit restarted. | Unit restarted.
San Juan CT 5 | Fire protection trip. | 2026-04-21 | 4:01 | 2026-04-21 | 9:19 | 5.3 | Incorrect signal system failure, instrumentation section bypass logic, unit back online. | SJ 5 FIRE PROTECTION TRIP DUE TO WATER INSTRUSSION
San Juan CT 5 | Blade path temperature trip. | 2026-04-21 | 15:29 | 2026-04-21 | 16:20 | 0.85 | The automatic regulator failed. The regulator was bypassed and the system operated through the manual valve. | Blade path temperature trip
San Juan ST 5 | Fire protection trip. | 2026-04-21 | 4:01 | 2026-04-21 | 14:29 | 10.97 | Incorrect signal system failure, instrumentation section bypass logic, unit back online. | SJ 5 FIRE PROTECTION TRIP DUE TO WATER INSTRUSSION
San Juan ST 5 | Blade path temperature trip. | 2026-04-21 | 15:29 | 2026-04-21 | 18:41 | 3.2 | The automatic regulator failed. The regulator was bypassed and the system operated through the manual valve. | Blade path temperature trip.
Palo Seco 4 | Boiler lead leak. | 2026-04-09 | 21:40 | 2026-04-10 | 22:41 | 25.02 | The leak was corrected in the Boiler lead. | No RCA is required for this event, valve's packing was replaced.
Palo Seco 4 | Broken Boiler lines. | 2026-04-16 | 0:14 | 2026-04-20 | 8:31 | 104.28 | Lines were fixed. | No RCA is required for this event, boiler tubes were repaired and hidrostatic test was performed.
Palo Seco 4 | Broken Boiler lines. | 2026-04-27 | 19:51 | 2026-04-30 | 24:00 | 76.13 | Lines were fixed. | No RCA is required for this event, boiler tubes were repaired and hidrostatic test was performed.
Palo Seco 1-2 | High exhaust temperature fuel nozzles need replacement. | 2026-04-09 | 17:00 | 2026-04-10 | 13:00 | 20 | Fuel nozzles replaced. | Fuel nozzles replaced.
Palo Seco 1-2 | Fuel line leak. | 2026-04-27 | 19:17 | 2026-04-27 | 20:39 | 1.37 | Fuel line replaced. | Fuel line replaced.
Palo Seco 1-2 | Fuel line leak. | 2026-04-28 | 15:17 | 2026-04-29 | 17:43 | 26.43 | Fuel line replaced. | Fuel line replaced.
Palo Seco MP 1 | Turbine lubrication motor failed. | 2026-04-07 | 10:26 | 2026-04-07 | 16:19 | 5.88 | Replacement motor installed; scavenged from MP 3 unit. | No RCA is required for this event. A new motor was installed and Lube Oil PCV was adjusted following OEM parameters.
Palo Seco MP 3 | Combustor replacement needed. | 2026-04-06 | 12:22 | 2026-04-24 | 20:17 | 439.92 | Replacement completed. | No RCA is required for this event.
Palo Seco TM 2 | Loss of 480V. | 2026-04-17 | 19:00 | 2026-04-18 | 0:39 | 5.65 | Repairs completed. | Repairs completed.
Palo Seco TM 2 | VSV Driver failure. | 2026-04-29 | 20:09 | 2026-04-30 | 10:21 | 14.2 | VSV Pumps replaced. | VSV Pumps replaced.

## May 2026
May 2026 Forced Outages Report
Unit | Cause | Date Out | Time Out | Date In | Time In | Duration (Hrs) | Corrective Action | RCA Document // Comments
Aguirre CC 2-2 | Unit tripped over temperature exhaust gases, EX 2100 trip, Generator lockout, and external trip. Unit went up to 61 MW when Costa Sur 5 tripped. | 2026-05-25 | 21:56 | 2026-05-25 | 22:37 | 0.7 | The unit was normalized and put into service. | RCA CC 2-2 May 25, 2026.pdf
Aguirre CC 2-4 | Unit tripped when synchronizing by Inlet Guide Vane Control Trouble trip. | 2026-05-19 | 16:37 | 2026-05-19 | 17:25 | 0.8 | The L4IGVT signal was forced. | RCA CC 2-4 May 19, 2026.pdf
Aguirre CC 2-4 | Unit tripped over temperature exhaust gases, EX 2100 trip, Generator lockout, and external trip. Unit went up to 61 MW when Costa Sur 5 tripped. | 2026-05-25 | 21:56 | 2026-05-25 | 22:50 | 0.9 | The unit was normalized and ran at 3,600 rpm, LUMA TOC did not want it in service. | RCA CC 2-4 May 25, 2026.pdf
Aguirre CC 1-1 | Unit trip due to exhaust blower 1-1B output. | 2026-05-30 | 16:23 | 2026-05-30 | 17:07 | 0.7 | The unit was available with the exhaust blower 1-1A. The next day the motor was changed to 1-1B. | RCA CC 1-1 May 30, 2026.pdf
Cambalache 3 | Engine trip by low frequency. Electrical grid disturbance originated in Costa Sur 6 unit. | 2026-05-04 | 16:49 | 2026-05-04 | 18:59 | 2.17 | None. Out of Management Control (OMC) event for Cambalache plant. | 5.4.2026 - GCA-GT3 - MCB Tripped by Electrical Grid Disturbance.pdf
Costa Sur 6 | Unit 6 on 100% Bunker C. Bunker C control valve water accumulator broke apart causing the valve to shut instantaneously. This also caused a master fuel trip and tripped the Boiler and the unit out of service. | 2026-05-04 | 16:48 | 2026-05-04 | 18:38 | 1.85 | Water accumulator eliminated from the instrumentation line supply and proceeded with the synchronization of the unit. | BC_water_accumulator_4_5_26
Costa Sur 5 | MKVI activated the prot trip. | 2026-05-25 | 21:55 | 2026-05-28 | 13:03 | 63.13 | Checked the internal and termination wiring, also the circuit for the MKVI cabinet and proceeded with the synchronization of the unit. | MKVI_prot_trip_25_5_26
Mayaguez 2B | Flame out trip. | 2026-05-02 | 1:18 | 2026-05-02 | 8:02 | 6.73 | A reset was performed. | RCA Mayaguez_Unit 2B_Flame Out Trip_ 2-5-26 & 6-5-26.pdf
Mayaguez 2B | Flame out trip. | 2026-05-06 | 1:21 | 2026-05-06 | 16:18 | 14.95 | The igniters were cleaned and swapped out. | RCA Mayaguez_Unit 2B_Flame Out Trip_ 2-5-26 & 6-5-26.pdf
Mayaguez 3A | The Hydraulic System started a Permissive trip. | 2026-05-11 | 5:42 | 2026-05-11 | 7:25 | 1.72 | A reset was performed. | The unit failed a remote start by LUMA TOC during the period that there's no personnel from Genera in the Plant. At 7:00am when the Ops supervisor arrived the condition was inspected, reset an the unit was normalized.
Mayaguez 3A | Uni 3B was being aligned, therefore unit 3A was unavailable. | 2026-05-15 | 8:36 | 2026-05-16 | 17:01 | 32.42 | Alignment completed. | Swap Engine 3B no RCA is performed.
Mayaguez 3B | Unit 3B PB DOT trip. A boroscope was performed. Also pressure transmitters were high. Those are related with the scavange. | 2026-05-18 | 20:19 | 2026-05-29 | 18:27 | 262.13 | A boroscope was performed. Pressure Transmitters were calibrated, solenoid valve were replaced. | RCA Unit 3B - PB Dot Trip 18_05_2026.pdf
Mayaguez 3B | Pressure Transmitters remained high. | 2026-05-29 | 18:35 | 2026-05-30 | 14:09 | 19.57 | A loose fitting was found. | RCA Mayaguez_Unit 3B_PT616 and PT621 High Alarm 29_05_2026.pdf
Palo Seco 3 | Broken Boiler. | 2026-05-21 | 13:08 | 2026-05-31 | 23:59 | 250.85 | Corrected. | No RCA is required for this event, boiler tubes were repaired and hidrostatic test was performed.
Palo Seco 4 | Broken Boiler. | 2026-05-10 | 20:08 | 2026-05-13 | 12:45 | 64.62 | Corrected. | No RCA is required for this event, boiler tubes were repaired and hidrostatic test was performed.
Jobos 1-2 | Transformer 4003 out of service. Breaker 0010 open. | 2026-05-05 | 11:34 | 2026-05-05 | 19:35 | 8.1 | Luma corrected the fault in the transformer and closed breaker 0010. Out of Management Control (OMC) event for GeneraPR.
San Juan 9 | Electrical failure on Boiler Feed Pump 9-2. | 2026-05-23 | 15:20 | 2026-05-25 | 16:25 | 49.08 | Checked connections on Boiler Feed Pump 9-2 and certified a burned motor. | Electrical failure on Boiler Feed Pump 9-2.
San Juan TM 10 | Lost of mega vars controls. | 2026-05-19 | 5:14 | 2026-05-19 | 7:51 | 2.62 | Inspected and reset. | No RCA required,Frequency variance and activated a trip on the unit.
San Juan TM 10 | N1n5 node fault. | 2026-05-23 | 20:06 | 2026-05-23 | 23:35 | 3.48 | Cleaned and reset. | These are the nodes that works with the electrical cards in the unit. Communication to the turbine. Test was performed a cable was losse and reconnected.
San Juan TM 10 | Breaker issue. | 2026-05-25 | 1:15 | 2026-05-26 | 5:14 | 27.98 | Breaker repaired. | The 52G breaker conactor failed, system was repaired and put back on service.
San Juan TM 2 | Node n-1 issues. | 2026-05-01 | 16:06 | 2026-05-04 | 16:36 | 72.5 | System cleaned and reset. | There was a ground fault on the N1 communication to the turbine, multiple troubleshooting were needed to fix the issue, due to a ramdom ground fault
San Juan TM 2 | Node n-1 issues. | 2026-05-04 | 20:35 | 2026-05-06 | 16:25 | 43.83 | System cleaned and reset.
San Juan TM 2 | Node n-1 issues. | 2026-05-08 | 21:32 | 2026-05-12 | 12:00 | 86.47 | System cleaned and reset.
San Juan TM 2 | Node n-1 issues. | 2026-05-12 | 15:53 | 2026-05-14 | 14:55 | 47.03 | System cleaned and reset.
San Juan TM 2 | Node n-1 issues. | 2026-05-15 | 15:09 | 2026-05-21 | 17:42 | 146.55 | System cleaned and reset.
San Juan TM 2 | Node n-1 issues. | 2026-05-28 | 16:30 | 2026-05-31 | 23:59 | 79.48 | System cleaned and reset.
San Juan TM 2 | Node n-1 issues. | 2026-05-28 | 15:19 | 2026-05-28 | 16:09 | 0.83 | System cleaned and reset.
San Juan TM 5 | Main breaker failure. | 2026-05-25 | 1:16 | 2026-05-25 | 2:22 | 2.1 | Breaker fixed. | Principal Transformer Breaker Problem, The units must be taken out of service to fix issue. Breaker repaired.
San Juan TM 3 | Main breaker failure. | 2026-05-25 | 1:16 | 2026-05-25 | 2:22 | 2.1 | Breaker fixed. | Principal Transformer Breaker Problem, The units must be taken out of service to fix issue. Breaker repaired.
San Juan TM 7 | Main breaker failure. | 2026-05-25 | 1:16 | 2026-05-25 | 2:22 | 2.1 | Breaker fixed. | Principal Transformer Breaker Problem, The units must be taken out of service to fix issue. Breaker repaired.