## GSA_Noms_units considered
GSA Nominations
Units considered as available for relevant month (indicated as ON):
| SJTM1 | SJTM2 | SJTM3 | SJTM4 | SJTM5 | SJTM6 | SJTM7 | SJTM8 | SJTM9 | SJTM10 | # of units | PSTM1 | PSTM2 | PSTM3 | PSTM4 | # of units | PSMP1 | PSMP2 | PSMP3 | # of units
2025-12-01 | OFF | ON | ON | ON | ON | ON | ON | OFF | OFF | ON | 7 | OFF | ON | OFF | OFF | 1 | N/A | N/A | N/A | --
2026-01-01 | OFF | ON | ON | ON | ON | ON | ON | OFF | OFF | ON | 7 | OFF | ON | OFF | OFF | 1 | N/A | N/A | N/A | --
2026-02-01 | ON | ON | ON | ON | ON | ON | ON | OFF | OFF | ON | 8 | OFF | ON | OFF | OFF | 1 | N/A | N/A | N/A | --
2026-03-01 | OFF | ON | ON | ON | ON | ON | ON | OFF | OFF | ON | 7 | OFF | ON | OFF | OFF | 1 | ON | ON | ON | 3
2026-04-01 | OFF | ON | ON | ON | ON | ON | ON | OFF | OFF | ON | 7 | OFF | ON | OFF | OFF | 1 | ON | ON | ON | 3
2026-05-01 | ON | ON | ON | ON | ON | ON | ON | OFF | OFF | ON | 8 | OFF | ON | OFF | OFF | 1 | ON | OFF | ON | 2
2026-06-01 | OFF | ON | ON | ON | ON | ON | ON | OFF | OFF | ON | 7 | OFF | ON | OFF | OFF | 1 | ON | OFF | OFF | 1
2026-07-01 | OFF | ON | ON | ON | ON | ON | ON | OFF | OFF | ON | 7 | OFF | ON | OFF | ON | 2 | ON | OFF | ON | 2
2026-08-01 | OFF | OFF | ON | ON | ON | ON | ON | OFF | OFF | ON | 6 | OFF | ON | OFF | ON | 2 | ON | OFF | ON | 2
2026-09-01 | OFF | ON | ON | ON | ON | OFF | ON | OFF | OFF | ON | 6 | OFF | ON | OFF | OFF | 1 | ON | OFF | ON | 2
Note on C11: Jose Carrasco: OFF: May 1-7, on rest of month

## December 2025
December 2025
Unit | Description | Out Date | In Date | Duration (Hrs) | Corrective Action
Palo Seco TM 2 | Trip VSV Driver fault, cable E47 was disconnected from the servovalve. | 2025-12-13 | 2025-12-13 | 2.58 | The cable was reconnected, everything was put back in place and the alarm resetted.
Palo Seco TM 3 | Trip T54 High Temperature. | 2025-12-03 | 2025-12-31 | 677.88 | Pending new fuel nozzles. Still out of service.
San Juan TM 1 | Due to a failure on the isolators from the metal clad cabinet near GT-01, the breaker on the MPT opened causing an outage to the rest of the units. | 2025-12-01 | 2025-12-16 | 375.67 | Unit was isolated and proceeded to close the breaker on the MPT. GT-01 output cables were left disconnected in order to normalize the rest of the plant.
San Juan TM 10 | NOX Water Injection metering Valve demand & position FBK failing to operate. | 2025-12-16 | 2025-12-17 | 18.99 | NOX Water injection replaced.
San Juan TM 10 | MCD-1064D alarm for more than 10 minutes. | 2025-12-30 | 2025-12-30 | 4.28 | Cleaned MCD-1064D.
San Juan TM 2 | Turbine Lubrication Oil Supply Pressure LL. | 2025-12-19 | 2025-12-19 | 1 | Replacement of TLO SUPPLY and SCAVENGE filters.
San Juan TM 2 | GEN Lube Oil Supply Pressure LL / isolation cable ripped. | 2025-12-23 | 2025-12-23 | 2.26 | Replaced cable C28S/XG28P.
San Juan TM 2 | GEN Lube Oil Supply Pressure LL. | 2025-12-28 | 2025-12-28 | 1 | Replaced Relay of FTM 107.1 K16
San Juan TM 4 | CPU Card Fail Micronet. | 2025-12-08 | 2025-12-16 | 201.5 | IP address input re-entered.
San Juan TM 8 | High Spread T48. | 2025-12-03 | 2025-12-31 | 674.88 | Still out of service.
Nominated unit | Downtime | Allocation of MMBtu's per unit downtime
SJTM2 | 4.26 | 527.407
SJTM3
SJTM4 | 201.5 | 24946.5973
SJTM5
SJTM6
SJTM7
SJTM10 | 23.27 | 2880.9296
PSTM2 | 2.58 | 348.945
| 231.61 | 28703.8789 | MMBtu

## January 2026
January 2026
Unit | Description | Out Date | In Date | Duration (Hrs) | Corrective Action
Palo Seco MP 1 | DC Lube Oil Pump Generator failure. | 2026-01-23 | 2026-01-24 | 23.92 | Pump motor replacement.
Palo Seco MP 2 | DC Lube oil Pump Generator failure. | 2026-01-03 | 2026-01-05 | 47.43 | Lube Oil Pump Motor replacement.
Palo Seco MP 2 | Diesel fuel Pump Oil leak. | 2026-01-05 | 2026-01-06 | 17.53 | Pump Seal and packing replacement.
Palo Seco MP 2 | AC lube oil motor failure. | 2026-01-16 | 2026-01-17 | 21.55 | AC pump motor replacement.
Palo Seco TM 2 | Problems with Regas protection system, low gas supply pressure. | 2026-01-05 | 2026-01-05 | 0.55 | The gas plant normalized their pumps.
San Juan TM 1 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-31 | 193.17 | Work in progress.
San Juan TM 10 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-24 | 44.02 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit.
San Juan TM 2 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-27 | 114.35 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit.
San Juan TM 2 | Lube oil system problems. | 2026-01-18 | 2026-01-18 | 2.05 | Replaced N47 relay switch.
San Juan TM 3 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-27 | 114.35 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit.
San Juan TM 4 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-26 | 91.53 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit.
San Juan TM 5 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-24 | 44.02 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit.
San Juan TM 5 | Gas leak on manifold, J-tubes and convoluted hoses. | 2026-01-23 | 2026-01-29 | 126.12 | Replaced gas manifold, J-tubes and convoluted hoses.
San Juan TM 6 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-24 | 44.02 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit.
San Juan TM 7 | Issue with the water injection pump. | 2026-01-13 | 2026-01-14 | 15.49 | The water injection pump was replaced.
San Juan TM 7 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-24 | 44.02 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit.
Nominated unit | Downtime | Allocation of MMBtu's per unit downtime
SJTM2 | 116.4 | 15743.7929
SJTM3 | 114.35 | 15466.5182
SJTM4 | 91.53 | 12379.9773
SJTM5 | 170.14 | 23012.4477
SJTM6 | 44.02 | 5953.967
SJTM7 | 59.51 | 8049.0817
SJTM10 | 44.02 | 5953.967
PSTM2 | 0.55 | 74.3875
| 640.52 | 86634.1393 | MMBtu

## February 2026
February 2026
Unit | Description | Out Date | In Date | Duration (Hrs) | Corrective Action
Palo Seco MP 2 | Lube Oil Presure Drain High Breeder. | 2026-02-18 | 2026-02-28 | 239.5 | In process of troubleshooting.
Palo Seco MP 3 | Gen Lube Oil Pump Coupling failure. | 2026-02-21 | 2026-02-28 | 175.07 | Waiting for coupling delivery.
Nominated unit | Downtime
SJTM1
SJTM2
SJTM3
SJTM4
SJTM5
SJTM6
SJTM7
SJTM10
PSTM2
0

## March 2026
March 2026
Unit | Description | Out Date | In Date | Duration (Hrs) | Corrective Action
Palo Seco MP 1 | Gas leak and Gen LO failure. | 2026-03-22 | 2026-03-28 | 145.35 | Replaced Gen LO motor, a gas hose and seals.
Palo Seco MP 1 | LUMA switchyard event. | 2026-03-30 | 2026-03-30 | 2.33 | Out of Management Control (OMC) event.
Palo Seco MP 3 | Turbine oil leak. | 2026-03-03 | 2026-03-04 | 31.5 | Replaced seal.
Palo Seco MP 3 | LUMA switchyard event. | 2026-03-30 | 2026-03-30 | 2.33 | Out of Management Control (OMC) event.
Palo Seco TM 2 | Voltage fluctuation and MVAR caused the trip of the units. | 2026-03-30 | 2026-03-30 | 2.17 | Out of management control (OMC) event / LUMA restored the nominal voltage, unit became available.
San Juan TM 2 | Lube oli system problems | 2026-03-02 | 2026-03-02 | 0.42 | Verified generator oil levels and the connection to the oil level transmitter.
San Juan TM 2 | Lube oli system problems | 2026-03-04 | 2026-03-04 | 12.22 | Verified generator oil levels and the connection to the oil level transmitter.
San Juan TM 2 | Lube oli system problems | 2026-03-07 | 2026-03-07 | 0.45 | Verified generator oil levels and the connection to the oil level transmitter.
San Juan TM 2 | Lube oli system problems | 2026-03-17 | 2026-03-17 | 0.32 | Verified generator oil levels and the connection to the oil level transmitter.
San Juan TM 2 | Lube oli system problems | 2026-03-19 | 2026-03-19 | 1.5 | Verified generator oil levels and the connection to the oil level transmitter.
San Juan TM 2 | Lube oli system problems | 2026-03-20 | 2026-03-20 | 1.33 | Verified generator oil levels and the connection to the oil level transmitter.
San Juan TM 2 | Blackstart Diesel Fuel Pump Failure. | 2026-03-21 | 2026-03-26 | 116.72 | Removed diesel fuel pump, none available in stock. A 480v external feeder was rerouted from GT-05 Switchgear to energize auxiliary equipments.
San Juan TM 2 | Lube oli system problems | 2026-03-31 | 2026-03-31 | 0.62 | Verified generator oil levels and the connection to the oil level transmitter.
San Juan TM 3 | Blackstart Diesel Fuel Pump Failure. | 2026-03-21 | 2026-03-26 | 116.72 | Removed diesel fuel pump, none available in stock. A 480v external feeder was rerouted from GT-05 Switchgear to energize auxiliary equipments.
San Juan TM 4 | Liquid fuel primary manifold thermocouple failure | 2026-03-25 | 2026-03-25 | 0.37 | Replaced thermocouple on primary manifold liquid fuel system.
San Juan TM 6 | NPT Hi Speed Derivative. | 2026-03-21 | 2026-03-21 | 0.58 | Replaced acelerometer
Nominated unit | Downtime | Allocation of MMBtu's per unit downtime
SJTM2 | 133.58 | 22341.3319
SJTM3 | 116.72 | 19521.4872
SJTM4 | 0.37 | 61.8827
SJTM5
SJTM6 | 0.58 | 97.0053
SJTM7
SJTM10
PSTM2 | 2.17 | 250.5417
PSMP1 | 147.68 | 17050.6882
PSMP2
PSMP3 | 33.83 | 3905.9099
| 434.93 | 63228.847 | MMBtu

## April 2026
April 2026
Unit | Description | Date Out | Time Out | Date In | Time In | Duration (Hrs) | Corrective Action
Palo Seco MP 1 | Turbine lubrication motor failed. | 2026-04-07 | 10:26 | 2026-04-07 | 16:19 | 5.88 | Replacement motor installed scavenged from MP 3 unit.
Palo Seco MP 3 | Combustor replacement needed. | 2026-04-06 | 12:22 | 2026-04-24 | 20:17 | 439.92 | Replacement completed.
Palo Seco TM 2 | Loss of 480V. | 2026-04-17 | 19:00 | 2026-04-18 | 0:39 | 5.65 | Repairs completed.
Palo Seco TM 2 | VSV Driver failure. | 2026-04-29 | 20:09 | 2026-04-30 | 10:21 | 14.2 | VSV Pumps replaced.
San Juan TM 2 | Node fault. | 2026-04-28 | 18:30 | 2026-04-30 | 24:00 | 53.48 | System cleaned.
San Juan TM 2 | Node fault. | 2026-04-02 | 17:44 | 2026-04-02 | 19:05 | 1.35 | System cleaned.
San Juan TM 2 | Regas working relief valve. Out of Management Control (OMC) event. | 2026-04-25 | 7:45 | 2026-04-25 | 10:21 | 2.6 | Regas finished work.
San Juan TM 2 | Node fault. | 2026-04-28 | 14:12 | 2026-04-28 | 14:26 | 0.73 | System cleaned.
San Juan TM 3 | Regas working relief valve. Out of Management Control (OMC) event. | 2026-04-25 | 7:45 | 2026-04-25 | 10:21 | 2.6 | Regas finished work.
San Juan TM 4 | Regas working relief valve. Out of Management Control (OMC) event. | 2026-04-25 | 7:45 | 2026-04-25 | 10:21 | 2.6 | Regas finished work.
San Juan TM 7 | Undiagnostic trip. | 2026-04-02 | 18:46 | 2026-04-02 | 22:17 | 3.52 | Unit restarted.
Nominated unit | Downtime | Allocation of MMBtu's per unit downtime
SJTM2 | 58.16 | 10488.5329
SJTM3 | 2.6 | 468.8821
SJTM4 | 2.6 | 468.8821
SJTM5
SJTM6
SJTM7 | 3.52 | 634.7943
SJTM10
PSTM2 | 19.85 | 2280.749
PSMP1 | 5.88 | 675.6073
PSMP2
PSMP3 | 439.92 | 50546.4532
| 532.53 | 65563.9009 | MMBtu

## May 2026
May 2026
Unit | Description | Date Out | Time Out | Date In | Time In | Duration (Hrs) | Corrective Action
Palo Seco MP 1 | High vibration in K-Flange. | 2026-05-05 | 0:00 | 2026-05-05 | 7:52 | 7.87 | Faulty sensor was diagnosed and replaced.
San Juan TM 10 | Lost of mega vars controls. | 2026-05-19 | 5:14 | 2026-05-19 | 7:51 | 2.62 | Inspected and reset.
San Juan TM 10 | N1n5 node fault. | 2026-05-23 | 20:06 | 2026-05-23 | 23:35 | 3.48 | Cleaned and reset.
San Juan TM 10 | Breaker issue. | 2026-05-25 | 1:15 | 2026-05-26 | 5:14 | 27.98 | Breaker repaired.
San Juan TM 2 | Node n-1 issues. | 2026-05-01 | 16:06 | 2026-05-04 | 16:36 | 72.5 | System cleaned and reset.
San Juan TM 2 | Node n-1 issues. | 2026-05-04 | 20:35 | 2026-05-06 | 16:25 | 43.83 | System cleaned and reset.
San Juan TM 2 | Node n-1 issues. | 2026-05-08 | 21:32 | 2026-05-12 | 12:00 | 86.47 | System cleaned and reset.
San Juan TM 2 | Node n-1 issues. | 2026-05-12 | 15:53 | 2026-05-14 | 14:55 | 47.03 | System cleaned and reset.
San Juan TM 2 | Node n-1 issues. | 2026-05-15 | 15:09 | 2026-05-21 | 17:42 | 146.55 | System cleaned and reset.
San Juan TM 2 | Node n-1 issues. | 2026-05-28 | 15:19 | 2026-05-28 | 16:09 | 0.83 | System cleaned and reset.
San Juan TM 2 | Node n-1 issues. | 2026-05-28 | 16:30 | 2026-05-31 | 24:00 | 79.48 | System cleaned and reset.
San Juan TM 3 | Main breaker failure. | 2026-05-25 | 1:16 | 2026-05-25 | 2:22 | 2.1 | Breaker fixed.
San Juan TM 5 | Main breaker failure. | 2026-05-25 | 1:16 | 2026-05-25 | 2:22 | 2.1 | Breaker fixed.
San Juan TM 7 | Main breaker failure. | 2026-05-25 | 1:16 | 2026-05-25 | 2:22 | 2.1 | Breaker fixed.
Nominated unit | Downtime | Allocation of MMBtu's per unit downtime
SJTM1
SJTM2 | 476.69 | 83539.2017
SJTM3 | 2.1 | 368.0218
SJTM4
SJTM5 | 2.1 | 368.0218
SJTM6
SJTM7 | 2.1 | 368.0218
SJTM10 | 34.08 | 5972.4685
PSTM2
PSMP1 | 7.87 | 1245.8647
PSMP3
| 524.94 | 91861.6004 | MMBtu

## June 2026
June 2026
Unit | Description | Date Out | Time Out | Date In | Time In | Duration (Hrs) | Corrective Action
San Juan TM 10 | Instrumentation fail. | 2026-06-23 | 15:47 | 2026-06-23 | 16:06 | 0.32 | System inspected and reset.
San Juan TM 2 | Node n-1 issues. | 2026-06-04 | 10:17 | 2026-06-09 | 10:50 | 120.55 | System inspected and reset.
San Juan TM 6 | Synchronizer fail. | 2026-06-02 | 18:19 | 2026-06-02 | 19:09 | 0.83 | Synchonizer fixed.
San Juan TM 7 | High temperature spread. | 2026-06-22 | 22:25 | 2026-06-23 | 15:30 | 17.08 | Technician replaced bolts.
Nominated unit | Downtime | Allocation of MMBtu's per unit downtime
SJTM2 | 120.55 | 21739.9009
SJTM3
SJTM4
SJTM5
SJTM6 | 0.83 | 149.6816
SJTM7 | 17.08 | 3080.195
SJTM10 | 0.32 | 57.7086
PSTM2
PSMP1
| 138.78 | 25027.4861 | MMBtu

## July 2026
July 2026
Unit | Description | Date Out | Time Out | Date In | Time In | Duration (Hrs) | Corrective Action
Palo Seco MP 3 | Fuel leak. | 2026-07-18 | 19:42 | 2026-07-18 | 22:32 | 2.83 | Fuel leak corrected.
Palo Seco MP 3 | Turbine revolutions dropped below safe parameters and tripped. | 2026-07-19 | 0:53 | 2026-07-19 | 1:11 | 0.3 | Unit inspected and reset back to service.
Palo Seco MP 3 | Water injection pump failed. | 2026-07-21 | 17:58 | 2026-07-21 | 18:50 | 0.87 | Systems inspected and ran without water injection.
Palo Seco TM 2 | Operating Procedure error involving auxiliary transformers. Tripped unit from loss of power. | 2026-07-31 | 10:28 | 2026-07-31 | 14:00 | 3.53 | Unit inspected and reset back to service.
San Juan TM 10 | High blade path spread. | 2026-07-12 | 18:42 | 2026-07-13 | 14:16 | 19.57 | Clogged fuel nozzles.
San Juan TM 10 | High blade path spread. | 2026-07-13 | 15:03 | 2026-07-15 | 11:50 | 44.78 | Fuel nozzles replaced.
San Juan TM 4 | Unit tripped due to a undiagnosed issue. | 2026-07-17 | 14:00 | 2026-07-17 | 14:07 | 0.12 | Unit was inspected and greenlit for return to service.
San Juan TM 4 | Diesel skid trip and tripped the unit off. | 2026-07-22 | 0:00 | 2026-07-22 | 0:21 | 0.35 | System reset.
San Juan TM 5 | Swap out broken Water injection pump. | 2026-07-11 | 1:11 | 2026-07-11 | 11:16 | 10.08 | Water injection pump swapped and operated successfully.
San Juan TM 7 | Loose gas lines causing leak. | 2026-07-14 | 1:21 | 2026-07-14 | 2:40 | 1.32 | Lines were tightened.
San Juan TM 7 | Primary diesel skid tripped and left unit without fuel. | 2026-07-21 | 14:45 | 2026-07-21 | 14:53 | 0.13 | Pumps inspected and reset.
San Juan TM 7 | Diesel skid tripped and left unit without fuel. | 2026-07-22 | 0:00 | 2026-07-22 | 0:15 | 0.25 | Pumps inspected and reset.
San Juan TM 7 | High Lower Explosion Limit (LEL) detected in Enclosure. Unit was removed from service. | 2026-07-23 | 22:09 | 2026-07-24 | 1:55 | 3.77 | Lines were tightened.
San Juan TM 7 | High Lower Explosion Limit (LEL) detected in Enclosure. Unit was removed from service. | 2026-07-24 | 17:07 | 2026-07-25 | 16:26 | 23.32 | Lines were replaced.
Nominated unit | Downtime | Allocation of MMBtu's per unit downtime
SJTM2
SJTM3
SJTM4 | 0.47 | 84.7595
SJTM5 | 10.08 | 1817.82
SJTM6
SJTM7 | 28.79 | 5191.968
SJTM10 | 64.35 | 11604.833
PSTM2 | 3.53 | 636.8341
PSTM4
PSMP1
PSMP3 | 4 | 721.625
| 111.22 | 20057.8396 | MMBtu

## August 2026
August 2026
Unit | Description | Date Out | Time Out | Date In | Time In | Duration (Hrs) | Corrective Action
Palo Seco MP1 | GT-ANHDOT flameout. | 2026-08-17 | 0:36 | 2026-08-31 | 24:00 | 359.4 | Pending.
Palo Seco MP3 | Tripped due to high pressure at sensor PDT629A. | 2026-08-16 | 19:18 | 2026-08-31 | 24:00 | 364.7 | Pending.
Palo Seco TM 2 | Loss of Transformer for the unit. | 2026-08-06 | 8:56 | 2026-08-31 | 24:00 | 615.1 | Pending.
San Juan TM 10 | VSV driver fault. | 2026-08-05 | 15:36 | 2026-08-05 | 18:20 | 2.73 | Inspected and reset.
San Juan TM 10 | VSV driver fault. | 2026-08-05 | 18:34 | 2026-08-06 | 10:25 | 15.85 | Servo valve replacement for VSV.
San Juan TM 10 | Fuel supplier pressure issues. | 2026-08-08 | 18:28 | 2026-08-08 | 19:20 | 0.87 | Fuel supplier resolved issue.
San Juan TM 10 | Hydraulic pump shaft broken, gas generator couldn't reach correct speed, stuck at 1900 RPM. | 2026-08-15 | 15:43 | 2026-08-17 | 18:25 | 50.7 | Hydraulic pump, Gearbox and clutch were swapped.
San Juan TM 10 | Auxiliary Transformer connection opened. | 2026-08-23 | 6:35 | 2026-08-24 | 20:33 | 37.97 | Lightning rod and Breakers serviced.
San Juan TM 10 | Fuel supplier issues. | 2026-08-27 | 21:30 | 2026-08-28 | 7:41 | 10.18 | Greenlit for ULSD operation.
San Juan TM 2 | Faulty reading on Glo supply sensor. | 2026-08-05 | 19:25 | 2026-08-05 | 21:22 | 1.95 | Connections were cleaned and tested.
San Juan TM 2 | Faulty reading on turbine fuel supply sensor. | 2026-08-06 | 9:04 | 2026-08-06 | 13:03 | 3.98 | Sensor connections cleaned and tested.
San Juan TM 2 | Fuel supplier pressure issues. | 2026-08-07 | 22:51 | 2026-08-07 | 23:10 | 0.32 | Fuel Supplier corrected their issues with supply pressure.
San Juan TM 2 | Trip enclosure Damper B closed. | 2026-08-08 | 17:02 | 2026-08-08 | 22:43 | 5.68 | Systems inspected and reset.
San Juan TM 2 | Trip enclosure Damper B closed. | 2026-08-09 | 15:48 | 2026-08-09 | 19:06 | 3.3 | Systems inspected and reset.
San Juan TM 2 | Node connection issues. | 2026-08-10 | 23:47 | 2026-08-11 | 13:15 | 13.47 | Grounds and connections cleaned and tested.
San Juan TM 2 | Node N1 trip. | 2026-08-10 | 15:45 | 2026-08-10 | 20:52 | 5.12 | Connections cleaned and tested.
San Juan TM 2 | Node connection issues. | 2026-08-11 | 14:23 | 2026-08-12 | 10:58 | 20.58 | Connection cleaned and tested.
San Juan TM 2 | Faulty sensor reading for oil level. | 2026-08-12 | 12:41 | 2026-08-12 | 16:27 | 3.77 | Bypassed sensor readings.
San Juan TM 2 | Auxiliary Transformer connection opened. | 2026-08-23 | 6:35 | 2026-08-24 | 20:33 | 37.97 | Lightning rod and Breakers serviced.
San Juan TM 2 | Loss of fuel supplier pressure. Hydraulic crank pump broke shaft. | 2026-08-28 | 1:35 | 2026-08-28 | 12:35 | 11 | Hydraulic pump swapped out.
San Juan TM 3 | Fuel supplier pressure issues. | 2026-08-07 | 22:51 | 2026-08-07 | 23:11 | 0.33 | Fuel supplier resolved issue.
San Juan TM 3 | Auxiliary Transformer connection opened. | 2026-08-23 | 6:35 | 2026-08-24 | 20:33 | 37.97 | Lightning rod and Breakers serviced.
San Juan TM 3 | Trip due to Compressor sensor PT-8004 PS3. | 2026-08-27 | 16:10 | 2026-08-29 | 12:59 | 44.82 | Sensor was cleaned and calibrated, Breaker to hydraulic pump serviced, Hydraulic pump swapped.
San Juan TM 4 | Fuel supplier pressure issues. | 2026-08-07 | 22:51 | 2026-08-07 | 23:11 | 0.33 | Fuel supplier resolved issue.
San Juan TM 4 | Water injection pump failed. | 2026-08-10 | 15:39 | 2026-08-10 | 17:47 | 2.13 | Returned to service without Water Injection until replacement available.
San Juan TM 4 | Auxiliary Transformer connection opened. | 2026-08-23 | 6:35 | 2026-08-24 | 20:33 | 37.97 | Lightning rod and Breakers serviced.
San Juan TM 5 | Water injection pump trip. | 2026-08-10 | 15:30 | 2026-08-10 | 17:47 | 2.28 | Returned to service without Water Injection until replacement available.
San Juan TM 5 | Fuel supplier pressure issues. | 2026-08-08 | 18:28 | 2026-08-08 | 19:20 | 0.87 | Fuel supplier resolved issue.
San Juan TM 5 | Auxiliary Transformer connection opened. | 2026-08-23 | 6:35 | 2026-08-24 | 20:33 | 37.97 | Lightning rod and Breakers serviced.
San Juan TM 6 | Auxiliary Transformer connection opened. | 2026-08-23 | 6:35 | 2026-08-24 | 20:33 | 37.97 | Lightning rod and Breakers serviced.
San Juan TM 7 | Fuel supplier pressure issues. | 2026-08-08 | 18:28 | 2026-08-08 | 19:20 | 0.87 | Greenlit for ULSD operation.
San Juan TM 7 | Auxiliary Transformer connection opened. | 2026-08-23 | 6:35 | 2026-08-24 | 20:33 | 37.97 | Lightning rod and Breakers serviced.
San Juan TM 7 | Fuel supplier issues. | 2026-08-27 | 21:19 | 2026-08-28 | 7:41 | 10.37 | Greenlit for ULSD operation.
Nominated unit | Downtime | Allocation of MMBtu's per unit downtime
SJTM3 | 83.12 | 14989.8839
SJTM4 | 40.43 | 7291.1574
SJTM5 | 41.12 | 7415.5922
SJTM6 | 37.97 | 6847.5203
SJTM7 | 49.21 | 8874.5451
SJTM10 | 118.3 | 21334.2549
PSTM2 | 615.1 | 110967.8844
PSTM4
PSMP1 | 359.4 | 64838.0062
PSMP3 | 364.7 | 65794.1594
| 1709.35 | 308353.0038 | MMBtu

## Sept 2026
September 2026
Unit | Description | Date Out | Time Out | Date In | Time In | Duration (Hrs) | Corrective Action
Palo Seco MP1 | Loss of Supplier Gas Pressure. Outside of Management Control (OMC) event. | 2026-09-13 | 13:09 | 2026-09-13 | 13:33 | 0.4 | Supplier restored pressure levels to correct parameters.
Palo Seco MP1 | Issues with Electrical grid activated protection systems. Outside of Management Control (OMC) event. | 2026-09-30 | 2:10 | 2026-09-30 | 2:24 | 0.23 | Systems inspected and reset.
San Juan TM 10 | Trip caused by sensor TE-4021B. | 2026-09-01 | 14:07 | 2026-09-01 | 15:59 | 1.87 | Sensor replaced.
San Juan TM 10 | High temperature in enclosure; loss of fans. | 2026-09-17 | 17:47 | 2026-09-17 | 18:09 | 0.37 | VSV systems were tested and corrected.
San Juan TM 10 | VSV fault. | 2026-09-17 | 18:33 | 2026-09-18 | 18:36 | 24.05 | VSV systems were tested and corrected.
San Juan TM 10 | LUMA grid event activated Power Plant protections. Outside of Management Control (OMC) event. | 2026-09-23 | 20:52 | 2026-09-24 | 1:20 | 4.47 | Breaker reconnected and systems tested. Greenlit for operation.
San Juan TM 10 | 38KV Breaker tripped due to LUMA grid event. Outside of Management Control (OMC) event. | 2026-09-30 | 2:09 | 2026-09-30 | 3:30 | 1.35 | Systems inspected and reset Breaker. Greenlit for operation.
San Juan TM 2 | High pressure in diesel manifold trip. | 2026-09-01 | 1:46 | 2026-09-01 | 2:32 | 0.77 | Filter swap and replacement.
San Juan TM 2 | Loose cable on sensor TE-2305. | 2026-09-01 | 15:53 | 2026-09-01 | 16:34 | 0.68 | Reconnected sensor.
San Juan TM 2 | Loss of LNG pressure. Outside of Management Control (OMC) event. | 2026-09-16 | 0:00 | 2026-09-16 | 7:25 | 7.42 | Supplier corrected the issue.
San Juan TM 2 | LUMA grid event activated Power Plant protections. Outside of Management Control (OMC) event. | 2026-09-23 | 20:52 | 2026-09-24 | 1:20 | 4.47 | Breaker reconnected and systems tested. Greenlit for operation.
San Juan TM 2 | 38KV Breaker tripped due to LUMA grid event. Outside of Management Control (OMC) event. | 2026-09-30 | 2:09 | 2026-09-30 | 3:30 | 1.35 | Systems inspected and reset Breaker. Greenlit for operation.
San Juan TM 3 | LUMA grid event activated Power Plant protections. Outside of Management Control (OMC) event. | 2026-09-23 | 20:52 | 2026-09-24 | 1:20 | 4.47 | Breaker reconnected and systems tested. Greenlit for operation.
San Juan TM 3 | 38KV Breaker tripped due to LUMA grid event. Outside of Management Control (OMC) event. | 2026-09-30 | 2:09 | 2026-09-30 | 3:30 | 1.35 | Systems inspected and reset Breaker. Greenlit for operation.
San Juan TM 4 | Temperature flame spread trip. | 2026-09-16 | 19:03 | 2026-09-16 | 20:42 | 1.65 | Systems inspected and reset.
San Juan TM 4 | LUMA grid event activated Power Plant protections. Outside of Management Control (OMC) event. | 2026-09-23 | 20:52 | 2026-09-24 | 1:20 | 4.47 | Breaker reconnected and systems tested. Greenlit for operation.
San Juan TM 4 | 38KV Breaker tripped due to LUMA grid event. Outside of Management Control (OMC) event. | 2026-09-30 | 2:09 | 2026-09-30 | 3:30 | 1.35 | Systems inspected and reset Breaker. Greenlit for operation.
San Juan TM 5 | NGGDOT flameout, fuel skid tripped. | 2026-09-16 | 19:29 | 2026-09-16 | 20:42 | 1.22 | Systems inspected and reset.
San Juan TM 5 | Fuel pressure fluctuation trip. | 2026-09-19 | 14:27 | 2026-09-19 | 15:19 | 0.87 | Systems inspected and reset.
San Juan TM 5 | LUMA grid event activated Power Plant protections. Outside of Management Control (OMC) event. | 2026-09-23 | 20:52 | 2026-09-24 | 1:20 | 4.47 | Breaker reconnected and systems tested. Greenlit for operation.
San Juan TM 5 | Fuel skid trip. | 2026-09-25 | 21:22 | 2026-09-25 | 21:39 | 0.28 | Systems inspected and reset.
San Juan TM 5 | 38KV Breaker tripped due to LUMA grid event. Outside of Management Control (OMC) event. | 2026-09-30 | 2:09 | 2026-09-30 | 3:30 | 1.35 | Systems inspected and reset Breaker. Greenlit for operation.
San Juan TM 6 | LUMA grid event activated Power Plant protections. Outside of Management Control (OMC) event. | 2026-09-23 | 20:52 | 2026-09-24 | 1:20 | 4.47 | Breaker reconnected and systems tested. Greenlit for operation.
San Juan TM 6 | 38KV Breaker tripped due to LUMA grid event. Outside of Management Control (OMC) event. | 2026-09-30 | 2:09 | 2026-09-30 | 3:30 | 1.35 | Systems inspected and reset Breaker. Greenlit for operation.
San Juan TM 7 | Temperature spread trip. | 2026-09-16 | 19:15 | 2026-09-17 | 20:17 | 25.03 | Combustor swap to send old ones for cleaning.
San Juan TM 7 | LUMA grid event activated Power Plant protections. Outside of Management Control (OMC) event. | 2026-09-23 | 20:52 | 2026-09-24 | 1:20 | 4.47 | Breaker reconnected and systems tested. Greenlit for operation.
San Juan TM 7 | 38KV Breaker tripped due to LUMA grid event. Outside of Management Control (OMC) event. | 2026-09-30 | 2:09 | 2026-09-30 | 3:30 | 1.35 | Systems inspected and reset Breaker. Greenlit for operation.
Nominated unit | Downtime | Allocation of MMBtu's per unit downtime
SJTM2 | 14.69 | 2649.1987
SJTM3 | 5.82 | 1049.5804
SJTM4 | 7.47 | 1347.1419
SJTM5 | 8.19 | 1476.9869
SJTM7 | 30.85 | 5563.4976
SJTM10 | 32.11 | 5790.7263
PSTM2
PSMP1 | 0.63 | 120.3562
PSMP3
| 99.76 | 17997.488 | MMBtu