## Service Planner
Date | 2026-10-26
SITE | Turbine Number | GG PT SERIAL Number | Before Genera Last Hot section Date | Pec Report | NFE Certificate used | Last Hotsection Date Hours | Forced Outage Date | IN/OUT of service | Comments
PSTP | GT01 | 557-259 |  | Operating beyond OEM recommendations | 2024-05-17 |  | 2025-09-02 | Out | FORCED
[5 empty] | 9531 |  |  |  | VSV / HOT SECTION DAMAGE
| GT02 | 557-121 |  | Operating beyond OEM recommendations | 2024-05-02 | HS is on site. Once TM 6 is avalible to be removed from service. The LPT will be removed and joined with the new hot section for PS tm 2 | 2026-08-06 | Out | Hot section damaged / Tx failure- Hot section received
| GT03 | 481-559 |  |  |  | - | 2025-12-03 | Out | FORCED
[6 empty] | - |  |  | Major OH/ High Temperature Spread
| GT04 | 481-717 |  | Operating beyond OEM recommendations | 2024-05-02 | - | 2025-06-13 | Out | FORCED
[6 empty] | - |  |  | Major OH/ VSV Failure
SJTP | GT01 | 557-238 | 2023-08-20 |  |  |  | 2026-01-22 | Out | FORCED
|  |  | 3361 | [5 empty] | Hot section/VSV AUX Switchgear Explosion
| GT02 | 557-251 |  | Operating beyond OEM recommendations |  | 8/13/2026 Repaired by Genera |  | IN
17903
| GT03 | 557-258 |  | Operating beyond OEM recommendations
IN
| GT04 | 557-268 |  | Operating beyond OEM recommendations
[6 empty] | Hot Section is on site .Once unit is avaible to be removed from service hot section will be installed |  | IN
| GT05 | 557-252 | 2023-08-14
4140
| GT06 | 557-254 |  | Operating beyond OEM recommendations |  | Hs is being procured and unit needs to be shipped to the states for repair. The LPT will be removed and used on PS TM 2 |  |  | Emergency use
[8 empty] | IN | HOT SECTION DAMAGE
| GT07 | 557-230 | 2024-01-17
2403
| GT08 | 557-242 | 2024-01-26 |  |  |  | 2025-12-03 | Out | FORCED
|  |  | 5487 | [5 empty] | HS/VSV/ High Temperature Spread
| GT09 | 557-266 | 2024-02-01 |  |  | IN the USA Currently being repaired by Genera | 2025-01-08 | Out | FORCED
[8 empty] | IN | HOT SECTION DAMAGE - SW Explosion
| GT10 | 557-262 | 2024-02-05 |  |  |  |  | IN
5562

## Pec Report summary
San Juan Power Plant – Gas Turbine Maintenance Status
Unit | Current Status / Findings | Last HSE / Inspection | Recommended Action | Scheduled / Due
GT-1 | Hot Section Exchange (HSE) completed | HSE: Aug. 20, 2023 | Continue annual borescope inspections. Prepare for next HSE after 25,000 fired hours. | Based on fired hours
GT-2 | Operating beyond OEM recommendations | — | Perform Hot Section Exchange as soon as possible. | Oct. 1, 2024
GT-3 | Operating beyond OEM recommendations | — | Perform Hot Section Exchange as soon as possible. | Oct. 7, 2024
GT-4 | Operating beyond OEM recommendations | — | Perform Hot Section Exchange as soon as possible. | May 15, 2024
GT-5 | Hot Section Exchange (HSE) completed | HSE: Aug. 14, 2023 | Continue annual borescope inspections. Prepare for next HSE after 25,000 fired hours. | Based on fired hours
GT-6 | Operating within OEM specifications based on last borescope inspection | Borescope: Mar. 6, 2024 | Perform Hot Section Exchange based on operating hours. | Oct. 14, 2024
GT-7 | Hot Section Exchange (HSE) completed | HSE: Jan. 17, 2024 | Continue annual borescope inspections. Prepare for next HSE after 25,000 fired hours. | Based on fired hours
GT-8 | Hot Section Exchange (HSE) completed | HSE: Jan. 26, 2024 | Continue annual borescope inspections. Prepare for next HSE after 25,000 fired hours. | Based on fired hours
GT-9 | Hot Section Exchange (HSE) completed | HSE: Feb. 1, 2024 | Continue annual borescope inspections. Prepare for next HSE after 25,000 fired hours. | Based on fired hours
GT-10 | Hot Section Exchange (HSE) completed | HSE: Feb. 5, 2024 | Continue annual borescope inspections. Prepare for next HSE after 25,000 fired hours. | Based on fired hours
Palo Seco Power Plant – Gas Turbine Maintenance Status
Unit | Current Status / Findings | Last HSE / Inspection | Recommended Action | Scheduled / Due
GT-1 | Operating beyond OEM recommendations | — | Perform Hot Section Exchange as soon as possible. | May 15, 2024
GT-2 | Stage 16 High Pressure Compressor and outlet guide vane damage. Operating beyond OEM recommendations. Risk of damaged Stage 16 blade liberation and additional unit damage. | Borescope: Mar. 12, 2024 | Stage 16 High Pressure Compressor Exchange and outlet guide vane replacement as soon as possible. Schedule outage immediately. | ASAP / Outage required
GT-3 | Annual borescope inspection required; previous inspection completed May 2023. | Borescope: May 2023 | Schedule annual borescope inspection. Determine Hot Section Exchange timing based on findings and unit operating regime. | Borescope due in 2024
GT-4 | Stage 16 High Pressure Compressor and outlet guide vane damage. Operating beyond OEM recommendations. Risk of damaged Stage 16 blade liberation and additional unit damage. | Borescope: Mar. 14, 2024 | Stage 16 High Pressure Compressor Exchange and outlet guide vane replacement as soon as possible. Schedule outage immediately. | ASAP / Outage required