## Sheet1
TM's Borescope Inspection Summary | [6 empty] | 2025 | [5 empty] | 2024
[7 empty] | Cost of Inspection $164.076,92, O&M services also included | [5 empty] | Cost of Inspection $421,595.2, Semi-annual inspections included
Cost of Inspection $77,000. 00 |  |  |  | Account: 01-1071-31101-555-663-100G26109002 |  |  | Account: 01-1071-31101-555-663-100G26109002 | [5 empty] | Account: 01-1071-31101-555-663-100G26109002
Site | Unit | Date | Hours | Done By | Findings | Comparison Against Previous Reports | Site | Unit | Date | Hours | Done By | Findings | Site | Unit | Date | Hours | Done By | Findings
SJTP | GT01 | 2026-06-12 | 16172.54 | GESA | VSV actuation system failed to move freely Hot Section is SERVICEABLE | Inspection results are consistent with normal wear from previous inspection. No abnormal damage detected | SJTP | GT01 | 2025-08-04 | 7266 | SOM | Serviceable | SJTP | GT01 | 2024-11-29 | 6272 | PPGEnergy | Serviceable
| GT02 | 2026-06-13 | 17903 | GESA | NOT SERVICEABLE - Combustor Cracks HPT copious amounts of material missing | Inspection results are consistent with previous inspection findings. Perform Hot Section replacement |  | GT02 | N/A | NFE reported that it was not done since contractor was asked to replace Nozzles at Palo Seco |  |  |  | GT02 | 2024-12-01 | 11613 | PPGEnergy | Not Serviceable
| GT03 | 2026-06-14 | 17297 | GESA | NOT SERVICEABLE - Combustor burn through HPT cooling holes plugged and burn through | Inspection results are consistent with previous inspection findings. Perform Hot Section replacement |  | GT03 | 2025-08-06 | 14052 | SOM | Not Serviceable |  | GT03 | 2024-12-04 | 2081 | PPGEnergy | Not Serviceable
| GT04 | 2026-06-15 | 14429 | GESA | NOT SERVICEABLE - Combustor missing rivets/burn through HPT Trailing edge heavy erosion | Inspection results show clear deterioration compared to previous inspection findings. Schedule a Hot Section replacement. |  | GT04 | 2025-08-07 | N/A | SOM | Serviceable |  | GT04 | N/A | Unit suffered Hot Section Damage in Nov. Report requested to NFE
| GT05 | 2026-06-16 | 19606 | GESA | NOT SERVICEABLE - Combustor cracks/burn through HPT Serviceable light erosion | Inspection results are consistent with previous inspection findings. Combustor cracks have increased and should be replaced |  | GT05 | 2025-08-08 | 16253 | SOM | Serviceable |  | GT05 | 2024-12-07 | 12223 | PPGEnergy | Serviceable
| GT06 | 2026-06-17 | 16621 | GESA | NOT SERVICEABLE - Compressor STG16 blade damage HPT Burn trough holes/ heavy erosion | Inspection results are consistent with previous inspection findings. Top Case service is needed and Hot Section replacement |  | GT06 | 2025-08-11 | 13422 | SOM | Not Serviceable |  | GT06 | 2024-11-23 | 9148 | PPGEnergy | Not Serviceable
| GT07 | 2026-06-18 | 17279 | GESA | NOT SERVICEABLE - Combustor burn through and cracks HPT Damage, missing material | Inspection results show clear deterioration compared to previous inspection findings. Schedule a Hot Section replacement. |  | GT07 | 2025-08-12 | 13736 | SOM | Serviceable |  | GT07 | 2024-12-13 | 9305 | PPGEnergy | Serviceable
| GT08 | 2026-06-19 | 16778 | GESA | NOT SERVICEABLE - Combustor burn through HPT Burn trough holes/ heavy erosion | Inspection results confirm previous inspection findings. Perform Hot Section replacement |  | GT08 | 2025-08-13 | 15618 | SOM | Not Serviceable |  | GT08 | 2024-11-26 | 11345 | PPGEnergy | Serviceable
| GT09 | 2026-06-20 | 12293.89 | GESA | NOT SERVICEABLE - Combustor burn through HPT Burn trough holes/ heavy erosion | Inspection results are consistent with the previous failure report on Nov 2024 |  | GT09 | N/A | Unit suffered Hot Section Damage in Nov. Unit 4 and 9 were swaped |  |  |  | GT09 | 2024-12-31 | 12269 | PPGEnergy | Serviceable | 557-260
| GT10 | 2026-06-21 | 19731.01 | GESA | NOT SERVICEABLE - Combustor cracks/burn through HPT Burn trough holes/ Rubbing | Inspection results show a deterioration compared to previous inspection findings. Schedule a Hot Section replacement. |  | GT10 | 2025-08-14 | 16133 | SOM | Serviceable |  | GT10 | N/A | Explanation as to why it was not done has been requested to NFE
PSTP | GT01 | 2026-06-08 | 18954 | GESA | NOT SERVICEABLE - Combustor heavy burn through. HPT Numerous large holes | Inspection results are consistent with previous inspection findings. Perform Hot Section replacement ASAP | PSTP | GT01 | 2025-08-22 | 18733 | SOM | Not Serviceable | PSTP | GT01 | 2024-12-23 | 14391 | PPGEnergy | Not Serviceable
| GT02 | 2026-06-11 | 21343 | GESA | NOT SERVICEABLE - Dome burn through. HPT Erosion and missing material. LPT STG1 Damage | Cracks and erosion identified in previous report have progressed to a point where now a replacement of the Hot Section is needed |  | GT02 | 2025-08-05 | 16772 | SOM | Serviceable |  | GT02 | 2024-12-27 | 13074 | PPGEnergy | Serviceable
| GT03 | 2026-06-09 | 42842.97 | GESA | NOT SERVICEABLE - Combustor burns on inner liners HPT Damage, missing material | Hot Section especially the HPT has continued to deterioate further as seen in prevoius report. Hot Section needs to be replaced. |  | GT03 | 2025-08-21 | 40833 | SOM | Serviceable |  | GT03 | 2024-12-16 | 36823 | PPGEnergy | Not serviceable
| GT04 | 2026-06-10 | 43186.68 | GESA | NOT SERVICEABLE - VSV stuck. Broken vane arm -Combustor Burn through and chipping -HPT Burn trough holes and rubbing | Inspection results show clear deterioration compared to previous inspection findings. Replace Hot Section ASAP |  | GT04 | 2025-08-19 | 43186 | SOM | Serviceable |  | GT04 | 2024-12-20 | 40781 | PPGEnergy | Serviceable