## Status
SITE | Turbine Number | GG SERIAL Number | PT SERIAL Number | Model | Nameplate Rating ISO | Available Capacity MW | Current Status | Forcede Outage Date | Cause | Plan /Action Taken | Estimated Return to Service
Palo Seco | MP01 | 743315 | 80552 | PT8-3600 CW | 27 MW | 27 | Available |  |  | Although unit is available it is due for Hot Section inspection and Service | Send to Depot after Unit 3 returns. Probable return to service June 2027
| MP02 | 743313 | 80551 | PT8-3600 CW | 27 MW | 0 | Not Available | 2026-02-18 | High scavenge oil pressure Hot Section in need of repairs | REQ 363941 - For repairs at Mitsubishi Power Aero Repair Depot. Contract 111804 | Estimated return to service. 16 weeks after Unit is shipped out. Aprox Feb 2027 | Use Mayaguez 2A engine?
| MP03 | 743323 | 80560 | PT8-3600 CW | 27 MW | 0 | Not Available | 2026-08-16 | High scavenge oil pressure | Send to Mitsubishi Depot for repair. | Estimated return to service. 16 weeks after funds and contract is approved.

## Schedule
MobilePacs Service Schedule
Updated | 2026-09-09 | [7 empty] | 12500 |  | 50000
SITE | Turbine Number | GG SERIAL Number | PT SERIAL Number | Running Hours | Last Borescope Inspection | Next Borescope Inspection | Annual Inspection | Hot Section Inspection Hours | Next Hot Section 12500hrs | Next Hot Section Date | Mayor Inspection Depot | Comments
Palo Seco | MP01 | 743315 | 80552 | 12549.4 | 2026-02-11 | 2027-02-11 | 2027-02-11 | 0 | 12500 | 2026-09-02 18:18 | 2039-08-20 14:40 | Hot Section Inspection overdue
| MP02 | 743313 | 80551 | 11179.5 | 2026-02-13 | 2027-02-13 | 2027-02-13 | 0 | 12500 | 2027-02-22 17:31 | 2040-02-09 13:53 | To be sent to Depot
| MP03 | 743323 | 80560 | 11841.1 | 2026-02-15 | 2027-02-15 | 2027-02-15 | 0 | 12500 | 2026-12-01 04:40 | 2039-11-18 01:02 | To be sent to Depot
Run Factor | 0.33
Formulas:
Next Borescope Inspection = +[Last Borescope Inspection]+365
Next Hot Section Date = C2+(([Next Hot Section 12500hrs]-[Running Hours])/(24*C8))
Mayor Inspection Depot = C2+((M2-[Running Hours])/(24*C8))

## Hours
MobilePacs Service Schedule
Updated | 2026-09-09
SITE | Turbine Number | Total Starts | Cycles | Running Hours | Liquid Hours | Gas Hours
Palo Seco | MP01 | 1024 | 880 | 13885.8 | 12549.4 | 1336.1
| MP02 | 876 | 671 | 11215.1 | 11179.5 | 35.6
| MP03 | 983 | 773 | 12710.9 | 11841.1 | 869.9
Turbine Number | Project | GG S/N | PT S/N
MP01 | 1411 | 743315 | 80552
MP02 | 1410 | 743313 | 80551
MP03 | 1412 | 743323 | 80560