## Sheet1
Unit | Description | Out Date | In Date | Duration (Hrs) | Corrective Action
Palo Seco TM 2 | Fuel nozzles/vanes | 2025-08-04 | 2025-08-16 | 282.27 | Fuel nozzles in the combustion chamber were replaced and an axial wash was performed on the turbine. After the interventions, the operational stability of the unit was verified and the Temperature readings were normalized.
San Juan TM 1 | Miscellaneous plant auxiliary process and services instrumentation and controls | 2025-08-06 | 2025-08-07 | 15.85 | FCV-2001 (Gas Fuel Metering VLV) funtional tests were carried out, review and simulation at sensors were reviewed and simulated to the control loop, and the connections on the control cards were tightened.
San Juan TM 1 | Stator widings, bushings, and terminals | 2025-09-07 | 2025-09-07 | 4.6 | Wire harness replaced with spare harness.
Palo Seco TM 3 | Other exciter problems | 2025-09-09 | 2025-09-09 | 4.72 | Micronet was resetted, initiated the startup for the unit, and syncronized successfully.
Palo Seco TM 1 | Bearings | 2025-09-12 | 2025-09-13 | 1.72 | Inspection and cleaning of Magnetic Chip Detector D to determine bearing conditions.
San Juan TM 2 | Other miscellaneous balance of plant problems | 2025-09-17 | 2025-09-17 | 13.43 | Repairs on the lift pump, correcting the gas leak.
San Juan TM 7 | Other service water problems | 2025-09-21 | 2025-09-30 | 215.75 | The FCV-2019 was replaced and the driver was calibrated.
San Juan TM 1 | Switchyard or high voltage system problems | 2025-10-16 | 2025-10-31 | 356.9 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. The output cables were left disconnected in order to normalize the rest of the plant.
San Juan TM 2 | Switchyard or high voltage system problems | 2025-10-16 | 2025-10-17 | 38.08 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer.
San Juan TM 3 | Switchyard or high voltage system problems | 2025-10-16 | 2025-10-17 | 38.08 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer.
San Juan TM 5 | Switchyard or high voltage system problems | 2025-10-16 | 2025-10-17 | 38.08 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer.
San Juan TM 6 | Switchyard or high voltage system problems | 2025-10-16 | 2025-10-17 | 38.08 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer.
San Juan TM 7 | Switchyard or high voltage system problems | 2025-10-16 | 2025-10-17 | 38.08 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer.
San Juan TM 8 | Switchyard or high voltage system problems | 2025-10-16 | 2025-10-17 | 38.08 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer.
San Juan TM 10 | Switchyard or high voltage system problems | 2025-10-16 | 2025-10-17 | 38.08 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer.
San Juan TM 1 | Breaker on the Main Power Transformer opened, causing a trip to the rest of the units. | 2025-10-16 | 2025-10-31 | 368.83 | Unit was isolated and proceeded to close the breaker on the Main Power Transformer. GT-01 output cables were left disconnected in order to normalize the rest of the plant. Works are ongoing.
Palo Seco TM 3 | Service water pump failure | 2025-11-13 | 2025-11-13 | 2.53 | Replaced water injection pump.
San Juan TM 10 | Hydraulic oil system pumps | 2025-11-17 | 2025-11-18 | 16.22 | Replaced the hydraulics pumps.
San Juan TM 8 | Clogged Fuel nozzles/ vanes | 2025-11-23 | 2025-11-23 | 1.88 | Unclogged the fuel nozzles.
San Juan TM 7 | Clogged Fuel nozzles/ vanes | 2025-11-23 | 2025-11-24 | 12.33 | Unclogged the fuel nozzles.
Palo Seco TM 3 | High spread (Water Wash) | 2025-11-30 | 2025-11-30 | 3.35 | Gas turbine/compressor washing.
San Juan TM 1 | Breaker on the Main Power Transformer opened, causing a trip to the rest of the units. | 2025-12-01 | 2025-12-16 | 375.67 | Forced outage continuation from last month. Unit was isolated and proceeded to close the breaker on the Main Power Transformer. GT-01 output cables were left disconnected in order to normalize the rest of the plant.
Palo Seco TM 3 | T54 High Temperature spread | 2025-12-03 | 2025-12-31 | 677.88 | Pending new fuel nozzles. Still out of service.
San Juan TM 8 | T48 High temperature spread | 2025-12-03 | 2025-12-31 | 674.88 | Out of service.
San Juan TM 4 | CPU Card fail micronet | 2025-12-08 | 2025-12-16 | 201.5 | IP address input re-entered.
Palo Seco TM 2 | VSV Driver fault, cable E47 was disconnected from the servovalve | 2025-12-13 | 2025-12-13 | 2.58 | The cable was connected, everything was put back in place and the alarm resetted.
San Juan TM 10 | NOX Water Injection metering Valve demand and position FBK failing to operate | 2025-12-16 | 2025-12-17 | 18.99 | NOX Water injection replaced.
San Juan TM 2 | Lubrication oil supply pressure | 2025-12-19 | 2025-12-19 | 1 | Replacement of TLO supply and SCAVENGE filters.
San Juan TM 2 | Generator Lube oil supply pressure | 2025-12-23 | 2025-12-23 | 2.26 | Replaced cable.
San Juan TM 2 | Generator Lube oil supply pressure | 2025-12-28 | 2025-12-28 | 1 | Replaced the relay.
San Juan TM 10 | Lube oil system general issue. | 2025-12-30 | 2025-12-30 | 4.28 | Lube oil system was cleaned.
San Juan TM 7 | Issue with the water injection pump. | 2026-01-13 | 2026-01-14 | 15.49 | The water injection pump was replaced.
San Juan TM 2 | Lube oil system problems. | 2026-01-18 | 2026-01-18 | 2.05 | Replaced N47 relay switch.
San Juan TM 1 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-31 | 193.17 | Work in progress.
San Juan TM 2 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-27 | 114.35 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit.
San Juan TM 3 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-27 | 114.35 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit.
San Juan TM 4 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-26 | 91.53 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit.
San Juan TM 5 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-24 | 44.02 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit.
San Juan TM 6 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-24 | 44.02 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit.
San Juan TM 7 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-24 | 44.02 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit.
San Juan TM 10 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-24 | 44.02 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit.
San Juan TM 5 | Gas leak on manifold, J-tubes and convoluted hoses. | 2026-01-23 | 2026-01-29 | 126.12 | Replaced gas manifold, J-tubes and convoluted hoses.
San Juan TM 2 | Lube oli system problems | 2026-03-02 | 2026-03-02 | 0.42 | Verified generator oil levels and the connection to the oil level transmitter.
San Juan TM 2 | Lube oli system problems | 2026-03-04 | 2026-03-04 | 12.22 | Verified generator oil levels and the connection to the oil level transmitter.
San Juan TM 2 | Lube oli system problems | 2026-03-07 | 2026-03-07 | 0.45 | Verified generator oil levels and the connection to the oil level transmitter.
San Juan TM 2 | Lube oli system problems | 2026-03-17 | 2026-03-17 | 0.32 | Verified generator oil levels and the connection to the oil level transmitter.
San Juan TM 2 | Lube oli system problems | 2026-03-19 | 2026-03-19 | 1.5 | Verified generator oil levels and the connection to the oil level transmitter.
San Juan TM 2 | Lube oli system problems | 2026-03-20 | 2026-03-20 | 1.33 | Verified generator oil levels and the connection to the oil level transmitter.
San Juan TM 6 | NPT Hi Speed Derivative. | 2026-03-21 | 2026-03-21 | 0.58 | Replaced acelerometer
San Juan TM 2 | Blackstart Diesel Fuel Pump Failure. | 2026-03-21 | 2026-03-26 | 116.72 | Removed diesel fuel pump, none available in stock. A 480v external feeder was rerouted from GT-05 Switchgear to energize auxiliary equipments.
San Juan TM 3 | Blackstart Diesel Fuel Pump Failure. | 2026-03-21 | 2026-03-26 | 116.72 | Removed diesel fuel pump, none available in stock. A 480v external feeder was rerouted from GT-05 Switchgear to energize auxiliary equipments.
San Juan TM 4 | Liquid fuel primary manifold thermocouple failure | 2026-03-25 | 2026-03-25 | 0.37 | Replaced thermocouple on primary manifold liquid fuel system.
San Juan TM 2 | Lube oli system problems | 2026-03-31 | 2026-03-31 | 0.62 | Verified generator oil levels and the connection to the oil level transmitter.
San Juan TM 2 | Node fault. | 2026-04-02 | 2026-04-02 | 1.35 | System cleaned.
San Juan TM 7 | Undiagnostic trip. | 2026-04-02 | 2026-04-02 | 3.52 | Unit restarted.
Palo Seco TM 2 | Loss of 480V. | 2026-04-17 | 2026-04-18 | 5.65 | Repairs completed.
San Juan TM 2 | Node fault. | 2026-04-28 | 2026-04-30 | 53.48 | System cleaned.
San Juan TM 2 | Node fault. | 2026-04-28 | 2026-04-28 | 0.73 | System cleaned.
Palo Seco TM 2 | VSV Driver failure. | 2026-04-29 | 2026-04-30 | 14.2 | VSV Pumps replaced.
San Juan TM 2 | Node n-1 issues. | 2026-05-01 | 2026-05-04 | 72.5 | System cleaned and reset.
San Juan TM 2 | Node n-1 issues. | 2026-05-04 | 2026-05-06 | 43.83 | System cleaned and reset.
San Juan TM 2 | Node n-1 issues. | 2026-05-08 | 2026-05-12 | 86.47 | System cleaned and reset.
San Juan TM 2 | Node n-1 issues. | 2026-05-12 | 2026-05-14 | 47.03 | System cleaned and reset.
San Juan TM 2 | Node n-1 issues. | 2026-05-15 | 2026-05-21 | 146.55 | System cleaned and reset.
San Juan TM 10 | Lost of mega vars controls. | 2026-05-19 | 2026-05-19 | 2.62 | Inspected and reset.
San Juan TM 10 | N1n5 node fault. | 2026-05-23 | 2026-05-23 | 3.48 | Cleaned and reset.
San Juan TM 10 | Breaker issue. | 2026-05-25 | 2026-05-26 | 27.98 | Breaker repaired.
San Juan TM 5 | Main breaker failure. | 2026-05-25 | 2026-05-25 | 2.1 | Breaker fixed.
San Juan TM 3 | Main breaker failure. | 2026-05-25 | 2026-05-25 | 2.1 | Breaker fixed.
San Juan TM 7 | Main breaker failure. | 2026-05-25 | 2026-05-25 | 2.1 | Breaker fixed.
San Juan TM 2 | Node n-1 issues. | 2026-05-28 | 2026-05-31 | 79.48 | System cleaned and reset.
San Juan TM 2 | Node n-1 issues. | 2026-05-28 | 2026-05-28 | 0.83 | System cleaned and reset.
San Juan TM 6 | Synchronizer fail. | 2026-06-02 | 2026-06-02 | 0.83 | Synchonizer fixed.
San Juan TM 2 | Node n-1 issues. | 2026-06-04 | 2026-06-09 | 120.55 | System inspected and reset.
San Juan TM 7 | High temperature spread. | 2026-06-22 | 2026-06-23 | 17.08 | Technician replaced bolts.
San Juan TM 10 | Instrumentation fail. | 2026-06-23 | 2026-06-23 | 0.32 | System inspected and reset.
San Juan TM 5 | Swap out broken Water injection pump. | 2026-07-11 | 2026-07-11 | 10.08 | Water injection pump swapped and operated successfully.
San Juan TM 10 | High blade path spread. | 2026-07-12 | 2026-07-13 | 19.57 | Clogged fuel nozzles.
San Juan TM 10 | High blade path spread. | 2026-07-13 | 2026-07-15 | 44.78 | Fuel nozzles replaced.
San Juan TM 7 | Loose gas lines causing leak. | 2026-07-14 | 2026-07-14 | 1.32 | Lines were tightened.
San Juan TM 4 | Unit tripped due to a undiagnosed issue. | 2026-07-17 | 2026-07-17 | 0.12 | Unit was inspected and greenlit for return to service.
San Juan TM 7 | Primary diesel skid tripped and left unit without fuel. | 2026-07-21 | 2026-07-21 | 0.13 | Pumps inspected and reset.
San Juan TM 4 | Diesel skid trip and tripped the unit off. | 2026-07-22 | 2026-07-22 | 0.35 | System reset.
San Juan TM 7 | Diesel skid tripped and left unit without fuel. | 2026-07-22 | 2026-07-22 | 0.25 | Pumps inspected and reset.
San Juan TM 7 | High Lower Explosion Limit (LEL) detected in Enclosure. Unit was removed from service. | 2026-07-23 | 2026-07-24 | 3.77 | Lines were tightened.
San Juan TM 7 | High Lower Explosion Limit (LEL) detected in Enclosure. Unit was removed from service. | 2026-07-24 | 2026-07-25 | 23.32 | Lines were replaced.
Palo Seco TM 2 | Operating Procedure error involving auxiliary transformers. Tripped unit from loss of power. | 2026-07-31 | 2026-07-31 | 3.53 | Unit inspected and reset back to service.
San Juan TM 2 | Faulty reading on Glo supply sensor. | 2026-08-05 | 2026-08-05 | 1.95 | Connections were cleaned and tested.
San Juan TM 10 | VSV driver fault. | 2026-08-05 | 2026-08-05 | 2.73 | Inspected and reset.
San Juan TM 10 | VSV driver fault. | 2026-08-05 | 2026-08-06 | 15.85 | Servo valve replacement for VSV.
Palo Seco TM 2 | Loss of Transformer for the unit. | 2026-08-06 | 2026-08-31 | 615.1 | Pending.
San Juan TM 2 | Faulty reading on turbine fuel supply sensor. | 2026-08-06 | 2026-08-06 | 3.98 | Sensor connections cleaned and tested.
San Juan TM 2 | Trip enclosure Damper B closed. | 2026-08-08 | 2026-08-08 | 5.68 | Systems inspected and reset.
San Juan TM 2 | Trip enclosure Damper B closed. | 2026-08-09 | 2026-08-09 | 3.3 | Systems inspected and reset.
San Juan TM 2 | Node connection issues. | 2026-08-10 | 2026-08-11 | 13.47 | Grounds and connections cleaned and tested.
San Juan TM 2 | Node N1 trip. | 2026-08-10 | 2026-08-10 | 5.12 | Connections cleaned and tested.
San Juan TM 4 | Water injection pump failed. | 2026-08-10 | 2026-08-10 | 2.13 | Returned to service without Water Injection until replacement available.
San Juan TM 5 | Water injection pump trip. | 2026-08-10 | 2026-08-10 | 2.28 | Returned to service without Water Injection until replacement available.
San Juan TM 2 | Node connection issues. | 2026-08-11 | 2026-08-12 | 20.58 | Connection cleaned and tested.
San Juan TM 2 | Faulty sensor reading for oil level. | 2026-08-12 | 2026-08-12 | 3.77 | Bypassed sensor readings.
San Juan TM 10 | Hydraulic pump shaft broken, gas generator couldn't reach correct speed, stuck at 1900 RPM. | 2026-08-15 | 2026-08-17 | 50.7 | Hydraulic pump, Gearbox and clutch were swapped.
San Juan TM 2 | Auxiliary Transformer connection opened. | 2026-08-23 | 2026-08-24 | 37.97 | Lightning rod and Breakers serviced.
San Juan TM 3 | Auxiliary Transformer connection opened. | 2026-08-23 | 2026-08-24 | 37.97 | Lightning rod and Breakers serviced.
San Juan TM 4 | Auxiliary Transformer connection opened. | 2026-08-23 | 2026-08-24 | 37.97 | Lightning rod and Breakers serviced.
San Juan TM 5 | Auxiliary Transformer connection opened. | 2026-08-23 | 2026-08-24 | 37.97 | Lightning rod and Breakers serviced.
San Juan TM 6 | Auxiliary Transformer connection opened. | 2026-08-23 | 2026-08-24 | 37.97 | Lightning rod and Breakers serviced.
San Juan TM 7 | Auxiliary Transformer connection opened. | 2026-08-23 | 2026-08-24 | 37.97 | Lightning rod and Breakers serviced.
San Juan TM 10 | Auxiliary Transformer connection opened. | 2026-08-23 | 2026-08-24 | 37.97 | Lightning rod and Breakers serviced.
San Juan TM 3 | Trip due to Compressor sensor PT-8004 PS3. | 2026-08-27 | 2026-08-29 | 44.82 | Sensor was cleaned and calibrated, Breaker to hydraulic pump serviced, Hydraulic pump swapped.
San Juan TM 2 | Loss of fuel supplier pressure. Hydraulic crank pump broke shaft. | 2026-08-28 | 2026-08-28 | 11 | Hydraulic pump swapped out.