## Outages 24h or more
Q4 FY2026 Forced Outages of 24 Hours or More: Effect of Parts Availability on Event Duration
PREB Resolution and Order of September 18, 2026 (NEPR-MI-2021-0014), Item 5: "A revised version of Attachment 5 that, for every failure or outage event, identifies [...] whether the duration of the event was affected by the availability or unavailability of Consumables, Spare Parts, and Capital Spare Parts."
From Exhibit 3 (revised Attachment 5, filed October 8, 2026) | [9 empty] | Effect of parts availability
Plant | Unit | Month | Cause (as reported) | Out | In | Duration (hrs) | Duration (days) | Corrective action (as reported) | Note | Was a Consumable, Spare Part or Capital Spare Part needed to return the unit to service? | Type of part | Part or component | Was the part available in inventory when needed? | Was the duration of the event affected by the availability or unavailability of the part? | Explanation (required if column O is "Yes")
Aguirre | Aguirre CC 2-1 | June 2026 | Unit trip with output bars explore. | 2026-06-13 08:42 | 2026-06-18 20:28 | 131.8 | 5.4917 | Completed, the output bars were removed, the insulation was changed and bars were cleaned. A test was perfomed on the transformer. | Affected Aguirre CC 2-2 and 2-4 | Yes | Consumable | Insulation | Yes | No | N/A
Aguirre | Aguirre CC 2-2 | June 2026 | Unit trip when U2-1 output bars explode. Lockout generator. | 2026-06-13 08:42 | 2026-06-14 18:36 | 33.9 | 1.4125 | The U2-1 output bars were disconnected to isolate the fault. | Caused by Aguirre CC 2-1 | No | N/A | N/A | N/A | No | N/A
Aguirre | Aguirre CC 2-2 | June 2026 | Unit trips when it syncs U2-1 for generator lockkout and relay 64G-2. Only one unit can be in service, going out through MPT 2-1/2-2. | 2026-06-18 20:58 | 2026-06-24 16:49 | 139.9 | 5.8292 | After the U2-1 exciter explosion, it disconnected from the transformer and the relays of the U2-2 generator were calibrated. | Caused by Aguirre CC 2-1 | No | N/A | N/A | N/A | No | N/A
Cambalache | Cambalache 2 | June 2026 | Unavailability of the turbine's CO2 fire protection system. For safety reasons, the unit cannot operate without a fire protection system. | 2026-06-18 09:55 | 2026-06-26 16:32 | 198.61 | 8.2754 | Repair on compressor and filling of the CO2 tank of the turbine fire protection system. | Same event: Cambalache 3 | Yes | Capital Spare Part | CO2 system Unit Compressor | No | Yes | The event's duration was due to the wait for the compressor repair and the CO2 delivery.
Cambalache | Cambalache 3 | June 2026 | Unavailability of the turbine's CO2 fire protection system. For safety reasons, the unit cannot operate without a fire protection system. | 2026-06-18 09:55 | 2026-06-26 16:32 | 198.61 | 8.2754 | Repair on compressor and filling of the CO2 tank of the turbine fire protection system. | Same event: Cambalache 2 | Yes | Capital Spare Part | CO2 system Unit Compressor | No | Yes | The event's duration was due to the wait for the compressor repair and the CO2 delivery.
Costa Sur | Costa Sur 5 | April 2026 | Platen superheater issue. | 2026-04-11 00:36 | 2026-04-15 00:30 | 95.89 | 3.9954 | Boiler repaired, hydrostatic performed and unit synchronized. |  | Yes | Consumable | Boiler tubes | Yes | No | N/A
Costa Sur | Costa Sur 5 | May 2026 | MKVI activated the prot trip. | 2026-05-25 21:55 | 2026-05-28 13:03 | 63.13 | 2.6304 | Checked the internal and termination wiring, also the circuit for the MKVI cabinet and proceeded with the synchronization of the unit. |  | No | N/A | N/A | N/A | No | N/A
Costa Sur | Costa Sur 6 | April 2026 | Main stop valves issue. | 2026-04-20 16:42 | 2026-05-01 | 247.3 | 10.3042 | Pending repair of main steam inlet valves to the turbine. | Recorded through the end of the month. | Yes | Spare Part | Valves | Yes | No | N/A
Daguao | Daguao 1-1 | April 2026 | Circuit breaker 0010 opened. | 2026-04-18 02:00 | 2026-04-19 15:48 | 37.8 | 1.575 | Luma staff reset breaker and closed it. | Same event: Daguao 1-2 | No | N/A | N/A | N/A | No | N/A
Daguao | Daguao 1-1 | April 2026 | Ground fault main power transformer. Water ingress in connection box. | 2026-04-22 12:40 | 2026-04-24 17:49 | 53.15 | 2.2146 | Cleaned, painted and replaced lid gasket preventive maintenace was performed. | Same event: Daguao 1-2 | Yes | Consumable | Gasket | Yes | No | N/A
Daguao | Daguao 1-2 | April 2026 | Circuit breaker 0010 opened. | 2026-04-18 02:00 | 2026-04-19 15:48 | 37.8 | 1.575 | Luma staff reset breaker and closed. | Same event: Daguao 1-1 | No | N/A | N/A | N/A | No | N/A
Daguao | Daguao 1-2 | April 2026 | Ground fault main power transformer. Water ingress in connection box. | 2026-04-22 12:40 | 2026-04-24 17:49 | 53.15 | 2.2146 | Cleaning, Painting and replaced cover gasket. | Same event: Daguao 1-1 | Yes | Consumable | Gasket | Yes | No | N/A
Daguao | Daguao 1-2 | June 2026 | High exhaust temperature spread. | 2026-06-11 17:05 | 2026-06-14 16:36 | 71.52 | 2.98 | The nozzles were replaced with new nozzles. |  | Yes | Spare Part | Fuel Nozzle | Yes | No | N/A
Jobos | Jobos 1-2 | June 2026 | The turbine does not slow down enought to start. | 2026-06-07 18:47 | 2026-06-09 16:25 | 45.63 | 1.9013 | Valve replacement 20 TU. |  | Yes | Spare Part | Solenoid Valve 20TU | Yes | No | N/A
Mayaguez | Mayaguez 2A | April 2026 | Unit trip due a erratic pressure differential in a scavange line. | 2026-04-28 19:23 | 2026-04-30 | 52.62 | 2.1925 | Unit 2A was disengaged in order to have online 2B. | Same event: Mayaguez 2B. Recorded through the end of the month. | No | N/A | N/A | N/A | No | N/A
Mayaguez | Mayaguez 2B | April 2026 | Because Unit 2A PT621 trip. Unit 2B can’t be online due to a high oil leak on 2A. | 2026-04-28 19:37 | 2026-04-30 | 24.1 | 1.0042 | Unit 2A decoupled to keep Unit 2B available. | Caused by Mayaguez 2A | No | N/A | N/A | N/A | No | N/A
Mayaguez | Mayaguez 3A | May 2026 | Uni 3B was being aligned, therefore unit 3A was unavailable. | 2026-05-15 08:36 | 2026-05-16 17:01 | 32.42 | 1.3508 | Alignment completed. | Caused by Mayaguez 3B | No | N/A | N/A | N/A | No | N/A
Mayaguez | Mayaguez 3B | May 2026 | Unit 3B PB DOT trip. A boroscope was performed. Also pressure transmitters were high. Those are related with the scavange. | 2026-05-18 20:19 | 2026-05-29 18:27 | 262.13 | 10.9221 | A boroscope was performed. Pressure Transmitters were calibrated, solenoid valve were replaced. |  | No | N/A | N/A | N/A | No | N/A
Mayaguez | Mayaguez 4A | April 2026 | The unit exhibited a back pressure issue. This is typically caused by the fuel injection system, water injection system, or bleed valves that may or may not have opened at a specific point in time. A trendline analysis was performed to graphically identify the problem, and no discrepancies were found. | 2026-04-11 19:58 | 2026-04-30 | 460.03 | 19.1679 | The data was sent to Mitsubishi. They instructed to calibrate the pressure transmitters and temperature sensors (TE). The process was been completed, and we are pending approval from Mitsubishi. Also, a boroscope inspection was made. | Affected Mayaguez 4B. Recorded through the end of the month. | No | N/A | N/A | N/A | No | N/A
Mayaguez | Mayaguez 4B | April 2026 | Unit trip due to a no light. | 2026-04-06 17:01 | 2026-04-07 17:07 | 24.1 | 1.0042 | A replacement of the igniters was made. |  | Yes | Spare Part | Igniter | Yes | No | N/A
Palo Seco | Palo Seco 1-2 | April 2026 | Fuel line leak. | 2026-04-28 15:17 | 2026-04-29 17:43 | 26.43 | 1.1013 | Fuel line replaced. |  | No | N/A | N/A | N/A | No | N/A
Palo Seco | Palo Seco 1-2 | June 2026 | Igniter issues. | 2026-06-25 17:00 | 2026-06-27 10:56 | 41.93 | 1.7471 | Reset igniter. |  | No | N/A | N/A | N/A | No | N/A
Palo Seco | Palo Seco 1-2 | June 2026 | Igniter issues. | 2026-06-28 18:15 | 2026-06-29 20:00 | 25.75 | 1.0729 | Reset igniter. |  | No | N/A | N/A | N/A | No | N/A
Palo Seco | Palo Seco 1-2 | June 2026 | Fuel leak. | 2026-06-29 20:52 | 2026-07-01 | 27.12 | 1.13 | Corrected. | Recorded through the end of the month. | No | N/A | N/A | N/A | No | N/A
Palo Seco | Palo Seco 3 | May 2026 | Broken Boiler. | 2026-05-21 13:08 | 2026-05-31 23:59 | 250.85 | 10.4521 | Corrected. | Recorded through the end of the month. | Yes | Spare Part | Pressure Part | Yes | No | N/A
Palo Seco | Palo Seco 3 | June 2026 | Broken Boiler. | 2026-06-01 22:21 | 2026-06-04 11:56 | 61.58 | 2.5658 | Leaks corrected. |  | Yes | Spare Part | Pressure Part | Yes | No | N/A
Palo Seco | Palo Seco 4 | April 2026 | Boiler lead leak. | 2026-04-09 21:40 | 2026-04-10 22:41 | 25.02 | 1.0425 | The leak was corrected in the Boiler lead. |  | Yes | Consumable | Packing | Yes | No | N/A
Palo Seco | Palo Seco 4 | April 2026 | Broken Boiler lines. | 2026-04-16 00:14 | 2026-04-20 08:31 | 104.28 | 4.345 | Lines were fixed. |  | Yes | Spare Part | Pressure Part | Yes | No | N/A
Palo Seco | Palo Seco 4 | April 2026 | Broken Boiler lines. | 2026-04-27 19:51 | 2026-05-01 | 76.13 | 3.1721 | Lines were fixed. | Recorded through the end of the month. | Yes | Spare Part | Pressure Part | Yes | No | N/A
Palo Seco | Palo Seco 4 | May 2026 | Broken Boiler. | 2026-05-10 20:08 | 2026-05-13 12:45 | 64.62 | 2.6925 | Corrected. |  | Yes | Spare Part | Pressure Part | Yes | No | N/A
Palo Seco | Palo Seco MP 3 | April 2026 | Combustor replacement needed. | 2026-04-06 12:22 | 2026-04-24 20:17 | 439.92 | 18.33 | Replacement completed. |  | Yes | Spare Part | Combustor | Yes | No | N/A
San Juan | San Juan 9 | May 2026 | Electrical failure on Boiler Feed Pump 9-2. | 2026-05-23 15:20 | 2026-05-25 16:25 | 49.08 | 2.045 | Checked connections on Boiler Feed Pump 9-2 and certified a burned motor. |  | Yes | Spare Part | Electrical Motor | Yes | No | N/A
San Juan | San Juan 9 | June 2026 | Fire on burner corner C. | 2026-06-17 04:40 | 2026-07-01 | 331.33 | 13.8054 | Repairs in progress. | Recorded through the end of the month. | Yes | Capital Spare Part | Burners | Yes | No | N/A