## FY2026 Events
Fiscal Year 2026 Forced Outage Events Classified by System
Quarter | Month | Unit | Description (as reported) | Date Out | Date In | Duration (Hrs) | Corrective Action (as reported) | System | Component | Related Units / Note | Counted
Q1 | July 2025 | Costa Sur 5 | Platen superheater | 2025-07-04 | 2025-07-08 | 115.25 | Damaged boiler tubes were repaired. | Boiler pressure parts | Platen superheater tubes |  | Yes
Q1 | July 2025 | San Juan CT 6 | Other combustor problems | 2025-07-09 | 2025-07-10 | 40.1 | Fault was corrected and unit reincorporated into the system. | Gas turbine combustion, compressor and hot section | Combustor |  | Yes
Q1 | July 2025 | Aguirre 2 | Main transformer | 2025-07-11 | 2025-07-17 | 152.48 | Braids and cables were replaced where the parasitic currents land on the ground. | Electrical (breakers, transformers, DC and auxiliary power) | Main transformer grounding |  | Yes
Q1 | July 2025 | San Juan CT 6 | Other exciter problems | 2025-07-11 | 2025-07-11 | 4 | Fault was corrected and unit reincorporated into the system. | Generator, excitation and output bus | Exciter |  | Yes
Q1 | July 2025 | Cambalache 2 | Gas Turbine Control System - internal and termination wiring | 2025-07-12 | 2025-07-12 | 5.87 | Cabling and connectors were repaired. Threadlocker was applied to the threads of the speed sensor connectors. | Controls, instrumentation and protection | Control system wiring |  | Yes
Q1 | July 2025 | San Juan CT 6 | Boiler Water Condition | 2025-07-17 | 2025-07-19 | 29.2 | Fault was corrected and unit delivered to the TOC available. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Boiler water condition |  | Yes
Q1 | July 2025 | Palo Seco 3 | Burners | 2025-07-21 | 2025-07-21 | 4.67 | Burners were cleaned and put back on service. | Burners and firing | Burners |  | Yes
Q1 | July 2025 | Aguirre CC 1-2 | Other exhaust problems | 2025-07-22 | 2025-07-22 | 1.2 | Spread programming was changed to original, recommended by General Electric. | Controls, instrumentation and protection | Exhaust temperature spread (control programming) | Same cause: Aguirre CC 2-4 | Yes
Q1 | July 2025 | Aguirre CC 2-4 | Other exhaust problems | 2025-07-22 | 2025-07-22 | 1.9 | Spread programming was changed to original, recommended by General Electric. | Controls, instrumentation and protection | Exhaust temperature spread (control programming) | Same cause: Aguirre CC 1-2 | Yes
Q1 | July 2025 | San Juan 9 | Instrument Air compressors | 2025-07-24 | 2025-07-25 | 5.1 | Fault in the instrument was corrected and unit reincorporated into the system. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Instrument air compressors |  | Yes
Q1 | July 2025 | San Juan CT 6 | Other exciter problems | 2025-07-24 | 2025-07-24 | 9.3 | Fault was corrected and unit reincorporated into the system. | Generator, excitation and output bus | Exciter |  | Yes
Q1 | July 2025 | San Juan CT 6 | Other exciter problems | 2025-07-24 | 2025-07-24 | 1.3 | Fault was corrected and unit reincorporated into the system. | Generator, excitation and output bus | Exciter |  | Yes
Q1 | July 2025 | San Juan CT 6 | Other exciter problems | 2025-07-25 | 2025-07-25 | 10.7 | Fault was corrected and unit reincorporated into the system. | Generator, excitation and output bus | Exciter |  | Yes
Q1 | July 2025 | San Juan CT 6 | Other exciter problems | 2025-07-26 | 2025-07-26 | 9.1 | Fault was corrected and unit reincorporated into the system. | Generator, excitation and output bus | Exciter |  | Yes
Q1 | July 2025 | San Juan 9 | Waterwall (Furnace wall) | 2025-07-27 | 2025-07-28 | 24.23 | Fault in the valve was corrected and unit reincorporated into the system. | Boiler pressure parts | Waterwall |  | Yes
Q1 | July 2025 | San Juan 9 | Other main steam system problems | 2025-07-28 | 2025-07-28 | 1.33 | Fault was corrected and unit reincorporated into the system. | Steam and turbine valves | Main steam system |  | Yes
Q1 | July 2025 | San Juan CT 6 | Boiler Water Condition | 2025-07-28 | 2025-07-29 | 30.2 | Fault was corrected and unit reincorporated into the system. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Boiler water condition |  | Yes
Q1 | August 2025 | Aguirre CC 2-1 | Other 400-700 volt problems | 2025-08-01 | 2025-08-01 | 1.5 | The megger was applied to the large equipment, the breaker was left off and the power was normalized. The unit was synchronized due to system needs. | Electrical (breakers, transformers, DC and auxiliary power) | 480 V bars and breaker |  | Yes
Q1 | August 2025 | Costa Sur 6 | Air heater fouling (regenerative) | 2025-08-01 | 2025-08-03 | 70.35 | Cleaning of air heater baskets was performed. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Air heater fouling |  | Yes
Q1 | August 2025 | Aguirre CC 1-1 | Vibration of the turbine generator unit | 2025-08-02 | 2025-08-02 | 2.7 | Vibrations sensor of Bearing 2 was changed. | Controls, instrumentation and protection | Bearing 2 vibration sensor |  | Yes
Q1 | August 2025 | Aguirre CC 2-2 | Fuel piping and valves | 2025-08-03 | 2025-08-04 | 28.9 | The affected section was changed. | Fuel system | Fuel piping and valves |  | Yes
Q1 | August 2025 | Aguirre CC 2-2 | Fuel filters | 2025-08-04 | 2025-08-04 | 2.7 | Fuel line was welded. | Fuel system | Fuel filters (line welded) |  | Yes
Q1 | August 2025 | Aguirre CC 2-2 | Fuel filters | 2025-08-04 | 2025-08-04 | 2.1 | Tubes were welded. | Fuel system | Fuel filters (tubes welded) |  | Yes
Q1 | August 2025 | Costa Sur 6 | Other main steam valves | 2025-08-04 | 2025-08-05 | 27.1 | The breakage was repaired and valve replaced. | Steam and turbine valves | Main steam valve |  | Yes
Q1 | August 2025 | Palo Seco TM 2 | Fuel nozzles/vanes | 2025-08-04 | 2025-08-16 | 282.27 | Fuel nozzles in the combustion chamber were replaced and an axial wash was performed on the turbine. After the interventions, the operational stability of the unit was verified and the Temperature readings were normalized. | Fuel system | Fuel nozzles |  | Yes
Q1 | August 2025 | Aguirre CC 2-1 | Other 400-700 volt problems | 2025-08-06 | 2025-08-06 | 13.7 | Bars and breaker in unit 2-1 and 2-2 were changed. | Electrical (breakers, transformers, DC and auxiliary power) | 480 V bars and breaker |  | Yes
Q1 | August 2025 | San Juan TM 1 | Miscellaneous plant auxiliary process and services instrumentation and controls | 2025-08-06 | 2025-08-07 | 15.85 | FCV-2001 (Gas Fuel Metering VLV) funtional tests were carried out, review and simulation at sensors were reviewed and simulated to the control loop, and the connections on the control cards were tightened. | Fuel system | Gas fuel metering valve |  | Yes
Q1 | August 2025 | Aguirre 2 | Economizer piping | 2025-08-08 | 2025-08-12 | 92.81 | Repaired economizer recirculation line. | Boiler pressure parts | Economizer piping |  | Yes
Q1 | August 2025 | San Juan CT 6 | Other fire protection system problems | 2025-08-14 | 2025-08-25 | 268.3 | Failure in fire protection system was corrected and unit reincorporated to the electrical system. | Fire protection | Fire protection |  | Yes
Q1 | August 2025 | Aguirre 2 | Main transformer | 2025-08-15 | 2025-08-15 | 9.73 | The cables that land on the ground were changed and connected to another part of the mesh. | Electrical (breakers, transformers, DC and auxiliary power) | Main transformer grounding |  | Yes
Q1 | August 2025 | San Juan ST 5 | Control valves | 2025-08-20 | 2025-08-20 | 6.1 | Failure in control valve was corrected and unit reincorporated to the electrical system. | Steam and turbine valves | Control valve |  | Yes
Q1 | August 2025 | Aguirre 2 | Burner management system | 2025-08-21 | 2025-08-21 | 3.48 | The main fuse of the Burner Management System was changed. | Controls, instrumentation and protection | Burner management system fuse |  | Yes
Q1 | August 2025 | San Juan CT 6 | Inspection | 2025-08-26 | 2025-08-28 | 41.9 | Bearing inspection requested by contrator. Failure was corrected and unit reincorporated to the electrical system. | Turbine bearings, gears and vibration | Bearing inspection |  | Yes
Q1 | August 2025 | Mayaguez 3A | DC instrument power battery chargers | 2025-08-28 | 2025-08-30 | 37.75 | The dead battery was replaced. | Electrical (breakers, transformers, DC and auxiliary power) | DC battery |  | Yes
Q1 | August 2025 | San Juan CT 6 | Inspection | 2025-08-28 | 2025-08-31 | 73.1 | Bearing inspection requested by contrator in progress. | Turbine bearings, gears and vibration | Bearing inspection | Continuation of the August 26 event | No
Q1 | August 2025 | Aguirre 2 | Desuperheaters / Attemperators | 2025-08-31 | 2025-08-31 | 8.48 | High pressure heater purchase in process. | Boiler pressure parts | Desuperheaters / attemperators |  | Yes
Q1 | September 2025 | Palo Seco 3 | 400-700 volt protection devices | 2025-09-01 | 2025-09-01 | 8.85 | Electrical work on bar 480V. | Electrical (breakers, transformers, DC and auxiliary power) | 480 V protection devices |  | Yes
Q1 | September 2025 | San Juan TM 1 | Stator widings, bushings, and terminals | 2025-09-07 | 2025-09-07 | 4.6 | Wire harness replaced with spare harness. | Generator, excitation and output bus | Generator wire harness |  | Yes
Q1 | September 2025 | Palo Seco 3 | Other exciter problems | 2025-09-09 | 2025-09-09 | 6.63 | Corrections done on relays of ground field and press release. | Generator, excitation and output bus | Exciter (ground field relays) |  | Yes
Q1 | September 2025 | Palo Seco TM 3 | Other exciter problems | 2025-09-09 | 2025-09-09 | 4.72 | Micronet was resetted, initiated the startup for the unit, and syncronized successfully. | Controls, instrumentation and protection | Control system (Micronet) |  | Yes
Q1 | September 2025 | San Juan CT 5 | Other fire protection system problems | 2025-09-11 | 2025-09-12 | 18.7 | Correction on fire protection system. | Fire protection | Fire protection | Affected San Juan ST 5 | Yes
Q1 | September 2025 | San Juan ST 5 | Other fire protection system problems | 2025-09-11 | 2025-09-12 | 21.2 | Correction on fire protection system. | Event at another unit (companion or shared equipment) | Trip of combustion turbine 5 (fire protection) | Caused by San Juan CT 5 | No
Q1 | September 2025 | Palo Seco 1-2 | Hydraulic oil system piping/valves | 2025-09-12 | 2025-09-12 | 2.8 | The valve was replaced and the unit was synchronized. Unit online and available. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Hydraulic oil valve |  | Yes
Q1 | September 2025 | Palo Seco TM 1 | Bearings | 2025-09-12 | 2025-09-13 | 1.72 | Inspection and cleaning of Magnetic Chip Detector D to determine bearing conditions. | Turbine bearings, gears and vibration | Bearing (chip detector) |  | Yes
Q1 | September 2025 | Palo Seco 4 | Major overhaul | 2025-09-17 | 2025-09-26 | 231.12 | Leak corrected. | Generator, excitation and output bus | Generator (leak) |  | Yes
Q1 | September 2025 | San Juan TM 2 | Other miscellaneous balance of plant problems | 2025-09-17 | 2025-09-17 | 13.43 | Repairs on the lift pump, correcting the gas leak. | Fuel system | Lift pump gas leak |  | Yes
Q1 | September 2025 | San Juan TM 7 | Other service water problems | 2025-09-21 | 2025-09-30 | 215.75 | The FCV-2019 was replaced and the driver was calibrated. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Service water valve FCV-2019 |  | Yes
Q1 | September 2025 | Mayaguez 4B | Thrust bearings | 2025-09-23 | 2025-09-23 | 1.38 | Power Turbine Thrust bearing balance was calibrated. | Turbine bearings, gears and vibration | Power turbine thrust bearing balance |  | Yes
Q1 | September 2025 | San Juan 9 | Induced draft fans | 2025-09-23 | 2025-09-27 | 97 | Work completed on bearing induced draft fan (IDF) to fix vibrations. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Induced draft fan |  | Yes
Q1 | September 2025 | Costa Sur 6 | Boiler recirculation pumps - motors | 2025-09-26 | 2025-09-28 | 44.27 | Boiler pump motor was replaced and unit synchronized. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Boiler recirculation pump motor |  | Yes
Q1 | September 2025 | Mayaguez 4B | Thrust bearings | 2025-09-26 | 2025-09-26 | 1.87 | All sensors of the Power Turbine Thrust bearing balance were calibrated. | Turbine bearings, gears and vibration | Power turbine thrust bearing balance |  | Yes
Q1 | September 2025 | Costa Sur 6 | Other boiler recirculation problems | 2025-09-28 | 2025-09-29 | 20.52 | Flow meter was calibrated and unit synchronized. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Boiler recirculation (flow meter) |  | Yes
Q1 | September 2025 | Aguirre 2 | Generator voltage control | 2025-09-29 | 2025-09-29 | 2.37 | The system (AVR) was resetted. | Generator, excitation and output bus | Voltage regulator (AVR) |  | Yes
Q2 | October 2025 | Costa Sur 5 | Platen superheater | 2025-10-02 | 2025-10-06 | 73.3 | Damaged tubes were repaired in the Boiler. | Boiler pressure parts | Platen superheater tubes |  | Yes
Q2 | October 2025 | Palo Seco 4 | Burner problems | 2025-10-02 | 2025-10-02 | 8.53 | Foxboro logic bypass administered. | Burners and firing | Burners (control logic) |  | Yes
Q2 | October 2025 | Aguirre CC 2-1 | Reduction gear | 2025-10-03 | 2025-10-13 | 236.3 | Replaced 8 bearings and gear with shaft #1. | Turbine bearings, gears and vibration | Reduction gear |  | Yes
Q2 | October 2025 | Palo Seco 4 | Circulating water pumps | 2025-10-03 | 2025-10-04 | 5.4 | Correction on vaccum loss, system backwash failure and circulating water pump suction. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Circulating water and condenser vacuum |  | Yes
Q2 | October 2025 | Palo Seco 4 | Circulating water pumps | 2025-10-04 | 2025-10-05 | 40.6 | Correction on vaccum loss, system backwash failure and circulating water pump suction. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Circulating water and condenser vacuum |  | Yes
Q2 | October 2025 | Cambalache 2 | Exhaust problems | 2025-10-06 | 2025-10-06 | 2.7 | Waited for the temperature to drop below 350 degrees F. | Gas turbine combustion, compressor and hot section | Exhaust temperature |  | Yes
Q2 | October 2025 | Palo Seco 4 | Circulating water pumps | 2025-10-07 | 2025-10-07 | 16.58 | Correction on vaccum loss, system backwash failure and circulating water pump suction. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Circulating water and condenser vacuum |  | Yes
Q2 | October 2025 | San Juan CT 6 | Fuel system problems | 2025-10-08 | 2025-10-08 | 1.47 | Sensor were inspected and greenlit. | Fuel system | Fuel system sensor |  | Yes
Q2 | October 2025 | Palo Seco 3 | Air heater fouling | 2025-10-10 | 2025-10-14 | 103.55 | Programmed cleaning executed during this period. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Air heater fouling |  | Yes
Q2 | October 2025 | Aguirre CC 2-1 | Gas fuel system including controls and instrumentation | 2025-10-16 | 2025-10-17 | 17.2 | Changed the solenoids and defective cables of the fuel bypass valve. | Fuel system | Fuel bypass valve (solenoids and cables) |  | Yes
Q2 | October 2025 | San Juan CT 6 | Circulating water piping | 2025-10-16 | 2025-10-17 | 19.85 | Pipe welded and sealed. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Circulating water piping |  | Yes
Q2 | October 2025 | San Juan TM 1 | Switchyard or high voltage system problems | 2025-10-16 | 2025-10-31 | 356.9 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. The output cables were left disconnected in order to normalize the rest of the plant. | Shared plant equipment (one event affected three or more units) | Metal-clad cabinet and main power transformer breaker | Same event (October 16, 2025): San Juan TM 1, 2, 3, 5, 6, 7, 8 and 10 | No
Q2 | October 2025 | San Juan TM 1 | Breaker on the Main Power Transformer opened, causing a trip to the rest of the units. | 2025-10-16 | 2025-10-31 | 368.83 | Unit was isolated and proceeded to close the breaker on the Main Power Transformer. GT-01 output cables were left disconnected in order to normalize the rest of the plant. Works are ongoing. | Shared plant equipment (one event affected three or more units) | Metal-clad cabinet and main power transformer breaker | Continuation of the October 16 event | No
Q2 | October 2025 | San Juan TM 2 | Switchyard or high voltage system problems | 2025-10-16 | 2025-10-17 | 38.08 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. | Shared plant equipment (one event affected three or more units) | Metal-clad cabinet and main power transformer breaker | Same event (October 16, 2025): San Juan TM 1, 2, 3, 5, 6, 7, 8 and 10 | No
Q2 | October 2025 | San Juan TM 3 | Switchyard or high voltage system problems | 2025-10-16 | 2025-10-17 | 38.08 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. | Shared plant equipment (one event affected three or more units) | Metal-clad cabinet and main power transformer breaker | Same event (October 16, 2025): San Juan TM 1, 2, 3, 5, 6, 7, 8 and 10 | No
Q2 | October 2025 | San Juan TM 5 | Switchyard or high voltage system problems | 2025-10-16 | 2025-10-17 | 38.08 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. | Shared plant equipment (one event affected three or more units) | Metal-clad cabinet and main power transformer breaker | Same event (October 16, 2025): San Juan TM 1, 2, 3, 5, 6, 7, 8 and 10 | No
Q2 | October 2025 | San Juan TM 6 | Switchyard or high voltage system problems | 2025-10-16 | 2025-10-17 | 38.08 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. | Shared plant equipment (one event affected three or more units) | Metal-clad cabinet and main power transformer breaker | Same event (October 16, 2025): San Juan TM 1, 2, 3, 5, 6, 7, 8 and 10 | No
Q2 | October 2025 | San Juan TM 7 | Switchyard or high voltage system problems | 2025-10-16 | 2025-10-17 | 38.08 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. | Shared plant equipment (one event affected three or more units) | Metal-clad cabinet and main power transformer breaker | Same event (October 16, 2025): San Juan TM 1, 2, 3, 5, 6, 7, 8 and 10 | No
Q2 | October 2025 | San Juan TM 8 | Switchyard or high voltage system problems | 2025-10-16 | 2025-10-17 | 38.08 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. | Shared plant equipment (one event affected three or more units) | Metal-clad cabinet and main power transformer breaker | Same event (October 16, 2025): San Juan TM 1, 2, 3, 5, 6, 7, 8 and 10 | No
Q2 | October 2025 | San Juan TM 10 | Switchyard or high voltage system problems | 2025-10-16 | 2025-10-17 | 38.08 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. | Shared plant equipment (one event affected three or more units) | Metal-clad cabinet and main power transformer breaker | Same event (October 16, 2025): San Juan TM 1, 2, 3, 5, 6, 7, 8 and 10 | No
Q2 | October 2025 | San Juan CT 5 | Feedwater pump | 2025-10-17 | 2025-10-17 | 2.32 | Pumps were inspected and greenlit. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Feedwater pump |  | Yes
Q2 | October 2025 | San Juan CT 5 | Combustion inspection | 2025-10-17 | 2025-10-21 | 85.7 | Boroscope inspection by supplier. | Gas turbine combustion, compressor and hot section | Combustion inspection |  | Yes
Q2 | October 2025 | Palo Seco 4 | AC Conductors and buses | 2025-10-18 | 2025-10-19 | 5.43 | Fuse replaced. | Electrical (breakers, transformers, DC and auxiliary power) | AC conductors and buses (fuse) |  | Yes
Q2 | October 2025 | Aguirre CC 2-1 | Gas fuel system including controls and instrumentation | 2025-10-19 | 2025-10-19 | 3.2 | Changed the position indicator of the fuel bypass valve. | Fuel system | Fuel bypass valve (position indicator) |  | Yes
Q2 | October 2025 | Aguirre CC 2-1 | Gas fuel system including controls and instrumentation | 2025-10-19 | 2025-10-20 | 16.7 | Electrical section perfomed megger test on the exciter, generator rotor and stator. Instrumentation section, fuel bypass valve caliber, and remote Mark VIe works. | Fuel system | Gas fuel system |  | Yes
Q2 | October 2025 | Palo Seco 4 | Feedwater pump | 2025-10-19 | 2025-10-20 | 17.47 | Corrected normal and emergency connections to Boiler Feed Pump. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Boiler feed pump |  | Yes
Q2 | October 2025 | Aguirre CC 2-1 | Gas fuel system including controls and instrumentation | 2025-10-20 | 2025-10-21 | 20.6 | Changed the control card; it gives voltage to the speed pickup to monitor the fuel flow. Adjusted the voltage on the two fuel bypass valve solenoids. Charged the high fuel filters. Cleaned a small piece of rubber and calibrated the pickup gears. | Fuel system | Fuel control card (speed pickup) |  | Yes
Q2 | October 2025 | Mayaguez 4B | Instrumentation services and control | 2025-10-22 | 2025-10-24 | 52.43 | The CPU and Network (RTN) unit short- circuited and the computer did not detect the signal. A new CPU unit was found in Costa Sur plant and it was replaced. | Controls, instrumentation and protection | Control CPU and network |  | Yes
Q2 | October 2025 | Aguirre CC 1-2 | Turbine instrument and control problems | 2025-10-24 | 2025-10-25 | 16.5 | The Mark VIe was reset. | Controls, instrumentation and protection | Mark VIe control |  | Yes
Q2 | October 2025 | Aguirre 2 | Rotor collector rings | 2025-10-26 | 2025-10-31 | 135.05 | A Management of Change (MOC) procedure was implemented to configure and install a redundant ground- fault detection system for the generator field circuit, ensuring redundancy for ground-fault monitoring and trip functions. | Generator, excitation and output bus | Rotor collector rings |  | Yes
Q2 | October 2025 | Aguirre CC 2-2 | Atomizing air system | 2025-10-27 | 2025-10-31 | 105.8 | Air-to-air heat exchanger was replaced. The atomizing compressor was also replaced. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Atomizing air system |  | Yes
Q2 | November 2025 | Aguirre CC 2-2 | Oil consumption issues. | 2025-11-01 | 2025-11-05 | 110.3 | Completed. Forced outage continuation from last month. Air exchanger was replaced. The atomising compressor was also replaced. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Atomizing air system (oil consumption) | Continuation of the October 27 event | No
Q2 | November 2025 | Aguirre 2 | Generator rotor field ground trip | 2025-11-03 | 2025-11-03 | 1.96 | Exciter system was inspected. Generator rotor low IR alarms were resetted satisfactorily. Unit was synchronized to the grid the same day. | Generator, excitation and output bus | Rotor field ground |  | Yes
Q2 | November 2025 | Aguirre 2 | Generator rotor field ground trip | 2025-11-03 | 2025-11-03 | 1.82 | Exciter system was inspected. Generator rotor low IR alarms were resetted satisfactorily. The alternate field ground protection was left disabled for monitoring purpose only. Unit was synchronized to the grid the same day. Additional troubleshooting is required to determine root cause of intermittent field ground indications. | Generator, excitation and output bus | Rotor field ground |  | Yes
Q2 | November 2025 | Cambalache 2 | Turbine shutdown due to low pressure in the cooling water system and suspected rupture of one of the generator's cooling air coolers. | 2025-11-03 | 2025-11-03 | 10.48 | During inspection of the generator's cooling air coolers, mechanical damage was found in cooler 1. This cooler was replaced with one from GT1 generator. GT1 has been out of service and unavailable since 2011. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Generator air coolers (cooling water) |  | Yes
Q2 | November 2025 | Palo Seco 4 | Boiler feed pump line leaks | 2025-11-04 | 2025-11-05 | 23.63 | Repairs to Boiler feed pump line. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Boiler feed pump line |  | Yes
Q2 | November 2025 | Aguirre CC 2-2 | Forced shutdown due to oil leak from auxiliary tank gasket in the turbine area. | 2025-11-06 | 2025-11-06 | 15.6 | Changed the tank's gasket. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Lube oil tank gasket |  | Yes
Q2 | November 2025 | Aguirre 2 | Boiler tube failure | 2025-11-07 | 2025-11-11 | 80.22 | Unit was repaired and synchronized satisfactorily to the electrical grid. During the hydrostatic test performed, additional leaks were identified in multiple areas of the waterwalls and superheater areas. | Boiler pressure parts | Boiler tubes |  | Yes
Q2 | November 2025 | Daguao 1-1 | Lube oil high temperature | 2025-11-10 | 2025-11-11 | 15.53 | Major repair. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Lube oil high temperature | Same event: Daguao 1-2 | Yes
Q2 | November 2025 | Daguao 1-2 | Lube oil high temperature | 2025-11-10 | 2025-11-11 | 15.53 | Major repair. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Lube oil high temperature | Same event: Daguao 1-1 | Yes
Q2 | November 2025 | Palo Seco 4 | Service fuel pump 4-1 trip | 2025-11-11 | 2025-11-17 | 32.5 | Pump replacement. | Fuel system | Fuel pump 4-1 |  | Yes
Q2 | November 2025 | Daguao 1-2 | Bleed valve position trouble | 2025-11-13 | 2025-11-13 | 0.87 | Reduced generation. | Gas turbine combustion, compressor and hot section | Compressor bleed valve |  | Yes
Q2 | November 2025 | Palo Seco MP 2 | Vibration system monitoring failure | 2025-11-13 | 2025-11-18 | 117.33 | Unit control reprogramming. | Controls, instrumentation and protection | Vibration monitoring system |  | Yes
Q2 | November 2025 | Palo Seco TM 3 | Service water pump failure | 2025-11-13 | 2025-11-13 | 2.53 | Replaced water injection pump. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Water injection pump |  | Yes
Q2 | November 2025 | Daguao 1-2 | Cooling fan failure | 2025-11-14 | 2025-11-16 | 43.92 | Coupling replaced. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Cooling fan coupling |  | Yes
Q2 | November 2025 | Costa Sur 6 | Waterwall (Furnace wall) | 2025-11-16 | 2025-11-19 | 68.95 | Broken Boiler tubes repaired, hydrostatic test performed and unit synchronized. | Boiler pressure parts | Waterwall tubes |  | Yes
Q2 | November 2025 | Palo Seco 1-2 | Fuel nozzle failure. | 2025-11-16 | 2025-11-17 | 21.5 | Fuel nozzle replaced. | Fuel system | Fuel nozzles |  | Yes
Q2 | November 2025 | San Juan TM 10 | Hydraulic oil system pumps | 2025-11-17 | 2025-11-18 | 16.22 | Replaced the hydraulics pumps. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Hydraulic oil pumps |  | Yes
Q2 | November 2025 | San Juan CT 5 | Combustion inspection, replacement of combustors | 2025-11-19 | 2025-11-30 | 264.1 | Work in process. | Gas turbine combustion, compressor and hot section | Combustors (combustion inspection) | Affected San Juan ST 5 | Yes
Q2 | November 2025 | San Juan ST 5 | Combustion inspection, replacement of combustors | 2025-11-19 | 2025-11-30 | 264.4 | Work in process. | Event at another unit (companion or shared equipment) | Combustion turbine 5 combustion inspection | Caused by San Juan CT 5 | No
Q2 | November 2025 | Palo Seco 3 | Boiler water line breaking | 2025-11-21 | 2025-11-24 | 57.9 | Boiler water line repairs. | Boiler pressure parts | Boiler water line |  | Yes
Q2 | November 2025 | San Juan TM 7 | Clogged Fuel nozzles/ vanes | 2025-11-23 | 2025-11-24 | 12.33 | Unclogged the fuel nozzles. | Fuel system | Fuel nozzles |  | Yes
Q2 | November 2025 | San Juan TM 8 | Clogged Fuel nozzles/ vanes | 2025-11-23 | 2025-11-23 | 1.88 | Unclogged the fuel nozzles. | Fuel system | Fuel nozzles |  | Yes
Q2 | November 2025 | Palo Seco 3 | Loss of atomizing steam preassure, fuel line break and cooling water break | 2025-11-29 | 2025-11-30 | 33.92 | Repairs to fuel and cooling lines. | Fuel system | Fuel line, atomizing steam and cooling water lines |  | Yes
Q2 | November 2025 | San Juan CT 6 | Low natural gas pressure from supplier | 2025-11-29 | 2025-11-29 | 1.5 | Supplier fixed pressure. | Outside the plant (LUMA switchyard, grid, third-party fuel supply) | Gas supply pressure (supplier) |  | No
Q2 | November 2025 | Palo Seco TM 3 | High spread (Water Wash) | 2025-11-30 | 2025-11-30 | 3.35 | Gas turbine/compressor washing. | Gas turbine combustion, compressor and hot section | Exhaust temperature spread (compressor wash) |  | Yes
Q2 | December 2025 | Aguirre CC 2-4 | Oil leak and vibrations in the accessory gearbox | 2025-12-01 | 2025-12-05 | 95.3 | Worked on the accessory box cover and performed maintenance on the coupling shaft between the turbine and the accessory box. | Turbine bearings, gears and vibration | Accessory gearbox |  | Yes
Q2 | December 2025 | Costa Sur 6 | Waterwall (Furnace wall) | 2025-12-01 | 2025-12-05 | 98.95 | Broken Boiler tubes were repaired, hydrostatic test performed and unit synchronized. | Boiler pressure parts | Waterwall tubes |  | Yes
Q2 | December 2025 | San Juan CT 5 | Combustion inspection, replacement of combustors | 2025-12-01 | 2025-12-23 | 543.62 | Forced outage continuation from last month. Completed installation of combustors. | Gas turbine combustion, compressor and hot section | Combustors (combustion inspection) | Continuation of the November 19 event | No
Q2 | December 2025 | San Juan ST 5 | Combustion inspection, replacement of combustors | 2025-12-01 | 2026-12-24 | 561.68 | Forced outage continuation from last month. Completed installation of combustors. | Event at another unit (companion or shared equipment) | Combustion turbine 5 combustion inspection | Caused by San Juan CT 5 (continuation) | No
Q2 | December 2025 | San Juan TM 1 | Breaker on the Main Power Transformer opened, causing a trip to the rest of the units. | 2025-12-01 | 2025-12-16 | 375.67 | Forced outage continuation from last month. Unit was isolated and proceeded to close the breaker on the Main Power Transformer. GT-01 output cables were left disconnected in order to normalize the rest of the plant. | Shared plant equipment (one event affected three or more units) | Metal-clad cabinet and main power transformer breaker | Continuation of the October 16 event | No
Q2 | December 2025 | Mayaguez 3A | Shut off valve and water injection relay damage | 2025-12-03 | 2025-12-03 | 4.18 | Replaced items. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Water injection (shut-off valve and relay) |  | Yes
Q2 | December 2025 | Mayaguez 3A | Igniters damage | 2025-12-03 | 2025-12-03 | 4.18 | Replaced items. | Ignition and flame detection | Igniters | Same outage as the water injection record | No
Q2 | December 2025 | Palo Seco TM 3 | T54 High Temperature spread | 2025-12-03 | 2025-12-31 | 677.88 | Pending new fuel nozzles. Still out of service. | Fuel system | Fuel nozzles (temperature spread) |  | Yes
Q2 | December 2025 | San Juan TM 8 | T48 High temperature spread | 2025-12-03 | 2025-12-31 | 674.88 | Out of service. | Gas turbine combustion, compressor and hot section | High temperature spread (T48) |  | Yes
Q2 | December 2025 | Jobos 1-2 | Turning gear and motor failure | 2025-12-04 | 2025-12-31 | 683 | Work in progress. | Starting system | Turning gear and motor |  | Yes
Q2 | December 2025 | Aguirre 2 | Boiler tube failure | 2025-12-08 | 2025-12-15 | 171.85 | Unit was repaired and synchronized satisfactorily to the electrical grid. | Boiler pressure parts | Boiler tubes |  | Yes
Q2 | December 2025 | San Juan TM 4 | CPU Card fail micronet | 2025-12-08 | 2025-12-16 | 201.5 | IP address input re-entered. | Controls, instrumentation and protection | Control CPU card (Micronet) |  | Yes
Q2 | December 2025 | Palo Seco 4 | Air compressor trip | 2025-12-11 | 2025-12-12 | 24.63 | Fixed air compressor drain solenoid. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Air compressor drain solenoid |  | Yes
Q2 | December 2025 | Palo Seco TM 2 | VSV Driver fault, cable E47 was disconnected from the servovalve | 2025-12-13 | 2025-12-13 | 2.58 | The cable was connected, everything was put back in place and the alarm resetted. | Controls, instrumentation and protection | Variable stator vane driver cable |  | Yes
Q2 | December 2025 | Aguirre CC 1-2 | Exhaust gas spread, thermocouple #3 defective. | 2025-12-15 | 2025-12-15 | 0.7 | Changed thermocouple #3 and performed maintenance on the others. | Controls, instrumentation and protection | Exhaust thermocouple |  | Yes
Q2 | December 2025 | Aguirre CC 2-4 | Low pressure in the liquid fuel filter. Fuel pump 2-4A broke the bearing and 2-4B didn't start. | 2025-12-16 | 2025-12-16 | 0.9 | Fuel pump 2-4 B was put into service and the pressure switch was changed. | Fuel system | Liquid fuel pump 2-4A |  | Yes
Q2 | December 2025 | San Juan CT 6 | Works on Steam Turbine | 2025-12-16 | 2026-12-23 | 175 | Works ongoing. From December 23, the unit will be out of service as a Scheduled Planned Outage. | Turbine bearings, gears and vibration | Steam turbine work |  | Yes
Q2 | December 2025 | San Juan TM 10 | NOX Water Injection metering Valve demand and position FBK failing to operate | 2025-12-16 | 2025-12-17 | 18.99 | NOX Water injection replaced. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Water injection metering valve |  | Yes
Q2 | December 2025 | San Juan TM 2 | Lubrication oil supply pressure | 2025-12-19 | 2025-12-19 | 1 | Replacement of TLO supply and SCAVENGE filters. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Lube oil system |  | Yes
Q2 | December 2025 | Aguirre CC 2-1 | Fuel control issue | 2025-12-23 | 2025-12-24 | 13.3 | Fuel bypass valve rod out of position, valve was calibrated. | Fuel system | Fuel control (bypass valve) |  | Yes
Q2 | December 2025 | San Juan CT 5 | Circulating water pump, high temperature in upper bearing | 2025-12-23 | 2026-12-23 | 1.78 | Temperature sensor recalibrated. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Circulating water pump bearing temperature sensor |  | Yes
Q2 | December 2025 | San Juan TM 2 | Generator Lube oil supply pressure | 2025-12-23 | 2025-12-23 | 2.26 | Replaced cable. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Lube oil system |  | Yes
Q2 | December 2025 | Aguirre CC 2-1 | Fuel control issue | 2025-12-26 | 2026-12-27 | 20.4 | Assembled the fuel bypass valve solenoid. | Fuel system | Fuel control (bypass valve) |  | Yes
Q2 | December 2025 | Daguao 1-2 | Lube Oil Pump failure | 2025-12-27 | 2025-12-30 | 96 | Electrical work performed, relay replaced. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Lube oil pump |  | Yes
Q2 | December 2025 | San Juan TM 2 | Generator Lube oil supply pressure | 2025-12-28 | 2025-12-28 | 1 | Replaced the relay. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Lube oil system |  | Yes
Q2 | December 2025 | Aguirre CC 2-2 | Forced shutdown due to load fluctuations | 2025-12-29 | 2025-12-30 | 21.6 | The two solenoides of the inlet guide vanes were changed. | Controls, instrumentation and protection | Inlet guide vane solenoids |  | Yes
Q2 | December 2025 | San Juan TM 10 | Lube oil system general issue. | 2025-12-30 | 2025-12-30 | 4.28 | Lube oil system was cleaned. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Lube oil system |  | Yes
Q2 | December 2025 | Aguirre CC 1-2 | Oil leak in the inlet guide vanes block | 2025-12-31 | 2025-12-31 | 8.6 | Work in progress. | Controls, instrumentation and protection | Inlet guide vane block (oil leak) |  | Yes
Q2 | December 2025 | Daguao 1-1 | Main Power Transformer failure | 2025-12-31 | 2025-12-31 | 24 | Pending lockout protection system inspection. | Electrical (breakers, transformers, DC and auxiliary power) | Main power transformer | Same event: Daguao 1-2 | Yes
Q2 | December 2025 | Daguao 1-2 | Main Power Transformer failure | 2025-12-31 | 2025-12-31 | 24 | Pending lockout protection system inspection. | Electrical (breakers, transformers, DC and auxiliary power) | Main power transformer | Same event: Daguao 1-1 | Yes
Q3 | January 2026 | Aguirre CC 1-2 | Continuation from previous month. The work continued on oil leak in the inlet guide vanes block. | 2026-01-01 | 2026-01-02 | 45 | The piston and inlet guide valve block were replaced. The fuel bypass valve solenoids were changed. | Controls, instrumentation and protection | Inlet guide vane block (oil leak) | Continuation of the December 31, 2025 event | No
Q3 | January 2026 | Aguirre 2 | Unit tripped due to instrument air header pressure loss. | 2026-01-03 | 2026-01-03 | 10.48 | IACs were restored to normal operation (oil make-up completed), and the unit was successfully synchronized. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Instrument air header pressure |  | Yes
Q3 | January 2026 | Palo Seco MP 2 | DC Lube oil Pump Generator failure. | 2026-01-03 | 2026-01-05 | 47.43 | Lube Oil Pump Motor replacement. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Generator DC lube oil pump |  | Yes
Q3 | January 2026 | Palo Seco MP 2 | Diesel fuel Pump Oil leak. | 2026-01-05 | 2026-01-06 | 17.53 | Pump Seal and packing replacement. | Fuel system | Diesel fuel pump |  | Yes
Q3 | January 2026 | Palo Seco TM 2 | Problems with Regas protection system, low gas supply pressure. | 2026-01-05 | 2026-01-05 | 0.55 | The gas plant normalized their pumps. | Outside the plant (LUMA switchyard, grid, third-party fuel supply) | Gas supply pressure (regasification plant) |  | No
Q3 | January 2026 | Costa Sur 5 | Feedwater valves | 2026-01-11 | 2026-01-25 | 343.08 | Heater #6 inlet valve repaired. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Feedwater heater 6 inlet valve |  | Yes
Q3 | January 2026 | Mayaguez 4B | The unit tripped due to secondary fan alarm. | 2026-01-11 | 2026-01-11 | 4.47 | Worked on the fan limit switch and alarm setting, and solved the issue. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Secondary fan limit switch |  | Yes
Q3 | January 2026 | San Juan TM 7 | Issue with the water injection pump. | 2026-01-13 | 2026-01-14 | 15.49 | The water injection pump was replaced. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Water injection pump |  | Yes
Q3 | January 2026 | Palo Seco MP 2 | AC lube oil motor failure. | 2026-01-16 | 2026-01-17 | 21.55 | AC pump motor replacement. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | AC lube oil pump motor |  | Yes
Q3 | January 2026 | Aguirre CC 2-1 | Trip due to lockout generator, relay #40 (loss of excitation), external trip, and fuel. | 2026-01-18 | 2026-01-20 | 38.9 | Reset the EX2100 and calibrate the fuel bypass valve, a megger test was done on the generator, managed to raise the generator breaker that had tripped on one side. | Generator, excitation and output bus | Excitation (loss of excitation, EX2100) |  | Yes
Q3 | January 2026 | Mayaguez 4B | Water Injection Level Switch was damaged. | 2026-01-18 | 2026-01-20 | 41.37 | A water injection level switch was replaced. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Water injection level switch |  | Yes
Q3 | January 2026 | San Juan TM 2 | Lube oil system problems. | 2026-01-18 | 2026-01-18 | 2.05 | Replaced N47 relay switch. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Lube oil system |  | Yes
Q3 | January 2026 | San Juan CT 5 | Non-authorized works were done on Breaker 5E-1. Emergency Breaker was closed causing normal to open, then the emergency breaker was opened, leaving both breakers open. | 2026-01-21 | 2026-01-21 | 1.05 | Procedures were in place. Personnel was trained and advised. | Electrical (breakers, transformers, DC and auxiliary power) | Breaker 5E-1 (unauthorized work) | Same event: San Juan ST 5 | Yes
Q3 | January 2026 | San Juan ST 5 | Non-authorized works were done on Breaker 5E-1. Emergency Breaker was closed causing normal to open, then the emergency breaker was opened, leaving both breakers open. | 2026-01-21 | 2026-01-26 | 118 | Procedures were in place. Personnel was trained and advised. | Electrical (breakers, transformers, DC and auxiliary power) | Breaker 5E-1 (unauthorized work) | Same event: San Juan CT 5 | Yes
Q3 | January 2026 | San Juan TM 1 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-31 | 193.17 | Work in progress. | Shared plant equipment (one event affected three or more units) | Metal-clad cabinet and main power transformer breaker | Same event (January 22, 2026): San Juan TM 1, 2, 3, 4, 5, 6, 7 and 10 | No
Q3 | January 2026 | San Juan TM 2 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-27 | 114.35 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit. | Shared plant equipment (one event affected three or more units) | Metal-clad cabinet and main power transformer breaker | Same event (January 22, 2026): San Juan TM 1, 2, 3, 4, 5, 6, 7 and 10 | No
Q3 | January 2026 | San Juan TM 3 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-27 | 114.35 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit. | Shared plant equipment (one event affected three or more units) | Metal-clad cabinet and main power transformer breaker | Same event (January 22, 2026): San Juan TM 1, 2, 3, 4, 5, 6, 7 and 10 | No
Q3 | January 2026 | San Juan TM 4 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-26 | 91.53 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit. | Shared plant equipment (one event affected three or more units) | Metal-clad cabinet and main power transformer breaker | Same event (January 22, 2026): San Juan TM 1, 2, 3, 4, 5, 6, 7 and 10 | No
Q3 | January 2026 | San Juan TM 5 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-24 | 44.02 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit. | Shared plant equipment (one event affected three or more units) | Metal-clad cabinet and main power transformer breaker | Same event (January 22, 2026): San Juan TM 1, 2, 3, 4, 5, 6, 7 and 10 | No
Q3 | January 2026 | San Juan TM 6 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-24 | 44.02 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit. | Shared plant equipment (one event affected three or more units) | Metal-clad cabinet and main power transformer breaker | Same event (January 22, 2026): San Juan TM 1, 2, 3, 4, 5, 6, 7 and 10 | No
Q3 | January 2026 | San Juan TM 7 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-24 | 44.02 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit. | Shared plant equipment (one event affected three or more units) | Metal-clad cabinet and main power transformer breaker | Same event (January 22, 2026): San Juan TM 1, 2, 3, 4, 5, 6, 7 and 10 | No
Q3 | January 2026 | San Juan TM 10 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-24 | 44.02 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit. | Shared plant equipment (one event affected three or more units) | Metal-clad cabinet and main power transformer breaker | Same event (January 22, 2026): San Juan TM 1, 2, 3, 4, 5, 6, 7 and 10 | No
Q3 | January 2026 | Palo Seco MP 1 | DC Lube Oil Pump Generator failure. | 2026-01-23 | 2026-01-24 | 23.92 | Pump motor replacement. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Generator DC lube oil pump |  | Yes
Q3 | January 2026 | San Juan TM 5 | Gas leak on manifold, J-tubes and convoluted hoses. | 2026-01-23 | 2026-01-29 | 126.12 | Replaced gas manifold, J-tubes and convoluted hoses. | Fuel system | Gas manifold, J-tubes and hoses |  | Yes
Q3 | January 2026 | Palo Seco 1-2 | Starting System failure | 2026-01-24 | 2026-01-26 | 47.65 | Acceleration control valve in Diesel Engine replacement. | Starting system | Starting diesel engine acceleration control valve |  | Yes
Q3 | January 2026 | Yabucoa 1-2 | Torque Converter failure. | 2026-01-25 | 2026-01-31 | 155 | During inspection, an SSS clutch failure was found. In process of replacement. | Starting system | Torque converter (SSS clutch) |  | Yes
Q3 | January 2026 | Costa Sur 5 | Boiler tube leaks platen superheater | 2026-01-27 | 2026-01-31 | 97.13 | Broken Boiler tubes repaired, hydrostatic test performed. | Boiler pressure parts | Platen superheater tubes |  | Yes
Q3 | January 2026 | San Juan CT 6 | Vacuum loss due to vacuum pump bravo uncoupling and discharge valve left open. | 2026-01-27 | 2026-01-27 | 3.2 | Vacuum pump bravo in repairs. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Condenser vacuum pump B | Same event: San Juan ST 5 | Yes
Q3 | January 2026 | San Juan ST 5 | Vacuum loss due to vacuum pump bravo uncoupling and discharge valve left open. | 2026-01-27 | 2026-01-27 | 8.5 | Vacuum pump bravo in repairs. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Condenser vacuum pump B | Same event: San Juan CT 6 | Yes
Q3 | January 2026 | Aguirre CC 2-4 | Excitation problem, excitation loss, relay #40, and generator lockout. | 2026-01-29 | 2026-01-29 | 2.3 | The 180 ohms resistor in the excitation system of the exciter was replaced. The one from unit 2-3 was used. | Generator, excitation and output bus | Excitation (resistor) |  | Yes
Q3 | January 2026 | San Juan 9 | Voltage regulator failed when switched from manual to auto. | 2026-01-30 | 2026-01-30 | 8.33 | Megger tests were done. No faults found. | Generator, excitation and output bus | Voltage regulator |  | Yes
Q3 | February 2026 | Costa Sur 5 | Generator neutral grounding equipment. | 2026-02-02 | 2026-02-02 | 3.99 | Cleaning and maintenance performed. | Generator, excitation and output bus | Generator neutral grounding |  | Yes
Q3 | February 2026 | Aguirre 2 | Boiler tube leakage / waterwall area. | 2026-02-06 | 2026-02-09 | 81.38 | Corrective Maintenance activities were performed. Unit was synchronized to the grid. | Boiler pressure parts | Waterwall tubes |  | Yes
Q3 | February 2026 | San Juan CT 5 | Bladepath variance. | 2026-02-07 | 2026-02-07 | 3.3 | Inspected and corrected. | Controls, instrumentation and protection | Blade path temperature |  | Yes
Q3 | February 2026 | San Juan ST 5 | High vibrations. | 2026-02-07 | 2026-02-14 | 172.27 | Inspected and nothing found. | Turbine bearings, gears and vibration | Turbine vibration |  | Yes
Q3 | February 2026 | San Juan 9 | Broken boiler lines. | 2026-02-15 | 2026-02-15 | 1.67 | Boiler lines fixed. | Boiler pressure parts | Boiler lines |  | Yes
Q3 | February 2026 | Palo Seco 4 | High temperature in unit 3/4 server room. | 2026-02-17 | 2026-02-18 | 13.63 | Server room cooling system fixed. | Controls, instrumentation and protection | Control server room cooling |  | Yes
Q3 | February 2026 | Palo Seco 1-2 | Starting System failure, DC Control cable damage. | 2026-02-18 | 2026-02-20 | 46.5 | DC Control cable replaced. | Starting system | Starting system DC control cable |  | Yes
Q3 | February 2026 | Palo Seco MP 2 | Lube Oil Presure Drain High Breeder. | 2026-02-18 | 2026-02-28 | 239.5 | In process of troubleshooting. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Lube oil system |  | Yes
Q3 | February 2026 | Palo Seco MP 3 | Gen Lube Oil Pump Coupling failure. | 2026-02-21 | 2026-02-28 | 175.07 | Waiting for coupling delivery. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Generator lube oil pump coupling |  | Yes
Q3 | February 2026 | Aguirre 2 | Boiler tube leakage / waterwall area. | 2026-02-24 | 2026-02-28 | 115.18 | Corrective Maintenance activities were performed, including boiler air in leakage (ash hopper area). Unit was synchronized to the grid. | Boiler pressure parts | Waterwall tubes |  | Yes
Q3 | February 2026 | Aguirre CC 2-1 | Exciter to Mark VIe communication fault. Ex2100 trip alarm. | 2026-02-25 | 2026-02-25 | 1.1 | EX2100 and Mark VIe were reset; unit was put in service. | Generator, excitation and output bus | Excitation (EX2100 communication) |  | Yes
Q3 | March 2026 | Aguirre 2 | Boiler tube leakage / waterwall area. | 2026-03-01 | 2026-03-02 | 33.7 | Continuation of previous month. Corrective Maintenance activities were performed, including boiler air in leakage (ash hopper area). Unit was synchronized to the grid. | Boiler pressure parts | Waterwall tubes | Continuation of the February 24 event | No
Q3 | March 2026 | Cambalache 3 | Turbine Vane 3 broken shim | 2026-03-01 | 2026-03-10 | 234.73 | Class-C Service. Unit reassembly. Turbocharger balancing. Commissioning. | Gas turbine combustion, compressor and hot section | Turbine vane 3 (broken shim) |  | Yes
Q3 | March 2026 | Daguao 1-1 | Main Power Transformer failure. Lockout activated. | 2026-03-01 | 2026-03-14 | 312 | Transformer output bus cleaning, lightning protection, generator output bus cleaning and megger. | Electrical (breakers, transformers, DC and auxiliary power) | Main power transformer |  | Yes
Q3 | March 2026 | Jobos 1-2 | Torque converter failure | 2026-03-01 | 2026-03-03 | 65.3 | Continuation from previous month. During inspection, an SSS clutch failure was found; it was replaced. | Starting system | Torque converter (SSS clutch) | Continuation from February 2026 | Yes
Q3 | March 2026 | Mayaguez 4A | Unit was no available due to a major overhaul. The entire gas generator component was out. Gas generator includes: compressor, combustors and turbine. | 2026-03-01 | 2026-03-17 | 400.3 | Continuation of previous month. On March 5, the installation began. Tests were performed. | Gas turbine combustion, compressor and hot section | Gas generator overhaul | Continuation from February 2026 | Yes
Q3 | March 2026 | Cambalache 2 | Stage 3 Blow-Off Valve failure. On March 1st, with the unit online at base load, an open valve alarm was triggered. The unit remained online in that condition until it was taken offline by the TOC. | 2026-03-02 | 2026-03-02 | 1.82 | Mechanical opening and closing tests of the valve were performed. The valve closing indicator switch was replaced. | Gas turbine combustion, compressor and hot section | Compressor stage 3 blow-off valve |  | Yes
Q3 | March 2026 | San Juan TM 2 | Lube oli system problems | 2026-03-02 | 2026-03-02 | 0.42 | Verified generator oil levels and the connection to the oil level transmitter. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Lube oil system |  | Yes
Q3 | March 2026 | Jobos 1-2 | Synchronization failure. | 2026-03-03 | 2026-03-05 | 44.93 | Inspection, cleaning connections and load breaker. | Controls, instrumentation and protection | Synchronization (load breaker connections) |  | Yes
Q3 | March 2026 | Palo Seco MP 3 | Turbine oil leak. | 2026-03-03 | 2026-03-04 | 31.5 | Replaced seal. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Turbine lube oil seal |  | Yes
Q3 | March 2026 | San Juan TM 2 | Lube oli system problems | 2026-03-04 | 2026-03-04 | 12.22 | Verified generator oil levels and the connection to the oil level transmitter. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Lube oil system |  | Yes
Q3 | March 2026 | Daguao 1-2 | Unit does not synchronize. | 2026-03-07 | 2026-03-10 | 73.3 | The synchronization control in the MCC was replaced. | Controls, instrumentation and protection | Synchronization control |  | Yes
Q3 | March 2026 | Palo Seco 1-2 | Control system issue. | 2026-03-07 | 2026-03-09 | 47.87 | Replaced I/O board. | Controls, instrumentation and protection | Control system I/O board |  | Yes
Q3 | March 2026 | San Juan TM 2 | Lube oli system problems | 2026-03-07 | 2026-03-07 | 0.45 | Verified generator oil levels and the connection to the oil level transmitter. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Lube oil system |  | Yes
Q3 | March 2026 | Jobos 1-2 | Gas turbine vibration. | 2026-03-08 | 2026-03-11 | 63.4 | During inspection we found the defective accesory shaft. This axle was replaced with a new one. | Turbine bearings, gears and vibration | Accessory shaft (gas turbine vibration) |  | Yes
Q3 | March 2026 | Mayaguez 3A | Speed sensor was giving problems during turn down. | 2026-03-08 | 2026-03-08 | 11.23 | Calibration was performed. | Controls, instrumentation and protection | Speed sensor |  | Yes
Q3 | March 2026 | Mayaguez 4B | The gas generator was being installed on Unit 4A, and the shaft connecting to the generator was also being aligned. This required a LOTO on the starter, which is limiting Unit 4B. | 2026-03-08 | 2026-03-12 | 97.22 | Once the shaft was installed and aligned, authorization was granted to remove the LOTO, releasing the starter and making Unit 4B available. | Event at another unit (companion or shared equipment) | Unit 4A gas generator installation | Caused by Mayaguez 4A | No
Q3 | March 2026 | San Juan CT 5 | Hot reheat bypass issue. | 2026-03-08 | 2026-03-08 | 6.17 | Instrumentation section fixed. | Controls, instrumentation and protection | Hot reheat bypass instrumentation |  | Yes
Q3 | March 2026 | Aguirre CC 2-1 | No progress in startup, relay activated and generator lockout. | 2026-03-10 | 2026-03-12 | 49.2 | Cable of the heater output bars. They repaired the heater cable, changed the insulation of the bars, and performed a megger test. | Generator, excitation and output bus | Generator output bars (heater cable) | Affected Aguirre CC 2-2 | Yes
Q3 | March 2026 | Aguirre CC 2-2 | No progress in startup, relay activated and generator lockout. It was unit 2-1 but the bars are joined at the outputs. | 2026-03-10 | 2026-03-12 | 49 | Cable of the heater output bars. They repaired the heater cable, changed the insulation of the bars, and performed a megger test. | Event at another unit (companion or shared equipment) | Aguirre CC 2-1 output bars | Caused by Aguirre CC 2-1 | No
Q3 | March 2026 | Cambalache 3 | Turbine Vane 3 broken shim | 2026-03-11 | 2026-03-11 | 14.5 | Class-C Service. Unit reassembly. Turbocharger balancing. Commissioning. | Gas turbine combustion, compressor and hot section | Turbine vane 3 (broken shim) | Continuation of the March 1 event | No
Q3 | March 2026 | Cambalache 3 | Turbine Vane 3 broken shim | 2026-03-11 | 2026-03-13 | 42.47 | Class-C Service. Unit reassembly. Turbocharger balancing. Commissioning. | Gas turbine combustion, compressor and hot section | Turbine vane 3 (broken shim) | Continuation of the March 1 event | No
Q3 | March 2026 | Cambalache 3 | Turbine Vane 3 broken shim | 2026-03-13 | 2026-03-14 | 21.88 | Class-C Service. Unit reassembly. Turbocharger balancing. Commissioning. | Gas turbine combustion, compressor and hot section | Turbine vane 3 (broken shim) | Continuation of the March 1 event | No
Q3 | March 2026 | Cambalache 3 | Turbine Vane 3 broken shim | 2026-03-14 | 2026-03-15 | 22.07 | Class-C Service. Unit reassembly. Turbocharger balancing. Commissioning. | Gas turbine combustion, compressor and hot section | Turbine vane 3 (broken shim) | Continuation of the March 1 event | No
Q3 | March 2026 | Aguirre CC 2-4 | Unit did not start due to vibrations in bearing #1. | 2026-03-15 | 2026-03-15 | 1.6 | Changed the vibration sensor of bearing #1. | Controls, instrumentation and protection | Bearing 1 vibration sensor |  | Yes
Q3 | March 2026 | Cambalache 3 | Turbine Vane 3 broken shim | 2026-03-15 | 2026-03-16 | 20.27 | Class-C Service. Unit reassembly. Turbocharger balancing. Commissioning. | Gas turbine combustion, compressor and hot section | Turbine vane 3 (broken shim) | Continuation of the March 1 event | No
Q3 | March 2026 | Palo Seco 1-2 | Excitation problem. | 2026-03-15 | 2026-03-17 | 44.58 | Replacement of brushes, cleaning and alignment. | Generator, excitation and output bus | Excitation brushes |  | Yes
Q3 | March 2026 | San Juan 9 | Operation error during transformer switch. | 2026-03-16 | 2026-04-16 | 2.83 | System was checked and greenlit. | Electrical (breakers, transformers, DC and auxiliary power) | Transformer switching (operating error) |  | Yes
Q3 | March 2026 | San Juan TM 2 | Lube oli system problems | 2026-03-17 | 2026-03-17 | 0.32 | Verified generator oil levels and the connection to the oil level transmitter. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Lube oil system |  | Yes
Q3 | March 2026 | Mayaguez 3A | Speed sensor trip. | 2026-03-19 | 2026-03-19 | 11.77 | A reset was performed. | Controls, instrumentation and protection | Speed sensor |  | Yes
Q3 | March 2026 | San Juan TM 2 | Lube oli system problems | 2026-03-19 | 2026-03-19 | 1.5 | Verified generator oil levels and the connection to the oil level transmitter. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Lube oil system |  | Yes
Q3 | March 2026 | San Juan TM 2 | Lube oli system problems | 2026-03-20 | 2026-03-20 | 1.33 | Verified generator oil levels and the connection to the oil level transmitter. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Lube oil system |  | Yes
Q3 | March 2026 | Aguirre CC 2-2 | Forced unit shutdown because the Inlet Guide Vane (IGV) did not open. | 2026-03-21 | 2026-03-22 | 24.7 | Calibrated the IGV that were stuck and transmitters. | Controls, instrumentation and protection | Inlet guide vane control |  | Yes
Q3 | March 2026 | Mayaguez 3A | Speed sensor trip. | 2026-03-21 | 2026-03-21 | 10.07 | A reset was performed. | Controls, instrumentation and protection | Speed sensor |  | Yes
Q3 | March 2026 | San Juan TM 2 | Blackstart Diesel Fuel Pump Failure. | 2026-03-21 | 2026-03-26 | 116.72 | Removed diesel fuel pump, none available in stock. A 480v external feeder was rerouted from GT-05 Switchgear to energize auxiliary equipments. | Starting system | Black start diesel fuel pump | Same event: San Juan TM 3 | Yes
Q3 | March 2026 | San Juan TM 3 | Blackstart Diesel Fuel Pump Failure. | 2026-03-21 | 2026-03-26 | 116.72 | Removed diesel fuel pump, none available in stock. A 480v external feeder was rerouted from GT-05 Switchgear to energize auxiliary equipments. | Starting system | Black start diesel fuel pump | Same event: San Juan TM 2 | Yes
Q3 | March 2026 | San Juan TM 6 | NPT Hi Speed Derivative. | 2026-03-21 | 2026-03-21 | 0.58 | Replaced acelerometer | Controls, instrumentation and protection | Speed pickup (accelerometer) |  | Yes
Q3 | March 2026 | Mayaguez 3A | Speed sensor trip. | 2026-03-22 | 2026-03-22 | 10.38 | A reset was performed. | Controls, instrumentation and protection | Speed sensor |  | Yes
Q3 | March 2026 | Palo Seco MP 1 | Gas leak and Gen LO failure. | 2026-03-22 | 2026-03-28 | 145.35 | Replaced Gen LO motor, a gas hose and seals. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Generator lube oil motor and gas hose |  | Yes
Q3 | March 2026 | San Juan 9 | Circulating Water Pump 9-1 trip with bus bar B losing vaccum. | 2026-03-22 | 2026-03-28 | 147.4 | Boiler lines were fixed, swapped to circulating waster pump 9-2 while the 9-1 is in reparations. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Circulating water pump 9-1 |  | Yes
Q3 | March 2026 | Mayaguez 4A | Unit Vacuum Pump was not working. Chip detetectors were lealing. | 2026-03-23 | 2026-03-23 | 4.25 | The replacemnt of the Vacuum Pump Equipment was performed. A torque adjustment were made in the lines of the chip detectors. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Vacuum pump and chip detectors |  | Yes
Q3 | March 2026 | Mayaguez 4B | An inspection on solenoid valve was conducted, taking advantage of the forced outage via circuit 4A. | 2026-03-23 | 2026-03-23 | 4.25 | It was determined that a change was needed. An order was placed. | Event at another unit (companion or shared equipment) | Unit 4A forced outage | Caused by Mayaguez 4A | No
Q3 | March 2026 | Mayaguez 4B | Unit trip due to flame out. | 2026-03-24 | 2026-03-25 | 23.13 | A governor solenoid was replaced. | Fuel system | Fuel governor solenoid |  | Yes
Q3 | March 2026 | San Juan ST 5 | High vibration in bearing. | 2026-03-24 | 2026-03-25 | 20.97 | System checked and greenlit. | Turbine bearings, gears and vibration | Turbine bearing vibration |  | Yes
Q3 | March 2026 | San Juan TM 4 | Liquid fuel primary manifold thermocouple failure | 2026-03-25 | 2026-03-25 | 0.37 | Replaced thermocouple on primary manifold liquid fuel system. | Controls, instrumentation and protection | Liquid fuel manifold thermocouple |  | Yes
Q3 | March 2026 | Mayaguez 4B | Solenoid valve failure. | 2026-03-26 | 2026-03-26 | 2.53 | The solenoid valve was replaced. | Fuel system | Fuel solenoid valve |  | Yes
Q3 | March 2026 | San Juan CT 5 | Fire protection system trip. | 2026-03-26 | 2026-03-26 | 5.92 | Found pullout box filled with rain water due to being broken and causing a short circuit and a false alarm. | Fire protection | Fire protection (water intrusion) | Affected San Juan ST 5 | Yes
Q3 | March 2026 | San Juan ST 5 | Fire protection system trip. | 2026-03-26 | 2026-03-26 | 9.35 | System inspected and cleaned. | Event at another unit (companion or shared equipment) | Trip of combustion turbine 5 (fire protection) | Caused by San Juan CT 5 | No
Q3 | March 2026 | Jobos 1-2 | Gas turbine loses speed reference. | 2026-03-29 | 2026-03-30 | 15.12 | Replacement of speed sensor connection terminal. | Controls, instrumentation and protection | Speed sensor connection |  | Yes
Q3 | March 2026 | Mayaguez 3A | Unit was not injecting water. | 2026-03-30 | 2026-03-30 | 2.28 | Pressure transmitters were calibrated. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Water injection system |  | Yes
Q3 | March 2026 | Mayaguez 3A | Unit was not injecting water. | 2026-03-30 | 2026-03-31 | 17.42 | A flow meter replacement was performed. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Water injection system |  | Yes
Q3 | March 2026 | Aguirre CC 2-1 | Fuel control issue. | 2026-03-31 | 2026-03-31 | 2 | Work in progress. | Fuel system | Fuel control |  | Yes
Q3 | March 2026 | Palo Seco 4 | Fuel pump 4-1 safety trip due to high amperage. | 2026-03-31 | 2026-03-31 | 2.5 | Fuel pump 3-2 was put in service. Fuel pump 4-1 will be swapped out. | Fuel system | Fuel pump 4-1 |  | Yes
Q3 | March 2026 | San Juan TM 2 | Lube oli system problems | 2026-03-31 | 2026-03-31 | 0.62 | Verified generator oil levels and the connection to the oil level transmitter. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Lube oil system |  | Yes
Q4 | April 2026 | Aguirre CC 2-1 | Trip unit by fuel control. | 2026-04-01 | 2026-04-02 | 22.4 | Changed the TCQC board, which had low voltage and did not reach the fuel bypass valve control (LVDT). From the terminal block (QTBA), all cables associated with the natrual gas system were removed. | Fuel system | Fuel control trip |  | Yes
Q4 | April 2026 | San Juan TM 2 | Node fault. | 2026-04-02 | 2026-04-02 | 1.35 | System cleaned. | Controls, instrumentation and protection | Control node fault |  | Yes
Q4 | April 2026 | San Juan TM 7 | Undiagnostic trip. | 2026-04-02 | 2026-04-02 | 3.52 | Unit restarted. | Undetermined | Undiagnosed trip |  | Yes
Q4 | April 2026 | Aguirre CC 2-1 | Trip unit by fuel control. | 2026-04-06 | 2026-04-07 | 17.3 | Changed the solenoid of the fuel bypass valve. Finished removing the cables associated with natural gas on the terminal block (QTBA). | Fuel system | Fuel control trip |  | Yes
Q4 | April 2026 | Mayaguez 3A | Unit was out due to a flame trip. | 2026-04-06 | 2026-04-06 | 3.2 | A software reset was made. | Ignition and flame detection | Flame trip |  | Yes
Q4 | April 2026 | Mayaguez 4B | Unit trip due to a no light. | 2026-04-06 | 2026-04-07 | 24.1 | A replacement of the igniters was made. | Ignition and flame detection | Igniters (no light) |  | Yes
Q4 | April 2026 | Palo Seco MP 3 | Combustor replacement needed. | 2026-04-06 | 2026-04-24 | 439.92 | Replacement completed. | Gas turbine combustion, compressor and hot section | Combustor |  | Yes
Q4 | April 2026 | Aguirre CC 2-1 | Trip unit by fuel control. | 2026-04-07 | 2026-04-08 | 18.7 | Changed the solenoid block. | Fuel system | Fuel control trip |  | Yes
Q4 | April 2026 | Palo Seco MP 1 | Turbine lubrication motor failed. | 2026-04-07 | 2026-04-07 | 5.88 | Replacement motor installed; scavenged from MP 3 unit. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Lube oil motor |  | Yes
Q4 | April 2026 | Aguirre CC 2-1 | Trip unit by fuel control. | 2026-04-08 | 2026-04-08 | 1.9 | Disconnected RVDT #1 from the inlet guide vanes that was affecting the circuit. | Fuel system | Fuel control trip |  | Yes
Q4 | April 2026 | Palo Seco 1-2 | High exhaust temperature fuel nozzles need replacement. | 2026-04-09 | 2026-04-10 | 20 | Fuel nozzles replaced. | Fuel system | Fuel nozzles |  | Yes
Q4 | April 2026 | Palo Seco 4 | Boiler lead leak. | 2026-04-09 | 2026-04-10 | 25.02 | The leak was corrected in the Boiler lead. | Boiler pressure parts | Boiler lead leak (valve packing) |  | Yes
Q4 | April 2026 | Mayaguez 4B | The secondary fans located in the pump compartments have failed. | 2026-04-10 | 2026-04-10 | 0.25 | A software reset was made. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Pump compartment secondary fans |  | Yes
Q4 | April 2026 | Costa Sur 5 | Platen superheater issue. | 2026-04-11 | 2026-04-15 | 95.89 | Boiler repaired, hydrostatic performed and unit synchronized. | Boiler pressure parts | Platen superheater |  | Yes
Q4 | April 2026 | Mayaguez 4A | The unit exhibited a back pressure issue. This is typically caused by the fuel injection system, water injection system, or bleed valves that may or may not have opened at a specific point in time. A trendline analysis was performed to graphically identify the problem, and no discrepancies were found. | 2026-04-11 | 2026-04-30 | 460.03 | The data was sent to Mitsubishi. They instructed to calibrate the pressure transmitters and temperature sensors (TE). The process was been completed, and we are pending approval from Mitsubishi. Also, a boroscope inspection was made. | Fuel system | Fuel injection back pressure | Affected Mayaguez 4B | Yes
Q4 | April 2026 | Aguirre 2 | Unit tripped due to loss of condenser vacuum - Vacuum Pump 2-1 coupling failure. | 2026-04-12 | 2026-04-12 | 2.6 | Unit was returned to service limited to 20MW due to low condenser operating vacuum conditions. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Condenser vacuum pump 2-1 |  | Yes
Q4 | April 2026 | Aguirre 2 | Unit tripped due to loss of condenser vacuum - Vacuum Pump 2-1 operating issues. | 2026-04-13 | 2026-04-13 | 2.55 | Vacuump Pump 2-1 was troubleshooted in order to normalize the main condenser vacuum operating conditions. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Condenser vacuum pump 2-1 |  | Yes
Q4 | April 2026 | Mayaguez 4B | Because Unit A was under a boroscope inspection, unit B was not available. | 2026-04-14 | 2026-04-14 | 7.7 | Because Unit A was under a boroscope inspection, unit B was not available. | Event at another unit (companion or shared equipment) | Companion engine 4A boroscope inspection | Caused by Mayaguez 4A | No
Q4 | April 2026 | Costa Sur 5 | Rotor collector rings issue. | 2026-04-15 | 2026-04-15 | 12.3 | Brush holder area cleaning performed and unit synchronized. | Generator, excitation and output bus | Rotor collector rings |  | Yes
Q4 | April 2026 | Mayaguez 4B | Because Unit A was under a boroscope inspection, unit B was not available. | 2026-04-15 | 2026-04-15 | 8.93 | Because Unit A was under a boroscope inspection, unit B was not available. | Event at another unit (companion or shared equipment) | Companion engine 4A boroscope inspection | Caused by Mayaguez 4A | No
Q4 | April 2026 | Palo Seco 4 | Broken Boiler lines. | 2026-04-16 | 2026-04-20 | 104.28 | Lines were fixed. | Boiler pressure parts | Boiler tube failure |  | Yes
Q4 | April 2026 | Palo Seco TM 2 | Loss of 480V. | 2026-04-17 | 2026-04-18 | 5.65 | Repairs completed. | Electrical (breakers, transformers, DC and auxiliary power) | Loss of 480 V power |  | Yes
Q4 | April 2026 | Daguao 1-1 | Circuit breaker 0010 opened. | 2026-04-18 | 2026-04-19 | 37.8 | Luma staff reset breaker and closed it. | Outside the plant (LUMA switchyard, grid, third-party fuel supply) | Switchyard breaker 0010 (LUMA) | Same event: Daguao 1-2 | No
Q4 | April 2026 | Daguao 1-2 | Circuit breaker 0010 opened. | 2026-04-18 | 2026-04-19 | 37.8 | Luma staff reset breaker and closed. | Outside the plant (LUMA switchyard, grid, third-party fuel supply) | Switchyard breaker 0010 (LUMA) | Same event: Daguao 1-1 | No
Q4 | April 2026 | Mayaguez 4B | Unit was out due to a LUMA Switchyard open 0080 breaker. | 2026-04-19 | 2026-04-19 | 3.47 | LUMA personnel worked on Breaker 0080. | Outside the plant (LUMA switchyard, grid, third-party fuel supply) | Switchyard breaker 0080 (LUMA) |  | No
Q4 | April 2026 | Costa Sur 6 | Main stop valves issue. | 2026-04-20 | 2026-04-30 | 247.3 | Pending repair of main steam inlet valves to the turbine. | Steam and turbine valves | Main stop valves |  | Yes
Q4 | April 2026 | San Juan CT 5 | Fire protection trip. | 2026-04-21 | 2026-04-21 | 5.3 | Incorrect signal system failure, instrumentation section bypass logic, unit back online. | Fire protection | False fire protection signal (water intrusion) | Affected San Juan ST 5 | Yes
Q4 | April 2026 | San Juan CT 5 | Blade path temperature trip. | 2026-04-21 | 2026-04-21 | 0.85 | The automatic regulator failed. The regulator was bypassed and the system operated through the manual valve. | Controls, instrumentation and protection | Blade path temperature regulator | Affected San Juan ST 5 | Yes
Q4 | April 2026 | San Juan ST 5 | Fire protection trip. | 2026-04-21 | 2026-04-21 | 10.97 | Incorrect signal system failure, instrumentation section bypass logic, unit back online. | Event at another unit (companion or shared equipment) | Trip of combustion turbine 5 (fire protection signal) | Caused by San Juan CT 5 | No
Q4 | April 2026 | San Juan ST 5 | Blade path temperature trip. | 2026-04-21 | 2026-04-21 | 3.2 | The automatic regulator failed. The regulator was bypassed and the system operated through the manual valve. | Event at another unit (companion or shared equipment) | Trip of combustion turbine 5 (blade path temperature) | Caused by San Juan CT 5 | No
Q4 | April 2026 | Daguao 1-1 | Ground fault main power transformer. Water ingress in connection box. | 2026-04-22 | 2026-04-24 | 53.15 | Cleaned, painted and replaced lid gasket preventive maintenace was performed. | Electrical (breakers, transformers, DC and auxiliary power) | Main power transformer ground fault (water ingress) | Same event: Daguao 1-2 | Yes
Q4 | April 2026 | Daguao 1-2 | Ground fault main power transformer. Water ingress in connection box. | 2026-04-22 | 2026-04-24 | 53.15 | Cleaning, Painting and replaced cover gasket. | Electrical (breakers, transformers, DC and auxiliary power) | Main power transformer ground fault (water ingress) | Same event: Daguao 1-1 | Yes
Q4 | April 2026 | Mayaguez 4B | Unit 4A was under a pressure transmiter and temperature sensor calibration. Therefore Unit 4B was out. | 2026-04-22 | 2026-04-22 | 0.52 | Pressure transmitter and temperature sensor calibrated. | Event at another unit (companion or shared equipment) | Companion engine 4A sensor calibration | Caused by Mayaguez 4A | No
Q4 | April 2026 | San Juan TM 2 | Regas working relief valve. | 2026-04-25 | 2026-04-25 | 2.6 | Regas finished work. | Outside the plant (LUMA switchyard, grid, third-party fuel supply) | Regasification relief valve work (fuel supply) | Same event: San Juan TM 3 and TM 4 | No
Q4 | April 2026 | San Juan TM 3 | Regas working relief valve. | 2026-04-25 | 2026-04-25 | 2.6 | Regas finished work. | Outside the plant (LUMA switchyard, grid, third-party fuel supply) | Regasification relief valve work (fuel supply) | Same event: San Juan TM 2 and TM 4 | No
Q4 | April 2026 | San Juan TM 4 | Regas working relief valve. | 2026-04-25 | 2026-04-25 | 2.6 | Regas finished work. | Outside the plant (LUMA switchyard, grid, third-party fuel supply) | Regasification relief valve work (fuel supply) | Same event: San Juan TM 2 and TM 3 | No
Q4 | April 2026 | Palo Seco 1-2 | Fuel line leak. | 2026-04-27 | 2026-04-27 | 1.37 | Fuel line replaced. | Fuel system | Fuel line leak |  | Yes
Q4 | April 2026 | Palo Seco 4 | Broken Boiler lines. | 2026-04-27 | 2026-04-30 | 76.13 | Lines were fixed. | Boiler pressure parts | Boiler tube failure |  | Yes
Q4 | April 2026 | Mayaguez 2A | Unit trip due a erratic pressure differential in a scavange line. | 2026-04-28 | 2026-04-30 | 52.62 | Unit 2A was disengaged in order to have online 2B. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Lube oil scavenge line pressure | Affected Mayaguez 2B | Yes
Q4 | April 2026 | Mayaguez 2B | Because Unit 2A PT621 trip. Unit 2B can’t be online due to a high oil leak on 2A. | 2026-04-28 | 2026-04-30 | 24.1 | Unit 2A decoupled to keep Unit 2B available. | Event at another unit (companion or shared equipment) | Companion engine 2A oil leak | Caused by Mayaguez 2A | No
Q4 | April 2026 | Mayaguez 4B | Unit out of service due to a permissive alarm on 4A. The alarm is related to metal and carbon particles in the filters and chip detectors. | 2026-04-28 | 2026-04-29 | 17.28 | Unit 4A was disengaged in order to have unit 4B online. | Event at another unit (companion or shared equipment) | Companion engine 4A permissive alarm | Caused by Mayaguez 4A | No
Q4 | April 2026 | Palo Seco 1-2 | Fuel line leak. | 2026-04-28 | 2026-04-29 | 26.43 | Fuel line replaced. | Fuel system | Fuel line leak |  | Yes
Q4 | April 2026 | San Juan TM 2 | Node fault. | 2026-04-28 | 2026-04-30 | 53.48 | System cleaned. | Controls, instrumentation and protection | Control node fault |  | Yes
Q4 | April 2026 | San Juan TM 2 | Node fault. | 2026-04-28 | 2026-04-28 | 0.73 | System cleaned. | Controls, instrumentation and protection | Control node fault |  | Yes
Q4 | April 2026 | Palo Seco TM 2 | VSV Driver failure. | 2026-04-29 | 2026-04-30 | 14.2 | VSV Pumps replaced. | Controls, instrumentation and protection | Variable stator vane driver |  | Yes
Q4 | April 2026 | Daguao 1-1 | Tripped due to fuel flow divider issues. | 2026-04-30 | 2026-04-30 | 0.47 | Calibrate and Master reset. | Fuel system | Fuel flow divider |  | Yes
Q4 | May 2026 | San Juan TM 2 | Node n-1 issues. | 2026-05-01 | 2026-05-04 | 72.5 | System cleaned and reset. | Controls, instrumentation and protection | Control node fault |  | Yes
Q4 | May 2026 | Mayaguez 2B | Flame out trip. | 2026-05-02 | 2026-05-02 | 6.73 | A reset was performed. | Ignition and flame detection | Flame out (igniters) |  | Yes
Q4 | May 2026 | Cambalache 3 | Engine trip by low frequency. Electrical grid disturbance originated in Costa Sur 6 unit. | 2026-05-04 | 2026-05-04 | 2.17 | None. Out of Management Control (OMC) event for Cambalache plant. | Outside the plant (LUMA switchyard, grid, third-party fuel supply) | Grid disturbance (low frequency) originated at Costa Sur 6 | Caused by Costa Sur 6 | No
Q4 | May 2026 | Costa Sur 6 | Unit 6 on 100% Bunker C. Bunker C control valve water accumulator broke apart causing the valve to shut instantaneously. This also caused a master fuel trip and tripped the Boiler and the unit out of service. | 2026-05-04 | 2026-05-04 | 1.85 | Water accumulator eliminated from the instrumentation line supply and proceeded with the synchronization of the unit. | Fuel system | Bunker C control valve water accumulator | Affected Cambalache 3 | Yes
Q4 | May 2026 | San Juan TM 2 | Node n-1 issues. | 2026-05-04 | 2026-05-06 | 43.83 | System cleaned and reset. | Controls, instrumentation and protection | Control node fault |  | Yes
Q4 | May 2026 | Jobos 1-2 | Transformer 4003 out of service. Breaker 0010 open. | 2026-05-05 | 2026-05-05 | 8.1 | Luma corrected the fault in the transformer and closed breaker 0010. Out of Management Control (OMC) event for GeneraPR. | Outside the plant (LUMA switchyard, grid, third-party fuel supply) | Transformer 4003 and breaker 0010 (LUMA) |  | No
Q4 | May 2026 | Mayaguez 2B | Flame out trip. | 2026-05-06 | 2026-05-06 | 14.95 | The igniters were cleaned and swapped out. | Ignition and flame detection | Flame out (igniters) |  | Yes
Q4 | May 2026 | San Juan TM 2 | Node n-1 issues. | 2026-05-08 | 2026-05-12 | 86.47 | System cleaned and reset. | Controls, instrumentation and protection | Control node fault |  | Yes
Q4 | May 2026 | Palo Seco 4 | Broken Boiler. | 2026-05-10 | 2026-05-13 | 64.62 | Corrected. | Boiler pressure parts | Boiler tube failure |  | Yes
Q4 | May 2026 | Mayaguez 3A | The Hydraulic System started a Permissive trip. | 2026-05-11 | 2026-05-11 | 1.72 | A reset was performed. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Hydraulic system permissive |  | Yes
Q4 | May 2026 | San Juan TM 2 | Node n-1 issues. | 2026-05-12 | 2026-05-14 | 47.03 | System cleaned and reset. | Controls, instrumentation and protection | Control node fault |  | Yes
Q4 | May 2026 | Mayaguez 3A | Uni 3B was being aligned, therefore unit 3A was unavailable. | 2026-05-15 | 2026-05-16 | 32.42 | Alignment completed. | Event at another unit (companion or shared equipment) | Companion engine 3B alignment | Caused by Mayaguez 3B | No
Q4 | May 2026 | San Juan TM 2 | Node n-1 issues. | 2026-05-15 | 2026-05-21 | 146.55 | System cleaned and reset. | Controls, instrumentation and protection | Control node fault |  | Yes
Q4 | May 2026 | Mayaguez 3B | Unit 3B PB DOT trip. A boroscope was performed. Also pressure transmitters were high. Those are related with the scavange. | 2026-05-18 | 2026-05-29 | 262.13 | A boroscope was performed. Pressure Transmitters were calibrated, solenoid valve were replaced. | Controls, instrumentation and protection | Pressure transmitters (PB DOT trip) |  | Yes
Q4 | May 2026 | Aguirre CC 2-4 | Unit tripped when synchronizing by Inlet Guide Vane Control Trouble trip. | 2026-05-19 | 2026-05-19 | 0.8 | The L4IGVT signal was forced. | Controls, instrumentation and protection | Inlet guide vane control |  | Yes
Q4 | May 2026 | San Juan TM 10 | Lost of mega vars controls. | 2026-05-19 | 2026-05-19 | 2.62 | Inspected and reset. | Controls, instrumentation and protection | Reactive power (MVAR) control |  | Yes
Q4 | May 2026 | Palo Seco 3 | Broken Boiler. | 2026-05-21 | 2026-05-31 | 250.85 | Corrected. | Boiler pressure parts | Boiler tube failure |  | Yes
Q4 | May 2026 | San Juan 9 | Electrical failure on Boiler Feed Pump 9-2. | 2026-05-23 | 2026-05-25 | 49.08 | Checked connections on Boiler Feed Pump 9-2 and certified a burned motor. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Boiler feed pump 9-2 motor |  | Yes
Q4 | May 2026 | San Juan TM 10 | N1n5 node fault. | 2026-05-23 | 2026-05-23 | 3.48 | Cleaned and reset. | Controls, instrumentation and protection | Control node fault |  | Yes
Q4 | May 2026 | Aguirre CC 2-2 | Unit tripped over temperature exhaust gases, EX 2100 trip, Generator lockout, and external trip. Unit went up to 61 MW when Costa Sur 5 tripped. | 2026-05-25 | 2026-05-25 | 0.7 | The unit was normalized and put into service. | Controls, instrumentation and protection | Exhaust over-temperature and EX2100 protection trip | Same event: Aguirre CC 2-4 | Yes
Q4 | May 2026 | Aguirre CC 2-4 | Unit tripped over temperature exhaust gases, EX 2100 trip, Generator lockout, and external trip. Unit went up to 61 MW when Costa Sur 5 tripped. | 2026-05-25 | 2026-05-25 | 0.9 | The unit was normalized and ran at 3,600 rpm, LUMA TOC did not want it in service. | Controls, instrumentation and protection | Exhaust over-temperature and EX2100 protection trip | Same event: Aguirre CC 2-2 | Yes
Q4 | May 2026 | Costa Sur 5 | MKVI activated the prot trip. | 2026-05-25 | 2026-05-28 | 63.13 | Checked the internal and termination wiring, also the circuit for the MKVI cabinet and proceeded with the synchronization of the unit. | Controls, instrumentation and protection | Mark VI protection trip |  | Yes
Q4 | May 2026 | San Juan TM 3 | Main breaker failure. | 2026-05-25 | 2026-05-25 | 2.1 | Breaker fixed. | Shared plant equipment (one event affected three or more units) | Main transformer breaker | Same event: San Juan TM 5 and TM 7 | No
Q4 | May 2026 | San Juan TM 5 | Main breaker failure. | 2026-05-25 | 2026-05-25 | 2.1 | Breaker fixed. | Shared plant equipment (one event affected three or more units) | Main transformer breaker | Same event: San Juan TM 3 and TM 7 | No
Q4 | May 2026 | San Juan TM 7 | Main breaker failure. | 2026-05-25 | 2026-05-25 | 2.1 | Breaker fixed. | Shared plant equipment (one event affected three or more units) | Main transformer breaker | Same event: San Juan TM 3 and TM 5 | No
Q4 | May 2026 | San Juan TM 10 | Breaker issue. | 2026-05-25 | 2026-05-26 | 27.98 | Breaker repaired. | Electrical (breakers, transformers, DC and auxiliary power) | Generator breaker (52G) contactor |  | Yes
Q4 | May 2026 | San Juan TM 2 | Node n-1 issues. | 2026-05-28 | 2026-05-31 | 79.48 | System cleaned and reset. | Controls, instrumentation and protection | Control node fault |  | Yes
Q4 | May 2026 | San Juan TM 2 | Node n-1 issues. | 2026-05-28 | 2026-05-28 | 0.83 | System cleaned and reset. | Controls, instrumentation and protection | Control node fault |  | Yes
Q4 | May 2026 | Mayaguez 3B | Pressure Transmitters remained high. | 2026-05-29 | 2026-05-30 | 19.57 | A loose fitting was found. | Controls, instrumentation and protection | Pressure transmitters (loose fitting) |  | Yes
Q4 | May 2026 | Aguirre CC 1-1 | Unit trip due to exhaust blower 1-1B output. | 2026-05-30 | 2026-05-30 | 0.7 | The unit was available with the exhaust blower 1-1A. The next day the motor was changed to 1-1B. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Exhaust blower 1-1B |  | Yes
Q4 | June 2026 | Aguirre CC 1-1 | Unit trip over temperature exahust gases (spread trip). | 2026-06-01 | 2026-06-01 | 2.1 | Themocouples #4 and #12 they crossed the signal with thermocouple #5 and #1, respectively. Another day they were changed. | Controls, instrumentation and protection | Exhaust thermocouples (spread trip) |  | Yes
Q4 | June 2026 | Mayaguez 3A | Inspection revealed that the starter of Unit 3B was damaged. Prior to this finding, the operators had shutted down both units 3A & 3B due to abnormal noise originating from within the equipment. | 2026-06-01 | 2026-06-01 | 0.52 | After confirming that the source of the noise was the starter of Unit 3B, Unit 3A was released for operation and placed back into service. | Event at another unit (companion or shared equipment) | Companion engine 3B starter | Caused by Mayaguez 3B | No
Q4 | June 2026 | Mayaguez 3B | Inspection revealed that the starter of Unit 3B was damaged. Prior to this finding, the operators had shutted down both units 3A & 3B due to abnormal noise originating from within the equipment. | 2026-06-01 | 2026-06-02 | 15.12 | Starter was replaced. | Starting system | Starter | Affected Mayaguez 3A | Yes
Q4 | June 2026 | Palo Seco 3 | Broken Boiler. | 2026-06-01 | 2026-06-04 | 61.58 | Leaks corrected. | Boiler pressure parts | Boiler tube failure |  | Yes
Q4 | June 2026 | San Juan TM 6 | Synchronizer fail. | 2026-06-02 | 2026-06-02 | 0.83 | Synchonizer fixed. | Controls, instrumentation and protection | Synchronizer |  | Yes
Q4 | June 2026 | Daguao 1-1 | Generator Voltage Control trouble. | 2026-06-03 | 2026-06-03 | 0.2 | The Unit was repaired and brought back online. | Generator, excitation and output bus | Generator voltage control |  | Yes
Q4 | June 2026 | Aguirre CC 2-1 | It was not a unit trip. When taking baterry bank 2-1 out of service, breaker 0012 and 0014 opened on the 230kv. | 2026-06-04 | 2026-06-04 | 2.7 | Battery bank 2-1 was put into service, 2 fuses on the UPS were replaced, and the trip coil on the incomming breaker 2A (4.16kv) was changed. | Shared plant equipment (one event affected three or more units) | Battery bank 2-1 (DC system) | Same event: Aguirre CC 2-2 and 2-4 | No
Q4 | June 2026 | Aguirre CC 2-2 | It was not a unit trip. When taking baterry bank 2-1 out of service, breaker 0012 and 0014 opened on the 230kv. | 2026-06-04 | 2026-06-04 | 2.7 | Battery bank 2-1 was put into service, 2 fuses on the UPS were replaced, and the trip coil on the incomming breaker 2A (4.16kv) was changed. | Shared plant equipment (one event affected three or more units) | Battery bank 2-1 (DC system) | Same event: Aguirre CC 2-1 and 2-4 | No
Q4 | June 2026 | Aguirre CC 2-4 | It was not a unit trip. When taking baterry bank 2-1 out of service, breaker 0012 and 0014 opened on the 230kv. | 2026-06-04 | 2026-06-04 | 2.7 | Battery bank 2-1 was put into service, 2 fuses on the UPS were replaced, and the trip coil on the incomming breaker 2A (4.16kv) was changed. | Shared plant equipment (one event affected three or more units) | Battery bank 2-1 (DC system) | Same event: Aguirre CC 2-1 and 2-2 | No
Q4 | June 2026 | San Juan TM 2 | Node n-1 issues. | 2026-06-04 | 2026-06-09 | 120.55 | System inspected and reset. | Controls, instrumentation and protection | Control node fault |  | Yes
Q4 | June 2026 | Jobos 1-2 | The turbine does not slow down enought to start. | 2026-06-07 | 2026-06-09 | 45.63 | Valve replacement 20 TU. | Starting system | Valve 20TU (unit does not slow down to start) |  | Yes
Q4 | June 2026 | Daguao 1-2 | Diesel leak at nozzle number 5. | 2026-06-09 | 2026-06-09 | 0.55 | The leak was repaired and brought back online. | Fuel system | Fuel nozzles |  | Yes
Q4 | June 2026 | Mayaguez 3A | One of the PLC cards failed, resulting in erroneous readings from PT501/PT502, which caused the unit to trip, as well as incorrect readings from other pressure transmitters, including PT1011 and PT1012. | 2026-06-09 | 2026-06-09 | 4.73 | The defective card was identified and replaced, restoring normal operation. | Controls, instrumentation and protection | PLC card | Same event: Mayaguez 3B | Yes
Q4 | June 2026 | Mayaguez 3B | One of the PLC cards failed, resulting in erroneous readings from PT501/PT502, which caused the unit to trip, as well as incorrect readings from other pressure transmitters, including PT1011 and PT1012. | 2026-06-09 | 2026-06-09 | 5.15 | The defective card was identified and replaced, restoring normal operation. | Controls, instrumentation and protection | PLC card | Same event: Mayaguez 3A | Yes
Q4 | June 2026 | Daguao 1-2 | High exhaust temperature spread. | 2026-06-11 | 2026-06-14 | 71.52 | The nozzles were replaced with new nozzles. | Fuel system | Fuel nozzles |  | Yes
Q4 | June 2026 | Aguirre CC 2-1 | Unit trip with output bars explore. | 2026-06-13 | 2026-06-18 | 131.8 | Completed, the output bars were removed, the insulation was changed and bars were cleaned. A test was perfomed on the transformer. | Generator, excitation and output bus | Generator output bars | Affected Aguirre CC 2-2 and 2-4 | Yes
Q4 | June 2026 | Aguirre CC 2-2 | Unit trip when U2-1 output bars explode. Lockout generator. | 2026-06-13 | 2026-06-14 | 33.9 | The U2-1 output bars were diconnected to isolate the fault. | Event at another unit (companion or shared equipment) | Aguirre CC 2-1 output bars fault | Caused by Aguirre CC 2-1 | No
Q4 | June 2026 | Aguirre CC 2-4 | It was not a unit trip, it was out of service when the fault occurred in the U2-1 output bars. | 2026-06-13 | 2026-06-13 | 2.6 | Completed, MOD 0015 was opened to isolate the fault and be able to energize the 230kv. | Event at another unit (companion or shared equipment) | Aguirre CC 2-1 output bars fault | Caused by Aguirre CC 2-1 | No
Q4 | June 2026 | Mayaguez 3A | Switchyard breaker 0010 opened while the unit was in operation, resulting in a unit shutdown/trip. | 2026-06-13 | 2026-06-13 | 0.95 | LUMA was requested to reclose the breaker, as it falls under their area of responsibility. A subject matter expert later identified that the issue was caused by an Main Power Transformer relay associated with the step-up transformer (13.8 kV/115 kV). The issue was successfully resolved. | Outside the plant (LUMA switchyard, grid, third-party fuel supply) | Switchyard breaker 0010 (LUMA) | Same event: Mayaguez 3B | No
Q4 | June 2026 | Mayaguez 3B | Switchyard breaker 0010 opened while the unit was in operation, resulting in a unit shutdown/trip. | 2026-06-13 | 2026-06-13 | 0.95 | LUMA was requested to reclose the breaker, as it falls under their area of responsibility. A subject matter expert later identified that the issue was caused by an MPT relay associated with the step-up transformer (13.8 kV/115 kV). The issue was successfully resolved. | Outside the plant (LUMA switchyard, grid, third-party fuel supply) | Switchyard breaker 0010 (LUMA) | Same event: Mayaguez 3A | No
Q4 | June 2026 | Daguao 1-2 | The water supply line to the speed reducer broke. | 2026-06-14 | 2026-06-14 | 3.78 | The water line was repaired and returned to service. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Speed reducer cooling water line |  | Yes
Q4 | June 2026 | Daguao 1-2 | Flame detector failure the unit was cycling on and off. | 2026-06-15 | 2026-06-15 | 3.25 | The flame detector cable was found broke, it was replaced. | Ignition and flame detection | Flame detector |  | Yes
Q4 | June 2026 | San Juan 9 | Fire on burner corner C. | 2026-06-17 | 2026-06-30 | 331.33 | Repairs in progress. | Burners and firing | Burner fire (corner C) |  | Yes
Q4 | June 2026 | Aguirre CC 2-2 | Unit trips when it syncs U2-1 for generator lockkout and relay 64G-2. Only one unit can be in service, going out through MPT 2-1/2-2. | 2026-06-18 | 2026-06-24 | 139.9 | After the U2-1 exciter explosion, it disconnected from the transformer and the relays of the U2-2 generator were calibrated. | Event at another unit (companion or shared equipment) | Aguirre CC 2-1 generator lockout (relay 64G-2) | Caused by Aguirre CC 2-1 | No
Q4 | June 2026 | Cambalache 2 | Unavailability of the turbine's CO2 fire protection system. For safety reasons, the unit cannot operate without a fire protection system. | 2026-06-18 | 2026-06-26 | 198.61 | Repair on compressor and filling of the CO2 tank of the turbine fire protection system. | Fire protection | CO2 fire protection system (compressor) | Same event: Cambalache 3 | Yes
Q4 | June 2026 | Cambalache 3 | Unavailability of the turbine's CO2 fire protection system. For safety reasons, the unit cannot operate without a fire protection system. | 2026-06-18 | 2026-06-26 | 198.61 | Repair on compressor and filling of the CO2 tank of the turbine fire protection system. | Fire protection | CO2 fire protection system (compressor) | Same event: Cambalache 2 | Yes
Q4 | June 2026 | Daguao 1-2 | Flame detector fault, causing the unit to trip. | 2026-06-18 | 2026-06-18 | 6.58 | The flame detector were removed, cleaned and the unit was returned to service. | Ignition and flame detection | Flame detector |  | Yes
Q4 | June 2026 | Daguao 1-1 | Ignition cable broke, preventing the unit from starting. | 2026-06-19 | 2026-06-19 | 3.83 | The ignition cables were replaced, and the unit was returned to service. | Ignition and flame detection | Ignition cable |  | Yes
Q4 | June 2026 | Daguao 1-1 | High exhaust temperature spread. | 2026-06-20 | 2026-06-20 | 2.83 | Fuel check valves were replaced,and the unit was returned to service. | Fuel system | Fuel check valves |  | Yes
Q4 | June 2026 | Daguao 1-2 | Cooling system fan drive failure, causing the unit to trip on high temperature. | 2026-06-21 | 2026-06-21 | 3 | The fan system pins were repaired, and the unit was returned to service. | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Cooling fan drive |  | Yes
Q4 | June 2026 | Aguirre CC 2-1 | Unit trip due to generator and exciter fault. Generator and transfomer lockout activated, relay 87T-2 and 87G-2. | 2026-06-22 | 2026-06-30 | 193.2 | The unit was disconnected from the transformer to isolate the fault. | Generator, excitation and output bus | Generator and exciter fault | Affected Aguirre CC 2-2 and 2-4 | Yes
Q4 | June 2026 | Aguirre CC 2-4 | Unit trips due to the area exciter U2-1 explotion when the 230kv goes out. | 2026-06-22 | 2026-06-23 | 10.1 | Completed, MOD 0015 was opened to isolate the fault and be able to energize the 230kv. | Event at another unit (companion or shared equipment) | Aguirre CC 2-1 exciter failure | Caused by Aguirre CC 2-1 | No
Q4 | June 2026 | San Juan TM 7 | High temperature spread. | 2026-06-22 | 2026-06-23 | 17.08 | Technician replaced bolts. | Gas turbine combustion, compressor and hot section | Exhaust temperature spread (bolts replaced) |  | Yes
Q4 | June 2026 | San Juan TM 10 | Instrumentation fail. | 2026-06-23 | 2026-06-23 | 0.32 | System inspected and reset. | Controls, instrumentation and protection | Instrumentation |  | Yes
Q4 | June 2026 | Palo Seco 3 | Real air flow indicator bad signal caused trip. | 2026-06-24 | 2026-06-24 | 3.8 | Indicator corrected. | Controls, instrumentation and protection | Air flow indicator signal |  | Yes
Q4 | June 2026 | Palo Seco 1-2 | Igniter issues. | 2026-06-25 | 2026-06-27 | 41.93 | Reset igniter. | Ignition and flame detection | Igniters |  | Yes
Q4 | June 2026 | Palo Seco 1-2 | Igniter issues. | 2026-06-28 | 2026-06-29 | 25.75 | Reset igniter. | Ignition and flame detection | Igniters |  | Yes
Q4 | June 2026 | Palo Seco 1-2 | Fuel leak. | 2026-06-29 | 2026-06-30 | 27.12 | Corrected. | Fuel system | Fuel line leak |  | Yes
Q4 | June 2026 | Palo Seco 1-2 | Fuel leak. | 2026-06-30 | 2026-06-30 | 0.48 | Corrected. | Fuel system | Fuel line leak |  | Yes

## January 2026
January 2026
Unit | Description | Out Date | In Date | Duration (Hrs) | Corrective Action | Root Cause Analysis // Comments
Aguirre 2 | Unit tripped due to instrument air header pressure loss. | 2026-01-03 | 2026-01-03 | 10.48 | IACs were restored to normal operation (oil make-up completed), and the unit was successfully synchronized. | Root cause analysis: Exhibit 4, pp. 1–10.
Aguirre CC 1-2 | Continuation from previous month. The work continued on oil leak in the inlet guide vanes block. | 2026-01-01 | 2026-01-02 | 45 | The piston and inlet guide valve block were replaced. The fuel bypass valve solenoids were changed. | No separate root cause analysis was prepared. The inlet guide vane piston was repaired at the workshop (WO 15555077).
Aguirre CC 2-1 | Trip due to lockout generator, relay #40 (loss of excitation), external trip, and fuel. | 2026-01-18 | 2026-01-20 | 38.9 | Reset the EX2100 and calibrate the fuel bypass valve, a megger test was done on the generator, managed to raise the generator breaker that had tripped on one side. | No separate root cause analysis was prepared. The event was identified as an external trip (GRIP).
Aguirre CC 2-4 | Excitation problem, excitation loss, relay #40, and generator lockout. | 2026-01-29 | 2026-01-29 | 2.3 | The 180 ohms resistor in the excitation system of the exciter was replaced. The one from unit 2-3 was used. | No separate root cause analysis was prepared. An open-circuit 180-ohm resistor was found in the exciter excitation voltage system; the unit was tested at 30 MW and 5 Mvar with no issues (WO 1557643).
Costa Sur 5 | Feedwater valves | 2026-01-11 | 2026-01-25 | 343.08 | Heater #6 inlet valve repaired. | No separate root cause analysis was prepared. The heater 6 inlet valve was repaired (WR 63844, completed).
Costa Sur 5 | Boiler tube leaks platen superheater | 2026-01-27 | 2026-01-31 | 97.13 | Broken Boiler tubes repaired, hydrostatic test performed. | Root cause analysis: Exhibit 4 of Genera's October 8, 2026 filing, pp. 90–94.
Mayaguez 4B | The unit tripped due to secondary fan alarm. | 2026-01-11 | 2026-01-11 | 4.47 | Worked on the fan limit switch and alarm setting, and solved the issue. | Root cause analysis: Exhibit 4, pp. 19–20.
Mayaguez 4B | Water Injection Level Switch was damaged. | 2026-01-18 | 2026-01-20 | 41.37 | A water injection level switch was replaced. | Root cause analysis: Exhibit 4, pp. 21–22.
Palo Seco 1-2 | Starting System failure | 2026-01-24 | 2026-01-26 | 47.65 | Acceleration control valve in Diesel Engine replacement. | No separate root cause analysis was prepared.
Palo Seco MP 1 | DC Lube Oil Pump Generator failure. | 2026-01-23 | 2026-01-24 | 23.92 | Pump motor replacement. | No separate root cause analysis was prepared.
Palo Seco MP 2 | DC Lube oil Pump Generator failure. | 2026-01-03 | 2026-01-05 | 47.43 | Lube Oil Pump Motor replacement. | No separate root cause analysis was prepared.
Palo Seco MP 2 | Diesel fuel Pump Oil leak. | 2026-01-05 | 2026-01-06 | 17.53 | Pump Seal and packing replacement. | No separate root cause analysis was prepared.
Palo Seco MP 2 | AC lube oil motor failure. | 2026-01-16 | 2026-01-17 | 21.55 | AC pump motor replacement. | No separate root cause analysis was prepared.
Yabucoa 1-2 | Torque Converter failure. | 2026-01-25 | 2026-01-31 | 155 | During inspection, an SSS clutch failure was found. In process of replacement. | No separate root cause analysis was prepared.
Palo Seco TM 2 | Problems with Regas protection system, low gas supply pressure. | 2026-01-05 | 2026-01-05 | 0.55 | The gas plant normalized their pumps. | No separate root cause analysis was prepared.
San Juan CT 5 | Non-authorized works were done on Breaker 5E-1. Emergency Breaker was closed causing normal to open, then the emergency breaker was opened, leaving both breakers open. | 2026-01-21 | 2026-01-21 | 1.05 | Procedures were in place. Personnel was trained and advised. | Root cause analysis: Exhibit 4, pp. 35–42.
San Juan ST 5 | Non-authorized works were done on Breaker 5E-1. Emergency Breaker was closed causing normal to open, then the emergency breaker was opened, leaving both breakers open. | 2026-01-21 | 2026-01-26 | 118 | Procedures were in place. Personnel was trained and advised. | Root cause analysis: Exhibit 4, pp. 35–42.
San Juan CT 6 | Vacuum loss due to vacuum pump bravo uncoupling and discharge valve left open. | 2026-01-27 | 2026-01-27 | 3.2 | Vacuum pump bravo in repairs. | No separate root cause analysis was prepared. The vacuum pump coupling was replaced.
San Juan ST 5 | Vacuum loss due to vacuum pump bravo uncoupling and discharge valve left open. | 2026-01-27 | 2026-01-27 | 8.5 | Vacuum pump bravo in repairs. | No separate root cause analysis was prepared. The vacuum pump coupling was replaced.
San Juan 9 | Voltage regulator failed when switched from manual to auto. | 2026-01-30 | 2026-01-30 | 8.33 | Megger tests were done. No faults found. | No separate root cause analysis was prepared.
San Juan TM 1 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-31 | 193.17 | Work in progress. | Root cause analysis: Exhibit 4, pp. 43–50.
San Juan TM 2 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-27 | 114.35 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit. | Root cause analysis: Exhibit 4, pp. 43–50.
San Juan TM 2 | Lube oil system problems. | 2026-01-18 | 2026-01-18 | 2.05 | Replaced N47 relay switch. | No separate root cause analysis was prepared.
San Juan TM 3 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-27 | 114.35 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit. | Root cause analysis: Exhibit 4, pp. 43–50.
San Juan TM 4 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-26 | 91.53 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit. | Root cause analysis: Exhibit 4, pp. 43–50.
San Juan TM 5 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-24 | 44.02 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit. | Root cause analysis: Exhibit 4, pp. 43–50.
San Juan TM 5 | Gas leak on manifold, J-tubes and convoluted hoses. | 2026-01-23 | 2026-01-29 | 126.12 | Replaced gas manifold, J-tubes and convoluted hoses. | No separate root cause analysis was prepared.
San Juan TM 6 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-24 | 44.02 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit. | Root cause analysis: Exhibit 4, pp. 43–50.
San Juan TM 7 | Issue with the water injection pump. | 2026-01-13 | 2026-01-14 | 15.49 | The water injection pump was replaced. | No separate root cause analysis was prepared.
San Juan TM 7 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-24 | 44.02 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit. | Root cause analysis: Exhibit 4, pp. 43–50.
San Juan TM 10 | Due to a failure on the isolators from the metal clad cabinet near GT-01 the breaker on the Main Power Transformer opened causing a trip to the rest of the units. | 2026-01-22 | 2026-01-24 | 44.02 | The fault on the cabinet was isolated and proceeded to close the breaker on the Main Power Transformer. EDG#1 was repaired and 480v was available for auxiliary equipments on the unit. | Root cause analysis: Exhibit 4, pp. 43–50.

## February 2026
February 2026
Unit | Description | Out Date | In Date | Duration (Hrs) | Corrective Action | Root Cause Analysis // Comments
Aguirre 2 | Boiler tube leakage / waterwall area. | 2026-02-06 | 2026-02-09 | 81.3833 | Corrective Maintenance activities were performed. Unit was synchronized to the grid. | No separate root cause analysis was prepared. Boiler tubes were repaired and a hydrostatic test was performed.
Aguirre 2 | Boiler tube leakage / waterwall area. | 2026-02-24 | 2026-02-28 | 115.1833 | Corrective Maintenance activities were performed, including boiler air in leakage (ash hopper area). Unit was synchronized to the grid. | No separate root cause analysis was prepared. Boiler tubes were repaired and a hydrostatic test was performed (WO 01558307, completed).
Aguirre CC 2-1 | Exciter to Mark VIe communication fault. Ex2100 trip alarm. | 2026-02-25 | 2026-02-25 | 1.1 | EX2100 and Mark VIe were reset; unit was put in service. | No separate root cause analysis was prepared.
Costa Sur 5 | Generator neutral grounding equipment. | 2026-02-02 | 2026-02-02 | 3.99 | Cleaning and maintenance performed. | Root cause analysis: Exhibit 4, pp. 11–16.
Palo Seco 4 | High temperature in unit 3/4 server room. | 2026-02-17 | 2026-02-18 | 13.63 | Server room cooling system fixed. | No separate root cause analysis was prepared. New air conditioning units were acquired and are pending installation.
Palo Seco MP 2 | Lube Oil Presure Drain High Breeder. | 2026-02-18 | 2026-02-28 | 239.5 | In process of troubleshooting. | No separate root cause analysis was prepared.
Palo Seco MP 3 | Gen Lube Oil Pump Coupling failure. | 2026-02-21 | 2026-02-28 | 175.07 | Waiting for coupling delivery. | No separate root cause analysis was prepared.
Palo Seco 1-2 | Starting System failure, DC Control cable damage. | 2026-02-18 | 2026-02-20 | 46.5 | DC Control cable replaced. | No separate root cause analysis was prepared.
San Juan CT 5 | Bladepath variance. | 2026-02-07 | 2026-02-07 | 3.3 | Inspected and corrected. | Blade path temperature spread; see the root cause analysis of the April 21, 2026 blade path spread trip: Exhibit 4 of Genera's October 8, 2026 filing, pp. 155–163.
San Juan ST 5 | High vibrations. | 2026-02-07 | 2026-02-14 | 172.27 | Inspected and nothing found. | Root cause analysis: Exhibit 4, pp. 59–67.
San Juan 9 | Broken boiler lines. | 2026-02-15 | 2026-02-15 | 1.67 | Boiler lines fixed. | No separate root cause analysis was prepared. Boiler tubes were repaired and a hydrostatic test was performed.

## March 2026
March 2026
Unit | Description | Out Date | In Date | Duration (Hrs) | Corrective Action | Root Cause Analysis // Comments
Aguirre 2 | Boiler tube leakage / waterwall area. | 2026-03-01 | 2026-03-02 | 33.7 | Continuation of previous month. Corrective Maintenance activities were performed, including boiler air in leakage (ash hopper area). Unit was synchronized to the grid. | No separate root cause analysis was prepared. Boiler tubes were repaired and a hydrostatic test was performed (WO 01558307, completed).
Aguirre CC 2-1 | No progress in startup, relay activated and generator lockout. | 2026-03-10 | 2026-03-12 | 49.2 | Cable of the heater output bars. They repaired the heater cable, changed the insulation of the bars, and performed a megger test. | No separate root cause analysis was prepared. A loose heater cable was found in contact with the 13 kV busbar in the Unit 2-1 bus duct; the cable was removed, insulation was installed, and insulation resistance testing was performed (WO 1562049).
Aguirre CC 2-1 | Fuel control issue. | 2026-03-31 | 2026-03-31 | 2 | Work in progress. | No separate root cause analysis was prepared. Dirty filters were found (WO 1561470 and WO 1561574).
Aguirre CC 2-2 | No progress in startup, relay activated and generator lockout. It was unit 2-1 but the bars are joined at the outputs. | 2026-03-10 | 2026-03-12 | 49 | Cable of the heater output bars. They repaired the heater cable, changed the insulation of the bars, and performed a megger test. | No separate root cause analysis was prepared. A loose heater cable was found in contact with the 13 kV busbar in the Unit 2-1 bus duct; the cable was removed, insulation was installed, and insulation resistance testing was performed (WO 1562049).
Aguirre CC 2-2 | Forced unit shutdown because the Inlet Guide Vane (IGV) did not open. | 2026-03-21 | 2026-03-22 | 24.7 | Calibrated the IGV that were stuck and transmitters. | No separate root cause analysis was prepared. The servo valves were replaced and the RVDTs were adjusted and calibrated (WO 1563205).
Aguirre CC 2-4 | Unit did not start due to vibrations in bearing #1. | 2026-03-15 | 2026-03-15 | 1.6 | Changed the vibration sensor of bearing #1. | No separate root cause analysis was prepared.
Cambalache 2 | Stage 3 Blow-Off Valve failure. On March 1st, with the unit online at base load, an open valve alarm was triggered. The unit remained online in that condition until it was taken offline by the TOC. | 2026-03-02 | 2026-03-02 | 1.82 | Mechanical opening and closing tests of the valve were performed. The valve closing indicator switch was replaced. | Root cause analysis: Exhibit 4, pp. 17–18.
Cambalache 3 | Turbine Vane 3 broken shim | 2026-03-01 | 2026-03-10 | 234.73 | Class-C Service. Unit reassembly. Turbocharger balancing. Commissioning. | No separate root cause analysis was prepared. The unit was under inspection.
Cambalache 3 | Turbine Vane 3 broken shim | 2026-03-11 | 2026-03-11 | 14.5 | Class-C Service. Unit reassembly. Turbocharger balancing. Commissioning. | No separate root cause analysis was prepared. The unit was under inspection.
Cambalache 3 | Turbine Vane 3 broken shim | 2026-03-11 | 2026-03-13 | 42.47 | Class-C Service. Unit reassembly. Turbocharger balancing. Commissioning. | No separate root cause analysis was prepared. The unit was under inspection.
Cambalache 3 | Turbine Vane 3 broken shim | 2026-03-13 | 2026-03-14 | 21.88 | Class-C Service. Unit reassembly. Turbocharger balancing. Commissioning. | No separate root cause analysis was prepared. The unit was under inspection.
Cambalache 3 | Turbine Vane 3 broken shim | 2026-03-14 | 2026-03-15 | 22.07 | Class-C Service. Unit reassembly. Turbocharger balancing. Commissioning. | No separate root cause analysis was prepared. The unit was under inspection.
Cambalache 3 | Turbine Vane 3 broken shim | 2026-03-15 | 2026-03-16 | 20.27 | Class-C Service. Unit reassembly. Turbocharger balancing. Commissioning. | No separate root cause analysis was prepared. The unit was under inspection.
Mayaguez 4A | Unit was no available due to a major overhaul. The entire gas generator component was out. Gas generator includes: compressor, combustors and turbine. | 2026-03-01 | 2026-03-17 | 400.3 | Continuation of previous month. On March 5, the installation began. Tests were performed. | No separate root cause analysis was prepared. The unit was under inspection.
Mayaguez 4A | Unit Vacuum Pump was not working. Chip detetectors were lealing. | 2026-03-23 | 2026-03-23 | 4.25 | The replacemnt of the Vacuum Pump Equipment was performed. A torque adjustment were made in the lines of the chip detectors. | Root cause analysis: Exhibit 4, pp. 27–28.
Mayaguez 3A | Speed sensor was giving problems during turn down. | 2026-03-08 | 2026-03-08 | 11.23 | Calibration was performed. | Root cause analysis: Exhibit 4, pp. 23–24.
Mayaguez 3A | Speed sensor trip. | 2026-03-19 | 2026-03-19 | 11.77 | A reset was performed. | Root cause analysis: Exhibit 4, pp. 23–24.
Mayaguez 3A | Speed sensor trip. | 2026-03-21 | 2026-03-21 | 10.07 | A reset was performed. | Root cause analysis: Exhibit 4, pp. 23–24.
Mayaguez 3A | Speed sensor trip. | 2026-03-22 | 2026-03-22 | 10.38 | A reset was performed. | Root cause analysis: Exhibit 4, pp. 23–24.
Mayaguez 3A | Unit was not injecting water. | 2026-03-30 | 2026-03-30 | 2.28 | Pressure transmitters were calibrated. | Root cause analysis: Exhibit 4, pp. 25–26.
Mayaguez 3A | Unit was not injecting water. | 2026-03-30 | 2026-03-31 | 17.42 | A flow meter replacement was performed. | Root cause analysis: Exhibit 4, pp. 25–26.
Mayaguez 4B | The gas generator was being installed on Unit 4A, and the shaft connecting to the generator was also being aligned. This required a LOTO on the starter, which is limiting Unit 4B. | 2026-03-08 | 2026-03-12 | 97.22 | Once the shaft was installed and aligned, authorization was granted to remove the LOTO, releasing the starter and making Unit 4B available. | No separate root cause analysis was prepared.
Mayaguez 4B | An inspection on solenoid valve was conducted, taking advantage of the forced outage via circuit 4A. | 2026-03-23 | 2026-03-23 | 4.25 | It was determined that a change was needed. An order was placed. | Root cause analysis: Exhibit 4, pp. 29–30.
Mayaguez 4B | Unit trip due to flame out. | 2026-03-24 | 2026-03-25 | 23.13 | A governor solenoid was replaced. | Root cause analysis: Exhibit 4, pp. 31–32.
Mayaguez 4B | Solenoid valve failure. | 2026-03-26 | 2026-03-26 | 2.53 | The solenoid valve was replaced. | Root cause analysis: Exhibit 4, pp. 33–34.
San Juan TM 2 | Lube oli system problems | 2026-03-02 | 2026-03-02 | 0.42 | Verified generator oil levels and the connection to the oil level transmitter. | No separate root cause analysis was prepared.
San Juan TM 2 | Lube oli system problems | 2026-03-04 | 2026-03-04 | 12.22 | Verified generator oil levels and the connection to the oil level transmitter. | No separate root cause analysis was prepared.
San Juan TM 2 | Lube oli system problems | 2026-03-07 | 2026-03-07 | 0.45 | Verified generator oil levels and the connection to the oil level transmitter. | No separate root cause analysis was prepared.
San Juan TM 2 | Lube oli system problems | 2026-03-17 | 2026-03-17 | 0.32 | Verified generator oil levels and the connection to the oil level transmitter. | No separate root cause analysis was prepared.
San Juan TM 2 | Lube oli system problems | 2026-03-19 | 2026-03-19 | 1.5 | Verified generator oil levels and the connection to the oil level transmitter. | No separate root cause analysis was prepared.
San Juan TM 2 | Lube oli system problems | 2026-03-20 | 2026-03-20 | 1.33 | Verified generator oil levels and the connection to the oil level transmitter. | No separate root cause analysis was prepared.
San Juan TM 6 | NPT Hi Speed Derivative. | 2026-03-21 | 2026-03-21 | 0.58 | Replaced acelerometer | No separate root cause analysis was prepared.
San Juan TM 2 | Blackstart Diesel Fuel Pump Failure. | 2026-03-21 | 2026-03-26 | 116.72 | Removed diesel fuel pump, none available in stock. A 480v external feeder was rerouted from GT-05 Switchgear to energize auxiliary equipments. | No separate root cause analysis was prepared.
San Juan TM 3 | Blackstart Diesel Fuel Pump Failure. | 2026-03-21 | 2026-03-26 | 116.72 | Removed diesel fuel pump, none available in stock. A 480v external feeder was rerouted from GT-05 Switchgear to energize auxiliary equipments. | No separate root cause analysis was prepared.
San Juan TM 4 | Liquid fuel primary manifold thermocouple failure | 2026-03-25 | 2026-03-25 | 0.37 | Replaced thermocouple on primary manifold liquid fuel system. | No separate root cause analysis was prepared.
San Juan TM 2 | Lube oli system problems | 2026-03-31 | 2026-03-31 | 0.62 | Verified generator oil levels and the connection to the oil level transmitter. | No separate root cause analysis was prepared.
Jobos 1-2 | Torque converter failure | 2026-03-01 | 2026-03-03 | 65.3 | Continuation from previous month. During inspection, an SSS clutch failure was found; it was replaced. | No separate root cause analysis was prepared.
Jobos 1-2 | Synchronization failure. | 2026-03-03 | 2026-03-05 | 44.93 | Inspection, cleaning connections and load breaker. | No separate root cause analysis was prepared.
Jobos 1-2 | Gas turbine vibration. | 2026-03-08 | 2026-03-11 | 63.4 | During inspection we found the defective accesory shaft. This axle was replaced with a new one. | No separate root cause analysis was prepared.
Jobos 1-2 | Gas turbine loses speed reference. | 2026-03-29 | 2026-03-30 | 15.12 | Replacement of speed sensor connection terminal. | No separate root cause analysis was prepared.
Daguao 1-1 | Main Power Transformer failure. Lockout activated. | 2026-03-01 | 2026-03-14 | 312 | Transformer output bus cleaning, lightning protection, generator output bus cleaning and megger. | No separate root cause analysis was prepared.
Daguao 1-2 | Unit does not synchronize. | 2026-03-07 | 2026-03-10 | 73.3 | The synchronization control in the MCC was replaced. | No separate root cause analysis was prepared.
Palo Seco MP 1 | Gas leak and Gen LO failure. | 2026-03-22 | 2026-03-28 | 145.35 | Replaced Gen LO motor, a gas hose and seals. | No separate root cause analysis was prepared.
Palo Seco MP 3 | Turbine oil leak. | 2026-03-03 | 2026-03-04 | 31.5 | Replaced seal. | No separate root cause analysis was prepared.
Palo Seco 1-2 | Control system issue. | 2026-03-07 | 2026-03-09 | 47.87 | Replaced I/O board. | No separate root cause analysis was prepared.
Palo Seco 1-2 | Excitation problem. | 2026-03-15 | 2026-03-17 | 44.58 | Replacement of brushes, cleaning and alignment. | No separate root cause analysis was prepared.
San Juan 9 | Operation error during transformer switch. | 2026-03-16 | 2026-03-16 | 2.83 | System was checked and greenlit. | No separate root cause analysis was prepared. The procedure was revised and provided to the operator.
San Juan 9 | Circulating Water Pump 9-1 trip with bus bar B losing vaccum. | 2026-03-22 | 2026-03-28 | 147.4 | Boiler lines were fixed, swapped to circulating waster pump 9-2 while the 9-1 is in reparations. | Root cause analysis: Exhibit 4, pp. 51–58.
San Juan CT 5 | Fire protection system trip. | 2026-03-26 | 2026-03-26 | 5.92 | Found pullout box filled with rain water due to being broken and causing a short circuit and a false alarm. | Root cause analysis: Exhibit 4 of Genera's October 8, 2026 filing, pp. 148–154.
San Juan CT 5 | Hot reheat bypass issue. | 2026-03-08 | 2026-03-08 | 6.17 | Instrumentation section fixed. | No separate root cause analysis was prepared.
San Juan ST 5 | High vibration in bearing. | 2026-03-24 | 2026-03-25 | 20.97 | System checked and greenlit. | Same condition as the February 7, 2026 trip. Root cause analysis: Exhibit 4, pp. 59–67.
San Juan ST 5 | Fire protection system trip. | 2026-03-26 | 2026-03-26 | 9.35 | System inspected and cleaned. | Root cause analysis: Exhibit 4 of Genera's October 8, 2026 filing, pp. 148–154.
Palo Seco 4 | Fuel pump 4-1 safety trip due to high amperage. | 2026-03-31 | 2026-03-31 | 2.5 | Fuel pump 3-2 was put in service. Fuel pump 4-1 will be swapped out. | No separate root cause analysis was prepared. The Bunker C service pump was replaced.

## April 2026
April 2026 Forced Outages Report
Unit | Cause | Out Date | Time Out | In Date | Time In | Duration (Hrs) | Corrective Action
Aguirre 2 | Unit tripped due to loss of condenser vacuum - Vacuum Pump 2-1 coupling failure. | 2026-04-12 | 19:18 | 2026-04-12 | 21:54 | 2.6 | Unit was returned to service limited to 20MW due to low condenser operating vacuum conditions.
Aguirre 2 | Unit tripped due to loss of condenser vacuum - Vacuum Pump 2-1 operating issues. | 2026-04-13 | 14:12 | 2026-04-13 | 16:45 | 2.55 | Vacuump Pump 2-1 was troubleshooted in order to normalize the main condenser vacuum operating conditions.
Aguirre CC 2-1 | Trip unit by fuel control. | 2026-04-01 | 18:00 | 2026-04-02 | 16:25 | 22.4 | Changed the TCQC board, which had low voltage and did not reach the fuel bypass valve control (LVDT). From the terminal block (QTBA), all cables associated with the natrual gas system were removed.
Aguirre CC 2-1 | Trip unit by fuel control. | 2026-04-06 | 22:05 | 2026-04-07 | 15:22 | 17.3 | Changed the solenoid of the fuel bypass valve. Finished removing the cables associated with natural gas on the terminal block (QTBA).
Aguirre CC 2-1 | Trip unit by fuel control. | 2026-04-07 | 19:24 | 2026-04-08 | 14:03 | 18.7 | Changed the solenoid block.
Aguirre CC 2-1 | Trip unit by fuel control. | 2026-04-08 | 16:25 | 2026-04-08 | 18:19 | 1.9 | Disconnected RVDT #1 from the inlet guide vanes that was affecting the circuit.
Daguao 1-1 | Circuit breaker 0010 opened. | 2026-04-18 | 2:00 | 2026-04-19 | 15:48 | 37.8 | Luma staff reset breaker and closed it.
Daguao 1-1 | Ground fault main power transformer. Water ingress in connection box. | 2026-04-22 | 12:40 | 2026-04-24 | 17:49 | 53.15 | Cleaned, painted and replaced lid gasket preventive maintenace was performed.
Daguao 1-1 | Tripped due to fuel flow divider issues. | 2026-04-30 | 21:04 | 2026-04-30 | 21:32 | 0.47 | Calibrate and Master reset.
Daguao 1-2 | Ground fault main power transformer. Water ingress in connection box. | 2026-04-22 | 12:40 | 2026-04-24 | 17:49 | 53.15 | Cleaning, Painting and replaced cover gasket.
Daguao 1-2 | Circuit breaker 0010 opened. | 2026-04-18 | 2:00 | 2026-04-19 | 15:48 | 37.8 | Luma staff reset breaker and closed.
Mayaguez 2A | Unit trip due a erratic pressure differential in a scavange line. | 2026-04-28 | 19:23 | 2026-04-30 | 0:00 | 52.62 | Unit 2A was disengaged in order to have online 2B.
Mayaguez 2B | Because Unit 2A PT621 trip. Unit 2B can’t be online due to a high oil leak on 2A. | 2026-04-28 | 19:37 | 2026-04-30 | 0:00 | 24.1 | Unit 2A decoupled to keep Unit 2B available.
Mayaguez 3A | Unit was out due to a flame trip. | 2026-04-06 | 16:39 | 2026-04-06 | 19:51 | 3.2 | A software reset was made.
Mayaguez 4A | The unit exhibited a back pressure issue. This is typically caused by the fuel injection system, water injection system, or bleed valves that may or may not have opened at a specific point in time. A trendline analysis was performed to graphically identify the problem, and no discrepancies were found. | 2026-04-11 | 19:58 | 2026-04-30 | 24:00 | 460.03 | The data was sent to Mitsubishi. They instructed to calibrate the pressure transmitters and temperature sensors (TE). The process was been completed, and we are pending approval from Mitsubishi. Also, a boroscope inspection was made.
Mayaguez 4B | Unit trip due to a no light. | 2026-04-06 | 17:01 | 2026-04-07 | 17:07 | 24.1 | A replacement of the igniters was made.
Mayaguez 4B | The secondary fans located in the pump compartments have failed. | 2026-04-10 | 16:42 | 2026-04-10 | 16:57 | 0.25 | A software reset was made.
Mayaguez 4B | Because Unit A was under a boroscope inspection, unit B was not available. | 2026-04-14 | 9:26 | 2026-04-14 | 17:08 | 7.7 | Because Unit A was under a boroscope inspection, unit B was not available.
Mayaguez 4B | Because Unit A was under a boroscope inspection, unit B was not available. | 2026-04-15 | 9:03 | 2026-04-15 | 17:59 | 8.93 | Because Unit A was under a boroscope inspection, unit B was not available.
Mayaguez 4B | Unit was out due to a LUMA Switchyard open 0080 breaker. | 2026-04-19 | 18:02 | 2026-04-19 | 21:30 | 3.47 | LUMA personnel worked on Breaker 0080.
Mayaguez 4B | Unit 4A was under a pressure transmiter and temperature sensor calibration. Therefore Unit 4B was out. | 2026-04-22 | 15:22 | 2026-04-22 | 15:53 | 0.52 | Pressure transmitter and temperature sensor calibrated.
Mayaguez 4B | Unit out of service due to a permissive alarm on 4A. The alarm is related to metal and carbon particles in the filters and chip detectors. | 2026-04-28 | 22:05 | 2026-04-29 | 15:22 | 17.28 | Unit 4A was disengaged in order to have unit 4B online.
Costa Sur 5 | Platen superheater issue. | 2026-04-11 | 0:36 | 2026-04-15 | 0:30 | 95.89 | Boiler repaired, hydrostatic performed and unit synchronized.
Costa Sur 5 | Rotor collector rings issue. | 2026-04-15 | 0:55 | 2026-04-15 | 13:13 | 12.3 | Brush holder area cleaning performed and unit synchronized.
Costa Sur 6 | Main stop valves issue. | 2026-04-20 | 16:42 | 2026-04-30 | 24:00 | 247.3 | Pending repair of main steam inlet valves to the turbine.
San Juan TM 2 | Node fault. | 2026-04-28 | 18:30 | 2026-04-30 | 24:00 | 53.48 | System cleaned.
San Juan TM 2 | Node fault. | 2026-04-02 | 17:44 | 2026-04-02 | 19:05 | 1.35 | System cleaned.
San Juan TM 2 | Regas working relief valve. | 2026-04-25 | 7:45 | 2026-04-25 | 10:21 | 2.6 | Regas finished work.
San Juan TM 2 | Node fault. | 2026-04-28 | 14:12 | 2026-04-28 | 14:26 | 0.73 | System cleaned.
San Juan TM 3 | Regas working relief valve. | 2026-04-25 | 7:45 | 2026-04-25 | 10:21 | 2.6 | Regas finished work.
San Juan TM 4 | Regas working relief valve. | 2026-04-25 | 7:45 | 2026-04-25 | 10:21 | 2.6 | Regas finished work.
San Juan TM 7 | Undiagnostic trip. | 2026-04-02 | 18:46 | 2026-04-02 | 22:17 | 3.52 | Unit restarted.
San Juan CT 5 | Fire protection trip. | 2026-04-21 | 4:01 | 2026-04-21 | 9:19 | 5.3 | Incorrect signal system failure, instrumentation section bypass logic, unit back online.
San Juan CT 5 | Blade path temperature trip. | 2026-04-21 | 15:29 | 2026-04-21 | 16:20 | 0.85 | The automatic regulator failed. The regulator was bypassed and the system operated through the manual valve.
San Juan ST 5 | Fire protection trip. | 2026-04-21 | 4:01 | 2026-04-21 | 14:29 | 10.97 | Incorrect signal system failure, instrumentation section bypass logic, unit back online.
San Juan ST 5 | Blade path temperature trip. | 2026-04-21 | 15:29 | 2026-04-21 | 18:41 | 3.2 | The automatic regulator failed. The regulator was bypassed and the system operated through the manual valve.
Palo Seco 4 | Boiler lead leak. | 2026-04-09 | 21:40 | 2026-04-10 | 22:41 | 25.02 | The leak was corrected in the Boiler lead.
Palo Seco 4 | Broken Boiler lines. | 2026-04-16 | 0:14 | 2026-04-20 | 8:31 | 104.28 | Lines were fixed.
Palo Seco 4 | Broken Boiler lines. | 2026-04-27 | 19:51 | 2026-04-30 | 24:00 | 76.13 | Lines were fixed.
Palo Seco 1-2 | High exhaust temperature fuel nozzles need replacement. | 2026-04-09 | 17:00 | 2026-04-10 | 13:00 | 20 | Fuel nozzles replaced.
Palo Seco 1-2 | Fuel line leak. | 2026-04-27 | 19:17 | 2026-04-27 | 20:39 | 1.37 | Fuel line replaced.
Palo Seco 1-2 | Fuel line leak. | 2026-04-28 | 15:17 | 2026-04-29 | 17:43 | 26.43 | Fuel line replaced.
Palo Seco MP 1 | Turbine lubrication motor failed. | 2026-04-07 | 10:26 | 2026-04-07 | 16:19 | 5.88 | Replacement motor installed; scavenged from MP 3 unit.
Palo Seco MP 3 | Combustor replacement needed. | 2026-04-06 | 12:22 | 2026-04-24 | 20:17 | 439.92 | Replacement completed.
Palo Seco TM 2 | Loss of 480V. | 2026-04-17 | 19:00 | 2026-04-18 | 0:39 | 5.65 | Repairs completed.
Palo Seco TM 2 | VSV Driver failure. | 2026-04-29 | 20:09 | 2026-04-30 | 10:21 | 14.2 | VSV Pumps replaced.

## May 2026
May 2026 Forced Outages Report
Unit | Cause | Date Out | Time Out | Date In | Time In | Duration (Hrs) | Corrective Action
Aguirre CC 2-2 | Unit tripped over temperature exhaust gases, EX 2100 trip, Generator lockout, and external trip. Unit went up to 61 MW when Costa Sur 5 tripped. | 2026-05-25 | 21:56 | 2026-05-25 | 22:37 | 0.7 | The unit was normalized and put into service.
Aguirre CC 2-4 | Unit tripped when synchronizing by Inlet Guide Vane Control Trouble trip. | 2026-05-19 | 16:37 | 2026-05-19 | 17:25 | 0.8 | The L4IGVT signal was forced.
Aguirre CC 2-4 | Unit tripped over temperature exhaust gases, EX 2100 trip, Generator lockout, and external trip. Unit went up to 61 MW when Costa Sur 5 tripped. | 2026-05-25 | 21:56 | 2026-05-25 | 22:50 | 0.9 | The unit was normalized and ran at 3,600 rpm, LUMA TOC did not want it in service.
Aguirre CC 1-1 | Unit trip due to exhaust blower 1-1B output. | 2026-05-30 | 16:23 | 2026-05-30 | 17:07 | 0.7 | The unit was available with the exhaust blower 1-1A. The next day the motor was changed to 1-1B.
Cambalache 3 | Engine trip by low frequency. Electrical grid disturbance originated in Costa Sur 6 unit. | 2026-05-04 | 16:49 | 2026-05-04 | 18:59 | 2.17 | None. Out of Management Control (OMC) event for Cambalache plant.
Costa Sur 6 | Unit 6 on 100% Bunker C. Bunker C control valve water accumulator broke apart causing the valve to shut instantaneously. This also caused a master fuel trip and tripped the Boiler and the unit out of service. | 2026-05-04 | 16:48 | 2026-05-04 | 18:38 | 1.85 | Water accumulator eliminated from the instrumentation line supply and proceeded with the synchronization of the unit.
Costa Sur 5 | MKVI activated the prot trip. | 2026-05-25 | 21:55 | 2026-05-28 | 13:03 | 63.13 | Checked the internal and termination wiring, also the circuit for the MKVI cabinet and proceeded with the synchronization of the unit.
Mayaguez 2B | Flame out trip. | 2026-05-02 | 1:18 | 2026-05-02 | 8:02 | 6.73 | A reset was performed.
Mayaguez 2B | Flame out trip. | 2026-05-06 | 1:21 | 2026-05-06 | 16:18 | 14.95 | The igniters were cleaned and swapped out.
Mayaguez 3A | The Hydraulic System started a Permissive trip. | 2026-05-11 | 5:42 | 2026-05-11 | 7:25 | 1.72 | A reset was performed.
Mayaguez 3A | Uni 3B was being aligned, therefore unit 3A was unavailable. | 2026-05-15 | 8:36 | 2026-05-16 | 17:01 | 32.42 | Alignment completed.
Mayaguez 3B | Unit 3B PB DOT trip. A boroscope was performed. Also pressure transmitters were high. Those are related with the scavange. | 2026-05-18 | 20:19 | 2026-05-29 | 18:27 | 262.13 | A boroscope was performed. Pressure Transmitters were calibrated, solenoid valve were replaced.
Mayaguez 3B | Pressure Transmitters remained high. | 2026-05-29 | 18:35 | 2026-05-30 | 14:09 | 19.57 | A loose fitting was found.
Palo Seco 3 | Broken Boiler. | 2026-05-21 | 13:08 | 2026-05-31 | 23:59 | 250.85 | Corrected.
Palo Seco 4 | Broken Boiler. | 2026-05-10 | 20:08 | 2026-05-13 | 12:45 | 64.62 | Corrected.
Jobos 1-2 | Transformer 4003 out of service. Breaker 0010 open. | 2026-05-05 | 11:34 | 2026-05-05 | 19:35 | 8.1 | Luma corrected the fault in the transformer and closed breaker 0010. Out of Management Control (OMC) event for GeneraPR.
San Juan 9 | Electrical failure on Boiler Feed Pump 9-2. | 2026-05-23 | 15:20 | 2026-05-25 | 16:25 | 49.08 | Checked connections on Boiler Feed Pump 9-2 and certified a burned motor.
San Juan TM 10 | Lost of mega vars controls. | 2026-05-19 | 5:14 | 2026-05-19 | 7:51 | 2.62 | Inspected and reset.
San Juan TM 10 | N1n5 node fault. | 2026-05-23 | 20:06 | 2026-05-23 | 23:35 | 3.48 | Cleaned and reset.
San Juan TM 10 | Breaker issue. | 2026-05-25 | 1:15 | 2026-05-26 | 5:14 | 27.98 | Breaker repaired.
San Juan TM 2 | Node n-1 issues. | 2026-05-01 | 16:06 | 2026-05-04 | 16:36 | 72.5 | System cleaned and reset.
San Juan TM 2 | Node n-1 issues. | 2026-05-04 | 20:35 | 2026-05-06 | 16:25 | 43.83 | System cleaned and reset.
San Juan TM 2 | Node n-1 issues. | 2026-05-08 | 21:32 | 2026-05-12 | 12:00 | 86.47 | System cleaned and reset.
San Juan TM 2 | Node n-1 issues. | 2026-05-12 | 15:53 | 2026-05-14 | 14:55 | 47.03 | System cleaned and reset.
San Juan TM 2 | Node n-1 issues. | 2026-05-15 | 15:09 | 2026-05-21 | 17:42 | 146.55 | System cleaned and reset.
San Juan TM 2 | Node n-1 issues. | 2026-05-28 | 16:30 | 2026-05-31 | 23:59 | 79.48 | System cleaned and reset.
San Juan TM 2 | Node n-1 issues. | 2026-05-28 | 15:19 | 2026-05-28 | 16:09 | 0.83 | System cleaned and reset.
San Juan TM 5 | Main breaker failure. | 2026-05-25 | 1:16 | 2026-05-25 | 2:22 | 2.1 | Breaker fixed.
San Juan TM 3 | Main breaker failure. | 2026-05-25 | 1:16 | 2026-05-25 | 2:22 | 2.1 | Breaker fixed.
San Juan TM 7 | Main breaker failure. | 2026-05-25 | 1:16 | 2026-05-25 | 2:22 | 2.1 | Breaker fixed.

## June 2026
June 2026 Forced Outages Report
Unit | Description | Date Out | Time Out | Date In | Time In | Duration (Hrs) | Corrective Action
Aguirre CC 1-1 | Unit trip over temperature exahust gases (spread trip). | 2026-06-01 | 16:34 | 2026-06-01 | 18:42 | 2.1 | Themocouples #4 and #12 they crossed the signal with thermocouple #5 and #1, respectively. Another day they were changed.
Aguirre CC 2-1 | It was not a unit trip. When taking baterry bank 2-1 out of service, breaker 0012 and 0014 opened on the 230kv. | 2026-06-04 | 14:16 | 2026-06-04 | 17:00 | 2.7 | Battery bank 2-1 was put into service, 2 fuses on the UPS were replaced, and the trip coil on the incomming breaker 2A (4.16kv) was changed.
Aguirre CC 2-1 | Unit trip with output bars explore. | 2026-06-13 | 8:42 | 2026-06-18 | 20:28 | 131.8 | Completed, the output bars were removed, the insulation was changed and bars were cleaned. A test was perfomed on the transformer.
Aguirre CC 2-1 | Unit trip due to generator and exciter fault. Generator and transfomer lockout activated, relay 87T-2 and 87G-2. | 46195 | 0.94931 | 46203 | 0.99999 | 193.2 | The unit was disconnected from the transformer to isolate the fault.
Aguirre CC 2-2 | It was not a unit trip. When taking baterry bank 2-1 out of service, breaker 0012 and 0014 opened on the 230kv. | 46177 | 0.59444 | 46177 | 0.70833 | 2.7 | Battery bank 2-1 was put into service, 2 fuses on the UPS were replaced, and the trip coil on the incomming breaker 2A (4.16kv) was changed.
Aguirre CC 2-2 | Unit trip when U2-1 output bars explode. Lockout generator. | 46186 | 0.3625 | 46187 | 0.775 | 33.9 | The U2-1 output bars were diconnected to isolate the fault.
Aguirre CC 2-2 | Unit trips when it syncs U2-1 for generator lockkout and relay 64G-2. Only one unit can be in service, going out through MPT 2-1/2-2. | 46191 | 0.87361 | 46197 | 0.70069 | 139.9 | After the U2-1 exciter explosion, it disconnected from the transformer and the relays of the U2-2 generator were calibrated.
Aguirre CC 2-4 | It was not a unit trip. When taking baterry bank 2-1 out of service, breaker 0012 and 0014 opened on the 230kv. | 46177 | 0.59444 | 46177 | 0.70833 | 2.7 | Battery bank 2-1 was put into service, 2 fuses on the UPS were replaced, and the trip coil on the incomming breaker 2A (4.16kv) was changed.
Aguirre CC 2-4 | It was not a unit trip, it was out of service when the fault occurred in the U2-1 output bars. | 46186 | 0.3625 | 46186 | 0.47222 | 2.6 | Completed, MOD 0015 was opened to isolate the fault and be able to energize the 230kv.
Aguirre CC 2-4 | Unit trips due to the area exciter U2-1 explotion when the 230kv goes out. | 46195 | 0.94931 | 46196 | 0.36806 | 10.1 | Completed, MOD 0015 was opened to isolate the fault and be able to energize the 230kv.
Cambalache 2 | Unavailability of the turbine's CO2 fire protection system. For safety reasons, the unit cannot operate without a fire protection system. | 46191 | 0.41319 | 46199 | 0.68889 | 198.61 | Repair on compressor and filling of the CO2 tank of the turbine fire protection system.
Cambalache 3 | Unavailability of the turbine's CO2 fire protection system. For safety reasons, the unit cannot operate without a fire protection system. | 46191 | 0.41319 | 46199 | 0.68889 | 198.61 | Repair on compressor and filling of the CO2 tank of the turbine fire protection system.
Mayaguez 3A | Inspection revealed that the starter of Unit 3B was damaged. Prior to this finding, the operators had shutted down both units 3A & 3B due to abnormal noise originating from within the equipment. | 46174 | 0.73264 | 46174 | 0.75417 | 0.52 | After confirming that the source of the noise was the starter of Unit 3B, Unit 3A was released for operation and placed back into service.
Mayaguez 3A | One of the PLC cards failed, resulting in erroneous readings from PT501/PT502, which caused the unit to trip, as well as incorrect readings from other pressure transmitters, including PT1011 and PT1012. | 46182 | 0.22986 | 46182 | 0.42708 | 4.73 | The defective card was identified and replaced, restoring normal operation.
Mayaguez 3A | Switchyard breaker 0010 opened while the unit was in operation, resulting in a unit shutdown/trip. | 46186 | 0.76111 | 46186 | 0.80069 | 0.95 | LUMA was requested to reclose the breaker, as it falls under their area of responsibility. A subject matter expert later identified that the issue was caused by an Main Power Transformer relay associated with the step-up transformer (13.8 kV/115 kV). The issue was successfully resolved.
Mayaguez 3B | Inspection revealed that the starter of Unit 3B was damaged. Prior to this finding, the operators had shutted down both units 3A & 3B due to abnormal noise originating from within the equipment. | 46174 | 0.70347 | 46175 | 0.33333 | 15.12 | Starter was replaced.
Mayaguez 3B | One of the PLC cards failed, resulting in erroneous readings from PT501/PT502, which caused the unit to trip, as well as incorrect readings from other pressure transmitters, including PT1011 and PT1012. | 46182 | 0.2125 | 46182 | 0.42708 | 5.15 | The defective card was identified and replaced, restoring normal operation.
Mayaguez 3B | Switchyard breaker 0010 opened while the unit was in operation, resulting in a unit shutdown/trip. | 46186 | 0.76111 | 46186 | 0.80069 | 0.95 | LUMA was requested to reclose the breaker, as it falls under their area of responsibility. A subject matter expert later identified that the issue was caused by an MPT relay associated with the step-up transformer (13.8 kV/115 kV). The issue was successfully resolved.
Palo Seco 1-2 | Igniter issues. | 46198 | 0.70833 | 46200 | 0.45556 | 41.93 | Reset igniter.
Palo Seco 1-2 | Igniter issues. | 46201 | 0.76042 | 46202 | 0.83333 | 25.75 | Reset igniter.
Palo Seco 1-2 | Fuel leak. | 46202 | 0.86944 | 46203 | 0.99999 | 27.12 | Corrected.
Palo Seco 1-2 | Fuel leak. | 46203 | 0.69861 | 46203 | 0.71875 | 0.48 | Corrected.
Palo Seco 3 | Broken Boiler. | 46174 | 0.93125 | 46177 | 0.49722 | 61.58 | Leaks corrected.
Palo Seco 3 | Real air flow indicator bad signal caused trip. | 46197 | 0.48611 | 46197 | 0.64444 | 3.8 | Indicator corrected.
San Juan TM 2 | Node n-1 issues. | 46177 | 0.42847 | 46182 | 0.45139 | 120.55 | System inspected and reset.
San Juan TM 6 | Synchronizer fail. | 46175 | 0.76319 | 46175 | 0.79792 | 0.83 | Synchonizer fixed.
San Juan TM 7 | High temperature spread. | 46195 | 0.93403 | 46196 | 0.64583 | 17.08 | Technician replaced bolts.
San Juan TM 10 | Instrumentation fail. | 46196 | 0.65764 | 46196 | 0.67083 | 0.32 | System inspected and reset.
San Juan 9 | Fire on burner corner C. | 46190 | 0.19444 | 46203 | 0.99999 | 331.33 | Repairs in progress.
Jobos 1-2 | The turbine does not slow down enought to start. | 46180 | 0.78264 | 46182 | 0.68403 | 45.63 | Valve replacement 20 TU.
Daguao 1-1 | Generator Voltage Control trouble. | 46176 | 0.74167 | 46176 | 0.75 | 0.2 | The Unit was repaired and brought back online.
Daguao 1-2 | Diesel leak at nozzle number 5. | 46182 | 0.64375 | 46182 | 0.66667 | 0.55 | The leak was repaired and brought back online.
Daguao 1-2 | High exhaust temperature spread. | 46184 | 0.71181 | 46187 | 0.69167 | 71.52 | The nozzles were replaced with new nozzles.
Daguao 1-2 | The water supply line to the speed reducer broke. | 46187 | 0.83889 | 46187 | 0.99653 | 3.78 | The water line was repaired and returned to service.
Daguao 1-2 | Flame detector failure the unit was cycling on and off. | 46188 | 0.70972 | 46188 | 0.84514 | 3.25 | The flame detector cable was found broke, it was replaced.
Daguao 1-2 | Flame detector fault, causing the unit to trip. | 46191 | 0.72569 | 46191 | 24:00 | 6.58 | The flame detector were removed, cleaned and the unit was returned to service.
Daguao 1-1 | Ignition cable broke, preventing the unit from starting. | 46192 | 0.81944 | 46192 | 0.97917 | 3.83 | The ignition cables were replaced, and the unit was returned to service.
Daguao 1-1 | High exhaust temperature spread. | 46193 | 0.63889 | 46193 | 0.75694 | 2.83 | Fuel check valves were replaced,and the unit was returned to service.
Daguao 1-2 | Cooling system fan drive failure, causing the unit to trip on high temperature. | 46194 | 0.5625 | 46194 | 0.6875 | 3 | The fan system pins were repaired, and the unit was returned to service.

## Grouped by Cause
Fiscal Year 2026 (July 2025 to June 2026) Units with Two or More Events from the Same System
Unit | System | What Failed | Number of Events | Total Duration (Hrs) | Dates Out | Quarters | Changes Made to the Maintenance Program
San Juan TM 2 | Controls, instrumentation and protection | Control node fault | 11 | 652.8 | Apr 2, 28; May 1, 4, 8, 12, 15, 28; Jun 4 | Q4 | These outages did not result in changes to the maintenance program since this temporary unit does not represent significant capacity in the system.
Aguirre CC 2-1 | Fuel system | Fuel bypass valve (solenoids and cables); Fuel bypass valve (position indicator); Gas fuel system; Fuel control card (speed pickup); Fuel control (bypass valve); Fuel control; Fuel control trip | 11 | 153.7 | Oct 16, 19, 20; Dec 23, 26; Mar 31; Apr 1, 6, 7, 8 | Q2, Q3, Q4 | These outages did not result in changes to the maintenance program since they were relatively short outages.
San Juan TM 2 | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Lube oil system | 11 | 23.17 | Dec 19, 23, 28; Jan 18; Mar 2, 4, 7, 17, 19, 20, 31 | Q2, Q3 | These outages did not result in changes to the maintenance program since this temporary unit does not represent significant capacity in the system.
Aguirre 2 | Boiler pressure parts | Economizer piping; Desuperheaters / attemperators; Boiler tubes; Waterwall tubes | 6 | 583.62 | Aug 8, 31; Nov 7; Dec 8; Feb 6, 24 | Q1, Q2, Q3 | These outages did not result in changes to the maintenance program since they were relatively short outages.
Palo Seco 4 | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Circulating water and condenser vacuum; Boiler feed pump; Boiler feed pump line; Air compressor drain solenoid | 6 | 128.31 | Oct 3, 4, 7, 19; Nov 4; Dec 11 | Q2 | These outages did not result in changes to the maintenance program since they were relatively short outages and occurred in the low-demand season.
Palo Seco 1-2 | Fuel system | Fuel nozzles; Fuel line leak | 6 | 96.9 | Nov 16; Apr 9, 27, 28; Jun 29, 30 | Q2, Q4 | These outages did not result in changes to the maintenance program since this peaking unit does not represent significant capacity in the system and is proposed for retirement in the Integrated Resource Plan.
Aguirre CC 2-1 | Generator, excitation and output bus | Excitation (loss of excitation, EX2100); Excitation (EX2100 communication); Generator output bars (heater cable); Generator output bars; Generator and exciter fault | 5 | 414.2 | Jan 18; Feb 25; Mar 10; Jun 13, 22 | Q3, Q4 | These outages did not result in changes to the maintenance program since this unit does not represent significant capacity in the system.
Daguao 1-2 | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Lube oil high temperature; Cooling fan coupling; Lube oil pump; Speed reducer cooling water line; Cooling fan drive | 5 | 162.23 | Nov 10, 14; Dec 27; Jun 14, 21 | Q2, Q4 | These outages did not result in changes to the maintenance program since they were relatively short outages and this peaking unit does not represent significant capacity in the system.
Mayaguez 3A | Controls, instrumentation and protection | Speed sensor; PLC card | 5 | 48.18 | Mar 8, 19, 21, 22; Jun 9 | Q3, Q4 | The maintenance program was changed: a preventive maintenance task to verify speed sensor calibration, cable integrity and connections is being implemented.
San Juan CT 6 | Generator, excitation and output bus | Exciter | 5 | 34.4 | Jul 11, 24, 25, 26 | Q1 | These outages did not result in changes to the maintenance program since they were relatively short outages.
Costa Sur 5 | Boiler pressure parts | Platen superheater tubes; Platen superheater | 4 | 381.57 | Jul 4; Oct 2; Jan 27; Apr 11 | Q1, Q2, Q3, Q4 | These outages did not result in changes to the maintenance program since they were relatively short outages.
San Juan 9 | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Instrument air compressors; Induced draft fan; Circulating water pump 9-1; Boiler feed pump 9-2 motor | 4 | 298.58 | Jul 24; Sep 23; Mar 22; May 23 | Q1, Q3, Q4 | These outages did not result in changes to the maintenance program since they were relatively short outages.
Palo Seco 4 | Boiler pressure parts | Boiler lead leak (valve packing); Boiler tube failure | 4 | 270.05 | Apr 9, 16, 27; May 10 | Q4 | These outages did not result in changes to the maintenance program since they were relatively short outages.
Aguirre 2 | Generator, excitation and output bus | Voltage regulator (AVR); Rotor collector rings; Rotor field ground | 4 | 141.2 | Sep 29; Oct 26; Nov 3 | Q1, Q2 | These outages did not result in changes to the maintenance program since they were relatively short outages.
San Juan CT 6 | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Boiler water condition; Circulating water piping; Condenser vacuum pump B | 4 | 82.45 | Jul 17, 28; Oct 16; Jan 27 | Q1, Q2, Q3 | These outages did not result in changes to the maintenance program since they were relatively short outages.
Aguirre CC 1-2 | Controls, instrumentation and protection | Exhaust temperature spread (control programming); Mark VIe control; Exhaust thermocouple; Inlet guide vane block (oil leak) | 4 | 72 | Jul 22; Oct 24; Dec 15, 31 | Q1, Q2, Q3 | These outages did not result in changes to the maintenance program since they were relatively short outages.
Mayaguez 3A | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Water injection (shut-off valve and relay); Water injection system; Hydraulic system permissive | 4 | 25.6 | Dec 3; Mar 30; May 11 | Q2, Q3, Q4 | The maintenance program was changed: a preventive maintenance task to inspect the water injection system, including pressure transmitter and flow meter calibration, is being implemented.
Aguirre CC 2-4 | Controls, instrumentation and protection | Exhaust temperature spread (control programming); Bearing 1 vibration sensor; Inlet guide vane control; Exhaust over-temperature and EX2100 protection trip | 4 | 5.2 | Jul 22; Mar 15; May 19, 25 | Q1, Q3, Q4 | These outages did not result in changes to the maintenance program since they were relatively short outages.
Jobos 1-2 | Starting system | Turning gear and motor; Torque converter (SSS clutch); Valve 20TU (unit does not slow down to start) | 3 | 793.93 | Dec 4; Mar 1; Jun 7 | Q2, Q3, Q4 | These outages did not result in changes to the maintenance program since this peaking unit does not represent significant capacity in the system.
Daguao 1-1 | Electrical (breakers, transformers, DC and auxiliary power) | Main power transformer; Main power transformer ground fault (water ingress) | 3 | 389.15 | Dec 31; Mar 1; Apr 22 | Q2, Q3, Q4 | These outages did not result in changes to the maintenance program since this peaking unit does not represent significant capacity in the system.
Palo Seco 3 | Boiler pressure parts | Boiler water line; Boiler tube failure | 3 | 370.33 | Nov 21; May 21; Jun 1 | Q2, Q4 | These outages did not result in changes to the maintenance program since no outages were scheduled for May and June.
Palo Seco MP 2 | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Generator DC lube oil pump; AC lube oil pump motor; Lube oil system | 3 | 308.48 | Jan 3, 16; Feb 18 | Q3 | These outages did not result in changes to the maintenance program since this peaking unit does not represent significant capacity in the system.
Mayaguez 3B | Controls, instrumentation and protection | Pressure transmitters (PB DOT trip); Pressure transmitters (loose fitting); PLC card | 3 | 286.85 | May 18, 29; Jun 9 | Q4 | These outages did not result in changes to the maintenance program since this peaking unit does not represent significant capacity in the system.
Palo Seco MP 1 | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Generator DC lube oil pump; Generator lube oil motor and gas hose; Lube oil motor | 3 | 175.15 | Jan 23; Mar 22; Apr 7 | Q3, Q4 | These outages did not result in changes to the maintenance program since this peaking unit does not represent significant capacity in the system.
Costa Sur 6 | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Air heater fouling; Boiler recirculation pump motor; Boiler recirculation (flow meter) | 3 | 135.14 | Aug 1; Sep 26, 28 | Q1 | These outages did not result in changes to the maintenance program since they were relatively short outages.
Aguirre CC 2-2 | Controls, instrumentation and protection | Inlet guide vane solenoids; Inlet guide vane control; Exhaust over-temperature and EX2100 protection trip | 3 | 47 | Dec 29; Mar 21; May 25 | Q2, Q3, Q4 | These outages did not result in changes to the maintenance program since they were relatively short outages.
Mayaguez 4B | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Secondary fan limit switch; Water injection level switch; Pump compartment secondary fans | 3 | 46.09 | Jan 11, 18; Apr 10 | Q3, Q4 | The maintenance program was changed: a new preventive maintenance task inspects the secondary fan limit switch and alarm settings.
San Juan TM 10 | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Hydraulic oil pumps; Water injection metering valve; Lube oil system | 3 | 39.49 | Nov 17; Dec 16, 30 | Q2 | These outages did not result in changes to the maintenance program since this temporary unit does not represent significant capacity in the system.
Aguirre CC 2-2 | Fuel system | Fuel piping and valves; Fuel filters (line welded); Fuel filters (tubes welded) | 3 | 33.7 | Aug 3, 4 | Q1 | These outages did not result in changes to the maintenance program since they were relatively short outages.
San Juan CT 5 | Fire protection | Fire protection; Fire protection (water intrusion); False fire protection signal (water intrusion) | 3 | 29.92 | Sep 11; Mar 26; Apr 21 | Q1, Q3, Q4 | The maintenance program was changed: enclosure and seal integrity checks are being added to the preventive maintenance.
Aguirre 2 | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Instrument air header pressure; Condenser vacuum pump 2-1 | 3 | 15.63 | Jan 3; Apr 12, 13 | Q3, Q4 | The maintenance program was changed: the coupling lubrication task was reinstated at Aguirre and Costa Sur, and its interval was reduced from six to three months.
San Juan CT 5 | Controls, instrumentation and protection | Blade path temperature; Hot reheat bypass instrumentation; Blade path temperature regulator | 3 | 10.32 | Feb 7; Mar 8; Apr 21 | Q3, Q4 | These outages did not result in changes to the maintenance program since they were relatively short outages.
San Juan TM 10 | Controls, instrumentation and protection | Reactive power (MVAR) control; Control node fault; Instrumentation | 3 | 6.42 | May 19, 23; Jun 23 | Q4 | These outages did not result in changes to the maintenance program since this temporary unit does not represent significant capacity in the system.
San Juan CT 5 | Gas turbine combustion, compressor and hot section | Combustion inspection; Combustors (combustion inspection) | 2 | 893.42 | Oct 17; Nov 19 | Q2 | The maintenance program was affected because the transmission and distribution operator did not authorize the scheduled outage. Nevertheless, Genera decided to force the outage to perform borescope inspections and turbine repairs. The original equipment manufacturer, after these inspections, recommended that the unit be taken out of service for the turbine repairs, as established under the long-term service agreement (had Genera not done so, it would have been out of compliance with that agreement).
San Juan CT 6 | Turbine bearings, gears and vibration | Bearing inspection; Steam turbine work | 2 | 290 | Aug 26; Dec 16 | Q1, Q2 | The maintenance program was affected because the transmission and distribution operator did not authorize the scheduled outage. Nevertheless, Genera decided to force the outage to perform borescope inspections and turbine repairs. The original equipment manufacturer, after these inspections, recommended that the unit be taken out of service for the turbine repairs, as established under the long-term service agreement (had Genera not done so, it would have been out of compliance with that agreement).
Costa Sur 6 | Steam and turbine valves | Main steam valve; Main stop valves | 2 | 274.4 | Aug 4; Apr 20 | Q1, Q4 | The maintenance program was changed: a new preventive maintenance task to disassemble, inspect and refurbish the main and reheat stop valves every two years during environmental outages.
Aguirre CC 2-2 | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Atomizing air system; Atomizing air system (oil consumption); Lube oil tank gasket | 2 | 231.7 | Oct 27; Nov 6 | Q2 | These outages did not result in changes to the maintenance program since this unit does not represent significant capacity in the system.
San Juan TM 7 | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Service water valve FCV-2019; Water injection pump | 2 | 231.24 | Sep 21; Jan 13 | Q1, Q3 | These outages did not result in changes to the maintenance program since this temporary unit does not represent significant capacity in the system.
Palo Seco MP 3 | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Generator lube oil pump coupling; Turbine lube oil seal | 2 | 206.57 | Feb 21; Mar 3 | Q3 | These outages did not result in changes to the maintenance program since this peaking unit does not represent significant capacity in the system.
San Juan TM 4 | Controls, instrumentation and protection | Control CPU card (Micronet); Liquid fuel manifold thermocouple | 2 | 201.87 | Dec 8; Mar 25 | Q2, Q3 | These outages did not result in changes to the maintenance program since this temporary unit does not represent significant capacity in the system.
San Juan ST 5 | Turbine bearings, gears and vibration | Turbine vibration; Turbine bearing vibration | 2 | 193.24 | Feb 7; Mar 24 | Q3 | These outages did not result in changes to the maintenance program; the root cause analysis proposes a turbine overhaul to correct the condition.
Costa Sur 6 | Boiler pressure parts | Waterwall tubes | 2 | 167.9 | Nov 16; Dec 1 | Q2 | These outages did not result in changes to the maintenance program since they were relatively short outages.
Aguirre 2 | Electrical (breakers, transformers, DC and auxiliary power) | Main transformer grounding | 2 | 162.21 | Jul 11; Aug 15 | Q1 | These outages did not result in changes to the maintenance program since they were relatively short outages.
Palo Seco 1-2 | Starting system | Starting diesel engine acceleration control valve; Starting system DC control cable | 2 | 94.15 | Jan 24; Feb 18 | Q3 | These outages did not result in changes to the maintenance program since this peaking unit does not represent significant capacity in the system and is proposed for retirement in the Integrated Resource Plan.
Daguao 1-2 | Electrical (breakers, transformers, DC and auxiliary power) | Main power transformer; Main power transformer ground fault (water ingress) | 2 | 77.15 | Dec 31; Apr 22 | Q2, Q4 | These outages did not result in changes to the maintenance program since this peaking unit does not represent significant capacity in the system.
Daguao 1-2 | Fuel system | Fuel nozzles | 2 | 72.07 | Jun 9, 11 | Q4 | These outages did not result in changes to the maintenance program since this peaking unit does not represent significant capacity in the system.
Palo Seco 1-2 | Ignition and flame detection | Igniters | 2 | 67.68 | Jun 25, 28 | Q4 | These outages did not result in changes to the maintenance program since this peaking unit does not represent significant capacity in the system and is proposed for retirement in the Integrated Resource Plan.
Jobos 1-2 | Controls, instrumentation and protection | Synchronization (load breaker connections); Speed sensor connection | 2 | 60.05 | Mar 3, 29 | Q3 | These outages did not result in changes to the maintenance program since this peaking unit does not represent significant capacity in the system.
Palo Seco 4 | Fuel system | Fuel pump 4-1 | 2 | 35 | Nov 11; Mar 31 | Q2, Q3 | These outages did not result in changes to the maintenance program since they were relatively short outages.
San Juan 9 | Boiler pressure parts | Waterwall; Boiler lines | 2 | 25.9 | Jul 27; Feb 15 | Q1, Q3 | These outages did not result in changes to the maintenance program since they were relatively short outages.
Mayaguez 4B | Fuel system | Fuel governor solenoid; Fuel solenoid valve | 2 | 25.66 | Mar 24, 26 | Q3 | The maintenance program was changed: a new preventive maintenance task inspects the solenoid valves, with progressive replacement of aging valves.
Mayaguez 2B | Ignition and flame detection | Flame out (igniters) | 2 | 21.68 | May 2, 6 | Q4 | The maintenance program was changed: a new preventive maintenance task for periodic igniter inspection and cleaning.
Palo Seco TM 2 | Controls, instrumentation and protection | Variable stator vane driver cable; Variable stator vane driver | 2 | 16.78 | Dec 13; Apr 29 | Q2, Q4 | These outages did not result in changes to the maintenance program since this temporary unit does not represent significant capacity in the system.
Costa Sur 5 | Generator, excitation and output bus | Generator neutral grounding; Rotor collector rings | 2 | 16.29 | Feb 2; Apr 15 | Q3, Q4 | The maintenance program is being changed: a procedure for deep cleaning of the brush area during short outages is being prepared.
Aguirre CC 2-1 | Electrical (breakers, transformers, DC and auxiliary power) | 480 V bars and breaker | 2 | 15.2 | Aug 1, 6 | Q1 | These outages did not result in changes to the maintenance program since they were relatively short outages.
Daguao 1-2 | Ignition and flame detection | Flame detector | 2 | 9.83 | Jun 15, 18 | Q4 | These outages did not result in changes to the maintenance program since they were relatively short outages and this peaking unit does not represent significant capacity in the system.
Aguirre CC 1-1 | Controls, instrumentation and protection | Bearing 2 vibration sensor; Exhaust thermocouples (spread trip) | 2 | 4.8 | Aug 2; Jun 1 | Q1, Q4 | These outages did not result in changes to the maintenance program since they were relatively short outages.
Cambalache 2 | Gas turbine combustion, compressor and hot section | Exhaust temperature; Compressor stage 3 blow-off valve | 2 | 4.52 | Oct 6; Mar 2 | Q2, Q3 | These outages did not result in changes to the maintenance program since they were relatively short outages.
San Juan CT 5 | Auxiliaries (pumps, fans, cooling, lubrication, hydraulics) | Feedwater pump; Circulating water pump bearing temperature sensor | 2 | 4.1 | Oct 17; Dec 23 | Q2 | These outages did not result in changes to the maintenance program since they were relatively short outages.
Daguao 1-1 | Fuel system | Fuel flow divider; Fuel check valves | 2 | 3.3 | Apr 30; Jun 20 | Q4 | These outages did not result in changes to the maintenance program since they were relatively short outages and this peaking unit does not represent significant capacity in the system.
Mayaguez 4B | Turbine bearings, gears and vibration | Power turbine thrust bearing balance | 2 | 3.25 | Sep 23, 26 | Q1 | These outages did not result in changes to the maintenance program since they were relatively short outages and this peaking unit does not represent significant capacity in the system.
San Juan TM 6 | Controls, instrumentation and protection | Speed pickup (accelerometer); Synchronizer | 2 | 1.41 | Mar 21; Jun 2 | Q3, Q4 | These outages did not result in changes to the maintenance program since they were relatively short outages and this temporary unit does not represent significant capacity in the system.